## Intro
DEER2016 Lighting Measures HVAC Interactive Effects and Adjustment Factor tables
Updated on 5/27/2015
This workbook presents the lighting hours-of-use (HOU), peak period coincident demand (CDF) and HVAC Interactive Effects for the DEER2016 update.
The DEER2016 update includes commercial indoor Linear Fluorescent, CFL and High-Bay Lighting applications only.
Tab |  | Description and Usage
Intro |  | information on workbook contents
Ltg HVAC IE Values |  | table with lighting HVAC interactive effects values, independent values chosen via radio controls and pull-down lists
DEER2014 |  | output from DEER2014 for lighting "basis" measures: normalized lighting measure impacts for each lighting category (downloaded via READI)
DEER2016 |  | output from DEER2016 for lighting "basis" measures: normalized lighting measure impacts for each lighting category (downloaded via READI with extended precision)
Note: DEER2016 did not update Residential indoor CFL energy impacts nor Commercial Exit lighting energy impacts.
Note: all interactive effects values and adjustment values are calculated based on the normalized energy impacts in the above two tabs
[Ltg HVAC IE Values] tab
This sheet presents normalized DEER lighting measure results and HVAC Interactive Effects for three lighting measure types.
The results are presented based on the following radio box and list selections:
| IOU | all values are specific to one of the three electric IOUs
| Building Vintage | Building vintage is either New or Existing
| Occ Sens Scenario | DEER2014 includes three occupancy sensor scenarios (see below for description)
Note: DEER2011 has results for "No Occupancy Sensors" only
| Climate Zone | Pull-down list of Title-24 climate zones plus the weighted IOU territory location
| Lighting Type | measure type is either Non-CFL (Linear Fluorescent and HID), CFL (including LED measures) or Exit Fixtures
Note: residential building types have results for CFL lighting type only
| DEER Version | DEER2011 or DEER2014 (update of DEER2011 based on 2013 Title-24 building codes)
| Building Type | Building type is any of the standard DEER building types or a sector weighted version (Com or Res)
IE Table Column Description
| Pre-Existing | EFLH | lighting system equivalent full-load hours for the pre-existing case
| Pre-Existing | CDF | lighting system coincident demand factor for the pre-existing case
| Measure | EFLH | lighting system equivalent full-load hours for the code/standard and measure cases
| Measure | CDF | lighting system coincident demand factor for the code/standard and measure cases
| Energy Impacts | (6 columns) | normalized energy impacts for the lighting measure, savings are per delta Watt of the improved lighting system
and include the direct lighting system energy savings and the HVAC interactive effects.
| HVAC IE Factors | kWh/kWh | defined as the whole-building electric energy savings divided by the direct end-use electric energy savings of the lighting measure
| HVAC IE Factors | kW/kW | defined as the whole-building electric demand savings divided by the direct end-use electric demand savings of the lighting measure
| HVAC IE Factors | therm/kWh | defined as the whole-building gas energy savings divided by the direct end-use electric energy savings of the lighting measure
Note: multiply direct energy impacts by the appropriate IE factor to determine the whole-building energy impacts of lighting measures.
Lighting Hours-of-Use, Coincident demand factor and normalized energy impacts are available for three occupancy sensor scenarios:
| No OS | No occupancy sensors assumed in the lighting system for all cases (pre-existing, code/standard and measure cases); this is the only option for DEER2011
| Building OS | Building-wide average Occupancy Sensors in the pre-existing case for recent vintages (after 2009), and in the code/standard and measure cases, only available for DEER2014
| All Space OS | Occupancy Sensors in all appropriate spaces in all cases (pre-existing, code/standard and measure cases), only available for DEER2014
Note: interactive effects factors do not vary by occupancy sensor scenario

## Ltg HVAC IE Values
Indoor Lighting Measures Energy Impacts and HVAC Interactive Effects
based on DEER2014 and Draft DEER2016 READI output for the normalized lighting measures impacts
|  |  | 1 |  |  |  | 1 |  |  |  |  | 1
|  |  | PGE |  |  |  | Ex |  |  |  |  | None | [7 empty] | 3
[18 empty] | ranges |  | 10.71
|  | 2 | [5 empty] | 2 |  |  |  |  | 1 |  |  |  |  | DEER2014!$A$6:$AI$9636 |  | 7.71
|  | CZ01 | [5 empty] | CFL |  |  |  |  | DEER2011 |  |  |  |  | DEER2016!$A$6:$AI$16035
DEER2014!$A$6:$AI$9636
DEER2011: CFL Lighting Energy Impacts for Pacific Gas & Electric
Occupancy sensor scenario: No occupancy sensors | [17 empty] | Location: CZ01, Building Vintage: Existing, Occupancy sensor scenario: No occupancy sensors |  |  | 3.5415e-05 | 0.035415
Independent Values |  |  |  |  | Pre-Existing |  | Measure |  | Energy Impacts per ΔWatt Lighting | [5 empty] | HVAC Interactive Effects Factors
Measure |  | Building | Building | Climate | HOUpre | CDFpre | HOUstd | CDFstd | Above Pre-Existing |  |  | Above Code/Standard |  |  | Energy | Demand | Gas
Type | IOU | Vintage | Type | Zone | hours | kW/kW | hours | kW/kW | kWh/ΔW | Watt/ΔW | kBTU/ΔW | kWh/ΔW | Watt/ΔW | kBTU/ΔW | kWh/kWh | kW/kW | therm/kWh | EFLH and CDF Lookup Value | IE factor lookup value
CFL | PGE | Ex | Asm | CZ01 | 2300 | 0.409 | 2300 | 0.409 | 2.19 | 0.474 | -4.09 | 2.19 | 0.474 | -4.09 | 0.952 | 1.16 | -0.017783 | CFLNonePGEAsmExCZ01 | CFLNonePGEAsmExCZ01
CFL | PGE | Ex | EPr | CZ01 | 2240 | 0.63 | 2240 | 0.63 | 2.22 | 0.75 | -4.03 | 2.22 | 0.75 | -4.03 | 0.991 | 1.19 | -0.017991 | CFLNonePGEEPrExCZ01 | CFLNonePGEEPrExCZ01
CFL | PGE | Ex | ESe | CZ01 | 2330 | 0.715 | 2330 | 0.715 | 2.26 | 0.847 | -4.76 | 2.26 | 0.847 | -4.76 | 0.97 | 1.18 | -0.020429 | CFLNonePGEESeExCZ01 | CFLNonePGEESeExCZ01
CFL | PGE | Ex | ECC | CZ01 | 2420 | 0.647 | 2420 | 0.647 | 2.49 | 0.79 | -4.79 | 2.49 | 0.79 | -4.79 | 1.03 | 1.22 | -0.019793 | CFLNonePGEECCExCZ01 | CFLNonePGEECCExCZ01
CFL | PGE | Ex | EUn | CZ01 | 2370 | 0.669 | 2370 | 0.669 | 2.5 | 0.821 | -2.51 | 2.5 | 0.821 | -2.51 | 1.05 | 1.23 | -0.010591 | CFLNonePGEEUnExCZ01 | CFLNonePGEEUnExCZ01
CFL | PGE | Ex | ERC | CZ01 | 2600 | 0.728 | 2600 | 0.728 | 2.52 | 0.864 | -4.34 | 2.52 | 0.864 | -4.34 | 0.969 | 1.19 | -0.016692 | CFLNonePGEERCExCZ01 | CFLNonePGEERCExCZ01
CFL | PGE | Ex | Gro | CZ01 | 3890 | 0.495 | 3890 | 0.495 | 3.13 | 0.462 | -6.84 | 3.13 | 0.462 | -6.84 | 0.805 | 0.933 | -0.017584 | CFLNonePGEGroExCZ01 | CFLNonePGEGroExCZ01
CFL | PGE | Ex | Hsp | CZ01 | 4200 | 0.717 | 4200 | 0.717 | 4.5 | 0.822 | -3.69 | 4.5 | 0.822 | -3.69 | 1.07 | 1.15 | -0.0087857 | CFLNonePGEHspExCZ01 | CFLNonePGEHspExCZ01
CFL | PGE | Ex | Nrs | CZ01 | 3570 | 0.565 | 3570 | 0.565 | 3.51 | 0.645 | -7.22 | 3.51 | 0.645 | -7.22 | 0.983 | 1.14 | -0.020224 | CFLNonePGENrsExCZ01 | CFLNonePGENrsExCZ01
CFL | PGE | Ex | Htl | CZ01 | 1670 | 0.199 | 1670 | 0.199 | 1.51 | 0.238 | -0.878 | 1.51 | 0.238 | -0.878 | 0.904 | 1.2 | -0.0052575 | CFLNonePGEHtlExCZ01 | CFLNonePGEHtlExCZ01
CFL | PGE | Ex | Mtl | CZ01 | 1370 | 0.151 | 1370 | 0.151 | 1.35 | 0.18 | -1.18 | 1.35 | 0.18 | -1.18 | 0.985 | 1.19 | -0.0086131 | CFLNonePGEMtlExCZ01 | CFLNonePGEMtlExCZ01
CFL | PGE | Ex | MBT | CZ01 | 3090 | 0.78 | 3090 | 0.78 | 3.33 | 0.92 | -0.355 | 3.33 | 0.92 | -0.355 | 1.08 | 1.18 | -0.0011489 | CFLNonePGEMBTExCZ01 | CFLNonePGEMBTExCZ01
CFL | PGE | Ex | MLI | CZ01 | 2580 | 0.777 | 2580 | 0.777 | 2.52 | 0.884 | -2.97 | 2.52 | 0.884 | -2.97 | 0.977 | 1.14 | -0.011512 | CFLNonePGEMLIExCZ01 | CFLNonePGEMLIExCZ01
CFL | PGE | Ex | OfL | CZ01 | 3000 | 0.625 | 3000 | 0.625 | 3.2 | 0.793 | -2.78 | 3.2 | 0.793 | -2.78 | 1.07 | 1.27 | -0.0092667 | CFLNonePGEOfLExCZ01 | CFLNonePGEOfLExCZ01
CFL | PGE | Ex | OfS | CZ01 | 2980 | 0.678 | 2980 | 0.678 | 2.99 | 0.804 | -1.86 | 2.99 | 0.804 | -1.86 | 1 | 1.19 | -0.0062416 | CFLNonePGEOfSExCZ01 | CFLNonePGEOfSExCZ01
CFL | PGE | Ex | RSD | CZ01 | 4830 | 0.8 | 4830 | 0.8 | 4.63 | 0.938 | -6.03 | 4.63 | 0.938 | -6.03 | 0.959 | 1.17 | -0.012484 | CFLNonePGERSDExCZ01 | CFLNonePGERSDExCZ01
CFL | PGE | Ex | RFF | CZ01 | 4810 | 0.808 | 4810 | 0.808 | 4.69 | 0.918 | -5.67 | 4.69 | 0.918 | -5.67 | 0.975 | 1.14 | -0.011788 | CFLNonePGERFFExCZ01 | CFLNonePGERFFExCZ01
CFL | PGE | Ex | Rt3 | CZ01 | 3710 | 0.631 | 3710 | 0.631 | 3.56 | 0.782 | -5.45 | 3.56 | 0.782 | -5.45 | 0.96 | 1.24 | -0.01469 | CFLNonePGERt3ExCZ01 | CFLNonePGERt3ExCZ01
CFL | PGE | Ex | RtL | CZ01 | 4350 | 0.689 | 4350 | 0.689 | 4.22 | 0.839 | -5.87 | 4.22 | 0.839 | -5.87 | 0.97 | 1.22 | -0.013494 | CFLNonePGERtLExCZ01 | CFLNonePGERtLExCZ01
CFL | PGE | Ex | RtS | CZ01 | 4010 | 0.7 | 4010 | 0.7 | 3.88 | 0.827 | -4.81 | 3.88 | 0.827 | -4.81 | 0.968 | 1.18 | -0.011995 | CFLNonePGERtSExCZ01 | CFLNonePGERtSExCZ01
CFL | PGE | Ex | SCn | CZ01 | 2760 | 0.575 | 2760 | 0.575 | 2.34 | 0.575 | -4.64 | 2.34 | 0.575 | -4.64 | 0.848 | 1 | -0.016812 | CFLNonePGESCnExCZ01 | CFLNonePGESCnExCZ01
CFL | PGE | Ex | SUn | CZ01 | 2760 | 0.575 | 2760 | 0.575 | 2.76 | 0.575 | 0 | 2.76 | 0.575 | 0 | 1 | 1 | 0 | CFLNonePGESUnExCZ01 | CFLNonePGESUnExCZ01
CFL | PGE | Ex | WRf | CZ01 | 4730 | 0.548 | 4730 | 0.548 | 7.56 | 0.773 | 0 | 7.56 | 0.773 | 0 | 1.6 | 1.41 | 0 | CFLNonePGEWRfExCZ01 | CFLNonePGEWRfExCZ01
CFL | PGE | Ex | Com | CZ01 | 3000 | 0.613 | 3000 | 0.613 | 2.9636 | 0.71616 | -3.5858 | 2.9636 | 0.71616 | -3.5858 | 0.987 | 1.17 | -0.011938 | CFLNonePGEComExCZ01 | CFLNonePGEComExCZ01
CFL | PGE | Ex | SFm | CZ01 | 541 | 0.049 | 541 | 0.049 | 0.525 | 0.0494 | -1.52 | 0.525 | 0.0494 | -1.52 | 0.97 | 1.01 | -0.028096 | CFLNonePGESFmExCZ01 | CFLNonePGESFmExCZ01
CFL | PGE | Ex | MFm | CZ01 | 541 | 0.049 | 541 | 0.049 | 0.494 | 0.0492 | -1.43 | 0.494 | 0.0492 | -1.43 | 0.913 | 1 | -0.026433 | CFLNonePGEMFmExCZ01 | CFLNonePGEMFmExCZ01
CFL | PGE | Ex | DMo | CZ01 | 541 | 0.049 | 541 | 0.049 | 0.519 | 0.0505 | -1.31 | 0.519 | 0.0505 | -1.31 | 0.959 | 1.03 | -0.024214 | CFLNonePGEDMoExCZ01 | CFLNonePGEDMoExCZ01
CFL | PGE | Ex | Res | CZ01 | 541 | 0.049 | 541 | 0.049 | 0.51718 | 0.049385 | -1.4914 | 0.51718 | 0.049385 | -1.4914 | 0.956 | 1.01 | -0.027567 | CFLNonePGEResExCZ01 | CFLNonePGEResExCZ01
Building Vintage
Existing
New
IOU
PGE
SCE
SDGE
DEER Version
Occupancy Sensor Scenario
No OS
Building OS
All Space OS
DEER2014
DEER2016
Lighting Type
LF
CFL
Exit
High Bay

## DEER2014
deer2014 database tables: Energy Impacts
| This file created on 1/15/2014 9:03:19 AM while connected to localhost as postgres by READI (v1.0.4). Values not rounded to 3 sig figs (temporary setting) | [19 empty] | Round to 5 significant digits (extended sig figs) | [6 empty] | Round to 3 significant digits
[6 empty] | Above Pre-Existing Impacts (per delta Watt) | [5 empty] | Above Code/Standard Impacts (per delta Watt) | [8 empty] | Hours of Use and Coincident demand |  |  |  | Calculate IE from WB/EU impacts
[6 empty] | End Use Values |  |  | Whole Building Values |  |  | End Use Values |  |  | Whole Building Values | [5 empty] | Pre-Existing Case |  | Code and Msr Cases |  | Energy | Demand | Gas | Pre-Existing Case |  | Code and Msr Cases |  | Energy | Demand | Gas
Lookup Index | EnergyImpactID | IOU | BldgType | BldgVint | BldgLoc | ACustEUkWh | ACustEUkW | ACustEUtherm | ACustWBkWh | ACustWBkW | ACustWBtherm | AStdEUkWh | AStdEUkW | AStdEUtherm | AStdWBkWh | AStdWBkW | AStdWBtherm |  | Ltg Type | OS | HOU | CDF | HOU | CDF | kWh/kWh | kW/kW | therm/kWh | HOU | CDF | HOU | CDF | kWh/kWh | kW/kW | therm/kWh
CFLBldgPGEAsmExCZ01 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Asm | Ex | CZ01 | 2.2997 | 0.00040895 | 0 | 2.1897 | 0.00047388 | -0.040895 | 2.2505 | 0.0004001 | 0 | 2.1497 | 0.00046405 | -0.040105 |  | CFL | Bldg | 2300 | 0.409 | 2250 | 0.4 | 0.955 | 1.16 | -0.01782 | 2300 | 0.409 | 2250 | 0.4 | 0.955 | 1.16 | -0.0178
CFLBldgPGEAsmExCZ02 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Asm | Ex | CZ02 | 2.2997 | 0.00040896 | 0 | 2.3697 | 0.00047891 | -0.023697 | 2.2504 | 0.00040008 | 0 | 2.3204 | 0.00046901 | -0.023204 |  | CFL | Bldg | 2300 | 0.409 | 2250 | 0.4 | 1.03 | 1.17 | -0.010311 | 2300 | 0.409 | 2250 | 0.4 | 1.03 | 1.17 | -0.0103
CFLBldgPGEAsmExCZ03 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Asm | Ex | CZ03 | 2.2998 | 0.00040897 | 0 | 2.3498 | 0.00047893 | -0.025997 | 2.2503 | 0.00040006 | 0 | 2.3003 | 0.00046901 | -0.025498 |  | CFL | Bldg | 2300 | 0.409 | 2250 | 0.4 | 1.02 | 1.17 | -0.011331 | 2300 | 0.409 | 2250 | 0.4 | 1.02 | 1.17 | -0.0113
CFLBldgPGEAsmExCZ04 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Asm | Ex | CZ04 | 2.2982 | 0.00040869 | 0 | 2.4082 | 0.0004786 | -0.019187 | 2.2504 | 0.00040009 | 0 | 2.3604 | 0.00046809 | -0.018804 |  | CFL | Bldg | 2300 | 0.409 | 2250 | 0.4 | 1.05 | 1.17 | -0.0083559 | 2300 | 0.409 | 2250 | 0.4 | 1.05 | 1.17 | -0.00836
CFLBldgPGEAsmExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Asm | Ex | CZ05 | 2.2982 | 0.00040869 | 0 | 2.3582 | 0.00046965 | -0.022982 | 2.2504 | 0.00040009 | 0 | 2.3104 | 0.00046009 | -0.022504 |  | CFL | Bldg | 2300 | 0.409 | 2250 | 0.4 | 1.03 | 1.15 | -0.01 | 2300 | 0.409 | 2250 | 0.4 | 1.03 | 1.15 | -0.01
CFLBldgPGEAsmExCZ11 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Asm | Ex | CZ11 | 2.2974 | 0.00040854 | 0 | 2.4174 | 0.00047648 | -0.020374 | 2.2507 | 0.00040013 | 0 | 2.38 | 0.00046713 | -0.02 |  | CFL | Bldg | 2300 | 0.409 | 2250 | 0.4 | 1.06 | 1.17 | -0.0088863 | 2300 | 0.409 | 2250 | 0.4 | 1.06 | 1.17 | -0.00889
CFLBldgPGEAsmExCZ12 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Asm | Ex | CZ12 | 2.2978 | 0.00040862 | 0 | 2.3978 | 0.00048151 | -0.021478 | 2.2505 | 0.00040011 | 0 | 2.3505 | 0.00047205 | -0.0211 |  | CFL | Bldg | 2300 | 0.409 | 2250 | 0.4 | 1.04 | 1.18 | -0.0093755 | 2300 | 0.409 | 2250 | 0.4 | 1.04 | 1.18 | -0.00938
CFLBldgPGEAsmExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Asm | Ex | CZ13 | 2.2975 | 0.00040856 | 0 | 2.4275 | 0.0004755 | -0.019781 | 2.2506 | 0.00040012 | 0 | 2.3806 | 0.00046612 | -0.0195 |  | CFL | Bldg | 2300 | 0.409 | 2250 | 0.4 | 1.06 | 1.16 | -0.0086642 | 2300 | 0.409 | 2250 | 0.4 | 1.06 | 1.16 | -0.00866
CFLBldgPGEAsmExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Asm | Ex | CZ16 | 2.2977 | 0.0004086 | 0 | 2.2377 | 0.00047049 | -0.030971 | 2.2506 | 0.00040011 | 0 | 2.2 | 0.00046106 | -0.030406 |  | CFL | Bldg | 2300 | 0.409 | 2250 | 0.4 | 0.978 | 1.15 | -0.01351 | 2300 | 0.409 | 2250 | 0.4 | 0.978 | 1.15 | -0.0135
CFLBldgPGEAsmExIOU | Com-Iltg-dWatt-CFL_OSbldg | PGE | Asm | Ex | IOU | 2.2987 | 0.00040877 | 0 | 2.3818 | 0.00047849 | -0.022778 | 2.2504 | 0.00040009 | 0 | 2.3342 | 0.00046867 | -0.022355 |  | CFL | Bldg | 2300 | 0.409 | 2250 | 0.4 | 1.04 | 1.17 | -0.0099333 | 2300 | 0.409 | 2250 | 0.4 | 1.04 | 1.17 | -0.00993
CFLBldgPGEAsmNewCZ01 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Asm | New | CZ01 | 2.26 | 0.000402 | 0 | 2.16 | 0.000464 | -0.04 | 2.26 | 0.000402 | 0 | 2.16 | 0.000464 | -0.04 |  | CFL | Bldg | 2260 | 0.402 | 2260 | 0.402 | 0.956 | 1.15 | -0.017699 | 2260 | 0.402 | 2260 | 0.402 | 0.956 | 1.15 | -0.0177
CFLBldgPGEAsmNewCZ02 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Asm | New | CZ02 | 2.26 | 0.000402 | 0 | 2.3 | 0.00047 | -0.0253 | 2.26 | 0.000402 | 0 | 2.3 | 0.00047 | -0.0253 |  | CFL | Bldg | 2260 | 0.402 | 2260 | 0.402 | 1.02 | 1.17 | -0.011195 | 2260 | 0.402 | 2260 | 0.402 | 1.02 | 1.17 | -0.0112
CFLBldgPGEAsmNewCZ03 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Asm | New | CZ03 | 2.26 | 0.000402 | 0 | 2.28 | 0.000464 | -0.0262 | 2.26 | 0.000402 | 0 | 2.28 | 0.000464 | -0.0262 |  | CFL | Bldg | 2260 | 0.402 | 2260 | 0.402 | 1.01 | 1.15 | -0.011593 | 2260 | 0.402 | 2260 | 0.402 | 1.01 | 1.15 | -0.0116
CFLBldgPGEAsmNewCZ04 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Asm | New | CZ04 | 2.26 | 0.000402 | 0 | 2.34 | 0.00047 | -0.0207 | 2.26 | 0.000402 | 0 | 2.34 | 0.00047 | -0.0207 |  | CFL | Bldg | 2260 | 0.402 | 2260 | 0.402 | 1.04 | 1.17 | -0.0091593 | 2260 | 0.402 | 2260 | 0.402 | 1.04 | 1.17 | -0.00916
CFLBldgPGEAsmNewCZ05 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Asm | New | CZ05 | 2.26 | 0.000402 | 0 | 2.3 | 0.000458 | -0.0228 | 2.26 | 0.000402 | 0 | 2.3 | 0.000458 | -0.0228 |  | CFL | Bldg | 2260 | 0.402 | 2260 | 0.402 | 1.02 | 1.14 | -0.010088 | 2260 | 0.402 | 2260 | 0.402 | 1.02 | 1.14 | -0.0101
CFLBldgPGEAsmNewCZ11 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Asm | New | CZ11 | 2.26 | 0.000402 | 0 | 2.36 | 0.000479 | -0.0218 | 2.26 | 0.000402 | 0 | 2.36 | 0.000479 | -0.0218 |  | CFL | Bldg | 2260 | 0.402 | 2260 | 0.402 | 1.04 | 1.19 | -0.009646 | 2260 | 0.402 | 2260 | 0.402 | 1.04 | 1.19 | -0.00965
CFLBldgPGEAsmNewCZ12 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Asm | New | CZ12 | 2.26 | 0.000402 | 0 | 2.34 | 0.000477 | -0.0231 | 2.26 | 0.000402 | 0 | 2.34 | 0.000477 | -0.0231 |  | CFL | Bldg | 2260 | 0.402 | 2260 | 0.402 | 1.04 | 1.19 | -0.010221 | 2260 | 0.402 | 2260 | 0.402 | 1.04 | 1.19 | -0.0102
CFLBldgPGEAsmNewCZ13 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Asm | New | CZ13 | 2.26 | 0.000402 | 0 | 2.37 | 0.000479 | -0.021 | 2.26 | 0.000402 | 0 | 2.37 | 0.000479 | -0.021 |  | CFL | Bldg | 2260 | 0.402 | 2260 | 0.402 | 1.05 | 1.19 | -0.009292 | 2260 | 0.402 | 2260 | 0.402 | 1.05 | 1.19 | -0.00929
CFLBldgPGEAsmNewCZ16 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Asm | New | CZ16 | 2.26 | 0.000402 | 0 | 2.21 | 0.000462 | -0.0303 | 2.26 | 0.000402 | 0 | 2.21 | 0.000462 | -0.0303 |  | CFL | Bldg | 2260 | 0.402 | 2260 | 0.402 | 0.978 | 1.15 | -0.013407 | 2260 | 0.402 | 2260 | 0.402 | 0.978 | 1.15 | -0.0134
CFLBldgPGEAsmNewIOU | Com-Iltg-dWatt-CFL_OSbldg | PGE | Asm | New | IOU | 2.26 | 0.000402 | 0 | 2.326 | 0.00047203 | -0.023304 | 2.26 | 0.000402 | 0 | 2.326 | 0.00047203 | -0.023304 |  | CFL | Bldg | 2260 | 0.402 | 2260 | 0.402 | 1.03 | 1.17 | -0.010311 | 2260 | 0.402 | 2260 | 0.402 | 1.03 | 1.17 | -0.0103
CFLBldgPGEComExCZ01 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Com | Ex | CZ01 | 3.003 | 0.00061288 | 0 | 2.9628 | 0.00071557 | -0.035844 | 2.9303 | 0.00058306 | 0 | 2.8916 | 0.00067988 | -0.035037 |  | CFL | Bldg | 3000 | 0.613 | 2930 | 0.583 | 0.987 | 1.17 | -0.011957 | 3000 | 0.613 | 2930 | 0.583 | 0.987 | 1.17 | -0.012
CFLBldgPGEComExCZ02 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Com | Ex | CZ02 | 3.0614 | 0.00053782 | 0 | 3.2022 | 0.00065466 | -0.022824 | 3.0024 | 0.00052415 | 0 | 3.141 | 0.00063755 | -0.022343 |  | CFL | Bldg | 3060 | 0.538 | 3000 | 0.524 | 1.05 | 1.22 | -0.0074416 | 3060 | 0.538 | 3000 | 0.524 | 1.05 | 1.22 | -0.00744
CFLBldgPGEComExCZ03 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Com | Ex | CZ03 | 3.0146 | 0.00055424 | 0 | 3.1825 | 0.0006779 | -0.020798 | 2.9388 | 0.00053489 | 0 | 3.1031 | 0.00065348 | -0.020249 |  | CFL | Bldg | 3010 | 0.554 | 2940 | 0.535 | 1.06 | 1.22 | -0.0068903 | 3010 | 0.554 | 2940 | 0.535 | 1.06 | 1.22 | -0.00689
CFLBldgPGEComExCZ04 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Com | Ex | CZ04 | 3.0224 | 0.00062206 | 0 | 3.2316 | 0.00076076 | -0.01691 | 2.9453 | 0.00059627 | 0 | 3.1495 | 0.00072851 | -0.016477 |  | CFL | Bldg | 3020 | 0.622 | 2950 | 0.596 | 1.07 | 1.22 | -0.0055944 | 3020 | 0.622 | 2950 | 0.596 | 1.07 | 1.22 | -0.00559
CFLBldgPGEComExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Com | Ex | CZ05 | 2.9277 | 0.000586 | 0 | 3.0917 | 0.00070368 | -0.020945 | 2.8633 | 0.00056026 | 0 | 3.0227 | 0.00067229 | -0.020458 |  | CFL | Bldg | 2930 | 0.586 | 2860 | 0.56 | 1.06 | 1.2 | -0.0071449 | 2930 | 0.586 | 2860 | 0.56 | 1.06 | 1.2 | -0.00714
CFLBldgPGEComExCZ11 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Com | Ex | CZ11 | 3.0711 | 0.000533 | 0 | 3.2678 | 0.00064615 | -0.020677 | 3.0105 | 0.00051808 | 0 | 3.2034 | 0.00062772 | -0.020258 |  | CFL | Bldg | 3070 | 0.533 | 3010 | 0.518 | 1.06 | 1.21 | -0.0067291 | 3070 | 0.533 | 3010 | 0.518 | 1.06 | 1.21 | -0.00673
CFLBldgPGEComExCZ12 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Com | Ex | CZ12 | 3.1114 | 0.0005529 | 0 | 3.3027 | 0.00067154 | -0.020328 | 3.0508 | 0.00053845 | 0 | 3.2382 | 0.0006537 | -0.019915 |  | CFL | Bldg | 3110 | 0.553 | 3050 | 0.538 | 1.06 | 1.21 | -0.0065277 | 3110 | 0.553 | 3050 | 0.538 | 1.06 | 1.21 | -0.00653
CFLBldgPGEComExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Com | Ex | CZ13 | 3.1226 | 0.0005418 | 0 | 3.3901 | 0.00065528 | -0.018508 | 3.0536 | 0.00052496 | 0 | 3.3141 | 0.00063456 | -0.018109 |  | CFL | Bldg | 3120 | 0.542 | 3050 | 0.525 | 1.09 | 1.21 | -0.0059305 | 3120 | 0.542 | 3050 | 0.525 | 1.09 | 1.21 | -0.00593
CFLBldgPGEComExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Com | Ex | CZ16 | 2.8463 | 0.00050439 | 0 | 2.7814 | 0.00058914 | -0.030026 | 2.7832 | 0.00049062 | 0 | 2.7204 | 0.00057274 | -0.029326 |  | CFL | Bldg | 2850 | 0.504 | 2780 | 0.491 | 0.977 | 1.17 | -0.010537 | 2850 | 0.504 | 2780 | 0.491 | 0.977 | 1.17 | -0.0105
CFLBldgPGEComExIOU | Com-Iltg-dWatt-CFL_OSbldg | PGE | Com | Ex | IOU | 3.0519 | 0.00056174 | 0 | 3.24 | 0.0006838 | -0.020139 | 2.9821 | 0.00054307 | 0 | 3.166 | 0.00066052 | -0.019664 |  | CFL | Bldg | 3050 | 0.562 | 2980 | 0.543 | 1.06 | 1.22 | -0.006594 | 3050 | 0.562 | 2980 | 0.543 | 1.06 | 1.22 | -0.00659
CFLBldgPGEComNewCZ05 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Com | New | CZ05 | 2.828 | 0.00054376 | 0 | 2.9338 | 0.00065715 | -0.020337 | 2.828 | 0.00054376 | 0 | 2.9338 | 0.00065715 | -0.020337 |  | CFL | Bldg | 2830 | 0.544 | 2830 | 0.544 | 1.04 | 1.21 | -0.0071912 | 2830 | 0.544 | 2830 | 0.544 | 1.04 | 1.21 | -0.00719
CFLBldgPGEComNewCZ11 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Com | New | CZ11 | 3.0009 | 0.00052556 | 0 | 3.1815 | 0.00064182 | -0.019567 | 3.0009 | 0.00052556 | 0 | 3.1815 | 0.00064182 | -0.019567 |  | CFL | Bldg | 3000 | 0.526 | 3000 | 0.526 | 1.06 | 1.22 | -0.0065203 | 3000 | 0.526 | 3000 | 0.526 | 1.06 | 1.22 | -0.00652
CFLBldgPGEComNewCZ12 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Com | New | CZ12 | 3.0386 | 0.0005432 | 0 | 3.2204 | 0.00065931 | -0.019014 | 3.0386 | 0.0005432 | 0 | 3.2204 | 0.00065931 | -0.019014 |  | CFL | Bldg | 3040 | 0.543 | 3040 | 0.543 | 1.06 | 1.21 | -0.0062573 | 3040 | 0.543 | 3040 | 0.543 | 1.06 | 1.21 | -0.00626
CFLBldgPGEComNewCZ13 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Com | New | CZ13 | 3.0714 | 0.00053629 | 0 | 3.3147 | 0.00064937 | -0.017772 | 3.0714 | 0.00053629 | 0 | 3.3147 | 0.00064937 | -0.017772 |  | CFL | Bldg | 3070 | 0.536 | 3070 | 0.536 | 1.08 | 1.21 | -0.0057863 | 3070 | 0.536 | 3070 | 0.536 | 1.08 | 1.21 | -0.00579
CFLBldgPGEComNewCZ16 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Com | New | CZ16 | 2.7498 | 0.00049048 | 0 | 2.6809 | 0.00056977 | -0.027549 | 2.7498 | 0.00049048 | 0 | 2.6809 | 0.00056977 | -0.027549 |  | CFL | Bldg | 2750 | 0.49 | 2750 | 0.49 | 0.975 | 1.16 | -0.010019 | 2750 | 0.49 | 2750 | 0.49 | 0.975 | 1.16 | -0.01
CFLBldgPGEComNewIOU | Com-Iltg-dWatt-CFL_OSbldg | PGE | Com | New | IOU | 3.0134 | 0.00055073 | 0 | 3.177 | 0.00066814 | -0.019094 | 3.0134 | 0.00055073 | 0 | 3.177 | 0.00066814 | -0.019094 |  | CFL | Bldg | 3010 | 0.551 | 3010 | 0.551 | 1.05 | 1.21 | -0.0063366 | 3010 | 0.551 | 3010 | 0.551 | 1.05 | 1.21 | -0.00634
CFLBldgPGEECCExCZ01 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ECC | Ex | CZ01 | 2.417 | 0.00064517 | 0 | 2.4868 | 0.00078776 | -0.047841 | 2.31 | 0.00058095 | 0 | 2.3797 | 0.00070992 | -0.045797 |  | CFL | Bldg | 2420 | 0.645 | 2310 | 0.581 | 1.03 | 1.22 | -0.019826 | 2420 | 0.645 | 2310 | 0.581 | 1.03 | 1.22 | -0.0198
CFLBldgPGEECCExCZ02 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ECC | Ex | CZ02 | 2.4147 | 0.00041788 | 0 | 2.6242 | 0.00055116 | -0.029233 | 2.31 | 0.00037695 | 0 | 2.5195 | 0.0004969 | -0.027995 |  | CFL | Bldg | 2410 | 0.418 | 2310 | 0.377 | 1.09 | 1.32 | -0.012119 | 2410 | 0.418 | 2310 | 0.377 | 1.09 | 1.32 | -0.0121
CFLBldgPGEECCExCZ03 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ECC | Ex | CZ03 | 2.416 | 0.00041838 | 0 | 2.6056 | 0.00052098 | -0.030449 | 2.31 | 0.00037696 | 0 | 2.4996 | 0.00046993 | -0.0291 |  | CFL | Bldg | 2420 | 0.418 | 2310 | 0.377 | 1.08 | 1.25 | -0.012597 | 2420 | 0.418 | 2310 | 0.377 | 1.08 | 1.25 | -0.0126
CFLBldgPGEECCExCZ04 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ECC | Ex | CZ04 | 2.4143 | 0.00064346 | 0 | 2.6638 | 0.00083637 | -0.023343 | 2.31 | 0.0005809 | 0 | 2.55 | 0.00075579 | -0.0223 |  | CFL | Bldg | 2410 | 0.643 | 2310 | 0.581 | 1.1 | 1.3 | -0.0096537 | 2410 | 0.643 | 2310 | 0.581 | 1.1 | 1.3 | -0.00965
CFLBldgPGEECCExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ECC | Ex | CZ05 | 2.4143 | 0.00064346 | 0 | 2.6038 | 0.00079463 | -0.029727 | 2.31 | 0.0005809 | 0 | 2.49 | 0.00071784 | -0.0284 |  | CFL | Bldg | 2410 | 0.643 | 2310 | 0.581 | 1.08 | 1.24 | -0.012294 | 2410 | 0.643 | 2310 | 0.581 | 1.08 | 1.24 | -0.0123
CFLBldgPGEECCExCZ11 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ECC | Ex | CZ11 | 2.4134 | 0.00041734 | 0 | 2.6927 | 0.00051968 | -0.026821 | 2.31 | 0.00037694 | 0 | 2.58 | 0.00046988 | -0.025694 |  | CFL | Bldg | 2410 | 0.417 | 2310 | 0.377 | 1.12 | 1.25 | -0.011123 | 2410 | 0.417 | 2310 | 0.377 | 1.12 | 1.25 | -0.0111
CFLBldgPGEECCExCZ12 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ECC | Ex | CZ12 | 2.4136 | 0.00041744 | 0 | 2.673 | 0.00052474 | -0.02633 | 2.31 | 0.00037694 | 0 | 2.56 | 0.00047388 | -0.0252 |  | CFL | Bldg | 2410 | 0.417 | 2310 | 0.377 | 1.11 | 1.26 | -0.010909 | 2410 | 0.417 | 2310 | 0.377 | 1.11 | 1.26 | -0.0109
CFLBldgPGEECCExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ECC | Ex | CZ13 | 2.4134 | 0.00041736 | 0 | 2.7222 | 0.00054951 | -0.02324 | 2.31 | 0.00037694 | 0 | 2.6 | 0.00049688 | -0.0223 |  | CFL | Bldg | 2410 | 0.417 | 2310 | 0.377 | 1.13 | 1.32 | -0.0096537 | 2410 | 0.417 | 2310 | 0.377 | 1.13 | 1.32 | -0.00965
CFLBldgPGEECCExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ECC | Ex | CZ16 | 2.4151 | 0.00041803 | 0 | 2.5451 | 0.00049563 | -0.041815 | 2.31 | 0.00037695 | 0 | 2.44 | 0.00044691 | -0.04 |  | CFL | Bldg | 2420 | 0.418 | 2310 | 0.377 | 1.06 | 1.19 | -0.017316 | 2420 | 0.418 | 2310 | 0.377 | 1.06 | 1.19 | -0.0173
CFLBldgPGEECCExIOU | Com-Iltg-dWatt-CFL_OSbldg | PGE | ECC | Ex | IOU | 2.4147 | 0.00046096 | 0 | 2.6412 | 0.00058327 | -0.028339 | 2.31 | 0.00041584 | 0 | 2.5303 | 0.00052662 | -0.027111 |  | CFL | Bldg | 2410 | 0.461 | 2310 | 0.416 | 1.1 | 1.27 | -0.011736 | 2410 | 0.461 | 2310 | 0.416 | 1.1 | 1.27 | -0.0117
CFLBldgPGEECCNewCZ01 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ECC | New | CZ01 | 2.31 | 0.000579 | 0 | 2.36 | 0.000676 | -0.0471 | 2.31 | 0.000579 | 0 | 2.36 | 0.000676 | -0.0471 |  | CFL | Bldg | 2310 | 0.579 | 2310 | 0.579 | 1.02 | 1.17 | -0.02039 | 2310 | 0.579 | 2310 | 0.579 | 1.02 | 1.17 | -0.0204
CFLBldgPGEECCNewCZ02 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ECC | New | CZ02 | 2.31 | 0.000376 | 0 | 2.5 | 0.000512 | -0.0286 | 2.31 | 0.000376 | 0 | 2.5 | 0.000512 | -0.0286 |  | CFL | Bldg | 2310 | 0.376 | 2310 | 0.376 | 1.08 | 1.36 | -0.012381 | 2310 | 0.376 | 2310 | 0.376 | 1.08 | 1.36 | -0.0124
CFLBldgPGEECCNewCZ03 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ECC | New | CZ03 | 2.31 | 0.000376 | 0 | 2.45 | 0.000493 | -0.0314 | 2.31 | 0.000376 | 0 | 2.45 | 0.000493 | -0.0314 |  | CFL | Bldg | 2310 | 0.376 | 2310 | 0.376 | 1.06 | 1.31 | -0.013593 | 2310 | 0.376 | 2310 | 0.376 | 1.06 | 1.31 | -0.0136
CFLBldgPGEECCNewCZ04 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ECC | New | CZ04 | 2.31 | 0.000579 | 0 | 2.53 | 0.000736 | -0.0231 | 2.31 | 0.000579 | 0 | 2.53 | 0.000736 | -0.0231 |  | CFL | Bldg | 2310 | 0.579 | 2310 | 0.579 | 1.1 | 1.27 | -0.01 | 2310 | 0.579 | 2310 | 0.579 | 1.1 | 1.27 | -0.01
CFLBldgPGEECCNewCZ05 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ECC | New | CZ05 | 2.31 | 0.000579 | 0 | 2.46 | 0.00071 | -0.0305 | 2.31 | 0.000579 | 0 | 2.46 | 0.00071 | -0.0305 |  | CFL | Bldg | 2310 | 0.579 | 2310 | 0.579 | 1.06 | 1.23 | -0.013203 | 2310 | 0.579 | 2310 | 0.579 | 1.06 | 1.23 | -0.0132
CFLBldgPGEECCNewCZ11 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ECC | New | CZ11 | 2.31 | 0.000376 | 0 | 2.56 | 0.000502 | -0.024 | 2.31 | 0.000376 | 0 | 2.56 | 0.000502 | -0.024 |  | CFL | Bldg | 2310 | 0.376 | 2310 | 0.376 | 1.11 | 1.34 | -0.01039 | 2310 | 0.376 | 2310 | 0.376 | 1.11 | 1.34 | -0.0104
CFLBldgPGEECCNewCZ12 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ECC | New | CZ12 | 2.31 | 0.000376 | 0 | 2.55 | 0.000513 | -0.0245 | 2.31 | 0.000376 | 0 | 2.55 | 0.000513 | -0.0245 |  | CFL | Bldg | 2310 | 0.376 | 2310 | 0.376 | 1.1 | 1.36 | -0.010606 | 2310 | 0.376 | 2310 | 0.376 | 1.1 | 1.36 | -0.0106
CFLBldgPGEECCNewCZ13 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ECC | New | CZ13 | 2.31 | 0.000376 | 0 | 2.59 | 0.000507 | -0.0209 | 2.31 | 0.000376 | 0 | 2.59 | 0.000507 | -0.0209 |  | CFL | Bldg | 2310 | 0.376 | 2310 | 0.376 | 1.12 | 1.35 | -0.0090476 | 2310 | 0.376 | 2310 | 0.376 | 1.12 | 1.35 | -0.00905
CFLBldgPGEECCNewCZ16 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ECC | New | CZ16 | 2.31 | 0.000376 | 0 | 2.43 | 0.000487 | -0.0383 | 2.31 | 0.000376 | 0 | 2.43 | 0.000487 | -0.0383 |  | CFL | Bldg | 2310 | 0.376 | 2310 | 0.376 | 1.05 | 1.3 | -0.01658 | 2310 | 0.376 | 2310 | 0.376 | 1.05 | 1.3 | -0.0166
CFLBldgPGEECCNewIOU | Com-Iltg-dWatt-CFL_OSbldg | PGE | ECC | New | IOU | 2.31 | 0.00041495 | 0 | 2.5138 | 0.00054474 | -0.026789 | 2.31 | 0.00041495 | 0 | 2.5138 | 0.00054474 | -0.026789 |  | CFL | Bldg | 2310 | 0.415 | 2310 | 0.415 | 1.09 | 1.31 | -0.011597 | 2310 | 0.415 | 2310 | 0.415 | 1.09 | 1.31 | -0.0116
CFLBldgPGEEPrExCZ01 | Com-Iltg-dWatt-CFL_OSbldg | PGE | EPr | Ex | CZ01 | 2.235 | 0.00062767 | 0 | 2.215 | 0.00074722 | -0.040212 | 2.11 | 0.00056419 | 0 | 2.09 | 0.00067123 | -0.038 |  | CFL | Bldg | 2240 | 0.628 | 2110 | 0.564 | 0.991 | 1.19 | -0.018009 | 2240 | 0.628 | 2110 | 0.564 | 0.991 | 1.19 | -0.018
CFLBldgPGEEPrExCZ02 | Com-Iltg-dWatt-CFL_OSbldg | PGE | EPr | Ex | CZ02 | 2.236 | 1.9942e-05 | 0 | 2.3557 | 1.9942e-05 | -0.024157 | 2.11 | 1.7906e-05 | 0 | 2.22 | 1.7906e-05 | -0.0228 |  | CFL | Bldg | 2240 | 0.0199 | 2110 | 0.0179 | 1.05 | 1 | -0.010806 | 2240 | 0.0199 | 2110 | 0.0179 | 1.05 | 1 | -0.0108
CFLBldgPGEEPrExCZ03 | Com-Iltg-dWatt-CFL_OSbldg | PGE | EPr | Ex | CZ03 | 2.2369 | 1.9954e-05 | 0 | 2.3766 | 1.9954e-05 | -0.023469 | 2.11 | 1.7905e-05 | 0 | 2.24 | 1.7905e-05 | -0.0222 |  | CFL | Bldg | 2240 | 0.02 | 2110 | 0.0179 | 1.06 | 1 | -0.010521 | 2240 | 0.02 | 2110 | 0.0179 | 1.06 | 1 | -0.0105
CFLBldgPGEEPrExCZ04 | Com-Iltg-dWatt-CFL_OSbldg | PGE | EPr | Ex | CZ04 | 2.2359 | 0.00062806 | 0 | 2.4056 | 0.00076962 | -0.018568 | 2.11 | 0.00056416 | 0 | 2.2797 | 0.00069119 | -0.0176 |  | CFL | Bldg | 2240 | 0.628 | 2110 | 0.564 | 1.08 | 1.23 | -0.0083412 | 2240 | 0.628 | 2110 | 0.564 | 1.08 | 1.23 | -0.00834
CFLBldgPGEEPrExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | PGE | EPr | Ex | CZ05 | 2.2359 | 0.00062806 | 0 | 2.3659 | 0.00075368 | -0.022162 | 2.11 | 0.00056416 | 0 | 2.24 | 0.00067719 | -0.021 |  | CFL | Bldg | 2240 | 0.628 | 2110 | 0.564 | 1.06 | 1.2 | -0.0099526 | 2240 | 0.628 | 2110 | 0.564 | 1.06 | 1.2 | -0.00995
CFLBldgPGEEPrExCZ11 | Com-Iltg-dWatt-CFL_OSbldg | PGE | EPr | Ex | CZ11 | 2.2323 | 1.9888e-05 | 0 | 2.3623 | 1.9888e-05 | -0.022123 | 2.11 | 1.7912e-05 | 0 | 2.24 | 1.7912e-05 | -0.0209 |  | CFL | Bldg | 2230 | 0.0199 | 2110 | 0.0179 | 1.06 | 1 | -0.0099052 | 2230 | 0.0199 | 2110 | 0.0179 | 1.06 | 1 | -0.00991
CFLBldgPGEEPrExCZ12 | Com-Iltg-dWatt-CFL_OSbldg | PGE | EPr | Ex | CZ12 | 2.2333 | 1.9902e-05 | 0 | 2.3633 | 1.9902e-05 | -0.023033 | 2.11 | 1.791e-05 | 0 | 2.24 | 1.791e-05 | -0.0218 |  | CFL | Bldg | 2230 | 0.0199 | 2110 | 0.0179 | 1.06 | 1 | -0.010332 | 2230 | 0.0199 | 2110 | 0.0179 | 1.06 | 1 | -0.0103
CFLBldgPGEEPrExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | PGE | EPr | Ex | CZ13 | 2.233 | 1.9898e-05 | 0 | 2.3925 | 1.9898e-05 | -0.019941 | 2.11 | 1.7911e-05 | 0 | 2.26 | 1.7911e-05 | -0.0189 |  | CFL | Bldg | 2230 | 0.0199 | 2110 | 0.0179 | 1.07 | 1 | -0.0089573 | 2230 | 0.0199 | 2110 | 0.0179 | 1.07 | 1 | -0.00896
CFLBldgPGEEPrExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | PGE | EPr | Ex | CZ16 | 2.2329 | 1.9897e-05 | 0 | 2.1635 | 1.9897e-05 | -0.039775 | 2.11 | 1.7911e-05 | 0 | 2.05 | 1.7911e-05 | -0.0376 |  | CFL | Bldg | 2230 | 0.0199 | 2110 | 0.0179 | 0.972 | 1 | -0.01782 | 2230 | 0.0199 | 2110 | 0.0179 | 0.972 | 1 | -0.0178
CFLBldgPGEEPrExIOU | Com-Iltg-dWatt-CFL_OSbldg | PGE | EPr | Ex | IOU | 2.2349 | 0.00012693 | 0 | 2.3742 | 0.00015129 | -0.022328 | 2.11 | 0.00011403 | 0 | 2.2443 | 0.0001359 | -0.02113 |  | CFL | Bldg | 2230 | 0.127 | 2110 | 0.114 | 1.06 | 1.19 | -0.010014 | 2230 | 0.127 | 2110 | 0.114 | 1.06 | 1.19 | -0.01
CFLBldgPGEEPrNewCZ01 | Com-Iltg-dWatt-CFL_OSbldg | PGE | EPr | New | CZ01 | 2.11 | 0.000569 | 0 | 2.08 | 0.000655 | -0.045 | 2.11 | 0.000569 | 0 | 2.08 | 0.000655 | -0.045 |  | CFL | Bldg | 2110 | 0.569 | 2110 | 0.569 | 0.986 | 1.15 | -0.021327 | 2110 | 0.569 | 2110 | 0.569 | 0.986 | 1.15 | -0.0213
CFLBldgPGEEPrNewCZ02 | Com-Iltg-dWatt-CFL_OSbldg | PGE | EPr | New | CZ02 | 2.11 | 1.81e-05 | 0 | 2.2 | 1.81e-05 | -0.0289 | 2.11 | 1.81e-05 | 0 | 2.2 | 1.81e-05 | -0.0289 |  | CFL | Bldg | 2110 | 0.0181 | 2110 | 0.0181 | 1.04 | 1 | -0.013697 | 2110 | 0.0181 | 2110 | 0.0181 | 1.04 | 1 | -0.0137
CFLBldgPGEEPrNewCZ03 | Com-Iltg-dWatt-CFL_OSbldg | PGE | EPr | New | CZ03 | 2.11 | 1.81e-05 | 0 | 2.18 | 1.81e-05 | -0.0275 | 2.11 | 1.81e-05 | 0 | 2.18 | 1.81e-05 | -0.0275 |  | CFL | Bldg | 2110 | 0.0181 | 2110 | 0.0181 | 1.03 | 1 | -0.013033 | 2110 | 0.0181 | 2110 | 0.0181 | 1.03 | 1 | -0.013
CFLBldgPGEEPrNewCZ04 | Com-Iltg-dWatt-CFL_OSbldg | PGE | EPr | New | CZ04 | 2.11 | 0.000569 | 0 | 2.24 | 0.000739 | -0.0224 | 2.11 | 0.000569 | 0 | 2.24 | 0.000739 | -0.0224 |  | CFL | Bldg | 2110 | 0.569 | 2110 | 0.569 | 1.06 | 1.3 | -0.010616 | 2110 | 0.569 | 2110 | 0.569 | 1.06 | 1.3 | -0.0106
CFLBldgPGEEPrNewCZ05 | Com-Iltg-dWatt-CFL_OSbldg | PGE | EPr | New | CZ05 | 2.11 | 0.000569 | 0 | 2.19 | 0.000703 | -0.0228 | 2.11 | 0.000569 | 0 | 2.19 | 0.000703 | -0.0228 |  | CFL | Bldg | 2110 | 0.569 | 2110 | 0.569 | 1.04 | 1.24 | -0.010806 | 2110 | 0.569 | 2110 | 0.569 | 1.04 | 1.24 | -0.0108
CFLBldgPGEEPrNewCZ11 | Com-Iltg-dWatt-CFL_OSbldg | PGE | EPr | New | CZ11 | 2.11 | 1.81e-05 | 0 | 2.27 | 1.81e-05 | -0.0253 | 2.11 | 1.81e-05 | 0 | 2.27 | 1.81e-05 | -0.0253 |  | CFL | Bldg | 2110 | 0.0181 | 2110 | 0.0181 | 1.08 | 1 | -0.011991 | 2110 | 0.0181 | 2110 | 0.0181 | 1.08 | 1 | -0.012
CFLBldgPGEEPrNewCZ12 | Com-Iltg-dWatt-CFL_OSbldg | PGE | EPr | New | CZ12 | 2.11 | 1.81e-05 | 0 | 2.24 | 1.81e-05 | -0.026 | 2.11 | 1.81e-05 | 0 | 2.24 | 1.81e-05 | -0.026 |  | CFL | Bldg | 2110 | 0.0181 | 2110 | 0.0181 | 1.06 | 1 | -0.012322 | 2110 | 0.0181 | 2110 | 0.0181 | 1.06 | 1 | -0.0123
CFLBldgPGEEPrNewCZ13 | Com-Iltg-dWatt-CFL_OSbldg | PGE | EPr | New | CZ13 | 2.11 | 1.81e-05 | 0 | 2.28 | 1.81e-05 | -0.0232 | 2.11 | 1.81e-05 | 0 | 2.28 | 1.81e-05 | -0.0232 |  | CFL | Bldg | 2110 | 0.0181 | 2110 | 0.0181 | 1.08 | 1 | -0.010995 | 2110 | 0.0181 | 2110 | 0.0181 | 1.08 | 1 | -0.011
CFLBldgPGEEPrNewCZ16 | Com-Iltg-dWatt-CFL_OSbldg | PGE | EPr | New | CZ16 | 2.11 | 1.81e-05 | 0 | 2.11 | 1.81e-05 | -0.0332 | 2.11 | 1.81e-05 | 0 | 2.11 | 1.81e-05 | -0.0332 |  | CFL | Bldg | 2110 | 0.0181 | 2110 | 0.0181 | 1 | 1 | -0.015735 | 2110 | 0.0181 | 2110 | 0.0181 | 1 | 1 | -0.0157
CFLBldgPGEEPrNewIOU | Com-Iltg-dWatt-CFL_OSbldg | PGE | EPr | New | IOU | 2.11 | 9.5803e-05 | 0 | 2.2354 | 0.0001184 | -0.025523 | 2.11 | 9.5803e-05 | 0 | 2.2354 | 0.0001184 | -0.025523 |  | CFL | Bldg | 2110 | 0.0958 | 2110 | 0.0958 | 1.06 | 1.24 | -0.012096 | 2110 | 0.0958 | 2110 | 0.0958 | 1.06 | 1.24 | -0.0121
CFLBldgPGEERCExCZ01 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ERC | Ex | CZ01 | 2.592 | 0.0007243 | 0 | 2.5124 | 0.00085961 | -0.043263 | 2.39 | 0.0006233 | 0 | 2.32 | 0.00073938 | -0.0398 |  | CFL | Bldg | 2590 | 0.724 | 2390 | 0.623 | 0.971 | 1.19 | -0.016653 | 2590 | 0.724 | 2390 | 0.623 | 0.971 | 1.19 | -0.0167
CFLBldgPGEERCExCZ02 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ERC | Ex | CZ02 | 2.5935 | 2.0914e-05 | 0 | 2.6135 | 2.0914e-05 | -0.03112 | 2.39 | 1.8006e-05 | 0 | 2.41 | 1.8006e-05 | -0.0286 |  | CFL | Bldg | 2590 | 0.0209 | 2390 | 0.018 | 1.01 | 1 | -0.011967 | 2590 | 0.0209 | 2390 | 0.018 | 1.01 | 1 | -0.012
CFLBldgPGEERCExCZ03 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ERC | Ex | CZ03 | 2.5949 | 2.0933e-05 | 0 | 2.6247 | 2.0933e-05 | -0.029042 | 2.39 | 1.8005e-05 | 0 | 2.41 | 1.8005e-05 | -0.0267 |  | CFL | Bldg | 2590 | 0.0209 | 2390 | 0.018 | 1.01 | 1 | -0.011172 | 2590 | 0.0209 | 2390 | 0.018 | 1.01 | 1 | -0.0112
CFLBldgPGEERCExCZ04 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ERC | Ex | CZ04 | 2.5933 | 0.00072492 | 0 | 2.693 | 0.00087032 | -0.02424 | 2.39 | 0.00062325 | 0 | 2.48 | 0.00074832 | -0.0224 |  | CFL | Bldg | 2590 | 0.725 | 2390 | 0.623 | 1.04 | 1.2 | -0.0093724 | 2590 | 0.725 | 2390 | 0.623 | 1.04 | 1.2 | -0.00937
CFLBldgPGEERCExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ERC | Ex | CZ05 | 2.5933 | 0.00072491 | 0 | 2.6233 | 0.00086634 | -0.028727 | 2.39 | 0.00062325 | 0 | 2.42 | 0.00074435 | -0.0265 |  | CFL | Bldg | 2590 | 0.725 | 2390 | 0.623 | 1.01 | 1.19 | -0.011088 | 2590 | 0.725 | 2390 | 0.623 | 1.01 | 1.19 | -0.0111
CFLBldgPGEERCExCZ11 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ERC | Ex | CZ11 | 2.5876 | 2.0835e-05 | 0 | 2.677 | 2.0835e-05 | -0.026076 | 2.39 | 1.8012e-05 | 0 | 2.47 | 1.8012e-05 | -0.0241 |  | CFL | Bldg | 2590 | 0.0208 | 2390 | 0.018 | 1.03 | 1 | -0.010084 | 2590 | 0.0208 | 2390 | 0.018 | 1.03 | 1 | -0.0101
CFLBldgPGEERCExCZ12 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ERC | Ex | CZ12 | 2.5891 | 2.0855e-05 | 0 | 2.6686 | 2.0855e-05 | -0.027681 | 2.39 | 1.801e-05 | 0 | 2.46 | 1.801e-05 | -0.0255 |  | CFL | Bldg | 2590 | 0.0209 | 2390 | 0.018 | 1.03 | 1 | -0.010669 | 2590 | 0.0209 | 2390 | 0.018 | 1.03 | 1 | -0.0107
CFLBldgPGEERCExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ERC | Ex | CZ13 | 2.5888 | 2.085e-05 | 0 | 2.7177 | 2.085e-05 | -0.024693 | 2.39 | 1.8011e-05 | 0 | 2.5 | 1.8011e-05 | -0.0228 |  | CFL | Bldg | 2590 | 0.0209 | 2390 | 0.018 | 1.05 | 1 | -0.0095397 | 2590 | 0.0209 | 2390 | 0.018 | 1.05 | 1 | -0.00954
CFLBldgPGEERCExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ERC | Ex | CZ16 | 2.5886 | 2.0848e-05 | 0 | 2.5486 | 2.0848e-05 | -0.041616 | 2.39 | 1.8011e-05 | 0 | 2.35 | 1.8011e-05 | -0.0384 |  | CFL | Bldg | 2590 | 0.0208 | 2390 | 0.018 | 0.983 | 1 | -0.016067 | 2590 | 0.0208 | 2390 | 0.018 | 0.983 | 1 | -0.0161
CFLBldgPGEERCExIOU | Com-Iltg-dWatt-CFL_OSbldg | PGE | ERC | Ex | IOU | 2.5917 | 0.00014476 | 0 | 2.6606 | 0.00017017 | -0.027534 | 2.39 | 0.00012451 | 0 | 2.4489 | 0.00014635 | -0.025369 |  | CFL | Bldg | 2590 | 0.145 | 2390 | 0.125 | 1.02 | 1.18 | -0.010615 | 2590 | 0.145 | 2390 | 0.125 | 1.02 | 1.18 | -0.0106
CFLBldgPGEERCNewCZ01 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ERC | New | CZ01 | 2.39 | 0.000631 | 0 | 2.45 | 0.000747 | -0.047 | 2.39 | 0.000631 | 0 | 2.45 | 0.000747 | -0.047 |  | CFL | Bldg | 2390 | 0.631 | 2390 | 0.631 | 1.03 | 1.18 | -0.019665 | 2390 | 0.631 | 2390 | 0.631 | 1.03 | 1.18 | -0.0197
CFLBldgPGEERCNewCZ02 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ERC | New | CZ02 | 2.39 | 1.82e-05 | 0 | 2.56 | 1.82e-05 | -0.031 | 2.39 | 1.82e-05 | 0 | 2.56 | 1.82e-05 | -0.031 |  | CFL | Bldg | 2390 | 0.0182 | 2390 | 0.0182 | 1.07 | 1 | -0.012971 | 2390 | 0.0182 | 2390 | 0.0182 | 1.07 | 1 | -0.013
CFLBldgPGEERCNewCZ03 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ERC | New | CZ03 | 2.39 | 1.82e-05 | 0 | 2.56 | 1.82e-05 | -0.0284 | 2.39 | 1.82e-05 | 0 | 2.56 | 1.82e-05 | -0.0284 |  | CFL | Bldg | 2390 | 0.0182 | 2390 | 0.0182 | 1.07 | 1 | -0.011883 | 2390 | 0.0182 | 2390 | 0.0182 | 1.07 | 1 | -0.0119
CFLBldgPGEERCNewCZ04 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ERC | New | CZ04 | 2.39 | 0.000631 | 0 | 2.63 | 0.000797 | -0.0246 | 2.39 | 0.000631 | 0 | 2.63 | 0.000797 | -0.0246 |  | CFL | Bldg | 2390 | 0.631 | 2390 | 0.631 | 1.1 | 1.26 | -0.010293 | 2390 | 0.631 | 2390 | 0.631 | 1.1 | 1.26 | -0.0103
CFLBldgPGEERCNewCZ05 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ERC | New | CZ05 | 2.39 | 0.000631 | 0 | 2.55 | 0.000809 | -0.0272 | 2.39 | 0.000631 | 0 | 2.55 | 0.000809 | -0.0272 |  | CFL | Bldg | 2390 | 0.631 | 2390 | 0.631 | 1.07 | 1.28 | -0.011381 | 2390 | 0.631 | 2390 | 0.631 | 1.07 | 1.28 | -0.0114
CFLBldgPGEERCNewCZ11 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ERC | New | CZ11 | 2.39 | 1.82e-05 | 0 | 2.68 | 1.82e-05 | -0.0284 | 2.39 | 1.82e-05 | 0 | 2.68 | 1.82e-05 | -0.0284 |  | CFL | Bldg | 2390 | 0.0182 | 2390 | 0.0182 | 1.12 | 1 | -0.011883 | 2390 | 0.0182 | 2390 | 0.0182 | 1.12 | 1 | -0.0119
CFLBldgPGEERCNewCZ12 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ERC | New | CZ12 | 2.39 | 1.82e-05 | 0 | 2.63 | 1.82e-05 | -0.0289 | 2.39 | 1.82e-05 | 0 | 2.63 | 1.82e-05 | -0.0289 |  | CFL | Bldg | 2390 | 0.0182 | 2390 | 0.0182 | 1.1 | 1 | -0.012092 | 2390 | 0.0182 | 2390 | 0.0182 | 1.1 | 1 | -0.0121
CFLBldgPGEERCNewCZ13 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ERC | New | CZ13 | 2.39 | 1.82e-05 | 0 | 2.67 | 1.82e-05 | -0.0253 | 2.39 | 1.82e-05 | 0 | 2.67 | 1.82e-05 | -0.0253 |  | CFL | Bldg | 2390 | 0.0182 | 2390 | 0.0182 | 1.12 | 1 | -0.010586 | 2390 | 0.0182 | 2390 | 0.0182 | 1.12 | 1 | -0.0106
CFLBldgPGEERCNewCZ16 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ERC | New | CZ16 | 2.39 | 1.82e-05 | 0 | 2.45 | 1.82e-05 | -0.0439 | 2.39 | 1.82e-05 | 0 | 2.45 | 1.82e-05 | -0.0439 |  | CFL | Bldg | 2390 | 0.0182 | 2390 | 0.0182 | 1.03 | 1 | -0.018368 | 2390 | 0.0182 | 2390 | 0.0182 | 1.03 | 1 | -0.0184
CFLBldgPGEERCNewIOU | Com-Iltg-dWatt-CFL_OSbldg | PGE | ERC | New | IOU | 2.39 | 0.00010463 | 0 | 2.6226 | 0.00012776 | -0.027908 | 2.39 | 0.00010463 | 0 | 2.6226 | 0.00012776 | -0.027908 |  | CFL | Bldg | 2390 | 0.105 | 2390 | 0.105 | 1.1 | 1.22 | -0.011677 | 2390 | 0.105 | 2390 | 0.105 | 1.1 | 1.22 | -0.0117
CFLBldgPGEESeExCZ01 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ESe | Ex | CZ01 | 2.3254 | 0.00071282 | 0 | 2.2558 | 0.0008444 | -0.047505 | 2.21 | 0.00065319 | 0 | 2.15 | 0.00077323 | -0.0451 |  | CFL | Bldg | 2330 | 0.713 | 2210 | 0.653 | 0.973 | 1.18 | -0.020407 | 2330 | 0.713 | 2210 | 0.653 | 0.973 | 1.18 | -0.0204
CFLBldgPGEESeExCZ02 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ESe | Ex | CZ02 | 2.3263 | 1.9951e-05 | 0 | 2.426 | 1.9951e-05 | -0.029754 | 2.21 | 1.8303e-05 | 0 | 2.3 | 1.8303e-05 | -0.0283 |  | CFL | Bldg | 2330 | 0.02 | 2210 | 0.0183 | 1.04 | 1 | -0.012805 | 2330 | 0.02 | 2210 | 0.0183 | 1.04 | 1 | -0.0128
CFLBldgPGEESeExCZ03 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ESe | Ex | CZ03 | 2.3271 | 1.9962e-05 | 0 | 2.4171 | 1.9962e-05 | -0.030762 | 2.21 | 1.8302e-05 | 0 | 2.3 | 1.8302e-05 | -0.0292 |  | CFL | Bldg | 2330 | 0.02 | 2210 | 0.0183 | 1.04 | 1 | -0.013213 | 2330 | 0.02 | 2210 | 0.0183 | 1.04 | 1 | -0.0132
CFLBldgPGEESeExCZ04 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ESe | Ex | CZ04 | 2.3262 | 0.00071319 | 0 | 2.4759 | 0.00086481 | -0.023759 | 2.21 | 0.00065316 | 0 | 2.35 | 0.00079219 | -0.022597 |  | CFL | Bldg | 2330 | 0.713 | 2210 | 0.653 | 1.06 | 1.21 | -0.010225 | 2330 | 0.713 | 2210 | 0.653 | 1.06 | 1.21 | -0.0102
CFLBldgPGEESeExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ESe | Ex | CZ05 | 2.3262 | 0.00071318 | 0 | 2.4259 | 0.00084484 | -0.028152 | 2.21 | 0.00065316 | 0 | 2.3 | 0.00077319 | -0.026797 |  | CFL | Bldg | 2330 | 0.713 | 2210 | 0.653 | 1.04 | 1.18 | -0.012125 | 2330 | 0.713 | 2210 | 0.653 | 1.04 | 1.18 | -0.0121
CFLBldgPGEESeExCZ11 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ESe | Ex | CZ11 | 2.3229 | 1.9906e-05 | 0 | 2.4723 | 1.9906e-05 | -0.026223 | 2.21 | 1.8306e-05 | 0 | 2.35 | 1.8306e-05 | -0.025 |  | CFL | Bldg | 2320 | 0.0199 | 2210 | 0.0183 | 1.06 | 1 | -0.011312 | 2320 | 0.0199 | 2210 | 0.0183 | 1.06 | 1 | -0.0113
CFLBldgPGEESeExCZ12 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ESe | Ex | CZ12 | 2.3238 | 1.9917e-05 | 0 | 2.4533 | 1.9917e-05 | -0.027428 | 2.21 | 1.8305e-05 | 0 | 2.33 | 1.8305e-05 | -0.0261 |  | CFL | Bldg | 2320 | 0.0199 | 2210 | 0.0183 | 1.05 | 1 | -0.01181 | 2320 | 0.0199 | 2210 | 0.0183 | 1.05 | 1 | -0.0118
CFLBldgPGEESeExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ESe | Ex | CZ13 | 2.3236 | 1.9914e-05 | 0 | 2.493 | 1.9914e-05 | -0.023936 | 2.21 | 1.8305e-05 | 0 | 2.37 | 1.8305e-05 | -0.0228 |  | CFL | Bldg | 2320 | 0.0199 | 2210 | 0.0183 | 1.07 | 1 | -0.010317 | 2320 | 0.0199 | 2210 | 0.0183 | 1.07 | 1 | -0.0103
CFLBldgPGEESeExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ESe | Ex | CZ16 | 2.3235 | 1.9913e-05 | 0 | 2.2735 | 1.9913e-05 | -0.041181 | 2.21 | 1.8305e-05 | 0 | 2.16 | 1.8305e-05 | -0.0391 |  | CFL | Bldg | 2320 | 0.0199 | 2210 | 0.0183 | 0.977 | 1 | -0.017692 | 2320 | 0.0199 | 2210 | 0.0183 | 0.977 | 1 | -0.0177
CFLBldgPGEESeExIOU | Com-Iltg-dWatt-CFL_OSbldg | PGE | ESe | Ex | IOU | 2.3252 | 0.00014192 | 0 | 2.4478 | 0.00016799 | -0.027708 | 2.21 | 0.00013002 | 0 | 2.326 | 0.0001539 | -0.026348 |  | CFL | Bldg | 2330 | 0.142 | 2210 | 0.13 | 1.05 | 1.18 | -0.011922 | 2330 | 0.142 | 2210 | 0.13 | 1.05 | 1.18 | -0.0119
CFLBldgPGEESeNewCZ01 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ESe | New | CZ01 | 2.21 | 0.000658 | 0 | 2.18 | 0.000757 | -0.0356 | 2.21 | 0.000658 | 0 | 2.18 | 0.000757 | -0.0356 |  | CFL | Bldg | 2210 | 0.658 | 2210 | 0.658 | 0.986 | 1.15 | -0.016109 | 2210 | 0.658 | 2210 | 0.658 | 0.986 | 1.15 | -0.0161
CFLBldgPGEESeNewCZ02 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ESe | New | CZ02 | 2.21 | 1.84e-05 | 0 | 2.33 | 1.84e-05 | -0.0327 | 2.21 | 1.84e-05 | 0 | 2.33 | 1.84e-05 | -0.0327 |  | CFL | Bldg | 2210 | 0.0184 | 2210 | 0.0184 | 1.05 | 1 | -0.014796 | 2210 | 0.0184 | 2210 | 0.0184 | 1.05 | 1 | -0.0148
CFLBldgPGEESeNewCZ03 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ESe | New | CZ03 | 2.21 | 1.84e-05 | 0 | 2.3 | 1.84e-05 | -0.0287 | 2.21 | 1.84e-05 | 0 | 2.3 | 1.84e-05 | -0.0287 |  | CFL | Bldg | 2210 | 0.0184 | 2210 | 0.0184 | 1.04 | 1 | -0.012986 | 2210 | 0.0184 | 2210 | 0.0184 | 1.04 | 1 | -0.013
CFLBldgPGEESeNewCZ04 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ESe | New | CZ04 | 2.21 | 0.000658 | 0 | 2.36 | 0.000856 | -0.0261 | 2.21 | 0.000658 | 0 | 2.36 | 0.000856 | -0.0261 |  | CFL | Bldg | 2210 | 0.658 | 2210 | 0.658 | 1.07 | 1.3 | -0.01181 | 2210 | 0.658 | 2210 | 0.658 | 1.07 | 1.3 | -0.0118
CFLBldgPGEESeNewCZ05 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ESe | New | CZ05 | 2.21 | 0.000658 | 0 | 2.29 | 0.000797 | -0.025 | 2.21 | 0.000658 | 0 | 2.29 | 0.000797 | -0.025 |  | CFL | Bldg | 2210 | 0.658 | 2210 | 0.658 | 1.04 | 1.21 | -0.011312 | 2210 | 0.658 | 2210 | 0.658 | 1.04 | 1.21 | -0.0113
CFLBldgPGEESeNewCZ11 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ESe | New | CZ11 | 2.21 | 1.84e-05 | 0 | 2.41 | 1.84e-05 | -0.0283 | 2.21 | 1.84e-05 | 0 | 2.41 | 1.84e-05 | -0.0283 |  | CFL | Bldg | 2210 | 0.0184 | 2210 | 0.0184 | 1.09 | 1 | -0.012805 | 2210 | 0.0184 | 2210 | 0.0184 | 1.09 | 1 | -0.0128
CFLBldgPGEESeNewCZ12 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ESe | New | CZ12 | 2.21 | 1.84e-05 | 0 | 2.38 | 1.84e-05 | -0.0292 | 2.21 | 1.84e-05 | 0 | 2.38 | 1.84e-05 | -0.0292 |  | CFL | Bldg | 2210 | 0.0184 | 2210 | 0.0184 | 1.08 | 1 | -0.013213 | 2210 | 0.0184 | 2210 | 0.0184 | 1.08 | 1 | -0.0132
CFLBldgPGEESeNewCZ13 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ESe | New | CZ13 | 2.21 | 1.84e-05 | 0 | 2.43 | 1.84e-05 | -0.0263 | 2.21 | 1.84e-05 | 0 | 2.43 | 1.84e-05 | -0.0263 |  | CFL | Bldg | 2210 | 0.0184 | 2210 | 0.0184 | 1.1 | 1 | -0.0119 | 2210 | 0.0184 | 2210 | 0.0184 | 1.1 | 1 | -0.0119
CFLBldgPGEESeNewCZ16 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ESe | New | CZ16 | 2.21 | 1.84e-05 | 0 | 2.21 | 1.84e-05 | -0.0327 | 2.21 | 1.84e-05 | 0 | 2.21 | 1.84e-05 | -0.0327 |  | CFL | Bldg | 2210 | 0.0184 | 2210 | 0.0184 | 1 | 1 | -0.014796 | 2210 | 0.0184 | 2210 | 0.0184 | 1 | 1 | -0.0148
CFLBldgPGEESeNewIOU | Com-Iltg-dWatt-CFL_OSbldg | PGE | ESe | New | IOU | 2.21 | 0.00010861 | 0 | 2.3699 | 0.00013465 | -0.028244 | 2.21 | 0.00010861 | 0 | 2.3699 | 0.00013465 | -0.028244 |  | CFL | Bldg | 2210 | 0.109 | 2210 | 0.109 | 1.07 | 1.24 | -0.01278 | 2210 | 0.109 | 2210 | 0.109 | 1.07 | 1.24 | -0.0128
CFLBldgPGEEUnExCZ01 | Com-Iltg-dWatt-CFL_OSbldg | PGE | EUn | Ex | CZ01 | 2.367 | 0.00066682 | 0 | 2.497 | 0.00081833 | -0.02507 | 2.26 | 0.00059092 | 0 | 2.39 | 0.00072492 | -0.024 |  | CFL | Bldg | 2370 | 0.667 | 2260 | 0.591 | 1.06 | 1.23 | -0.010619 | 2370 | 0.667 | 2260 | 0.591 | 1.06 | 1.23 | -0.0106
CFLBldgPGEEUnExCZ02 | Com-Iltg-dWatt-CFL_OSbldg | PGE | EUn | Ex | CZ02 | 2.3647 | 0.00043645 | 0 | 2.5947 | 0.00054083 | -0.018361 | 2.26 | 0.0003879 | 0 | 2.49 | 0.00048086 | -0.0176 |  | CFL | Bldg | 2360 | 0.436 | 2260 | 0.388 | 1.1 | 1.24 | -0.0077876 | 2360 | 0.436 | 2260 | 0.388 | 1.1 | 1.24 | -0.00779
CFLBldgPGEEUnExCZ03 | Com-Iltg-dWatt-CFL_OSbldg | PGE | EUn | Ex | CZ03 | 2.366 | 0.00043705 | 0 | 2.5956 | 0.00052865 | -0.017571 | 2.26 | 0.00038793 | 0 | 2.48 | 0.00046893 | -0.0168 |  | CFL | Bldg | 2370 | 0.437 | 2260 | 0.388 | 1.1 | 1.21 | -0.0074336 | 2370 | 0.437 | 2260 | 0.388 | 1.1 | 1.21 | -0.00743
CFLBldgPGEEUnExCZ04 | Com-Iltg-dWatt-CFL_OSbldg | PGE | EUn | Ex | CZ04 | 2.3643 | 0.00066484 | 0 | 2.6338 | 0.00084966 | -0.014265 | 2.26 | 0.0005909 | 0 | 2.5295 | 0.00075486 | -0.013697 |  | CFL | Bldg | 2360 | 0.665 | 2260 | 0.591 | 1.12 | 1.28 | -0.0060604 | 2360 | 0.665 | 2260 | 0.591 | 1.12 | 1.28 | -0.00606
CFLBldgPGEEUnExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | PGE | EUn | Ex | CZ05 | 2.3643 | 0.00066484 | 0 | 2.5838 | 0.00080895 | -0.016758 | 2.26 | 0.0005909 | 0 | 2.47 | 0.0007189 | -0.016095 |  | CFL | Bldg | 2360 | 0.665 | 2260 | 0.591 | 1.09 | 1.22 | -0.0071216 | 2360 | 0.665 | 2260 | 0.591 | 1.09 | 1.22 | -0.00712
CFLBldgPGEEUnExCZ11 | Com-Iltg-dWatt-CFL_OSbldg | PGE | EUn | Ex | CZ11 | 2.3633 | 0.0004358 | 0 | 2.6428 | 0.00054895 | -0.016458 | 2.26 | 0.00038788 | 0 | 2.5394 | 0.00048788 | -0.0158 |  | CFL | Bldg | 2360 | 0.436 | 2260 | 0.388 | 1.12 | 1.26 | -0.0069912 | 2360 | 0.436 | 2260 | 0.388 | 1.12 | 1.26 | -0.00699
CFLBldgPGEEUnExCZ12 | Com-Iltg-dWatt-CFL_OSbldg | PGE | EUn | Ex | CZ12 | 2.3636 | 0.00043592 | 0 | 2.633 | 0.00054516 | -0.016359 | 2.26 | 0.00038788 | 0 | 2.5294 | 0.00048488 | -0.0157 |  | CFL | Bldg | 2360 | 0.436 | 2260 | 0.388 | 1.12 | 1.25 | -0.0069469 | 2360 | 0.436 | 2260 | 0.388 | 1.12 | 1.25 | -0.00695
CFLBldgPGEEUnExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | PGE | EUn | Ex | CZ13 | 2.3634 | 0.00043581 | 0 | 2.6628 | 0.00055391 | -0.014364 | 2.26 | 0.00038788 | 0 | 2.55 | 0.00049282 | -0.0138 |  | CFL | Bldg | 2360 | 0.436 | 2260 | 0.388 | 1.13 | 1.27 | -0.0061062 | 2360 | 0.436 | 2260 | 0.388 | 1.13 | 1.27 | -0.00611
CFLBldgPGEEUnExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | PGE | EUn | Ex | CZ16 | 2.3651 | 0.00043663 | 0 | 2.5146 | 0.00052714 | -0.025746 | 2.26 | 0.00038791 | 0 | 2.4095 | 0.00046791 | -0.024696 |  | CFL | Bldg | 2370 | 0.437 | 2260 | 0.388 | 1.07 | 1.21 | -0.010927 | 2370 | 0.437 | 2260 | 0.388 | 1.07 | 1.21 | -0.0109
CFLBldgPGEEUnExIOU | Com-Iltg-dWatt-CFL_OSbldg | PGE | EUn | Ex | IOU | 2.3647 | 0.00048007 | 0 | 2.6135 | 0.00059445 | -0.016811 | 2.26 | 0.00042661 | 0 | 2.5031 | 0.00052801 | -0.01611 |  | CFL | Bldg | 2360 | 0.48 | 2260 | 0.427 | 1.11 | 1.24 | -0.0071285 | 2360 | 0.48 | 2260 | 0.427 | 1.11 | 1.24 | -0.00713
CFLBldgPGEEUnNewCZ01 | Com-Iltg-dWatt-CFL_OSbldg | PGE | EUn | New | CZ01 | 2.26 | 0.000588 | 0 | 2.37 | 0.00069 | -0.0218 | 2.26 | 0.000588 | 0 | 2.37 | 0.00069 | -0.0218 |  | CFL | Bldg | 2260 | 0.588 | 2260 | 0.588 | 1.05 | 1.17 | -0.009646 | 2260 | 0.588 | 2260 | 0.588 | 1.05 | 1.17 | -0.00965
CFLBldgPGEEUnNewCZ02 | Com-Iltg-dWatt-CFL_OSbldg | PGE | EUn | New | CZ02 | 2.26 | 0.000386 | 0 | 2.5 | 0.000502 | -0.0176 | 2.26 | 0.000386 | 0 | 2.5 | 0.000502 | -0.0176 |  | CFL | Bldg | 2260 | 0.386 | 2260 | 0.386 | 1.11 | 1.3 | -0.0077876 | 2260 | 0.386 | 2260 | 0.386 | 1.11 | 1.3 | -0.00779
CFLBldgPGEEUnNewCZ03 | Com-Iltg-dWatt-CFL_OSbldg | PGE | EUn | New | CZ03 | 2.26 | 0.000386 | 0 | 2.45 | 0.000487 | -0.013 | 2.26 | 0.000386 | 0 | 2.45 | 0.000487 | -0.013 |  | CFL | Bldg | 2260 | 0.386 | 2260 | 0.386 | 1.08 | 1.26 | -0.0057522 | 2260 | 0.386 | 2260 | 0.386 | 1.08 | 1.26 | -0.00575
CFLBldgPGEEUnNewCZ04 | Com-Iltg-dWatt-CFL_OSbldg | PGE | EUn | New | CZ04 | 2.26 | 0.000588 | 0 | 2.52 | 0.000738 | -0.0117 | 2.26 | 0.000588 | 0 | 2.52 | 0.000738 | -0.0117 |  | CFL | Bldg | 2260 | 0.588 | 2260 | 0.588 | 1.12 | 1.26 | -0.005177 | 2260 | 0.588 | 2260 | 0.588 | 1.12 | 1.26 | -0.00518
CFLBldgPGEEUnNewCZ05 | Com-Iltg-dWatt-CFL_OSbldg | PGE | EUn | New | CZ05 | 2.26 | 0.000588 | 0 | 2.46 | 0.000708 | -0.0141 | 2.26 | 0.000588 | 0 | 2.46 | 0.000708 | -0.0141 |  | CFL | Bldg | 2260 | 0.588 | 2260 | 0.588 | 1.09 | 1.2 | -0.0062389 | 2260 | 0.588 | 2260 | 0.588 | 1.09 | 1.2 | -0.00624
CFLBldgPGEEUnNewCZ11 | Com-Iltg-dWatt-CFL_OSbldg | PGE | EUn | New | CZ11 | 2.26 | 0.000386 | 0 | 2.56 | 0.0005 | -0.0131 | 2.26 | 0.000386 | 0 | 2.56 | 0.0005 | -0.0131 |  | CFL | Bldg | 2260 | 0.386 | 2260 | 0.386 | 1.13 | 1.3 | -0.0057965 | 2260 | 0.386 | 2260 | 0.386 | 1.13 | 1.3 | -0.0058
CFLBldgPGEEUnNewCZ12 | Com-Iltg-dWatt-CFL_OSbldg | PGE | EUn | New | CZ12 | 2.26 | 0.000386 | 0 | 2.55 | 0.000502 | -0.0142 | 2.26 | 0.000386 | 0 | 2.55 | 0.000502 | -0.0142 |  | CFL | Bldg | 2260 | 0.386 | 2260 | 0.386 | 1.13 | 1.3 | -0.0062832 | 2260 | 0.386 | 2260 | 0.386 | 1.13 | 1.3 | -0.00628
CFLBldgPGEEUnNewCZ13 | Com-Iltg-dWatt-CFL_OSbldg | PGE | EUn | New | CZ13 | 2.26 | 0.000386 | 0 | 2.62 | 0.000523 | -0.0147 | 2.26 | 0.000386 | 0 | 2.62 | 0.000523 | -0.0147 |  | CFL | Bldg | 2260 | 0.386 | 2260 | 0.386 | 1.16 | 1.35 | -0.0065044 | 2260 | 0.386 | 2260 | 0.386 | 1.16 | 1.35 | -0.0065
CFLBldgPGEEUnNewCZ16 | Com-Iltg-dWatt-CFL_OSbldg | PGE | EUn | New | CZ16 | 2.26 | 0.000386 | 0 | 2.4 | 0.000482 | -0.0235 | 2.26 | 0.000386 | 0 | 2.4 | 0.000482 | -0.0235 |  | CFL | Bldg | 2260 | 0.386 | 2260 | 0.386 | 1.06 | 1.25 | -0.010398 | 2260 | 0.386 | 2260 | 0.386 | 1.06 | 1.25 | -0.0104
CFLBldgPGEEUnNewIOU | Com-Iltg-dWatt-CFL_OSbldg | PGE | EUn | New | IOU | 2.26 | 0.00042476 | 0 | 2.5181 | 0.00054336 | -0.013959 | 2.26 | 0.00042476 | 0 | 2.5181 | 0.00054336 | -0.013959 |  | CFL | Bldg | 2260 | 0.425 | 2260 | 0.425 | 1.11 | 1.28 | -0.0061766 | 2260 | 0.425 | 2260 | 0.425 | 1.11 | 1.28 | -0.00618
CFLBldgPGEGroExCZ01 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Gro | Ex | CZ01 | 3.8916 | 0.00049529 | 0 | 3.1309 | 0.00046234 | -0.068441 | 3.85 | 0.00048995 | 0 | 3.1 | 0.000457 | -0.0678 |  | CFL | Bldg | 3890 | 0.495 | 3850 | 0.49 | 0.805 | 0.933 | -0.01761 | 3890 | 0.495 | 3850 | 0.49 | 0.805 | 0.933 | -0.0176
CFLBldgPGEGroExCZ02 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Gro | Ex | CZ02 | 3.8923 | 0.00049541 | 0 | 3.5208 | 0.00066364 | -0.053332 | 3.85 | 0.00048995 | 0 | 3.48 | 0.00065614 | -0.052786 |  | CFL | Bldg | 3890 | 0.495 | 3850 | 0.49 | 0.904 | 1.34 | -0.013711 | 3890 | 0.495 | 3850 | 0.49 | 0.904 | 1.34 | -0.0137
CFLBldgPGEGroExCZ03 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Gro | Ex | CZ03 | 3.8917 | 0.00049532 | 0 | 3.361 | 0.00062539 | -0.060732 | 3.85 | 0.00048996 | 0 | 3.3288 | 0.000618 | -0.0601 |  | CFL | Bldg | 3890 | 0.495 | 3850 | 0.49 | 0.865 | 1.26 | -0.01561 | 3890 | 0.495 | 3850 | 0.49 | 0.865 | 1.26 | -0.0156
CFLBldgPGEGroExCZ04 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Gro | Ex | CZ04 | 3.888 | 0.0004947 | 0 | 3.588 | 0.00062865 | -0.05128 | 3.85 | 0.00048995 | 0 | 3.55 | 0.000622 | -0.0509 |  | CFL | Bldg | 3890 | 0.495 | 3850 | 0.49 | 0.922 | 1.27 | -0.013221 | 3890 | 0.495 | 3850 | 0.49 | 0.922 | 1.27 | -0.0132
CFLBldgPGEGroExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Gro | Ex | CZ05 | 3.888 | 0.00049469 | 0 | 3.3285 | 0.0006067 | -0.06067 | 3.85 | 0.00048995 | 0 | 3.3 | 0.000601 | -0.0601 |  | CFL | Bldg | 3890 | 0.495 | 3850 | 0.49 | 0.857 | 1.23 | -0.01561 | 3890 | 0.495 | 3850 | 0.49 | 0.857 | 1.23 | -0.0156
CFLBldgPGEGroExCZ11 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Gro | Ex | CZ11 | 3.887 | 0.00049461 | 0 | 3.807 | 0.00065953 | -0.043566 | 3.85 | 0.00048997 | 0 | 3.77 | 0.00065305 | -0.043195 |  | CFL | Bldg | 3890 | 0.495 | 3850 | 0.49 | 0.979 | 1.33 | -0.01122 | 3890 | 0.495 | 3850 | 0.49 | 0.979 | 1.33 | -0.0112
CFLBldgPGEGroExCZ12 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Gro | Ex | CZ12 | 3.8874 | 0.00049465 | 0 | 3.698 | 0.00065454 | -0.047374 | 3.85 | 0.00048998 | 0 | 3.67 | 0.000648 | -0.047 |  | CFL | Bldg | 3890 | 0.495 | 3850 | 0.49 | 0.953 | 1.32 | -0.012208 | 3890 | 0.495 | 3850 | 0.49 | 0.953 | 1.32 | -0.0122
CFLBldgPGEGroExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Gro | Ex | CZ13 | 3.887 | 0.0004946 | 0 | 3.837 | 0.00065448 | -0.041173 | 3.85 | 0.00048997 | 0 | 3.8 | 0.000648 | -0.040895 |  | CFL | Bldg | 3890 | 0.495 | 3850 | 0.49 | 0.987 | 1.32 | -0.010622 | 3890 | 0.495 | 3850 | 0.49 | 0.987 | 1.32 | -0.0106
CFLBldgPGEGroExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Gro | Ex | CZ16 | 3.8873 | 0.00049464 | 0 | 3.3476 | 0.00061953 | -0.056362 | 3.85 | 0.00048998 | 0 | 3.3196 | 0.000613 | -0.055896 |  | CFL | Bldg | 3890 | 0.495 | 3850 | 0.49 | 0.862 | 1.25 | -0.014518 | 3890 | 0.495 | 3850 | 0.49 | 0.862 | 1.25 | -0.0145
CFLBldgPGEGroExIOU | Com-Iltg-dWatt-CFL_OSbldg | PGE | Gro | Ex | IOU | 3.889 | 0.0004949 | 0 | 3.5864 | 0.00064046 | -0.051469 | 3.85 | 0.00048996 | 0 | 3.5528 | 0.00063364 | -0.051016 |  | CFL | Bldg | 3890 | 0.495 | 3850 | 0.49 | 0.923 | 1.29 | -0.013251 | 3890 | 0.495 | 3850 | 0.49 | 0.923 | 1.29 | -0.0133
CFLBldgPGEGroNewCZ01 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Gro | New | CZ01 | 3.85 | 0.000489 | 0 | 3.19 | 0.000576 | -0.0721 | 3.85 | 0.000489 | 0 | 3.19 | 0.000576 | -0.0721 |  | CFL | Bldg | 3850 | 0.489 | 3850 | 0.489 | 0.829 | 1.18 | -0.018727 | 3850 | 0.489 | 3850 | 0.489 | 0.829 | 1.18 | -0.0187
CFLBldgPGEGroNewCZ02 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Gro | New | CZ02 | 3.85 | 0.000489 | 0 | 3.63 | 0.00068 | -0.0528 | 3.85 | 0.000489 | 0 | 3.63 | 0.00068 | -0.0528 |  | CFL | Bldg | 3850 | 0.489 | 3850 | 0.489 | 0.943 | 1.39 | -0.013714 | 3850 | 0.489 | 3850 | 0.489 | 0.943 | 1.39 | -0.0137
CFLBldgPGEGroNewCZ03 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Gro | New | CZ03 | 3.85 | 0.000489 | 0 | 3.44 | 0.00064 | -0.0594 | 3.85 | 0.000489 | 0 | 3.44 | 0.00064 | -0.0594 |  | CFL | Bldg | 3850 | 0.489 | 3850 | 0.489 | 0.894 | 1.31 | -0.015429 | 3850 | 0.489 | 3850 | 0.489 | 0.894 | 1.31 | -0.0154
CFLBldgPGEGroNewCZ04 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Gro | New | CZ04 | 3.85 | 0.000489 | 0 | 3.72 | 0.000639 | -0.0486 | 3.85 | 0.000489 | 0 | 3.72 | 0.000639 | -0.0486 |  | CFL | Bldg | 3850 | 0.489 | 3850 | 0.489 | 0.966 | 1.31 | -0.012623 | 3850 | 0.489 | 3850 | 0.489 | 0.966 | 1.31 | -0.0126
CFLBldgPGEGroNewCZ05 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Gro | New | CZ05 | 3.85 | 0.000489 | 0 | 3.43 | 0.000619 | -0.059 | 3.85 | 0.000489 | 0 | 3.43 | 0.000619 | -0.059 |  | CFL | Bldg | 3850 | 0.489 | 3850 | 0.489 | 0.891 | 1.27 | -0.015325 | 3850 | 0.489 | 3850 | 0.489 | 0.891 | 1.27 | -0.0153
CFLBldgPGEGroNewCZ11 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Gro | New | CZ11 | 3.85 | 0.000489 | 0 | 3.9 | 0.000685 | -0.042 | 3.85 | 0.000489 | 0 | 3.9 | 0.000685 | -0.042 |  | CFL | Bldg | 3850 | 0.489 | 3850 | 0.489 | 1.01 | 1.4 | -0.010909 | 3850 | 0.489 | 3850 | 0.489 | 1.01 | 1.4 | -0.0109
CFLBldgPGEGroNewCZ12 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Gro | New | CZ12 | 3.85 | 0.000489 | 0 | 3.82 | 0.000687 | -0.0466 | 3.85 | 0.000489 | 0 | 3.82 | 0.000687 | -0.0466 |  | CFL | Bldg | 3850 | 0.489 | 3850 | 0.489 | 0.992 | 1.4 | -0.012104 | 3850 | 0.489 | 3850 | 0.489 | 0.992 | 1.4 | -0.0121
CFLBldgPGEGroNewCZ13 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Gro | New | CZ13 | 3.85 | 0.000489 | 0 | 3.94 | 0.000664 | -0.0397 | 3.85 | 0.000489 | 0 | 3.94 | 0.000664 | -0.0397 |  | CFL | Bldg | 3850 | 0.489 | 3850 | 0.489 | 1.02 | 1.36 | -0.010312 | 3850 | 0.489 | 3850 | 0.489 | 1.02 | 1.36 | -0.0103
CFLBldgPGEGroNewCZ16 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Gro | New | CZ16 | 3.85 | 0.000489 | 0 | 3.48 | 0.000623 | -0.0547 | 3.85 | 0.000489 | 0 | 3.48 | 0.000623 | -0.0547 |  | CFL | Bldg | 3850 | 0.489 | 3850 | 0.489 | 0.904 | 1.27 | -0.014208 | 3850 | 0.489 | 3850 | 0.489 | 0.904 | 1.27 | -0.0142
CFLBldgPGEGroNewIOU | Com-Iltg-dWatt-CFL_OSbldg | PGE | Gro | New | IOU | 3.85 | 0.000489 | 0 | 3.7296 | 0.0006629 | -0.048674 | 3.85 | 0.000489 | 0 | 3.7296 | 0.0006629 | -0.048674 |  | CFL | Bldg | 3850 | 0.489 | 3850 | 0.489 | 0.969 | 1.36 | -0.012642 | 3850 | 0.489 | 3850 | 0.489 | 0.969 | 1.36 | -0.0126
CFLBldgPGEHspExCZ01 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Hsp | Ex | CZ01 | 4.2029 | 0.00071749 | 0 | 4.5024 | 0.00082244 | -0.036924 | 4.1804 | 0.000713 | 0 | 4.48 | 0.000817 | -0.0367 |  | CFL | Bldg | 4200 | 0.717 | 4180 | 0.713 | 1.07 | 1.15 | -0.008779 | 4200 | 0.717 | 4180 | 0.713 | 1.07 | 1.15 | -0.00878
CFLBldgPGEHspExCZ02 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Hsp | Ex | CZ02 | 4.2044 | 0.00071777 | 0 | 4.6268 | 0.00088197 | -0.028819 | 4.1805 | 0.000713 | 0 | 4.6076 | 0.000876 | -0.0287 |  | CFL | Bldg | 4200 | 0.718 | 4180 | 0.713 | 1.1 | 1.23 | -0.0068652 | 4200 | 0.718 | 4180 | 0.713 | 1.1 | 1.23 | -0.00687
CFLBldgPGEHspExCZ03 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Hsp | Ex | CZ03 | 4.204 | 0.00071771 | 0 | 4.6536 | 0.00086089 | -0.02734 | 4.1805 | 0.000713 | 0 | 4.6277 | 0.00085523 | -0.0272 |  | CFL | Bldg | 4200 | 0.718 | 4180 | 0.713 | 1.11 | 1.2 | -0.0065064 | 4200 | 0.718 | 4180 | 0.713 | 1.11 | 1.2 | -0.00651
CFLBldgPGEHspExCZ04 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Hsp | Ex | CZ04 | 4.1995 | 0.00071679 | 0 | 4.649 | 0.00087374 | -0.025995 | 4.1805 | 0.000713 | 0 | 4.63 | 0.000869 | -0.0259 |  | CFL | Bldg | 4200 | 0.717 | 4180 | 0.713 | 1.11 | 1.22 | -0.0061954 | 4200 | 0.717 | 4180 | 0.713 | 1.11 | 1.22 | -0.0062
CFLBldgPGEHspExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Hsp | Ex | CZ05 | 4.1995 | 0.00071679 | 0 | 4.5695 | 0.00084474 | -0.028995 | 4.1805 | 0.000713 | 0 | 4.56 | 0.00083905 | -0.0289 |  | CFL | Bldg | 4200 | 0.717 | 4180 | 0.713 | 1.09 | 1.18 | -0.006913 | 4200 | 0.717 | 4180 | 0.713 | 1.09 | 1.18 | -0.00691
CFLBldgPGEHspExCZ11 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Hsp | Ex | CZ11 | 4.2002 | 0.00071692 | 0 | 4.6696 | 0.0008869 | -0.027102 | 4.1806 | 0.000713 | 0 | 4.65 | 0.0008811 | -0.027 |  | CFL | Bldg | 4200 | 0.717 | 4180 | 0.713 | 1.11 | 1.24 | -0.0064584 | 4200 | 0.717 | 4180 | 0.713 | 1.11 | 1.24 | -0.00646
CFLBldgPGEHspExCZ12 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Hsp | Ex | CZ12 | 4.2002 | 0.00071692 | 0 | 4.6596 | 0.00088489 | -0.026398 | 4.1806 | 0.000713 | 0 | 4.64 | 0.00087911 | -0.0263 |  | CFL | Bldg | 4200 | 0.717 | 4180 | 0.713 | 1.11 | 1.23 | -0.0062909 | 4200 | 0.717 | 4180 | 0.713 | 1.11 | 1.23 | -0.00629
CFLBldgPGEHspExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Hsp | Ex | CZ13 | 4.2002 | 0.00071692 | 0 | 4.6896 | 0.00088289 | -0.025498 | 4.1806 | 0.000713 | 0 | 4.67 | 0.000878 | -0.025396 |  | CFL | Bldg | 4200 | 0.717 | 4180 | 0.713 | 1.12 | 1.23 | -0.0060746 | 4200 | 0.717 | 4180 | 0.713 | 1.12 | 1.23 | -0.00607
CFLBldgPGEHspExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Hsp | Ex | CZ16 | 4.2002 | 0.00071693 | 0 | 4.4196 | 0.00085691 | -0.041796 | 4.1805 | 0.000713 | 0 | 4.4 | 0.000852 | -0.0416 |  | CFL | Bldg | 4200 | 0.717 | 4180 | 0.713 | 1.05 | 1.19 | -0.0099509 | 4200 | 0.717 | 4180 | 0.713 | 1.05 | 1.19 | -0.00995
CFLBldgPGEHspExIOU | Com-Iltg-dWatt-CFL_OSbldg | PGE | Hsp | Ex | IOU | 4.2016 | 0.00071722 | 0 | 4.6545 | 0.00087442 | -0.026977 | 4.1806 | 0.000713 | 0 | 4.6334 | 0.00086894 | -0.026863 |  | CFL | Bldg | 4200 | 0.717 | 4180 | 0.713 | 1.11 | 1.22 | -0.0064256 | 4200 | 0.717 | 4180 | 0.713 | 1.11 | 1.22 | -0.00643
CFLBldgPGEHspNewCZ01 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Hsp | New | CZ01 | 4.19 | 0.000713 | 0 | 4.28 | 0.000778 | -0.039 | 4.19 | 0.000713 | 0 | 4.28 | 0.000778 | -0.039 |  | CFL | Bldg | 4190 | 0.713 | 4190 | 0.713 | 1.02 | 1.09 | -0.0093079 | 4190 | 0.713 | 4190 | 0.713 | 1.02 | 1.09 | -0.00931
CFLBldgPGEHspNewCZ02 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Hsp | New | CZ02 | 4.19 | 0.000713 | 0 | 4.44 | 0.000852 | -0.0312 | 4.19 | 0.000713 | 0 | 4.44 | 0.000852 | -0.0312 |  | CFL | Bldg | 4190 | 0.713 | 4190 | 0.713 | 1.06 | 1.19 | -0.0074463 | 4190 | 0.713 | 4190 | 0.713 | 1.06 | 1.19 | -0.00745
CFLBldgPGEHspNewCZ03 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Hsp | New | CZ03 | 4.19 | 0.000713 | 0 | 4.42 | 0.000831 | -0.028 | 4.19 | 0.000713 | 0 | 4.42 | 0.000831 | -0.028 |  | CFL | Bldg | 4190 | 0.713 | 4190 | 0.713 | 1.05 | 1.17 | -0.0066826 | 4190 | 0.713 | 4190 | 0.713 | 1.05 | 1.17 | -0.00668
CFLBldgPGEHspNewCZ04 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Hsp | New | CZ04 | 4.19 | 0.000713 | 0 | 4.47 | 0.000845 | -0.0272 | 4.19 | 0.000713 | 0 | 4.47 | 0.000845 | -0.0272 |  | CFL | Bldg | 4190 | 0.713 | 4190 | 0.713 | 1.07 | 1.19 | -0.0064916 | 4190 | 0.713 | 4190 | 0.713 | 1.07 | 1.19 | -0.00649
CFLBldgPGEHspNewCZ05 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Hsp | New | CZ05 | 4.19 | 0.000713 | 0 | 4.39 | 0.00082 | -0.0314 | 4.19 | 0.000713 | 0 | 4.39 | 0.00082 | -0.0314 |  | CFL | Bldg | 4190 | 0.713 | 4190 | 0.713 | 1.05 | 1.15 | -0.007494 | 4190 | 0.713 | 4190 | 0.713 | 1.05 | 1.15 | -0.00749
CFLBldgPGEHspNewCZ11 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Hsp | New | CZ11 | 4.19 | 0.000713 | 0 | 4.53 | 0.000857 | -0.029 | 4.19 | 0.000713 | 0 | 4.53 | 0.000857 | -0.029 |  | CFL | Bldg | 4190 | 0.713 | 4190 | 0.713 | 1.08 | 1.2 | -0.0069212 | 4190 | 0.713 | 4190 | 0.713 | 1.08 | 1.2 | -0.00692
CFLBldgPGEHspNewCZ12 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Hsp | New | CZ12 | 4.19 | 0.000713 | 0 | 4.5 | 0.000857 | -0.0282 | 4.19 | 0.000713 | 0 | 4.5 | 0.000857 | -0.0282 |  | CFL | Bldg | 4190 | 0.713 | 4190 | 0.713 | 1.07 | 1.2 | -0.0067303 | 4190 | 0.713 | 4190 | 0.713 | 1.07 | 1.2 | -0.00673
CFLBldgPGEHspNewCZ13 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Hsp | New | CZ13 | 4.19 | 0.000713 | 0 | 4.55 | 0.000855 | -0.0275 | 4.19 | 0.000713 | 0 | 4.55 | 0.000855 | -0.0275 |  | CFL | Bldg | 4190 | 0.713 | 4190 | 0.713 | 1.09 | 1.2 | -0.0065632 | 4190 | 0.713 | 4190 | 0.713 | 1.09 | 1.2 | -0.00656
CFLBldgPGEHspNewCZ16 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Hsp | New | CZ16 | 4.19 | 0.000713 | 0 | 4.23 | 0.000829 | -0.0465 | 4.19 | 0.000713 | 0 | 4.23 | 0.000829 | -0.0465 |  | CFL | Bldg | 4190 | 0.713 | 4190 | 0.713 | 1.01 | 1.16 | -0.011098 | 4190 | 0.713 | 4190 | 0.713 | 1.01 | 1.16 | -0.0111
CFLBldgPGEHspNewIOU | Com-Iltg-dWatt-CFL_OSbldg | PGE | Hsp | New | IOU | 4.19 | 0.000713 | 0 | 4.4785 | 0.00084689 | -0.028443 | 4.19 | 0.000713 | 0 | 4.4785 | 0.00084689 | -0.028443 |  | CFL | Bldg | 4190 | 0.713 | 4190 | 0.713 | 1.07 | 1.19 | -0.0067882 | 4190 | 0.713 | 4190 | 0.713 | 1.07 | 1.19 | -0.00679
CFLBldgPGEHtlExCZ01 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Htl | Ex | CZ01 | 1.6786 | 0.00020015 | 0 | 1.5192 | 0.0002395 | -0.0088224 | 1.6494 | 0.000195 | 0 | 1.49 | 0.000234 | -0.0086457 |  | CFL | Bldg | 1680 | 0.2 | 1650 | 0.195 | 0.903 | 1.2 | -0.0052418 | 1680 | 0.2 | 1650 | 0.195 | 0.903 | 1.2 | -0.00524
CFLBldgPGEHtlExCZ02 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Htl | Ex | CZ02 | 1.6791 | 0.00020021 | 0 | 1.6555 | 0.00024851 | -0.0064191 | 1.6494 | 0.000195 | 0 | 1.6236 | 0.00024258 | -0.0062866 |  | CFL | Bldg | 1680 | 0.2 | 1650 | 0.195 | 0.984 | 1.24 | -0.0038115 | 1680 | 0.2 | 1650 | 0.195 | 0.984 | 1.24 | -0.00381
CFLBldgPGEHtlExCZ03 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Htl | Ex | CZ03 | 1.6827 | 0.00020069 | 0 | 1.6827 | 0.00024611 | -0.0061965 | 1.6497 | 0.000195 | 0 | 1.6497 | 0.00023952 | -0.0060587 |  | CFL | Bldg | 1680 | 0.201 | 1650 | 0.195 | 1 | 1.23 | -0.0036726 | 1680 | 0.201 | 1650 | 0.195 | 1 | 1.23 | -0.00367
CFLBldgPGEHtlExCZ04 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Htl | Ex | CZ04 | 1.6681 | 0.00019875 | 0 | 1.7081 | 0.00024669 | -0.0051638 | 1.6494 | 0.000195 | 0 | 1.68 | 0.000242 | -0.0050794 |  | CFL | Bldg | 1670 | 0.199 | 1650 | 0.195 | 1.02 | 1.24 | -0.0030796 | 1670 | 0.199 | 1650 | 0.195 | 1.02 | 1.24 | -0.00308
CFLBldgPGEHtlExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Htl | Ex | CZ05 | 1.6681 | 0.00019875 | 0 | 1.6481 | 0.00024075 | -0.0063631 | 1.6494 | 0.000195 | 0 | 1.6294 | 0.000237 | -0.0062694 |  | CFL | Bldg | 1670 | 0.199 | 1650 | 0.195 | 0.988 | 1.22 | -0.0038011 | 1670 | 0.199 | 1650 | 0.195 | 0.988 | 1.22 | -0.0038
CFLBldgPGEHtlExCZ11 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Htl | Ex | CZ11 | 1.6705 | 0.00019907 | 0 | 1.7305 | 0.00025109 | -0.0055817 | 1.6493 | 0.000195 | 0 | 1.7009 | 0.00024685 | -0.005491 |  | CFL | Bldg | 1670 | 0.199 | 1650 | 0.195 | 1.03 | 1.27 | -0.0033293 | 1670 | 0.199 | 1650 | 0.195 | 1.03 | 1.27 | -0.00333
CFLBldgPGEHtlExCZ12 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Htl | Ex | CZ12 | 1.6704 | 0.00019906 | 0 | 1.7004 | 0.00025007 | -0.0056815 | 1.6492 | 0.000195 | 0 | 1.6709 | 0.00024583 | -0.0055911 |  | CFL | Bldg | 1670 | 0.199 | 1650 | 0.195 | 1.01 | 1.26 | -0.0033901 | 1670 | 0.199 | 1650 | 0.195 | 1.01 | 1.26 | -0.00339
CFLBldgPGEHtlExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Htl | Ex | CZ13 | 1.6704 | 0.00019905 | 0 | 1.7504 | 0.00024907 | -0.0052012 | 1.6493 | 0.000195 | 0 | 1.7208 | 0.000244 | -0.0051201 |  | CFL | Bldg | 1670 | 0.199 | 1650 | 0.195 | 1.04 | 1.25 | -0.0031044 | 1670 | 0.199 | 1650 | 0.195 | 1.04 | 1.25 | -0.0031
CFLBldgPGEHtlExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Htl | Ex | CZ16 | 1.6716 | 0.00019921 | 0 | 1.5316 | 0.00024326 | -0.0088671 | 1.6494 | 0.000195 | 0 | 1.5093 | 0.00023882 | -0.008721 |  | CFL | Bldg | 1670 | 0.199 | 1650 | 0.195 | 0.915 | 1.22 | -0.0052876 | 1670 | 0.199 | 1650 | 0.195 | 0.915 | 1.22 | -0.00529
CFLBldgPGEHtlExIOU | Com-Iltg-dWatt-CFL_OSbldg | PGE | Htl | Ex | IOU | 1.6761 | 0.00019981 | 0 | 1.6874 | 0.00024685 | -0.0059792 | 1.6495 | 0.000195 | 0 | 1.6572 | 0.00024133 | -0.0058643 |  | CFL | Bldg | 1680 | 0.2 | 1650 | 0.195 | 1 | 1.24 | -0.0035552 | 1680 | 0.2 | 1650 | 0.195 | 1 | 1.24 | -0.00356
CFLBldgPGEHtlNewCZ01 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Htl | New | CZ01 | 1.64 | 0.000195 | 0 | 1.45 | 0.000233 | -0.00953 | 1.64 | 0.000195 | 0 | 1.45 | 0.000233 | -0.00953 |  | CFL | Bldg | 1640 | 0.195 | 1640 | 0.195 | 0.884 | 1.19 | -0.005811 | 1640 | 0.195 | 1640 | 0.195 | 0.884 | 1.19 | -0.00581
CFLBldgPGEHtlNewCZ02 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Htl | New | CZ02 | 1.64 | 0.000195 | 0 | 1.6 | 0.000247 | -0.00745 | 1.64 | 0.000195 | 0 | 1.6 | 0.000247 | -0.00745 |  | CFL | Bldg | 1640 | 0.195 | 1640 | 0.195 | 0.976 | 1.27 | -0.0045427 | 1640 | 0.195 | 1640 | 0.195 | 0.976 | 1.27 | -0.00454
CFLBldgPGEHtlNewCZ03 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Htl | New | CZ03 | 1.64 | 0.000195 | 0 | 1.59 | 0.00024 | -0.00681 | 1.64 | 0.000195 | 0 | 1.59 | 0.00024 | -0.00681 |  | CFL | Bldg | 1640 | 0.195 | 1640 | 0.195 | 0.97 | 1.23 | -0.0041524 | 1640 | 0.195 | 1640 | 0.195 | 0.97 | 1.23 | -0.00415
CFLBldgPGEHtlNewCZ04 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Htl | New | CZ04 | 1.64 | 0.000195 | 0 | 1.67 | 0.000247 | -0.00588 | 1.64 | 0.000195 | 0 | 1.67 | 0.000247 | -0.00588 |  | CFL | Bldg | 1640 | 0.195 | 1640 | 0.195 | 1.02 | 1.27 | -0.0035854 | 1640 | 0.195 | 1640 | 0.195 | 1.02 | 1.27 | -0.00359
CFLBldgPGEHtlNewCZ05 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Htl | New | CZ05 | 1.64 | 0.000195 | 0 | 1.59 | 0.000238 | -0.00724 | 1.64 | 0.000195 | 0 | 1.59 | 0.000238 | -0.00724 |  | CFL | Bldg | 1640 | 0.195 | 1640 | 0.195 | 0.97 | 1.22 | -0.0044146 | 1640 | 0.195 | 1640 | 0.195 | 0.97 | 1.22 | -0.00441
CFLBldgPGEHtlNewCZ11 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Htl | New | CZ11 | 1.64 | 0.000195 | 0 | 1.68 | 0.000249 | -0.00647 | 1.64 | 0.000195 | 0 | 1.68 | 0.000249 | -0.00647 |  | CFL | Bldg | 1640 | 0.195 | 1640 | 0.195 | 1.02 | 1.28 | -0.0039451 | 1640 | 0.195 | 1640 | 0.195 | 1.02 | 1.28 | -0.00395
CFLBldgPGEHtlNewCZ12 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Htl | New | CZ12 | 1.64 | 0.000195 | 0 | 1.66 | 0.000248 | -0.00654 | 1.64 | 0.000195 | 0 | 1.66 | 0.000248 | -0.00654 |  | CFL | Bldg | 1640 | 0.195 | 1640 | 0.195 | 1.01 | 1.27 | -0.0039878 | 1640 | 0.195 | 1640 | 0.195 | 1.01 | 1.27 | -0.00399
CFLBldgPGEHtlNewCZ13 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Htl | New | CZ13 | 1.64 | 0.000195 | 0 | 1.69 | 0.000247 | -0.00593 | 1.64 | 0.000195 | 0 | 1.69 | 0.000247 | -0.00593 |  | CFL | Bldg | 1640 | 0.195 | 1640 | 0.195 | 1.03 | 1.27 | -0.0036159 | 1640 | 0.195 | 1640 | 0.195 | 1.03 | 1.27 | -0.00362
CFLBldgPGEHtlNewCZ16 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Htl | New | CZ16 | 1.64 | 0.000195 | 0 | 1.48 | 0.00024 | -0.0107 | 1.64 | 0.000195 | 0 | 1.48 | 0.00024 | -0.0107 |  | CFL | Bldg | 1640 | 0.195 | 1640 | 0.195 | 0.902 | 1.23 | -0.0065244 | 1640 | 0.195 | 1640 | 0.195 | 0.902 | 1.23 | -0.00652
CFLBldgPGEHtlNewIOU | Com-Iltg-dWatt-CFL_OSbldg | PGE | Htl | New | IOU | 1.64 | 0.000195 | 0 | 1.6311 | 0.00024449 | -0.0066856 | 1.64 | 0.000195 | 0 | 1.6311 | 0.00024449 | -0.0066856 |  | CFL | Bldg | 1640 | 0.195 | 1640 | 0.195 | 0.995 | 1.25 | -0.0040766 | 1640 | 0.195 | 1640 | 0.195 | 0.995 | 1.25 | -0.00408
CFLBldgPGEMBTExCZ01 | Com-Iltg-dWatt-CFL_OSbldg | PGE | MBT | Ex | CZ01 | 3.0875 | 0.00077924 | 0 | 3.3275 | 0.00091909 | -0.003547 | 3.04 | 0.000765 | 0 | 3.28 | 0.000902 | -0.00349 |  | CFL | Bldg | 3090 | 0.779 | 3040 | 0.765 | 1.08 | 1.18 | -0.001148 | 3090 | 0.779 | 3040 | 0.765 | 1.08 | 1.18 | -0.00115
CFLBldgPGEMBTExCZ02 | Com-Iltg-dWatt-CFL_OSbldg | PGE | MBT | Ex | CZ02 | 3.088 | 0.0007794 | 0 | 3.4276 | 0.00091931 | -0.0017888 | 3.04 | 0.000765 | 0 | 3.37 | 0.000903 | -0.00176 |  | CFL | Bldg | 3090 | 0.779 | 3040 | 0.765 | 1.11 | 1.18 | -0.00057895 | 3090 | 0.779 | 3040 | 0.765 | 1.11 | 1.18 | -0.000579
CFLBldgPGEMBTExCZ03 | Com-Iltg-dWatt-CFL_OSbldg | PGE | MBT | Ex | CZ03 | 3.0884 | 0.00077953 | 0 | 3.4484 | 0.00092244 | -0.0015591 | 3.04 | 0.000765 | 0 | 3.4 | 0.000905 | -0.00153 |  | CFL | Bldg | 3090 | 0.78 | 3040 | 0.765 | 1.12 | 1.18 | -0.00050329 | 3090 | 0.78 | 3040 | 0.765 | 1.12 | 1.18 | -0.000503
CFLBldgPGEMBTExCZ04 | Com-Iltg-dWatt-CFL_OSbldg | PGE | MBT | Ex | CZ04 | 3.0878 | 0.00077934 | 0 | 3.4474 | 0.00093325 | -0.0011991 | 3.04 | 0.000765 | 0 | 3.39 | 0.000917 | -0.00118 |  | CFL | Bldg | 3090 | 0.779 | 3040 | 0.765 | 1.12 | 1.2 | -0.00038816 | 3090 | 0.779 | 3040 | 0.765 | 1.12 | 1.2 | -0.000388
CFLBldgPGEMBTExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | PGE | MBT | Ex | CZ05 | 3.0878 | 0.00077934 | 0 | 3.4274 | 0.00092325 | -0.00097829 | 3.04 | 0.000765 | 0 | 3.37 | 0.000907 | -0.000963 |  | CFL | Bldg | 3090 | 0.779 | 3040 | 0.765 | 1.11 | 1.19 | -0.00031678 | 3090 | 0.779 | 3040 | 0.765 | 1.11 | 1.19 | -0.000317
CFLBldgPGEMBTExCZ11 | Com-Iltg-dWatt-CFL_OSbldg | PGE | MBT | Ex | CZ11 | 3.0944 | 0.00078133 | 0 | 3.4553 | 0.00094059 | -0.0019227 | 3.04 | 0.000765 | 0 | 3.3915 | 0.000921 | -0.00189 |  | CFL | Bldg | 3090 | 0.781 | 3040 | 0.765 | 1.12 | 1.2 | -0.00062171 | 3090 | 0.781 | 3040 | 0.765 | 1.12 | 1.2 | -0.000622
CFLBldgPGEMBTExCZ12 | Com-Iltg-dWatt-CFL_OSbldg | PGE | MBT | Ex | CZ12 | 3.0936 | 0.00078109 | 0 | 3.4349 | 0.00091536 | -0.0018834 | 3.04 | 0.000765 | 0 | 3.38 | 0.000897 | -0.00185 |  | CFL | Bldg | 3090 | 0.781 | 3040 | 0.765 | 1.11 | 1.17 | -0.00060855 | 3090 | 0.781 | 3040 | 0.765 | 1.11 | 1.17 | -0.000609
CFLBldgPGEMBTExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | PGE | MBT | Ex | CZ13 | 3.0951 | 0.00078153 | 0 | 3.4661 | 0.00091767 | -0.0015837 | 3.04 | 0.000765 | 0 | 3.4 | 0.000898 | -0.00156 |  | CFL | Bldg | 3100 | 0.782 | 3040 | 0.765 | 1.12 | 1.17 | -0.00051316 | 3100 | 0.782 | 3040 | 0.765 | 1.12 | 1.17 | -0.000513
CFLBldgPGEMBTExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | PGE | MBT | Ex | CZ16 | 3.095 | 0.0007815 | 0 | 3.3144 | 0.00090086 | -0.0082324 | 3.04 | 0.000765 | 0 | 3.25 | 0.000882 | -0.0080816 |  | CFL | Bldg | 3100 | 0.782 | 3040 | 0.765 | 1.07 | 1.15 | -0.0026584 | 3100 | 0.782 | 3040 | 0.765 | 1.07 | 1.15 | -0.00266
CFLBldgPGEMBTExIOU | Com-Iltg-dWatt-CFL_OSbldg | PGE | MBT | Ex | IOU | 3.0905 | 0.00078013 | 0 | 3.4439 | 0.00092292 | -0.0016658 | 3.04 | 0.000765 | 0 | 3.3887 | 0.00090523 | -0.001637 |  | CFL | Bldg | 3090 | 0.78 | 3040 | 0.765 | 1.11 | 1.18 | -0.00053848 | 3090 | 0.78 | 3040 | 0.765 | 1.11 | 1.18 | -0.000538
CFLBldgPGEMBTNewCZ01 | Com-Iltg-dWatt-CFL_OSbldg | PGE | MBT | New | CZ01 | 3.04 | 0.000765 | 0 | 3.11 | 0.000866 | -0.00337 | 3.04 | 0.000765 | 0 | 3.11 | 0.000866 | -0.00337 |  | CFL | Bldg | 3040 | 0.765 | 3040 | 0.765 | 1.02 | 1.13 | -0.0011086 | 3040 | 0.765 | 3040 | 0.765 | 1.02 | 1.13 | -0.00111
CFLBldgPGEMBTNewCZ02 | Com-Iltg-dWatt-CFL_OSbldg | PGE | MBT | New | CZ02 | 3.04 | 0.000765 | 0 | 3.24 | 0.00094 | -0.0016 | 3.04 | 0.000765 | 0 | 3.24 | 0.00094 | -0.0016 |  | CFL | Bldg | 3040 | 0.765 | 3040 | 0.765 | 1.07 | 1.23 | -0.00052632 | 3040 | 0.765 | 3040 | 0.765 | 1.07 | 1.23 | -0.000526
CFLBldgPGEMBTNewCZ03 | Com-Iltg-dWatt-CFL_OSbldg | PGE | MBT | New | CZ03 | 3.04 | 0.000765 | 0 | 3.21 | 0.000911 | -0.00151 | 3.04 | 0.000765 | 0 | 3.21 | 0.000911 | -0.00151 |  | CFL | Bldg | 3040 | 0.765 | 3040 | 0.765 | 1.06 | 1.19 | -0.00049671 | 3040 | 0.765 | 3040 | 0.765 | 1.06 | 1.19 | -0.000497
CFLBldgPGEMBTNewCZ04 | Com-Iltg-dWatt-CFL_OSbldg | PGE | MBT | New | CZ04 | 3.04 | 0.000765 | 0 | 3.27 | 0.000931 | -0.00121 | 3.04 | 0.000765 | 0 | 3.27 | 0.000931 | -0.00121 |  | CFL | Bldg | 3040 | 0.765 | 3040 | 0.765 | 1.08 | 1.22 | -0.00039803 | 3040 | 0.765 | 3040 | 0.765 | 1.08 | 1.22 | -0.000398
CFLBldgPGEMBTNewCZ05 | Com-Iltg-dWatt-CFL_OSbldg | PGE | MBT | New | CZ05 | 3.04 | 0.000765 | 0 | 3.23 | 0.000907 | -0.000805 | 3.04 | 0.000765 | 0 | 3.23 | 0.000907 | -0.000805 |  | CFL | Bldg | 3040 | 0.765 | 3040 | 0.765 | 1.06 | 1.19 | -0.0002648 | 3040 | 0.765 | 3040 | 0.765 | 1.06 | 1.19 | -0.000265
CFLBldgPGEMBTNewCZ11 | Com-Iltg-dWatt-CFL_OSbldg | PGE | MBT | New | CZ11 | 3.04 | 0.000765 | 0 | 3.3 | 0.000949 | -0.00167 | 3.04 | 0.000765 | 0 | 3.3 | 0.000949 | -0.00167 |  | CFL | Bldg | 3040 | 0.765 | 3040 | 0.765 | 1.09 | 1.24 | -0.00054934 | 3040 | 0.765 | 3040 | 0.765 | 1.09 | 1.24 | -0.000549
CFLBldgPGEMBTNewCZ12 | Com-Iltg-dWatt-CFL_OSbldg | PGE | MBT | New | CZ12 | 3.04 | 0.000765 | 0 | 3.28 | 0.000941 | -0.00145 | 3.04 | 0.000765 | 0 | 3.28 | 0.000941 | -0.00145 |  | CFL | Bldg | 3040 | 0.765 | 3040 | 0.765 | 1.08 | 1.23 | -0.00047697 | 3040 | 0.765 | 3040 | 0.765 | 1.08 | 1.23 | -0.000477
CFLBldgPGEMBTNewCZ13 | Com-Iltg-dWatt-CFL_OSbldg | PGE | MBT | New | CZ13 | 3.04 | 0.000765 | 0 | 3.32 | 0.000938 | -0.00135 | 3.04 | 0.000765 | 0 | 3.32 | 0.000938 | -0.00135 |  | CFL | Bldg | 3040 | 0.765 | 3040 | 0.765 | 1.09 | 1.23 | -0.00044408 | 3040 | 0.765 | 3040 | 0.765 | 1.09 | 1.23 | -0.000444
CFLBldgPGEMBTNewCZ16 | Com-Iltg-dWatt-CFL_OSbldg | PGE | MBT | New | CZ16 | 3.04 | 0.000765 | 0 | 3.18 | 0.000907 | -0.00626 | 3.04 | 0.000765 | 0 | 3.18 | 0.000907 | -0.00626 |  | CFL | Bldg | 3040 | 0.765 | 3040 | 0.765 | 1.05 | 1.19 | -0.0020592 | 3040 | 0.765 | 3040 | 0.765 | 1.05 | 1.19 | -0.00206
CFLBldgPGEMBTNewIOU | Com-Iltg-dWatt-CFL_OSbldg | PGE | MBT | New | IOU | 3.04 | 0.000765 | 0 | 3.2638 | 0.00093034 | -0.0014974 | 3.04 | 0.000765 | 0 | 3.2638 | 0.00093034 | -0.0014974 |  | CFL | Bldg | 3040 | 0.765 | 3040 | 0.765 | 1.07 | 1.22 | -0.00049255 | 3040 | 0.765 | 3040 | 0.765 | 1.07 | 1.22 | -0.000493
CFLBldgPGEMLIExCZ01 | Com-Iltg-dWatt-CFL_OSbldg | PGE | MLI | Ex | CZ01 | 2.58 | 0.00077737 | 0 | 2.5195 | 0.00088437 | -0.029695 | 2.58 | 0.00077595 | 0 | 2.5147 | 0.00088295 | -0.029647 |  | CFL | Bldg | 2580 | 0.777 | 2580 | 0.776 | 0.975 | 1.14 | -0.011491 | 2580 | 0.777 | 2580 | 0.776 | 0.975 | 1.14 | -0.0115
CFLBldgPGEMLIExCZ02 | Com-Iltg-dWatt-CFL_OSbldg | PGE | MLI | Ex | CZ02 | 2.58 | 0.00077744 | 0 | 2.69 | 0.00090144 | -0.0147 | 2.58 | 0.00077596 | 0 | 2.69 | 0.000899 | -0.0147 |  | CFL | Bldg | 2580 | 0.777 | 2580 | 0.776 | 1.04 | 1.16 | -0.0056977 | 2580 | 0.777 | 2580 | 0.776 | 1.04 | 1.16 | -0.0057
CFLBldgPGEMLIExCZ03 | Com-Iltg-dWatt-CFL_OSbldg | PGE | MLI | Ex | CZ03 | 2.58 | 0.000777 | 0 | 2.6897 | 0.000901 | -0.0136 | 2.58 | 0.00077597 | 0 | 2.6806 | 0.00089997 | -0.0136 |  | CFL | Bldg | 2580 | 0.777 | 2580 | 0.776 | 1.04 | 1.16 | -0.0052713 | 2580 | 0.777 | 2580 | 0.776 | 1.04 | 1.16 | -0.00527
CFLBldgPGEMLIExCZ04 | Com-Iltg-dWatt-CFL_OSbldg | PGE | MLI | Ex | CZ04 | 2.58 | 0.00077697 | 0 | 2.7196 | 0.00089707 | -0.011 | 2.58 | 0.00077596 | 0 | 2.7106 | 0.000896 | -0.011 |  | CFL | Bldg | 2580 | 0.777 | 2580 | 0.776 | 1.05 | 1.15 | -0.0042636 | 2580 | 0.777 | 2580 | 0.776 | 1.05 | 1.15 | -0.00426
CFLBldgPGEMLIExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | PGE | MLI | Ex | CZ05 | 2.58 | 0.00077697 | 0 | 2.68 | 0.00089997 | -0.0126 | 2.58 | 0.00077596 | 0 | 2.68 | 0.00089806 | -0.0126 |  | CFL | Bldg | 2580 | 0.777 | 2580 | 0.776 | 1.04 | 1.16 | -0.0048837 | 2580 | 0.777 | 2580 | 0.776 | 1.04 | 1.16 | -0.00488
CFLBldgPGEMLIExCZ11 | Com-Iltg-dWatt-CFL_OSbldg | PGE | MLI | Ex | CZ11 | 2.58 | 0.00077687 | 0 | 2.7 | 0.00089987 | -0.0154 | 2.58 | 0.00077593 | 0 | 2.7 | 0.000898 | -0.0154 |  | CFL | Bldg | 2580 | 0.777 | 2580 | 0.776 | 1.05 | 1.16 | -0.005969 | 2580 | 0.777 | 2580 | 0.776 | 1.05 | 1.16 | -0.00597
CFLBldgPGEMLIExCZ12 | Com-Iltg-dWatt-CFL_OSbldg | PGE | MLI | Ex | CZ12 | 2.58 | 0.00077689 | 0 | 2.6995 | 0.00090489 | -0.014895 | 2.58 | 0.00077595 | 0 | 2.69 | 0.00090395 | -0.0148 |  | CFL | Bldg | 2580 | 0.777 | 2580 | 0.776 | 1.04 | 1.16 | -0.0057364 | 2580 | 0.777 | 2580 | 0.776 | 1.04 | 1.16 | -0.00574
CFLBldgPGEMLIExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | PGE | MLI | Ex | CZ13 | 2.58 | 0.00077689 | 0 | 2.7296 | 0.00088994 | -0.0134 | 2.58 | 0.00077596 | 0 | 2.7296 | 0.000889 | -0.0134 |  | CFL | Bldg | 2580 | 0.777 | 2580 | 0.776 | 1.06 | 1.15 | -0.0051938 | 2580 | 0.777 | 2580 | 0.776 | 1.06 | 1.15 | -0.00519
CFLBldgPGEMLIExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | PGE | MLI | Ex | CZ16 | 2.58 | 0.0007769 | 0 | 2.54 | 0.00088294 | -0.030996 | 2.58 | 0.00077596 | 0 | 2.54 | 0.000882 | -0.030902 |  | CFL | Bldg | 2580 | 0.777 | 2580 | 0.776 | 0.984 | 1.14 | -0.011977 | 2580 | 0.777 | 2580 | 0.776 | 0.984 | 1.14 | -0.012
CFLBldgPGEMLIExIOU | Com-Iltg-dWatt-CFL_OSbldg | PGE | MLI | Ex | IOU | 2.58 | 0.00077698 | 0 | 2.6994 | 0.00089932 | -0.013792 | 2.58 | 0.00077596 | 0 | 2.6928 | 0.00089815 | -0.013772 |  | CFL | Bldg | 2580 | 0.777 | 2580 | 0.776 | 1.04 | 1.16 | -0.005338 | 2580 | 0.777 | 2580 | 0.776 | 1.04 | 1.16 | -0.00534
CFLBldgPGEMLINewCZ01 | Com-Iltg-dWatt-CFL_OSbldg | PGE | MLI | New | CZ01 | 2.58 | 0.000775 | 0 | 2.45 | 0.000842 | -0.0395 | 2.58 | 0.000775 | 0 | 2.45 | 0.000842 | -0.0395 |  | CFL | Bldg | 2580 | 0.775 | 2580 | 0.775 | 0.95 | 1.09 | -0.01531 | 2580 | 0.775 | 2580 | 0.775 | 0.95 | 1.09 | -0.0153
CFLBldgPGEMLINewCZ02 | Com-Iltg-dWatt-CFL_OSbldg | PGE | MLI | New | CZ02 | 2.58 | 0.000775 | 0 | 2.6 | 0.000894 | -0.0218 | 2.58 | 0.000775 | 0 | 2.6 | 0.000894 | -0.0218 |  | CFL | Bldg | 2580 | 0.775 | 2580 | 0.775 | 1.01 | 1.15 | -0.0084496 | 2580 | 0.775 | 2580 | 0.775 | 1.01 | 1.15 | -0.00845
CFLBldgPGEMLINewCZ03 | Com-Iltg-dWatt-CFL_OSbldg | PGE | MLI | New | CZ03 | 2.58 | 0.000775 | 0 | 2.56 | 0.000903 | -0.0213 | 2.58 | 0.000775 | 0 | 2.56 | 0.000903 | -0.0213 |  | CFL | Bldg | 2580 | 0.775 | 2580 | 0.775 | 0.992 | 1.17 | -0.0082558 | 2580 | 0.775 | 2580 | 0.775 | 0.992 | 1.17 | -0.00826
CFLBldgPGEMLINewCZ04 | Com-Iltg-dWatt-CFL_OSbldg | PGE | MLI | New | CZ04 | 2.58 | 0.000775 | 0 | 2.63 | 0.000892 | -0.0172 | 2.58 | 0.000775 | 0 | 2.63 | 0.000892 | -0.0172 |  | CFL | Bldg | 2580 | 0.775 | 2580 | 0.775 | 1.02 | 1.15 | -0.0066667 | 2580 | 0.775 | 2580 | 0.775 | 1.02 | 1.15 | -0.00667
CFLBldgPGEMLINewCZ05 | Com-Iltg-dWatt-CFL_OSbldg | PGE | MLI | New | CZ05 | 2.58 | 0.000775 | 0 | 2.55 | 0.000889 | -0.0208 | 2.58 | 0.000775 | 0 | 2.55 | 0.000889 | -0.0208 |  | CFL | Bldg | 2580 | 0.775 | 2580 | 0.775 | 0.988 | 1.15 | -0.008062 | 2580 | 0.775 | 2580 | 0.775 | 0.988 | 1.15 | -0.00806
CFLBldgPGEMLINewCZ11 | Com-Iltg-dWatt-CFL_OSbldg | PGE | MLI | New | CZ11 | 2.58 | 0.000775 | 0 | 2.7 | 0.000926 | -0.0183 | 2.58 | 0.000775 | 0 | 2.7 | 0.000926 | -0.0183 |  | CFL | Bldg | 2580 | 0.775 | 2580 | 0.775 | 1.05 | 1.19 | -0.007093 | 2580 | 0.775 | 2580 | 0.775 | 1.05 | 1.19 | -0.00709
CFLBldgPGEMLINewCZ12 | Com-Iltg-dWatt-CFL_OSbldg | PGE | MLI | New | CZ12 | 2.58 | 0.000775 | 0 | 2.66 | 0.000914 | -0.0199 | 2.58 | 0.000775 | 0 | 2.66 | 0.000914 | -0.0199 |  | CFL | Bldg | 2580 | 0.775 | 2580 | 0.775 | 1.03 | 1.18 | -0.0077132 | 2580 | 0.775 | 2580 | 0.775 | 1.03 | 1.18 | -0.00771
CFLBldgPGEMLINewCZ13 | Com-Iltg-dWatt-CFL_OSbldg | PGE | MLI | New | CZ13 | 2.58 | 0.000775 | 0 | 2.73 | 0.000932 | -0.0172 | 2.58 | 0.000775 | 0 | 2.73 | 0.000932 | -0.0172 |  | CFL | Bldg | 2580 | 0.775 | 2580 | 0.775 | 1.06 | 1.2 | -0.0066667 | 2580 | 0.775 | 2580 | 0.775 | 1.06 | 1.2 | -0.00667
CFLBldgPGEMLINewCZ16 | Com-Iltg-dWatt-CFL_OSbldg | PGE | MLI | New | CZ16 | 2.58 | 0.000775 | 0 | 2.53 | 0.000881 | -0.0335 | 2.58 | 0.000775 | 0 | 2.53 | 0.000881 | -0.0335 |  | CFL | Bldg | 2580 | 0.775 | 2580 | 0.775 | 0.981 | 1.14 | -0.012984 | 2580 | 0.775 | 2580 | 0.775 | 0.981 | 1.14 | -0.013
CFLBldgPGEMLINewIOU | Com-Iltg-dWatt-CFL_OSbldg | PGE | MLI | New | IOU | 2.58 | 0.000775 | 0 | 2.6366 | 0.00090867 | -0.019641 | 2.58 | 0.000775 | 0 | 2.6366 | 0.00090867 | -0.019641 |  | CFL | Bldg | 2580 | 0.775 | 2580 | 0.775 | 1.02 | 1.17 | -0.0076128 | 2580 | 0.775 | 2580 | 0.775 | 1.02 | 1.17 | -0.00761
CFLBldgPGEMtlExCZ01 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Mtl | Ex | CZ01 | 1.3675 | 0.00015069 | 0 | 1.3475 | 0.00017963 | -0.011781 | 1.33 | 0.000146 | 0 | 1.31 | 0.000174 | -0.0115 |  | CFL | Bldg | 1370 | 0.151 | 1330 | 0.146 | 0.985 | 1.19 | -0.0086466 | 1370 | 0.151 | 1330 | 0.146 | 0.985 | 1.19 | -0.00865
CFLBldgPGEMtlExCZ02 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Mtl | Ex | CZ02 | 1.3677 | 0.00015071 | 0 | 1.4276 | 0.00018569 | -0.0078072 | 1.33 | 0.000146 | 0 | 1.39 | 0.00018004 | -0.0076096 |  | CFL | Bldg | 1370 | 0.151 | 1330 | 0.146 | 1.05 | 1.23 | -0.0057215 | 1370 | 0.151 | 1330 | 0.146 | 1.05 | 1.23 | -0.00572
CFLBldgPGEMtlExCZ03 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Mtl | Ex | CZ03 | 1.3742 | 0.00015153 | 0 | 1.4442 | 0.00018264 | -0.0076052 | 1.33 | 0.000146 | 0 | 1.4 | 0.000176 | -0.0073786 |  | CFL | Bldg | 1370 | 0.152 | 1330 | 0.146 | 1.05 | 1.21 | -0.0055479 | 1370 | 0.152 | 1330 | 0.146 | 1.05 | 1.21 | -0.00555
CFLBldgPGEMtlExCZ04 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Mtl | Ex | CZ04 | 1.3736 | 0.00015146 | 0 | 1.4636 | 0.00018555 | -0.0062886 | 1.33 | 0.000146 | 0 | 1.42 | 0.000179 | -0.0060985 |  | CFL | Bldg | 1370 | 0.151 | 1330 | 0.146 | 1.07 | 1.23 | -0.0045853 | 1370 | 0.151 | 1330 | 0.146 | 1.07 | 1.23 | -0.00459
CFLBldgPGEMtlExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Mtl | Ex | CZ05 | 1.3736 | 0.00015146 | 0 | 1.4237 | 0.00018155 | -0.0080038 | 1.33 | 0.000146 | 0 | 1.38 | 0.000175 | -0.0077591 |  | CFL | Bldg | 1370 | 0.151 | 1330 | 0.146 | 1.04 | 1.2 | -0.0058339 | 1370 | 0.151 | 1330 | 0.146 | 1.04 | 1.2 | -0.00583
CFLBldgPGEMtlExCZ11 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Mtl | Ex | CZ11 | 1.3673 | 0.00015066 | 0 | 1.4673 | 0.00018759 | -0.0065684 | 1.33 | 0.000146 | 0 | 1.43 | 0.000182 | -0.00641 |  | CFL | Bldg | 1370 | 0.151 | 1330 | 0.146 | 1.08 | 1.25 | -0.0048195 | 1370 | 0.151 | 1330 | 0.146 | 1.08 | 1.25 | -0.00482
CFLBldgPGEMtlExCZ12 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Mtl | Ex | CZ12 | 1.3669 | 0.00015062 | 0 | 1.4569 | 0.00018754 | -0.0069362 | 1.33 | 0.000146 | 0 | 1.42 | 0.000182 | -0.00677 |  | CFL | Bldg | 1370 | 0.151 | 1330 | 0.146 | 1.07 | 1.25 | -0.0050902 | 1370 | 0.151 | 1330 | 0.146 | 1.07 | 1.25 | -0.00509
CFLBldgPGEMtlExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Mtl | Ex | CZ13 | 1.3674 | 0.00015067 | 0 | 1.4874 | 0.00018756 | -0.0061488 | 1.33 | 0.000146 | 0 | 1.45 | 0.00018102 | -0.00599 |  | CFL | Bldg | 1370 | 0.151 | 1330 | 0.146 | 1.09 | 1.24 | -0.0045038 | 1370 | 0.151 | 1330 | 0.146 | 1.09 | 1.24 | -0.0045
CFLBldgPGEMtlExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Mtl | Ex | CZ16 | 1.3674 | 0.00015068 | 0 | 1.3381 | 0.00018061 | -0.010481 | 1.33 | 0.000146 | 0 | 1.31 | 0.000175 | -0.0102 |  | CFL | Bldg | 1370 | 0.151 | 1330 | 0.146 | 0.985 | 1.2 | -0.0076692 | 1370 | 0.151 | 1330 | 0.146 | 0.985 | 1.2 | -0.00767
CFLBldgPGEMtlExIOU | Com-Iltg-dWatt-CFL_OSbldg | PGE | Mtl | Ex | IOU | 1.3716 | 0.00015121 | 0 | 1.4477 | 0.00018437 | -0.0073103 | 1.33 | 0.000146 | 0 | 1.4062 | 0.00017805 | -0.0071045 |  | CFL | Bldg | 1370 | 0.151 | 1330 | 0.146 | 1.06 | 1.22 | -0.0053417 | 1370 | 0.151 | 1330 | 0.146 | 1.06 | 1.22 | -0.00534
CFLBldgPGEMtlNewCZ01 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Mtl | New | CZ01 | 1.33 | 0.000146 | 0 | 1.26 | 0.000174 | -0.0148 | 1.33 | 0.000146 | 0 | 1.26 | 0.000174 | -0.0148 |  | CFL | Bldg | 1330 | 0.146 | 1330 | 0.146 | 0.947 | 1.19 | -0.011128 | 1330 | 0.146 | 1330 | 0.146 | 0.947 | 1.19 | -0.0111
CFLBldgPGEMtlNewCZ02 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Mtl | New | CZ02 | 1.33 | 0.000146 | 0 | 1.36 | 0.000185 | -0.00998 | 1.33 | 0.000146 | 0 | 1.36 | 0.000185 | -0.00998 |  | CFL | Bldg | 1330 | 0.146 | 1330 | 0.146 | 1.02 | 1.27 | -0.0075038 | 1330 | 0.146 | 1330 | 0.146 | 1.02 | 1.27 | -0.0075
CFLBldgPGEMtlNewCZ03 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Mtl | New | CZ03 | 1.33 | 0.000146 | 0 | 1.37 | 0.000179 | -0.00938 | 1.33 | 0.000146 | 0 | 1.37 | 0.000179 | -0.00938 |  | CFL | Bldg | 1330 | 0.146 | 1330 | 0.146 | 1.03 | 1.23 | -0.0070526 | 1330 | 0.146 | 1330 | 0.146 | 1.03 | 1.23 | -0.00705
CFLBldgPGEMtlNewCZ04 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Mtl | New | CZ04 | 1.33 | 0.000146 | 0 | 1.41 | 0.000183 | -0.0079 | 1.33 | 0.000146 | 0 | 1.41 | 0.000183 | -0.0079 |  | CFL | Bldg | 1330 | 0.146 | 1330 | 0.146 | 1.06 | 1.25 | -0.0059398 | 1330 | 0.146 | 1330 | 0.146 | 1.06 | 1.25 | -0.00594
CFLBldgPGEMtlNewCZ05 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Mtl | New | CZ05 | 1.33 | 0.000146 | 0 | 1.35 | 0.000177 | -0.0105 | 1.33 | 0.000146 | 0 | 1.35 | 0.000177 | -0.0105 |  | CFL | Bldg | 1330 | 0.146 | 1330 | 0.146 | 1.02 | 1.21 | -0.0078947 | 1330 | 0.146 | 1330 | 0.146 | 1.02 | 1.21 | -0.00789
CFLBldgPGEMtlNewCZ11 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Mtl | New | CZ11 | 1.33 | 0.000146 | 0 | 1.42 | 0.000187 | -0.00799 | 1.33 | 0.000146 | 0 | 1.42 | 0.000187 | -0.00799 |  | CFL | Bldg | 1330 | 0.146 | 1330 | 0.146 | 1.07 | 1.28 | -0.0060075 | 1330 | 0.146 | 1330 | 0.146 | 1.07 | 1.28 | -0.00601
CFLBldgPGEMtlNewCZ12 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Mtl | New | CZ12 | 1.33 | 0.000146 | 0 | 1.41 | 0.000186 | -0.00835 | 1.33 | 0.000146 | 0 | 1.41 | 0.000186 | -0.00835 |  | CFL | Bldg | 1330 | 0.146 | 1330 | 0.146 | 1.06 | 1.27 | -0.0062782 | 1330 | 0.146 | 1330 | 0.146 | 1.06 | 1.27 | -0.00628
CFLBldgPGEMtlNewCZ13 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Mtl | New | CZ13 | 1.33 | 0.000146 | 0 | 1.43 | 0.000185 | -0.00751 | 1.33 | 0.000146 | 0 | 1.43 | 0.000185 | -0.00751 |  | CFL | Bldg | 1330 | 0.146 | 1330 | 0.146 | 1.08 | 1.27 | -0.0056466 | 1330 | 0.146 | 1330 | 0.146 | 1.08 | 1.27 | -0.00565
CFLBldgPGEMtlNewCZ16 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Mtl | New | CZ16 | 1.33 | 0.000146 | 0 | 1.28 | 0.000178 | -0.0118 | 1.33 | 0.000146 | 0 | 1.28 | 0.000178 | -0.0118 |  | CFL | Bldg | 1330 | 0.146 | 1330 | 0.146 | 0.962 | 1.22 | -0.0088722 | 1330 | 0.146 | 1330 | 0.146 | 0.962 | 1.22 | -0.00887
CFLBldgPGEMtlNewIOU | Com-Iltg-dWatt-CFL_OSbldg | PGE | Mtl | New | IOU | 1.33 | 0.000146 | 0 | 1.3887 | 0.00018251 | -0.0088986 | 1.33 | 0.000146 | 0 | 1.3887 | 0.00018251 | -0.0088986 |  | CFL | Bldg | 1330 | 0.146 | 1330 | 0.146 | 1.04 | 1.25 | -0.0066907 | 1330 | 0.146 | 1330 | 0.146 | 1.04 | 1.25 | -0.00669
CFLBldgPGENrsExCZ01 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Nrs | Ex | CZ01 | 3.5679 | 0.00056457 | 0 | 3.5078 | 0.00064453 | -0.072153 | 3.5201 | 0.00055501 | 0 | 3.46 | 0.00063402 | -0.071102 |  | CFL | Bldg | 3570 | 0.565 | 3520 | 0.555 | 0.983 | 1.14 | -0.020198 | 3570 | 0.565 | 3520 | 0.555 | 0.983 | 1.14 | -0.0202
CFLBldgPGENrsExCZ02 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Nrs | Ex | CZ02 | 3.5676 | 0.0005645 | 0 | 3.6971 | 0.00070935 | -0.052161 | 3.5202 | 0.00055502 | 0 | 3.6497 | 0.00069702 | -0.051402 |  | CFL | Bldg | 3570 | 0.565 | 3520 | 0.555 | 1.04 | 1.26 | -0.014602 | 3570 | 0.565 | 3520 | 0.555 | 1.04 | 1.26 | -0.0146
CFLBldgPGENrsExCZ03 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Nrs | Ex | CZ03 | 3.5794 | 0.00056683 | 0 | 3.6689 | 0.00069019 | -0.053025 | 3.5205 | 0.00055505 | 0 | 3.61 | 0.00067605 | -0.052105 |  | CFL | Bldg | 3580 | 0.567 | 3520 | 0.555 | 1.03 | 1.22 | -0.0148 | 3580 | 0.567 | 3520 | 0.555 | 1.03 | 1.22 | -0.0148
CFLBldgPGENrsExCZ04 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Nrs | Ex | CZ04 | 3.5807 | 0.00056709 | 0 | 3.7607 | 0.0007065 | -0.044797 | 3.5205 | 0.00055505 | 0 | 3.7005 | 0.00069136 | -0.044005 |  | CFL | Bldg | 3580 | 0.567 | 3520 | 0.555 | 1.05 | 1.25 | -0.0125 | 3580 | 0.567 | 3520 | 0.555 | 1.05 | 1.25 | -0.0125
CFLBldgPGENrsExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Nrs | Ex | CZ05 | 3.5807 | 0.00056709 | 0 | 3.6402 | 0.0006725 | -0.054443 | 3.5205 | 0.00055505 | 0 | 3.58 | 0.00065805 | -0.053505 |  | CFL | Bldg | 3580 | 0.567 | 3520 | 0.555 | 1.02 | 1.19 | -0.015198 | 3580 | 0.567 | 3520 | 0.555 | 1.02 | 1.19 | -0.0152
CFLBldgPGENrsExCZ11 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Nrs | Ex | CZ11 | 3.5675 | 0.00056444 | 0 | 3.7969 | 0.00071431 | -0.043169 | 3.5206 | 0.00055506 | 0 | 3.75 | 0.00070306 | -0.042606 |  | CFL | Bldg | 3570 | 0.564 | 3520 | 0.555 | 1.07 | 1.27 | -0.012102 | 3570 | 0.564 | 3520 | 0.555 | 1.07 | 1.27 | -0.0121
CFLBldgPGENrsExCZ12 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Nrs | Ex | CZ12 | 3.5675 | 0.00056443 | 0 | 3.7669 | 0.00071125 | -0.045362 | 3.5206 | 0.00055506 | 0 | 3.72 | 0.00069906 | -0.044706 |  | CFL | Bldg | 3570 | 0.564 | 3520 | 0.555 | 1.06 | 1.26 | -0.012698 | 3570 | 0.564 | 3520 | 0.555 | 1.06 | 1.26 | -0.0127
CFLBldgPGENrsExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Nrs | Ex | CZ13 | 3.5696 | 0.00056485 | 0 | 3.8189 | 0.00071185 | -0.041394 | 3.5206 | 0.00055506 | 0 | 3.77 | 0.00070006 | -0.040896 |  | CFL | Bldg | 3570 | 0.565 | 3520 | 0.555 | 1.07 | 1.26 | -0.011616 | 3570 | 0.565 | 3520 | 0.555 | 1.07 | 1.26 | -0.0116
CFLBldgPGENrsExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Nrs | Ex | CZ16 | 3.5696 | 0.00056488 | 0 | 3.5896 | 0.00068379 | -0.062886 | 3.5205 | 0.00055505 | 0 | 3.5405 | 0.00067109 | -0.062005 |  | CFL | Bldg | 3570 | 0.565 | 3520 | 0.555 | 1.01 | 1.21 | -0.017612 | 3570 | 0.565 | 3520 | 0.555 | 1.01 | 1.21 | -0.0176
CFLBldgPGENrsExIOU | Com-Iltg-dWatt-CFL_OSbldg | PGE | Nrs | Ex | IOU | 3.5733 | 0.0005656 | 0 | 3.7357 | 0.00070304 | -0.047894 | 3.5205 | 0.00055505 | 0 | 3.6829 | 0.00069 | -0.047156 |  | CFL | Bldg | 3570 | 0.566 | 3520 | 0.555 | 1.05 | 1.24 | -0.013395 | 3570 | 0.566 | 3520 | 0.555 | 1.05 | 1.24 | -0.0134
CFLBldgPGENrsNewCZ01 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Nrs | New | CZ01 | 3.53 | 0.000556 | 0 | 3.35 | 0.000607 | -0.0776 | 3.53 | 0.000556 | 0 | 3.35 | 0.000607 | -0.0776 |  | CFL | Bldg | 3530 | 0.556 | 3530 | 0.556 | 0.949 | 1.09 | -0.021983 | 3530 | 0.556 | 3530 | 0.556 | 0.949 | 1.09 | -0.022
CFLBldgPGENrsNewCZ02 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Nrs | New | CZ02 | 3.53 | 0.000556 | 0 | 3.53 | 0.000695 | -0.0546 | 3.53 | 0.000556 | 0 | 3.53 | 0.000695 | -0.0546 |  | CFL | Bldg | 3530 | 0.556 | 3530 | 0.556 | 1 | 1.25 | -0.015467 | 3530 | 0.556 | 3530 | 0.556 | 1 | 1.25 | -0.0155
CFLBldgPGENrsNewCZ03 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Nrs | New | CZ03 | 3.53 | 0.000556 | 0 | 3.47 | 0.000683 | -0.0571 | 3.53 | 0.000556 | 0 | 3.47 | 0.000683 | -0.0571 |  | CFL | Bldg | 3530 | 0.556 | 3530 | 0.556 | 0.983 | 1.23 | -0.016176 | 3530 | 0.556 | 3530 | 0.556 | 0.983 | 1.23 | -0.0162
CFLBldgPGENrsNewCZ04 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Nrs | New | CZ04 | 3.53 | 0.000556 | 0 | 3.62 | 0.000695 | -0.0462 | 3.53 | 0.000556 | 0 | 3.62 | 0.000695 | -0.0462 |  | CFL | Bldg | 3530 | 0.556 | 3530 | 0.556 | 1.03 | 1.25 | -0.013088 | 3530 | 0.556 | 3530 | 0.556 | 1.03 | 1.25 | -0.0131
CFLBldgPGENrsNewCZ05 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Nrs | New | CZ05 | 3.53 | 0.000556 | 0 | 3.47 | 0.000659 | -0.0592 | 3.53 | 0.000556 | 0 | 3.47 | 0.000659 | -0.0592 |  | CFL | Bldg | 3530 | 0.556 | 3530 | 0.556 | 0.983 | 1.19 | -0.016771 | 3530 | 0.556 | 3530 | 0.556 | 0.983 | 1.19 | -0.0168
CFLBldgPGENrsNewCZ11 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Nrs | New | CZ11 | 3.53 | 0.000556 | 0 | 3.7 | 0.000704 | -0.0441 | 3.53 | 0.000556 | 0 | 3.7 | 0.000704 | -0.0441 |  | CFL | Bldg | 3530 | 0.556 | 3530 | 0.556 | 1.05 | 1.27 | -0.012493 | 3530 | 0.556 | 3530 | 0.556 | 1.05 | 1.27 | -0.0125
CFLBldgPGENrsNewCZ12 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Nrs | New | CZ12 | 3.53 | 0.000556 | 0 | 3.65 | 0.000706 | -0.0462 | 3.53 | 0.000556 | 0 | 3.65 | 0.000706 | -0.0462 |  | CFL | Bldg | 3530 | 0.556 | 3530 | 0.556 | 1.03 | 1.27 | -0.013088 | 3530 | 0.556 | 3530 | 0.556 | 1.03 | 1.27 | -0.0131
CFLBldgPGENrsNewCZ13 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Nrs | New | CZ13 | 3.53 | 0.000556 | 0 | 3.71 | 0.000705 | -0.042 | 3.53 | 0.000556 | 0 | 3.71 | 0.000705 | -0.042 |  | CFL | Bldg | 3530 | 0.556 | 3530 | 0.556 | 1.05 | 1.27 | -0.011898 | 3530 | 0.556 | 3530 | 0.556 | 1.05 | 1.27 | -0.0119
CFLBldgPGENrsNewCZ16 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Nrs | New | CZ16 | 3.53 | 0.000556 | 0 | 3.48 | 0.000674 | -0.0652 | 3.53 | 0.000556 | 0 | 3.48 | 0.000674 | -0.0652 |  | CFL | Bldg | 3530 | 0.556 | 3530 | 0.556 | 0.986 | 1.21 | -0.01847 | 3530 | 0.556 | 3530 | 0.556 | 0.986 | 1.21 | -0.0185
CFLBldgPGENrsNewIOU | Com-Iltg-dWatt-CFL_OSbldg | PGE | Nrs | New | IOU | 3.53 | 0.000556 | 0 | 3.6008 | 0.00069586 | -0.049207 | 3.53 | 0.000556 | 0 | 3.6008 | 0.00069586 | -0.049207 |  | CFL | Bldg | 3530 | 0.556 | 3530 | 0.556 | 1.02 | 1.25 | -0.01394 | 3530 | 0.556 | 3530 | 0.556 | 1.02 | 1.25 | -0.0139
CFLBldgPGEOfLExCZ01 | Com-Iltg-dWatt-CFL_OSbldg | PGE | OfL | Ex | CZ01 | 2.998 | 0.00062449 | 0 | 3.1978 | 0.00079236 | -0.027784 | 2.88 | 0.00059296 | 0 | 3.0796 | 0.00075199 | -0.026793 |  | CFL | Bldg | 3000 | 0.624 | 2880 | 0.593 | 1.07 | 1.27 | -0.0093031 | 3000 | 0.624 | 2880 | 0.593 | 1.07 | 1.27 | -0.0093
CFLBldgPGEOfLExCZ02 | Com-Iltg-dWatt-CFL_OSbldg | PGE | OfL | Ex | CZ02 | 2.9975 | 0.00062436 | 0 | 3.2873 | 0.00083411 | -0.020685 | 2.88 | 0.00059295 | 0 | 3.1691 | 0.00079189 | -0.0199 |  | CFL | Bldg | 3000 | 0.624 | 2880 | 0.593 | 1.1 | 1.34 | -0.0069097 | 3000 | 0.624 | 2880 | 0.593 | 1.1 | 1.34 | -0.00691
CFLBldgPGEOfLExCZ03 | Com-Iltg-dWatt-CFL_OSbldg | PGE | OfL | Ex | CZ03 | 3.0353 | 0.00063536 | 0 | 3.3227 | 0.00082661 | -0.019423 | 2.88 | 0.00059295 | 0 | 3.16 | 0.00077095 | -0.0184 |  | CFL | Bldg | 3040 | 0.635 | 2880 | 0.593 | 1.1 | 1.3 | -0.0063889 | 3040 | 0.635 | 2880 | 0.593 | 1.1 | 1.3 | -0.00639
CFLBldgPGEOfLExCZ04 | Com-Iltg-dWatt-CFL_OSbldg | PGE | OfL | Ex | CZ04 | 3.027 | 0.00063297 | 0 | 3.3526 | 0.00082748 | -0.017544 | 2.88 | 0.00059294 | 0 | 3.1963 | 0.00077525 | -0.0167 |  | CFL | Bldg | 3030 | 0.633 | 2880 | 0.593 | 1.11 | 1.31 | -0.0057986 | 3030 | 0.633 | 2880 | 0.593 | 1.11 | 1.31 | -0.0058
CFLBldgPGEOfLExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | PGE | OfL | Ex | CZ05 | 3.0269 | 0.00063295 | 0 | 3.3094 | 0.00080521 | -0.019175 | 2.88 | 0.00059294 | 0 | 3.15 | 0.00075394 | -0.0183 |  | CFL | Bldg | 3030 | 0.633 | 2880 | 0.593 | 1.09 | 1.27 | -0.0063542 | 3030 | 0.633 | 2880 | 0.593 | 1.09 | 1.27 | -0.00635
CFLBldgPGEOfLExCZ11 | Com-Iltg-dWatt-CFL_OSbldg | PGE | OfL | Ex | CZ11 | 2.9903 | 0.00062232 | 0 | 3.3586 | 0.00083035 | -0.019835 | 2.88 | 0.00059292 | 0 | 3.2392 | 0.00079084 | -0.019192 |  | CFL | Bldg | 2990 | 0.622 | 2880 | 0.593 | 1.12 | 1.33 | -0.0066639 | 2990 | 0.622 | 2880 | 0.593 | 1.12 | 1.33 | -0.00666
CFLBldgPGEOfLExCZ12 | Com-Iltg-dWatt-CFL_OSbldg | PGE | OfL | Ex | CZ12 | 2.9906 | 0.0006224 | 0 | 3.3098 | 0.00082254 | -0.019037 | 2.88 | 0.00059292 | 0 | 3.1992 | 0.00078384 | -0.018392 |  | CFL | Bldg | 2990 | 0.622 | 2880 | 0.593 | 1.11 | 1.32 | -0.0063861 | 2990 | 0.622 | 2880 | 0.593 | 1.11 | 1.32 | -0.00639
CFLBldgPGEOfLExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | PGE | OfL | Ex | CZ13 | 2.9994 | 0.00062497 | 0 | 3.3994 | 0.00083691 | -0.018001 | 2.88 | 0.00059292 | 0 | 3.2692 | 0.00079384 | -0.0173 |  | CFL | Bldg | 3000 | 0.625 | 2880 | 0.593 | 1.14 | 1.34 | -0.0060069 | 3000 | 0.625 | 2880 | 0.593 | 1.14 | 1.34 | -0.00601
CFLBldgPGEOfLExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | PGE | OfL | Ex | CZ16 | 3.0069 | 0.00062713 | 0 | 3.1282 | 0.00080669 | -0.035483 | 2.88 | 0.00059294 | 0 | 3 | 0.00076207 | -0.034 |  | CFL | Bldg | 3010 | 0.627 | 2880 | 0.593 | 1.04 | 1.29 | -0.011806 | 3010 | 0.627 | 2880 | 0.593 | 1.04 | 1.29 | -0.0118
CFLBldgPGEOfLExIOU | Com-Iltg-dWatt-CFL_OSbldg | PGE | OfL | Ex | IOU | 3.0218 | 0.00063145 | 0 | 3.3296 | 0.00082674 | -0.019018 | 2.88 | 0.00059294 | 0 | 3.1811 | 0.00077616 | -0.018127 |  | CFL | Bldg | 3020 | 0.631 | 2880 | 0.593 | 1.1 | 1.31 | -0.0062941 | 3020 | 0.631 | 2880 | 0.593 | 1.1 | 1.31 | -0.00629
CFLBldgPGEOfLNewCZ01 | Com-Iltg-dWatt-CFL_OSbldg | PGE | OfL | New | CZ01 | 2.88 | 0.000592 | 0 | 3.05 | 0.00072 | -0.0174 | 2.88 | 0.000592 | 0 | 3.05 | 0.00072 | -0.0174 |  | CFL | Bldg | 2880 | 0.592 | 2880 | 0.592 | 1.06 | 1.22 | -0.0060417 | 2880 | 0.592 | 2880 | 0.592 | 1.06 | 1.22 | -0.00604
CFLBldgPGEOfLNewCZ02 | Com-Iltg-dWatt-CFL_OSbldg | PGE | OfL | New | CZ02 | 2.88 | 0.000592 | 0 | 3.18 | 0.000733 | -0.0116 | 2.88 | 0.000592 | 0 | 3.18 | 0.000733 | -0.0116 |  | CFL | Bldg | 2880 | 0.592 | 2880 | 0.592 | 1.1 | 1.24 | -0.0040278 | 2880 | 0.592 | 2880 | 0.592 | 1.1 | 1.24 | -0.00403
CFLBldgPGEOfLNewCZ03 | Com-Iltg-dWatt-CFL_OSbldg | PGE | OfL | New | CZ03 | 2.88 | 0.000592 | 0 | 3.16 | 0.000731 | -0.0114 | 2.88 | 0.000592 | 0 | 3.16 | 0.000731 | -0.0114 |  | CFL | Bldg | 2880 | 0.592 | 2880 | 0.592 | 1.1 | 1.23 | -0.0039583 | 2880 | 0.592 | 2880 | 0.592 | 1.1 | 1.23 | -0.00396
CFLBldgPGEOfLNewCZ04 | Com-Iltg-dWatt-CFL_OSbldg | PGE | OfL | New | CZ04 | 2.88 | 0.000592 | 0 | 3.2 | 0.000735 | -0.0105 | 2.88 | 0.000592 | 0 | 3.2 | 0.000735 | -0.0105 |  | CFL | Bldg | 2880 | 0.592 | 2880 | 0.592 | 1.11 | 1.24 | -0.0036458 | 2880 | 0.592 | 2880 | 0.592 | 1.11 | 1.24 | -0.00365
CFLBldgPGEOfLNewCZ05 | Com-Iltg-dWatt-CFL_OSbldg | PGE | OfL | New | CZ05 | 2.88 | 0.000592 | 0 | 3.15 | 0.000716 | -0.0091 | 2.88 | 0.000592 | 0 | 3.15 | 0.000716 | -0.0091 |  | CFL | Bldg | 2880 | 0.592 | 2880 | 0.592 | 1.09 | 1.21 | -0.0031597 | 2880 | 0.592 | 2880 | 0.592 | 1.09 | 1.21 | -0.00316
CFLBldgPGEOfLNewCZ11 | Com-Iltg-dWatt-CFL_OSbldg | PGE | OfL | New | CZ11 | 2.88 | 0.000592 | 0 | 3.22 | 0.00074 | -0.00996 | 2.88 | 0.000592 | 0 | 3.22 | 0.00074 | -0.00996 |  | CFL | Bldg | 2880 | 0.592 | 2880 | 0.592 | 1.12 | 1.25 | -0.0034583 | 2880 | 0.592 | 2880 | 0.592 | 1.12 | 1.25 | -0.00346
CFLBldgPGEOfLNewCZ12 | Com-Iltg-dWatt-CFL_OSbldg | PGE | OfL | New | CZ12 | 2.88 | 0.000592 | 0 | 3.2 | 0.000737 | -0.0112 | 2.88 | 0.000592 | 0 | 3.2 | 0.000737 | -0.0112 |  | CFL | Bldg | 2880 | 0.592 | 2880 | 0.592 | 1.11 | 1.24 | -0.0038889 | 2880 | 0.592 | 2880 | 0.592 | 1.11 | 1.24 | -0.00389
CFLBldgPGEOfLNewCZ13 | Com-Iltg-dWatt-CFL_OSbldg | PGE | OfL | New | CZ13 | 2.88 | 0.000592 | 0 | 3.23 | 0.000739 | -0.00976 | 2.88 | 0.000592 | 0 | 3.23 | 0.000739 | -0.00976 |  | CFL | Bldg | 2880 | 0.592 | 2880 | 0.592 | 1.12 | 1.25 | -0.0033889 | 2880 | 0.592 | 2880 | 0.592 | 1.12 | 1.25 | -0.00339
CFLBldgPGEOfLNewCZ16 | Com-Iltg-dWatt-CFL_OSbldg | PGE | OfL | New | CZ16 | 2.88 | 0.000592 | 0 | 3.07 | 0.000725 | -0.0244 | 2.88 | 0.000592 | 0 | 3.07 | 0.000725 | -0.0244 |  | CFL | Bldg | 2880 | 0.592 | 2880 | 0.592 | 1.07 | 1.22 | -0.0084722 | 2880 | 0.592 | 2880 | 0.592 | 1.07 | 1.22 | -0.00847
CFLBldgPGEOfLNewIOU | Com-Iltg-dWatt-CFL_OSbldg | PGE | OfL | New | IOU | 2.88 | 0.000592 | 0 | 3.1848 | 0.00073385 | -0.011002 | 2.88 | 0.000592 | 0 | 3.1848 | 0.00073385 | -0.011002 |  | CFL | Bldg | 2880 | 0.592 | 2880 | 0.592 | 1.11 | 1.24 | -0.00382 | 2880 | 0.592 | 2880 | 0.592 | 1.11 | 1.24 | -0.00382
CFLBldgPGEOfSExCZ01 | Com-Iltg-dWatt-CFL_OSbldg | PGE | OfS | Ex | CZ01 | 2.9825 | 0.00067904 | 0 | 2.9925 | 0.00080523 | -0.018619 | 2.72 | 0.00059405 | 0 | 2.73 | 0.00070405 | -0.017 |  | CFL | Bldg | 2980 | 0.679 | 2720 | 0.594 | 1 | 1.19 | -0.00625 | 2980 | 0.679 | 2720 | 0.594 | 1 | 1.19 | -0.00625
CFLBldgPGEOfSExCZ02 | Com-Iltg-dWatt-CFL_OSbldg | PGE | OfS | Ex | CZ02 | 2.9795 | 0.00067807 | 0 | 3.1201 | 0.00082802 | -0.012095 | 2.72 | 0.00059406 | 0 | 2.85 | 0.00072506 | -0.011 |  | CFL | Bldg | 2980 | 0.678 | 2720 | 0.594 | 1.05 | 1.22 | -0.0040441 | 2980 | 0.678 | 2720 | 0.594 | 1.05 | 1.22 | -0.00404
CFLBldgPGEOfSExCZ03 | Com-Iltg-dWatt-CFL_OSbldg | PGE | OfS | Ex | CZ03 | 2.9653 | 0.00067329 | 0 | 3.0953 | 0.00082128 | -0.010249 | 2.72 | 0.00059404 | 0 | 2.85 | 0.00072409 | -0.0093902 |  | CFL | Bldg | 2970 | 0.673 | 2720 | 0.594 | 1.05 | 1.22 | -0.0034523 | 2970 | 0.673 | 2720 | 0.594 | 1.05 | 1.22 | -0.00345
CFLBldgPGEOfSExCZ04 | Com-Iltg-dWatt-CFL_OSbldg | PGE | OfS | Ex | CZ04 | 2.9649 | 0.00067315 | 0 | 3.1543 | 0.00082505 | -0.0082085 | 2.72 | 0.00059404 | 0 | 2.9 | 0.0007271 | -0.0075398 |  | CFL | Bldg | 2960 | 0.673 | 2720 | 0.594 | 1.07 | 1.22 | -0.002772 | 2960 | 0.673 | 2720 | 0.594 | 1.07 | 1.22 | -0.00277
CFLBldgPGEOfSExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | PGE | OfS | Ex | CZ05 | 2.9649 | 0.00067315 | 0 | 3.1143 | 0.00080516 | -0.0085273 | 2.72 | 0.00059404 | 0 | 2.86 | 0.00071004 | -0.0078398 |  | CFL | Bldg | 2960 | 0.673 | 2720 | 0.594 | 1.05 | 1.2 | -0.0028823 | 2960 | 0.673 | 2720 | 0.594 | 1.05 | 1.2 | -0.00288
CFLBldgPGEOfSExCZ11 | Com-Iltg-dWatt-CFL_OSbldg | PGE | OfS | Ex | CZ11 | 2.9652 | 0.00067329 | 0 | 3.1647 | 0.00082326 | -0.012637 | 2.72 | 0.00059406 | 0 | 2.9006 | 0.00072611 | -0.0116 |  | CFL | Bldg | 2970 | 0.673 | 2720 | 0.594 | 1.07 | 1.22 | -0.0042647 | 2970 | 0.673 | 2720 | 0.594 | 1.07 | 1.22 | -0.00426
CFLBldgPGEOfSExCZ12 | Com-Iltg-dWatt-CFL_OSbldg | PGE | OfS | Ex | CZ12 | 2.9644 | 0.00067301 | 0 | 3.1438 | 0.00082487 | -0.012234 | 2.72 | 0.00059406 | 0 | 2.8806 | 0.00072712 | -0.0112 |  | CFL | Bldg | 2960 | 0.673 | 2720 | 0.594 | 1.06 | 1.22 | -0.0041176 | 2960 | 0.673 | 2720 | 0.594 | 1.06 | 1.22 | -0.00412
CFLBldgPGEOfSExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | PGE | OfS | Ex | CZ13 | 2.9983 | 0.0006844 | 0 | 3.2098 | 0.00082976 | -0.011662 | 2.72 | 0.00059406 | 0 | 2.91 | 0.00072006 | -0.0106 |  | CFL | Bldg | 3000 | 0.684 | 2720 | 0.594 | 1.07 | 1.21 | -0.0038971 | 3000 | 0.684 | 2720 | 0.594 | 1.07 | 1.21 | -0.0039
CFLBldgPGEOfSExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | PGE | OfS | Ex | CZ16 | 3.0032 | 0.00068601 | 0 | 2.9737 | 0.00082362 | -0.023195 | 2.72 | 0.00059405 | 0 | 2.7 | 0.00071305 | -0.021005 |  | CFL | Bldg | 3000 | 0.686 | 2720 | 0.594 | 0.993 | 1.2 | -0.0077225 | 3000 | 0.686 | 2720 | 0.594 | 0.993 | 1.2 | -0.00772
CFLBldgPGEOfSExIOU | Com-Iltg-dWatt-CFL_OSbldg | PGE | OfS | Ex | IOU | 2.973 | 0.00067588 | 0 | 3.1437 | 0.00082449 | -0.011058 | 2.72 | 0.00059405 | 0 | 2.8786 | 0.00072407 | -0.010111 |  | CFL | Bldg | 2970 | 0.676 | 2720 | 0.594 | 1.06 | 1.22 | -0.0037171 | 2970 | 0.676 | 2720 | 0.594 | 1.06 | 1.22 | -0.00372
CFLBldgPGEOfSNewCZ01 | Com-Iltg-dWatt-CFL_OSbldg | PGE | OfS | New | CZ01 | 2.72 | 0.000595 | 0 | 2.67 | 0.0007 | -0.0157 | 2.72 | 0.000595 | 0 | 2.67 | 0.0007 | -0.0157 |  | CFL | Bldg | 2720 | 0.595 | 2720 | 0.595 | 0.982 | 1.18 | -0.0057721 | 2720 | 0.595 | 2720 | 0.595 | 0.982 | 1.18 | -0.00577
CFLBldgPGEOfSNewCZ02 | Com-Iltg-dWatt-CFL_OSbldg | PGE | OfS | New | CZ02 | 2.72 | 0.000595 | 0 | 2.84 | 0.00074 | -0.00847 | 2.72 | 0.000595 | 0 | 2.84 | 0.00074 | -0.00847 |  | CFL | Bldg | 2720 | 0.595 | 2720 | 0.595 | 1.04 | 1.24 | -0.003114 | 2720 | 0.595 | 2720 | 0.595 | 1.04 | 1.24 | -0.00311
CFLBldgPGEOfSNewCZ03 | Com-Iltg-dWatt-CFL_OSbldg | PGE | OfS | New | CZ03 | 2.72 | 0.000595 | 0 | 2.8 | 0.000722 | -0.00923 | 2.72 | 0.000595 | 0 | 2.8 | 0.000722 | -0.00923 |  | CFL | Bldg | 2720 | 0.595 | 2720 | 0.595 | 1.03 | 1.21 | -0.0033934 | 2720 | 0.595 | 2720 | 0.595 | 1.03 | 1.21 | -0.00339
CFLBldgPGEOfSNewCZ04 | Com-Iltg-dWatt-CFL_OSbldg | PGE | OfS | New | CZ04 | 2.72 | 0.000595 | 0 | 2.87 | 0.000736 | -0.00676 | 2.72 | 0.000595 | 0 | 2.87 | 0.000736 | -0.00676 |  | CFL | Bldg | 2720 | 0.595 | 2720 | 0.595 | 1.06 | 1.24 | -0.0024853 | 2720 | 0.595 | 2720 | 0.595 | 1.06 | 1.24 | -0.00249
CFLBldgPGEOfSNewCZ05 | Com-Iltg-dWatt-CFL_OSbldg | PGE | OfS | New | CZ05 | 2.72 | 0.000595 | 0 | 2.82 | 0.00071 | -0.00733 | 2.72 | 0.000595 | 0 | 2.82 | 0.00071 | -0.00733 |  | CFL | Bldg | 2720 | 0.595 | 2720 | 0.595 | 1.04 | 1.19 | -0.0026949 | 2720 | 0.595 | 2720 | 0.595 | 1.04 | 1.19 | -0.00269
CFLBldgPGEOfSNewCZ11 | Com-Iltg-dWatt-CFL_OSbldg | PGE | OfS | New | CZ11 | 2.72 | 0.000595 | 0 | 2.9 | 0.000747 | -0.00937 | 2.72 | 0.000595 | 0 | 2.9 | 0.000747 | -0.00937 |  | CFL | Bldg | 2720 | 0.595 | 2720 | 0.595 | 1.07 | 1.26 | -0.0034449 | 2720 | 0.595 | 2720 | 0.595 | 1.07 | 1.26 | -0.00344
CFLBldgPGEOfSNewCZ12 | Com-Iltg-dWatt-CFL_OSbldg | PGE | OfS | New | CZ12 | 2.72 | 0.000595 | 0 | 2.88 | 0.000743 | -0.00907 | 2.72 | 0.000595 | 0 | 2.88 | 0.000743 | -0.00907 |  | CFL | Bldg | 2720 | 0.595 | 2720 | 0.595 | 1.06 | 1.25 | -0.0033346 | 2720 | 0.595 | 2720 | 0.595 | 1.06 | 1.25 | -0.00333
CFLBldgPGEOfSNewCZ13 | Com-Iltg-dWatt-CFL_OSbldg | PGE | OfS | New | CZ13 | 2.72 | 0.000595 | 0 | 2.91 | 0.000739 | -0.00863 | 2.72 | 0.000595 | 0 | 2.91 | 0.000739 | -0.00863 |  | CFL | Bldg | 2720 | 0.595 | 2720 | 0.595 | 1.07 | 1.24 | -0.0031728 | 2720 | 0.595 | 2720 | 0.595 | 1.07 | 1.24 | -0.00317
CFLBldgPGEOfSNewCZ16 | Com-Iltg-dWatt-CFL_OSbldg | PGE | OfS | New | CZ16 | 2.72 | 0.000595 | 0 | 2.7 | 0.000719 | -0.0196 | 2.72 | 0.000595 | 0 | 2.7 | 0.000719 | -0.0196 |  | CFL | Bldg | 2720 | 0.595 | 2720 | 0.595 | 0.993 | 1.21 | -0.0072059 | 2720 | 0.595 | 2720 | 0.595 | 0.993 | 1.21 | -0.00721
CFLBldgPGEOfSNewIOU | Com-Iltg-dWatt-CFL_OSbldg | PGE | OfS | New | IOU | 2.72 | 0.000595 | 0 | 2.8603 | 0.00073488 | -0.0087204 | 2.72 | 0.000595 | 0 | 2.8603 | 0.00073488 | -0.0087204 |  | CFL | Bldg | 2720 | 0.595 | 2720 | 0.595 | 1.05 | 1.24 | -0.003206 | 2720 | 0.595 | 2720 | 0.595 | 1.05 | 1.24 | -0.00321
CFLBldgPGERFFExCZ01 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RFF | Ex | CZ01 | 4.81 | 0.000808 | 0 | 4.69 | 0.000918 | -0.056706 | 4.81 | 0.000808 | 0 | 4.69 | 0.000918 | -0.056706 |  | CFL | Bldg | 4810 | 0.808 | 4810 | 0.808 | 0.975 | 1.14 | -0.011789 | 4810 | 0.808 | 4810 | 0.808 | 0.975 | 1.14 | -0.0118
CFLBldgPGERFFExCZ02 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RFF | Ex | CZ02 | 4.81 | 0.000808 | 0 | 4.97 | 0.000938 | -0.0368 | 4.81 | 0.000808 | 0 | 4.97 | 0.000938 | -0.0368 |  | CFL | Bldg | 4810 | 0.808 | 4810 | 0.808 | 1.03 | 1.16 | -0.0076507 | 4810 | 0.808 | 4810 | 0.808 | 1.03 | 1.16 | -0.00765
CFLBldgPGERFFExCZ03 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RFF | Ex | CZ03 | 4.81 | 0.000808 | 0 | 4.9102 | 0.000932 | -0.039002 | 4.81 | 0.000808 | 0 | 4.9102 | 0.000932 | -0.039002 |  | CFL | Bldg | 4810 | 0.808 | 4810 | 0.808 | 1.02 | 1.15 | -0.0081086 | 4810 | 0.808 | 4810 | 0.808 | 1.02 | 1.15 | -0.00811
CFLBldgPGERFFExCZ04 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RFF | Ex | CZ04 | 4.81 | 0.000808 | 0 | 5.04 | 0.000937 | -0.031 | 4.81 | 0.000808 | 0 | 5.04 | 0.000937 | -0.031 |  | CFL | Bldg | 4810 | 0.808 | 4810 | 0.808 | 1.05 | 1.16 | -0.0064449 | 4810 | 0.808 | 4810 | 0.808 | 1.05 | 1.16 | -0.00644
CFLBldgPGERFFExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RFF | Ex | CZ05 | 4.81 | 0.000808 | 0 | 4.89 | 0.000923 | -0.0394 | 4.81 | 0.000808 | 0 | 4.89 | 0.000923 | -0.0394 |  | CFL | Bldg | 4810 | 0.808 | 4810 | 0.808 | 1.02 | 1.14 | -0.0081913 | 4810 | 0.808 | 4810 | 0.808 | 1.02 | 1.14 | -0.00819
CFLBldgPGERFFExCZ11 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RFF | Ex | CZ11 | 4.81 | 0.000808 | 0 | 5.07 | 0.000956 | -0.0303 | 4.81 | 0.000808 | 0 | 5.07 | 0.000956 | -0.0303 |  | CFL | Bldg | 4810 | 0.808 | 4810 | 0.808 | 1.05 | 1.18 | -0.0062994 | 4810 | 0.808 | 4810 | 0.808 | 1.05 | 1.18 | -0.0063
CFLBldgPGERFFExCZ12 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RFF | Ex | CZ12 | 4.81 | 0.000808 | 0 | 5.04 | 0.000946 | -0.0317 | 4.81 | 0.000808 | 0 | 5.04 | 0.000946 | -0.0317 |  | CFL | Bldg | 4810 | 0.808 | 4810 | 0.808 | 1.05 | 1.17 | -0.0065904 | 4810 | 0.808 | 4810 | 0.808 | 1.05 | 1.17 | -0.00659
CFLBldgPGERFFExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RFF | Ex | CZ13 | 4.81 | 0.000808 | 0 | 5.08 | 0.000942 | -0.029 | 4.81 | 0.000808 | 0 | 5.08 | 0.000942 | -0.029 |  | CFL | Bldg | 4810 | 0.808 | 4810 | 0.808 | 1.06 | 1.17 | -0.0060291 | 4810 | 0.808 | 4810 | 0.808 | 1.06 | 1.17 | -0.00603
CFLBldgPGERFFExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RFF | Ex | CZ16 | 4.81 | 0.000808 | 0 | 4.72 | 0.000929 | -0.0553 | 4.81 | 0.000808 | 0 | 4.72 | 0.000929 | -0.0553 |  | CFL | Bldg | 4810 | 0.808 | 4810 | 0.808 | 0.981 | 1.15 | -0.011497 | 4810 | 0.808 | 4810 | 0.808 | 0.981 | 1.15 | -0.0115
CFLBldgPGERFFExIOU | Com-Iltg-dWatt-CFL_OSbldg | PGE | RFF | Ex | IOU | 4.81 | 0.000808 | 0 | 4.9886 | 0.00093854 | -0.034655 | 4.81 | 0.000808 | 0 | 4.9886 | 0.00093854 | -0.034655 |  | CFL | Bldg | 4810 | 0.808 | 4810 | 0.808 | 1.04 | 1.16 | -0.0072048 | 4810 | 0.808 | 4810 | 0.808 | 1.04 | 1.16 | -0.0072
CFLBldgPGERFFNewCZ01 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RFF | New | CZ01 | 4.81 | 0.000808 | 0 | 4.52 | 0.000879 | -0.0596 | 4.81 | 0.000808 | 0 | 4.52 | 0.000879 | -0.0596 |  | CFL | Bldg | 4810 | 0.808 | 4810 | 0.808 | 0.94 | 1.09 | -0.012391 | 4810 | 0.808 | 4810 | 0.808 | 0.94 | 1.09 | -0.0124
CFLBldgPGERFFNewCZ02 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RFF | New | CZ02 | 4.81 | 0.000808 | 0 | 4.86 | 0.000974 | -0.0437 | 4.81 | 0.000808 | 0 | 4.86 | 0.000974 | -0.0437 |  | CFL | Bldg | 4810 | 0.808 | 4810 | 0.808 | 1.01 | 1.21 | -0.0090852 | 4810 | 0.808 | 4810 | 0.808 | 1.01 | 1.21 | -0.00909
CFLBldgPGERFFNewCZ03 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RFF | New | CZ03 | 4.81 | 0.000808 | 0 | 4.76 | 0.000945 | -0.0445 | 4.81 | 0.000808 | 0 | 4.76 | 0.000945 | -0.0445 |  | CFL | Bldg | 4810 | 0.808 | 4810 | 0.808 | 0.99 | 1.17 | -0.0092516 | 4810 | 0.808 | 4810 | 0.808 | 0.99 | 1.17 | -0.00925
CFLBldgPGERFFNewCZ04 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RFF | New | CZ04 | 4.81 | 0.000808 | 0 | 4.94 | 0.000964 | -0.0368 | 4.81 | 0.000808 | 0 | 4.94 | 0.000964 | -0.0368 |  | CFL | Bldg | 4810 | 0.808 | 4810 | 0.808 | 1.03 | 1.19 | -0.0076507 | 4810 | 0.808 | 4810 | 0.808 | 1.03 | 1.19 | -0.00765
CFLBldgPGERFFNewCZ05 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RFF | New | CZ05 | 4.81 | 0.000808 | 0 | 4.76 | 0.000932 | -0.0394 | 4.81 | 0.000808 | 0 | 4.76 | 0.000932 | -0.0394 |  | CFL | Bldg | 4810 | 0.808 | 4810 | 0.808 | 0.99 | 1.15 | -0.0081913 | 4810 | 0.808 | 4810 | 0.808 | 0.99 | 1.15 | -0.00819
CFLBldgPGERFFNewCZ11 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RFF | New | CZ11 | 4.81 | 0.000808 | 0 | 5.05 | 0.000996 | -0.0332 | 4.81 | 0.000808 | 0 | 5.05 | 0.000996 | -0.0332 |  | CFL | Bldg | 4810 | 0.808 | 4810 | 0.808 | 1.05 | 1.23 | -0.0069023 | 4810 | 0.808 | 4810 | 0.808 | 1.05 | 1.23 | -0.0069
CFLBldgPGERFFNewCZ12 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RFF | New | CZ12 | 4.81 | 0.000808 | 0 | 5 | 0.000986 | -0.039 | 4.81 | 0.000808 | 0 | 5 | 0.000986 | -0.039 |  | CFL | Bldg | 4810 | 0.808 | 4810 | 0.808 | 1.04 | 1.22 | -0.0081081 | 4810 | 0.808 | 4810 | 0.808 | 1.04 | 1.22 | -0.00811
CFLBldgPGERFFNewCZ13 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RFF | New | CZ13 | 4.81 | 0.000808 | 0 | 5.06 | 0.000984 | -0.0346 | 4.81 | 0.000808 | 0 | 5.06 | 0.000984 | -0.0346 |  | CFL | Bldg | 4810 | 0.808 | 4810 | 0.808 | 1.05 | 1.22 | -0.0071933 | 4810 | 0.808 | 4810 | 0.808 | 1.05 | 1.22 | -0.00719
CFLBldgPGERFFNewCZ16 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RFF | New | CZ16 | 4.81 | 0.000808 | 0 | 4.68 | 0.000952 | -0.0615 | 4.81 | 0.000808 | 0 | 4.68 | 0.000952 | -0.0615 |  | CFL | Bldg | 4810 | 0.808 | 4810 | 0.808 | 0.973 | 1.18 | -0.012786 | 4810 | 0.808 | 4810 | 0.808 | 0.973 | 1.18 | -0.0128
CFLBldgPGERFFNewIOU | Com-Iltg-dWatt-CFL_OSbldg | PGE | RFF | New | IOU | 4.81 | 0.000808 | 0 | 4.9059 | 0.000967 | -0.040184 | 4.81 | 0.000808 | 0 | 4.9059 | 0.000967 | -0.040184 |  | CFL | Bldg | 4810 | 0.808 | 4810 | 0.808 | 1.02 | 1.2 | -0.0083542 | 4810 | 0.808 | 4810 | 0.808 | 1.02 | 1.2 | -0.00835
CFLBldgPGERSDExCZ01 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RSD | Ex | CZ01 | 4.83 | 0.0008 | 0 | 4.6311 | 0.000938 | -0.060311 | 4.83 | 0.0008 | 0 | 4.6311 | 0.000938 | -0.060311 |  | CFL | Bldg | 4830 | 0.8 | 4830 | 0.8 | 0.959 | 1.17 | -0.012487 | 4830 | 0.8 | 4830 | 0.8 | 0.959 | 1.17 | -0.0125
CFLBldgPGERSDExCZ02 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RSD | Ex | CZ02 | 4.83 | 0.0008 | 0 | 5.0016 | 0.000938 | -0.0354 | 4.83 | 0.0008 | 0 | 5.0016 | 0.000938 | -0.0354 |  | CFL | Bldg | 4830 | 0.8 | 4830 | 0.8 | 1.04 | 1.17 | -0.0073292 | 4830 | 0.8 | 4830 | 0.8 | 1.04 | 1.17 | -0.00733
CFLBldgPGERSDExCZ03 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RSD | Ex | CZ03 | 4.83 | 0.0008 | 0 | 4.94 | 0.000939 | -0.0396 | 4.83 | 0.0008 | 0 | 4.94 | 0.000939 | -0.0396 |  | CFL | Bldg | 4830 | 0.8 | 4830 | 0.8 | 1.02 | 1.17 | -0.0081988 | 4830 | 0.8 | 4830 | 0.8 | 1.02 | 1.17 | -0.0082
CFLBldgPGERSDExCZ04 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RSD | Ex | CZ04 | 4.83 | 0.0008 | 0 | 5.0902 | 0.000942 | -0.0294 | 4.83 | 0.0008 | 0 | 5.0902 | 0.000942 | -0.0294 |  | CFL | Bldg | 4830 | 0.8 | 4830 | 0.8 | 1.05 | 1.18 | -0.006087 | 4830 | 0.8 | 4830 | 0.8 | 1.05 | 1.18 | -0.00609
CFLBldgPGERSDExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RSD | Ex | CZ05 | 4.83 | 0.0008 | 0 | 4.9502 | 0.000932 | -0.0382 | 4.83 | 0.0008 | 0 | 4.9502 | 0.000932 | -0.0382 |  | CFL | Bldg | 4830 | 0.8 | 4830 | 0.8 | 1.02 | 1.17 | -0.0079089 | 4830 | 0.8 | 4830 | 0.8 | 1.02 | 1.17 | -0.00791
CFLBldgPGERSDExCZ11 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RSD | Ex | CZ11 | 4.83 | 0.0008 | 0 | 5.11 | 0.000947 | -0.0306 | 4.83 | 0.0008 | 0 | 5.11 | 0.000947 | -0.0306 |  | CFL | Bldg | 4830 | 0.8 | 4830 | 0.8 | 1.06 | 1.18 | -0.0063354 | 4830 | 0.8 | 4830 | 0.8 | 1.06 | 1.18 | -0.00634
CFLBldgPGERSDExCZ12 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RSD | Ex | CZ12 | 4.83 | 0.0008 | 0 | 5.06 | 0.000917 | -0.0316 | 4.83 | 0.0008 | 0 | 5.06 | 0.000917 | -0.0316 |  | CFL | Bldg | 4830 | 0.8 | 4830 | 0.8 | 1.05 | 1.15 | -0.0065424 | 4830 | 0.8 | 4830 | 0.8 | 1.05 | 1.15 | -0.00654
CFLBldgPGERSDExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RSD | Ex | CZ13 | 4.83 | 0.0008 | 0 | 5.14 | 0.000943 | -0.029 | 4.83 | 0.0008 | 0 | 5.14 | 0.000943 | -0.029 |  | CFL | Bldg | 4830 | 0.8 | 4830 | 0.8 | 1.06 | 1.18 | -0.0060041 | 4830 | 0.8 | 4830 | 0.8 | 1.06 | 1.18 | -0.006
CFLBldgPGERSDExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RSD | Ex | CZ16 | 4.83 | 0.0008 | 0 | 4.71 | 0.000916 | -0.0541 | 4.83 | 0.0008 | 0 | 4.71 | 0.000916 | -0.0541 |  | CFL | Bldg | 4830 | 0.8 | 4830 | 0.8 | 0.975 | 1.15 | -0.011201 | 4830 | 0.8 | 4830 | 0.8 | 0.975 | 1.15 | -0.0112
CFLBldgPGERSDExIOU | Com-Iltg-dWatt-CFL_OSbldg | PGE | RSD | Ex | IOU | 4.83 | 0.0008 | 0 | 5.0234 | 0.00093527 | -0.03453 | 4.83 | 0.0008 | 0 | 5.0234 | 0.00093527 | -0.03453 |  | CFL | Bldg | 4830 | 0.8 | 4830 | 0.8 | 1.04 | 1.17 | -0.007149 | 4830 | 0.8 | 4830 | 0.8 | 1.04 | 1.17 | -0.00715
CFLBldgPGERSDNewCZ01 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RSD | New | CZ01 | 4.83 | 0.0008 | 0 | 4.61 | 0.00091 | -0.0146 | 4.83 | 0.0008 | 0 | 4.61 | 0.00091 | -0.0146 |  | CFL | Bldg | 4830 | 0.8 | 4830 | 0.8 | 0.954 | 1.14 | -0.0030228 | 4830 | 0.8 | 4830 | 0.8 | 0.954 | 1.14 | -0.00302
CFLBldgPGERSDNewCZ02 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RSD | New | CZ02 | 4.83 | 0.0008 | 0 | 4.94 | 0.000974 | -0.0393 | 4.83 | 0.0008 | 0 | 4.94 | 0.000974 | -0.0393 |  | CFL | Bldg | 4830 | 0.8 | 4830 | 0.8 | 1.02 | 1.22 | -0.0081366 | 4830 | 0.8 | 4830 | 0.8 | 1.02 | 1.22 | -0.00814
CFLBldgPGERSDNewCZ03 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RSD | New | CZ03 | 4.83 | 0.0008 | 0 | 4.8 | 0.000928 | -0.0492 | 4.83 | 0.0008 | 0 | 4.8 | 0.000928 | -0.0492 |  | CFL | Bldg | 4830 | 0.8 | 4830 | 0.8 | 0.994 | 1.16 | -0.010186 | 4830 | 0.8 | 4830 | 0.8 | 0.994 | 1.16 | -0.0102
CFLBldgPGERSDNewCZ04 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RSD | New | CZ04 | 4.83 | 0.0008 | 0 | 5.03 | 0.000974 | -0.0329 | 4.83 | 0.0008 | 0 | 5.03 | 0.000974 | -0.0329 |  | CFL | Bldg | 4830 | 0.8 | 4830 | 0.8 | 1.04 | 1.22 | -0.0068116 | 4830 | 0.8 | 4830 | 0.8 | 1.04 | 1.22 | -0.00681
CFLBldgPGERSDNewCZ05 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RSD | New | CZ05 | 4.83 | 0.0008 | 0 | 4.84 | 0.000938 | -0.0422 | 4.83 | 0.0008 | 0 | 4.84 | 0.000938 | -0.0422 |  | CFL | Bldg | 4830 | 0.8 | 4830 | 0.8 | 1 | 1.17 | -0.0087371 | 4830 | 0.8 | 4830 | 0.8 | 1 | 1.17 | -0.00874
CFLBldgPGERSDNewCZ11 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RSD | New | CZ11 | 4.83 | 0.0008 | 0 | 5.1 | 0.000994 | -0.0339 | 4.83 | 0.0008 | 0 | 5.1 | 0.000994 | -0.0339 |  | CFL | Bldg | 4830 | 0.8 | 4830 | 0.8 | 1.06 | 1.24 | -0.0070186 | 4830 | 0.8 | 4830 | 0.8 | 1.06 | 1.24 | -0.00702
CFLBldgPGERSDNewCZ12 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RSD | New | CZ12 | 4.83 | 0.0008 | 0 | 5.02 | 0.000958 | -0.0341 | 4.83 | 0.0008 | 0 | 5.02 | 0.000958 | -0.0341 |  | CFL | Bldg | 4830 | 0.8 | 4830 | 0.8 | 1.04 | 1.2 | -0.00706 | 4830 | 0.8 | 4830 | 0.8 | 1.04 | 1.2 | -0.00706
CFLBldgPGERSDNewCZ13 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RSD | New | CZ13 | 4.83 | 0.0008 | 0 | 5.12 | 0.000992 | -0.0324 | 4.83 | 0.0008 | 0 | 5.12 | 0.000992 | -0.0324 |  | CFL | Bldg | 4830 | 0.8 | 4830 | 0.8 | 1.06 | 1.24 | -0.0067081 | 4830 | 0.8 | 4830 | 0.8 | 1.06 | 1.24 | -0.00671
CFLBldgPGERSDNewCZ16 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RSD | New | CZ16 | 4.83 | 0.0008 | 0 | 4.68 | 0.000943 | -0.0453 | 4.83 | 0.0008 | 0 | 4.68 | 0.000943 | -0.0453 |  | CFL | Bldg | 4830 | 0.8 | 4830 | 0.8 | 0.969 | 1.18 | -0.0093789 | 4830 | 0.8 | 4830 | 0.8 | 0.969 | 1.18 | -0.00938
CFLBldgPGERSDNewIOU | Com-Iltg-dWatt-CFL_OSbldg | PGE | RSD | New | IOU | 4.83 | 0.0008 | 0 | 4.955 | 0.00095805 | -0.038863 | 4.83 | 0.0008 | 0 | 4.955 | 0.00095805 | -0.038863 |  | CFL | Bldg | 4830 | 0.8 | 4830 | 0.8 | 1.03 | 1.2 | -0.0080463 | 4830 | 0.8 | 4830 | 0.8 | 1.03 | 1.2 | -0.00805
CFLBldgPGERt3ExCZ01 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Rt3 | Ex | CZ01 | 3.71 | 0.00063182 | 0 | 3.56 | 0.00078282 | -0.0545 | 3.71 | 0.000629 | 0 | 3.56 | 0.00077955 | -0.0545 |  | CFL | Bldg | 3710 | 0.632 | 3710 | 0.629 | 0.96 | 1.24 | -0.01469 | 3710 | 0.632 | 3710 | 0.629 | 0.96 | 1.24 | -0.0147
CFLBldgPGERt3ExCZ02 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Rt3 | Ex | CZ02 | 3.71 | 0.00063187 | 0 | 3.9 | 0.00076835 | -0.027695 | 3.71 | 0.000629 | 0 | 3.9 | 0.000765 | -0.027648 |  | CFL | Bldg | 3710 | 0.632 | 3710 | 0.629 | 1.05 | 1.22 | -0.0074524 | 3710 | 0.632 | 3710 | 0.629 | 1.05 | 1.22 | -0.00745
CFLBldgPGERt3ExCZ03 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Rt3 | Ex | CZ03 | 3.71 | 0.000631 | 0 | 3.92 | 0.00077196 | -0.026595 | 3.71 | 0.000629 | 0 | 3.92 | 0.00076991 | -0.026505 |  | CFL | Bldg | 3710 | 0.631 | 3710 | 0.629 | 1.06 | 1.22 | -0.0071441 | 3710 | 0.631 | 3710 | 0.629 | 1.06 | 1.22 | -0.00714
CFLBldgPGERt3ExCZ04 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Rt3 | Ex | CZ04 | 3.71 | 0.00063102 | 0 | 3.99 | 0.00077108 | -0.0183 | 3.71 | 0.000629 | 0 | 3.99 | 0.000769 | -0.0183 |  | CFL | Bldg | 3710 | 0.631 | 3710 | 0.629 | 1.08 | 1.22 | -0.0049326 | 3710 | 0.631 | 3710 | 0.629 | 1.08 | 1.22 | -0.00493
CFLBldgPGERt3ExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Rt3 | Ex | CZ05 | 3.71 | 0.00063102 | 0 | 3.9295 | 0.00076397 | -0.021995 | 3.71 | 0.000629 | 0 | 3.9206 | 0.000761 | -0.021906 |  | CFL | Bldg | 3710 | 0.631 | 3710 | 0.629 | 1.06 | 1.21 | -0.0059046 | 3710 | 0.631 | 3710 | 0.629 | 1.06 | 1.21 | -0.0059
CFLBldgPGERt3ExCZ11 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Rt3 | Ex | CZ11 | 3.71 | 0.00063086 | 0 | 3.9193 | 0.0007738 | -0.0263 | 3.71 | 0.000629 | 0 | 3.91 | 0.00077193 | -0.0263 |  | CFL | Bldg | 3710 | 0.631 | 3710 | 0.629 | 1.05 | 1.23 | -0.0070889 | 3710 | 0.631 | 3710 | 0.629 | 1.05 | 1.23 | -0.00709
CFLBldgPGERt3ExCZ12 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Rt3 | Ex | CZ12 | 3.71 | 0.00063088 | 0 | 3.9294 | 0.00077788 | -0.0256 | 3.71 | 0.000629 | 0 | 3.92 | 0.000776 | -0.0256 |  | CFL | Bldg | 3710 | 0.631 | 3710 | 0.629 | 1.06 | 1.23 | -0.0069003 | 3710 | 0.631 | 3710 | 0.629 | 1.06 | 1.23 | -0.0069
CFLBldgPGERt3ExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Rt3 | Ex | CZ13 | 3.71 | 0.00063086 | 0 | 3.9495 | 0.00077179 | -0.0242 | 3.71 | 0.000629 | 0 | 3.9402 | 0.00076993 | -0.0242 |  | CFL | Bldg | 3710 | 0.631 | 3710 | 0.629 | 1.06 | 1.22 | -0.0065229 | 3710 | 0.631 | 3710 | 0.629 | 1.06 | 1.22 | -0.00652
CFLBldgPGERt3ExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Rt3 | Ex | CZ16 | 3.71 | 0.00063089 | 0 | 3.61 | 0.00075483 | -0.0508 | 3.71 | 0.000629 | 0 | 3.61 | 0.00075294 | -0.0508 |  | CFL | Bldg | 3710 | 0.631 | 3710 | 0.629 | 0.973 | 1.2 | -0.013693 | 3710 | 0.631 | 3710 | 0.629 | 0.973 | 1.2 | -0.0137
CFLBldgPGERt3ExIOU | Com-Iltg-dWatt-CFL_OSbldg | PGE | Rt3 | Ex | IOU | 3.71 | 0.00063102 | 0 | 3.9303 | 0.00077291 | -0.025171 | 3.71 | 0.000629 | 0 | 3.9261 | 0.0007708 | -0.025136 |  | CFL | Bldg | 3710 | 0.631 | 3710 | 0.629 | 1.06 | 1.23 | -0.0067752 | 3710 | 0.631 | 3710 | 0.629 | 1.06 | 1.23 | -0.00678
CFLBldgPGERt3NewCZ01 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Rt3 | New | CZ01 | 3.71 | 0.000629 | 0 | 3.49 | 0.000767 | -0.0601 | 3.71 | 0.000629 | 0 | 3.49 | 0.000767 | -0.0601 |  | CFL | Bldg | 3710 | 0.629 | 3710 | 0.629 | 0.941 | 1.22 | -0.016199 | 3710 | 0.629 | 3710 | 0.629 | 0.941 | 1.22 | -0.0162
CFLBldgPGERt3NewCZ02 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Rt3 | New | CZ02 | 3.71 | 0.000629 | 0 | 3.8 | 0.000747 | -0.0324 | 3.71 | 0.000629 | 0 | 3.8 | 0.000747 | -0.0324 |  | CFL | Bldg | 3710 | 0.629 | 3710 | 0.629 | 1.02 | 1.19 | -0.0087332 | 3710 | 0.629 | 3710 | 0.629 | 1.02 | 1.19 | -0.00873
CFLBldgPGERt3NewCZ03 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Rt3 | New | CZ03 | 3.71 | 0.000629 | 0 | 3.76 | 0.000753 | -0.0329 | 3.71 | 0.000629 | 0 | 3.76 | 0.000753 | -0.0329 |  | CFL | Bldg | 3710 | 0.629 | 3710 | 0.629 | 1.01 | 1.2 | -0.0088679 | 3710 | 0.629 | 3710 | 0.629 | 1.01 | 1.2 | -0.00887
CFLBldgPGERt3NewCZ04 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Rt3 | New | CZ04 | 3.71 | 0.000629 | 0 | 3.87 | 0.000758 | -0.0235 | 3.71 | 0.000629 | 0 | 3.87 | 0.000758 | -0.0235 |  | CFL | Bldg | 3710 | 0.629 | 3710 | 0.629 | 1.04 | 1.21 | -0.0063342 | 3710 | 0.629 | 3710 | 0.629 | 1.04 | 1.21 | -0.00633
CFLBldgPGERt3NewCZ05 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Rt3 | New | CZ05 | 3.71 | 0.000629 | 0 | 3.79 | 0.000749 | -0.0273 | 3.71 | 0.000629 | 0 | 3.79 | 0.000749 | -0.0273 |  | CFL | Bldg | 3710 | 0.629 | 3710 | 0.629 | 1.02 | 1.19 | -0.0073585 | 3710 | 0.629 | 3710 | 0.629 | 1.02 | 1.19 | -0.00736
CFLBldgPGERt3NewCZ11 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Rt3 | New | CZ11 | 3.71 | 0.000629 | 0 | 3.89 | 0.000775 | -0.0278 | 3.71 | 0.000629 | 0 | 3.89 | 0.000775 | -0.0278 |  | CFL | Bldg | 3710 | 0.629 | 3710 | 0.629 | 1.05 | 1.23 | -0.0074933 | 3710 | 0.629 | 3710 | 0.629 | 1.05 | 1.23 | -0.00749
CFLBldgPGERt3NewCZ12 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Rt3 | New | CZ12 | 3.71 | 0.000629 | 0 | 3.86 | 0.000772 | -0.0298 | 3.71 | 0.000629 | 0 | 3.86 | 0.000772 | -0.0298 |  | CFL | Bldg | 3710 | 0.629 | 3710 | 0.629 | 1.04 | 1.23 | -0.0080323 | 3710 | 0.629 | 3710 | 0.629 | 1.04 | 1.23 | -0.00803
CFLBldgPGERt3NewCZ13 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Rt3 | New | CZ13 | 3.71 | 0.000629 | 0 | 3.9 | 0.000767 | -0.0268 | 3.71 | 0.000629 | 0 | 3.9 | 0.000767 | -0.0268 |  | CFL | Bldg | 3710 | 0.629 | 3710 | 0.629 | 1.05 | 1.22 | -0.0072237 | 3710 | 0.629 | 3710 | 0.629 | 1.05 | 1.22 | -0.00722
CFLBldgPGERt3NewCZ16 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Rt3 | New | CZ16 | 3.71 | 0.000629 | 0 | 3.54 | 0.000692 | -0.0485 | 3.71 | 0.000629 | 0 | 3.54 | 0.000692 | -0.0485 |  | CFL | Bldg | 3710 | 0.629 | 3710 | 0.629 | 0.954 | 1.1 | -0.013073 | 3710 | 0.629 | 3710 | 0.629 | 0.954 | 1.1 | -0.0131
CFLBldgPGERt3NewIOU | Com-Iltg-dWatt-CFL_OSbldg | PGE | Rt3 | New | IOU | 3.71 | 0.000629 | 0 | 3.8352 | 0.0007622 | -0.029535 | 3.71 | 0.000629 | 0 | 3.8352 | 0.0007622 | -0.029535 |  | CFL | Bldg | 3710 | 0.629 | 3710 | 0.629 | 1.03 | 1.21 | -0.0079609 | 3710 | 0.629 | 3710 | 0.629 | 1.03 | 1.21 | -0.00796
CFLBldgPGERtLExCZ01 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RtL | Ex | CZ01 | 4.3497 | 0.00068895 | 0 | 4.22 | 0.00083892 | -0.0587 | 4.3497 | 0.000688 | 0 | 4.22 | 0.00083797 | -0.0587 |  | CFL | Bldg | 4350 | 0.689 | 4350 | 0.688 | 0.97 | 1.22 | -0.013495 | 4350 | 0.689 | 4350 | 0.688 | 0.97 | 1.22 | -0.0135
CFLBldgPGERtLExCZ02 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RtL | Ex | CZ02 | 4.3497 | 0.00068895 | 0 | 4.5697 | 0.00083692 | -0.0305 | 4.3497 | 0.000688 | 0 | 4.5602 | 0.00083597 | -0.0305 |  | CFL | Bldg | 4350 | 0.689 | 4350 | 0.688 | 1.05 | 1.22 | -0.007012 | 4350 | 0.689 | 4350 | 0.688 | 1.05 | 1.22 | -0.00701
CFLBldgPGERtLExCZ03 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RtL | Ex | CZ03 | 4.3495 | 0.00068907 | 0 | 4.5995 | 0.00083303 | -0.0287 | 4.3495 | 0.000688 | 0 | 4.5912 | 0.00083112 | -0.0287 |  | CFL | Bldg | 4350 | 0.689 | 4350 | 0.688 | 1.06 | 1.21 | -0.0065984 | 4350 | 0.689 | 4350 | 0.688 | 1.06 | 1.21 | -0.0066
CFLBldgPGERtLExCZ04 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RtL | Ex | CZ04 | 4.3495 | 0.0006891 | 0 | 4.6695 | 0.00083805 | -0.0214 | 4.3495 | 0.000688 | 0 | 4.6615 | 0.00083615 | -0.0214 |  | CFL | Bldg | 4350 | 0.689 | 4350 | 0.688 | 1.07 | 1.22 | -0.0049201 | 4350 | 0.689 | 4350 | 0.688 | 1.07 | 1.22 | -0.00492
CFLBldgPGERtLExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RtL | Ex | CZ05 | 4.3495 | 0.0006891 | 0 | 4.5795 | 0.00082305 | -0.0284 | 4.3495 | 0.000688 | 0 | 4.5715 | 0.000821 | -0.0284 |  | CFL | Bldg | 4350 | 0.689 | 4350 | 0.688 | 1.05 | 1.19 | -0.0065295 | 4350 | 0.689 | 4350 | 0.688 | 1.05 | 1.19 | -0.00653
CFLBldgPGERtLExCZ11 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RtL | Ex | CZ11 | 4.3493 | 0.00068893 | 0 | 4.6 | 0.00084493 | -0.029093 | 4.3493 | 0.000688 | 0 | 4.6 | 0.000844 | -0.029 |  | CFL | Bldg | 4350 | 0.689 | 4350 | 0.688 | 1.06 | 1.23 | -0.0066677 | 4350 | 0.689 | 4350 | 0.688 | 1.06 | 1.23 | -0.00667
CFLBldgPGERtLExCZ12 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RtL | Ex | CZ12 | 4.3494 | 0.00068894 | 0 | 4.6094 | 0.00085288 | -0.0266 | 4.3494 | 0.000688 | 0 | 4.6 | 0.000851 | -0.0266 |  | CFL | Bldg | 4350 | 0.689 | 4350 | 0.688 | 1.06 | 1.24 | -0.0061158 | 4350 | 0.689 | 4350 | 0.688 | 1.06 | 1.24 | -0.00612
CFLBldgPGERtLExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RtL | Ex | CZ13 | 4.3498 | 0.00068893 | 0 | 4.64 | 0.00084591 | -0.0257 | 4.3498 | 0.000688 | 0 | 4.64 | 0.00084405 | -0.0257 |  | CFL | Bldg | 4350 | 0.689 | 4350 | 0.688 | 1.07 | 1.23 | -0.0059084 | 4350 | 0.689 | 4350 | 0.688 | 1.07 | 1.23 | -0.00591
CFLBldgPGERtLExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RtL | Ex | CZ16 | 4.3498 | 0.00068894 | 0 | 4.23 | 0.00081189 | -0.057804 | 4.3498 | 0.000688 | 0 | 4.23 | 0.00081 | -0.057804 |  | CFL | Bldg | 4350 | 0.689 | 4350 | 0.688 | 0.972 | 1.18 | -0.013289 | 4350 | 0.689 | 4350 | 0.688 | 0.972 | 1.18 | -0.0133
CFLBldgPGERtLExIOU | Com-Iltg-dWatt-CFL_OSbldg | PGE | RtL | Ex | IOU | 4.3495 | 0.00068901 | 0 | 4.6098 | 0.00084086 | -0.0273 | 4.3495 | 0.000688 | 0 | 4.6029 | 0.00083909 | -0.027295 |  | CFL | Bldg | 4350 | 0.689 | 4350 | 0.688 | 1.06 | 1.22 | -0.0062755 | 4350 | 0.689 | 4350 | 0.688 | 1.06 | 1.22 | -0.00628
CFLBldgPGERtLNewCZ01 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RtL | New | CZ01 | 4.34 | 0.000688 | 0 | 4.18 | 0.00082 | -0.0652 | 4.34 | 0.000688 | 0 | 4.18 | 0.00082 | -0.0652 |  | CFL | Bldg | 4340 | 0.688 | 4340 | 0.688 | 0.963 | 1.19 | -0.015023 | 4340 | 0.688 | 4340 | 0.688 | 0.963 | 1.19 | -0.015
CFLBldgPGERtLNewCZ02 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RtL | New | CZ02 | 4.34 | 0.000688 | 0 | 4.51 | 0.000875 | -0.0346 | 4.34 | 0.000688 | 0 | 4.51 | 0.000875 | -0.0346 |  | CFL | Bldg | 4340 | 0.688 | 4340 | 0.688 | 1.04 | 1.27 | -0.0079724 | 4340 | 0.688 | 4340 | 0.688 | 1.04 | 1.27 | -0.00797
CFLBldgPGERtLNewCZ03 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RtL | New | CZ03 | 4.34 | 0.000688 | 0 | 4.46 | 0.00085 | -0.0324 | 4.34 | 0.000688 | 0 | 4.46 | 0.00085 | -0.0324 |  | CFL | Bldg | 4340 | 0.688 | 4340 | 0.688 | 1.03 | 1.24 | -0.0074654 | 4340 | 0.688 | 4340 | 0.688 | 1.03 | 1.24 | -0.00747
CFLBldgPGERtLNewCZ04 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RtL | New | CZ04 | 4.34 | 0.000688 | 0 | 4.61 | 0.000865 | -0.0246 | 4.34 | 0.000688 | 0 | 4.61 | 0.000865 | -0.0246 |  | CFL | Bldg | 4340 | 0.688 | 4340 | 0.688 | 1.06 | 1.26 | -0.0056682 | 4340 | 0.688 | 4340 | 0.688 | 1.06 | 1.26 | -0.00567
CFLBldgPGERtLNewCZ05 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RtL | New | CZ05 | 4.34 | 0.000688 | 0 | 4.47 | 0.00083 | -0.0337 | 4.34 | 0.000688 | 0 | 4.47 | 0.00083 | -0.0337 |  | CFL | Bldg | 4340 | 0.688 | 4340 | 0.688 | 1.03 | 1.21 | -0.007765 | 4340 | 0.688 | 4340 | 0.688 | 1.03 | 1.21 | -0.00777
CFLBldgPGERtLNewCZ11 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RtL | New | CZ11 | 4.34 | 0.000688 | 0 | 4.64 | 0.000879 | -0.031 | 4.34 | 0.000688 | 0 | 4.64 | 0.000879 | -0.031 |  | CFL | Bldg | 4340 | 0.688 | 4340 | 0.688 | 1.07 | 1.28 | -0.0071429 | 4340 | 0.688 | 4340 | 0.688 | 1.07 | 1.28 | -0.00714
CFLBldgPGERtLNewCZ12 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RtL | New | CZ12 | 4.34 | 0.000688 | 0 | 4.61 | 0.000888 | -0.0305 | 4.34 | 0.000688 | 0 | 4.61 | 0.000888 | -0.0305 |  | CFL | Bldg | 4340 | 0.688 | 4340 | 0.688 | 1.06 | 1.29 | -0.0070276 | 4340 | 0.688 | 4340 | 0.688 | 1.06 | 1.29 | -0.00703
CFLBldgPGERtLNewCZ13 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RtL | New | CZ13 | 4.34 | 0.000688 | 0 | 4.67 | 0.000881 | -0.0289 | 4.34 | 0.000688 | 0 | 4.67 | 0.000881 | -0.0289 |  | CFL | Bldg | 4340 | 0.688 | 4340 | 0.688 | 1.08 | 1.28 | -0.006659 | 4340 | 0.688 | 4340 | 0.688 | 1.08 | 1.28 | -0.00666
CFLBldgPGERtLNewCZ16 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RtL | New | CZ16 | 4.34 | 0.000688 | 0 | 4.26 | 0.00084 | -0.0608 | 4.34 | 0.000688 | 0 | 4.26 | 0.00084 | -0.0608 |  | CFL | Bldg | 4340 | 0.688 | 4340 | 0.688 | 0.982 | 1.22 | -0.014009 | 4340 | 0.688 | 4340 | 0.688 | 0.982 | 1.22 | -0.014
CFLBldgPGERtLNewIOU | Com-Iltg-dWatt-CFL_OSbldg | PGE | RtL | New | IOU | 4.34 | 0.000688 | 0 | 4.5699 | 0.00087042 | -0.030695 | 4.34 | 0.000688 | 0 | 4.5699 | 0.00087042 | -0.030695 |  | CFL | Bldg | 4340 | 0.688 | 4340 | 0.688 | 1.05 | 1.27 | -0.0070726 | 4340 | 0.688 | 4340 | 0.688 | 1.05 | 1.27 | -0.00707
CFLBldgPGERtSExCZ01 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RtS | Ex | CZ01 | 4.01 | 0.0007 | 0 | 3.88 | 0.000827 | -0.0481 | 4.01 | 0.0007 | 0 | 3.88 | 0.000827 | -0.0481 |  | CFL | Bldg | 4010 | 0.7 | 4010 | 0.7 | 0.968 | 1.18 | -0.011995 | 4010 | 0.7 | 4010 | 0.7 | 0.968 | 1.18 | -0.012
CFLBldgPGERtSExCZ02 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RtS | Ex | CZ02 | 4.01 | 0.0007 | 0 | 4.18 | 0.000835 | -0.0263 | 4.01 | 0.0007 | 0 | 4.18 | 0.000835 | -0.0263 |  | CFL | Bldg | 4010 | 0.7 | 4010 | 0.7 | 1.04 | 1.19 | -0.0065586 | 4010 | 0.7 | 4010 | 0.7 | 1.04 | 1.19 | -0.00656
CFLBldgPGERtSExCZ03 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RtS | Ex | CZ03 | 4.01 | 0.0007 | 0 | 4.18 | 0.000848 | -0.0248 | 4.01 | 0.0007 | 0 | 4.18 | 0.000848 | -0.0248 |  | CFL | Bldg | 4010 | 0.7 | 4010 | 0.7 | 1.04 | 1.21 | -0.0061845 | 4010 | 0.7 | 4010 | 0.7 | 1.04 | 1.21 | -0.00618
CFLBldgPGERtSExCZ04 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RtS | Ex | CZ04 | 4.01 | 0.0007 | 0 | 4.26 | 0.000848 | -0.0186 | 4.01 | 0.0007 | 0 | 4.26 | 0.000848 | -0.0186 |  | CFL | Bldg | 4010 | 0.7 | 4010 | 0.7 | 1.06 | 1.21 | -0.0046384 | 4010 | 0.7 | 4010 | 0.7 | 1.06 | 1.21 | -0.00464
CFLBldgPGERtSExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RtS | Ex | CZ05 | 4.01 | 0.0007 | 0 | 4.18 | 0.000834 | -0.0218 | 4.01 | 0.0007 | 0 | 4.18 | 0.000834 | -0.0218 |  | CFL | Bldg | 4010 | 0.7 | 4010 | 0.7 | 1.04 | 1.19 | -0.0054364 | 4010 | 0.7 | 4010 | 0.7 | 1.04 | 1.19 | -0.00544
CFLBldgPGERtSExCZ11 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RtS | Ex | CZ11 | 4.01 | 0.0007 | 0 | 4.21 | 0.000857 | -0.0248 | 4.01 | 0.0007 | 0 | 4.21 | 0.000857 | -0.0248 |  | CFL | Bldg | 4010 | 0.7 | 4010 | 0.7 | 1.05 | 1.22 | -0.0061845 | 4010 | 0.7 | 4010 | 0.7 | 1.05 | 1.22 | -0.00618
CFLBldgPGERtSExCZ12 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RtS | Ex | CZ12 | 4.01 | 0.0007 | 0 | 4.2 | 0.000844 | -0.0256 | 4.01 | 0.0007 | 0 | 4.2 | 0.000844 | -0.0256 |  | CFL | Bldg | 4010 | 0.7 | 4010 | 0.7 | 1.05 | 1.21 | -0.006384 | 4010 | 0.7 | 4010 | 0.7 | 1.05 | 1.21 | -0.00638
CFLBldgPGERtSExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RtS | Ex | CZ13 | 4.01 | 0.0007 | 0 | 4.23 | 0.000849 | -0.0232 | 4.01 | 0.0007 | 0 | 4.23 | 0.000849 | -0.0232 |  | CFL | Bldg | 4010 | 0.7 | 4010 | 0.7 | 1.05 | 1.21 | -0.0057855 | 4010 | 0.7 | 4010 | 0.7 | 1.05 | 1.21 | -0.00579
CFLBldgPGERtSExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RtS | Ex | CZ16 | 4.01 | 0.0007 | 0 | 3.93 | 0.000832 | -0.0449 | 4.01 | 0.0007 | 0 | 3.93 | 0.000832 | -0.0449 |  | CFL | Bldg | 4010 | 0.7 | 4010 | 0.7 | 0.98 | 1.19 | -0.011197 | 4010 | 0.7 | 4010 | 0.7 | 0.98 | 1.19 | -0.0112
CFLBldgPGERtSExIOU | Com-Iltg-dWatt-CFL_OSbldg | PGE | RtS | Ex | IOU | 4.01 | 0.0007 | 0 | 4.2007 | 0.0008462 | -0.024223 | 4.01 | 0.0007 | 0 | 4.2007 | 0.0008462 | -0.024223 |  | CFL | Bldg | 4010 | 0.7 | 4010 | 0.7 | 1.05 | 1.21 | -0.0060407 | 4010 | 0.7 | 4010 | 0.7 | 1.05 | 1.21 | -0.00604
CFLBldgPGERtSNewCZ01 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RtS | New | CZ01 | 4.01 | 0.0007 | 0 | 3.86 | 0.000815 | -0.0538 | 4.01 | 0.0007 | 0 | 3.86 | 0.000815 | -0.0538 |  | CFL | Bldg | 4010 | 0.7 | 4010 | 0.7 | 0.963 | 1.16 | -0.013416 | 4010 | 0.7 | 4010 | 0.7 | 0.963 | 1.16 | -0.0134
CFLBldgPGERtSNewCZ02 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RtS | New | CZ02 | 4.01 | 0.0007 | 0 | 4.13 | 0.000855 | -0.029 | 4.01 | 0.0007 | 0 | 4.13 | 0.000855 | -0.029 |  | CFL | Bldg | 4010 | 0.7 | 4010 | 0.7 | 1.03 | 1.22 | -0.0072319 | 4010 | 0.7 | 4010 | 0.7 | 1.03 | 1.22 | -0.00723
CFLBldgPGERtSNewCZ03 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RtS | New | CZ03 | 4.01 | 0.0007 | 0 | 4.07 | 0.000839 | -0.0276 | 4.01 | 0.0007 | 0 | 4.07 | 0.000839 | -0.0276 |  | CFL | Bldg | 4010 | 0.7 | 4010 | 0.7 | 1.01 | 1.2 | -0.0068828 | 4010 | 0.7 | 4010 | 0.7 | 1.01 | 1.2 | -0.00688
CFLBldgPGERtSNewCZ04 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RtS | New | CZ04 | 4.01 | 0.0007 | 0 | 4.19 | 0.000847 | -0.0208 | 4.01 | 0.0007 | 0 | 4.19 | 0.000847 | -0.0208 |  | CFL | Bldg | 4010 | 0.7 | 4010 | 0.7 | 1.04 | 1.21 | -0.005187 | 4010 | 0.7 | 4010 | 0.7 | 1.04 | 1.21 | -0.00519
CFLBldgPGERtSNewCZ05 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RtS | New | CZ05 | 4.01 | 0.0007 | 0 | 4.09 | 0.000825 | -0.0246 | 4.01 | 0.0007 | 0 | 4.09 | 0.000825 | -0.0246 |  | CFL | Bldg | 4010 | 0.7 | 4010 | 0.7 | 1.02 | 1.18 | -0.0061347 | 4010 | 0.7 | 4010 | 0.7 | 1.02 | 1.18 | -0.00613
CFLBldgPGERtSNewCZ11 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RtS | New | CZ11 | 4.01 | 0.0007 | 0 | 4.23 | 0.000871 | -0.0251 | 4.01 | 0.0007 | 0 | 4.23 | 0.000871 | -0.0251 |  | CFL | Bldg | 4010 | 0.7 | 4010 | 0.7 | 1.05 | 1.24 | -0.0062594 | 4010 | 0.7 | 4010 | 0.7 | 1.05 | 1.24 | -0.00626
CFLBldgPGERtSNewCZ12 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RtS | New | CZ12 | 4.01 | 0.0007 | 0 | 4.2 | 0.000862 | -0.0267 | 4.01 | 0.0007 | 0 | 4.2 | 0.000862 | -0.0267 |  | CFL | Bldg | 4010 | 0.7 | 4010 | 0.7 | 1.05 | 1.23 | -0.0066584 | 4010 | 0.7 | 4010 | 0.7 | 1.05 | 1.23 | -0.00666
CFLBldgPGERtSNewCZ13 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RtS | New | CZ13 | 4.01 | 0.0007 | 0 | 4.24 | 0.000861 | -0.0242 | 4.01 | 0.0007 | 0 | 4.24 | 0.000861 | -0.0242 |  | CFL | Bldg | 4010 | 0.7 | 4010 | 0.7 | 1.06 | 1.23 | -0.0060349 | 4010 | 0.7 | 4010 | 0.7 | 1.06 | 1.23 | -0.00603
CFLBldgPGERtSNewCZ16 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RtS | New | CZ16 | 4.01 | 0.0007 | 0 | 3.92 | 0.000832 | -0.0481 | 4.01 | 0.0007 | 0 | 3.92 | 0.000832 | -0.0481 |  | CFL | Bldg | 4010 | 0.7 | 4010 | 0.7 | 0.978 | 1.19 | -0.011995 | 4010 | 0.7 | 4010 | 0.7 | 0.978 | 1.19 | -0.012
CFLBldgPGERtSNewIOU | Com-Iltg-dWatt-CFL_OSbldg | PGE | RtS | New | IOU | 4.01 | 0.0007 | 0 | 4.1637 | 0.00085277 | -0.026004 | 4.01 | 0.0007 | 0 | 4.1637 | 0.00085277 | -0.026004 |  | CFL | Bldg | 4010 | 0.7 | 4010 | 0.7 | 1.04 | 1.22 | -0.0064847 | 4010 | 0.7 | 4010 | 0.7 | 1.04 | 1.22 | -0.00648
CFLBldgPGESCnExCZ01 | Com-Iltg-dWatt-CFL_OSbldg | PGE | SCn | Ex | CZ01 | 2.7587 | 0.00057427 | 0 | 2.3393 | 0.00057427 | -0.04638 | 2.74 | 0.000564 | 0 | 2.33 | 0.000564 | -0.0461 |  | CFL | Bldg | 2760 | 0.574 | 2740 | 0.564 | 0.85 | 1 | -0.016825 | 2760 | 0.574 | 2740 | 0.564 | 0.85 | 1 | -0.0168
CFLBldgPGESCnExCZ02 | Com-Iltg-dWatt-CFL_OSbldg | PGE | SCn | Ex | CZ02 | 2.759 | 0.00057444 | 0 | 2.649 | 0.00071629 | -0.02469 | 2.74 | 0.000564 | 0 | 2.63 | 0.000703 | -0.0245 |  | CFL | Bldg | 2760 | 0.574 | 2740 | 0.564 | 0.96 | 1.25 | -0.0089416 | 2760 | 0.574 | 2740 | 0.564 | 0.96 | 1.25 | -0.00894
CFLBldgPGESCnExCZ03 | Com-Iltg-dWatt-CFL_OSbldg | PGE | SCn | Ex | CZ03 | 2.759 | 0.00057445 | 0 | 2.559 | 0.00075824 | -0.02699 | 2.74 | 0.000564 | 0 | 2.54 | 0.000744 | -0.0268 |  | CFL | Bldg | 2760 | 0.574 | 2740 | 0.564 | 0.927 | 1.32 | -0.009781 | 2760 | 0.574 | 2740 | 0.564 | 0.927 | 1.32 | -0.00978
CFLBldgPGESCnExCZ04 | Com-Iltg-dWatt-CFL_OSbldg | PGE | SCn | Ex | CZ04 | 2.759 | 0.00057445 | 0 | 2.7095 | 0.0007173 | -0.021495 | 2.74 | 0.000564 | 0 | 2.7 | 0.000704 | -0.0214 |  | CFL | Bldg | 2760 | 0.574 | 2740 | 0.564 | 0.985 | 1.25 | -0.0078102 | 2760 | 0.574 | 2740 | 0.564 | 0.985 | 1.25 | -0.00781
CFLBldgPGESCnExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | PGE | SCn | Ex | CZ05 | 2.759 | 0.00057445 | 0 | 2.539 | 0.00068435 | -0.02679 | 2.74 | 0.000564 | 0 | 2.52 | 0.000672 | -0.0266 |  | CFL | Bldg | 2760 | 0.574 | 2740 | 0.564 | 0.92 | 1.19 | -0.009708 | 2760 | 0.574 | 2740 | 0.564 | 0.92 | 1.19 | -0.00971
CFLBldgPGESCnExCZ11 | Com-Iltg-dWatt-CFL_OSbldg | PGE | SCn | Ex | CZ11 | 2.758 | 0.00057388 | 0 | 2.708 | 0.00069757 | -0.02279 | 2.74 | 0.000564 | 0 | 2.69 | 0.000685 | -0.0227 |  | CFL | Bldg | 2760 | 0.574 | 2740 | 0.564 | 0.982 | 1.21 | -0.0082847 | 2760 | 0.574 | 2740 | 0.564 | 0.982 | 1.21 | -0.00828
CFLBldgPGESCnExCZ12 | Com-Iltg-dWatt-CFL_OSbldg | PGE | SCn | Ex | CZ12 | 2.7581 | 0.00057394 | 0 | 2.7181 | 0.00070674 | -0.022981 | 2.74 | 0.000564 | 0 | 2.7 | 0.000695 | -0.0228 |  | CFL | Bldg | 2760 | 0.574 | 2740 | 0.564 | 0.985 | 1.23 | -0.0083212 | 2760 | 0.574 | 2740 | 0.564 | 0.985 | 1.23 | -0.00832
CFLBldgPGESCnExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | PGE | SCn | Ex | CZ13 | 2.7581 | 0.00057396 | 0 | 2.7381 | 0.00069477 | -0.020381 | 2.74 | 0.000564 | 0 | 2.72 | 0.000683 | -0.0202 |  | CFL | Bldg | 2760 | 0.574 | 2740 | 0.564 | 0.993 | 1.21 | -0.0073723 | 2760 | 0.574 | 2740 | 0.564 | 0.993 | 1.21 | -0.00737
CFLBldgPGESCnExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | PGE | SCn | Ex | CZ16 | 2.7582 | 0.00057398 | 0 | 2.4581 | 0.0006818 | -0.032281 | 2.74 | 0.000564 | 0 | 2.44 | 0.00067 | -0.0321 |  | CFL | Bldg | 2760 | 0.574 | 2740 | 0.564 | 0.891 | 1.19 | -0.011715 | 2760 | 0.574 | 2740 | 0.564 | 0.891 | 1.19 | -0.0117
CFLBldgPGESCnExIOU | Com-Iltg-dWatt-CFL_OSbldg | PGE | SCn | Ex | IOU | 2.7586 | 0.00057422 | 0 | 2.6535 | 0.00072255 | -0.024186 | 2.74 | 0.000564 | 0 | 2.6362 | 0.00070961 | -0.024017 |  | CFL | Bldg | 2760 | 0.574 | 2740 | 0.564 | 0.962 | 1.26 | -0.0087652 | 2760 | 0.574 | 2740 | 0.564 | 0.962 | 1.26 | -0.00877
CFLBldgPGESCnNewCZ01 | Com-Iltg-dWatt-CFL_OSbldg | PGE | SCn | New | CZ01 | 2.74 | 0.000564 | 0 | 2.35 | 0.000564 | -0.0497 | 2.74 | 0.000564 | 0 | 2.35 | 0.000564 | -0.0497 |  | CFL | Bldg | 2740 | 0.564 | 2740 | 0.564 | 0.858 | 1 | -0.018139 | 2740 | 0.564 | 2740 | 0.564 | 0.858 | 1 | -0.0181
CFLBldgPGESCnNewCZ02 | Com-Iltg-dWatt-CFL_OSbldg | PGE | SCn | New | CZ02 | 2.74 | 0.000564 | 0 | 2.62 | 0.000683 | -0.0259 | 2.74 | 0.000564 | 0 | 2.62 | 0.000683 | -0.0259 |  | CFL | Bldg | 2740 | 0.564 | 2740 | 0.564 | 0.956 | 1.21 | -0.0094526 | 2740 | 0.564 | 2740 | 0.564 | 0.956 | 1.21 | -0.00945
CFLBldgPGESCnNewCZ03 | Com-Iltg-dWatt-CFL_OSbldg | PGE | SCn | New | CZ03 | 2.74 | 0.000564 | 0 | 2.54 | 0.000705 | -0.0291 | 2.74 | 0.000564 | 0 | 2.54 | 0.000705 | -0.0291 |  | CFL | Bldg | 2740 | 0.564 | 2740 | 0.564 | 0.927 | 1.25 | -0.01062 | 2740 | 0.564 | 2740 | 0.564 | 0.927 | 1.25 | -0.0106
CFLBldgPGESCnNewCZ04 | Com-Iltg-dWatt-CFL_OSbldg | PGE | SCn | New | CZ04 | 2.74 | 0.000564 | 0 | 2.68 | 0.000677 | -0.0231 | 2.74 | 0.000564 | 0 | 2.68 | 0.000677 | -0.0231 |  | CFL | Bldg | 2740 | 0.564 | 2740 | 0.564 | 0.978 | 1.2 | -0.0084307 | 2740 | 0.564 | 2740 | 0.564 | 0.978 | 1.2 | -0.00843
CFLBldgPGESCnNewCZ05 | Com-Iltg-dWatt-CFL_OSbldg | PGE | SCn | New | CZ05 | 2.74 | 0.000564 | 0 | 2.52 | 0.000674 | -0.0294 | 2.74 | 0.000564 | 0 | 2.52 | 0.000674 | -0.0294 |  | CFL | Bldg | 2740 | 0.564 | 2740 | 0.564 | 0.92 | 1.2 | -0.01073 | 2740 | 0.564 | 2740 | 0.564 | 0.92 | 1.2 | -0.0107
CFLBldgPGESCnNewCZ11 | Com-Iltg-dWatt-CFL_OSbldg | PGE | SCn | New | CZ11 | 2.74 | 0.000564 | 0 | 2.68 | 0.00067 | -0.0237 | 2.74 | 0.000564 | 0 | 2.68 | 0.00067 | -0.0237 |  | CFL | Bldg | 2740 | 0.564 | 2740 | 0.564 | 0.978 | 1.19 | -0.0086496 | 2740 | 0.564 | 2740 | 0.564 | 0.978 | 1.19 | -0.00865
CFLBldgPGESCnNewCZ12 | Com-Iltg-dWatt-CFL_OSbldg | PGE | SCn | New | CZ12 | 2.74 | 0.000564 | 0 | 2.68 | 0.000673 | -0.024 | 2.74 | 0.000564 | 0 | 2.68 | 0.000673 | -0.024 |  | CFL | Bldg | 2740 | 0.564 | 2740 | 0.564 | 0.978 | 1.19 | -0.0087591 | 2740 | 0.564 | 2740 | 0.564 | 0.978 | 1.19 | -0.00876
CFLBldgPGESCnNewCZ13 | Com-Iltg-dWatt-CFL_OSbldg | PGE | SCn | New | CZ13 | 2.74 | 0.000564 | 0 | 2.67 | 0.000656 | -0.0208 | 2.74 | 0.000564 | 0 | 2.67 | 0.000656 | -0.0208 |  | CFL | Bldg | 2740 | 0.564 | 2740 | 0.564 | 0.974 | 1.16 | -0.0075912 | 2740 | 0.564 | 2740 | 0.564 | 0.974 | 1.16 | -0.00759
CFLBldgPGESCnNewCZ16 | Com-Iltg-dWatt-CFL_OSbldg | PGE | SCn | New | CZ16 | 2.74 | 0.000564 | 0 | 2.43 | 0.000651 | -0.0338 | 2.74 | 0.000564 | 0 | 2.43 | 0.000651 | -0.0338 |  | CFL | Bldg | 2740 | 0.564 | 2740 | 0.564 | 0.887 | 1.15 | -0.012336 | 2740 | 0.564 | 2740 | 0.564 | 0.887 | 1.15 | -0.0123
CFLBldgPGESCnNewIOU | Com-Iltg-dWatt-CFL_OSbldg | PGE | SCn | New | IOU | 2.74 | 0.000564 | 0 | 2.6364 | 0.00067663 | -0.024869 | 2.74 | 0.000564 | 0 | 2.6364 | 0.00067663 | -0.024869 |  | CFL | Bldg | 2740 | 0.564 | 2740 | 0.564 | 0.962 | 1.2 | -0.0090763 | 2740 | 0.564 | 2740 | 0.564 | 0.962 | 1.2 | -0.00908
CFLBldgPGESUnExCZ01 | Com-Iltg-dWatt-CFL_OSbldg | PGE | SUn | Ex | CZ01 | 2.7587 | 0.00057427 | 0 | 2.7587 | 0.00057427 | 0 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 |  | CFL | Bldg | 2760 | 0.574 | 2740 | 0.564 | 1 | 1 | 0 | 2760 | 0.574 | 2740 | 0.564 | 1 | 1 | 0
CFLBldgPGESUnExCZ02 | Com-Iltg-dWatt-CFL_OSbldg | PGE | SUn | Ex | CZ02 | 2.759 | 0.00057444 | 0 | 2.759 | 0.00057444 | 0 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 |  | CFL | Bldg | 2760 | 0.574 | 2740 | 0.564 | 1 | 1 | 0 | 2760 | 0.574 | 2740 | 0.564 | 1 | 1 | 0
CFLBldgPGESUnExCZ03 | Com-Iltg-dWatt-CFL_OSbldg | PGE | SUn | Ex | CZ03 | 2.759 | 0.00057445 | 0 | 2.759 | 0.00057445 | 0 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 |  | CFL | Bldg | 2760 | 0.574 | 2740 | 0.564 | 1 | 1 | 0 | 2760 | 0.574 | 2740 | 0.564 | 1 | 1 | 0
CFLBldgPGESUnExCZ04 | Com-Iltg-dWatt-CFL_OSbldg | PGE | SUn | Ex | CZ04 | 2.759 | 0.00057445 | 0 | 2.759 | 0.00057445 | 0 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 |  | CFL | Bldg | 2760 | 0.574 | 2740 | 0.564 | 1 | 1 | 0 | 2760 | 0.574 | 2740 | 0.564 | 1 | 1 | 0
CFLBldgPGESUnExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | PGE | SUn | Ex | CZ05 | 2.759 | 0.00057445 | 0 | 2.759 | 0.00057445 | 0 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 |  | CFL | Bldg | 2760 | 0.574 | 2740 | 0.564 | 1 | 1 | 0 | 2760 | 0.574 | 2740 | 0.564 | 1 | 1 | 0
CFLBldgPGESUnExCZ11 | Com-Iltg-dWatt-CFL_OSbldg | PGE | SUn | Ex | CZ11 | 2.758 | 0.00057388 | 0 | 2.758 | 0.00057388 | 0 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 |  | CFL | Bldg | 2760 | 0.574 | 2740 | 0.564 | 1 | 1 | 0 | 2760 | 0.574 | 2740 | 0.564 | 1 | 1 | 0
CFLBldgPGESUnExCZ12 | Com-Iltg-dWatt-CFL_OSbldg | PGE | SUn | Ex | CZ12 | 2.7581 | 0.00057394 | 0 | 2.7581 | 0.00057394 | 0 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 |  | CFL | Bldg | 2760 | 0.574 | 2740 | 0.564 | 1 | 1 | 0 | 2760 | 0.574 | 2740 | 0.564 | 1 | 1 | 0
CFLBldgPGESUnExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | PGE | SUn | Ex | CZ13 | 2.7581 | 0.00057396 | 0 | 2.7581 | 0.00057396 | 0 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 |  | CFL | Bldg | 2760 | 0.574 | 2740 | 0.564 | 1 | 1 | 0 | 2760 | 0.574 | 2740 | 0.564 | 1 | 1 | 0
CFLBldgPGESUnExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | PGE | SUn | Ex | CZ16 | 2.7582 | 0.00057398 | 0 | 2.7582 | 0.00057398 | 0 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 |  | CFL | Bldg | 2760 | 0.574 | 2740 | 0.564 | 1 | 1 | 0 | 2760 | 0.574 | 2740 | 0.564 | 1 | 1 | 0
CFLBldgPGESUnExIOU | Com-Iltg-dWatt-CFL_OSbldg | PGE | SUn | Ex | IOU | 2.7586 | 0.00057422 | 0 | 2.7586 | 0.00057422 | 0 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 |  | CFL | Bldg | 2760 | 0.574 | 2740 | 0.564 | 1 | 1 | 0 | 2760 | 0.574 | 2740 | 0.564 | 1 | 1 | 0
CFLBldgPGESUnNewCZ01 | Com-Iltg-dWatt-CFL_OSbldg | PGE | SUn | New | CZ01 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 |  | CFL | Bldg | 2740 | 0.564 | 2740 | 0.564 | 1 | 1 | 0 | 2740 | 0.564 | 2740 | 0.564 | 1 | 1 | 0
CFLBldgPGESUnNewCZ02 | Com-Iltg-dWatt-CFL_OSbldg | PGE | SUn | New | CZ02 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 |  | CFL | Bldg | 2740 | 0.564 | 2740 | 0.564 | 1 | 1 | 0 | 2740 | 0.564 | 2740 | 0.564 | 1 | 1 | 0
CFLBldgPGESUnNewCZ03 | Com-Iltg-dWatt-CFL_OSbldg | PGE | SUn | New | CZ03 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 |  | CFL | Bldg | 2740 | 0.564 | 2740 | 0.564 | 1 | 1 | 0 | 2740 | 0.564 | 2740 | 0.564 | 1 | 1 | 0
CFLBldgPGESUnNewCZ04 | Com-Iltg-dWatt-CFL_OSbldg | PGE | SUn | New | CZ04 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 |  | CFL | Bldg | 2740 | 0.564 | 2740 | 0.564 | 1 | 1 | 0 | 2740 | 0.564 | 2740 | 0.564 | 1 | 1 | 0
CFLBldgPGESUnNewCZ05 | Com-Iltg-dWatt-CFL_OSbldg | PGE | SUn | New | CZ05 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 |  | CFL | Bldg | 2740 | 0.564 | 2740 | 0.564 | 1 | 1 | 0 | 2740 | 0.564 | 2740 | 0.564 | 1 | 1 | 0
CFLBldgPGESUnNewCZ11 | Com-Iltg-dWatt-CFL_OSbldg | PGE | SUn | New | CZ11 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 |  | CFL | Bldg | 2740 | 0.564 | 2740 | 0.564 | 1 | 1 | 0 | 2740 | 0.564 | 2740 | 0.564 | 1 | 1 | 0
CFLBldgPGESUnNewCZ12 | Com-Iltg-dWatt-CFL_OSbldg | PGE | SUn | New | CZ12 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 |  | CFL | Bldg | 2740 | 0.564 | 2740 | 0.564 | 1 | 1 | 0 | 2740 | 0.564 | 2740 | 0.564 | 1 | 1 | 0
CFLBldgPGESUnNewCZ13 | Com-Iltg-dWatt-CFL_OSbldg | PGE | SUn | New | CZ13 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 |  | CFL | Bldg | 2740 | 0.564 | 2740 | 0.564 | 1 | 1 | 0 | 2740 | 0.564 | 2740 | 0.564 | 1 | 1 | 0
CFLBldgPGESUnNewCZ16 | Com-Iltg-dWatt-CFL_OSbldg | PGE | SUn | New | CZ16 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 |  | CFL | Bldg | 2740 | 0.564 | 2740 | 0.564 | 1 | 1 | 0 | 2740 | 0.564 | 2740 | 0.564 | 1 | 1 | 0
CFLBldgPGESUnNewIOU | Com-Iltg-dWatt-CFL_OSbldg | PGE | SUn | New | IOU | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 |  | CFL | Bldg | 2740 | 0.564 | 2740 | 0.564 | 1 | 1 | 0 | 2740 | 0.564 | 2740 | 0.564 | 1 | 1 | 0
CFLBldgPGEWRfExCZ01 | Com-Iltg-dWatt-CFL_OSbldg | PGE | WRf | Ex | CZ01 | 4.7254 | 0.00054728 | 0 | 7.5528 | 0.00077195 | 0 | 4.66 | 0.00053607 | 0 | 7.45 | 0.00075607 | 0 |  | CFL | Bldg | 4730 | 0.547 | 4660 | 0.536 | 1.6 | 1.41 | 0 | 4730 | 0.547 | 4660 | 0.536 | 1.6 | 1.41 | 0
CFLBldgPGEWRfExCZ02 | Com-Iltg-dWatt-CFL_OSbldg | PGE | WRf | Ex | CZ02 | 4.7261 | 0.00054739 | 0 | 7.6639 | 0.00069517 | 0 | 4.66 | 0.00053606 | 0 | 7.56 | 0.000681 | 0 |  | CFL | Bldg | 4730 | 0.547 | 4660 | 0.536 | 1.62 | 1.27 | 0 | 4730 | 0.547 | 4660 | 0.536 | 1.62 | 1.27 | 0
CFLBldgPGEWRfExCZ03 | Com-Iltg-dWatt-CFL_OSbldg | PGE | WRf | Ex | CZ03 | 4.7262 | 0.0005474 | 0 | 7.644 | 0.00072419 | 0 | 4.66 | 0.00053605 | 0 | 7.54 | 0.00070905 | 0 |  | CFL | Bldg | 4730 | 0.547 | 4660 | 0.536 | 1.62 | 1.32 | 0 | 4730 | 0.547 | 4660 | 0.536 | 1.62 | 1.32 | 0
CFLBldgPGEWRfExCZ04 | Com-Iltg-dWatt-CFL_OSbldg | PGE | WRf | Ex | CZ04 | 4.7263 | 0.00054742 | 0 | 7.6642 | 0.0006992 | 0 | 4.66 | 0.00053605 | 0 | 7.5505 | 0.000685 | 0 |  | CFL | Bldg | 4730 | 0.547 | 4660 | 0.536 | 1.62 | 1.28 | 0 | 4730 | 0.547 | 4660 | 0.536 | 1.62 | 1.28 | 0
CFLBldgPGEWRfExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | PGE | WRf | Ex | CZ05 | 4.7263 | 0.00054741 | 0 | 7.5047 | 0.0007202 | 0 | 4.66 | 0.00053605 | 0 | 7.4005 | 0.000706 | 0 |  | CFL | Bldg | 4730 | 0.547 | 4660 | 0.536 | 1.59 | 1.32 | 0 | 4730 | 0.547 | 4660 | 0.536 | 1.59 | 1.32 | 0
CFLBldgPGEWRfExCZ11 | Com-Iltg-dWatt-CFL_OSbldg | PGE | WRf | Ex | CZ11 | 4.723 | 0.0005469 | 0 | 7.619 | 0.0007155 | 0 | 4.66 | 0.0005361 | 0 | 7.52 | 0.0007011 | 0 |  | CFL | Bldg | 4720 | 0.547 | 4660 | 0.536 | 1.61 | 1.31 | 0 | 4720 | 0.547 | 4660 | 0.536 | 1.61 | 1.31 | 0
CFLBldgPGEWRfExCZ12 | Com-Iltg-dWatt-CFL_OSbldg | PGE | WRf | Ex | CZ12 | 4.7213 | 0.00054663 | 0 | 7.5763 | 0.00070113 | 0 | 4.66 | 0.00053612 | 0 | 7.4712 | 0.00068712 | 0 |  | CFL | Bldg | 4720 | 0.547 | 4660 | 0.536 | 1.6 | 1.28 | 0 | 4720 | 0.547 | 4660 | 0.536 | 1.6 | 1.28 | 0
CFLBldgPGEWRfExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | PGE | WRf | Ex | CZ13 | 4.7236 | 0.00054699 | 0 | 7.6799 | 0.00069062 | 0 | 4.66 | 0.00053609 | 0 | 7.58 | 0.000677 | 0 |  | CFL | Bldg | 4720 | 0.547 | 4660 | 0.536 | 1.63 | 1.26 | 0 | 4720 | 0.547 | 4660 | 0.536 | 1.63 | 1.26 | 0
CFLBldgPGEWRfExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | PGE | WRf | Ex | CZ16 | 4.7231 | 0.00054692 | 0 | 6.9012 | 0.00075152 | 0 | 4.66 | 0.0005361 | 0 | 6.811 | 0.0007371 | 0 |  | CFL | Bldg | 4720 | 0.547 | 4660 | 0.536 | 1.46 | 1.37 | 0 | 4720 | 0.547 | 4660 | 0.536 | 1.46 | 1.37 | 0
CFLBldgPGEWRfExIOU | Com-Iltg-dWatt-CFL_OSbldg | PGE | WRf | Ex | IOU | 4.7243 | 0.00054711 | 0 | 7.636 | 0.00070726 | 0 | 4.66 | 0.00053608 | 0 | 7.5326 | 0.00069294 | 0 |  | CFL | Bldg | 4720 | 0.547 | 4660 | 0.536 | 1.62 | 1.29 | 0 | 4720 | 0.547 | 4660 | 0.536 | 1.62 | 1.29 | 0
CFLBldgPGEWRfNewCZ01 | Com-Iltg-dWatt-CFL_OSbldg | PGE | WRf | New | CZ01 | 4.66 | 0.000537 | 0 | 6.19 | 0.00107 | 0 | 4.66 | 0.000537 | 0 | 6.19 | 0.00107 | 0 |  | CFL | Bldg | 4660 | 0.537 | 4660 | 0.537 | 1.33 | 1.99 | 0 | 4660 | 0.537 | 4660 | 0.537 | 1.33 | 1.99 | 0
CFLBldgPGEWRfNewCZ02 | Com-Iltg-dWatt-CFL_OSbldg | PGE | WRf | New | CZ02 | 4.66 | 0.000537 | 0 | 6.55 | 0.000725 | 0 | 4.66 | 0.000537 | 0 | 6.55 | 0.000725 | 0 |  | CFL | Bldg | 4660 | 0.537 | 4660 | 0.537 | 1.41 | 1.35 | 0 | 4660 | 0.537 | 4660 | 0.537 | 1.41 | 1.35 | 0
CFLBldgPGEWRfNewCZ03 | Com-Iltg-dWatt-CFL_OSbldg | PGE | WRf | New | CZ03 | 4.66 | 0.000537 | 0 | 6.62 | 0.00107 | 0 | 4.66 | 0.000537 | 0 | 6.62 | 0.00107 | 0 |  | CFL | Bldg | 4660 | 0.537 | 4660 | 0.537 | 1.42 | 1.99 | 0 | 4660 | 0.537 | 4660 | 0.537 | 1.42 | 1.99 | 0
CFLBldgPGEWRfNewCZ04 | Com-Iltg-dWatt-CFL_OSbldg | PGE | WRf | New | CZ04 | 4.66 | 0.000537 | 0 | 6.74 | 0.000787 | 0 | 4.66 | 0.000537 | 0 | 6.74 | 0.000787 | 0 |  | CFL | Bldg | 4660 | 0.537 | 4660 | 0.537 | 1.45 | 1.47 | 0 | 4660 | 0.537 | 4660 | 0.537 | 1.45 | 1.47 | 0
CFLBldgPGEWRfNewCZ05 | Com-Iltg-dWatt-CFL_OSbldg | PGE | WRf | New | CZ05 | 4.66 | 0.000537 | 0 | 6.56 | 0.00107 | 0 | 4.66 | 0.000537 | 0 | 6.56 | 0.00107 | 0 |  | CFL | Bldg | 4660 | 0.537 | 4660 | 0.537 | 1.41 | 1.99 | 0 | 4660 | 0.537 | 4660 | 0.537 | 1.41 | 1.99 | 0
CFLBldgPGEWRfNewCZ11 | Com-Iltg-dWatt-CFL_OSbldg | PGE | WRf | New | CZ11 | 4.66 | 0.000537 | 0 | 6.72 | 0.000847 | 0 | 4.66 | 0.000537 | 0 | 6.72 | 0.000847 | 0 |  | CFL | Bldg | 4660 | 0.537 | 4660 | 0.537 | 1.44 | 1.58 | 0 | 4660 | 0.537 | 4660 | 0.537 | 1.44 | 1.58 | 0
CFLBldgPGEWRfNewCZ12 | Com-Iltg-dWatt-CFL_OSbldg | PGE | WRf | New | CZ12 | 4.66 | 0.000537 | 0 | 6.69 | 0.000734 | 0 | 4.66 | 0.000537 | 0 | 6.69 | 0.000734 | 0 |  | CFL | Bldg | 4660 | 0.537 | 4660 | 0.537 | 1.44 | 1.37 | 0 | 4660 | 0.537 | 4660 | 0.537 | 1.44 | 1.37 | 0
CFLBldgPGEWRfNewCZ13 | Com-Iltg-dWatt-CFL_OSbldg | PGE | WRf | New | CZ13 | 4.66 | 0.000537 | 0 | 6.84 | 0.000671 | 0 | 4.66 | 0.000537 | 0 | 6.84 | 0.000671 | 0 |  | CFL | Bldg | 4660 | 0.537 | 4660 | 0.537 | 1.47 | 1.25 | 0 | 4660 | 0.537 | 4660 | 0.537 | 1.47 | 1.25 | 0
CFLBldgPGEWRfNewCZ16 | Com-Iltg-dWatt-CFL_OSbldg | PGE | WRf | New | CZ16 | 4.66 | 0.000537 | 0 | 6.14 | 0.00107 | 0 | 4.66 | 0.000537 | 0 | 6.14 | 0.00107 | 0 |  | CFL | Bldg | 4660 | 0.537 | 4660 | 0.537 | 1.32 | 1.99 | 0 | 4660 | 0.537 | 4660 | 0.537 | 1.32 | 1.99 | 0
CFLBldgPGEWRfNewIOU | Com-Iltg-dWatt-CFL_OSbldg | PGE | WRf | New | IOU | 4.66 | 0.000537 | 0 | 6.7195 | 0.00080384 | 0 | 4.66 | 0.000537 | 0 | 6.7195 | 0.00080384 | 0 |  | CFL | Bldg | 4660 | 0.537 | 4660 | 0.537 | 1.44 | 1.5 | 0 | 4660 | 0.537 | 4660 | 0.537 | 1.44 | 1.5 | 0
CFLBldgSCEAsmExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Asm | Ex | CZ05 | 2.2977 | 0.0004086 | 0 | 2.4077 | 0.00048954 | -0.022377 | 2.2506 | 0.00040012 | 0 | 2.3606 | 0.00048012 | -0.021906 |  | CFL | Bldg | 2300 | 0.409 | 2250 | 0.4 | 1.05 | 1.2 | -0.0097334 | 2300 | 0.409 | 2250 | 0.4 | 1.05 | 1.2 | -0.00973
CFLBldgSCEAsmExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Asm | Ex | CZ06 | 2.2977 | 0.0004086 | 0 | 2.5671 | 0.00050949 | -0.010594 | 2.2506 | 0.00040011 | 0 | 2.52 | 0.00049911 | -0.010406 |  | CFL | Bldg | 2300 | 0.409 | 2250 | 0.4 | 1.12 | 1.25 | -0.0046236 | 2300 | 0.409 | 2250 | 0.4 | 1.12 | 1.25 | -0.00462
CFLBldgSCEAsmExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Asm | Ex | CZ08 | 2.2977 | 0.0004086 | 0 | 2.5772 | 0.00049549 | -0.0096009 | 2.2506 | 0.00040011 | 0 | 2.53 | 0.00048606 | -0.0094217 |  | CFL | Bldg | 2300 | 0.409 | 2250 | 0.4 | 1.12 | 1.21 | -0.0041864 | 2300 | 0.409 | 2250 | 0.4 | 1.12 | 1.21 | -0.00419
CFLBldgSCEAsmExCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Asm | Ex | CZ09 | 2.2978 | 0.00040861 | 0 | 2.5578 | 0.0005075 | -0.011489 | 2.2506 | 0.00040011 | 0 | 2.5106 | 0.00049711 | -0.011205 |  | CFL | Bldg | 2300 | 0.409 | 2250 | 0.4 | 1.12 | 1.24 | -0.004979 | 2300 | 0.409 | 2250 | 0.4 | 1.12 | 1.24 | -0.00498
CFLBldgSCEAsmExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Asm | Ex | CZ10 | 2.2944 | 0.00040802 | 0 | 2.4844 | 0.00048974 | -0.012672 | 2.2514 | 0.00040028 | 0 | 2.4414 | 0.00048114 | -0.012414 |  | CFL | Bldg | 2290 | 0.408 | 2250 | 0.4 | 1.08 | 1.2 | -0.0055139 | 2290 | 0.408 | 2250 | 0.4 | 1.08 | 1.2 | -0.00551
CFLBldgSCEAsmExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Asm | Ex | CZ13 | 2.2965 | 0.00040838 | 0 | 2.4665 | 0.00049521 | -0.019765 | 2.2509 | 0.00040018 | 0 | 2.4209 | 0.00048518 | -0.0194 |  | CFL | Bldg | 2300 | 0.408 | 2250 | 0.4 | 1.08 | 1.21 | -0.0086189 | 2300 | 0.408 | 2250 | 0.4 | 1.08 | 1.21 | -0.00862
CFLBldgSCEAsmExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Asm | Ex | CZ14 | 2.2959 | 0.00040827 | 0 | 2.4559 | 0.00046307 | -0.019559 | 2.251 | 0.00040021 | 0 | 2.411 | 0.0004541 | -0.0192 |  | CFL | Bldg | 2300 | 0.408 | 2250 | 0.4 | 1.07 | 1.13 | -0.0085294 | 2300 | 0.408 | 2250 | 0.4 | 1.07 | 1.13 | -0.00853
CFLBldgSCEAsmExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Asm | Ex | CZ15 | 2.2944 | 0.00040802 | 0 | 2.813 | 0.00047788 | -0.0055974 | 2.2514 | 0.00040028 | 0 | 2.77 | 0.00046928 | -0.0055028 |  | CFL | Bldg | 2290 | 0.408 | 2250 | 0.4 | 1.23 | 1.17 | -0.0024442 | 2290 | 0.408 | 2250 | 0.4 | 1.23 | 1.17 | -0.00244
CFLBldgSCEAsmExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Asm | Ex | CZ16 | 2.2956 | 0.00040823 | 0 | 2.2656 | 0.00048601 | -0.030745 | 2.2511 | 0.00040022 | 0 | 2.2211 | 0.00047711 | -0.030211 |  | CFL | Bldg | 2300 | 0.408 | 2250 | 0.4 | 0.987 | 1.19 | -0.013421 | 2300 | 0.408 | 2250 | 0.4 | 0.987 | 1.19 | -0.0134
CFLBldgSCEAsmExIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | Asm | Ex | IOU | 2.2968 | 0.00040845 | 0 | 2.5565 | 0.0004969 | -0.011471 | 2.2508 | 0.00040016 | 0 | 2.5104 | 0.00048732 | -0.011246 |  | CFL | Bldg | 2300 | 0.408 | 2250 | 0.4 | 1.12 | 1.22 | -0.0049965 | 2300 | 0.408 | 2250 | 0.4 | 1.12 | 1.22 | -0.005
CFLBldgSCEAsmNewCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Asm | New | CZ05 | 2.26 | 0.000402 | 0 | 2.34 | 0.000474 | -0.0223 | 2.26 | 0.000402 | 0 | 2.34 | 0.000474 | -0.0223 |  | CFL | Bldg | 2260 | 0.402 | 2260 | 0.402 | 1.04 | 1.18 | -0.0098673 | 2260 | 0.402 | 2260 | 0.402 | 1.04 | 1.18 | -0.00987
CFLBldgSCEAsmNewCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Asm | New | CZ06 | 2.26 | 0.000402 | 0 | 2.44 | 0.000492 | -0.0142 | 2.26 | 0.000402 | 0 | 2.44 | 0.000492 | -0.0142 |  | CFL | Bldg | 2260 | 0.402 | 2260 | 0.402 | 1.08 | 1.22 | -0.0062832 | 2260 | 0.402 | 2260 | 0.402 | 1.08 | 1.22 | -0.00628
CFLBldgSCEAsmNewCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Asm | New | CZ08 | 2.26 | 0.000402 | 0 | 2.47 | 0.000486 | -0.011 | 2.26 | 0.000402 | 0 | 2.47 | 0.000486 | -0.011 |  | CFL | Bldg | 2260 | 0.402 | 2260 | 0.402 | 1.09 | 1.21 | -0.0048673 | 2260 | 0.402 | 2260 | 0.402 | 1.09 | 1.21 | -0.00487
CFLBldgSCEAsmNewCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Asm | New | CZ09 | 2.26 | 0.000402 | 0 | 2.46 | 0.000513 | -0.0132 | 2.26 | 0.000402 | 0 | 2.46 | 0.000513 | -0.0132 |  | CFL | Bldg | 2260 | 0.402 | 2260 | 0.402 | 1.09 | 1.28 | -0.0058407 | 2260 | 0.402 | 2260 | 0.402 | 1.09 | 1.28 | -0.00584
CFLBldgSCEAsmNewCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Asm | New | CZ10 | 2.26 | 0.000402 | 0 | 2.45 | 0.000497 | -0.0131 | 2.26 | 0.000402 | 0 | 2.45 | 0.000497 | -0.0131 |  | CFL | Bldg | 2260 | 0.402 | 2260 | 0.402 | 1.08 | 1.24 | -0.0057965 | 2260 | 0.402 | 2260 | 0.402 | 1.08 | 1.24 | -0.0058
CFLBldgSCEAsmNewCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Asm | New | CZ13 | 2.26 | 0.000402 | 0 | 2.41 | 0.000501 | -0.0207 | 2.26 | 0.000402 | 0 | 2.41 | 0.000501 | -0.0207 |  | CFL | Bldg | 2260 | 0.402 | 2260 | 0.402 | 1.07 | 1.25 | -0.0091593 | 2260 | 0.402 | 2260 | 0.402 | 1.07 | 1.25 | -0.00916
CFLBldgSCEAsmNewCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Asm | New | CZ14 | 2.26 | 0.000402 | 0 | 2.4 | 0.000478 | -0.0203 | 2.26 | 0.000402 | 0 | 2.4 | 0.000478 | -0.0203 |  | CFL | Bldg | 2260 | 0.402 | 2260 | 0.402 | 1.06 | 1.19 | -0.0089823 | 2260 | 0.402 | 2260 | 0.402 | 1.06 | 1.19 | -0.00898
CFLBldgSCEAsmNewCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Asm | New | CZ15 | 2.26 | 0.000402 | 0 | 2.7 | 0.0005 | -0.00629 | 2.26 | 0.000402 | 0 | 2.7 | 0.0005 | -0.00629 |  | CFL | Bldg | 2260 | 0.402 | 2260 | 0.402 | 1.19 | 1.24 | -0.0027832 | 2260 | 0.402 | 2260 | 0.402 | 1.19 | 1.24 | -0.00278
CFLBldgSCEAsmNewCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Asm | New | CZ16 | 2.26 | 0.000402 | 0 | 2.24 | 0.000479 | -0.0301 | 2.26 | 0.000402 | 0 | 2.24 | 0.000479 | -0.0301 |  | CFL | Bldg | 2260 | 0.402 | 2260 | 0.402 | 0.991 | 1.19 | -0.013319 | 2260 | 0.402 | 2260 | 0.402 | 0.991 | 1.19 | -0.0133
CFLBldgSCEAsmNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | Asm | New | IOU | 2.26 | 0.000402 | 0 | 2.4713 | 0.00049425 | -0.013156 | 2.26 | 0.000402 | 0 | 2.4713 | 0.00049425 | -0.013156 |  | CFL | Bldg | 2260 | 0.402 | 2260 | 0.402 | 1.09 | 1.23 | -0.0058215 | 2260 | 0.402 | 2260 | 0.402 | 1.09 | 1.23 | -0.00582
CFLBldgSCEComExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Com | Ex | CZ05 | 3.429 | 0.00062958 | 0 | 3.6665 | 0.00078283 | -0.027038 | 3.3798 | 0.00061568 | 0 | 3.615 | 0.00076502 | -0.026667 |  | CFL | Bldg | 3430 | 0.63 | 3380 | 0.616 | 1.07 | 1.24 | -0.0078901 | 3430 | 0.63 | 3380 | 0.616 | 1.07 | 1.24 | -0.00789
CFLBldgSCEComExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Com | Ex | CZ06 | 3.0892 | 0.0006152 | 0 | 3.4785 | 0.00077279 | -0.011699 | 3.0279 | 0.00059425 | 0 | 3.4096 | 0.00074564 | -0.011465 |  | CFL | Bldg | 3090 | 0.615 | 3030 | 0.594 | 1.13 | 1.25 | -0.0037864 | 3090 | 0.615 | 3030 | 0.594 | 1.13 | 1.25 | -0.00379
CFLBldgSCEComExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Com | Ex | CZ08 | 3.0441 | 0.00062371 | 0 | 3.4178 | 0.0007801 | -0.010315 | 2.9808 | 0.00060074 | 0 | 3.3462 | 0.00075043 | -0.010084 |  | CFL | Bldg | 3040 | 0.624 | 2980 | 0.601 | 1.12 | 1.25 | -0.003383 | 3040 | 0.624 | 2980 | 0.601 | 1.12 | 1.25 | -0.00338
CFLBldgSCEComExCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Com | Ex | CZ09 | 3.0828 | 0.00062386 | 0 | 3.4699 | 0.00079683 | -0.012223 | 3.0144 | 0.00060062 | 0 | 3.3928 | 0.00076644 | -0.011926 |  | CFL | Bldg | 3080 | 0.624 | 3010 | 0.601 | 1.13 | 1.28 | -0.0039564 | 3080 | 0.624 | 3010 | 0.601 | 1.13 | 1.28 | -0.00396
CFLBldgSCEComExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Com | Ex | CZ10 | 3.1395 | 0.00062891 | 0 | 3.4243 | 0.00077732 | -0.01193 | 3.0886 | 0.00060965 | 0 | 3.3677 | 0.00075288 | -0.011733 |  | CFL | Bldg | 3140 | 0.629 | 3090 | 0.61 | 1.09 | 1.23 | -0.0037987 | 3140 | 0.629 | 3090 | 0.61 | 1.09 | 1.23 | -0.0038
CFLBldgSCEComExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Com | Ex | CZ13 | 3.1983 | 0.00053606 | 0 | 3.5858 | 0.00066916 | -0.018563 | 3.1316 | 0.00052127 | 0 | 3.5133 | 0.00065048 | -0.018172 |  | CFL | Bldg | 3200 | 0.536 | 3130 | 0.521 | 1.12 | 1.25 | -0.0058029 | 3200 | 0.536 | 3130 | 0.521 | 1.12 | 1.25 | -0.0058
CFLBldgSCEComExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Com | Ex | CZ14 | 3.1461 | 0.00063588 | 0 | 3.4143 | 0.0008014 | -0.020558 | 3.0888 | 0.00061373 | 0 | 3.3523 | 0.00077305 | -0.020197 |  | CFL | Bldg | 3150 | 0.636 | 3090 | 0.614 | 1.09 | 1.26 | -0.006539 | 3150 | 0.636 | 3090 | 0.614 | 1.09 | 1.26 | -0.00654
CFLBldgSCEComExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Com | Ex | CZ15 | 2.8843 | 0.00057946 | 0 | 3.4053 | 0.00073027 | -0.0048833 | 2.8297 | 0.00056173 | 0 | 3.3424 | 0.00070765 | -0.0047933 |  | CFL | Bldg | 2880 | 0.579 | 2830 | 0.562 | 1.18 | 1.26 | -0.0016939 | 2880 | 0.579 | 2830 | 0.562 | 1.18 | 1.26 | -0.00169
CFLBldgSCEComExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Com | Ex | CZ16 | 2.8328 | 0.00049792 | 0 | 2.8518 | 0.00060402 | -0.032074 | 2.7663 | 0.00048115 | 0 | 2.7861 | 0.00058341 | -0.031309 |  | CFL | Bldg | 2830 | 0.498 | 2770 | 0.481 | 1.01 | 1.21 | -0.011318 | 2830 | 0.498 | 2770 | 0.481 | 1.01 | 1.21 | -0.0113
CFLBldgSCEComExIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | Com | Ex | IOU | 3.0767 | 0.00061735 | 0 | 3.4349 | 0.00077366 | -0.011967 | 3.0158 | 0.00059604 | 0 | 3.3666 | 0.00074618 | -0.01172 |  | CFL | Bldg | 3080 | 0.617 | 3020 | 0.596 | 1.12 | 1.25 | -0.0038862 | 3080 | 0.617 | 3020 | 0.596 | 1.12 | 1.25 | -0.00389
CFLBldgSCEComNewCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Com | New | CZ05 | 3.4962 | 0.00062924 | 0 | 3.608 | 0.00076949 | -0.02854 | 3.4962 | 0.00062924 | 0 | 3.608 | 0.00076949 | -0.02854 |  | CFL | Bldg | 3500 | 0.629 | 3500 | 0.629 | 1.03 | 1.22 | -0.0081632 | 3500 | 0.629 | 3500 | 0.629 | 1.03 | 1.22 | -0.00816
CFLBldgSCEComNewCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Com | New | CZ06 | 3.1615 | 0.00060693 | 0 | 3.4575 | 0.00074508 | -0.011936 | 3.1615 | 0.00060693 | 0 | 3.4575 | 0.00074508 | -0.011936 |  | CFL | Bldg | 3160 | 0.607 | 3160 | 0.607 | 1.09 | 1.23 | -0.0037755 | 3160 | 0.607 | 3160 | 0.607 | 1.09 | 1.23 | -0.00378
CFLBldgSCEComNewCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Com | New | CZ08 | 3.0857 | 0.00060809 | 0 | 3.3694 | 0.00074069 | -0.0099532 | 3.0857 | 0.00060809 | 0 | 3.3694 | 0.00074069 | -0.0099532 |  | CFL | Bldg | 3090 | 0.608 | 3090 | 0.608 | 1.09 | 1.22 | -0.0032255 | 3090 | 0.608 | 3090 | 0.608 | 1.09 | 1.22 | -0.00323
CFLBldgSCEComNewCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Com | New | CZ09 | 3.1111 | 0.0006039 | 0 | 3.4283 | 0.00077408 | -0.011251 | 3.1111 | 0.0006039 | 0 | 3.4283 | 0.00077408 | -0.011251 |  | CFL | Bldg | 3110 | 0.604 | 3110 | 0.604 | 1.1 | 1.28 | -0.0036164 | 3110 | 0.604 | 3110 | 0.604 | 1.1 | 1.28 | -0.00362
CFLBldgSCEComNewCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Com | New | CZ10 | 3.0273 | 0.00060175 | 0 | 3.2541 | 0.00074435 | -0.010862 | 3.0273 | 0.00060175 | 0 | 3.2541 | 0.00074435 | -0.010862 |  | CFL | Bldg | 3030 | 0.602 | 3030 | 0.602 | 1.07 | 1.24 | -0.0035881 | 3030 | 0.602 | 3030 | 0.602 | 1.07 | 1.24 | -0.00359
CFLBldgSCEComNewCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Com | New | CZ13 | 3.2027 | 0.00054101 | 0 | 3.5794 | 0.00068144 | -0.017976 | 3.2027 | 0.00054101 | 0 | 3.5794 | 0.00068144 | -0.017976 |  | CFL | Bldg | 3200 | 0.541 | 3200 | 0.541 | 1.12 | 1.26 | -0.0056128 | 3200 | 0.541 | 3200 | 0.541 | 1.12 | 1.26 | -0.00561
CFLBldgSCEComNewCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Com | New | CZ14 | 3.133 | 0.00061256 | 0 | 3.3947 | 0.00078623 | -0.02051 | 3.133 | 0.00061256 | 0 | 3.3947 | 0.00078623 | -0.02051 |  | CFL | Bldg | 3130 | 0.613 | 3130 | 0.613 | 1.08 | 1.28 | -0.0065463 | 3130 | 0.613 | 3130 | 0.613 | 1.08 | 1.28 | -0.00655
CFLBldgSCEComNewCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Com | New | CZ15 | 2.8287 | 0.00057086 | 0 | 3.3285 | 0.00075085 | -0.003983 | 2.8287 | 0.00057086 | 0 | 3.3285 | 0.00075085 | -0.003983 |  | CFL | Bldg | 2830 | 0.571 | 2830 | 0.571 | 1.18 | 1.32 | -0.001408 | 2830 | 0.571 | 2830 | 0.571 | 1.18 | 1.32 | -0.00141
CFLBldgSCEComNewCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Com | New | CZ16 | 2.7895 | 0.0005116 | 0 | 2.8012 | 0.00062365 | -0.029982 | 2.7895 | 0.0005116 | 0 | 2.8012 | 0.00062365 | -0.029982 |  | CFL | Bldg | 2790 | 0.512 | 2790 | 0.512 | 1 | 1.22 | -0.010748 | 2790 | 0.512 | 2790 | 0.512 | 1 | 1.22 | -0.0107
CFLBldgSCEComNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | Com | New | IOU | 3.0621 | 0.00059876 | 0 | 3.3379 | 0.00074413 | -0.011561 | 3.0621 | 0.00059876 | 0 | 3.3379 | 0.00074413 | -0.011561 |  | CFL | Bldg | 3060 | 0.599 | 3060 | 0.599 | 1.09 | 1.24 | -0.0037754 | 3060 | 0.599 | 3060 | 0.599 | 1.09 | 1.24 | -0.00378
CFLBldgSCEECCExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ECC | Ex | CZ05 | 2.4145 | 0.00064362 | 0 | 2.604 | 0.00079583 | -0.028535 | 2.31 | 0.0005809 | 0 | 2.4995 | 0.00071885 | -0.0273 |  | CFL | Bldg | 2410 | 0.644 | 2310 | 0.581 | 1.08 | 1.24 | -0.011818 | 2410 | 0.644 | 2310 | 0.581 | 1.08 | 1.24 | -0.0118
CFLBldgSCEECCExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ECC | Ex | CZ06 | 2.4147 | 0.0006437 | 0 | 2.7737 | 0.00082678 | -0.013471 | 2.31 | 0.0005809 | 0 | 2.6595 | 0.00074685 | -0.0129 |  | CFL | Bldg | 2410 | 0.644 | 2310 | 0.581 | 1.15 | 1.29 | -0.0055844 | 2410 | 0.644 | 2310 | 0.581 | 1.15 | 1.29 | -0.00558
CFLBldgSCEECCExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ECC | Ex | CZ08 | 2.4148 | 0.00064376 | 0 | 2.7938 | 0.00082286 | -0.012271 | 2.31 | 0.00058091 | 0 | 2.6795 | 0.00074286 | -0.0117 |  | CFL | Bldg | 2410 | 0.644 | 2310 | 0.581 | 1.16 | 1.28 | -0.0050649 | 2410 | 0.644 | 2310 | 0.581 | 1.16 | 1.28 | -0.00506
CFLBldgSCEECCExCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ECC | Ex | CZ09 | 2.414 | 0.00064326 | 0 | 2.7829 | 0.00083911 | -0.014062 | 2.31 | 0.00058089 | 0 | 2.66 | 0.00075783 | -0.0134 |  | CFL | Bldg | 2410 | 0.643 | 2310 | 0.581 | 1.15 | 1.3 | -0.0058009 | 2410 | 0.643 | 2310 | 0.581 | 1.15 | 1.3 | -0.0058
CFLBldgSCEECCExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ECC | Ex | CZ10 | 2.4094 | 0.00064045 | 0 | 2.7475 | 0.00082652 | -0.013742 | 2.31 | 0.00058081 | 0 | 2.63 | 0.00074971 | -0.0132 |  | CFL | Bldg | 2410 | 0.64 | 2310 | 0.581 | 1.14 | 1.29 | -0.0057143 | 2410 | 0.64 | 2310 | 0.581 | 1.14 | 1.29 | -0.00571
CFLBldgSCEECCExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ECC | Ex | CZ13 | 2.4065 | 0.00041459 | 0 | 2.6953 | 0.00053699 | -0.021077 | 2.31 | 0.00037688 | 0 | 2.59 | 0.00048875 | -0.0202 |  | CFL | Bldg | 2410 | 0.415 | 2310 | 0.377 | 1.12 | 1.3 | -0.0087446 | 2410 | 0.415 | 2310 | 0.377 | 1.12 | 1.3 | -0.00874
CFLBldgSCEECCExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ECC | Ex | CZ14 | 2.4099 | 0.00064077 | 0 | 2.689 | 0.00081412 | -0.021908 | 2.31 | 0.00058082 | 0 | 2.58 | 0.00073873 | -0.021 |  | CFL | Bldg | 2410 | 0.641 | 2310 | 0.581 | 1.12 | 1.27 | -0.0090909 | 2410 | 0.641 | 2310 | 0.581 | 1.12 | 1.27 | -0.00909
CFLBldgSCEECCExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ECC | Ex | CZ15 | 2.4094 | 0.00064045 | 0 | 2.9575 | 0.00081562 | -0.006073 | 2.31 | 0.00058081 | 0 | 2.84 | 0.00073971 | -0.005829 |  | CFL | Bldg | 2410 | 0.64 | 2310 | 0.581 | 1.23 | 1.27 | -0.0025234 | 2410 | 0.64 | 2310 | 0.581 | 1.23 | 1.27 | -0.00252
CFLBldgSCEECCExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ECC | Ex | CZ16 | 2.4093 | 0.00041572 | 0 | 2.5083 | 0.00051175 | -0.039725 | 2.31 | 0.0003769 | 0 | 2.409 | 0.0004648 | -0.03819 |  | CFL | Bldg | 2410 | 0.416 | 2310 | 0.377 | 1.04 | 1.23 | -0.016533 | 2410 | 0.416 | 2310 | 0.377 | 1.04 | 1.23 | -0.0165
CFLBldgSCEECCExIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | ECC | Ex | IOU | 2.4131 | 0.00062128 | 0 | 2.7609 | 0.00079586 | -0.015268 | 2.31 | 0.00056138 | 0 | 2.6469 | 0.00071957 | -0.014612 |  | CFL | Bldg | 2410 | 0.621 | 2310 | 0.561 | 1.15 | 1.28 | -0.0063255 | 2410 | 0.621 | 2310 | 0.561 | 1.15 | 1.28 | -0.00633
CFLBldgSCEECCNewCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ECC | New | CZ05 | 2.31 | 0.000579 | 0 | 2.46 | 0.000732 | -0.0316 | 2.31 | 0.000579 | 0 | 2.46 | 0.000732 | -0.0316 |  | CFL | Bldg | 2310 | 0.579 | 2310 | 0.579 | 1.06 | 1.26 | -0.01368 | 2310 | 0.579 | 2310 | 0.579 | 1.06 | 1.26 | -0.0137
CFLBldgSCEECCNewCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ECC | New | CZ06 | 2.31 | 0.000579 | 0 | 2.6 | 0.000749 | -0.0164 | 2.31 | 0.000579 | 0 | 2.6 | 0.000749 | -0.0164 |  | CFL | Bldg | 2310 | 0.579 | 2310 | 0.579 | 1.13 | 1.29 | -0.0070996 | 2310 | 0.579 | 2310 | 0.579 | 1.13 | 1.29 | -0.0071
CFLBldgSCEECCNewCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ECC | New | CZ08 | 2.31 | 0.000579 | 0 | 2.62 | 0.000749 | -0.0116 | 2.31 | 0.000579 | 0 | 2.62 | 0.000749 | -0.0116 |  | CFL | Bldg | 2310 | 0.579 | 2310 | 0.579 | 1.13 | 1.29 | -0.0050216 | 2310 | 0.579 | 2310 | 0.579 | 1.13 | 1.29 | -0.00502
CFLBldgSCEECCNewCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ECC | New | CZ09 | 2.31 | 0.000579 | 0 | 2.61 | 0.000769 | -0.0135 | 2.31 | 0.000579 | 0 | 2.61 | 0.000769 | -0.0135 |  | CFL | Bldg | 2310 | 0.579 | 2310 | 0.579 | 1.13 | 1.33 | -0.0058442 | 2310 | 0.579 | 2310 | 0.579 | 1.13 | 1.33 | -0.00584
CFLBldgSCEECCNewCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ECC | New | CZ10 | 2.31 | 0.000579 | 0 | 2.64 | 0.000777 | -0.0134 | 2.31 | 0.000579 | 0 | 2.64 | 0.000777 | -0.0134 |  | CFL | Bldg | 2310 | 0.579 | 2310 | 0.579 | 1.14 | 1.34 | -0.0058009 | 2310 | 0.579 | 2310 | 0.579 | 1.14 | 1.34 | -0.0058
CFLBldgSCEECCNewCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ECC | New | CZ13 | 2.31 | 0.000376 | 0 | 2.61 | 0.000528 | -0.021 | 2.31 | 0.000376 | 0 | 2.61 | 0.000528 | -0.021 |  | CFL | Bldg | 2310 | 0.376 | 2310 | 0.376 | 1.13 | 1.4 | -0.0090909 | 2310 | 0.376 | 2310 | 0.376 | 1.13 | 1.4 | -0.00909
CFLBldgSCEECCNewCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ECC | New | CZ14 | 2.31 | 0.000579 | 0 | 2.6 | 0.000754 | -0.0219 | 2.31 | 0.000579 | 0 | 2.6 | 0.000754 | -0.0219 |  | CFL | Bldg | 2310 | 0.579 | 2310 | 0.579 | 1.13 | 1.3 | -0.0094805 | 2310 | 0.579 | 2310 | 0.579 | 1.13 | 1.3 | -0.00948
CFLBldgSCEECCNewCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ECC | New | CZ15 | 2.31 | 0.000579 | 0 | 2.8 | 0.000774 | -0.00515 | 2.31 | 0.000579 | 0 | 2.8 | 0.000774 | -0.00515 |  | CFL | Bldg | 2310 | 0.579 | 2310 | 0.579 | 1.21 | 1.34 | -0.0022294 | 2310 | 0.579 | 2310 | 0.579 | 1.21 | 1.34 | -0.00223
CFLBldgSCEECCNewCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ECC | New | CZ16 | 2.31 | 0.000376 | 0 | 2.42 | 0.000505 | -0.0393 | 2.31 | 0.000376 | 0 | 2.42 | 0.000505 | -0.0393 |  | CFL | Bldg | 2310 | 0.376 | 2310 | 0.376 | 1.05 | 1.34 | -0.017013 | 2310 | 0.376 | 2310 | 0.376 | 1.05 | 1.34 | -0.017
CFLBldgSCEECCNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | ECC | New | IOU | 2.31 | 0.00054578 | 0 | 2.6034 | 0.0007182 | -0.016893 | 2.31 | 0.00054578 | 0 | 2.6034 | 0.0007182 | -0.016893 |  | CFL | Bldg | 2310 | 0.546 | 2310 | 0.546 | 1.13 | 1.32 | -0.0073131 | 2310 | 0.546 | 2310 | 0.546 | 1.13 | 1.32 | -0.00731
CFLBldgSCEEPrExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | EPr | Ex | CZ05 | 2.2368 | 0.00062848 | 0 | 2.4268 | 0.00079606 | -0.020273 | 2.11 | 0.00056413 | 0 | 2.3 | 0.00071415 | -0.0192 |  | CFL | Bldg | 2240 | 0.628 | 2110 | 0.564 | 1.09 | 1.27 | -0.0090995 | 2240 | 0.628 | 2110 | 0.564 | 1.09 | 1.27 | -0.0091
CFLBldgSCEEPrExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | EPr | Ex | CZ06 | 2.2367 | 0.00062845 | 0 | 2.5862 | 0.000811 | -0.0099858 | 2.11 | 0.00056413 | 0 | 2.44 | 0.00072815 | -0.00944 |  | CFL | Bldg | 2240 | 0.628 | 2110 | 0.564 | 1.16 | 1.29 | -0.0044739 | 2240 | 0.628 | 2110 | 0.564 | 1.16 | 1.29 | -0.00447
CFLBldgSCEEPrExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | EPr | Ex | CZ08 | 2.2366 | 0.00062842 | 0 | 2.6161 | 0.00082193 | -0.0083676 | 2.11 | 0.00056413 | 0 | 2.47 | 0.00073815 | -0.0079 |  | CFL | Bldg | 2240 | 0.628 | 2110 | 0.564 | 1.17 | 1.31 | -0.0037441 | 2240 | 0.628 | 2110 | 0.564 | 1.17 | 1.31 | -0.00374
CFLBldgSCEEPrExCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | EPr | Ex | CZ09 | 2.2364 | 0.00062832 | 0 | 2.5759 | 0.00081879 | -0.010383 | 2.11 | 0.00056414 | 0 | 2.4397 | 0.00073517 | -0.00978 |  | CFL | Bldg | 2240 | 0.628 | 2110 | 0.564 | 1.16 | 1.3 | -0.0046351 | 2240 | 0.628 | 2110 | 0.564 | 1.16 | 1.3 | -0.00464
CFLBldgSCEEPrExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | EPr | Ex | CZ10 | 2.2321 | 0.0006263 | 0 | 2.5009 | 0.00079727 | -0.011358 | 2.11 | 0.0005643 | 0 | 2.36 | 0.00071836 | -0.010794 |  | CFL | Bldg | 2230 | 0.626 | 2110 | 0.564 | 1.12 | 1.27 | -0.0051156 | 2230 | 0.626 | 2110 | 0.564 | 1.12 | 1.27 | -0.00512
CFLBldgSCEEPrExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | EPr | Ex | CZ13 | 2.2315 | 1.9876e-05 | 0 | 2.4409 | 1.9876e-05 | -0.018535 | 2.11 | 1.7913e-05 | 0 | 2.31 | 1.7913e-05 | -0.0176 |  | CFL | Bldg | 2230 | 0.0199 | 2110 | 0.0179 | 1.09 | 1 | -0.0083412 | 2230 | 0.0199 | 2110 | 0.0179 | 1.09 | 1 | -0.00834
CFLBldgSCEEPrExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | EPr | Ex | CZ14 | 2.2332 | 0.00062679 | 0 | 2.4226 | 0.0008019 | -0.018442 | 2.11 | 0.00056426 | 0 | 2.29 | 0.00072231 | -0.017495 |  | CFL | Bldg | 2230 | 0.627 | 2110 | 0.564 | 1.09 | 1.28 | -0.0082913 | 2230 | 0.627 | 2110 | 0.564 | 1.09 | 1.28 | -0.00829
CFLBldgSCEEPrExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | EPr | Ex | CZ15 | 2.2321 | 0.0006263 | 0 | 2.6809 | 0.00080227 | -0.004823 | 2.11 | 0.0005643 | 0 | 2.54 | 0.00072336 | -0.00456 |  | CFL | Bldg | 2230 | 0.626 | 2110 | 0.564 | 1.2 | 1.28 | -0.0021611 | 2230 | 0.626 | 2110 | 0.564 | 1.2 | 1.28 | -0.00216
CFLBldgSCEEPrExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | EPr | Ex | CZ16 | 2.2324 | 1.9889e-05 | 0 | 2.1624 | 1.9889e-05 | -0.036577 | 2.11 | 1.7912e-05 | 0 | 2.0494 | 1.7912e-05 | -0.0346 |  | CFL | Bldg | 2230 | 0.0199 | 2110 | 0.0179 | 0.971 | 1 | -0.016398 | 2230 | 0.0199 | 2110 | 0.0179 | 0.971 | 1 | -0.0164
CFLBldgSCEEPrExIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | EPr | Ex | IOU | 2.2351 | 0.00058777 | 0 | 2.553 | 0.00076017 | -0.011199 | 2.11 | 0.0005282 | 0 | 2.4118 | 0.00068327 | -0.010596 |  | CFL | Bldg | 2240 | 0.588 | 2110 | 0.528 | 1.14 | 1.29 | -0.0050218 | 2240 | 0.588 | 2110 | 0.528 | 1.14 | 1.29 | -0.00502
CFLBldgSCEEPrNewCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | EPr | New | CZ05 | 2.11 | 0.000569 | 0 | 2.2 | 0.000733 | -0.0209 | 2.11 | 0.000569 | 0 | 2.2 | 0.000733 | -0.0209 |  | CFL | Bldg | 2110 | 0.569 | 2110 | 0.569 | 1.04 | 1.29 | -0.0099052 | 2110 | 0.569 | 2110 | 0.569 | 1.04 | 1.29 | -0.00991
CFLBldgSCEEPrNewCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | EPr | New | CZ06 | 2.11 | 0.000569 | 0 | 2.33 | 0.000766 | -0.0133 | 2.11 | 0.000569 | 0 | 2.33 | 0.000766 | -0.0133 |  | CFL | Bldg | 2110 | 0.569 | 2110 | 0.569 | 1.1 | 1.35 | -0.0063033 | 2110 | 0.569 | 2110 | 0.569 | 1.1 | 1.35 | -0.0063
CFLBldgSCEEPrNewCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | EPr | New | CZ08 | 2.11 | 0.000569 | 0 | 2.36 | 0.000787 | -0.0114 | 2.11 | 0.000569 | 0 | 2.36 | 0.000787 | -0.0114 |  | CFL | Bldg | 2110 | 0.569 | 2110 | 0.569 | 1.12 | 1.38 | -0.0054028 | 2110 | 0.569 | 2110 | 0.569 | 1.12 | 1.38 | -0.0054
CFLBldgSCEEPrNewCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | EPr | New | CZ09 | 2.11 | 0.000569 | 0 | 2.35 | 0.000803 | -0.0129 | 2.11 | 0.000569 | 0 | 2.35 | 0.000803 | -0.0129 |  | CFL | Bldg | 2110 | 0.569 | 2110 | 0.569 | 1.11 | 1.41 | -0.0061137 | 2110 | 0.569 | 2110 | 0.569 | 1.11 | 1.41 | -0.00611
CFLBldgSCEEPrNewCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | EPr | New | CZ10 | 2.11 | 0.000569 | 0 | 2.36 | 0.000816 | -0.0137 | 2.11 | 0.000569 | 0 | 2.36 | 0.000816 | -0.0137 |  | CFL | Bldg | 2110 | 0.569 | 2110 | 0.569 | 1.12 | 1.43 | -0.0064929 | 2110 | 0.569 | 2110 | 0.569 | 1.12 | 1.43 | -0.00649
CFLBldgSCEEPrNewCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | EPr | New | CZ13 | 2.11 | 1.81e-05 | 0 | 2.31 | 1.81e-05 | -0.0215 | 2.11 | 1.81e-05 | 0 | 2.31 | 1.81e-05 | -0.0215 |  | CFL | Bldg | 2110 | 0.0181 | 2110 | 0.0181 | 1.09 | 1 | -0.01019 | 2110 | 0.0181 | 2110 | 0.0181 | 1.09 | 1 | -0.0102
CFLBldgSCEEPrNewCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | EPr | New | CZ14 | 2.11 | 0.000569 | 0 | 2.31 | 0.000799 | -0.0215 | 2.11 | 0.000569 | 0 | 2.31 | 0.000799 | -0.0215 |  | CFL | Bldg | 2110 | 0.569 | 2110 | 0.569 | 1.09 | 1.4 | -0.01019 | 2110 | 0.569 | 2110 | 0.569 | 1.09 | 1.4 | -0.0102
CFLBldgSCEEPrNewCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | EPr | New | CZ15 | 2.11 | 0.000569 | 0 | 2.57 | 0.000827 | -0.006 | 2.11 | 0.000569 | 0 | 2.57 | 0.000827 | -0.006 |  | CFL | Bldg | 2110 | 0.569 | 2110 | 0.569 | 1.22 | 1.45 | -0.0028436 | 2110 | 0.569 | 2110 | 0.569 | 1.22 | 1.45 | -0.00284
CFLBldgSCEEPrNewCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | EPr | New | CZ16 | 2.11 | 1.81e-05 | 0 | 2.08 | 1.81e-05 | -0.0308 | 2.11 | 1.81e-05 | 0 | 2.08 | 1.81e-05 | -0.0308 |  | CFL | Bldg | 2110 | 0.0181 | 2110 | 0.0181 | 0.986 | 1 | -0.014597 | 2110 | 0.0181 | 2110 | 0.0181 | 0.986 | 1 | -0.0146
CFLBldgSCEEPrNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | EPr | New | IOU | 2.11 | 0.00050727 | 0 | 2.343 | 0.00071193 | -0.014672 | 2.11 | 0.00050727 | 0 | 2.343 | 0.00071193 | -0.014672 |  | CFL | Bldg | 2110 | 0.507 | 2110 | 0.507 | 1.11 | 1.4 | -0.0069534 | 2110 | 0.507 | 2110 | 0.507 | 1.11 | 1.4 | -0.00695
CFLBldgSCEERCExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ERC | Ex | CZ05 | 2.5948 | 0.00072558 | 0 | 2.6945 | 0.00090698 | -0.026445 | 2.39 | 0.0006232 | 0 | 2.48 | 0.00077925 | -0.0243 |  | CFL | Bldg | 2590 | 0.726 | 2390 | 0.623 | 1.04 | 1.25 | -0.010167 | 2590 | 0.726 | 2390 | 0.623 | 1.04 | 1.25 | -0.0102
CFLBldgSCEERCExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ERC | Ex | CZ06 | 2.5947 | 0.00072554 | 0 | 2.8442 | 0.00091093 | -0.015967 | 2.39 | 0.0006232 | 0 | 2.62 | 0.00078228 | -0.0147 |  | CFL | Bldg | 2590 | 0.726 | 2390 | 0.623 | 1.1 | 1.26 | -0.0061506 | 2590 | 0.726 | 2390 | 0.623 | 1.1 | 1.26 | -0.00615
CFLBldgSCEERCExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ERC | Ex | CZ08 | 2.5946 | 0.00072549 | 0 | 2.8841 | 0.00092182 | -0.013972 | 2.39 | 0.00062321 | 0 | 2.66 | 0.00079128 | -0.0129 |  | CFL | Bldg | 2590 | 0.725 | 2390 | 0.623 | 1.11 | 1.27 | -0.0053975 | 2590 | 0.725 | 2390 | 0.623 | 1.11 | 1.27 | -0.0054
CFLBldgSCEERCExCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ERC | Ex | CZ09 | 2.5942 | 0.00072533 | 0 | 2.8837 | 0.00091366 | -0.015764 | 2.39 | 0.00062322 | 0 | 2.66 | 0.0007853 | -0.0145 |  | CFL | Bldg | 2590 | 0.725 | 2390 | 0.623 | 1.11 | 1.26 | -0.0060669 | 2590 | 0.725 | 2390 | 0.623 | 1.11 | 1.26 | -0.00607
CFLBldgSCEERCExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ERC | Ex | CZ10 | 2.5873 | 0.00072212 | 0 | 2.8461 | 0.00090661 | -0.016121 | 2.39 | 0.00062349 | 0 | 2.63 | 0.00078261 | -0.0149 |  | CFL | Bldg | 2590 | 0.722 | 2390 | 0.623 | 1.1 | 1.26 | -0.0062343 | 2590 | 0.722 | 2390 | 0.623 | 1.1 | 1.26 | -0.00623
CFLBldgSCEERCExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ERC | Ex | CZ13 | 2.5863 | 2.0818e-05 | 0 | 2.7857 | 2.0818e-05 | -0.022676 | 2.39 | 1.8013e-05 | 0 | 2.58 | 1.8013e-05 | -0.0209 |  | CFL | Bldg | 2590 | 0.0208 | 2390 | 0.018 | 1.08 | 1 | -0.0087448 | 2590 | 0.0208 | 2390 | 0.018 | 1.08 | 1 | -0.00874
CFLBldgSCEERCExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ERC | Ex | CZ14 | 2.589 | 0.0007229 | 0 | 2.8279 | 0.00092054 | -0.021411 | 2.39 | 0.00062342 | 0 | 2.61 | 0.00079453 | -0.0198 |  | CFL | Bldg | 2590 | 0.723 | 2390 | 0.623 | 1.09 | 1.27 | -0.0082845 | 2590 | 0.723 | 2390 | 0.623 | 1.09 | 1.27 | -0.00828
CFLBldgSCEERCExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ERC | Ex | CZ15 | 2.5873 | 0.00072212 | 0 | 3.0548 | 0.00093242 | -0.0078012 | 2.39 | 0.00062349 | 0 | 2.82 | 0.00080467 | -0.0072 |  | CFL | Bldg | 2590 | 0.722 | 2390 | 0.623 | 1.18 | 1.29 | -0.0030126 | 2590 | 0.722 | 2390 | 0.623 | 1.18 | 1.29 | -0.00301
CFLBldgSCEERCExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ERC | Ex | CZ16 | 2.5877 | 2.0836e-05 | 0 | 2.5677 | 2.0836e-05 | -0.038218 | 2.39 | 1.8012e-05 | 0 | 2.37 | 1.8012e-05 | -0.0353 |  | CFL | Bldg | 2590 | 0.0208 | 2390 | 0.018 | 0.992 | 1 | -0.01477 | 2590 | 0.0208 | 2390 | 0.018 | 0.992 | 1 | -0.0148
CFLBldgSCEERCExIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | ERC | Ex | IOU | 2.5921 | 0.00067818 | 0 | 2.8571 | 0.00085619 | -0.016318 | 2.39 | 0.00058342 | 0 | 2.6363 | 0.00073638 | -0.015053 |  | CFL | Bldg | 2590 | 0.678 | 2390 | 0.583 | 1.1 | 1.26 | -0.0062985 | 2590 | 0.678 | 2390 | 0.583 | 1.1 | 1.26 | -0.0063
CFLBldgSCEERCNewCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ERC | New | CZ05 | 2.39 | 0.000631 | 0 | 2.59 | 0.00085 | -0.025 | 2.39 | 0.000631 | 0 | 2.59 | 0.00085 | -0.025 |  | CFL | Bldg | 2390 | 0.631 | 2390 | 0.631 | 1.08 | 1.35 | -0.01046 | 2390 | 0.631 | 2390 | 0.631 | 1.08 | 1.35 | -0.0105
CFLBldgSCEERCNewCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ERC | New | CZ06 | 2.39 | 0.000631 | 0 | 2.72 | 0.000813 | -0.0161 | 2.39 | 0.000631 | 0 | 2.72 | 0.000813 | -0.0161 |  | CFL | Bldg | 2390 | 0.631 | 2390 | 0.631 | 1.14 | 1.29 | -0.0067364 | 2390 | 0.631 | 2390 | 0.631 | 1.14 | 1.29 | -0.00674
CFLBldgSCEERCNewCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ERC | New | CZ08 | 2.39 | 0.000631 | 0 | 2.76 | 0.000833 | -0.014 | 2.39 | 0.000631 | 0 | 2.76 | 0.000833 | -0.014 |  | CFL | Bldg | 2390 | 0.631 | 2390 | 0.631 | 1.15 | 1.32 | -0.0058577 | 2390 | 0.631 | 2390 | 0.631 | 1.15 | 1.32 | -0.00586
CFLBldgSCEERCNewCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ERC | New | CZ09 | 2.39 | 0.000631 | 0 | 2.77 | 0.000855 | -0.0151 | 2.39 | 0.000631 | 0 | 2.77 | 0.000855 | -0.0151 |  | CFL | Bldg | 2390 | 0.631 | 2390 | 0.631 | 1.16 | 1.35 | -0.006318 | 2390 | 0.631 | 2390 | 0.631 | 1.16 | 1.35 | -0.00632
CFLBldgSCEERCNewCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ERC | New | CZ10 | 2.39 | 0.000631 | 0 | 2.78 | 0.000871 | -0.0159 | 2.39 | 0.000631 | 0 | 2.78 | 0.000871 | -0.0159 |  | CFL | Bldg | 2390 | 0.631 | 2390 | 0.631 | 1.16 | 1.38 | -0.0066527 | 2390 | 0.631 | 2390 | 0.631 | 1.16 | 1.38 | -0.00665
CFLBldgSCEERCNewCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ERC | New | CZ13 | 2.39 | 1.82e-05 | 0 | 2.74 | 1.82e-05 | -0.0233 | 2.39 | 1.82e-05 | 0 | 2.74 | 1.82e-05 | -0.0233 |  | CFL | Bldg | 2390 | 0.0182 | 2390 | 0.0182 | 1.15 | 1 | -0.009749 | 2390 | 0.0182 | 2390 | 0.0182 | 1.15 | 1 | -0.00975
CFLBldgSCEERCNewCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ERC | New | CZ14 | 2.39 | 0.000631 | 0 | 2.74 | 0.000858 | -0.0231 | 2.39 | 0.000631 | 0 | 2.74 | 0.000858 | -0.0231 |  | CFL | Bldg | 2390 | 0.631 | 2390 | 0.631 | 1.15 | 1.36 | -0.0096653 | 2390 | 0.631 | 2390 | 0.631 | 1.15 | 1.36 | -0.00967
CFLBldgSCEERCNewCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ERC | New | CZ15 | 2.39 | 0.000631 | 0 | 3.03 | 0.000873 | -0.00797 | 2.39 | 0.000631 | 0 | 3.03 | 0.000873 | -0.00797 |  | CFL | Bldg | 2390 | 0.631 | 2390 | 0.631 | 1.27 | 1.38 | -0.0033347 | 2390 | 0.631 | 2390 | 0.631 | 1.27 | 1.38 | -0.00333
CFLBldgSCEERCNewCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ERC | New | CZ16 | 2.39 | 1.82e-05 | 0 | 2.45 | 1.82e-05 | -0.0408 | 2.39 | 1.82e-05 | 0 | 2.45 | 1.82e-05 | -0.0408 |  | CFL | Bldg | 2390 | 0.0182 | 2390 | 0.0182 | 1.03 | 1 | -0.017071 | 2390 | 0.0182 | 2390 | 0.0182 | 1.03 | 1 | -0.0171
CFLBldgSCEERCNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | ERC | New | IOU | 2.39 | 0.00056233 | 0 | 2.7558 | 0.00075764 | -0.017254 | 2.39 | 0.00056233 | 0 | 2.7558 | 0.00075764 | -0.017254 |  | CFL | Bldg | 2390 | 0.562 | 2390 | 0.562 | 1.15 | 1.35 | -0.0072192 | 2390 | 0.562 | 2390 | 0.562 | 1.15 | 1.35 | -0.00722
CFLBldgSCEESeExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ESe | Ex | CZ05 | 2.327 | 0.00071358 | 0 | 2.4668 | 0.00088423 | -0.026068 | 2.21 | 0.00065312 | 0 | 2.34 | 0.00080915 | -0.0248 |  | CFL | Bldg | 2330 | 0.714 | 2210 | 0.653 | 1.06 | 1.24 | -0.011222 | 2330 | 0.714 | 2210 | 0.653 | 1.06 | 1.24 | -0.0112
CFLBldgSCEESeExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ESe | Ex | CZ06 | 2.327 | 0.00071356 | 0 | 2.6565 | 0.00092015 | -0.013782 | 2.21 | 0.00065313 | 0 | 2.52 | 0.00084218 | -0.0131 |  | CFL | Bldg | 2330 | 0.714 | 2210 | 0.653 | 1.14 | 1.29 | -0.0059276 | 2330 | 0.714 | 2210 | 0.653 | 1.14 | 1.29 | -0.00593
CFLBldgSCEESeExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ESe | Ex | CZ08 | 2.3269 | 0.00071353 | 0 | 2.6764 | 0.00091512 | -0.011982 | 2.21 | 0.00065313 | 0 | 2.54 | 0.00083815 | -0.0113 |  | CFL | Bldg | 2330 | 0.714 | 2210 | 0.653 | 1.15 | 1.28 | -0.0051131 | 2330 | 0.714 | 2210 | 0.653 | 1.15 | 1.28 | -0.00511
CFLBldgSCEESeExCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ESe | Ex | CZ09 | 2.3267 | 0.00071343 | 0 | 2.6561 | 0.00091599 | -0.013781 | 2.21 | 0.00065314 | 0 | 2.52 | 0.00083819 | -0.0131 |  | CFL | Bldg | 2330 | 0.713 | 2210 | 0.653 | 1.14 | 1.28 | -0.0059276 | 2330 | 0.713 | 2210 | 0.653 | 1.14 | 1.28 | -0.00593
CFLBldgSCEESeExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ESe | Ex | CZ10 | 2.3227 | 0.00071155 | 0 | 2.5821 | 0.00089958 | -0.014952 | 2.21 | 0.0006533 | 0 | 2.46 | 0.00082536 | -0.0142 |  | CFL | Bldg | 2320 | 0.712 | 2210 | 0.653 | 1.11 | 1.26 | -0.0064253 | 2320 | 0.712 | 2210 | 0.653 | 1.11 | 1.26 | -0.00643
CFLBldgSCEESeExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ESe | Ex | CZ13 | 2.3222 | 1.9896e-05 | 0 | 2.5415 | 1.9896e-05 | -0.022522 | 2.21 | 1.8307e-05 | 0 | 2.42 | 1.8307e-05 | -0.0214 |  | CFL | Bldg | 2320 | 0.0199 | 2210 | 0.0183 | 1.1 | 1 | -0.0096833 | 2320 | 0.0199 | 2210 | 0.0183 | 1.1 | 1 | -0.00968
CFLBldgSCEESeExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ESe | Ex | CZ14 | 2.3237 | 0.000712 | 0 | 2.5232 | 0.00087132 | -0.022837 | 2.21 | 0.00065326 | 0 | 2.4 | 0.00079931 | -0.0217 |  | CFL | Bldg | 2320 | 0.712 | 2210 | 0.653 | 1.09 | 1.22 | -0.009819 | 2320 | 0.712 | 2210 | 0.653 | 1.09 | 1.22 | -0.00982
CFLBldgSCEESeExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ESe | Ex | CZ15 | 2.3227 | 0.00071154 | 0 | 2.8109 | 0.00089663 | -0.0067888 | 2.21 | 0.0006533 | 0 | 2.67 | 0.00082336 | -0.00646 |  | CFL | Bldg | 2320 | 0.712 | 2210 | 0.653 | 1.21 | 1.26 | -0.0029231 | 2320 | 0.712 | 2210 | 0.653 | 1.21 | 1.26 | -0.00292
CFLBldgSCEESeExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ESe | Ex | CZ16 | 2.323 | 1.9906e-05 | 0 | 2.2636 | 1.9906e-05 | -0.038783 | 2.21 | 1.8306e-05 | 0 | 2.16 | 1.8306e-05 | -0.0369 |  | CFL | Bldg | 2320 | 0.0199 | 2210 | 0.0183 | 0.977 | 1 | -0.016697 | 2320 | 0.0199 | 2210 | 0.0183 | 0.977 | 1 | -0.0167
CFLBldgSCEESeExIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | ESe | Ex | IOU | 2.3255 | 0.00066731 | 0 | 2.6286 | 0.00085135 | -0.0148 | 2.21 | 0.00061136 | 0 | 2.4972 | 0.00077993 | -0.014038 |  | CFL | Bldg | 2330 | 0.667 | 2210 | 0.611 | 1.13 | 1.28 | -0.0063522 | 2330 | 0.667 | 2210 | 0.611 | 1.13 | 1.28 | -0.00635
CFLBldgSCEESeNewCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ESe | New | CZ05 | 2.21 | 0.000658 | 0 | 2.3 | 0.000826 | -0.023 | 2.21 | 0.000658 | 0 | 2.3 | 0.000826 | -0.023 |  | CFL | Bldg | 2210 | 0.658 | 2210 | 0.658 | 1.04 | 1.26 | -0.010407 | 2210 | 0.658 | 2210 | 0.658 | 1.04 | 1.26 | -0.0104
CFLBldgSCEESeNewCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ESe | New | CZ06 | 2.21 | 0.000658 | 0 | 2.44 | 0.000876 | -0.0164 | 2.21 | 0.000658 | 0 | 2.44 | 0.000876 | -0.0164 |  | CFL | Bldg | 2210 | 0.658 | 2210 | 0.658 | 1.1 | 1.33 | -0.0074208 | 2210 | 0.658 | 2210 | 0.658 | 1.1 | 1.33 | -0.00742
CFLBldgSCEESeNewCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ESe | New | CZ08 | 2.21 | 0.000658 | 0 | 2.47 | 0.000885 | -0.0134 | 2.21 | 0.000658 | 0 | 2.47 | 0.000885 | -0.0134 |  | CFL | Bldg | 2210 | 0.658 | 2210 | 0.658 | 1.12 | 1.34 | -0.0060633 | 2210 | 0.658 | 2210 | 0.658 | 1.12 | 1.34 | -0.00606
CFLBldgSCEESeNewCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ESe | New | CZ09 | 2.21 | 0.000658 | 0 | 2.47 | 0.000916 | -0.0158 | 2.21 | 0.000658 | 0 | 2.47 | 0.000916 | -0.0158 |  | CFL | Bldg | 2210 | 0.658 | 2210 | 0.658 | 1.12 | 1.39 | -0.0071493 | 2210 | 0.658 | 2210 | 0.658 | 1.12 | 1.39 | -0.00715
CFLBldgSCEESeNewCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ESe | New | CZ10 | 2.21 | 0.000658 | 0 | 2.49 | 0.000928 | -0.0168 | 2.21 | 0.000658 | 0 | 2.49 | 0.000928 | -0.0168 |  | CFL | Bldg | 2210 | 0.658 | 2210 | 0.658 | 1.13 | 1.41 | -0.0076018 | 2210 | 0.658 | 2210 | 0.658 | 1.13 | 1.41 | -0.0076
CFLBldgSCEESeNewCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ESe | New | CZ13 | 2.21 | 1.84e-05 | 0 | 2.47 | 1.84e-05 | -0.0248 | 2.21 | 1.84e-05 | 0 | 2.47 | 1.84e-05 | -0.0248 |  | CFL | Bldg | 2210 | 0.0184 | 2210 | 0.0184 | 1.12 | 1 | -0.011222 | 2210 | 0.0184 | 2210 | 0.0184 | 1.12 | 1 | -0.0112
CFLBldgSCEESeNewCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ESe | New | CZ14 | 2.21 | 0.000658 | 0 | 2.45 | 0.00091 | -0.0245 | 2.21 | 0.000658 | 0 | 2.45 | 0.00091 | -0.0245 |  | CFL | Bldg | 2210 | 0.658 | 2210 | 0.658 | 1.11 | 1.38 | -0.011086 | 2210 | 0.658 | 2210 | 0.658 | 1.11 | 1.38 | -0.0111
CFLBldgSCEESeNewCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ESe | New | CZ15 | 2.21 | 0.000658 | 0 | 2.75 | 0.00092 | -0.00736 | 2.21 | 0.000658 | 0 | 2.75 | 0.00092 | -0.00736 |  | CFL | Bldg | 2210 | 0.658 | 2210 | 0.658 | 1.24 | 1.4 | -0.0033303 | 2210 | 0.658 | 2210 | 0.658 | 1.24 | 1.4 | -0.00333
CFLBldgSCEESeNewCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ESe | New | CZ16 | 2.21 | 1.84e-05 | 0 | 2.2 | 1.84e-05 | -0.0307 | 2.21 | 1.84e-05 | 0 | 2.2 | 1.84e-05 | -0.0307 |  | CFL | Bldg | 2210 | 0.0184 | 2210 | 0.0184 | 0.995 | 1 | -0.013891 | 2210 | 0.0184 | 2210 | 0.0184 | 0.995 | 1 | -0.0139
CFLBldgSCEESeNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | ESe | New | IOU | 2.21 | 0.00058633 | 0 | 2.4692 | 0.00080768 | -0.017344 | 2.21 | 0.00058633 | 0 | 2.4692 | 0.00080768 | -0.017344 |  | CFL | Bldg | 2210 | 0.586 | 2210 | 0.586 | 1.12 | 1.38 | -0.0078481 | 2210 | 0.586 | 2210 | 0.586 | 1.12 | 1.38 | -0.00785
CFLBldgSCEEUnExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | EUn | Ex | CZ05 | 2.3645 | 0.00066498 | 0 | 2.614 | 0.00080913 | -0.016765 | 2.26 | 0.00059085 | 0 | 2.5095 | 0.00071885 | -0.0161 |  | CFL | Bldg | 2360 | 0.665 | 2260 | 0.591 | 1.11 | 1.22 | -0.0071239 | 2360 | 0.665 | 2260 | 0.591 | 1.11 | 1.22 | -0.00712
CFLBldgSCEEUnExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | EUn | Ex | CZ06 | 2.3647 | 0.00066507 | 0 | 2.7337 | 0.000843 | -0.0096387 | 2.26 | 0.00059085 | 0 | 2.6195 | 0.00074881 | -0.0092295 |  | CFL | Bldg | 2360 | 0.665 | 2260 | 0.591 | 1.16 | 1.27 | -0.0040839 | 2360 | 0.665 | 2260 | 0.591 | 1.16 | 1.27 | -0.00408
CFLBldgSCEEUnExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | EUn | Ex | CZ08 | 2.3648 | 0.00066514 | 0 | 2.7443 | 0.0008451 | -0.0093095 | 2.26 | 0.00059086 | 0 | 2.63 | 0.00074986 | -0.0089095 |  | CFL | Bldg | 2360 | 0.665 | 2260 | 0.591 | 1.16 | 1.27 | -0.0039423 | 2360 | 0.665 | 2260 | 0.591 | 1.16 | 1.27 | -0.00394
CFLBldgSCEEUnExCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | EUn | Ex | CZ09 | 2.364 | 0.00066455 | 0 | 2.7329 | 0.00085528 | -0.010472 | 2.26 | 0.00059083 | 0 | 2.61 | 0.00075984 | -0.01 |  | CFL | Bldg | 2360 | 0.665 | 2260 | 0.591 | 1.15 | 1.29 | -0.0044248 | 2360 | 0.665 | 2260 | 0.591 | 1.15 | 1.29 | -0.00442
CFLBldgSCEEUnExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | EUn | Ex | CZ10 | 2.3594 | 0.0006612 | 0 | 2.7075 | 0.00084598 | -0.0096376 | 2.26 | 0.00059071 | 0 | 2.599 | 0.00075562 | -0.009249 |  | CFL | Bldg | 2360 | 0.661 | 2260 | 0.591 | 1.15 | 1.28 | -0.0040925 | 2360 | 0.661 | 2260 | 0.591 | 1.15 | 1.28 | -0.00409
CFLBldgSCEEUnExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | EUn | Ex | CZ13 | 2.3565 | 0.00043248 | 0 | 2.6553 | 0.00054476 | -0.012926 | 2.26 | 0.00038775 | 0 | 2.5588 | 0.00048775 | -0.0124 |  | CFL | Bldg | 2360 | 0.432 | 2260 | 0.388 | 1.13 | 1.26 | -0.0054867 | 2360 | 0.432 | 2260 | 0.388 | 1.13 | 1.26 | -0.00549
CFLBldgSCEEUnExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | EUn | Ex | CZ14 | 2.3599 | 0.00066158 | 0 | 2.659 | 0.00083957 | -0.014145 | 2.26 | 0.00059072 | 0 | 2.55 | 0.00074963 | -0.0136 |  | CFL | Bldg | 2360 | 0.662 | 2260 | 0.591 | 1.13 | 1.27 | -0.0060177 | 2360 | 0.662 | 2260 | 0.591 | 1.13 | 1.27 | -0.00602
CFLBldgSCEEUnExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | EUn | Ex | CZ15 | 2.3594 | 0.0006612 | 0 | 2.8275 | 0.00084798 | -0.0050878 | 2.26 | 0.00059071 | 0 | 2.71 | 0.00075762 | -0.004889 |  | CFL | Bldg | 2360 | 0.661 | 2260 | 0.591 | 1.2 | 1.28 | -0.0021633 | 2360 | 0.661 | 2260 | 0.591 | 1.2 | 1.28 | -0.00216
CFLBldgSCEEUnExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | EUn | Ex | CZ16 | 2.3593 | 0.00043385 | 0 | 2.4793 | 0.00052868 | -0.027374 | 2.26 | 0.0003878 | 0 | 2.38 | 0.00047271 | -0.0262 |  | CFL | Bldg | 2360 | 0.434 | 2260 | 0.388 | 1.05 | 1.22 | -0.011593 | 2360 | 0.434 | 2260 | 0.388 | 1.05 | 1.22 | -0.0116
CFLBldgSCEEUnExIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | EUn | Ex | IOU | 2.3631 | 0.00064222 | 0 | 2.7146 | 0.00081554 | -0.010982 | 2.26 | 0.00057142 | 0 | 2.6018 | 0.00072519 | -0.010516 |  | CFL | Bldg | 2360 | 0.642 | 2260 | 0.571 | 1.15 | 1.27 | -0.0046533 | 2360 | 0.642 | 2260 | 0.571 | 1.15 | 1.27 | -0.00465
CFLBldgSCEEUnNewCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | EUn | New | CZ05 | 2.26 | 0.000588 | 0 | 2.45 | 0.000727 | -0.0148 | 2.26 | 0.000588 | 0 | 2.45 | 0.000727 | -0.0148 |  | CFL | Bldg | 2260 | 0.588 | 2260 | 0.588 | 1.08 | 1.24 | -0.0065487 | 2260 | 0.588 | 2260 | 0.588 | 1.08 | 1.24 | -0.00655
CFLBldgSCEEUnNewCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | EUn | New | CZ06 | 2.26 | 0.000588 | 0 | 2.59 | 0.000746 | -0.00669 | 2.26 | 0.000588 | 0 | 2.59 | 0.000746 | -0.00669 |  | CFL | Bldg | 2260 | 0.588 | 2260 | 0.588 | 1.15 | 1.27 | -0.0029602 | 2260 | 0.588 | 2260 | 0.588 | 1.15 | 1.27 | -0.00296
CFLBldgSCEEUnNewCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | EUn | New | CZ08 | 2.26 | 0.000588 | 0 | 2.61 | 0.000757 | -0.00592 | 2.26 | 0.000588 | 0 | 2.61 | 0.000757 | -0.00592 |  | CFL | Bldg | 2260 | 0.588 | 2260 | 0.588 | 1.15 | 1.29 | -0.0026195 | 2260 | 0.588 | 2260 | 0.588 | 1.15 | 1.29 | -0.00262
CFLBldgSCEEUnNewCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | EUn | New | CZ09 | 2.26 | 0.000588 | 0 | 2.63 | 0.000781 | -0.00682 | 2.26 | 0.000588 | 0 | 2.63 | 0.000781 | -0.00682 |  | CFL | Bldg | 2260 | 0.588 | 2260 | 0.588 | 1.16 | 1.33 | -0.0030177 | 2260 | 0.588 | 2260 | 0.588 | 1.16 | 1.33 | -0.00302
CFLBldgSCEEUnNewCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | EUn | New | CZ10 | 2.26 | 0.000588 | 0 | 2.63 | 0.000784 | -0.00723 | 2.26 | 0.000588 | 0 | 2.63 | 0.000784 | -0.00723 |  | CFL | Bldg | 2260 | 0.588 | 2260 | 0.588 | 1.16 | 1.33 | -0.0031991 | 2260 | 0.588 | 2260 | 0.588 | 1.16 | 1.33 | -0.0032
CFLBldgSCEEUnNewCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | EUn | New | CZ13 | 2.26 | 0.000386 | 0 | 2.65 | 0.000555 | -0.0148 | 2.26 | 0.000386 | 0 | 2.65 | 0.000555 | -0.0148 |  | CFL | Bldg | 2260 | 0.386 | 2260 | 0.386 | 1.17 | 1.44 | -0.0065487 | 2260 | 0.386 | 2260 | 0.386 | 1.17 | 1.44 | -0.00655
CFLBldgSCEEUnNewCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | EUn | New | CZ14 | 2.26 | 0.000588 | 0 | 2.5 | 0.000716 | -0.0121 | 2.26 | 0.000588 | 0 | 2.5 | 0.000716 | -0.0121 |  | CFL | Bldg | 2260 | 0.588 | 2260 | 0.588 | 1.11 | 1.22 | -0.005354 | 2260 | 0.588 | 2260 | 0.588 | 1.11 | 1.22 | -0.00535
CFLBldgSCEEUnNewCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | EUn | New | CZ15 | 2.26 | 0.000588 | 0 | 2.78 | 0.000796 | -0.0031 | 2.26 | 0.000588 | 0 | 2.78 | 0.000796 | -0.0031 |  | CFL | Bldg | 2260 | 0.588 | 2260 | 0.588 | 1.23 | 1.35 | -0.0013717 | 2260 | 0.588 | 2260 | 0.588 | 1.23 | 1.35 | -0.00137
CFLBldgSCEEUnNewCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | EUn | New | CZ16 | 2.26 | 0.000386 | 0 | 2.39 | 0.000499 | -0.0264 | 2.26 | 0.000386 | 0 | 2.39 | 0.000499 | -0.0264 |  | CFL | Bldg | 2260 | 0.386 | 2260 | 0.386 | 1.06 | 1.29 | -0.011681 | 2260 | 0.386 | 2260 | 0.386 | 1.06 | 1.29 | -0.0117
CFLBldgSCEEUnNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | EUn | New | IOU | 2.26 | 0.00055495 | 0 | 2.5898 | 0.00072156 | -0.0093887 | 2.26 | 0.00055495 | 0 | 2.5898 | 0.00072156 | -0.0093887 |  | CFL | Bldg | 2260 | 0.555 | 2260 | 0.555 | 1.15 | 1.3 | -0.0041543 | 2260 | 0.555 | 2260 | 0.555 | 1.15 | 1.3 | -0.00415
CFLBldgSCEGroExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Gro | Ex | CZ05 | 3.8875 | 0.00049463 | 0 | 3.7275 | 0.00061857 | -0.067663 | 3.85 | 0.00048994 | 0 | 3.69 | 0.000612 | -0.0671 |  | CFL | Bldg | 3890 | 0.495 | 3850 | 0.49 | 0.958 | 1.25 | -0.017429 | 3890 | 0.495 | 3850 | 0.49 | 0.958 | 1.25 | -0.0174
CFLBldgSCEGroExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Gro | Ex | CZ06 | 3.8875 | 0.00049463 | 0 | 3.9381 | 0.00062257 | -0.054375 | 3.85 | 0.00048994 | 0 | 3.91 | 0.000616 | -0.054 |  | CFL | Bldg | 3890 | 0.495 | 3850 | 0.49 | 1.02 | 1.26 | -0.014026 | 3890 | 0.495 | 3850 | 0.49 | 1.02 | 1.26 | -0.014
CFLBldgSCEGroExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Gro | Ex | CZ08 | 3.8875 | 0.00049463 | 0 | 4.0381 | 0.0006405 | -0.049375 | 3.85 | 0.00048994 | 0 | 4.01 | 0.000633 | -0.049 |  | CFL | Bldg | 3890 | 0.495 | 3850 | 0.49 | 1.04 | 1.29 | -0.012727 | 3890 | 0.495 | 3850 | 0.49 | 1.04 | 1.29 | -0.0127
CFLBldgSCEGroExCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Gro | Ex | CZ09 | 3.8874 | 0.00049462 | 0 | 4.0774 | 0.00064655 | -0.048175 | 3.85 | 0.00048994 | 0 | 4.04 | 0.00064 | -0.0478 |  | CFL | Bldg | 3890 | 0.495 | 3850 | 0.49 | 1.05 | 1.31 | -0.012416 | 3890 | 0.495 | 3850 | 0.49 | 1.05 | 1.31 | -0.0124
CFLBldgSCEGroExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Gro | Ex | CZ10 | 3.8855 | 0.00049433 | 0 | 4.0655 | 0.00066121 | -0.047044 | 3.85 | 0.00048989 | 0 | 4.03 | 0.000655 | -0.0466 |  | CFL | Bldg | 3890 | 0.494 | 3850 | 0.49 | 1.05 | 1.34 | -0.012104 | 3890 | 0.494 | 3850 | 0.49 | 1.05 | 1.34 | -0.0121
CFLBldgSCEGroExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Gro | Ex | CZ13 | 3.8861 | 0.00049441 | 0 | 4.0761 | 0.00065332 | -0.046261 | 3.85 | 0.0004899 | 0 | 4.04 | 0.000647 | -0.0459 |  | CFL | Bldg | 3890 | 0.494 | 3850 | 0.49 | 1.05 | 1.32 | -0.011922 | 3890 | 0.494 | 3850 | 0.49 | 1.05 | 1.32 | -0.0119
CFLBldgSCEGroExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Gro | Ex | CZ14 | 3.8858 | 0.00049438 | 0 | 4.0559 | 0.00067417 | -0.047359 | 3.85 | 0.0004899 | 0 | 4.02 | 0.000667 | -0.047 |  | CFL | Bldg | 3890 | 0.494 | 3850 | 0.49 | 1.04 | 1.36 | -0.012208 | 3890 | 0.494 | 3850 | 0.49 | 1.04 | 1.36 | -0.0122
CFLBldgSCEGroExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Gro | Ex | CZ15 | 3.8855 | 0.00049433 | 0 | 4.3755 | 0.0006591 | -0.027166 | 3.85 | 0.00048989 | 0 | 4.34 | 0.00065289 | -0.0269 |  | CFL | Bldg | 3890 | 0.494 | 3850 | 0.49 | 1.13 | 1.33 | -0.006987 | 3890 | 0.494 | 3850 | 0.49 | 1.13 | 1.33 | -0.00699
CFLBldgSCEGroExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Gro | Ex | CZ16 | 3.8859 | 0.00049438 | 0 | 3.6869 | 0.00062328 | -0.063338 | 3.85 | 0.0004899 | 0 | 3.66 | 0.000617 | -0.0628 |  | CFL | Bldg | 3890 | 0.494 | 3850 | 0.49 | 0.951 | 1.26 | -0.016312 | 3890 | 0.494 | 3850 | 0.49 | 0.951 | 1.26 | -0.0163
CFLBldgSCEGroExIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | Gro | Ex | IOU | 3.8869 | 0.00049453 | 0 | 4.0326 | 0.00064436 | -0.049229 | 3.85 | 0.00048992 | 0 | 4.0007 | 0.00063758 | -0.048839 |  | CFL | Bldg | 3890 | 0.495 | 3850 | 0.49 | 1.04 | 1.3 | -0.012686 | 3890 | 0.495 | 3850 | 0.49 | 1.04 | 1.3 | -0.0127
CFLBldgSCEGroNewCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Gro | New | CZ05 | 3.85 | 0.000489 | 0 | 3.79 | 0.000618 | -0.0644 | 3.85 | 0.000489 | 0 | 3.79 | 0.000618 | -0.0644 |  | CFL | Bldg | 3850 | 0.489 | 3850 | 0.489 | 0.984 | 1.26 | -0.016727 | 3850 | 0.489 | 3850 | 0.489 | 0.984 | 1.26 | -0.0167
CFLBldgSCEGroNewCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Gro | New | CZ06 | 3.85 | 0.000489 | 0 | 4.06 | 0.000621 | -0.0459 | 3.85 | 0.000489 | 0 | 4.06 | 0.000621 | -0.0459 |  | CFL | Bldg | 3850 | 0.489 | 3850 | 0.489 | 1.05 | 1.27 | -0.011922 | 3850 | 0.489 | 3850 | 0.489 | 1.05 | 1.27 | -0.0119
CFLBldgSCEGroNewCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Gro | New | CZ08 | 3.85 | 0.000489 | 0 | 4.11 | 0.000632 | -0.0401 | 3.85 | 0.000489 | 0 | 4.11 | 0.000632 | -0.0401 |  | CFL | Bldg | 3850 | 0.489 | 3850 | 0.489 | 1.07 | 1.29 | -0.010416 | 3850 | 0.489 | 3850 | 0.489 | 1.07 | 1.29 | -0.0104
CFLBldgSCEGroNewCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Gro | New | CZ09 | 3.85 | 0.000489 | 0 | 4.12 | 0.000668 | -0.0424 | 3.85 | 0.000489 | 0 | 4.12 | 0.000668 | -0.0424 |  | CFL | Bldg | 3850 | 0.489 | 3850 | 0.489 | 1.07 | 1.37 | -0.011013 | 3850 | 0.489 | 3850 | 0.489 | 1.07 | 1.37 | -0.011
CFLBldgSCEGroNewCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Gro | New | CZ10 | 3.85 | 0.000489 | 0 | 4.16 | 0.000697 | -0.0416 | 3.85 | 0.000489 | 0 | 4.16 | 0.000697 | -0.0416 |  | CFL | Bldg | 3850 | 0.489 | 3850 | 0.489 | 1.08 | 1.43 | -0.010805 | 3850 | 0.489 | 3850 | 0.489 | 1.08 | 1.43 | -0.0108
CFLBldgSCEGroNewCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Gro | New | CZ13 | 3.85 | 0.000489 | 0 | 4.16 | 0.000671 | -0.0436 | 3.85 | 0.000489 | 0 | 4.16 | 0.000671 | -0.0436 |  | CFL | Bldg | 3850 | 0.489 | 3850 | 0.489 | 1.08 | 1.37 | -0.011325 | 3850 | 0.489 | 3850 | 0.489 | 1.08 | 1.37 | -0.0113
CFLBldgSCEGroNewCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Gro | New | CZ14 | 3.85 | 0.000489 | 0 | 4.17 | 0.000679 | -0.0459 | 3.85 | 0.000489 | 0 | 4.17 | 0.000679 | -0.0459 |  | CFL | Bldg | 3850 | 0.489 | 3850 | 0.489 | 1.08 | 1.39 | -0.011922 | 3850 | 0.489 | 3850 | 0.489 | 1.08 | 1.39 | -0.0119
CFLBldgSCEGroNewCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Gro | New | CZ15 | 3.85 | 0.000489 | 0 | 4.49 | 0.000691 | -0.0237 | 3.85 | 0.000489 | 0 | 4.49 | 0.000691 | -0.0237 |  | CFL | Bldg | 3850 | 0.489 | 3850 | 0.489 | 1.17 | 1.41 | -0.0061558 | 3850 | 0.489 | 3850 | 0.489 | 1.17 | 1.41 | -0.00616
CFLBldgSCEGroNewCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Gro | New | CZ16 | 3.85 | 0.000489 | 0 | 3.78 | 0.00063 | -0.0597 | 3.85 | 0.000489 | 0 | 3.78 | 0.00063 | -0.0597 |  | CFL | Bldg | 3850 | 0.489 | 3850 | 0.489 | 0.982 | 1.29 | -0.015506 | 3850 | 0.489 | 3850 | 0.489 | 0.982 | 1.29 | -0.0155
CFLBldgSCEGroNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | Gro | New | IOU | 3.85 | 0.000489 | 0 | 4.1318 | 0.00066201 | -0.042174 | 3.85 | 0.000489 | 0 | 4.1318 | 0.00066201 | -0.042174 |  | CFL | Bldg | 3850 | 0.489 | 3850 | 0.489 | 1.07 | 1.35 | -0.010954 | 3850 | 0.489 | 3850 | 0.489 | 1.07 | 1.35 | -0.011
CFLBldgSCEHspExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Hsp | Ex | CZ05 | 4.1996 | 0.00071685 | 0 | 4.7092 | 0.00087277 | -0.029596 | 4.1804 | 0.000713 | 0 | 4.69 | 0.000867 | -0.0295 |  | CFL | Bldg | 4200 | 0.717 | 4180 | 0.713 | 1.12 | 1.22 | -0.0070568 | 4200 | 0.717 | 4180 | 0.713 | 1.12 | 1.22 | -0.00706
CFLBldgSCEHspExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Hsp | Ex | CZ06 | 4.1996 | 0.00071684 | 0 | 4.8592 | 0.00089576 | -0.0221 | 4.1804 | 0.000713 | 0 | 4.84 | 0.00089 | -0.0221 |  | CFL | Bldg | 4200 | 0.717 | 4180 | 0.713 | 1.16 | 1.25 | -0.0052866 | 4200 | 0.717 | 4180 | 0.713 | 1.16 | 1.25 | -0.00529
CFLBldgSCEHspExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Hsp | Ex | CZ08 | 4.1996 | 0.00071684 | 0 | 4.8892 | 0.0008948 | -0.021696 | 4.1804 | 0.000713 | 0 | 4.87 | 0.00088904 | -0.0216 |  | CFL | Bldg | 4200 | 0.717 | 4180 | 0.713 | 1.16 | 1.25 | -0.005167 | 4200 | 0.717 | 4180 | 0.713 | 1.16 | 1.25 | -0.00517
CFLBldgSCEHspExCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Hsp | Ex | CZ09 | 4.1995 | 0.0007168 | 0 | 4.909 | 0.00091875 | -0.021995 | 4.1805 | 0.000713 | 0 | 4.89 | 0.000914 | -0.0219 |  | CFL | Bldg | 4200 | 0.717 | 4180 | 0.713 | 1.17 | 1.28 | -0.0052386 | 4200 | 0.717 | 4180 | 0.713 | 1.17 | 1.28 | -0.00524
CFLBldgSCEHspExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Hsp | Ex | CZ10 | 4.1992 | 0.00071668 | 0 | 4.7784 | 0.0009066 | -0.023692 | 4.1808 | 0.000713 | 0 | 4.76 | 0.00090108 | -0.0236 |  | CFL | Bldg | 4200 | 0.717 | 4180 | 0.713 | 1.14 | 1.26 | -0.0056448 | 4200 | 0.717 | 4180 | 0.713 | 1.14 | 1.26 | -0.00564
CFLBldgSCEHspExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Hsp | Ex | CZ13 | 4.1993 | 0.00071674 | 0 | 4.7494 | 0.00090367 | -0.026994 | 4.1807 | 0.000713 | 0 | 4.74 | 0.000899 | -0.0269 |  | CFL | Bldg | 4200 | 0.717 | 4180 | 0.713 | 1.13 | 1.26 | -0.0064344 | 4200 | 0.717 | 4180 | 0.713 | 1.13 | 1.26 | -0.00643
CFLBldgSCEHspExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Hsp | Ex | CZ14 | 4.1993 | 0.00071671 | 0 | 4.7485 | 0.00090464 | -0.028893 | 4.1807 | 0.000713 | 0 | 4.73 | 0.00089907 | -0.0288 |  | CFL | Bldg | 4200 | 0.717 | 4180 | 0.713 | 1.13 | 1.26 | -0.0068887 | 4200 | 0.717 | 4180 | 0.713 | 1.13 | 1.26 | -0.00689
CFLBldgSCEHspExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Hsp | Ex | CZ15 | 4.1992 | 0.00071668 | 0 | 4.9684 | 0.0009156 | -0.018892 | 4.1808 | 0.000713 | 0 | 4.95 | 0.000911 | -0.0188 |  | CFL | Bldg | 4200 | 0.717 | 4180 | 0.713 | 1.18 | 1.28 | -0.0044967 | 4200 | 0.717 | 4180 | 0.713 | 1.18 | 1.28 | -0.0045
CFLBldgSCEHspExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Hsp | Ex | CZ16 | 4.1992 | 0.0007167 | 0 | 4.4385 | 0.00087754 | -0.039592 | 4.1808 | 0.000713 | 0 | 4.42 | 0.000872 | -0.0395 |  | CFL | Bldg | 4200 | 0.717 | 4180 | 0.713 | 1.06 | 1.22 | -0.009448 | 4200 | 0.717 | 4180 | 0.713 | 1.06 | 1.22 | -0.00945
CFLBldgSCEHspExIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | Hsp | Ex | IOU | 4.1995 | 0.00071679 | 0 | 4.8488 | 0.00090084 | -0.022935 | 4.1805 | 0.000713 | 0 | 4.8301 | 0.00089535 | -0.022867 |  | CFL | Bldg | 4200 | 0.717 | 4180 | 0.713 | 1.16 | 1.26 | -0.0054699 | 4200 | 0.717 | 4180 | 0.713 | 1.16 | 1.26 | -0.00547
CFLBldgSCEHspNewCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Hsp | New | CZ05 | 4.19 | 0.000713 | 0 | 4.42 | 0.000842 | -0.0313 | 4.19 | 0.000713 | 0 | 4.42 | 0.000842 | -0.0313 |  | CFL | Bldg | 4190 | 0.713 | 4190 | 0.713 | 1.05 | 1.18 | -0.0074702 | 4190 | 0.713 | 4190 | 0.713 | 1.05 | 1.18 | -0.00747
CFLBldgSCEHspNewCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Hsp | New | CZ06 | 4.19 | 0.000713 | 0 | 4.58 | 0.000858 | -0.024 | 4.19 | 0.000713 | 0 | 4.58 | 0.000858 | -0.024 |  | CFL | Bldg | 4190 | 0.713 | 4190 | 0.713 | 1.09 | 1.2 | -0.0057279 | 4190 | 0.713 | 4190 | 0.713 | 1.09 | 1.2 | -0.00573
CFLBldgSCEHspNewCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Hsp | New | CZ08 | 4.19 | 0.000713 | 0 | 4.63 | 0.000862 | -0.0221 | 4.19 | 0.000713 | 0 | 4.63 | 0.000862 | -0.0221 |  | CFL | Bldg | 4190 | 0.713 | 4190 | 0.713 | 1.11 | 1.21 | -0.0052745 | 4190 | 0.713 | 4190 | 0.713 | 1.11 | 1.21 | -0.00527
CFLBldgSCEHspNewCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Hsp | New | CZ09 | 4.19 | 0.000713 | 0 | 4.65 | 0.000886 | -0.0225 | 4.19 | 0.000713 | 0 | 4.65 | 0.000886 | -0.0225 |  | CFL | Bldg | 4190 | 0.713 | 4190 | 0.713 | 1.11 | 1.24 | -0.0053699 | 4190 | 0.713 | 4190 | 0.713 | 1.11 | 1.24 | -0.00537
CFLBldgSCEHspNewCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Hsp | New | CZ10 | 4.19 | 0.000713 | 0 | 4.63 | 0.000891 | -0.0247 | 4.19 | 0.000713 | 0 | 4.63 | 0.000891 | -0.0247 |  | CFL | Bldg | 4190 | 0.713 | 4190 | 0.713 | 1.11 | 1.25 | -0.005895 | 4190 | 0.713 | 4190 | 0.713 | 1.11 | 1.25 | -0.0059
CFLBldgSCEHspNewCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Hsp | New | CZ13 | 4.19 | 0.000713 | 0 | 4.61 | 0.000886 | -0.0279 | 4.19 | 0.000713 | 0 | 4.61 | 0.000886 | -0.0279 |  | CFL | Bldg | 4190 | 0.713 | 4190 | 0.713 | 1.1 | 1.24 | -0.0066587 | 4190 | 0.713 | 4190 | 0.713 | 1.1 | 1.24 | -0.00666
CFLBldgSCEHspNewCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Hsp | New | CZ14 | 4.19 | 0.000713 | 0 | 4.56 | 0.000884 | -0.0308 | 4.19 | 0.000713 | 0 | 4.56 | 0.000884 | -0.0308 |  | CFL | Bldg | 4190 | 0.713 | 4190 | 0.713 | 1.09 | 1.24 | -0.0073508 | 4190 | 0.713 | 4190 | 0.713 | 1.09 | 1.24 | -0.00735
CFLBldgSCEHspNewCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Hsp | New | CZ15 | 4.19 | 0.000713 | 0 | 4.85 | 0.000897 | -0.0199 | 4.19 | 0.000713 | 0 | 4.85 | 0.000897 | -0.0199 |  | CFL | Bldg | 4190 | 0.713 | 4190 | 0.713 | 1.16 | 1.26 | -0.0047494 | 4190 | 0.713 | 4190 | 0.713 | 1.16 | 1.26 | -0.00475
CFLBldgSCEHspNewCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Hsp | New | CZ16 | 4.19 | 0.000713 | 0 | 4.22 | 0.000852 | -0.0444 | 4.19 | 0.000713 | 0 | 4.22 | 0.000852 | -0.0444 |  | CFL | Bldg | 4190 | 0.713 | 4190 | 0.713 | 1.01 | 1.19 | -0.010597 | 4190 | 0.713 | 4190 | 0.713 | 1.01 | 1.19 | -0.0106
CFLBldgSCEHspNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | Hsp | New | IOU | 4.19 | 0.000713 | 0 | 4.6148 | 0.00087479 | -0.024452 | 4.19 | 0.000713 | 0 | 4.6148 | 0.00087479 | -0.024452 |  | CFL | Bldg | 4190 | 0.713 | 4190 | 0.713 | 1.1 | 1.23 | -0.0058359 | 4190 | 0.713 | 4190 | 0.713 | 1.1 | 1.23 | -0.00584
CFLBldgSCEHtlExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Htl | Ex | CZ05 | 1.669 | 0.00019886 | 0 | 1.679 | 0.00024983 | -0.0050169 | 1.6497 | 0.000195 | 0 | 1.65 | 0.000245 | -0.0049397 |  | CFL | Bldg | 1670 | 0.199 | 1650 | 0.195 | 1 | 1.26 | -0.0029944 | 1670 | 0.199 | 1650 | 0.195 | 1 | 1.26 | -0.00299
CFLBldgSCEHtlExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Htl | Ex | CZ06 | 1.6688 | 0.00019884 | 0 | 1.8484 | 0.0002518 | -0.003188 | 1.6496 | 0.000195 | 0 | 1.8196 | 0.000247 | -0.00314 |  | CFL | Bldg | 1670 | 0.199 | 1650 | 0.195 | 1.1 | 1.27 | -0.0019035 | 1670 | 0.199 | 1650 | 0.195 | 1.1 | 1.27 | -0.0019
CFLBldgSCEHtlExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Htl | Ex | CZ08 | 1.6688 | 0.00019885 | 0 | 1.8688 | 0.00025377 | -0.0028881 | 1.6496 | 0.000195 | 0 | 1.84 | 0.00024896 | -0.0028496 |  | CFL | Bldg | 1670 | 0.199 | 1650 | 0.195 | 1.12 | 1.28 | -0.0017274 | 1670 | 0.199 | 1650 | 0.195 | 1.12 | 1.28 | -0.00173
CFLBldgSCEHtlExCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Htl | Ex | CZ09 | 1.6684 | 0.00019879 | 0 | 1.8579 | 0.00025769 | -0.0030769 | 1.6495 | 0.000195 | 0 | 1.8295 | 0.00025295 | -0.0030295 |  | CFL | Bldg | 1670 | 0.199 | 1650 | 0.195 | 1.11 | 1.3 | -0.0018366 | 1670 | 0.199 | 1650 | 0.195 | 1.11 | 1.3 | -0.00184
CFLBldgSCEHtlExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Htl | Ex | CZ10 | 1.6669 | 0.00019858 | 0 | 1.8069 | 0.00025548 | -0.0031848 | 1.649 | 0.000195 | 0 | 1.78 | 0.0002519 | -0.00314 |  | CFL | Bldg | 1670 | 0.199 | 1650 | 0.195 | 1.08 | 1.29 | -0.0019042 | 1670 | 0.199 | 1650 | 0.195 | 1.08 | 1.29 | -0.0019
CFLBldgSCEHtlExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Htl | Ex | CZ13 | 1.6677 | 0.00019869 | 0 | 1.7577 | 0.00025461 | -0.0043546 | 1.6492 | 0.000195 | 0 | 1.7392 | 0.00025092 | -0.00429 |  | CFL | Bldg | 1670 | 0.199 | 1650 | 0.195 | 1.05 | 1.29 | -0.0026012 | 1670 | 0.199 | 1650 | 0.195 | 1.05 | 1.29 | -0.0026
CFLBldgSCEHtlExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Htl | Ex | CZ14 | 1.6671 | 0.00019862 | 0 | 1.7371 | 0.00025652 | -0.0044033 | 1.649 | 0.000195 | 0 | 1.71 | 0.000252 | -0.00434 |  | CFL | Bldg | 1670 | 0.199 | 1650 | 0.195 | 1.04 | 1.29 | -0.0026318 | 1670 | 0.199 | 1650 | 0.195 | 1.04 | 1.29 | -0.00263
CFLBldgSCEHtlExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Htl | Ex | CZ15 | 1.6669 | 0.00019858 | 0 | 1.9469 | 0.00025748 | -0.0017559 | 1.649 | 0.000195 | 0 | 1.92 | 0.000253 | -0.001729 |  | CFL | Bldg | 1670 | 0.199 | 1650 | 0.195 | 1.16 | 1.3 | -0.0010485 | 1670 | 0.199 | 1650 | 0.195 | 1.16 | 1.3 | -0.00105
CFLBldgSCEHtlExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Htl | Ex | CZ16 | 1.6674 | 0.00019866 | 0 | 1.5283 | 0.00024958 | -0.0071598 | 1.6492 | 0.000195 | 0 | 1.51 | 0.00024591 | -0.0070591 |  | CFL | Bldg | 1670 | 0.199 | 1650 | 0.195 | 0.916 | 1.26 | -0.0042805 | 1670 | 0.199 | 1650 | 0.195 | 0.916 | 1.26 | -0.00428
CFLBldgSCEHtlExIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | Htl | Ex | IOU | 1.6683 | 0.00019877 | 0 | 1.8498 | 0.00025425 | -0.0030992 | 1.6494 | 0.000195 | 0 | 1.8219 | 0.00024963 | -0.0030539 |  | CFL | Bldg | 1670 | 0.199 | 1650 | 0.195 | 1.1 | 1.28 | -0.0018515 | 1670 | 0.199 | 1650 | 0.195 | 1.1 | 1.28 | -0.00185
CFLBldgSCEHtlNewCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Htl | New | CZ05 | 1.64 | 0.000195 | 0 | 1.58 | 0.000247 | -0.00517 | 1.64 | 0.000195 | 0 | 1.58 | 0.000247 | -0.00517 |  | CFL | Bldg | 1640 | 0.195 | 1640 | 0.195 | 0.963 | 1.27 | -0.0031524 | 1640 | 0.195 | 1640 | 0.195 | 0.963 | 1.27 | -0.00315
CFLBldgSCEHtlNewCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Htl | New | CZ06 | 1.64 | 0.000195 | 0 | 1.78 | 0.000251 | -0.00284 | 1.64 | 0.000195 | 0 | 1.78 | 0.000251 | -0.00284 |  | CFL | Bldg | 1640 | 0.195 | 1640 | 0.195 | 1.09 | 1.29 | -0.0017317 | 1640 | 0.195 | 1640 | 0.195 | 1.09 | 1.29 | -0.00173
CFLBldgSCEHtlNewCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Htl | New | CZ08 | 1.64 | 0.000195 | 0 | 1.8 | 0.000253 | -0.0025 | 1.64 | 0.000195 | 0 | 1.8 | 0.000253 | -0.0025 |  | CFL | Bldg | 1640 | 0.195 | 1640 | 0.195 | 1.1 | 1.3 | -0.0015244 | 1640 | 0.195 | 1640 | 0.195 | 1.1 | 1.3 | -0.00152
CFLBldgSCEHtlNewCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Htl | New | CZ09 | 1.64 | 0.000195 | 0 | 1.79 | 0.000258 | -0.00284 | 1.64 | 0.000195 | 0 | 1.79 | 0.000258 | -0.00284 |  | CFL | Bldg | 1640 | 0.195 | 1640 | 0.195 | 1.09 | 1.32 | -0.0017317 | 1640 | 0.195 | 1640 | 0.195 | 1.09 | 1.32 | -0.00173
CFLBldgSCEHtlNewCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Htl | New | CZ10 | 1.64 | 0.000195 | 0 | 1.78 | 0.000266 | -0.00315 | 1.64 | 0.000195 | 0 | 1.78 | 0.000266 | -0.00315 |  | CFL | Bldg | 1640 | 0.195 | 1640 | 0.195 | 1.09 | 1.36 | -0.0019207 | 1640 | 0.195 | 1640 | 0.195 | 1.09 | 1.36 | -0.00192
CFLBldgSCEHtlNewCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Htl | New | CZ13 | 1.64 | 0.000195 | 0 | 1.71 | 0.000258 | -0.00432 | 1.64 | 0.000195 | 0 | 1.71 | 0.000258 | -0.00432 |  | CFL | Bldg | 1640 | 0.195 | 1640 | 0.195 | 1.04 | 1.32 | -0.0026341 | 1640 | 0.195 | 1640 | 0.195 | 1.04 | 1.32 | -0.00263
CFLBldgSCEHtlNewCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Htl | New | CZ14 | 1.64 | 0.000195 | 0 | 1.68 | 0.00026 | -0.00475 | 1.64 | 0.000195 | 0 | 1.68 | 0.00026 | -0.00475 |  | CFL | Bldg | 1640 | 0.195 | 1640 | 0.195 | 1.02 | 1.33 | -0.0028963 | 1640 | 0.195 | 1640 | 0.195 | 1.02 | 1.33 | -0.0029
CFLBldgSCEHtlNewCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Htl | New | CZ15 | 1.64 | 0.000195 | 0 | 1.93 | 0.000264 | -0.00157 | 1.64 | 0.000195 | 0 | 1.93 | 0.000264 | -0.00157 |  | CFL | Bldg | 1640 | 0.195 | 1640 | 0.195 | 1.18 | 1.35 | -0.00095732 | 1640 | 0.195 | 1640 | 0.195 | 1.18 | 1.35 | -0.000957
CFLBldgSCEHtlNewCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Htl | New | CZ16 | 1.64 | 0.000195 | 0 | 1.45 | 0.00025 | -0.00805 | 1.64 | 0.000195 | 0 | 1.45 | 0.00025 | -0.00805 |  | CFL | Bldg | 1640 | 0.195 | 1640 | 0.195 | 0.884 | 1.28 | -0.0049085 | 1640 | 0.195 | 1640 | 0.195 | 0.884 | 1.28 | -0.00491
CFLBldgSCEHtlNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | Htl | New | IOU | 1.64 | 0.000195 | 0 | 1.7995 | 0.0002577 | -0.002891 | 1.64 | 0.000195 | 0 | 1.7995 | 0.0002577 | -0.002891 |  | CFL | Bldg | 1640 | 0.195 | 1640 | 0.195 | 1.1 | 1.32 | -0.0017628 | 1640 | 0.195 | 1640 | 0.195 | 1.1 | 1.32 | -0.00176
CFLBldgSCEMBTExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | MBT | Ex | CZ05 | 3.0871 | 0.00077914 | 0 | 3.5365 | 0.00096896 | -0.0013083 | 3.04 | 0.000765 | 0 | 3.48 | 0.000952 | -0.0012894 |  | CFL | Bldg | 3090 | 0.779 | 3040 | 0.765 | 1.14 | 1.24 | -0.00042415 | 3090 | 0.779 | 3040 | 0.765 | 1.14 | 1.24 | -0.000424
CFLBldgSCEMBTExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | MBT | Ex | CZ06 | 3.0871 | 0.00077914 | 0 | 3.6166 | 0.00094397 | -0.00056449 | 3.04 | 0.000765 | 0 | 3.56 | 0.00092606 | -0.000556 |  | CFL | Bldg | 3090 | 0.779 | 3040 | 0.765 | 1.17 | 1.21 | -0.00018289 | 3090 | 0.779 | 3040 | 0.765 | 1.17 | 1.21 | -0.000183
CFLBldgSCEMBTExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | MBT | Ex | CZ08 | 3.0872 | 0.00077914 | 0 | 3.6366 | 0.00097997 | -0.00021077 | 3.04 | 0.000765 | 0 | 3.58 | 0.00096206 | -0.00020794 |  | CFL | Bldg | 3090 | 0.779 | 3040 | 0.765 | 1.18 | 1.26 | -6.8402e-05 | 3090 | 0.779 | 3040 | 0.765 | 1.18 | 1.26 | -6.84e-05
CFLBldgSCEMBTExCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | MBT | Ex | CZ09 | 3.0872 | 0.00077917 | 0 | 3.6267 | 0.00098301 | -0.00086723 | 3.04 | 0.000765 | 0 | 3.57 | 0.00096506 | -0.000854 |  | CFL | Bldg | 3090 | 0.779 | 3040 | 0.765 | 1.17 | 1.26 | -0.00028092 | 3090 | 0.779 | 3040 | 0.765 | 1.17 | 1.26 | -0.000281
CFLBldgSCEMBTExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | MBT | Ex | CZ10 | 3.083 | 0.00077791 | 0 | 3.5116 | 0.00098235 | -0.00096777 | 3.04 | 0.000765 | 0 | 3.46 | 0.000966 | -0.000954 |  | CFL | Bldg | 3080 | 0.778 | 3040 | 0.765 | 1.14 | 1.26 | -0.00031382 | 3080 | 0.778 | 3040 | 0.765 | 1.14 | 1.26 | -0.000314
CFLBldgSCEMBTExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | MBT | Ex | CZ13 | 3.0856 | 0.00077868 | 0 | 3.5147 | 0.00095041 | -0.0020173 | 3.04 | 0.000765 | 0 | 3.46 | 0.000934 | -0.00199 |  | CFL | Bldg | 3090 | 0.779 | 3040 | 0.765 | 1.14 | 1.22 | -0.00065461 | 3090 | 0.779 | 3040 | 0.765 | 1.14 | 1.22 | -0.000655
CFLBldgSCEMBTExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | MBT | Ex | CZ14 | 3.0848 | 0.00077845 | 0 | 3.5138 | 0.00098203 | -0.0023259 | 3.04 | 0.000765 | 0 | 3.46 | 0.000965 | -0.00229 |  | CFL | Bldg | 3080 | 0.778 | 3040 | 0.765 | 1.14 | 1.26 | -0.00075329 | 3080 | 0.778 | 3040 | 0.765 | 1.14 | 1.26 | -0.000753
CFLBldgSCEMBTExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | MBT | Ex | CZ15 | 3.083 | 0.00077791 | 0 | 3.6516 | 0.00098535 | 0 | 3.04 | 0.000765 | 0 | 3.6 | 0.000969 | 0 |  | CFL | Bldg | 3080 | 0.778 | 3040 | 0.765 | 1.18 | 1.27 | 0 | 3080 | 0.778 | 3040 | 0.765 | 1.18 | 1.27 | 0
CFLBldgSCEMBTExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | MBT | Ex | CZ16 | 3.0845 | 0.00077834 | 0 | 3.3034 | 0.00092701 | -0.0081745 | 3.04 | 0.000765 | 0 | 3.25 | 0.000911 | -0.00805 |  | CFL | Bldg | 3080 | 0.778 | 3040 | 0.765 | 1.07 | 1.19 | -0.002648 | 3080 | 0.778 | 3040 | 0.765 | 1.07 | 1.19 | -0.00265
CFLBldgSCEMBTExIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | MBT | Ex | IOU | 3.0861 | 0.00077882 | 0 | 3.596 | 0.00097147 | -0.0007991 | 3.04 | 0.000765 | 0 | 3.5408 | 0.00095401 | -0.00078729 |  | CFL | Bldg | 3090 | 0.779 | 3040 | 0.765 | 1.16 | 1.25 | -0.00025898 | 3090 | 0.779 | 3040 | 0.765 | 1.16 | 1.25 | -0.000259
CFLBldgSCEMBTNewCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | MBT | New | CZ05 | 3.04 | 0.000765 | 0 | 3.27 | 0.000945 | -0.00104 | 3.04 | 0.000765 | 0 | 3.27 | 0.000945 | -0.00104 |  | CFL | Bldg | 3040 | 0.765 | 3040 | 0.765 | 1.08 | 1.24 | -0.00034211 | 3040 | 0.765 | 3040 | 0.765 | 1.08 | 1.24 | -0.000342
CFLBldgSCEMBTNewCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | MBT | New | CZ06 | 3.04 | 0.000765 | 0 | 3.4 | 0.00095 | -0.000996 | 3.04 | 0.000765 | 0 | 3.4 | 0.00095 | -0.000996 |  | CFL | Bldg | 3040 | 0.765 | 3040 | 0.765 | 1.12 | 1.24 | -0.00032763 | 3040 | 0.765 | 3040 | 0.765 | 1.12 | 1.24 | -0.000328
CFLBldgSCEMBTNewCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | MBT | New | CZ08 | 3.04 | 0.000765 | 0 | 3.41 | 0.000975 | -0.000799 | 3.04 | 0.000765 | 0 | 3.41 | 0.000975 | -0.000799 |  | CFL | Bldg | 3040 | 0.765 | 3040 | 0.765 | 1.12 | 1.27 | -0.00026283 | 3040 | 0.765 | 3040 | 0.765 | 1.12 | 1.27 | -0.000263
CFLBldgSCEMBTNewCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | MBT | New | CZ09 | 3.04 | 0.000765 | 0 | 3.41 | 0.000997 | -0.000939 | 3.04 | 0.000765 | 0 | 3.41 | 0.000997 | -0.000939 |  | CFL | Bldg | 3040 | 0.765 | 3040 | 0.765 | 1.12 | 1.3 | -0.00030888 | 3040 | 0.765 | 3040 | 0.765 | 1.12 | 1.3 | -0.000309
CFLBldgSCEMBTNewCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | MBT | New | CZ10 | 3.04 | 0.000765 | 0 | 3.42 | 0.00101 | -0.00099 | 3.04 | 0.000765 | 0 | 3.42 | 0.00101 | -0.00099 |  | CFL | Bldg | 3040 | 0.765 | 3040 | 0.765 | 1.13 | 1.32 | -0.00032566 | 3040 | 0.765 | 3040 | 0.765 | 1.13 | 1.32 | -0.000326
CFLBldgSCEMBTNewCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | MBT | New | CZ13 | 3.04 | 0.000765 | 0 | 3.38 | 0.000985 | -0.00174 | 3.04 | 0.000765 | 0 | 3.38 | 0.000985 | -0.00174 |  | CFL | Bldg | 3040 | 0.765 | 3040 | 0.765 | 1.11 | 1.29 | -0.00057237 | 3040 | 0.765 | 3040 | 0.765 | 1.11 | 1.29 | -0.000572
CFLBldgSCEMBTNewCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | MBT | New | CZ14 | 3.04 | 0.000765 | 0 | 3.38 | 0.000999 | -0.00192 | 3.04 | 0.000765 | 0 | 3.38 | 0.000999 | -0.00192 |  | CFL | Bldg | 3040 | 0.765 | 3040 | 0.765 | 1.11 | 1.31 | -0.00063158 | 3040 | 0.765 | 3040 | 0.765 | 1.11 | 1.31 | -0.000632
CFLBldgSCEMBTNewCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | MBT | New | CZ15 | 3.04 | 0.000765 | 0 | 3.6 | 0.00101 | 0 | 3.04 | 0.000765 | 0 | 3.6 | 0.00101 | 0 |  | CFL | Bldg | 3040 | 0.765 | 3040 | 0.765 | 1.18 | 1.32 | 0 | 3040 | 0.765 | 3040 | 0.765 | 1.18 | 1.32 | 0
CFLBldgSCEMBTNewCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | MBT | New | CZ16 | 3.04 | 0.000765 | 0 | 3.21 | 0.000945 | -0.00653 | 3.04 | 0.000765 | 0 | 3.21 | 0.000945 | -0.00653 |  | CFL | Bldg | 3040 | 0.765 | 3040 | 0.765 | 1.06 | 1.24 | -0.002148 | 3040 | 0.765 | 3040 | 0.765 | 1.06 | 1.24 | -0.00215
CFLBldgSCEMBTNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | MBT | New | IOU | 3.04 | 0.000765 | 0 | 3.4237 | 0.00098842 | -0.0010748 | 3.04 | 0.000765 | 0 | 3.4237 | 0.00098842 | -0.0010748 |  | CFL | Bldg | 3040 | 0.765 | 3040 | 0.765 | 1.13 | 1.29 | -0.00035355 | 3040 | 0.765 | 3040 | 0.765 | 1.13 | 1.29 | -0.000354
CFLBldgSCEMLIExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | MLI | Ex | CZ05 | 2.58 | 0.00077689 | 0 | 2.72 | 0.00093988 | -0.0125 | 2.58 | 0.00077594 | 0 | 2.72 | 0.000938 | -0.0125 |  | CFL | Bldg | 2580 | 0.777 | 2580 | 0.776 | 1.05 | 1.21 | -0.004845 | 2580 | 0.777 | 2580 | 0.776 | 1.05 | 1.21 | -0.00485
CFLBldgSCEMLIExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | MLI | Ex | CZ06 | 2.58 | 0.00077689 | 0 | 2.8694 | 0.00092389 | -0.00433 | 2.58 | 0.00077594 | 0 | 2.86 | 0.000922 | -0.00433 |  | CFL | Bldg | 2580 | 0.777 | 2580 | 0.776 | 1.11 | 1.19 | -0.0016783 | 2580 | 0.777 | 2580 | 0.776 | 1.11 | 1.19 | -0.00168
CFLBldgSCEMLIExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | MLI | Ex | CZ08 | 2.58 | 0.00077689 | 0 | 2.88 | 0.00092189 | -0.00356 | 2.58 | 0.00077594 | 0 | 2.88 | 0.00092 | -0.00356 |  | CFL | Bldg | 2580 | 0.777 | 2580 | 0.776 | 1.12 | 1.19 | -0.0013798 | 2580 | 0.777 | 2580 | 0.776 | 1.12 | 1.19 | -0.00138
CFLBldgSCEMLIExCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | MLI | Ex | CZ09 | 2.58 | 0.00077689 | 0 | 2.8695 | 0.00094283 | -0.0048794 | 2.58 | 0.00077595 | 0 | 2.86 | 0.00094094 | -0.00487 |  | CFL | Bldg | 2580 | 0.777 | 2580 | 0.776 | 1.11 | 1.21 | -0.0018876 | 2580 | 0.777 | 2580 | 0.776 | 1.11 | 1.21 | -0.00189
CFLBldgSCEMLIExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | MLI | Ex | CZ10 | 2.58 | 0.00077672 | 0 | 2.78 | 0.00093558 | -0.0062686 | 2.58 | 0.00077586 | 0 | 2.78 | 0.00093386 | -0.00626 |  | CFL | Bldg | 2580 | 0.777 | 2580 | 0.776 | 1.08 | 1.2 | -0.0024264 | 2580 | 0.777 | 2580 | 0.776 | 1.08 | 1.2 | -0.00243
CFLBldgSCEMLIExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | MLI | Ex | CZ13 | 2.58 | 0.00077682 | 0 | 2.76 | 0.00092382 | -0.0139 | 2.58 | 0.00077591 | 0 | 2.76 | 0.000922 | -0.0139 |  | CFL | Bldg | 2580 | 0.777 | 2580 | 0.776 | 1.07 | 1.19 | -0.0053876 | 2580 | 0.777 | 2580 | 0.776 | 1.07 | 1.19 | -0.00539
CFLBldgSCEMLIExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | MLI | Ex | CZ14 | 2.58 | 0.00077679 | 0 | 2.73 | 0.00092879 | -0.016 | 2.58 | 0.0007759 | 0 | 2.73 | 0.000927 | -0.016 |  | CFL | Bldg | 2580 | 0.777 | 2580 | 0.776 | 1.06 | 1.19 | -0.0062016 | 2580 | 0.777 | 2580 | 0.776 | 1.06 | 1.19 | -0.0062
CFLBldgSCEMLIExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | MLI | Ex | CZ15 | 2.58 | 0.00077672 | 0 | 2.97 | 0.00092472 | -0.00161 | 2.58 | 0.00077586 | 0 | 2.97 | 0.00092386 | -0.00161 |  | CFL | Bldg | 2580 | 0.777 | 2580 | 0.776 | 1.15 | 1.19 | -0.00062403 | 2580 | 0.777 | 2580 | 0.776 | 1.15 | 1.19 | -0.000624
CFLBldgSCEMLIExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | MLI | Ex | CZ16 | 2.58 | 0.00077678 | 0 | 2.54 | 0.00091478 | -0.0312 | 2.58 | 0.00077589 | 0 | 2.54 | 0.000913 | -0.0312 |  | CFL | Bldg | 2580 | 0.777 | 2580 | 0.776 | 0.984 | 1.18 | -0.012093 | 2580 | 0.777 | 2580 | 0.776 | 0.984 | 1.18 | -0.0121
CFLBldgSCEMLIExIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | MLI | Ex | IOU | 2.58 | 0.00077684 | 0 | 2.8487 | 0.00092809 | -0.0055916 | 2.58 | 0.00077592 | 0 | 2.8452 | 0.0009263 | -0.0055887 |  | CFL | Bldg | 2580 | 0.777 | 2580 | 0.776 | 1.1 | 1.19 | -0.0021662 | 2580 | 0.777 | 2580 | 0.776 | 1.1 | 1.19 | -0.00217
CFLBldgSCEMLINewCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | MLI | New | CZ05 | 2.58 | 0.000775 | 0 | 2.56 | 0.000923 | -0.0206 | 2.58 | 0.000775 | 0 | 2.56 | 0.000923 | -0.0206 |  | CFL | Bldg | 2580 | 0.775 | 2580 | 0.775 | 0.992 | 1.19 | -0.0079845 | 2580 | 0.775 | 2580 | 0.775 | 0.992 | 1.19 | -0.00798
CFLBldgSCEMLINewCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | MLI | New | CZ06 | 2.58 | 0.000775 | 0 | 2.71 | 0.000906 | -0.00931 | 2.58 | 0.000775 | 0 | 2.71 | 0.000906 | -0.00931 |  | CFL | Bldg | 2580 | 0.775 | 2580 | 0.775 | 1.05 | 1.17 | -0.0036085 | 2580 | 0.775 | 2580 | 0.775 | 1.05 | 1.17 | -0.00361
CFLBldgSCEMLINewCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | MLI | New | CZ08 | 2.58 | 0.000775 | 0 | 2.75 | 0.000911 | -0.0075 | 2.58 | 0.000775 | 0 | 2.75 | 0.000911 | -0.0075 |  | CFL | Bldg | 2580 | 0.775 | 2580 | 0.775 | 1.07 | 1.18 | -0.002907 | 2580 | 0.775 | 2580 | 0.775 | 1.07 | 1.18 | -0.00291
CFLBldgSCEMLINewCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | MLI | New | CZ09 | 2.58 | 0.000775 | 0 | 2.82 | 0.000996 | -0.00864 | 2.58 | 0.000775 | 0 | 2.82 | 0.000996 | -0.00864 |  | CFL | Bldg | 2580 | 0.775 | 2580 | 0.775 | 1.09 | 1.29 | -0.0033488 | 2580 | 0.775 | 2580 | 0.775 | 1.09 | 1.29 | -0.00335
CFLBldgSCEMLINewCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | MLI | New | CZ10 | 2.58 | 0.000775 | 0 | 2.84 | 0.00101 | -0.00943 | 2.58 | 0.000775 | 0 | 2.84 | 0.00101 | -0.00943 |  | CFL | Bldg | 2580 | 0.775 | 2580 | 0.775 | 1.1 | 1.3 | -0.003655 | 2580 | 0.775 | 2580 | 0.775 | 1.1 | 1.3 | -0.00366
CFLBldgSCEMLINewCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | MLI | New | CZ13 | 2.58 | 0.000775 | 0 | 2.77 | 0.000975 | -0.0171 | 2.58 | 0.000775 | 0 | 2.77 | 0.000975 | -0.0171 |  | CFL | Bldg | 2580 | 0.775 | 2580 | 0.775 | 1.07 | 1.26 | -0.0066279 | 2580 | 0.775 | 2580 | 0.775 | 1.07 | 1.26 | -0.00663
CFLBldgSCEMLINewCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | MLI | New | CZ14 | 2.58 | 0.000775 | 0 | 2.73 | 0.000947 | -0.0186 | 2.58 | 0.000775 | 0 | 2.73 | 0.000947 | -0.0186 |  | CFL | Bldg | 2580 | 0.775 | 2580 | 0.775 | 1.06 | 1.22 | -0.0072093 | 2580 | 0.775 | 2580 | 0.775 | 1.06 | 1.22 | -0.00721
CFLBldgSCEMLINewCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | MLI | New | CZ15 | 2.58 | 0.000775 | 0 | 3.03 | 0.00103 | -0.00158 | 2.58 | 0.000775 | 0 | 3.03 | 0.00103 | -0.00158 |  | CFL | Bldg | 2580 | 0.775 | 2580 | 0.775 | 1.17 | 1.33 | -0.0006124 | 2580 | 0.775 | 2580 | 0.775 | 1.17 | 1.33 | -0.000612
CFLBldgSCEMLINewCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | MLI | New | CZ16 | 2.58 | 0.000775 | 0 | 2.54 | 0.000912 | -0.033 | 2.58 | 0.000775 | 0 | 2.54 | 0.000912 | -0.033 |  | CFL | Bldg | 2580 | 0.775 | 2580 | 0.775 | 0.984 | 1.18 | -0.012791 | 2580 | 0.775 | 2580 | 0.775 | 0.984 | 1.18 | -0.0128
CFLBldgSCEMLINewIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | MLI | New | IOU | 2.58 | 0.000775 | 0 | 2.8019 | 0.00096562 | -0.0094474 | 2.58 | 0.000775 | 0 | 2.8019 | 0.00096562 | -0.0094474 |  | CFL | Bldg | 2580 | 0.775 | 2580 | 0.775 | 1.09 | 1.25 | -0.0036618 | 2580 | 0.775 | 2580 | 0.775 | 1.09 | 1.25 | -0.00366
CFLBldgSCEMtlExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Mtl | Ex | CZ05 | 1.3686 | 0.00015083 | 0 | 1.4586 | 0.0001898 | -0.0065342 | 1.33 | 0.000146 | 0 | 1.42 | 0.000184 | -0.00637 |  | CFL | Bldg | 1370 | 0.151 | 1330 | 0.146 | 1.07 | 1.26 | -0.0047895 | 1370 | 0.151 | 1330 | 0.146 | 1.07 | 1.26 | -0.00479
CFLBldgSCEMtlExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Mtl | Ex | CZ06 | 1.3684 | 0.0001508 | 0 | 1.5684 | 0.00019077 | -0.0033961 | 1.33 | 0.000146 | 0 | 1.53 | 0.000185 | -0.0033 |  | CFL | Bldg | 1370 | 0.151 | 1330 | 0.146 | 1.15 | 1.27 | -0.0024812 | 1370 | 0.151 | 1330 | 0.146 | 1.15 | 1.27 | -0.00248
CFLBldgSCEMtlExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Mtl | Ex | CZ08 | 1.3685 | 0.00015081 | 0 | 1.5885 | 0.00019277 | -0.0028273 | 1.33 | 0.000146 | 0 | 1.55 | 0.000187 | -0.00276 |  | CFL | Bldg | 1370 | 0.151 | 1330 | 0.146 | 1.17 | 1.28 | -0.0020752 | 1370 | 0.151 | 1330 | 0.146 | 1.17 | 1.28 | -0.00208
CFLBldgSCEMtlExCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Mtl | Ex | CZ09 | 1.3679 | 0.00015074 | 0 | 1.5779 | 0.00019769 | -0.0031853 | 1.33 | 0.000146 | 0 | 1.54 | 0.000192 | -0.0031 |  | CFL | Bldg | 1370 | 0.151 | 1330 | 0.146 | 1.16 | 1.32 | -0.0023308 | 1370 | 0.151 | 1330 | 0.146 | 1.16 | 1.32 | -0.00233
CFLBldgSCEMtlExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Mtl | Ex | CZ10 | 1.3658 | 0.00015048 | 0 | 1.5459 | 0.00019738 | -0.0035607 | 1.33 | 0.000146 | 0 | 1.51 | 0.000192 | -0.00348 |  | CFL | Bldg | 1370 | 0.15 | 1330 | 0.146 | 1.14 | 1.32 | -0.0026165 | 1370 | 0.15 | 1330 | 0.146 | 1.14 | 1.32 | -0.00262
CFLBldgSCEMtlExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Mtl | Ex | CZ13 | 1.3669 | 0.00015061 | 0 | 1.5261 | 0.00019654 | -0.00504 | 1.33 | 0.000146 | 0 | 1.48 | 0.000191 | -0.0049108 |  | CFL | Bldg | 1370 | 0.151 | 1330 | 0.146 | 1.11 | 1.31 | -0.0036923 | 1370 | 0.151 | 1330 | 0.146 | 1.11 | 1.31 | -0.00369
CFLBldgSCEMtlExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Mtl | Ex | CZ14 | 1.3662 | 0.00015052 | 0 | 1.5062 | 0.00019742 | -0.0048875 | 1.33 | 0.000146 | 0 | 1.47 | 0.000192 | -0.00477 |  | CFL | Bldg | 1370 | 0.151 | 1330 | 0.146 | 1.11 | 1.32 | -0.0035865 | 1370 | 0.151 | 1330 | 0.146 | 1.11 | 1.32 | -0.00359
CFLBldgSCEMtlExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Mtl | Ex | CZ15 | 1.3658 | 0.00015048 | 0 | 1.6458 | 0.00020038 | -0.0014459 | 1.33 | 0.000146 | 0 | 1.61 | 0.000195 | -0.00141 |  | CFL | Bldg | 1370 | 0.15 | 1330 | 0.146 | 1.21 | 1.34 | -0.0010602 | 1370 | 0.15 | 1330 | 0.146 | 1.21 | 1.34 | -0.00106
CFLBldgSCEMtlExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Mtl | Ex | CZ16 | 1.3666 | 0.00015057 | 0 | 1.3575 | 0.00018949 | -0.0086705 | 1.33 | 0.000146 | 0 | 1.33 | 0.000184 | -0.00846 |  | CFL | Bldg | 1370 | 0.151 | 1330 | 0.146 | 1 | 1.26 | -0.0063609 | 1370 | 0.151 | 1330 | 0.146 | 1 | 1.26 | -0.00636
CFLBldgSCEMtlExIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | Mtl | Ex | IOU | 1.3677 | 0.00015071 | 0 | 1.5738 | 0.00019422 | -0.0032323 | 1.33 | 0.000146 | 0 | 1.5363 | 0.00018856 | -0.0031483 |  | CFL | Bldg | 1370 | 0.151 | 1330 | 0.146 | 1.16 | 1.29 | -0.0023671 | 1370 | 0.151 | 1330 | 0.146 | 1.16 | 1.29 | -0.00237
CFLBldgSCEMtlNewCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Mtl | New | CZ05 | 1.33 | 0.000146 | 0 | 1.37 | 0.000185 | -0.00855 | 1.33 | 0.000146 | 0 | 1.37 | 0.000185 | -0.00855 |  | CFL | Bldg | 1330 | 0.146 | 1330 | 0.146 | 1.03 | 1.27 | -0.0064286 | 1330 | 0.146 | 1330 | 0.146 | 1.03 | 1.27 | -0.00643
CFLBldgSCEMtlNewCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Mtl | New | CZ06 | 1.33 | 0.000146 | 0 | 1.5 | 0.000189 | -0.00453 | 1.33 | 0.000146 | 0 | 1.5 | 0.000189 | -0.00453 |  | CFL | Bldg | 1330 | 0.146 | 1330 | 0.146 | 1.13 | 1.29 | -0.003406 | 1330 | 0.146 | 1330 | 0.146 | 1.13 | 1.29 | -0.00341
CFLBldgSCEMtlNewCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Mtl | New | CZ08 | 1.33 | 0.000146 | 0 | 1.53 | 0.000192 | -0.00377 | 1.33 | 0.000146 | 0 | 1.53 | 0.000192 | -0.00377 |  | CFL | Bldg | 1330 | 0.146 | 1330 | 0.146 | 1.15 | 1.32 | -0.0028346 | 1330 | 0.146 | 1330 | 0.146 | 1.15 | 1.32 | -0.00283
CFLBldgSCEMtlNewCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Mtl | New | CZ09 | 1.33 | 0.000146 | 0 | 1.53 | 0.000197 | -0.0038 | 1.33 | 0.000146 | 0 | 1.53 | 0.000197 | -0.0038 |  | CFL | Bldg | 1330 | 0.146 | 1330 | 0.146 | 1.15 | 1.35 | -0.0028571 | 1330 | 0.146 | 1330 | 0.146 | 1.15 | 1.35 | -0.00286
CFLBldgSCEMtlNewCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Mtl | New | CZ10 | 1.33 | 0.000146 | 0 | 1.51 | 0.000198 | -0.0047 | 1.33 | 0.000146 | 0 | 1.51 | 0.000198 | -0.0047 |  | CFL | Bldg | 1330 | 0.146 | 1330 | 0.146 | 1.14 | 1.36 | -0.0035338 | 1330 | 0.146 | 1330 | 0.146 | 1.14 | 1.36 | -0.00353
CFLBldgSCEMtlNewCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Mtl | New | CZ13 | 1.33 | 0.000146 | 0 | 1.47 | 0.000195 | -0.00607 | 1.33 | 0.000146 | 0 | 1.47 | 0.000195 | -0.00607 |  | CFL | Bldg | 1330 | 0.146 | 1330 | 0.146 | 1.11 | 1.34 | -0.0045639 | 1330 | 0.146 | 1330 | 0.146 | 1.11 | 1.34 | -0.00456
CFLBldgSCEMtlNewCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Mtl | New | CZ14 | 1.33 | 0.000146 | 0 | 1.45 | 0.000197 | -0.00631 | 1.33 | 0.000146 | 0 | 1.45 | 0.000197 | -0.00631 |  | CFL | Bldg | 1330 | 0.146 | 1330 | 0.146 | 1.09 | 1.35 | -0.0047444 | 1330 | 0.146 | 1330 | 0.146 | 1.09 | 1.35 | -0.00474
CFLBldgSCEMtlNewCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Mtl | New | CZ15 | 1.33 | 0.000146 | 0 | 1.62 | 0.000202 | -0.00218 | 1.33 | 0.000146 | 0 | 1.62 | 0.000202 | -0.00218 |  | CFL | Bldg | 1330 | 0.146 | 1330 | 0.146 | 1.22 | 1.38 | -0.0016391 | 1330 | 0.146 | 1330 | 0.146 | 1.22 | 1.38 | -0.00164
CFLBldgSCEMtlNewCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Mtl | New | CZ16 | 1.33 | 0.000146 | 0 | 1.29 | 0.000186 | -0.00983 | 1.33 | 0.000146 | 0 | 1.29 | 0.000186 | -0.00983 |  | CFL | Bldg | 1330 | 0.146 | 1330 | 0.146 | 0.97 | 1.27 | -0.007391 | 1330 | 0.146 | 1330 | 0.146 | 0.97 | 1.27 | -0.00739
CFLBldgSCEMtlNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | Mtl | New | IOU | 1.33 | 0.000146 | 0 | 1.5266 | 0.0001952 | -0.0041202 | 1.33 | 0.000146 | 0 | 1.5266 | 0.0001952 | -0.0041202 |  | CFL | Bldg | 1330 | 0.146 | 1330 | 0.146 | 1.15 | 1.34 | -0.0030979 | 1330 | 0.146 | 1330 | 0.146 | 1.15 | 1.34 | -0.0031
CFLBldgSCENrsExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Nrs | Ex | CZ05 | 3.5685 | 0.00056466 | 0 | 3.6481 | 0.00069655 | -0.052173 | 3.5204 | 0.00055504 | 0 | 3.6 | 0.00068404 | -0.051404 |  | CFL | Bldg | 3570 | 0.565 | 3520 | 0.555 | 1.02 | 1.23 | -0.014602 | 3570 | 0.565 | 3520 | 0.555 | 1.02 | 1.23 | -0.0146
CFLBldgSCENrsExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Nrs | Ex | CZ06 | 3.5684 | 0.00056464 | 0 | 3.888 | 0.00072952 | -0.034484 | 3.5204 | 0.00055504 | 0 | 3.8304 | 0.00071704 | -0.034004 |  | CFL | Bldg | 3570 | 0.565 | 3520 | 0.555 | 1.09 | 1.29 | -0.0096591 | 3570 | 0.565 | 3520 | 0.555 | 1.09 | 1.29 | -0.00966
CFLBldgSCENrsExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Nrs | Ex | CZ08 | 3.5684 | 0.00056464 | 0 | 3.9276 | 0.00073252 | -0.033284 | 3.5204 | 0.00055504 | 0 | 3.87 | 0.00072004 | -0.0329 |  | CFL | Bldg | 3570 | 0.565 | 3520 | 0.555 | 1.1 | 1.3 | -0.0093455 | 3570 | 0.565 | 3520 | 0.555 | 1.1 | 1.3 | -0.00935
CFLBldgSCENrsExCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Nrs | Ex | CZ09 | 3.568 | 0.00056454 | 0 | 3.9375 | 0.00075439 | -0.03398 | 3.5205 | 0.00055505 | 0 | 3.8805 | 0.0007411 | -0.0336 |  | CFL | Bldg | 3570 | 0.565 | 3520 | 0.555 | 1.1 | 1.34 | -0.0095441 | 3570 | 0.565 | 3520 | 0.555 | 1.1 | 1.34 | -0.00954
CFLBldgSCENrsExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Nrs | Ex | CZ10 | 3.5668 | 0.00056427 | 0 | 3.886 | 0.00075303 | -0.03396 | 3.5208 | 0.00055508 | 0 | 3.8308 | 0.00074108 | -0.0335 |  | CFL | Bldg | 3570 | 0.564 | 3520 | 0.555 | 1.09 | 1.34 | -0.0095149 | 3570 | 0.564 | 3520 | 0.555 | 1.09 | 1.34 | -0.00951
CFLBldgSCENrsExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Nrs | Ex | CZ13 | 3.5674 | 0.00056441 | 0 | 3.8467 | 0.00074522 | -0.039267 | 3.5206 | 0.00055506 | 0 | 3.8 | 0.00073307 | -0.038707 |  | CFL | Bldg | 3570 | 0.564 | 3520 | 0.555 | 1.08 | 1.32 | -0.010994 | 3570 | 0.564 | 3520 | 0.555 | 1.08 | 1.32 | -0.011
CFLBldgSCENrsExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Nrs | Ex | CZ14 | 3.5671 | 0.00056434 | 0 | 3.8564 | 0.00074513 | -0.040664 | 3.5207 | 0.00055507 | 0 | 3.81 | 0.00073307 | -0.0402 |  | CFL | Bldg | 3570 | 0.564 | 3520 | 0.555 | 1.08 | 1.32 | -0.011418 | 3570 | 0.564 | 3520 | 0.555 | 1.08 | 1.32 | -0.0114
CFLBldgSCENrsExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Nrs | Ex | CZ15 | 3.5668 | 0.00056427 | 0 | 4.146 | 0.00075903 | -0.020384 | 3.5208 | 0.00055508 | 0 | 4.0908 | 0.00074616 | -0.020108 |  | CFL | Bldg | 3570 | 0.564 | 3520 | 0.555 | 1.16 | 1.34 | -0.0057112 | 3570 | 0.564 | 3520 | 0.555 | 1.16 | 1.34 | -0.00571
CFLBldgSCENrsExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Nrs | Ex | CZ16 | 3.567 | 0.00056432 | 0 | 3.557 | 0.00071209 | -0.059239 | 3.5208 | 0.00055508 | 0 | 3.52 | 0.00070008 | -0.0585 |  | CFL | Bldg | 3570 | 0.564 | 3520 | 0.555 | 1 | 1.26 | -0.016616 | 3570 | 0.564 | 3520 | 0.555 | 1 | 1.26 | -0.0166
CFLBldgSCENrsExIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | Nrs | Ex | IOU | 3.5679 | 0.00056454 | 0 | 3.9016 | 0.00073855 | -0.03467 | 3.5205 | 0.00055505 | 0 | 3.8458 | 0.00072605 | -0.034231 |  | CFL | Bldg | 3570 | 0.565 | 3520 | 0.555 | 1.09 | 1.31 | -0.0097231 | 3570 | 0.565 | 3520 | 0.555 | 1.09 | 1.31 | -0.00972
CFLBldgSCENrsNewCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Nrs | New | CZ05 | 3.53 | 0.000556 | 0 | 3.46 | 0.000677 | -0.0575 | 3.53 | 0.000556 | 0 | 3.46 | 0.000677 | -0.0575 |  | CFL | Bldg | 3530 | 0.556 | 3530 | 0.556 | 0.98 | 1.22 | -0.016289 | 3530 | 0.556 | 3530 | 0.556 | 0.98 | 1.22 | -0.0163
CFLBldgSCENrsNewCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Nrs | New | CZ06 | 3.53 | 0.000556 | 0 | 3.67 | 0.000708 | -0.0353 | 3.53 | 0.000556 | 0 | 3.67 | 0.000708 | -0.0353 |  | CFL | Bldg | 3530 | 0.556 | 3530 | 0.556 | 1.04 | 1.27 | -0.01 | 3530 | 0.556 | 3530 | 0.556 | 1.04 | 1.27 | -0.01
CFLBldgSCENrsNewCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Nrs | New | CZ08 | 3.53 | 0.000556 | 0 | 3.73 | 0.00071 | -0.0336 | 3.53 | 0.000556 | 0 | 3.73 | 0.00071 | -0.0336 |  | CFL | Bldg | 3530 | 0.556 | 3530 | 0.556 | 1.06 | 1.28 | -0.0095184 | 3530 | 0.556 | 3530 | 0.556 | 1.06 | 1.28 | -0.00952
CFLBldgSCENrsNewCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Nrs | New | CZ09 | 3.53 | 0.000556 | 0 | 3.75 | 0.000736 | -0.0339 | 3.53 | 0.000556 | 0 | 3.75 | 0.000736 | -0.0339 |  | CFL | Bldg | 3530 | 0.556 | 3530 | 0.556 | 1.06 | 1.32 | -0.0096034 | 3530 | 0.556 | 3530 | 0.556 | 1.06 | 1.32 | -0.0096
CFLBldgSCENrsNewCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Nrs | New | CZ10 | 3.53 | 0.000556 | 0 | 3.77 | 0.000738 | -0.0346 | 3.53 | 0.000556 | 0 | 3.77 | 0.000738 | -0.0346 |  | CFL | Bldg | 3530 | 0.556 | 3530 | 0.556 | 1.07 | 1.33 | -0.0098017 | 3530 | 0.556 | 3530 | 0.556 | 1.07 | 1.33 | -0.0098
CFLBldgSCENrsNewCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Nrs | New | CZ13 | 3.53 | 0.000556 | 0 | 3.74 | 0.000731 | -0.0409 | 3.53 | 0.000556 | 0 | 3.74 | 0.000731 | -0.0409 |  | CFL | Bldg | 3530 | 0.556 | 3530 | 0.556 | 1.06 | 1.31 | -0.011586 | 3530 | 0.556 | 3530 | 0.556 | 1.06 | 1.31 | -0.0116
CFLBldgSCENrsNewCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Nrs | New | CZ14 | 3.53 | 0.000556 | 0 | 3.74 | 0.000719 | -0.0427 | 3.53 | 0.000556 | 0 | 3.74 | 0.000719 | -0.0427 |  | CFL | Bldg | 3530 | 0.556 | 3530 | 0.556 | 1.06 | 1.29 | -0.012096 | 3530 | 0.556 | 3530 | 0.556 | 1.06 | 1.29 | -0.0121
CFLBldgSCENrsNewCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Nrs | New | CZ15 | 3.53 | 0.000556 | 0 | 4.05 | 0.000739 | -0.0165 | 3.53 | 0.000556 | 0 | 4.05 | 0.000739 | -0.0165 |  | CFL | Bldg | 3530 | 0.556 | 3530 | 0.556 | 1.15 | 1.33 | -0.0046742 | 3530 | 0.556 | 3530 | 0.556 | 1.15 | 1.33 | -0.00467
CFLBldgSCENrsNewCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Nrs | New | CZ16 | 3.53 | 0.000556 | 0 | 3.46 | 0.000695 | -0.0635 | 3.53 | 0.000556 | 0 | 3.46 | 0.000695 | -0.0635 |  | CFL | Bldg | 3530 | 0.556 | 3530 | 0.556 | 0.98 | 1.25 | -0.017989 | 3530 | 0.556 | 3530 | 0.556 | 0.98 | 1.25 | -0.018
CFLBldgSCENrsNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | Nrs | New | IOU | 3.53 | 0.000556 | 0 | 3.7355 | 0.00072199 | -0.035239 | 3.53 | 0.000556 | 0 | 3.7355 | 0.00072199 | -0.035239 |  | CFL | Bldg | 3530 | 0.556 | 3530 | 0.556 | 1.06 | 1.3 | -0.0099826 | 3530 | 0.556 | 3530 | 0.556 | 1.06 | 1.3 | -0.00998
CFLBldgSCEOfLExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | OfL | Ex | CZ05 | 2.9972 | 0.00062423 | 0 | 3.3169 | 0.000808 | -0.020681 | 2.88 | 0.00059298 | 0 | 3.1998 | 0.00076698 | -0.0199 |  | CFL | Bldg | 3000 | 0.624 | 2880 | 0.593 | 1.11 | 1.29 | -0.0069097 | 3000 | 0.624 | 2880 | 0.593 | 1.11 | 1.29 | -0.00691
CFLBldgSCEOfLExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | OfL | Ex | CZ06 | 2.9968 | 0.00062412 | 0 | 3.4565 | 0.00082981 | -0.013387 | 2.88 | 0.00059298 | 0 | 3.33 | 0.00078796 | -0.0129 |  | CFL | Bldg | 3000 | 0.624 | 2880 | 0.593 | 1.16 | 1.33 | -0.0044792 | 3000 | 0.624 | 2880 | 0.593 | 1.16 | 1.33 | -0.00448
CFLBldgSCEOfLExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | OfL | Ex | CZ08 | 3.006 | 0.00062679 | 0 | 3.4971 | 0.00085136 | -0.012828 | 2.88 | 0.00059297 | 0 | 3.35 | 0.00080495 | -0.0123 |  | CFL | Bldg | 3010 | 0.627 | 2880 | 0.593 | 1.16 | 1.36 | -0.0042708 | 3010 | 0.627 | 2880 | 0.593 | 1.16 | 1.36 | -0.00427
CFLBldgSCEOfLExCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | OfL | Ex | CZ09 | 3.0034 | 0.00062607 | 0 | 3.4741 | 0.00085037 | -0.015221 | 2.88 | 0.00059296 | 0 | 3.3396 | 0.00080492 | -0.0146 |  | CFL | Bldg | 3000 | 0.626 | 2880 | 0.593 | 1.16 | 1.36 | -0.0050694 | 3000 | 0.626 | 2880 | 0.593 | 1.16 | 1.36 | -0.00507
CFLBldgSCEOfLExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | OfL | Ex | CZ10 | 3.0003 | 0.00062526 | 0 | 3.4705 | 0.00084429 | -0.012295 | 2.88 | 0.00059291 | 0 | 3.3381 | 0.00080001 | -0.0118 |  | CFL | Bldg | 3000 | 0.625 | 2880 | 0.593 | 1.16 | 1.35 | -0.0040972 | 3000 | 0.625 | 2880 | 0.593 | 1.16 | 1.35 | -0.0041
CFLBldgSCEOfLExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | OfL | Ex | CZ13 | 2.9911 | 0.00062254 | 0 | 3.4396 | 0.00082273 | -0.017948 | 2.88 | 0.00059293 | 0 | 3.3193 | 0.00078385 | -0.017393 |  | CFL | Bldg | 2990 | 0.623 | 2880 | 0.593 | 1.15 | 1.32 | -0.0060391 | 2990 | 0.623 | 2880 | 0.593 | 1.15 | 1.32 | -0.00604
CFLBldgSCEOfLExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | OfL | Ex | CZ14 | 2.9915 | 0.00062266 | 0 | 3.4008 | 0.00083781 | -0.01735 | 2.88 | 0.00059293 | 0 | 3.28 | 0.00079693 | -0.0167 |  | CFL | Bldg | 2990 | 0.623 | 2880 | 0.593 | 1.14 | 1.34 | -0.0057986 | 2990 | 0.623 | 2880 | 0.593 | 1.14 | 1.34 | -0.0058
CFLBldgSCEOfLExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | OfL | Ex | CZ15 | 2.9892 | 0.00062209 | 0 | 3.6565 | 0.0008351 | -0.007643 | 2.88 | 0.00059297 | 0 | 3.5291 | 0.00079597 | -0.0073791 |  | CFL | Bldg | 2990 | 0.622 | 2880 | 0.593 | 1.23 | 1.34 | -0.0025622 | 2990 | 0.622 | 2880 | 0.593 | 1.23 | 1.34 | -0.00256
CFLBldgSCEOfLExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | OfL | Ex | CZ16 | 2.9917 | 0.00062276 | 0 | 3.1617 | 0.00079018 | -0.03171 | 2.88 | 0.00059298 | 0 | 3.05 | 0.00075202 | -0.030593 |  | CFL | Bldg | 2990 | 0.623 | 2880 | 0.593 | 1.06 | 1.27 | -0.010623 | 2990 | 0.623 | 2880 | 0.593 | 1.06 | 1.27 | -0.0106
CFLBldgSCEOfLExIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | OfL | Ex | IOU | 3.0014 | 0.00062548 | 0 | 3.476 | 0.00084277 | -0.013663 | 2.88 | 0.00059297 | 0 | 3.3403 | 0.00079848 | -0.013127 |  | CFL | Bldg | 3000 | 0.625 | 2880 | 0.593 | 1.16 | 1.35 | -0.004558 | 3000 | 0.625 | 2880 | 0.593 | 1.16 | 1.35 | -0.00456
CFLBldgSCEOfLNewCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | OfL | New | CZ05 | 2.88 | 0.000592 | 0 | 3.18 | 0.000734 | -0.00936 | 2.88 | 0.000592 | 0 | 3.18 | 0.000734 | -0.00936 |  | CFL | Bldg | 2880 | 0.592 | 2880 | 0.592 | 1.1 | 1.24 | -0.00325 | 2880 | 0.592 | 2880 | 0.592 | 1.1 | 1.24 | -0.00325
CFLBldgSCEOfLNewCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | OfL | New | CZ06 | 2.88 | 0.000592 | 0 | 3.31 | 0.000746 | -0.00625 | 2.88 | 0.000592 | 0 | 3.31 | 0.000746 | -0.00625 |  | CFL | Bldg | 2880 | 0.592 | 2880 | 0.592 | 1.15 | 1.26 | -0.0021701 | 2880 | 0.592 | 2880 | 0.592 | 1.15 | 1.26 | -0.00217
CFLBldgSCEOfLNewCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | OfL | New | CZ08 | 2.88 | 0.000592 | 0 | 3.32 | 0.000756 | -0.00544 | 2.88 | 0.000592 | 0 | 3.32 | 0.000756 | -0.00544 |  | CFL | Bldg | 2880 | 0.592 | 2880 | 0.592 | 1.15 | 1.28 | -0.0018889 | 2880 | 0.592 | 2880 | 0.592 | 1.15 | 1.28 | -0.00189
CFLBldgSCEOfLNewCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | OfL | New | CZ09 | 2.88 | 0.000592 | 0 | 3.31 | 0.000778 | -0.0076 | 2.88 | 0.000592 | 0 | 3.31 | 0.000778 | -0.0076 |  | CFL | Bldg | 2880 | 0.592 | 2880 | 0.592 | 1.15 | 1.31 | -0.0026389 | 2880 | 0.592 | 2880 | 0.592 | 1.15 | 1.31 | -0.00264
CFLBldgSCEOfLNewCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | OfL | New | CZ10 | 2.88 | 0.000592 | 0 | 3.34 | 0.000781 | -0.00659 | 2.88 | 0.000592 | 0 | 3.34 | 0.000781 | -0.00659 |  | CFL | Bldg | 2880 | 0.592 | 2880 | 0.592 | 1.16 | 1.32 | -0.0022882 | 2880 | 0.592 | 2880 | 0.592 | 1.16 | 1.32 | -0.00229
CFLBldgSCEOfLNewCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | OfL | New | CZ13 | 2.88 | 0.000592 | 0 | 3.27 | 0.00076 | -0.00982 | 2.88 | 0.000592 | 0 | 3.27 | 0.00076 | -0.00982 |  | CFL | Bldg | 2880 | 0.592 | 2880 | 0.592 | 1.14 | 1.28 | -0.0034097 | 2880 | 0.592 | 2880 | 0.592 | 1.14 | 1.28 | -0.00341
CFLBldgSCEOfLNewCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | OfL | New | CZ14 | 2.88 | 0.000592 | 0 | 3.28 | 0.000789 | -0.00867 | 2.88 | 0.000592 | 0 | 3.28 | 0.000789 | -0.00867 |  | CFL | Bldg | 2880 | 0.592 | 2880 | 0.592 | 1.14 | 1.33 | -0.0030104 | 2880 | 0.592 | 2880 | 0.592 | 1.14 | 1.33 | -0.00301
CFLBldgSCEOfLNewCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | OfL | New | CZ15 | 2.88 | 0.000592 | 0 | 3.46 | 0.000774 | -0.0032 | 2.88 | 0.000592 | 0 | 3.46 | 0.000774 | -0.0032 |  | CFL | Bldg | 2880 | 0.592 | 2880 | 0.592 | 1.2 | 1.31 | -0.0011111 | 2880 | 0.592 | 2880 | 0.592 | 1.2 | 1.31 | -0.00111
CFLBldgSCEOfLNewCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | OfL | New | CZ16 | 2.88 | 0.000592 | 0 | 3.09 | 0.000742 | -0.024 | 2.88 | 0.000592 | 0 | 3.09 | 0.000742 | -0.024 |  | CFL | Bldg | 2880 | 0.592 | 2880 | 0.592 | 1.07 | 1.25 | -0.0083333 | 2880 | 0.592 | 2880 | 0.592 | 1.07 | 1.25 | -0.00833
CFLBldgSCEOfLNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | OfL | New | IOU | 2.88 | 0.000592 | 0 | 3.321 | 0.00076581 | -0.0066909 | 2.88 | 0.000592 | 0 | 3.321 | 0.00076581 | -0.0066909 |  | CFL | Bldg | 2880 | 0.592 | 2880 | 0.592 | 1.15 | 1.29 | -0.0023232 | 2880 | 0.592 | 2880 | 0.592 | 1.15 | 1.29 | -0.00232
CFLBldgSCEOfSExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | OfS | Ex | CZ05 | 2.9657 | 0.00067342 | 0 | 3.2247 | 0.00084621 | -0.009276 | 2.72 | 0.00059402 | 0 | 2.96 | 0.00074602 | -0.0085198 |  | CFL | Bldg | 2970 | 0.673 | 2720 | 0.594 | 1.09 | 1.26 | -0.0031323 | 2970 | 0.673 | 2720 | 0.594 | 1.09 | 1.26 | -0.00313
CFLBldgSCEOfSExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | OfS | Ex | CZ06 | 2.9658 | 0.00067342 | 0 | 3.3741 | 0.00085816 | -0.0044787 | 2.72 | 0.00059402 | 0 | 3.1 | 0.00075702 | -0.00411 |  | CFL | Bldg | 2970 | 0.673 | 2720 | 0.594 | 1.14 | 1.27 | -0.001511 | 2970 | 0.673 | 2720 | 0.594 | 1.14 | 1.27 | -0.00151
CFLBldgSCEOfSExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | OfS | Ex | CZ08 | 3.0338 | 0.00069632 | 0 | 3.4731 | 0.00089259 | -0.0041561 | 2.72 | 0.00059405 | 0 | 3.12 | 0.00076138 | -0.00373 |  | CFL | Bldg | 3030 | 0.696 | 2720 | 0.594 | 1.15 | 1.28 | -0.0013713 | 3030 | 0.696 | 2720 | 0.594 | 1.15 | 1.28 | -0.00137
CFLBldgSCEOfSExCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | OfS | Ex | CZ09 | 3.0318 | 0.00069563 | 0 | 3.4607 | 0.00089992 | -0.00515 | 2.72 | 0.00059405 | 0 | 3.1005 | 0.00076837 | -0.0046274 |  | CFL | Bldg | 3030 | 0.696 | 2720 | 0.594 | 1.14 | 1.29 | -0.0017012 | 3030 | 0.696 | 2720 | 0.594 | 1.14 | 1.29 | -0.0017
CFLBldgSCEOfSExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | OfS | Ex | CZ10 | 3.0288 | 0.00069477 | 0 | 3.4048 | 0.00089154 | -0.0048123 | 2.72 | 0.00059409 | 0 | 3.06 | 0.00076209 | -0.0043271 |  | CFL | Bldg | 3030 | 0.695 | 2720 | 0.594 | 1.12 | 1.28 | -0.0015909 | 3030 | 0.695 | 2720 | 0.594 | 1.12 | 1.28 | -0.00159
CFLBldgSCEOfSExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | OfS | Ex | CZ13 | 2.9648 | 0.00067315 | 0 | 3.2636 | 0.0008578 | -0.011142 | 2.72 | 0.00059406 | 0 | 3 | 0.00075706 | -0.0102 |  | CFL | Bldg | 2960 | 0.673 | 2720 | 0.594 | 1.1 | 1.27 | -0.00375 | 2960 | 0.673 | 2720 | 0.594 | 1.1 | 1.27 | -0.00375
CFLBldgSCEOfSExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | OfS | Ex | CZ14 | 2.9594 | 0.00067143 | 0 | 3.2678 | 0.00087245 | -0.0088106 | 2.72 | 0.00059408 | 0 | 3.01 | 0.00077208 | -0.0081108 |  | CFL | Bldg | 2960 | 0.671 | 2720 | 0.594 | 1.11 | 1.3 | -0.0029819 | 2960 | 0.671 | 2720 | 0.594 | 1.11 | 1.3 | -0.00298
CFLBldgSCEOfSExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | OfS | Ex | CZ15 | 2.9719 | 0.00067565 | 0 | 3.5719 | 0.00085898 | -0.0014059 | 2.72 | 0.00059409 | 0 | 3.2794 | 0.00075509 | -0.0012809 |  | CFL | Bldg | 2970 | 0.676 | 2720 | 0.594 | 1.21 | 1.27 | -0.00047091 | 2970 | 0.676 | 2720 | 0.594 | 1.21 | 1.27 | -0.000471
CFLBldgSCEOfSExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | OfS | Ex | CZ16 | 2.9734 | 0.00067609 | 0 | 2.9834 | 0.00084559 | -0.021057 | 2.72 | 0.00059407 | 0 | 2.73 | 0.00074307 | -0.0193 |  | CFL | Bldg | 2970 | 0.676 | 2720 | 0.594 | 1 | 1.25 | -0.0070956 | 2970 | 0.676 | 2720 | 0.594 | 1 | 1.25 | -0.0071
CFLBldgSCEOfSExIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | OfS | Ex | IOU | 3.007 | 0.00068734 | 0 | 3.4155 | 0.00088062 | -0.0051201 | 2.72 | 0.00059406 | 0 | 3.0933 | 0.00076095 | -0.0046419 |  | CFL | Bldg | 3010 | 0.687 | 2720 | 0.594 | 1.14 | 1.28 | -0.0017066 | 3010 | 0.687 | 2720 | 0.594 | 1.14 | 1.28 | -0.00171
CFLBldgSCEOfSNewCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | OfS | New | CZ05 | 2.72 | 0.000595 | 0 | 2.85 | 0.000736 | -0.00771 | 2.72 | 0.000595 | 0 | 2.85 | 0.000736 | -0.00771 |  | CFL | Bldg | 2720 | 0.595 | 2720 | 0.595 | 1.05 | 1.24 | -0.0028346 | 2720 | 0.595 | 2720 | 0.595 | 1.05 | 1.24 | -0.00283
CFLBldgSCEOfSNewCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | OfS | New | CZ06 | 2.72 | 0.000595 | 0 | 3 | 0.000746 | -0.00311 | 2.72 | 0.000595 | 0 | 3 | 0.000746 | -0.00311 |  | CFL | Bldg | 2720 | 0.595 | 2720 | 0.595 | 1.1 | 1.25 | -0.0011434 | 2720 | 0.595 | 2720 | 0.595 | 1.1 | 1.25 | -0.00114
CFLBldgSCEOfSNewCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | OfS | New | CZ08 | 2.72 | 0.000595 | 0 | 3.02 | 0.000755 | -0.00275 | 2.72 | 0.000595 | 0 | 3.02 | 0.000755 | -0.00275 |  | CFL | Bldg | 2720 | 0.595 | 2720 | 0.595 | 1.11 | 1.27 | -0.001011 | 2720 | 0.595 | 2720 | 0.595 | 1.11 | 1.27 | -0.00101
CFLBldgSCEOfSNewCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | OfS | New | CZ09 | 2.72 | 0.000595 | 0 | 3.02 | 0.000774 | -0.00311 | 2.72 | 0.000595 | 0 | 3.02 | 0.000774 | -0.00311 |  | CFL | Bldg | 2720 | 0.595 | 2720 | 0.595 | 1.11 | 1.3 | -0.0011434 | 2720 | 0.595 | 2720 | 0.595 | 1.11 | 1.3 | -0.00114
CFLBldgSCEOfSNewCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | OfS | New | CZ10 | 2.72 | 0.000595 | 0 | 3.05 | 0.000784 | -0.00218 | 2.72 | 0.000595 | 0 | 3.05 | 0.000784 | -0.00218 |  | CFL | Bldg | 2720 | 0.595 | 2720 | 0.595 | 1.12 | 1.32 | -0.00080147 | 2720 | 0.595 | 2720 | 0.595 | 1.12 | 1.32 | -0.000801
CFLBldgSCEOfSNewCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | OfS | New | CZ13 | 2.72 | 0.000595 | 0 | 2.96 | 0.00077 | -0.00817 | 2.72 | 0.000595 | 0 | 2.96 | 0.00077 | -0.00817 |  | CFL | Bldg | 2720 | 0.595 | 2720 | 0.595 | 1.09 | 1.29 | -0.0030037 | 2720 | 0.595 | 2720 | 0.595 | 1.09 | 1.29 | -0.003
CFLBldgSCEOfSNewCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | OfS | New | CZ14 | 2.72 | 0.000595 | 0 | 2.98 | 0.000783 | -0.00681 | 2.72 | 0.000595 | 0 | 2.98 | 0.000783 | -0.00681 |  | CFL | Bldg | 2720 | 0.595 | 2720 | 0.595 | 1.1 | 1.32 | -0.0025037 | 2720 | 0.595 | 2720 | 0.595 | 1.1 | 1.32 | -0.0025
CFLBldgSCEOfSNewCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | OfS | New | CZ15 | 2.72 | 0.000595 | 0 | 3.2 | 0.000792 | -0.000204 | 2.72 | 0.000595 | 0 | 3.2 | 0.000792 | -0.000204 |  | CFL | Bldg | 2720 | 0.595 | 2720 | 0.595 | 1.18 | 1.33 | -7.5e-05 | 2720 | 0.595 | 2720 | 0.595 | 1.18 | 1.33 | -7.5e-05
CFLBldgSCEOfSNewCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | OfS | New | CZ16 | 2.72 | 0.000595 | 0 | 2.72 | 0.000747 | -0.0182 | 2.72 | 0.000595 | 0 | 2.72 | 0.000747 | -0.0182 |  | CFL | Bldg | 2720 | 0.595 | 2720 | 0.595 | 1 | 1.26 | -0.0066912 | 2720 | 0.595 | 2720 | 0.595 | 1 | 1.26 | -0.00669
CFLBldgSCEOfSNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | OfS | New | IOU | 2.72 | 0.000595 | 0 | 3.0289 | 0.00076826 | -0.0031781 | 2.72 | 0.000595 | 0 | 3.0289 | 0.00076826 | -0.0031781 |  | CFL | Bldg | 2720 | 0.595 | 2720 | 0.595 | 1.11 | 1.29 | -0.0011684 | 2720 | 0.595 | 2720 | 0.595 | 1.11 | 1.29 | -0.00117
CFLBldgSCERFFExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RFF | Ex | CZ05 | 4.81 | 0.000808 | 0 | 5 | 0.000957 | -0.0449 | 4.81 | 0.000808 | 0 | 5 | 0.000957 | -0.0449 |  | CFL | Bldg | 4810 | 0.808 | 4810 | 0.808 | 1.04 | 1.18 | -0.0093347 | 4810 | 0.808 | 4810 | 0.808 | 1.04 | 1.18 | -0.00933
CFLBldgSCERFFExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RFF | Ex | CZ06 | 4.81 | 0.000808 | 0 | 5.24 | 0.000978 | -0.025105 | 4.81 | 0.000808 | 0 | 5.24 | 0.000978 | -0.025105 |  | CFL | Bldg | 4810 | 0.808 | 4810 | 0.808 | 1.09 | 1.21 | -0.0052193 | 4810 | 0.808 | 4810 | 0.808 | 1.09 | 1.21 | -0.00522
CFLBldgSCERFFExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RFF | Ex | CZ08 | 4.81 | 0.000808 | 0 | 5.2936 | 0.00097 | -0.0221 | 4.81 | 0.000808 | 0 | 5.2936 | 0.00097 | -0.0221 |  | CFL | Bldg | 4810 | 0.808 | 4810 | 0.808 | 1.1 | 1.2 | -0.0045946 | 4810 | 0.808 | 4810 | 0.808 | 1.1 | 1.2 | -0.00459
CFLBldgSCERFFExCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RFF | Ex | CZ09 | 4.81 | 0.000808 | 0 | 5.3036 | 0.00099 | -0.0231 | 4.81 | 0.000808 | 0 | 5.3036 | 0.00099 | -0.0231 |  | CFL | Bldg | 4810 | 0.808 | 4810 | 0.808 | 1.1 | 1.23 | -0.0048025 | 4810 | 0.808 | 4810 | 0.808 | 1.1 | 1.23 | -0.0048
CFLBldgSCERFFExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RFF | Ex | CZ10 | 4.81 | 0.000808 | 0 | 5.2 | 0.000974 | -0.0256 | 4.81 | 0.000808 | 0 | 5.2 | 0.000974 | -0.0256 |  | CFL | Bldg | 4810 | 0.808 | 4810 | 0.808 | 1.08 | 1.21 | -0.0053222 | 4810 | 0.808 | 4810 | 0.808 | 1.08 | 1.21 | -0.00532
CFLBldgSCERFFExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RFF | Ex | CZ13 | 4.81 | 0.000808 | 0 | 5.2 | 0.00098 | -0.0338 | 4.81 | 0.000808 | 0 | 5.2 | 0.00098 | -0.0338 |  | CFL | Bldg | 4810 | 0.808 | 4810 | 0.808 | 1.08 | 1.21 | -0.007027 | 4810 | 0.808 | 4810 | 0.808 | 1.08 | 1.21 | -0.00703
CFLBldgSCERFFExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RFF | Ex | CZ14 | 4.81 | 0.000808 | 0 | 5.16 | 0.000991 | -0.0357 | 4.81 | 0.000808 | 0 | 5.16 | 0.000991 | -0.0357 |  | CFL | Bldg | 4810 | 0.808 | 4810 | 0.808 | 1.07 | 1.23 | -0.007422 | 4810 | 0.808 | 4810 | 0.808 | 1.07 | 1.23 | -0.00742
CFLBldgSCERFFExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RFF | Ex | CZ15 | 4.81 | 0.000808 | 0 | 5.5219 | 0.000987 | -0.012 | 4.81 | 0.000808 | 0 | 5.5219 | 0.000987 | -0.012 |  | CFL | Bldg | 4810 | 0.808 | 4810 | 0.808 | 1.15 | 1.22 | -0.0024948 | 4810 | 0.808 | 4810 | 0.808 | 1.15 | 1.22 | -0.00249
CFLBldgSCERFFExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RFF | Ex | CZ16 | 4.81 | 0.000808 | 0 | 4.81 | 0.000959 | -0.0649 | 4.81 | 0.000808 | 0 | 4.81 | 0.000959 | -0.0649 |  | CFL | Bldg | 4810 | 0.808 | 4810 | 0.808 | 1 | 1.19 | -0.013493 | 4810 | 0.808 | 4810 | 0.808 | 1 | 1.19 | -0.0135
CFLBldgSCERFFExIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | RFF | Ex | IOU | 4.81 | 0.000808 | 0 | 5.2537 | 0.00097739 | -0.02501 | 4.81 | 0.000808 | 0 | 5.2537 | 0.00097739 | -0.02501 |  | CFL | Bldg | 4810 | 0.808 | 4810 | 0.808 | 1.09 | 1.21 | -0.0051995 | 4810 | 0.808 | 4810 | 0.808 | 1.09 | 1.21 | -0.0052
CFLBldgSCERFFNewCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RFF | New | CZ05 | 4.81 | 0.000808 | 0 | 4.93 | 0.000971 | -0.0436 | 4.81 | 0.000808 | 0 | 4.93 | 0.000971 | -0.0436 |  | CFL | Bldg | 4810 | 0.808 | 4810 | 0.808 | 1.02 | 1.2 | -0.0090644 | 4810 | 0.808 | 4810 | 0.808 | 1.02 | 1.2 | -0.00906
CFLBldgSCERFFNewCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RFF | New | CZ06 | 4.81 | 0.000808 | 0 | 5.16 | 0.000999 | -0.0259 | 4.81 | 0.000808 | 0 | 5.16 | 0.000999 | -0.0259 |  | CFL | Bldg | 4810 | 0.808 | 4810 | 0.808 | 1.07 | 1.24 | -0.0053846 | 4810 | 0.808 | 4810 | 0.808 | 1.07 | 1.24 | -0.00538
CFLBldgSCERFFNewCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RFF | New | CZ08 | 4.81 | 0.000808 | 0 | 5.18 | 0.00097 | -0.0255 | 4.81 | 0.000808 | 0 | 5.18 | 0.00097 | -0.0255 |  | CFL | Bldg | 4810 | 0.808 | 4810 | 0.808 | 1.08 | 1.2 | -0.0053015 | 4810 | 0.808 | 4810 | 0.808 | 1.08 | 1.2 | -0.0053
CFLBldgSCERFFNewCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RFF | New | CZ09 | 4.81 | 0.000808 | 0 | 5.27 | 0.00104 | -0.0285 | 4.81 | 0.000808 | 0 | 5.27 | 0.00104 | -0.0285 |  | CFL | Bldg | 4810 | 0.808 | 4810 | 0.808 | 1.1 | 1.29 | -0.0059252 | 4810 | 0.808 | 4810 | 0.808 | 1.1 | 1.29 | -0.00593
CFLBldgSCERFFNewCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RFF | New | CZ10 | 4.81 | 0.000808 | 0 | 5.3 | 0.00104 | -0.0296 | 4.81 | 0.000808 | 0 | 5.3 | 0.00104 | -0.0296 |  | CFL | Bldg | 4810 | 0.808 | 4810 | 0.808 | 1.1 | 1.29 | -0.0061538 | 4810 | 0.808 | 4810 | 0.808 | 1.1 | 1.29 | -0.00615
CFLBldgSCERFFNewCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RFF | New | CZ13 | 4.81 | 0.000808 | 0 | 5.28 | 0.00104 | -0.0388 | 4.81 | 0.000808 | 0 | 5.28 | 0.00104 | -0.0388 |  | CFL | Bldg | 4810 | 0.808 | 4810 | 0.808 | 1.1 | 1.29 | -0.0080665 | 4810 | 0.808 | 4810 | 0.808 | 1.1 | 1.29 | -0.00807
CFLBldgSCERFFNewCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RFF | New | CZ14 | 4.81 | 0.000808 | 0 | 5.27 | 0.00105 | -0.0413 | 4.81 | 0.000808 | 0 | 5.27 | 0.00105 | -0.0413 |  | CFL | Bldg | 4810 | 0.808 | 4810 | 0.808 | 1.1 | 1.3 | -0.0085863 | 4810 | 0.808 | 4810 | 0.808 | 1.1 | 1.3 | -0.00859
CFLBldgSCERFFNewCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RFF | New | CZ15 | 4.81 | 0.000808 | 0 | 5.65 | 0.00106 | -0.0147 | 4.81 | 0.000808 | 0 | 5.65 | 0.00106 | -0.0147 |  | CFL | Bldg | 4810 | 0.808 | 4810 | 0.808 | 1.17 | 1.31 | -0.0030561 | 4810 | 0.808 | 4810 | 0.808 | 1.17 | 1.31 | -0.00306
CFLBldgSCERFFNewCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RFF | New | CZ16 | 4.81 | 0.000808 | 0 | 4.87 | 0.000998 | -0.0697 | 4.81 | 0.000808 | 0 | 4.87 | 0.000998 | -0.0697 |  | CFL | Bldg | 4810 | 0.808 | 4810 | 0.808 | 1.01 | 1.24 | -0.014491 | 4810 | 0.808 | 4810 | 0.808 | 1.01 | 1.24 | -0.0145
CFLBldgSCERFFNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | RFF | New | IOU | 4.81 | 0.000808 | 0 | 5.2452 | 0.0010151 | -0.028553 | 4.81 | 0.000808 | 0 | 5.2452 | 0.0010151 | -0.028553 |  | CFL | Bldg | 4810 | 0.808 | 4810 | 0.808 | 1.09 | 1.26 | -0.0059362 | 4810 | 0.808 | 4810 | 0.808 | 1.09 | 1.26 | -0.00594
CFLBldgSCERSDExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RSD | Ex | CZ05 | 4.83 | 0.0008 | 0 | 5.07 | 0.000973 | -0.0434 | 4.83 | 0.0008 | 0 | 5.07 | 0.000973 | -0.0434 |  | CFL | Bldg | 4830 | 0.8 | 4830 | 0.8 | 1.05 | 1.22 | -0.0089855 | 4830 | 0.8 | 4830 | 0.8 | 1.05 | 1.22 | -0.00899
CFLBldgSCERSDExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RSD | Ex | CZ06 | 4.83 | 0.0008 | 0 | 5.37 | 0.000985 | -0.0223 | 4.83 | 0.0008 | 0 | 5.37 | 0.000985 | -0.0223 |  | CFL | Bldg | 4830 | 0.8 | 4830 | 0.8 | 1.11 | 1.23 | -0.004617 | 4830 | 0.8 | 4830 | 0.8 | 1.11 | 1.23 | -0.00462
CFLBldgSCERSDExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RSD | Ex | CZ08 | 4.83 | 0.0008 | 0 | 5.41 | 0.00096 | -0.019 | 4.83 | 0.0008 | 0 | 5.41 | 0.00096 | -0.019 |  | CFL | Bldg | 4830 | 0.8 | 4830 | 0.8 | 1.12 | 1.2 | -0.0039337 | 4830 | 0.8 | 4830 | 0.8 | 1.12 | 1.2 | -0.00393
CFLBldgSCERSDExCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RSD | Ex | CZ09 | 4.83 | 0.0008 | 0 | 5.41 | 0.000976 | -0.0216 | 4.83 | 0.0008 | 0 | 5.41 | 0.000976 | -0.0216 |  | CFL | Bldg | 4830 | 0.8 | 4830 | 0.8 | 1.12 | 1.22 | -0.004472 | 4830 | 0.8 | 4830 | 0.8 | 1.12 | 1.22 | -0.00447
CFLBldgSCERSDExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RSD | Ex | CZ10 | 4.83 | 0.0008 | 0 | 5.31 | 0.000946 | -0.0228 | 4.83 | 0.0008 | 0 | 5.31 | 0.000946 | -0.0228 |  | CFL | Bldg | 4830 | 0.8 | 4830 | 0.8 | 1.1 | 1.18 | -0.0047205 | 4830 | 0.8 | 4830 | 0.8 | 1.1 | 1.18 | -0.00472
CFLBldgSCERSDExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RSD | Ex | CZ13 | 4.83 | 0.0008 | 0 | 5.28 | 0.000985 | -0.0335 | 4.83 | 0.0008 | 0 | 5.28 | 0.000985 | -0.0335 |  | CFL | Bldg | 4830 | 0.8 | 4830 | 0.8 | 1.09 | 1.23 | -0.0069358 | 4830 | 0.8 | 4830 | 0.8 | 1.09 | 1.23 | -0.00694
CFLBldgSCERSDExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RSD | Ex | CZ14 | 4.83 | 0.0008 | 0 | 5.23 | 0.000948 | -0.0347 | 4.83 | 0.0008 | 0 | 5.23 | 0.000948 | -0.0347 |  | CFL | Bldg | 4830 | 0.8 | 4830 | 0.8 | 1.08 | 1.19 | -0.0071843 | 4830 | 0.8 | 4830 | 0.8 | 1.08 | 1.19 | -0.00718
CFLBldgSCERSDExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RSD | Ex | CZ15 | 4.83 | 0.0008 | 0 | 5.68 | 0.001 | -0.00859 | 4.83 | 0.0008 | 0 | 5.68 | 0.001 | -0.00859 |  | CFL | Bldg | 4830 | 0.8 | 4830 | 0.8 | 1.18 | 1.25 | -0.0017785 | 4830 | 0.8 | 4830 | 0.8 | 1.18 | 1.25 | -0.00178
CFLBldgSCERSDExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RSD | Ex | CZ16 | 4.83 | 0.0008 | 0 | 4.85 | 0.000948 | -0.0618 | 4.83 | 0.0008 | 0 | 4.85 | 0.000948 | -0.0618 |  | CFL | Bldg | 4830 | 0.8 | 4830 | 0.8 | 1 | 1.19 | -0.012795 | 4830 | 0.8 | 4830 | 0.8 | 1 | 1.19 | -0.0128
CFLBldgSCERSDExIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | RSD | Ex | IOU | 4.83 | 0.0008 | 0 | 5.3677 | 0.00096639 | -0.022424 | 4.83 | 0.0008 | 0 | 5.3677 | 0.00096639 | -0.022424 |  | CFL | Bldg | 4830 | 0.8 | 4830 | 0.8 | 1.11 | 1.21 | -0.0046427 | 4830 | 0.8 | 4830 | 0.8 | 1.11 | 1.21 | -0.00464
CFLBldgSCERSDNewCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RSD | New | CZ05 | 4.83 | 0.0008 | 0 | 5 | 0.000982 | -0.0472 | 4.83 | 0.0008 | 0 | 5 | 0.000982 | -0.0472 |  | CFL | Bldg | 4830 | 0.8 | 4830 | 0.8 | 1.04 | 1.23 | -0.0097723 | 4830 | 0.8 | 4830 | 0.8 | 1.04 | 1.23 | -0.00977
CFLBldgSCERSDNewCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RSD | New | CZ06 | 4.83 | 0.0008 | 0 | 5.28 | 0.000998 | -0.0266 | 4.83 | 0.0008 | 0 | 5.28 | 0.000998 | -0.0266 |  | CFL | Bldg | 4830 | 0.8 | 4830 | 0.8 | 1.09 | 1.25 | -0.0055072 | 4830 | 0.8 | 4830 | 0.8 | 1.09 | 1.25 | -0.00551
CFLBldgSCERSDNewCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RSD | New | CZ08 | 4.83 | 0.0008 | 0 | 5.19 | 0.00087 | -0.0222 | 4.83 | 0.0008 | 0 | 5.19 | 0.00087 | -0.0222 |  | CFL | Bldg | 4830 | 0.8 | 4830 | 0.8 | 1.07 | 1.09 | -0.0045963 | 4830 | 0.8 | 4830 | 0.8 | 1.07 | 1.09 | -0.0046
CFLBldgSCERSDNewCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RSD | New | CZ09 | 4.83 | 0.0008 | 0 | 5.37 | 0.00105 | -0.0246 | 4.83 | 0.0008 | 0 | 5.37 | 0.00105 | -0.0246 |  | CFL | Bldg | 4830 | 0.8 | 4830 | 0.8 | 1.11 | 1.31 | -0.0050932 | 4830 | 0.8 | 4830 | 0.8 | 1.11 | 1.31 | -0.00509
CFLBldgSCERSDNewCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RSD | New | CZ10 | 4.83 | 0.0008 | 0 | 5.39 | 0.00105 | -0.0252 | 4.83 | 0.0008 | 0 | 5.39 | 0.00105 | -0.0252 |  | CFL | Bldg | 4830 | 0.8 | 4830 | 0.8 | 1.12 | 1.31 | -0.0052174 | 4830 | 0.8 | 4830 | 0.8 | 1.12 | 1.31 | -0.00522
CFLBldgSCERSDNewCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RSD | New | CZ13 | 4.83 | 0.0008 | 0 | 5.34 | 0.00105 | -0.0364 | 4.83 | 0.0008 | 0 | 5.34 | 0.00105 | -0.0364 |  | CFL | Bldg | 4830 | 0.8 | 4830 | 0.8 | 1.11 | 1.31 | -0.0075362 | 4830 | 0.8 | 4830 | 0.8 | 1.11 | 1.31 | -0.00754
CFLBldgSCERSDNewCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RSD | New | CZ14 | 4.83 | 0.0008 | 0 | 5.32 | 0.00105 | -0.0374 | 4.83 | 0.0008 | 0 | 5.32 | 0.00105 | -0.0374 |  | CFL | Bldg | 4830 | 0.8 | 4830 | 0.8 | 1.1 | 1.31 | -0.0077433 | 4830 | 0.8 | 4830 | 0.8 | 1.1 | 1.31 | -0.00774
CFLBldgSCERSDNewCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RSD | New | CZ15 | 4.83 | 0.0008 | 0 | 5.79 | 0.00108 | -0.0109 | 4.83 | 0.0008 | 0 | 5.79 | 0.00108 | -0.0109 |  | CFL | Bldg | 4830 | 0.8 | 4830 | 0.8 | 1.2 | 1.35 | -0.0022567 | 4830 | 0.8 | 4830 | 0.8 | 1.2 | 1.35 | -0.00226
CFLBldgSCERSDNewCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RSD | New | CZ16 | 4.83 | 0.0008 | 0 | 4.89 | 0.00099 | -0.0512 | 4.83 | 0.0008 | 0 | 4.89 | 0.00099 | -0.0512 |  | CFL | Bldg | 4830 | 0.8 | 4830 | 0.8 | 1.01 | 1.24 | -0.0106 | 4830 | 0.8 | 4830 | 0.8 | 1.01 | 1.24 | -0.0106
CFLBldgSCERSDNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | RSD | New | IOU | 4.83 | 0.0008 | 0 | 5.3221 | 0.0009961 | -0.025391 | 4.83 | 0.0008 | 0 | 5.3221 | 0.0009961 | -0.025391 |  | CFL | Bldg | 4830 | 0.8 | 4830 | 0.8 | 1.1 | 1.25 | -0.005257 | 4830 | 0.8 | 4830 | 0.8 | 1.1 | 1.25 | -0.00526
CFLBldgSCERt3ExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Rt3 | Ex | CZ05 | 3.71 | 0.00063087 | 0 | 3.99 | 0.00079687 | -0.0208 | 3.71 | 0.000629 | 0 | 3.99 | 0.000795 | -0.0208 |  | CFL | Bldg | 3710 | 0.631 | 3710 | 0.629 | 1.08 | 1.26 | -0.0056065 | 3710 | 0.631 | 3710 | 0.629 | 1.08 | 1.26 | -0.00561
CFLBldgSCERt3ExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Rt3 | Ex | CZ06 | 3.71 | 0.00063087 | 0 | 4.2794 | 0.00079781 | -0.0053794 | 3.71 | 0.000629 | 0 | 4.27 | 0.000795 | -0.00537 |  | CFL | Bldg | 3710 | 0.631 | 3710 | 0.629 | 1.15 | 1.26 | -0.0014474 | 3710 | 0.631 | 3710 | 0.629 | 1.15 | 1.26 | -0.00145
CFLBldgSCERt3ExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Rt3 | Ex | CZ08 | 3.71 | 0.00063087 | 0 | 4.2894 | 0.0007858 | -0.00471 | 3.71 | 0.000629 | 0 | 4.28 | 0.00078394 | -0.00471 |  | CFL | Bldg | 3710 | 0.631 | 3710 | 0.629 | 1.15 | 1.25 | -0.0012695 | 3710 | 0.631 | 3710 | 0.629 | 1.15 | 1.25 | -0.00127
CFLBldgSCERt3ExCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Rt3 | Ex | CZ09 | 3.71 | 0.00063087 | 0 | 4.2293 | 0.00079587 | -0.00723 | 3.71 | 0.000629 | 0 | 4.22 | 0.000794 | -0.00723 |  | CFL | Bldg | 3710 | 0.631 | 3710 | 0.629 | 1.14 | 1.26 | -0.0019488 | 3710 | 0.631 | 3710 | 0.629 | 1.14 | 1.26 | -0.00195
CFLBldgSCERt3ExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Rt3 | Ex | CZ10 | 3.71 | 0.00063076 | 0 | 4.13 | 0.00078476 | -0.0084588 | 3.71 | 0.000629 | 0 | 4.13 | 0.000783 | -0.00845 |  | CFL | Bldg | 3710 | 0.631 | 3710 | 0.629 | 1.11 | 1.24 | -0.0022776 | 3710 | 0.631 | 3710 | 0.629 | 1.11 | 1.24 | -0.00228
CFLBldgSCERt3ExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Rt3 | Ex | CZ13 | 3.71 | 0.00063079 | 0 | 4.029 | 0.00080279 | -0.02309 | 3.71 | 0.000629 | 0 | 4.02 | 0.000801 | -0.02309 |  | CFL | Bldg | 3710 | 0.631 | 3710 | 0.629 | 1.08 | 1.27 | -0.0062236 | 3710 | 0.631 | 3710 | 0.629 | 1.08 | 1.27 | -0.00622
CFLBldgSCERt3ExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Rt3 | Ex | CZ14 | 3.71 | 0.0006308 | 0 | 3.97 | 0.0007948 | -0.0248 | 3.71 | 0.000629 | 0 | 3.97 | 0.000793 | -0.0248 |  | CFL | Bldg | 3710 | 0.631 | 3710 | 0.629 | 1.07 | 1.26 | -0.0066846 | 3710 | 0.631 | 3710 | 0.629 | 1.07 | 1.26 | -0.00668
CFLBldgSCERt3ExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Rt3 | Ex | CZ15 | 3.71 | 0.00063076 | 0 | 4.28 | 0.00080764 | -0.00214 | 3.71 | 0.000629 | 0 | 4.28 | 0.00080588 | -0.00214 |  | CFL | Bldg | 3710 | 0.631 | 3710 | 0.629 | 1.15 | 1.28 | -0.00057682 | 3710 | 0.631 | 3710 | 0.629 | 1.15 | 1.28 | -0.000577
CFLBldgSCERt3ExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Rt3 | Ex | CZ16 | 3.71 | 0.00063079 | 0 | 3.63 | 0.00078069 | -0.04789 | 3.71 | 0.000629 | 0 | 3.63 | 0.000778 | -0.0478 |  | CFL | Bldg | 3710 | 0.631 | 3710 | 0.629 | 0.978 | 1.24 | -0.012884 | 3710 | 0.631 | 3710 | 0.629 | 0.978 | 1.24 | -0.0129
CFLBldgSCERt3ExIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | Rt3 | Ex | IOU | 3.71 | 0.00063084 | 0 | 4.2163 | 0.00079153 | -0.0077401 | 3.71 | 0.000629 | 0 | 4.2097 | 0.00078945 | -0.0077351 |  | CFL | Bldg | 3710 | 0.631 | 3710 | 0.629 | 1.13 | 1.26 | -0.0020849 | 3710 | 0.631 | 3710 | 0.629 | 1.13 | 1.26 | -0.00208
CFLBldgSCERt3NewCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Rt3 | New | CZ05 | 3.71 | 0.000629 | 0 | 3.84 | 0.000778 | -0.0257 | 3.71 | 0.000629 | 0 | 3.84 | 0.000778 | -0.0257 |  | CFL | Bldg | 3710 | 0.629 | 3710 | 0.629 | 1.04 | 1.24 | -0.0069272 | 3710 | 0.629 | 3710 | 0.629 | 1.04 | 1.24 | -0.00693
CFLBldgSCERt3NewCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Rt3 | New | CZ06 | 3.71 | 0.000629 | 0 | 4.11 | 0.00077 | -0.00774 | 3.71 | 0.000629 | 0 | 4.11 | 0.00077 | -0.00774 |  | CFL | Bldg | 3710 | 0.629 | 3710 | 0.629 | 1.11 | 1.22 | -0.0020863 | 3710 | 0.629 | 3710 | 0.629 | 1.11 | 1.22 | -0.00209
CFLBldgSCERt3NewCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Rt3 | New | CZ08 | 3.71 | 0.000629 | 0 | 4.14 | 0.00076 | -0.00634 | 3.71 | 0.000629 | 0 | 4.14 | 0.00076 | -0.00634 |  | CFL | Bldg | 3710 | 0.629 | 3710 | 0.629 | 1.12 | 1.21 | -0.0017089 | 3710 | 0.629 | 3710 | 0.629 | 1.12 | 1.21 | -0.00171
CFLBldgSCERt3NewCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Rt3 | New | CZ09 | 3.71 | 0.000629 | 0 | 4.09 | 0.000778 | -0.00952 | 3.71 | 0.000629 | 0 | 4.09 | 0.000778 | -0.00952 |  | CFL | Bldg | 3710 | 0.629 | 3710 | 0.629 | 1.1 | 1.24 | -0.002566 | 3710 | 0.629 | 3710 | 0.629 | 1.1 | 1.24 | -0.00257
CFLBldgSCERt3NewCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Rt3 | New | CZ10 | 3.71 | 0.000629 | 0 | 4.1 | 0.000785 | -0.011 | 3.71 | 0.000629 | 0 | 4.1 | 0.000785 | -0.011 |  | CFL | Bldg | 3710 | 0.629 | 3710 | 0.629 | 1.11 | 1.25 | -0.002965 | 3710 | 0.629 | 3710 | 0.629 | 1.11 | 1.25 | -0.00297
CFLBldgSCERt3NewCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Rt3 | New | CZ13 | 3.71 | 0.000629 | 0 | 3.98 | 0.000799 | -0.0252 | 3.71 | 0.000629 | 0 | 3.98 | 0.000799 | -0.0252 |  | CFL | Bldg | 3710 | 0.629 | 3710 | 0.629 | 1.07 | 1.27 | -0.0067925 | 3710 | 0.629 | 3710 | 0.629 | 1.07 | 1.27 | -0.00679
CFLBldgSCERt3NewCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Rt3 | New | CZ14 | 3.71 | 0.000629 | 0 | 3.96 | 0.00079 | -0.0262 | 3.71 | 0.000629 | 0 | 3.96 | 0.00079 | -0.0262 |  | CFL | Bldg | 3710 | 0.629 | 3710 | 0.629 | 1.07 | 1.26 | -0.007062 | 3710 | 0.629 | 3710 | 0.629 | 1.07 | 1.26 | -0.00706
CFLBldgSCERt3NewCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Rt3 | New | CZ15 | 3.71 | 0.000629 | 0 | 4.32 | 0.000841 | -0.00168 | 3.71 | 0.000629 | 0 | 4.32 | 0.000841 | -0.00168 |  | CFL | Bldg | 3710 | 0.629 | 3710 | 0.629 | 1.16 | 1.34 | -0.00045283 | 3710 | 0.629 | 3710 | 0.629 | 1.16 | 1.34 | -0.000453
CFLBldgSCERt3NewCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Rt3 | New | CZ16 | 3.71 | 0.000629 | 0 | 3.58 | 0.00071 | -0.0456 | 3.71 | 0.000629 | 0 | 3.58 | 0.00071 | -0.0456 |  | CFL | Bldg | 3710 | 0.629 | 3710 | 0.629 | 0.965 | 1.13 | -0.012291 | 3710 | 0.629 | 3710 | 0.629 | 0.965 | 1.13 | -0.0123
CFLBldgSCERt3NewIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | Rt3 | New | IOU | 3.71 | 0.000629 | 0 | 4.1014 | 0.00077836 | -0.010477 | 3.71 | 0.000629 | 0 | 4.1014 | 0.00077836 | -0.010477 |  | CFL | Bldg | 3710 | 0.629 | 3710 | 0.629 | 1.11 | 1.24 | -0.0028241 | 3710 | 0.629 | 3710 | 0.629 | 1.11 | 1.24 | -0.00282
CFLBldgSCERtLExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RtL | Ex | CZ05 | 4.3494 | 0.00068894 | 0 | 4.6594 | 0.00085794 | -0.026094 | 4.3494 | 0.000688 | 0 | 4.65 | 0.000857 | -0.026 |  | CFL | Bldg | 4350 | 0.689 | 4350 | 0.688 | 1.07 | 1.25 | -0.0059779 | 4350 | 0.689 | 4350 | 0.688 | 1.07 | 1.25 | -0.00598
CFLBldgSCERtLExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RtL | Ex | CZ06 | 4.3494 | 0.00068894 | 0 | 4.9494 | 0.00087187 | -0.0105 | 4.3494 | 0.000688 | 0 | 4.94 | 0.00087 | -0.0105 |  | CFL | Bldg | 4350 | 0.689 | 4350 | 0.688 | 1.14 | 1.26 | -0.0024141 | 4350 | 0.689 | 4350 | 0.688 | 1.14 | 1.26 | -0.00241
CFLBldgSCERtLExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RtL | Ex | CZ08 | 4.3493 | 0.00068893 | 0 | 4.96 | 0.00087287 | -0.0090494 | 4.3493 | 0.000688 | 0 | 4.96 | 0.000871 | -0.00904 |  | CFL | Bldg | 4350 | 0.689 | 4350 | 0.688 | 1.14 | 1.27 | -0.0020785 | 4350 | 0.689 | 4350 | 0.688 | 1.14 | 1.27 | -0.00208
CFLBldgSCERtLExCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RtL | Ex | CZ09 | 4.3493 | 0.00068893 | 0 | 4.91 | 0.00089387 | -0.0109 | 4.3493 | 0.000688 | 0 | 4.91 | 0.000892 | -0.0109 |  | CFL | Bldg | 4350 | 0.689 | 4350 | 0.688 | 1.13 | 1.3 | -0.0025061 | 4350 | 0.689 | 4350 | 0.688 | 1.13 | 1.3 | -0.00251
CFLBldgSCERtLExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RtL | Ex | CZ10 | 4.3488 | 0.00068888 | 0 | 4.8288 | 0.00088276 | -0.012 | 4.3488 | 0.000688 | 0 | 4.82 | 0.000881 | -0.012 |  | CFL | Bldg | 4350 | 0.689 | 4350 | 0.688 | 1.11 | 1.28 | -0.0027594 | 4350 | 0.689 | 4350 | 0.688 | 1.11 | 1.28 | -0.00276
CFLBldgSCERtLExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RtL | Ex | CZ13 | 4.349 | 0.0006889 | 0 | 4.74 | 0.00088879 | -0.0237 | 4.349 | 0.000688 | 0 | 4.74 | 0.000887 | -0.0237 |  | CFL | Bldg | 4350 | 0.689 | 4350 | 0.688 | 1.09 | 1.29 | -0.0054496 | 4350 | 0.689 | 4350 | 0.688 | 1.09 | 1.29 | -0.00545
CFLBldgSCERtLExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RtL | Ex | CZ14 | 4.349 | 0.0006889 | 0 | 4.7 | 0.0008959 | -0.0246 | 4.349 | 0.000688 | 0 | 4.7 | 0.000895 | -0.0246 |  | CFL | Bldg | 4350 | 0.689 | 4350 | 0.688 | 1.08 | 1.3 | -0.0056565 | 4350 | 0.689 | 4350 | 0.688 | 1.08 | 1.3 | -0.00566
CFLBldgSCERtLExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RtL | Ex | CZ15 | 4.3488 | 0.00068888 | 0 | 5.05 | 0.00089876 | -0.0042388 | 4.3488 | 0.000688 | 0 | 5.05 | 0.000897 | -0.00423 |  | CFL | Bldg | 4350 | 0.689 | 4350 | 0.688 | 1.16 | 1.3 | -0.00097268 | 4350 | 0.689 | 4350 | 0.688 | 1.16 | 1.3 | -0.000973
CFLBldgSCERtLExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RtL | Ex | CZ16 | 4.349 | 0.0006889 | 0 | 4.269 | 0.00084679 | -0.05439 | 4.349 | 0.000688 | 0 | 4.26 | 0.000845 | -0.0543 |  | CFL | Bldg | 4350 | 0.689 | 4350 | 0.688 | 0.98 | 1.23 | -0.012486 | 4350 | 0.689 | 4350 | 0.688 | 0.98 | 1.23 | -0.0125
CFLBldgSCERtLExIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | RtL | Ex | IOU | 4.3492 | 0.00068892 | 0 | 4.9006 | 0.00087977 | -0.011665 | 4.3492 | 0.000688 | 0 | 4.8963 | 0.00087798 | -0.011661 |  | CFL | Bldg | 4350 | 0.689 | 4350 | 0.688 | 1.13 | 1.28 | -0.0026813 | 4350 | 0.689 | 4350 | 0.688 | 1.13 | 1.28 | -0.00268
CFLBldgSCERtLNewCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RtL | New | CZ05 | 4.34 | 0.000688 | 0 | 4.52 | 0.000862 | -0.0311 | 4.34 | 0.000688 | 0 | 4.52 | 0.000862 | -0.0311 |  | CFL | Bldg | 4340 | 0.688 | 4340 | 0.688 | 1.04 | 1.25 | -0.0071659 | 4340 | 0.688 | 4340 | 0.688 | 1.04 | 1.25 | -0.00717
CFLBldgSCERtLNewCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RtL | New | CZ06 | 4.34 | 0.000688 | 0 | 4.76 | 0.000876 | -0.0144 | 4.34 | 0.000688 | 0 | 4.76 | 0.000876 | -0.0144 |  | CFL | Bldg | 4340 | 0.688 | 4340 | 0.688 | 1.1 | 1.27 | -0.003318 | 4340 | 0.688 | 4340 | 0.688 | 1.1 | 1.27 | -0.00332
CFLBldgSCERtLNewCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RtL | New | CZ08 | 4.34 | 0.000688 | 0 | 4.82 | 0.000888 | -0.0122 | 4.34 | 0.000688 | 0 | 4.82 | 0.000888 | -0.0122 |  | CFL | Bldg | 4340 | 0.688 | 4340 | 0.688 | 1.11 | 1.29 | -0.0028111 | 4340 | 0.688 | 4340 | 0.688 | 1.11 | 1.29 | -0.00281
CFLBldgSCERtLNewCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RtL | New | CZ09 | 4.34 | 0.000688 | 0 | 4.84 | 0.000931 | -0.0121 | 4.34 | 0.000688 | 0 | 4.84 | 0.000931 | -0.0121 |  | CFL | Bldg | 4340 | 0.688 | 4340 | 0.688 | 1.12 | 1.35 | -0.002788 | 4340 | 0.688 | 4340 | 0.688 | 1.12 | 1.35 | -0.00279
CFLBldgSCERtLNewCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RtL | New | CZ10 | 4.34 | 0.000688 | 0 | 4.86 | 0.000934 | -0.0141 | 4.34 | 0.000688 | 0 | 4.86 | 0.000934 | -0.0141 |  | CFL | Bldg | 4340 | 0.688 | 4340 | 0.688 | 1.12 | 1.36 | -0.0032488 | 4340 | 0.688 | 4340 | 0.688 | 1.12 | 1.36 | -0.00325
CFLBldgSCERtLNewCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RtL | New | CZ13 | 4.34 | 0.000688 | 0 | 4.76 | 0.000925 | -0.0266 | 4.34 | 0.000688 | 0 | 4.76 | 0.000925 | -0.0266 |  | CFL | Bldg | 4340 | 0.688 | 4340 | 0.688 | 1.1 | 1.34 | -0.006129 | 4340 | 0.688 | 4340 | 0.688 | 1.1 | 1.34 | -0.00613
CFLBldgSCERtLNewCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RtL | New | CZ14 | 4.34 | 0.000688 | 0 | 4.75 | 0.000927 | -0.0272 | 4.34 | 0.000688 | 0 | 4.75 | 0.000927 | -0.0272 |  | CFL | Bldg | 4340 | 0.688 | 4340 | 0.688 | 1.09 | 1.35 | -0.0062673 | 4340 | 0.688 | 4340 | 0.688 | 1.09 | 1.35 | -0.00627
CFLBldgSCERtLNewCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RtL | New | CZ15 | 4.34 | 0.000688 | 0 | 5.14 | 0.000944 | -0.00414 | 4.34 | 0.000688 | 0 | 5.14 | 0.000944 | -0.00414 |  | CFL | Bldg | 4340 | 0.688 | 4340 | 0.688 | 1.18 | 1.37 | -0.00095392 | 4340 | 0.688 | 4340 | 0.688 | 1.18 | 1.37 | -0.000954
CFLBldgSCERtLNewCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RtL | New | CZ16 | 4.34 | 0.000688 | 0 | 4.3 | 0.000874 | -0.0565 | 4.34 | 0.000688 | 0 | 4.3 | 0.000874 | -0.0565 |  | CFL | Bldg | 4340 | 0.688 | 4340 | 0.688 | 0.991 | 1.27 | -0.013018 | 4340 | 0.688 | 4340 | 0.688 | 0.991 | 1.27 | -0.013
CFLBldgSCERtLNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | RtL | New | IOU | 4.34 | 0.000688 | 0 | 4.8263 | 0.00091154 | -0.014685 | 4.34 | 0.000688 | 0 | 4.8263 | 0.00091154 | -0.014685 |  | CFL | Bldg | 4340 | 0.688 | 4340 | 0.688 | 1.11 | 1.32 | -0.0033835 | 4340 | 0.688 | 4340 | 0.688 | 1.11 | 1.32 | -0.00338
CFLBldgSCERtSExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RtS | Ex | CZ05 | 4.01 | 0.0007 | 0 | 4.24 | 0.00087 | -0.021 | 4.01 | 0.0007 | 0 | 4.24 | 0.00087 | -0.021 |  | CFL | Bldg | 4010 | 0.7 | 4010 | 0.7 | 1.06 | 1.24 | -0.0052369 | 4010 | 0.7 | 4010 | 0.7 | 1.06 | 1.24 | -0.00524
CFLBldgSCERtSExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RtS | Ex | CZ06 | 4.01 | 0.0007 | 0 | 4.49 | 0.000879 | -0.0077 | 4.01 | 0.0007 | 0 | 4.49 | 0.000879 | -0.0077 |  | CFL | Bldg | 4010 | 0.7 | 4010 | 0.7 | 1.12 | 1.26 | -0.0019202 | 4010 | 0.7 | 4010 | 0.7 | 1.12 | 1.26 | -0.00192
CFLBldgSCERtSExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RtS | Ex | CZ08 | 4.01 | 0.0007 | 0 | 4.51 | 0.000881 | -0.00658 | 4.01 | 0.0007 | 0 | 4.51 | 0.000881 | -0.00658 |  | CFL | Bldg | 4010 | 0.7 | 4010 | 0.7 | 1.12 | 1.26 | -0.0016409 | 4010 | 0.7 | 4010 | 0.7 | 1.12 | 1.26 | -0.00164
CFLBldgSCERtSExCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RtS | Ex | CZ09 | 4.01 | 0.0007 | 0 | 4.48 | 0.000894 | -0.00834 | 4.01 | 0.0007 | 0 | 4.48 | 0.000894 | -0.00834 |  | CFL | Bldg | 4010 | 0.7 | 4010 | 0.7 | 1.12 | 1.28 | -0.0020798 | 4010 | 0.7 | 4010 | 0.7 | 1.12 | 1.28 | -0.00208
CFLBldgSCERtSExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RtS | Ex | CZ10 | 4.01 | 0.0007 | 0 | 4.4 | 0.00088 | -0.00935 | 4.01 | 0.0007 | 0 | 4.4 | 0.00088 | -0.00935 |  | CFL | Bldg | 4010 | 0.7 | 4010 | 0.7 | 1.1 | 1.26 | -0.0023317 | 4010 | 0.7 | 4010 | 0.7 | 1.1 | 1.26 | -0.00233
CFLBldgSCERtSExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RtS | Ex | CZ13 | 4.01 | 0.0007 | 0 | 4.32 | 0.000888 | -0.0221 | 4.01 | 0.0007 | 0 | 4.32 | 0.000888 | -0.0221 |  | CFL | Bldg | 4010 | 0.7 | 4010 | 0.7 | 1.08 | 1.27 | -0.0055112 | 4010 | 0.7 | 4010 | 0.7 | 1.08 | 1.27 | -0.00551
CFLBldgSCERtSExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RtS | Ex | CZ14 | 4.01 | 0.0007 | 0 | 4.31 | 0.000883 | -0.0203 | 4.01 | 0.0007 | 0 | 4.31 | 0.000883 | -0.0203 |  | CFL | Bldg | 4010 | 0.7 | 4010 | 0.7 | 1.07 | 1.26 | -0.0050623 | 4010 | 0.7 | 4010 | 0.7 | 1.07 | 1.26 | -0.00506
CFLBldgSCERtSExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RtS | Ex | CZ15 | 4.01 | 0.0007 | 0 | 4.7 | 0.000873 | -0.0024 | 4.01 | 0.0007 | 0 | 4.7 | 0.000873 | -0.0024 |  | CFL | Bldg | 4010 | 0.7 | 4010 | 0.7 | 1.17 | 1.25 | -0.0005985 | 4010 | 0.7 | 4010 | 0.7 | 1.17 | 1.25 | -0.000599
CFLBldgSCERtSExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RtS | Ex | CZ16 | 4.01 | 0.0007 | 0 | 3.96 | 0.000864 | -0.0425 | 4.01 | 0.0007 | 0 | 3.96 | 0.000864 | -0.0425 |  | CFL | Bldg | 4010 | 0.7 | 4010 | 0.7 | 0.988 | 1.23 | -0.010599 | 4010 | 0.7 | 4010 | 0.7 | 0.988 | 1.23 | -0.0106
CFLBldgSCERtSExIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | RtS | Ex | IOU | 4.01 | 0.0007 | 0 | 4.4634 | 0.00088209 | -0.0089415 | 4.01 | 0.0007 | 0 | 4.4634 | 0.00088209 | -0.0089415 |  | CFL | Bldg | 4010 | 0.7 | 4010 | 0.7 | 1.11 | 1.26 | -0.0022298 | 4010 | 0.7 | 4010 | 0.7 | 1.11 | 1.26 | -0.00223
CFLBldgSCERtSNewCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RtS | New | CZ05 | 4.01 | 0.0007 | 0 | 4.12 | 0.000851 | -0.0234 | 4.01 | 0.0007 | 0 | 4.12 | 0.000851 | -0.0234 |  | CFL | Bldg | 4010 | 0.7 | 4010 | 0.7 | 1.03 | 1.22 | -0.0058354 | 4010 | 0.7 | 4010 | 0.7 | 1.03 | 1.22 | -0.00584
CFLBldgSCERtSNewCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RtS | New | CZ06 | 4.01 | 0.0007 | 0 | 4.34 | 0.000862 | -0.00979 | 4.01 | 0.0007 | 0 | 4.34 | 0.000862 | -0.00979 |  | CFL | Bldg | 4010 | 0.7 | 4010 | 0.7 | 1.08 | 1.23 | -0.0024414 | 4010 | 0.7 | 4010 | 0.7 | 1.08 | 1.23 | -0.00244
CFLBldgSCERtSNewCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RtS | New | CZ08 | 4.01 | 0.0007 | 0 | 4.38 | 0.000872 | -0.00818 | 4.01 | 0.0007 | 0 | 4.38 | 0.000872 | -0.00818 |  | CFL | Bldg | 4010 | 0.7 | 4010 | 0.7 | 1.09 | 1.25 | -0.0020399 | 4010 | 0.7 | 4010 | 0.7 | 1.09 | 1.25 | -0.00204
CFLBldgSCERtSNewCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RtS | New | CZ09 | 4.01 | 0.0007 | 0 | 4.37 | 0.000895 | -0.00943 | 4.01 | 0.0007 | 0 | 4.37 | 0.000895 | -0.00943 |  | CFL | Bldg | 4010 | 0.7 | 4010 | 0.7 | 1.09 | 1.28 | -0.0023516 | 4010 | 0.7 | 4010 | 0.7 | 1.09 | 1.28 | -0.00235
CFLBldgSCERtSNewCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RtS | New | CZ10 | 4.01 | 0.0007 | 0 | 4.41 | 0.000909 | -0.00979 | 4.01 | 0.0007 | 0 | 4.41 | 0.000909 | -0.00979 |  | CFL | Bldg | 4010 | 0.7 | 4010 | 0.7 | 1.1 | 1.3 | -0.0024414 | 4010 | 0.7 | 4010 | 0.7 | 1.1 | 1.3 | -0.00244
CFLBldgSCERtSNewCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RtS | New | CZ13 | 4.01 | 0.0007 | 0 | 4.3 | 0.000896 | -0.0228 | 4.01 | 0.0007 | 0 | 4.3 | 0.000896 | -0.0228 |  | CFL | Bldg | 4010 | 0.7 | 4010 | 0.7 | 1.07 | 1.28 | -0.0056858 | 4010 | 0.7 | 4010 | 0.7 | 1.07 | 1.28 | -0.00569
CFLBldgSCERtSNewCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RtS | New | CZ14 | 4.01 | 0.0007 | 0 | 4.31 | 0.000897 | -0.0214 | 4.01 | 0.0007 | 0 | 4.31 | 0.000897 | -0.0214 |  | CFL | Bldg | 4010 | 0.7 | 4010 | 0.7 | 1.07 | 1.28 | -0.0053367 | 4010 | 0.7 | 4010 | 0.7 | 1.07 | 1.28 | -0.00534
CFLBldgSCERtSNewCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RtS | New | CZ15 | 4.01 | 0.0007 | 0 | 4.62 | 0.000923 | -0.00195 | 4.01 | 0.0007 | 0 | 4.62 | 0.000923 | -0.00195 |  | CFL | Bldg | 4010 | 0.7 | 4010 | 0.7 | 1.15 | 1.32 | -0.00048628 | 4010 | 0.7 | 4010 | 0.7 | 1.15 | 1.32 | -0.000486
CFLBldgSCERtSNewCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RtS | New | CZ16 | 4.01 | 0.0007 | 0 | 3.94 | 0.00086 | -0.0453 | 4.01 | 0.0007 | 0 | 3.94 | 0.00086 | -0.0453 |  | CFL | Bldg | 4010 | 0.7 | 4010 | 0.7 | 0.983 | 1.23 | -0.011297 | 4010 | 0.7 | 4010 | 0.7 | 0.983 | 1.23 | -0.0113
CFLBldgSCERtSNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | RtS | New | IOU | 4.01 | 0.0007 | 0 | 4.3799 | 0.00088921 | -0.01053 | 4.01 | 0.0007 | 0 | 4.3799 | 0.00088921 | -0.01053 |  | CFL | Bldg | 4010 | 0.7 | 4010 | 0.7 | 1.09 | 1.27 | -0.002626 | 4010 | 0.7 | 4010 | 0.7 | 1.09 | 1.27 | -0.00263
CFLBldgSCEs_AgrExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_Agr | Ex | CZ05 | 2.7044 | 0.00077287 | 0 | 2.872 | 0.0009418 | -0.012003 | 2.608 | 0.0007396 | 0 | 2.768 | 0.0009004 | -0.011702 |  | CFL | Bldg | 2700 | 0.773 | 2610 | 0.74 | 1.06 | 1.22 | -0.004487 | 2700 | 0.773 | 2610 | 0.74 | 1.06 | 1.22 | -0.00449
CFLBldgSCEs_AgrExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_Agr | Ex | CZ06 | 2.7044 | 0.00077287 | 0 | 3.0257 | 0.00093196 | -0.0044316 | 2.608 | 0.0007396 | 0 | 2.916 | 0.0008898 | -0.004286 |  | CFL | Bldg | 2700 | 0.773 | 2610 | 0.74 | 1.12 | 1.2 | -0.0016434 | 2700 | 0.773 | 2610 | 0.74 | 1.12 | 1.2 | -0.00164
CFLBldgSCEs_AgrExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_Agr | Ex | CZ08 | 2.7044 | 0.00077287 | 0 | 3.0377 | 0.00093131 | -0.0037263 | 2.608 | 0.0007396 | 0 | 2.928 | 0.0008884 | -0.003594 |  | CFL | Bldg | 2700 | 0.773 | 2610 | 0.74 | 1.12 | 1.2 | -0.0013781 | 2700 | 0.773 | 2610 | 0.74 | 1.12 | 1.2 | -0.00138
CFLBldgSCEs_AgrExCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_Agr | Ex | CZ09 | 2.7045 | 0.00077289 | 0 | 3.0276 | 0.00094991 | -0.0049926 | 2.608 | 0.0007396 | 0 | 2.916 | 0.0009066 | -0.004828 |  | CFL | Bldg | 2700 | 0.773 | 2610 | 0.74 | 1.12 | 1.23 | -0.0018512 | 2700 | 0.773 | 2610 | 0.74 | 1.12 | 1.23 | -0.00185
CFLBldgSCEs_AgrExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_Agr | Ex | CZ10 | 2.7011 | 0.00077165 | 0 | 2.9401 | 0.0009411 | -0.0060297 | 2.608 | 0.0007396 | 0 | 2.836 | 0.0008996 | -0.00588 |  | CFL | Bldg | 2700 | 0.772 | 2610 | 0.74 | 1.09 | 1.22 | -0.0022546 | 2700 | 0.772 | 2610 | 0.74 | 1.09 | 1.22 | -0.00225
CFLBldgSCEs_AgrExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_Agr | Ex | CZ13 | 2.704 | 0.00077269 | 0 | 2.9135 | 0.00093156 | -0.013518 | 2.608 | 0.0007396 | 0 | 2.808 | 0.0008898 | -0.01316 |  | CFL | Bldg | 2700 | 0.773 | 2610 | 0.74 | 1.08 | 1.2 | -0.005046 | 2700 | 0.773 | 2610 | 0.74 | 1.08 | 1.2 | -0.00505
CFLBldgSCEs_AgrExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_Agr | Ex | CZ14 | 2.7019 | 0.00077197 | 0 | 2.8891 | 0.00093848 | -0.014702 | 2.608 | 0.0007396 | 0 | 2.786 | 0.000896 | -0.014422 |  | CFL | Bldg | 2700 | 0.772 | 2610 | 0.74 | 1.07 | 1.21 | -0.0055299 | 2700 | 0.772 | 2610 | 0.74 | 1.07 | 1.21 | -0.00553
CFLBldgSCEs_AgrExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_Agr | Ex | CZ15 | 2.7011 | 0.00077165 | 0 | 3.1432 | 0.00093134 | -0.0015878 | 2.608 | 0.0007396 | 0 | 3.03 | 0.0008902 | -0.001544 |  | CFL | Bldg | 2700 | 0.772 | 2610 | 0.74 | 1.16 | 1.2 | -0.00059202 | 2700 | 0.772 | 2610 | 0.74 | 1.16 | 1.2 | -0.000592
CFLBldgSCEs_AgrExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_Agr | Ex | CZ16 | 2.7028 | 0.00077224 | 0 | 2.6728 | 0.00092016 | -0.029489 | 2.608 | 0.0007396 | 0 | 2.578 | 0.000879 | -0.02882 |  | CFL | Bldg | 2700 | 0.772 | 2610 | 0.74 | 0.988 | 1.19 | -0.011051 | 2700 | 0.772 | 2610 | 0.74 | 0.988 | 1.19 | -0.0111
CFLBldgSCEs_AgrExIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_Agr | Ex | IOU | 2.7034 | 0.00077251 | 0 | 3.006 | 0.00093584 | -0.0055645 | 2.608 | 0.0007396 | 0 | 2.8977 | 0.0008935 | -0.0054014 |  | CFL | Bldg | 2700 | 0.773 | 2610 | 0.74 | 1.11 | 1.21 | -0.0020711 | 2700 | 0.773 | 2610 | 0.74 | 1.11 | 1.21 | -0.00207
CFLBldgSCEs_CliExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_Cli | Ex | CZ05 | 3.4091 | 0.00066352 | 0 | 3.588 | 0.00082675 | -0.031428 | 3.12 | 0.0005745 | 0 | 3.28 | 0.000715 | -0.029955 |  | CFL | Bldg | 3410 | 0.664 | 3120 | 0.575 | 1.05 | 1.24 | -0.009601 | 3410 | 0.664 | 3120 | 0.575 | 1.05 | 1.24 | -0.0096
CFLBldgSCEs_CliExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_Cli | Ex | CZ06 | 3.409 | 0.0006635 | 0 | 3.7919 | 0.0008511 | -0.019899 | 3.12 | 0.0005745 | 0 | 3.465 | 0.000737 | -0.019055 |  | CFL | Bldg | 3410 | 0.664 | 3120 | 0.575 | 1.11 | 1.28 | -0.0061074 | 3410 | 0.664 | 3120 | 0.575 | 1.11 | 1.28 | -0.00611
CFLBldgSCEs_CliExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_Cli | Ex | CZ08 | 3.409 | 0.0006635 | 0 | 3.8219 | 0.00085509 | -0.019076 | 3.12 | 0.0005745 | 0 | 3.495 | 0.000741 | -0.018265 |  | CFL | Bldg | 3410 | 0.664 | 3120 | 0.575 | 1.12 | 1.29 | -0.0058542 | 3410 | 0.664 | 3120 | 0.575 | 1.12 | 1.29 | -0.00585
CFLBldgSCEs_CliExCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_Cli | Ex | CZ09 | 3.4086 | 0.00066344 | 0 | 3.8212 | 0.00087043 | -0.019946 | 3.12 | 0.0005745 | 0 | 3.49 | 0.000755 | -0.01906 |  | CFL | Bldg | 3410 | 0.663 | 3120 | 0.575 | 1.12 | 1.31 | -0.006109 | 3410 | 0.663 | 3120 | 0.575 | 1.12 | 1.31 | -0.00611
CFLBldgSCEs_CliExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_Cli | Ex | CZ10 | 3.3988 | 0.00066038 | 0 | 3.7557 | 0.00086251 | -0.019698 | 3.12 | 0.0005745 | 0 | 3.445 | 0.0007515 | -0.01891 |  | CFL | Bldg | 3400 | 0.66 | 3120 | 0.575 | 1.1 | 1.31 | -0.0060609 | 3400 | 0.66 | 3120 | 0.575 | 1.1 | 1.31 | -0.00606
CFLBldgSCEs_CliExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_Cli | Ex | CZ13 | 3.4068 | 0.00066294 | 0 | 3.71 | 0.0008579 | -0.025858 | 3.12 | 0.0005745 | 0 | 3.395 | 0.000745 | -0.02445 |  | CFL | Bldg | 3410 | 0.663 | 3120 | 0.575 | 1.09 | 1.3 | -0.0078365 | 3410 | 0.663 | 3120 | 0.575 | 1.09 | 1.3 | -0.00784
CFLBldgSCEs_CliExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_Cli | Ex | CZ14 | 3.4012 | 0.00066112 | 0 | 3.7142 | 0.00086585 | -0.025361 | 3.12 | 0.0005745 | 0 | 3.41 | 0.0007525 | -0.024105 |  | CFL | Bldg | 3400 | 0.661 | 3120 | 0.575 | 1.09 | 1.31 | -0.007726 | 3400 | 0.661 | 3120 | 0.575 | 1.09 | 1.31 | -0.00773
CFLBldgSCEs_CliExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_Cli | Ex | CZ15 | 3.3988 | 0.00066038 | 0 | 4.0182 | 0.00086059 | -0.011075 | 3.12 | 0.0005745 | 0 | 3.68 | 0.0007505 | -0.01069 |  | CFL | Bldg | 3400 | 0.66 | 3120 | 0.575 | 1.18 | 1.31 | -0.0034263 | 3400 | 0.66 | 3120 | 0.575 | 1.18 | 1.31 | -0.00343
CFLBldgSCEs_CliExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_Cli | Ex | CZ16 | 3.4031 | 0.00066179 | 0 | 3.4031 | 0.00083107 | -0.041308 | 3.12 | 0.0005745 | 0 | 3.12 | 0.0007215 | -0.03885 |  | CFL | Bldg | 3400 | 0.662 | 3120 | 0.575 | 1 | 1.26 | -0.012452 | 3400 | 0.662 | 3120 | 0.575 | 1 | 1.26 | -0.0125
CFLBldgSCEs_CliExIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_Cli | Ex | IOU | 3.406 | 0.00066258 | 0 | 3.7916 | 0.00085685 | -0.020294 | 3.12 | 0.0005745 | 0 | 3.4688 | 0.00074358 | -0.01941 |  | CFL | Bldg | 3410 | 0.663 | 3120 | 0.575 | 1.11 | 1.29 | -0.006221 | 3410 | 0.663 | 3120 | 0.575 | 1.11 | 1.29 | -0.00622
CFLBldgSCEs_FStExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_FSt | Ex | CZ05 | 3.9628 | 0.00059969 | 0 | 3.9978 | 0.0007476 | -0.044563 | 3.93 | 0.000595 | 0 | 3.965 | 0.0007415 | -0.044 |  | CFL | Bldg | 3960 | 0.6 | 3930 | 0.595 | 1.01 | 1.25 | -0.011196 | 3960 | 0.6 | 3930 | 0.595 | 1.01 | 1.25 | -0.0112
CFLBldgSCEs_FStExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_FSt | Ex | CZ06 | 3.9628 | 0.00059969 | 0 | 4.2228 | 0.0007541 | -0.031269 | 3.93 | 0.000595 | 0 | 4.19 | 0.000748 | -0.0308 |  | CFL | Bldg | 3960 | 0.6 | 3930 | 0.595 | 1.07 | 1.26 | -0.0078371 | 3960 | 0.6 | 3930 | 0.595 | 1.07 | 1.26 | -0.00784
CFLBldgSCEs_FStExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_FSt | Ex | CZ08 | 3.9628 | 0.00059969 | 0 | 4.2878 | 0.00076359 | -0.028162 | 3.93 | 0.000595 | 0 | 4.255 | 0.0007575 | -0.02774 |  | CFL | Bldg | 3960 | 0.6 | 3930 | 0.595 | 1.08 | 1.27 | -0.0070585 | 3960 | 0.6 | 3930 | 0.595 | 1.08 | 1.27 | -0.00706
CFLBldgSCEs_FStExCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_FSt | Ex | CZ09 | 3.9628 | 0.00059968 | 0 | 4.2928 | 0.00077359 | -0.028441 | 3.93 | 0.000595 | 0 | 4.26 | 0.0007675 | -0.02802 |  | CFL | Bldg | 3960 | 0.6 | 3930 | 0.595 | 1.08 | 1.29 | -0.0071298 | 3960 | 0.6 | 3930 | 0.595 | 1.08 | 1.29 | -0.00713
CFLBldgSCEs_FStExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_FSt | Ex | CZ10 | 3.9611 | 0.00059944 | 0 | 4.2461 | 0.00077377 | -0.028325 | 3.93 | 0.000595 | 0 | 4.215 | 0.000768 | -0.02797 |  | CFL | Bldg | 3960 | 0.599 | 3930 | 0.595 | 1.07 | 1.29 | -0.007117 | 3960 | 0.599 | 3930 | 0.595 | 1.07 | 1.29 | -0.00712
CFLBldgSCEs_FStExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_FSt | Ex | CZ13 | 3.9616 | 0.00059951 | 0 | 4.2116 | 0.00077382 | -0.034311 | 3.93 | 0.000595 | 0 | 4.18 | 0.0007675 | -0.03395 |  | CFL | Bldg | 3960 | 0.6 | 3930 | 0.595 | 1.06 | 1.29 | -0.0086387 | 3960 | 0.6 | 3930 | 0.595 | 1.06 | 1.29 | -0.00864
CFLBldgSCEs_FStExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_FSt | Ex | CZ14 | 3.9614 | 0.00059948 | 0 | 4.1964 | 0.00078177 | -0.034008 | 3.93 | 0.000595 | 0 | 4.165 | 0.0007755 | -0.03365 |  | CFL | Bldg | 3960 | 0.599 | 3930 | 0.595 | 1.06 | 1.3 | -0.0085623 | 3960 | 0.599 | 3930 | 0.595 | 1.06 | 1.3 | -0.00856
CFLBldgSCEs_FStExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_FSt | Ex | CZ15 | 3.9611 | 0.00059944 | 0 | 4.5511 | 0.00076921 | -0.014872 | 3.93 | 0.000595 | 0 | 4.52 | 0.000763 | -0.01465 |  | CFL | Bldg | 3960 | 0.599 | 3930 | 0.595 | 1.15 | 1.28 | -0.0037277 | 3960 | 0.599 | 3930 | 0.595 | 1.15 | 1.28 | -0.00373
CFLBldgSCEs_FStExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_FSt | Ex | CZ16 | 3.9614 | 0.00059949 | 0 | 3.8369 | 0.00074633 | -0.053143 | 3.93 | 0.000595 | 0 | 3.81 | 0.0007405 | -0.05265 |  | CFL | Bldg | 3960 | 0.599 | 3930 | 0.595 | 0.969 | 1.24 | -0.013397 | 3960 | 0.599 | 3930 | 0.595 | 0.969 | 1.24 | -0.0134
CFLBldgSCEs_FStExIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_FSt | Ex | IOU | 3.9622 | 0.00059961 | 0 | 4.2605 | 0.00076633 | -0.029263 | 3.93 | 0.000595 | 0 | 4.2283 | 0.00076029 | -0.028855 |  | CFL | Bldg | 3960 | 0.6 | 3930 | 0.595 | 1.08 | 1.28 | -0.0073423 | 3960 | 0.6 | 3930 | 0.595 | 1.08 | 1.28 | -0.00734
CFLBldgSCEs_IndExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_Ind | Ex | CZ05 | 2.8571 | 0.00078558 | 0 | 3.1565 | 0.00096388 | -0.0069139 | 2.81 | 0.0007705 | 0 | 3.1 | 0.0009455 | -0.006895 |  | CFL | Bldg | 2860 | 0.786 | 2810 | 0.77 | 1.1 | 1.23 | -0.0024537 | 2860 | 0.786 | 2810 | 0.77 | 1.1 | 1.23 | -0.00245
CFLBldgSCEs_IndExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_Ind | Ex | CZ06 | 2.8571 | 0.00078559 | 0 | 3.2719 | 0.00094289 | -0.002452 | 2.81 | 0.0007705 | 0 | 3.22 | 0.0009245 | -0.002443 |  | CFL | Bldg | 2860 | 0.786 | 2810 | 0.77 | 1.15 | 1.2 | -0.0008694 | 2860 | 0.786 | 2810 | 0.77 | 1.15 | 1.2 | -0.000869
CFLBldgSCEs_IndExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_Ind | Ex | CZ08 | 2.8572 | 0.00078559 | 0 | 3.2866 | 0.00096033 | -0.0018868 | 2.81 | 0.0007705 | 0 | 3.23 | 0.000941 | -0.001884 |  | CFL | Bldg | 2860 | 0.786 | 2810 | 0.77 | 1.15 | 1.22 | -0.00067046 | 2860 | 0.786 | 2810 | 0.77 | 1.15 | 1.22 | -0.00067
CFLBldgSCEs_IndExCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_Ind | Ex | CZ09 | 2.8572 | 0.00078562 | 0 | 3.2767 | 0.00097095 | -0.0028802 | 2.81 | 0.0007705 | 0 | 3.22 | 0.000953 | -0.002867 |  | CFL | Bldg | 2860 | 0.786 | 2810 | 0.77 | 1.15 | 1.24 | -0.0010203 | 2860 | 0.786 | 2810 | 0.77 | 1.15 | 1.24 | -0.00102
CFLBldgSCEs_IndExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_Ind | Ex | CZ10 | 2.853 | 0.00078427 | 0 | 3.1716 | 0.00096592 | -0.0036258 | 2.81 | 0.0007705 | 0 | 3.12 | 0.00095 | -0.0036125 |  | CFL | Bldg | 2850 | 0.784 | 2810 | 0.77 | 1.11 | 1.23 | -0.0012856 | 2850 | 0.784 | 2810 | 0.77 | 1.11 | 1.23 | -0.00129
CFLBldgSCEs_IndExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_Ind | Ex | CZ13 | 2.8556 | 0.00078509 | 0 | 3.1647 | 0.00094628 | -0.0079769 | 2.81 | 0.0007705 | 0 | 3.11 | 0.0009285 | -0.007945 |  | CFL | Bldg | 2860 | 0.785 | 2810 | 0.77 | 1.11 | 1.21 | -0.0028274 | 2860 | 0.785 | 2810 | 0.77 | 1.11 | 1.21 | -0.00283
CFLBldgSCEs_IndExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_Ind | Ex | CZ14 | 2.8548 | 0.00078484 | 0 | 3.1493 | 0.00096303 | -0.0091809 | 2.81 | 0.0007705 | 0 | 3.1 | 0.000946 | -0.009145 |  | CFL | Bldg | 2850 | 0.785 | 2810 | 0.77 | 1.1 | 1.23 | -0.0032544 | 2850 | 0.785 | 2810 | 0.77 | 1.1 | 1.23 | -0.00325
CFLBldgSCEs_IndExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_Ind | Ex | CZ15 | 2.853 | 0.00078427 | 0 | 3.3366 | 0.00096543 | -0.000805 | 2.81 | 0.0007705 | 0 | 3.285 | 0.0009465 | -0.000805 |  | CFL | Bldg | 2850 | 0.784 | 2810 | 0.77 | 1.17 | 1.23 | -0.00028648 | 2850 | 0.784 | 2810 | 0.77 | 1.17 | 1.23 | -0.000286
CFLBldgSCEs_IndExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_Ind | Ex | CZ16 | 2.8545 | 0.00078473 | 0 | 2.9445 | 0.00092934 | -0.019746 | 2.81 | 0.0007705 | 0 | 2.9 | 0.000912 | -0.01963 |  | CFL | Bldg | 2850 | 0.785 | 2810 | 0.77 | 1.03 | 1.18 | -0.0069858 | 2850 | 0.785 | 2810 | 0.77 | 1.03 | 1.18 | -0.00699
CFLBldgSCEs_IndExIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_Ind | Ex | IOU | 2.8561 | 0.00078524 | 0 | 3.2501 | 0.00095844 | -0.0032015 | 2.81 | 0.0007705 | 0 | 3.1962 | 0.00094028 | -0.0031898 |  | CFL | Bldg | 2860 | 0.785 | 2810 | 0.77 | 1.14 | 1.22 | -0.0011352 | 2860 | 0.785 | 2810 | 0.77 | 1.14 | 1.22 | -0.00114
CFLBldgSCEs_MiCExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_MiC | Ex | CZ05 | 4.014 | 0.00075093 | 0 | 4.2666 | 0.00092948 | -0.024804 | 3.8533 | 0.000698 | 0 | 4.0933 | 0.000863 | -0.024303 |  | CFL | Bldg | 4010 | 0.751 | 3850 | 0.698 | 1.06 | 1.24 | -0.0063071 | 4010 | 0.751 | 3850 | 0.698 | 1.06 | 1.24 | -0.00631
CFLBldgSCEs_MiCExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_MiC | Ex | CZ06 | 4.014 | 0.00075093 | 0 | 4.5027 | 0.00094141 | -0.011613 | 3.8533 | 0.000698 | 0 | 4.32 | 0.00087367 | -0.01137 |  | CFL | Bldg | 4010 | 0.751 | 3850 | 0.698 | 1.12 | 1.25 | -0.0029507 | 4010 | 0.751 | 3850 | 0.698 | 1.12 | 1.25 | -0.00295
CFLBldgSCEs_MiCExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_MiC | Ex | CZ08 | 4.014 | 0.00075094 | 0 | 4.5294 | 0.00093541 | -0.0099906 | 3.8533 | 0.000698 | 0 | 4.3467 | 0.00086767 | -0.00977 |  | CFL | Bldg | 4010 | 0.751 | 3850 | 0.698 | 1.13 | 1.24 | -0.0025355 | 4010 | 0.751 | 3850 | 0.698 | 1.13 | 1.24 | -0.00254
CFLBldgSCEs_MiCExCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_MiC | Ex | CZ09 | 4.0141 | 0.00075096 | 0 | 4.516 | 0.00094808 | -0.011794 | 3.8533 | 0.000698 | 0 | 4.33 | 0.00087967 | -0.01152 |  | CFL | Bldg | 4010 | 0.751 | 3850 | 0.698 | 1.12 | 1.26 | -0.0029896 | 4010 | 0.751 | 3850 | 0.698 | 1.12 | 1.26 | -0.00299
CFLBldgSCEs_MiCExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_MiC | Ex | CZ10 | 4.0085 | 0.00074912 | 0 | 4.4335 | 0.0009284 | -0.012403 | 3.8533 | 0.000698 | 0 | 4.26 | 0.00086267 | -0.012153 |  | CFL | Bldg | 4010 | 0.749 | 3850 | 0.698 | 1.11 | 1.24 | -0.003154 | 4010 | 0.749 | 3850 | 0.698 | 1.11 | 1.24 | -0.00315
CFLBldgSCEs_MiCExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_MiC | Ex | CZ13 | 4.0134 | 0.00075073 | 0 | 4.3791 | 0.00094383 | -0.02253 | 3.8533 | 0.000698 | 0 | 4.2033 | 0.00087667 | -0.021933 |  | CFL | Bldg | 4010 | 0.751 | 3850 | 0.698 | 1.09 | 1.26 | -0.005692 | 4010 | 0.751 | 3850 | 0.698 | 1.09 | 1.26 | -0.00569
CFLBldgSCEs_MiCExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_MiC | Ex | CZ14 | 4.0099 | 0.00074957 | 0 | 4.3586 | 0.00093488 | -0.021536 | 3.8533 | 0.000698 | 0 | 4.1867 | 0.00086767 | -0.02107 |  | CFL | Bldg | 4010 | 0.75 | 3850 | 0.698 | 1.09 | 1.24 | -0.005468 | 4010 | 0.75 | 3850 | 0.698 | 1.09 | 1.24 | -0.00547
CFLBldgSCEs_MiCExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_MiC | Ex | CZ15 | 4.0085 | 0.00074912 | 0 | 4.7387 | 0.00094112 | -0.0041664 | 3.8533 | 0.000698 | 0 | 4.55 | 0.000876 | -0.0040933 |  | CFL | Bldg | 4010 | 0.749 | 3850 | 0.698 | 1.18 | 1.26 | -0.0010623 | 4010 | 0.749 | 3850 | 0.698 | 1.18 | 1.26 | -0.00106
CFLBldgSCEs_MiCExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_MiC | Ex | CZ16 | 4.0113 | 0.00075003 | 0 | 4.0079 | 0.00091671 | -0.042315 | 3.8533 | 0.000698 | 0 | 3.85 | 0.00085167 | -0.0412 |  | CFL | Bldg | 4010 | 0.75 | 3850 | 0.698 | 0.999 | 1.22 | -0.010692 | 4010 | 0.75 | 3850 | 0.698 | 0.999 | 1.22 | -0.0107
CFLBldgSCEs_MiCExIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_MiC | Ex | IOU | 4.0124 | 0.0007504 | 0 | 4.4895 | 0.00093707 | -0.012275 | 3.8533 | 0.000698 | 0 | 4.3089 | 0.00086989 | -0.012003 |  | CFL | Bldg | 4010 | 0.75 | 3850 | 0.698 | 1.12 | 1.25 | -0.0031149 | 4010 | 0.75 | 3850 | 0.698 | 1.12 | 1.25 | -0.00311
CFLBldgSCEs_TCUExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_TCU | Ex | CZ05 | 2.8884 | 0.00067113 | 0 | 3.0018 | 0.00081011 | -0.01435 | 2.732 | 0.0006182 | 0 | 2.832 | 0.0007444 | -0.013662 |  | CFL | Bldg | 2890 | 0.671 | 2730 | 0.618 | 1.04 | 1.2 | -0.0050007 | 2890 | 0.671 | 2730 | 0.618 | 1.04 | 1.2 | -0.005
CFLBldgSCEs_TCUExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_TCU | Ex | CZ06 | 2.8883 | 0.00067108 | 0 | 3.1493 | 0.00081978 | -0.0074859 | 2.732 | 0.0006182 | 0 | 2.974 | 0.0007528 | -0.007108 |  | CFL | Bldg | 2890 | 0.671 | 2730 | 0.618 | 1.09 | 1.22 | -0.0026018 | 2890 | 0.671 | 2730 | 0.618 | 1.09 | 1.22 | -0.0026
CFLBldgSCEs_TCUExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_TCU | Ex | CZ08 | 2.8882 | 0.00067108 | 0 | 3.1713 | 0.00082375 | -0.0067225 | 2.732 | 0.0006182 | 0 | 2.994 | 0.000756 | -0.006358 |  | CFL | Bldg | 2890 | 0.671 | 2730 | 0.618 | 1.1 | 1.22 | -0.0023272 | 2890 | 0.671 | 2730 | 0.618 | 1.1 | 1.22 | -0.00233
CFLBldgSCEs_TCUExCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_TCU | Ex | CZ09 | 2.8876 | 0.00067086 | 0 | 3.1605 | 0.00083224 | -0.0081923 | 2.732 | 0.0006182 | 0 | 2.984 | 0.0007644 | -0.00776 |  | CFL | Bldg | 2890 | 0.671 | 2730 | 0.618 | 1.09 | 1.24 | -0.0028404 | 2890 | 0.671 | 2730 | 0.618 | 1.09 | 1.24 | -0.00284
CFLBldgSCEs_TCUExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_TCU | Ex | CZ10 | 2.8798 | 0.00066793 | 0 | 3.1181 | 0.00082264 | -0.0079836 | 2.732 | 0.0006182 | 0 | 2.952 | 0.000759 | -0.007638 |  | CFL | Bldg | 2880 | 0.668 | 2730 | 0.618 | 1.08 | 1.23 | -0.0027958 | 2880 | 0.668 | 2730 | 0.618 | 1.08 | 1.23 | -0.0028
CFLBldgSCEs_TCUExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_TCU | Ex | CZ13 | 2.8843 | 0.00066956 | 0 | 3.0911 | 0.00081534 | -0.013168 | 2.732 | 0.0006182 | 0 | 2.922 | 0.0007504 | -0.0125 |  | CFL | Bldg | 2880 | 0.67 | 2730 | 0.618 | 1.07 | 1.21 | -0.0045754 | 2880 | 0.67 | 2730 | 0.618 | 1.07 | 1.21 | -0.00458
CFLBldgSCEs_TCUExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_TCU | Ex | CZ14 | 2.882 | 0.00066874 | 0 | 3.0728 | 0.00082196 | -0.01339 | 2.732 | 0.0006182 | 0 | 2.908 | 0.0007566 | -0.012802 |  | CFL | Bldg | 2880 | 0.669 | 2730 | 0.618 | 1.06 | 1.22 | -0.0046859 | 2880 | 0.669 | 2730 | 0.618 | 1.06 | 1.22 | -0.00469
CFLBldgSCEs_TCUExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_TCU | Ex | CZ15 | 2.8798 | 0.00066793 | 0 | 3.2866 | 0.00081643 | -0.0034556 | 2.732 | 0.0006182 | 0 | 3.108 | 0.000753 | -0.00329 |  | CFL | Bldg | 2880 | 0.668 | 2730 | 0.618 | 1.14 | 1.22 | -0.0012042 | 2880 | 0.668 | 2730 | 0.618 | 1.14 | 1.22 | -0.0012
CFLBldgSCEs_TCUExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_TCU | Ex | CZ16 | 2.8826 | 0.00066882 | 0 | 2.8644 | 0.00079794 | -0.024095 | 2.732 | 0.0006182 | 0 | 2.712 | 0.0007352 | -0.02288 |  | CFL | Bldg | 2880 | 0.669 | 2730 | 0.618 | 0.993 | 1.19 | -0.0083748 | 2880 | 0.669 | 2730 | 0.618 | 0.993 | 1.19 | -0.00837
CFLBldgSCEs_TCUExIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_TCU | Ex | IOU | 2.886 | 0.00067017 | 0 | 3.1496 | 0.00082294 | -0.0079159 | 2.732 | 0.0006182 | 0 | 2.976 | 0.00075651 | -0.0075144 |  | CFL | Bldg | 2890 | 0.67 | 2730 | 0.618 | 1.09 | 1.22 | -0.0027505 | 2890 | 0.67 | 2730 | 0.618 | 1.09 | 1.22 | -0.00275
CFLBldgSCESCnExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | SCn | Ex | CZ05 | 2.7589 | 0.00057437 | 0 | 2.5689 | 0.00071825 | -0.027588 | 2.74 | 0.000564 | 0 | 2.55 | 0.000706 | -0.0274 |  | CFL | Bldg | 2760 | 0.574 | 2740 | 0.564 | 0.931 | 1.25 | -0.01 | 2760 | 0.574 | 2740 | 0.564 | 0.931 | 1.25 | -0.01
CFLBldgSCESCnExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | SCn | Ex | CZ06 | 2.7588 | 0.00057436 | 0 | 2.8588 | 0.00074513 | -0.014294 | 2.74 | 0.000564 | 0 | 2.84 | 0.000731 | -0.0142 |  | CFL | Bldg | 2760 | 0.574 | 2740 | 0.564 | 1.04 | 1.3 | -0.0051825 | 2760 | 0.574 | 2740 | 0.564 | 1.04 | 1.3 | -0.00518
CFLBldgSCESCnExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | SCn | Ex | CZ08 | 2.7589 | 0.00057437 | 0 | 2.9088 | 0.0007422 | -0.012294 | 2.74 | 0.000564 | 0 | 2.89 | 0.000729 | -0.0122 |  | CFL | Bldg | 2760 | 0.574 | 2740 | 0.564 | 1.05 | 1.29 | -0.0044526 | 2760 | 0.574 | 2740 | 0.564 | 1.05 | 1.29 | -0.00445
CFLBldgSCESCnExCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | SCn | Ex | CZ09 | 2.7587 | 0.00057427 | 0 | 2.8887 | 0.00075607 | -0.014793 | 2.74 | 0.000564 | 0 | 2.87 | 0.000743 | -0.0147 |  | CFL | Bldg | 2760 | 0.574 | 2740 | 0.564 | 1.05 | 1.32 | -0.005365 | 2760 | 0.574 | 2740 | 0.564 | 1.05 | 1.32 | -0.00537
CFLBldgSCESCnExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | SCn | Ex | CZ10 | 2.7561 | 0.00057283 | 0 | 2.8661 | 0.00074524 | -0.01588 | 2.74 | 0.000564 | 0 | 2.85 | 0.000734 | -0.0158 |  | CFL | Bldg | 2760 | 0.573 | 2740 | 0.564 | 1.04 | 1.3 | -0.0057664 | 2760 | 0.573 | 2740 | 0.564 | 1.04 | 1.3 | -0.00577
CFLBldgSCESCnExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | SCn | Ex | CZ13 | 2.7571 | 0.00057339 | 0 | 2.8185 | 0.00073595 | -0.021271 | 2.74 | 0.000564 | 0 | 2.81 | 0.000724 | -0.0211 |  | CFL | Bldg | 2760 | 0.573 | 2740 | 0.564 | 1.03 | 1.28 | -0.0077007 | 2760 | 0.573 | 2740 | 0.564 | 1.03 | 1.28 | -0.0077
CFLBldgSCESCnExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | SCn | Ex | CZ14 | 2.7567 | 0.00057318 | 0 | 2.7967 | 0.00073452 | -0.023384 | 2.74 | 0.000564 | 0 | 2.78 | 0.000722 | -0.0233 |  | CFL | Bldg | 2760 | 0.573 | 2740 | 0.564 | 1.01 | 1.28 | -0.0085036 | 2760 | 0.573 | 2740 | 0.564 | 1.01 | 1.28 | -0.0085
CFLBldgSCESCnExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | SCn | Ex | CZ15 | 2.7561 | 0.00057283 | 0 | 3.0661 | 0.00073804 | -0.0062401 | 2.74 | 0.000564 | 0 | 3.05 | 0.000726 | -0.0062 |  | CFL | Bldg | 2760 | 0.573 | 2740 | 0.564 | 1.11 | 1.29 | -0.0022628 | 2760 | 0.573 | 2740 | 0.564 | 1.11 | 1.29 | -0.00226
CFLBldgSCESCnExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | SCn | Ex | CZ16 | 2.7562 | 0.00057292 | 0 | 2.5262 | 0.00071435 | -0.033662 | 2.74 | 0.000564 | 0 | 2.51 | 0.000703 | -0.0335 |  | CFL | Bldg | 2760 | 0.573 | 2740 | 0.564 | 0.916 | 1.25 | -0.012226 | 2760 | 0.573 | 2740 | 0.564 | 0.916 | 1.25 | -0.0122
CFLBldgSCESCnExIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | SCn | Ex | IOU | 2.7578 | 0.00057382 | 0 | 2.8825 | 0.00074467 | -0.014308 | 2.74 | 0.000564 | 0 | 2.8647 | 0.00073204 | -0.014217 |  | CFL | Bldg | 2760 | 0.574 | 2740 | 0.564 | 1.05 | 1.3 | -0.0051886 | 2760 | 0.574 | 2740 | 0.564 | 1.05 | 1.3 | -0.00519
CFLBldgSCESCnNewCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | SCn | New | CZ05 | 2.74 | 0.000564 | 0 | 2.56 | 0.000708 | -0.0302 | 2.74 | 0.000564 | 0 | 2.56 | 0.000708 | -0.0302 |  | CFL | Bldg | 2740 | 0.564 | 2740 | 0.564 | 0.934 | 1.26 | -0.011022 | 2740 | 0.564 | 2740 | 0.564 | 0.934 | 1.26 | -0.011
CFLBldgSCESCnNewCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | SCn | New | CZ06 | 2.74 | 0.000564 | 0 | 2.75 | 0.000678 | -0.0161 | 2.74 | 0.000564 | 0 | 2.75 | 0.000678 | -0.0161 |  | CFL | Bldg | 2740 | 0.564 | 2740 | 0.564 | 1 | 1.2 | -0.0058759 | 2740 | 0.564 | 2740 | 0.564 | 1 | 1.2 | -0.00588
CFLBldgSCESCnNewCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | SCn | New | CZ08 | 2.74 | 0.000564 | 0 | 2.81 | 0.000688 | -0.014 | 2.74 | 0.000564 | 0 | 2.81 | 0.000688 | -0.014 |  | CFL | Bldg | 2740 | 0.564 | 2740 | 0.564 | 1.03 | 1.22 | -0.0051095 | 2740 | 0.564 | 2740 | 0.564 | 1.03 | 1.22 | -0.00511
CFLBldgSCESCnNewCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | SCn | New | CZ09 | 2.74 | 0.000564 | 0 | 2.82 | 0.000711 | -0.015 | 2.74 | 0.000564 | 0 | 2.82 | 0.000711 | -0.015 |  | CFL | Bldg | 2740 | 0.564 | 2740 | 0.564 | 1.03 | 1.26 | -0.0054745 | 2740 | 0.564 | 2740 | 0.564 | 1.03 | 1.26 | -0.00547
CFLBldgSCESCnNewCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | SCn | New | CZ10 | 2.74 | 0.000564 | 0 | 2.82 | 0.000705 | -0.0164 | 2.74 | 0.000564 | 0 | 2.82 | 0.000705 | -0.0164 |  | CFL | Bldg | 2740 | 0.564 | 2740 | 0.564 | 1.03 | 1.25 | -0.0059854 | 2740 | 0.564 | 2740 | 0.564 | 1.03 | 1.25 | -0.00599
CFLBldgSCESCnNewCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | SCn | New | CZ13 | 2.74 | 0.000564 | 0 | 2.74 | 0.000686 | -0.0215 | 2.74 | 0.000564 | 0 | 2.74 | 0.000686 | -0.0215 |  | CFL | Bldg | 2740 | 0.564 | 2740 | 0.564 | 1 | 1.22 | -0.0078467 | 2740 | 0.564 | 2740 | 0.564 | 1 | 1.22 | -0.00785
CFLBldgSCESCnNewCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | SCn | New | CZ14 | 2.74 | 0.000564 | 0 | 2.77 | 0.000702 | -0.0241 | 2.74 | 0.000564 | 0 | 2.77 | 0.000702 | -0.0241 |  | CFL | Bldg | 2740 | 0.564 | 2740 | 0.564 | 1.01 | 1.24 | -0.0087956 | 2740 | 0.564 | 2740 | 0.564 | 1.01 | 1.24 | -0.0088
CFLBldgSCESCnNewCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | SCn | New | CZ15 | 2.74 | 0.000564 | 0 | 3 | 0.000708 | -0.00511 | 2.74 | 0.000564 | 0 | 3 | 0.000708 | -0.00511 |  | CFL | Bldg | 2740 | 0.564 | 2740 | 0.564 | 1.09 | 1.26 | -0.001865 | 2740 | 0.564 | 2740 | 0.564 | 1.09 | 1.26 | -0.00187
CFLBldgSCESCnNewCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | SCn | New | CZ16 | 2.74 | 0.000564 | 0 | 2.49 | 0.000678 | -0.0349 | 2.74 | 0.000564 | 0 | 2.49 | 0.000678 | -0.0349 |  | CFL | Bldg | 2740 | 0.564 | 2740 | 0.564 | 0.909 | 1.2 | -0.012737 | 2740 | 0.564 | 2740 | 0.564 | 0.909 | 1.2 | -0.0127
CFLBldgSCESCnNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | SCn | New | IOU | 2.74 | 0.000564 | 0 | 2.8095 | 0.00069959 | -0.016117 | 2.74 | 0.000564 | 0 | 2.8095 | 0.00069959 | -0.016117 |  | CFL | Bldg | 2740 | 0.564 | 2740 | 0.564 | 1.03 | 1.24 | -0.005882 | 2740 | 0.564 | 2740 | 0.564 | 1.03 | 1.24 | -0.00588
CFLBldgSCESUnExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | SUn | Ex | CZ05 | 2.7589 | 0.00057437 | 0 | 2.7589 | 0.00057437 | 0 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 |  | CFL | Bldg | 2760 | 0.574 | 2740 | 0.564 | 1 | 1 | 0 | 2760 | 0.574 | 2740 | 0.564 | 1 | 1 | 0
CFLBldgSCESUnExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | SUn | Ex | CZ06 | 2.7588 | 0.00057436 | 0 | 2.7588 | 0.00057436 | 0 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 |  | CFL | Bldg | 2760 | 0.574 | 2740 | 0.564 | 1 | 1 | 0 | 2760 | 0.574 | 2740 | 0.564 | 1 | 1 | 0
CFLBldgSCESUnExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | SUn | Ex | CZ08 | 2.7589 | 0.00057437 | 0 | 2.7589 | 0.00057437 | 0 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 |  | CFL | Bldg | 2760 | 0.574 | 2740 | 0.564 | 1 | 1 | 0 | 2760 | 0.574 | 2740 | 0.564 | 1 | 1 | 0
CFLBldgSCESUnExCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | SUn | Ex | CZ09 | 2.7587 | 0.00057427 | 0 | 2.7587 | 0.00057427 | 0 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 |  | CFL | Bldg | 2760 | 0.574 | 2740 | 0.564 | 1 | 1 | 0 | 2760 | 0.574 | 2740 | 0.564 | 1 | 1 | 0
CFLBldgSCESUnExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | SUn | Ex | CZ10 | 2.7561 | 0.00057283 | 0 | 2.7561 | 0.00057283 | 0 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 |  | CFL | Bldg | 2760 | 0.573 | 2740 | 0.564 | 1 | 1 | 0 | 2760 | 0.573 | 2740 | 0.564 | 1 | 1 | 0
CFLBldgSCESUnExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | SUn | Ex | CZ13 | 2.7571 | 0.00057339 | 0 | 2.7571 | 0.00057339 | 0 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 |  | CFL | Bldg | 2760 | 0.573 | 2740 | 0.564 | 1 | 1 | 0 | 2760 | 0.573 | 2740 | 0.564 | 1 | 1 | 0
CFLBldgSCESUnExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | SUn | Ex | CZ14 | 2.7567 | 0.00057318 | 0 | 2.7567 | 0.00057318 | 0 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 |  | CFL | Bldg | 2760 | 0.573 | 2740 | 0.564 | 1 | 1 | 0 | 2760 | 0.573 | 2740 | 0.564 | 1 | 1 | 0
CFLBldgSCESUnExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | SUn | Ex | CZ15 | 2.7561 | 0.00057283 | 0 | 2.7561 | 0.00057283 | 0 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 |  | CFL | Bldg | 2760 | 0.573 | 2740 | 0.564 | 1 | 1 | 0 | 2760 | 0.573 | 2740 | 0.564 | 1 | 1 | 0
CFLBldgSCESUnExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | SUn | Ex | CZ16 | 2.7562 | 0.00057292 | 0 | 2.7562 | 0.00057292 | 0 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 |  | CFL | Bldg | 2760 | 0.573 | 2740 | 0.564 | 1 | 1 | 0 | 2760 | 0.573 | 2740 | 0.564 | 1 | 1 | 0
CFLBldgSCESUnExIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | SUn | Ex | IOU | 2.7578 | 0.00057382 | 0 | 2.7578 | 0.00057382 | 0 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 |  | CFL | Bldg | 2760 | 0.574 | 2740 | 0.564 | 1 | 1 | 0 | 2760 | 0.574 | 2740 | 0.564 | 1 | 1 | 0
CFLBldgSCESUnNewCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | SUn | New | CZ05 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 |  | CFL | Bldg | 2740 | 0.564 | 2740 | 0.564 | 1 | 1 | 0 | 2740 | 0.564 | 2740 | 0.564 | 1 | 1 | 0
CFLBldgSCESUnNewCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | SUn | New | CZ06 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 |  | CFL | Bldg | 2740 | 0.564 | 2740 | 0.564 | 1 | 1 | 0 | 2740 | 0.564 | 2740 | 0.564 | 1 | 1 | 0
CFLBldgSCESUnNewCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | SUn | New | CZ08 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 |  | CFL | Bldg | 2740 | 0.564 | 2740 | 0.564 | 1 | 1 | 0 | 2740 | 0.564 | 2740 | 0.564 | 1 | 1 | 0
CFLBldgSCESUnNewCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | SUn | New | CZ09 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 |  | CFL | Bldg | 2740 | 0.564 | 2740 | 0.564 | 1 | 1 | 0 | 2740 | 0.564 | 2740 | 0.564 | 1 | 1 | 0
CFLBldgSCESUnNewCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | SUn | New | CZ10 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 |  | CFL | Bldg | 2740 | 0.564 | 2740 | 0.564 | 1 | 1 | 0 | 2740 | 0.564 | 2740 | 0.564 | 1 | 1 | 0
CFLBldgSCESUnNewCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | SUn | New | CZ13 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 |  | CFL | Bldg | 2740 | 0.564 | 2740 | 0.564 | 1 | 1 | 0 | 2740 | 0.564 | 2740 | 0.564 | 1 | 1 | 0
CFLBldgSCESUnNewCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | SUn | New | CZ14 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 |  | CFL | Bldg | 2740 | 0.564 | 2740 | 0.564 | 1 | 1 | 0 | 2740 | 0.564 | 2740 | 0.564 | 1 | 1 | 0
CFLBldgSCESUnNewCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | SUn | New | CZ15 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 |  | CFL | Bldg | 2740 | 0.564 | 2740 | 0.564 | 1 | 1 | 0 | 2740 | 0.564 | 2740 | 0.564 | 1 | 1 | 0
CFLBldgSCESUnNewCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | SUn | New | CZ16 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 |  | CFL | Bldg | 2740 | 0.564 | 2740 | 0.564 | 1 | 1 | 0 | 2740 | 0.564 | 2740 | 0.564 | 1 | 1 | 0
CFLBldgSCESUnNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | SUn | New | IOU | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 |  | CFL | Bldg | 2740 | 0.564 | 2740 | 0.564 | 1 | 1 | 0 | 2740 | 0.564 | 2740 | 0.564 | 1 | 1 | 0
CFLBldgSCEWRfExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | WRf | Ex | CZ06 | 4.7252 | 0.00054725 | 0 | 7.3625 | 0.00068704 | 0 | 4.66 | 0.00053607 | 0 | 7.26 | 0.00067307 | 0 |  | CFL | Bldg | 4730 | 0.547 | 4660 | 0.536 | 1.56 | 1.26 | 0 | 4730 | 0.547 | 4660 | 0.536 | 1.56 | 1.26 | 0
CFLBldgSCEWRfExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | WRf | Ex | CZ08 | 4.7252 | 0.00054725 | 0 | 7.4531 | 0.00068804 | 0 | 4.66 | 0.00053607 | 0 | 7.3507 | 0.00067407 | 0 |  | CFL | Bldg | 4730 | 0.547 | 4660 | 0.536 | 1.58 | 1.26 | 0 | 4730 | 0.547 | 4660 | 0.536 | 1.58 | 1.26 | 0
CFLBldgSCEWRfExCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | WRf | Ex | CZ09 | 4.7248 | 0.00054717 | 0 | 7.5617 | 0.00070487 | 0 | 4.66 | 0.00053607 | 0 | 7.46 | 0.000691 | 0 |  | CFL | Bldg | 4720 | 0.547 | 4660 | 0.536 | 1.6 | 1.29 | 0 | 4720 | 0.547 | 4660 | 0.536 | 1.6 | 1.29 | 0
CFLBldgSCEWRfExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | WRf | Ex | CZ10 | 4.7236 | 0.000547 | 0 | 7.61 | 0.00069163 | 0 | 4.66 | 0.00053609 | 0 | 7.51 | 0.000678 | 0 |  | CFL | Bldg | 4720 | 0.547 | 4660 | 0.536 | 1.61 | 1.26 | 0 | 4720 | 0.547 | 4660 | 0.536 | 1.61 | 1.26 | 0
CFLBldgSCEWRfExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | WRf | Ex | CZ13 | 4.7204 | 0.00054649 | 0 | 7.6149 | 0.00068907 | 0 | 4.66 | 0.00053614 | 0 | 7.52 | 0.00067614 | 0 |  | CFL | Bldg | 4720 | 0.546 | 4660 | 0.536 | 1.61 | 1.26 | 0 | 4720 | 0.546 | 4660 | 0.536 | 1.61 | 1.26 | 0
CFLBldgSCEWRfExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | WRf | Ex | CZ14 | 4.7237 | 0.00054701 | 0 | 7.441 | 0.00068774 | 0 | 4.66 | 0.00053609 | 0 | 7.3409 | 0.00067409 | 0 |  | CFL | Bldg | 4720 | 0.547 | 4660 | 0.536 | 1.58 | 1.26 | 0 | 4720 | 0.547 | 4660 | 0.536 | 1.58 | 1.26 | 0
CFLBldgSCEWRfExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | WRf | Ex | CZ15 | 4.7236 | 0.00054699 | 0 | 7.8399 | 0.00069162 | 0 | 4.66 | 0.00053609 | 0 | 7.74 | 0.000678 | 0 |  | CFL | Bldg | 4720 | 0.547 | 4660 | 0.536 | 1.66 | 1.26 | 0 | 4720 | 0.547 | 4660 | 0.536 | 1.66 | 1.26 | 0
CFLBldgSCEWRfExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | WRf | Ex | CZ16 | 4.7205 | 0.00054651 | 0 | 6.8765 | 0.00077483 | 0 | 4.66 | 0.00053614 | 0 | 6.79 | 0.00076014 | 0 |  | CFL | Bldg | 4720 | 0.547 | 4660 | 0.536 | 1.46 | 1.42 | 0 | 4720 | 0.547 | 4660 | 0.536 | 1.46 | 1.42 | 0
CFLBldgSCEWRfExIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | WRf | Ex | IOU | 4.7241 | 0.00054707 | 0 | 7.4972 | 0.00069049 | 0 | 4.66 | 0.00053608 | 0 | 7.3965 | 0.00067675 | 0 |  | CFL | Bldg | 4720 | 0.547 | 4660 | 0.536 | 1.59 | 1.26 | 0 | 4720 | 0.547 | 4660 | 0.536 | 1.59 | 1.26 | 0
CFLBldgSCEWRfNewCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | WRf | New | CZ05 | 4.66 | 0.000537 | 0 | 6.56 | 0.00107 | 0 | 4.66 | 0.000537 | 0 | 6.56 | 0.00107 | 0 |  | CFL | Bldg | 4660 | 0.537 | 4660 | 0.537 | 1.41 | 1.99 | 0 | 4660 | 0.537 | 4660 | 0.537 | 1.41 | 1.99 | 0
CFLBldgSCEWRfNewCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | WRf | New | CZ06 | 4.66 | 0.000537 | 0 | 7.07 | 0.000662 | 0 | 4.66 | 0.000537 | 0 | 7.07 | 0.000662 | 0 |  | CFL | Bldg | 4660 | 0.537 | 4660 | 0.537 | 1.52 | 1.23 | 0 | 4660 | 0.537 | 4660 | 0.537 | 1.52 | 1.23 | 0
CFLBldgSCEWRfNewCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | WRf | New | CZ08 | 4.66 | 0.000537 | 0 | 7.03 | 0.000663 | 0 | 4.66 | 0.000537 | 0 | 7.03 | 0.000663 | 0 |  | CFL | Bldg | 4660 | 0.537 | 4660 | 0.537 | 1.51 | 1.23 | 0 | 4660 | 0.537 | 4660 | 0.537 | 1.51 | 1.23 | 0
CFLBldgSCEWRfNewCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | WRf | New | CZ09 | 4.66 | 0.000537 | 0 | 6.89 | 0.000688 | 0 | 4.66 | 0.000537 | 0 | 6.89 | 0.000688 | 0 |  | CFL | Bldg | 4660 | 0.537 | 4660 | 0.537 | 1.48 | 1.28 | 0 | 4660 | 0.537 | 4660 | 0.537 | 1.48 | 1.28 | 0
CFLBldgSCEWRfNewCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | WRf | New | CZ10 | 4.66 | 0.000537 | 0 | 6.86 | 0.000671 | 0 | 4.66 | 0.000537 | 0 | 6.86 | 0.000671 | 0 |  | CFL | Bldg | 4660 | 0.537 | 4660 | 0.537 | 1.47 | 1.25 | 0 | 4660 | 0.537 | 4660 | 0.537 | 1.47 | 1.25 | 0
CFLBldgSCEWRfNewCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | WRf | New | CZ13 | 4.66 | 0.000537 | 0 | 6.84 | 0.000671 | 0 | 4.66 | 0.000537 | 0 | 6.84 | 0.000671 | 0 |  | CFL | Bldg | 4660 | 0.537 | 4660 | 0.537 | 1.47 | 1.25 | 0 | 4660 | 0.537 | 4660 | 0.537 | 1.47 | 1.25 | 0
CFLBldgSCEWRfNewCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | WRf | New | CZ14 | 4.66 | 0.000537 | 0 | 6.61 | 0.000665 | 0 | 4.66 | 0.000537 | 0 | 6.61 | 0.000665 | 0 |  | CFL | Bldg | 4660 | 0.537 | 4660 | 0.537 | 1.42 | 1.24 | 0 | 4660 | 0.537 | 4660 | 0.537 | 1.42 | 1.24 | 0
CFLBldgSCEWRfNewCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | WRf | New | CZ15 | 4.66 | 0.000537 | 0 | 7.09 | 0.000669 | 0 | 4.66 | 0.000537 | 0 | 7.09 | 0.000669 | 0 |  | CFL | Bldg | 4660 | 0.537 | 4660 | 0.537 | 1.52 | 1.25 | 0 | 4660 | 0.537 | 4660 | 0.537 | 1.52 | 1.25 | 0
CFLBldgSCEWRfNewCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | WRf | New | CZ16 | 4.66 | 0.000537 | 0 | 6.14 | 0.00107 | 0 | 4.66 | 0.000537 | 0 | 6.14 | 0.00107 | 0 |  | CFL | Bldg | 4660 | 0.537 | 4660 | 0.537 | 1.32 | 1.99 | 0 | 4660 | 0.537 | 4660 | 0.537 | 1.32 | 1.99 | 0
CFLBldgSCEWRfNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | WRf | New | IOU | 4.66 | 0.000537 | 0 | 6.9379 | 0.00067078 | 0 | 4.66 | 0.000537 | 0 | 6.9379 | 0.00067078 | 0 |  | CFL | Bldg | 4660 | 0.537 | 4660 | 0.537 | 1.49 | 1.25 | 0 | 4660 | 0.537 | 4660 | 0.537 | 1.49 | 1.25 | 0
CFLBldgSDGAsmExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Asm | Ex | CZ06 | 2.2963 | 0.00040835 | 0 | 2.5154 | 0.00050717 | -0.011982 | 2.2509 | 0.00040019 | 0 | 2.47 | 0.00049718 | -0.0118 |  | CFL | Bldg | 2300 | 0.408 | 2250 | 0.4 | 1.1 | 1.24 | -0.0052423 | 2300 | 0.408 | 2250 | 0.4 | 1.1 | 1.24 | -0.00524
CFLBldgSDGAsmExCZ07 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Asm | Ex | CZ07 | 2.2963 | 0.00040835 | 0 | 2.5254 | 0.00050617 | -0.010982 | 2.2509 | 0.00040019 | 0 | 2.48 | 0.00049618 | -0.0108 |  | CFL | Bldg | 2300 | 0.408 | 2250 | 0.4 | 1.1 | 1.24 | -0.004798 | 2300 | 0.408 | 2250 | 0.4 | 1.1 | 1.24 | -0.0048
CFLBldgSDGAsmExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Asm | Ex | CZ08 | 2.2963 | 0.00040835 | 0 | 2.5354 | 0.00049217 | -0.010482 | 2.2509 | 0.00040019 | 0 | 2.49 | 0.00048218 | -0.0103 |  | CFL | Bldg | 2300 | 0.408 | 2250 | 0.4 | 1.11 | 1.2 | -0.0045759 | 2300 | 0.408 | 2250 | 0.4 | 1.11 | 1.2 | -0.00458
CFLBldgSDGAsmExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Asm | Ex | CZ10 | 2.2963 | 0.00040835 | 0 | 2.5154 | 0.00049617 | -0.013281 | 2.2509 | 0.00040019 | 0 | 2.47 | 0.00048618 | -0.0131 |  | CFL | Bldg | 2300 | 0.408 | 2250 | 0.4 | 1.1 | 1.21 | -0.0058198 | 2300 | 0.408 | 2250 | 0.4 | 1.1 | 1.21 | -0.00582
CFLBldgSDGAsmExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Asm | Ex | CZ14 | 2.2963 | 0.00040835 | 0 | 2.4563 | 0.00046417 | -0.020963 | 2.2509 | 0.00040019 | 0 | 2.4109 | 0.00045509 | -0.020509 |  | CFL | Bldg | 2300 | 0.408 | 2250 | 0.4 | 1.07 | 1.14 | -0.0091115 | 2300 | 0.408 | 2250 | 0.4 | 1.07 | 1.14 | -0.00911
CFLBldgSDGAsmExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Asm | Ex | CZ15 | 2.2963 | 0.00040835 | 0 | 2.8754 | 0.00048317 | -0.0058517 | 2.2509 | 0.00040019 | 0 | 2.8209 | 0.00047409 | -0.0057519 |  | CFL | Bldg | 2300 | 0.408 | 2250 | 0.4 | 1.25 | 1.18 | -0.0025553 | 2300 | 0.408 | 2250 | 0.4 | 1.25 | 1.18 | -0.00256
CFLBldgSDGAsmExIOU | Com-Iltg-dWatt-CFL_OSbldg | SDG | Asm | Ex | IOU | 2.2963 | 0.00040835 | 0 | 2.5227 | 0.00050242 | -0.011781 | 2.2509 | 0.00040019 | 0 | 2.4772 | 0.00049245 | -0.011597 |  | CFL | Bldg | 2300 | 0.408 | 2250 | 0.4 | 1.1 | 1.23 | -0.0051521 | 2300 | 0.408 | 2250 | 0.4 | 1.1 | 1.23 | -0.00515
CFLBldgSDGAsmNewCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Asm | New | CZ06 | 2.26 | 0.000402 | 0 | 2.44 | 0.000495 | -0.0153 | 2.26 | 0.000402 | 0 | 2.44 | 0.000495 | -0.0153 |  | CFL | Bldg | 2260 | 0.402 | 2260 | 0.402 | 1.08 | 1.23 | -0.0067699 | 2260 | 0.402 | 2260 | 0.402 | 1.08 | 1.23 | -0.00677
CFLBldgSDGAsmNewCZ07 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Asm | New | CZ07 | 2.26 | 0.000402 | 0 | 2.46 | 0.000493 | -0.0134 | 2.26 | 0.000402 | 0 | 2.46 | 0.000493 | -0.0134 |  | CFL | Bldg | 2260 | 0.402 | 2260 | 0.402 | 1.09 | 1.23 | -0.0059292 | 2260 | 0.402 | 2260 | 0.402 | 1.09 | 1.23 | -0.00593
CFLBldgSDGAsmNewCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Asm | New | CZ08 | 2.26 | 0.000402 | 0 | 2.47 | 0.000489 | -0.0118 | 2.26 | 0.000402 | 0 | 2.47 | 0.000489 | -0.0118 |  | CFL | Bldg | 2260 | 0.402 | 2260 | 0.402 | 1.09 | 1.22 | -0.0052212 | 2260 | 0.402 | 2260 | 0.402 | 1.09 | 1.22 | -0.00522
CFLBldgSDGAsmNewCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Asm | New | CZ10 | 2.26 | 0.000402 | 0 | 2.46 | 0.0005 | -0.0141 | 2.26 | 0.000402 | 0 | 2.46 | 0.0005 | -0.0141 |  | CFL | Bldg | 2260 | 0.402 | 2260 | 0.402 | 1.09 | 1.24 | -0.0062389 | 2260 | 0.402 | 2260 | 0.402 | 1.09 | 1.24 | -0.00624
CFLBldgSDGAsmNewCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Asm | New | CZ14 | 2.26 | 0.000402 | 0 | 2.4 | 0.00048 | -0.0218 | 2.26 | 0.000402 | 0 | 2.4 | 0.00048 | -0.0218 |  | CFL | Bldg | 2260 | 0.402 | 2260 | 0.402 | 1.06 | 1.19 | -0.009646 | 2260 | 0.402 | 2260 | 0.402 | 1.06 | 1.19 | -0.00965
CFLBldgSDGAsmNewCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Asm | New | CZ15 | 2.26 | 0.000402 | 0 | 2.72 | 0.000504 | -0.00676 | 2.26 | 0.000402 | 0 | 2.72 | 0.000504 | -0.00676 |  | CFL | Bldg | 2260 | 0.402 | 2260 | 0.402 | 1.2 | 1.25 | -0.0029912 | 2260 | 0.402 | 2260 | 0.402 | 1.2 | 1.25 | -0.00299
CFLBldgSDGAsmNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SDG | Asm | New | IOU | 2.26 | 0.000402 | 0 | 2.4598 | 0.00049502 | -0.013702 | 2.26 | 0.000402 | 0 | 2.4598 | 0.00049502 | -0.013702 |  | CFL | Bldg | 2260 | 0.402 | 2260 | 0.402 | 1.09 | 1.23 | -0.0060627 | 2260 | 0.402 | 2260 | 0.402 | 1.09 | 1.23 | -0.00606
CFLBldgSDGComExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Com | Ex | CZ06 | 3.0689 | 0.0005905 | 0 | 3.3757 | 0.00073143 | -0.013106 | 3.0086 | 0.00056954 | 0 | 3.3092 | 0.00070495 | -0.01289 |  | CFL | Bldg | 3070 | 0.591 | 3010 | 0.57 | 1.1 | 1.24 | -0.0042844 | 3070 | 0.591 | 3010 | 0.57 | 1.1 | 1.24 | -0.00428
CFLBldgSDGComExCZ07 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Com | Ex | CZ07 | 3.0409 | 0.00060301 | 0 | 3.3783 | 0.0007418 | -0.0092764 | 2.9691 | 0.00057832 | 0 | 3.2978 | 0.00071099 | -0.0091189 |  | CFL | Bldg | 3040 | 0.603 | 2970 | 0.578 | 1.11 | 1.23 | -0.0030713 | 3040 | 0.603 | 2970 | 0.578 | 1.11 | 1.23 | -0.00307
CFLBldgSDGComExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Com | Ex | CZ08 | 3.3633 | 0.00065101 | 0 | 3.7675 | 0.00081482 | -0.010828 | 3.3037 | 0.00062856 | 0 | 3.7012 | 0.00078625 | -0.010638 |  | CFL | Bldg | 3360 | 0.651 | 3300 | 0.629 | 1.12 | 1.25 | -0.00322 | 3360 | 0.651 | 3300 | 0.629 | 1.12 | 1.25 | -0.00322
CFLBldgSDGComExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Com | Ex | CZ10 | 3.073 | 0.00062676 | 0 | 3.4028 | 0.00078691 | -0.011801 | 3.0092 | 0.00060276 | 0 | 3.3314 | 0.00075631 | -0.011575 |  | CFL | Bldg | 3070 | 0.627 | 3010 | 0.603 | 1.11 | 1.25 | -0.0038466 | 3070 | 0.627 | 3010 | 0.603 | 1.11 | 1.25 | -0.00385
CFLBldgSDGComExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Com | Ex | CZ14 | 2.6567 | 0.00057969 | 0 | 2.8973 | 0.0007244 | -0.014674 | 2.5785 | 0.00055109 | 0 | 2.8121 | 0.00068787 | -0.014268 |  | CFL | Bldg | 2660 | 0.58 | 2580 | 0.551 | 1.09 | 1.25 | -0.0055335 | 2660 | 0.58 | 2580 | 0.551 | 1.09 | 1.25 | -0.00553
CFLBldgSDGComExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Com | Ex | CZ15 | 2.3454 | 0.00045926 | 0 | 2.7775 | 0.000578 | -0.0034898 | 2.2863 | 0.00044066 | 0 | 2.7053 | 0.0005545 | -0.0034077 |  | CFL | Bldg | 2350 | 0.459 | 2290 | 0.441 | 1.18 | 1.26 | -0.0014905 | 2350 | 0.459 | 2290 | 0.441 | 1.18 | 1.26 | -0.00149
CFLBldgSDGComExIOU | Com-Iltg-dWatt-CFL_OSbldg | SDG | Com | Ex | IOU | 3.0553 | 0.00060909 | 0 | 3.3916 | 0.0007536 | -0.010038 | 2.9861 | 0.00058474 | 0 | 3.3142 | 0.00072302 | -0.0098604 |  | CFL | Bldg | 3060 | 0.609 | 2990 | 0.585 | 1.11 | 1.24 | -0.0033021 | 3060 | 0.609 | 2990 | 0.585 | 1.11 | 1.24 | -0.0033
CFLBldgSDGComNewCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Com | New | CZ06 | 2.9522 | 0.00054295 | 0 | 3.1982 | 0.00066868 | -0.013218 | 2.9522 | 0.00054295 | 0 | 3.1982 | 0.00066868 | -0.013218 |  | CFL | Bldg | 2950 | 0.543 | 2950 | 0.543 | 1.08 | 1.23 | -0.0044772 | 2950 | 0.543 | 2950 | 0.543 | 1.08 | 1.23 | -0.00448
CFLBldgSDGComNewCZ07 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Com | New | CZ07 | 2.907 | 0.00055702 | 0 | 3.1664 | 0.00067591 | -0.0090198 | 2.907 | 0.00055702 | 0 | 3.1664 | 0.00067591 | -0.0090198 |  | CFL | Bldg | 2910 | 0.557 | 2910 | 0.557 | 1.09 | 1.21 | -0.0031028 | 2910 | 0.557 | 2910 | 0.557 | 1.09 | 1.21 | -0.0031
CFLBldgSDGComNewCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Com | New | CZ08 | 3.37 | 0.0006288 | 0 | 3.7054 | 0.00078172 | -0.011054 | 3.37 | 0.0006288 | 0 | 3.7054 | 0.00078172 | -0.011054 |  | CFL | Bldg | 3370 | 0.629 | 3370 | 0.629 | 1.1 | 1.24 | -0.00328 | 3370 | 0.629 | 3370 | 0.629 | 1.1 | 1.24 | -0.00328
CFLBldgSDGComNewCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Com | New | CZ10 | 3.0153 | 0.00059668 | 0 | 3.3163 | 0.00077003 | -0.011824 | 3.0153 | 0.00059668 | 0 | 3.3163 | 0.00077003 | -0.011824 |  | CFL | Bldg | 3020 | 0.597 | 3020 | 0.597 | 1.1 | 1.29 | -0.0039212 | 3020 | 0.597 | 3020 | 0.597 | 1.1 | 1.29 | -0.00392
CFLBldgSDGComNewCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Com | New | CZ14 | 2.5174 | 0.0005248 | 0 | 2.7263 | 0.00067121 | -0.014151 | 2.5174 | 0.0005248 | 0 | 2.7263 | 0.00067121 | -0.014151 |  | CFL | Bldg | 2520 | 0.525 | 2520 | 0.525 | 1.08 | 1.28 | -0.0056214 | 2520 | 0.525 | 2520 | 0.525 | 1.08 | 1.28 | -0.00562
CFLBldgSDGComNewCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Com | New | CZ15 | 2.1487 | 0.00039256 | 0 | 2.5289 | 0.00051614 | -0.0030529 | 2.1487 | 0.00039256 | 0 | 2.5289 | 0.00051614 | -0.0030529 |  | CFL | Bldg | 2150 | 0.393 | 2150 | 0.393 | 1.18 | 1.31 | -0.0014208 | 2150 | 0.393 | 2150 | 0.393 | 1.18 | 1.31 | -0.00142
CFLBldgSDGComNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SDG | Com | New | IOU | 2.9423 | 0.00056714 | 0 | 3.213 | 0.00069998 | -0.0098746 | 2.9423 | 0.00056714 | 0 | 3.213 | 0.00069998 | -0.0098746 |  | CFL | Bldg | 2940 | 0.567 | 2940 | 0.567 | 1.09 | 1.23 | -0.0033561 | 2940 | 0.567 | 2940 | 0.567 | 1.09 | 1.23 | -0.00336
CFLBldgSDGECCExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SDG | ECC | Ex | CZ06 | 2.413 | 0.0006427 | 0 | 2.7024 | 0.00082043 | -0.014056 | 2.31 | 0.00058087 | 0 | 2.59 | 0.00074175 | -0.0134 |  | CFL | Bldg | 2410 | 0.643 | 2310 | 0.581 | 1.12 | 1.28 | -0.0058009 | 2410 | 0.643 | 2310 | 0.581 | 1.12 | 1.28 | -0.0058
CFLBldgSDGECCExCZ07 | Com-Iltg-dWatt-CFL_OSbldg | SDG | ECC | Ex | CZ07 | 2.4131 | 0.00064274 | 0 | 2.7319 | 0.00081855 | -0.011569 | 2.31 | 0.00058088 | 0 | 2.61 | 0.00073981 | -0.0111 |  | CFL | Bldg | 2410 | 0.643 | 2310 | 0.581 | 1.13 | 1.27 | -0.0048052 | 2410 | 0.643 | 2310 | 0.581 | 1.13 | 1.27 | -0.00481
CFLBldgSDGECCExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SDG | ECC | Ex | CZ08 | 2.4132 | 0.00064277 | 0 | 2.7419 | 0.00081659 | -0.012569 | 2.31 | 0.00058088 | 0 | 2.62 | 0.00073781 | -0.0121 |  | CFL | Bldg | 2410 | 0.643 | 2310 | 0.581 | 1.13 | 1.27 | -0.0052381 | 2410 | 0.643 | 2310 | 0.581 | 1.13 | 1.27 | -0.00524
CFLBldgSDGECCExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SDG | ECC | Ex | CZ10 | 2.4131 | 0.00064274 | 0 | 2.7319 | 0.00083243 | -0.014956 | 2.31 | 0.00058088 | 0 | 2.61 | 0.00075275 | -0.0143 |  | CFL | Bldg | 2410 | 0.643 | 2310 | 0.581 | 1.13 | 1.3 | -0.0061905 | 2410 | 0.643 | 2310 | 0.581 | 1.13 | 1.3 | -0.00619
CFLBldgSDGECCExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SDG | ECC | Ex | CZ14 | 2.413 | 0.0006427 | 0 | 2.6718 | 0.00082043 | -0.022537 | 2.31 | 0.00058087 | 0 | 2.5594 | 0.00074175 | -0.0216 |  | CFL | Bldg | 2410 | 0.643 | 2310 | 0.581 | 1.11 | 1.28 | -0.0093506 | 2410 | 0.643 | 2310 | 0.581 | 1.11 | 1.28 | -0.00935
CFLBldgSDGECCExIOU | Com-Iltg-dWatt-CFL_OSbldg | SDG | ECC | Ex | IOU | 2.4131 | 0.00064274 | 0 | 2.7315 | 0.00082182 | -0.012444 | 2.31 | 0.00058088 | 0 | 2.6097 | 0.00074286 | -0.011927 |  | CFL | Bldg | 2410 | 0.643 | 2310 | 0.581 | 1.13 | 1.28 | -0.0051634 | 2410 | 0.643 | 2310 | 0.581 | 1.13 | 1.28 | -0.00516
CFLBldgSDGECCNewCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SDG | ECC | New | CZ06 | 2.31 | 0.000579 | 0 | 2.6 | 0.000743 | -0.0164 | 2.31 | 0.000579 | 0 | 2.6 | 0.000743 | -0.0164 |  | CFL | Bldg | 2310 | 0.579 | 2310 | 0.579 | 1.13 | 1.28 | -0.0070996 | 2310 | 0.579 | 2310 | 0.579 | 1.13 | 1.28 | -0.0071
CFLBldgSDGECCNewCZ07 | Com-Iltg-dWatt-CFL_OSbldg | SDG | ECC | New | CZ07 | 2.31 | 0.000579 | 0 | 2.59 | 0.000748 | -0.0123 | 2.31 | 0.000579 | 0 | 2.59 | 0.000748 | -0.0123 |  | CFL | Bldg | 2310 | 0.579 | 2310 | 0.579 | 1.12 | 1.29 | -0.0053247 | 2310 | 0.579 | 2310 | 0.579 | 1.12 | 1.29 | -0.00532
CFLBldgSDGECCNewCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SDG | ECC | New | CZ08 | 2.31 | 0.000579 | 0 | 2.62 | 0.000742 | -0.012 | 2.31 | 0.000579 | 0 | 2.62 | 0.000742 | -0.012 |  | CFL | Bldg | 2310 | 0.579 | 2310 | 0.579 | 1.13 | 1.28 | -0.0051948 | 2310 | 0.579 | 2310 | 0.579 | 1.13 | 1.28 | -0.00519
CFLBldgSDGECCNewCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SDG | ECC | New | CZ10 | 2.31 | 0.000579 | 0 | 2.64 | 0.000765 | -0.0136 | 2.31 | 0.000579 | 0 | 2.64 | 0.000765 | -0.0136 |  | CFL | Bldg | 2310 | 0.579 | 2310 | 0.579 | 1.14 | 1.32 | -0.0058874 | 2310 | 0.579 | 2310 | 0.579 | 1.14 | 1.32 | -0.00589
CFLBldgSDGECCNewCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SDG | ECC | New | CZ14 | 2.31 | 0.000579 | 0 | 2.61 | 0.000741 | -0.0214 | 2.31 | 0.000579 | 0 | 2.61 | 0.000741 | -0.0214 |  | CFL | Bldg | 2310 | 0.579 | 2310 | 0.579 | 1.13 | 1.28 | -0.0092641 | 2310 | 0.579 | 2310 | 0.579 | 1.13 | 1.28 | -0.00926
CFLBldgSDGECCNewCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SDG | ECC | New | CZ15 | 2.31 | 0.000579 | 0 | 2.79 | 0.000759 | -0.00534 | 2.31 | 0.000579 | 0 | 2.79 | 0.000759 | -0.00534 |  | CFL | Bldg | 2310 | 0.579 | 2310 | 0.579 | 1.21 | 1.31 | -0.0023117 | 2310 | 0.579 | 2310 | 0.579 | 1.21 | 1.31 | -0.00231
CFLBldgSDGECCNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SDG | ECC | New | IOU | 2.31 | 0.000579 | 0 | 2.6022 | 0.00075188 | -0.012672 | 2.31 | 0.000579 | 0 | 2.6022 | 0.00075188 | -0.012672 |  | CFL | Bldg | 2310 | 0.579 | 2310 | 0.579 | 1.13 | 1.3 | -0.0054855 | 2310 | 0.579 | 2310 | 0.579 | 1.13 | 1.3 | -0.00549
CFLBldgSDGEPrExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SDG | EPr | Ex | CZ06 | 2.2354 | 0.00062783 | 0 | 2.5247 | 0.00080122 | -0.01038 | 2.11 | 0.00056418 | 0 | 2.3896 | 0.00072021 | -0.0098496 |  | CFL | Bldg | 2240 | 0.628 | 2110 | 0.564 | 1.13 | 1.28 | -0.0046681 | 2240 | 0.628 | 2110 | 0.564 | 1.13 | 1.28 | -0.00467
CFLBldgSDGEPrExCZ07 | Com-Iltg-dWatt-CFL_OSbldg | SDG | EPr | Ex | CZ07 | 2.2354 | 0.00062784 | 0 | 2.5247 | 0.0008082 | -0.0095905 | 2.11 | 0.00056418 | 0 | 2.3897 | 0.00072621 | -0.00906 |  | CFL | Bldg | 2240 | 0.628 | 2110 | 0.564 | 1.13 | 1.29 | -0.0042938 | 2240 | 0.628 | 2110 | 0.564 | 1.13 | 1.29 | -0.00429
CFLBldgSDGEPrExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SDG | EPr | Ex | CZ08 | 2.2354 | 0.00062784 | 0 | 2.5547 | 0.00080824 | -0.0087623 | 2.11 | 0.00056418 | 0 | 2.41 | 0.00072721 | -0.00828 |  | CFL | Bldg | 2240 | 0.628 | 2110 | 0.564 | 1.14 | 1.29 | -0.0039242 | 2240 | 0.628 | 2110 | 0.564 | 1.14 | 1.29 | -0.00392
CFLBldgSDGEPrExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SDG | EPr | Ex | CZ10 | 2.2354 | 0.00062784 | 0 | 2.5347 | 0.00080123 | -0.010979 | 2.11 | 0.00056418 | 0 | 2.39 | 0.00072021 | -0.0104 |  | CFL | Bldg | 2240 | 0.628 | 2110 | 0.564 | 1.13 | 1.28 | -0.0049289 | 2240 | 0.628 | 2110 | 0.564 | 1.13 | 1.28 | -0.00493
CFLBldgSDGEPrExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SDG | EPr | Ex | CZ14 | 2.2353 | 0.0006278 | 0 | 2.4253 | 0.00080219 | -0.01836 | 2.11 | 0.00056418 | 0 | 2.3 | 0.00072025 | -0.0173 |  | CFL | Bldg | 2240 | 0.628 | 2110 | 0.564 | 1.09 | 1.28 | -0.0081991 | 2240 | 0.628 | 2110 | 0.564 | 1.09 | 1.28 | -0.0082
CFLBldgSDGEPrExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SDG | EPr | Ex | CZ15 | 2.2356 | 0.00062792 | 0 | 2.7145 | 0.00080533 | -0.0046708 | 2.11 | 0.00056417 | 0 | 2.56 | 0.0007242 | -0.0044197 |  | CFL | Bldg | 2240 | 0.628 | 2110 | 0.564 | 1.21 | 1.28 | -0.0020946 | 2240 | 0.628 | 2110 | 0.564 | 1.21 | 1.28 | -0.00209
CFLBldgSDGEPrExIOU | Com-Iltg-dWatt-CFL_OSbldg | SDG | EPr | Ex | IOU | 2.2354 | 0.00062784 | 0 | 2.5292 | 0.00080553 | -0.010102 | 2.11 | 0.00056418 | 0 | 2.3905 | 0.00072396 | -0.0095542 |  | CFL | Bldg | 2240 | 0.628 | 2110 | 0.564 | 1.13 | 1.28 | -0.0045281 | 2240 | 0.628 | 2110 | 0.564 | 1.13 | 1.28 | -0.00453
CFLBldgSDGEPrNewCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SDG | EPr | New | CZ06 | 2.11 | 0.000569 | 0 | 2.32 | 0.000761 | -0.0134 | 2.11 | 0.000569 | 0 | 2.32 | 0.000761 | -0.0134 |  | CFL | Bldg | 2110 | 0.569 | 2110 | 0.569 | 1.1 | 1.34 | -0.0063507 | 2110 | 0.569 | 2110 | 0.569 | 1.1 | 1.34 | -0.00635
CFLBldgSDGEPrNewCZ07 | Com-Iltg-dWatt-CFL_OSbldg | SDG | EPr | New | CZ07 | 2.11 | 0.000569 | 0 | 2.29 | 0.000753 | -0.0125 | 2.11 | 0.000569 | 0 | 2.29 | 0.000753 | -0.0125 |  | CFL | Bldg | 2110 | 0.569 | 2110 | 0.569 | 1.09 | 1.32 | -0.0059242 | 2110 | 0.569 | 2110 | 0.569 | 1.09 | 1.32 | -0.00592
CFLBldgSDGEPrNewCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SDG | EPr | New | CZ08 | 2.11 | 0.000569 | 0 | 2.36 | 0.000782 | -0.0115 | 2.11 | 0.000569 | 0 | 2.36 | 0.000782 | -0.0115 |  | CFL | Bldg | 2110 | 0.569 | 2110 | 0.569 | 1.12 | 1.37 | -0.0054502 | 2110 | 0.569 | 2110 | 0.569 | 1.12 | 1.37 | -0.00545
CFLBldgSDGEPrNewCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SDG | EPr | New | CZ10 | 2.11 | 0.000569 | 0 | 2.36 | 0.00081 | -0.0139 | 2.11 | 0.000569 | 0 | 2.36 | 0.00081 | -0.0139 |  | CFL | Bldg | 2110 | 0.569 | 2110 | 0.569 | 1.12 | 1.42 | -0.0065877 | 2110 | 0.569 | 2110 | 0.569 | 1.12 | 1.42 | -0.00659
CFLBldgSDGEPrNewCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SDG | EPr | New | CZ14 | 2.11 | 0.000569 | 0 | 2.31 | 0.000793 | -0.0218 | 2.11 | 0.000569 | 0 | 2.31 | 0.000793 | -0.0218 |  | CFL | Bldg | 2110 | 0.569 | 2110 | 0.569 | 1.09 | 1.39 | -0.010332 | 2110 | 0.569 | 2110 | 0.569 | 1.09 | 1.39 | -0.0103
CFLBldgSDGEPrNewCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SDG | EPr | New | CZ15 | 2.11 | 0.000569 | 0 | 2.56 | 0.00082 | -0.00606 | 2.11 | 0.000569 | 0 | 2.56 | 0.00082 | -0.00606 |  | CFL | Bldg | 2110 | 0.569 | 2110 | 0.569 | 1.21 | 1.44 | -0.002872 | 2110 | 0.569 | 2110 | 0.569 | 1.21 | 1.44 | -0.00287
CFLBldgSDGEPrNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SDG | EPr | New | IOU | 2.11 | 0.000569 | 0 | 2.3189 | 0.00077406 | -0.013013 | 2.11 | 0.000569 | 0 | 2.3189 | 0.00077406 | -0.013013 |  | CFL | Bldg | 2110 | 0.569 | 2110 | 0.569 | 1.1 | 1.36 | -0.0061675 | 2110 | 0.569 | 2110 | 0.569 | 1.1 | 1.36 | -0.00617
CFLBldgSDGERCExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SDG | ERC | Ex | CZ06 | 2.5925 | 0.00072454 | 0 | 2.8318 | 0.00090169 | -0.015954 | 2.39 | 0.00062329 | 0 | 2.61 | 0.00077536 | -0.0147 |  | CFL | Bldg | 2590 | 0.725 | 2390 | 0.623 | 1.09 | 1.24 | -0.0061506 | 2590 | 0.725 | 2390 | 0.623 | 1.09 | 1.24 | -0.00615
CFLBldgSDGERCExCZ07 | Com-Iltg-dWatt-CFL_OSbldg | SDG | ERC | Ex | CZ07 | 2.5926 | 0.00072456 | 0 | 2.8918 | 0.00089974 | -0.012765 | 2.39 | 0.00062328 | 0 | 2.67 | 0.00077436 | -0.0118 |  | CFL | Bldg | 2590 | 0.725 | 2390 | 0.623 | 1.12 | 1.24 | -0.0049372 | 2590 | 0.725 | 2390 | 0.623 | 1.12 | 1.24 | -0.00494
CFLBldgSDGERCExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SDG | ERC | Ex | CZ08 | 2.5926 | 0.00072457 | 0 | 2.8715 | 0.00091168 | -0.013961 | 2.39 | 0.00062328 | 0 | 2.64 | 0.00078435 | -0.0129 |  | CFL | Bldg | 2590 | 0.725 | 2390 | 0.623 | 1.1 | 1.26 | -0.0053975 | 2590 | 0.725 | 2390 | 0.623 | 1.1 | 1.26 | -0.0054
CFLBldgSDGERCExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SDG | ERC | Ex | CZ10 | 2.5926 | 0.00072456 | 0 | 2.8415 | 0.00090671 | -0.01635 | 2.39 | 0.00062328 | 0 | 2.61 | 0.00077939 | -0.015 |  | CFL | Bldg | 2590 | 0.725 | 2390 | 0.623 | 1.09 | 1.25 | -0.0062762 | 2590 | 0.725 | 2390 | 0.623 | 1.09 | 1.25 | -0.00628
CFLBldgSDGERCExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SDG | ERC | Ex | CZ14 | 2.5924 | 0.0007245 | 0 | 2.8217 | 0.00092057 | -0.021635 | 2.39 | 0.00062329 | 0 | 2.6 | 0.0007914 | -0.0199 |  | CFL | Bldg | 2590 | 0.725 | 2390 | 0.623 | 1.09 | 1.27 | -0.0083264 | 2590 | 0.725 | 2390 | 0.623 | 1.09 | 1.27 | -0.00833
CFLBldgSDGERCExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SDG | ERC | Ex | CZ15 | 2.5928 | 0.00072468 | 0 | 3.0515 | 0.00093373 | -0.0079181 | 2.39 | 0.00062327 | 0 | 2.81 | 0.00080238 | -0.0073 |  | CFL | Bldg | 2590 | 0.725 | 2390 | 0.623 | 1.18 | 1.29 | -0.0030544 | 2590 | 0.725 | 2390 | 0.623 | 1.18 | 1.29 | -0.00305
CFLBldgSDGERCExIOU | Com-Iltg-dWatt-CFL_OSbldg | SDG | ERC | Ex | IOU | 2.5926 | 0.00072456 | 0 | 2.8712 | 0.00090303 | -0.014221 | 2.39 | 0.00062328 | 0 | 2.6456 | 0.00077681 | -0.013105 |  | CFL | Bldg | 2590 | 0.725 | 2390 | 0.623 | 1.11 | 1.25 | -0.0054835 | 2590 | 0.725 | 2390 | 0.623 | 1.11 | 1.25 | -0.00548
CFLBldgSDGERCNewCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SDG | ERC | New | CZ06 | 2.39 | 0.000631 | 0 | 2.72 | 0.000808 | -0.0162 | 2.39 | 0.000631 | 0 | 2.72 | 0.000808 | -0.0162 |  | CFL | Bldg | 2390 | 0.631 | 2390 | 0.631 | 1.14 | 1.28 | -0.0067782 | 2390 | 0.631 | 2390 | 0.631 | 1.14 | 1.28 | -0.00678
CFLBldgSDGERCNewCZ07 | Com-Iltg-dWatt-CFL_OSbldg | SDG | ERC | New | CZ07 | 2.39 | 0.000631 | 0 | 2.73 | 0.000796 | -0.0125 | 2.39 | 0.000631 | 0 | 2.73 | 0.000796 | -0.0125 |  | CFL | Bldg | 2390 | 0.631 | 2390 | 0.631 | 1.14 | 1.26 | -0.0052301 | 2390 | 0.631 | 2390 | 0.631 | 1.14 | 1.26 | -0.00523
CFLBldgSDGERCNewCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SDG | ERC | New | CZ08 | 2.39 | 0.000631 | 0 | 2.75 | 0.000827 | -0.0141 | 2.39 | 0.000631 | 0 | 2.75 | 0.000827 | -0.0141 |  | CFL | Bldg | 2390 | 0.631 | 2390 | 0.631 | 1.15 | 1.31 | -0.0058996 | 2390 | 0.631 | 2390 | 0.631 | 1.15 | 1.31 | -0.0059
CFLBldgSDGERCNewCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SDG | ERC | New | CZ10 | 2.39 | 0.000631 | 0 | 2.77 | 0.000864 | -0.0161 | 2.39 | 0.000631 | 0 | 2.77 | 0.000864 | -0.0161 |  | CFL | Bldg | 2390 | 0.631 | 2390 | 0.631 | 1.16 | 1.37 | -0.0067364 | 2390 | 0.631 | 2390 | 0.631 | 1.16 | 1.37 | -0.00674
CFLBldgSDGERCNewCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SDG | ERC | New | CZ14 | 2.39 | 0.000631 | 0 | 2.73 | 0.000852 | -0.0234 | 2.39 | 0.000631 | 0 | 2.73 | 0.000852 | -0.0234 |  | CFL | Bldg | 2390 | 0.631 | 2390 | 0.631 | 1.14 | 1.35 | -0.0097908 | 2390 | 0.631 | 2390 | 0.631 | 1.14 | 1.35 | -0.00979
CFLBldgSDGERCNewCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SDG | ERC | New | CZ15 | 2.39 | 0.000631 | 0 | 3.02 | 0.000866 | -0.00806 | 2.39 | 0.000631 | 0 | 3.02 | 0.000866 | -0.00806 |  | CFL | Bldg | 2390 | 0.631 | 2390 | 0.631 | 1.26 | 1.37 | -0.0033724 | 2390 | 0.631 | 2390 | 0.631 | 1.26 | 1.37 | -0.00337
CFLBldgSDGERCNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SDG | ERC | New | IOU | 2.39 | 0.000631 | 0 | 2.7443 | 0.0008211 | -0.014029 | 2.39 | 0.000631 | 0 | 2.7443 | 0.0008211 | -0.014029 |  | CFL | Bldg | 2390 | 0.631 | 2390 | 0.631 | 1.15 | 1.3 | -0.0058697 | 2390 | 0.631 | 2390 | 0.631 | 1.15 | 1.3 | -0.00587
CFLBldgSDGESeExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SDG | ESe | Ex | CZ06 | 2.3257 | 0.00071297 | 0 | 2.5954 | 0.00090444 | -0.013375 | 2.21 | 0.00065318 | 0 | 2.47 | 0.00082825 | -0.0127 |  | CFL | Bldg | 2330 | 0.713 | 2210 | 0.653 | 1.12 | 1.27 | -0.0057466 | 2330 | 0.713 | 2210 | 0.653 | 1.12 | 1.27 | -0.00575
CFLBldgSDGESeExCZ07 | Com-Iltg-dWatt-CFL_OSbldg | SDG | ESe | Ex | CZ07 | 2.3257 | 0.00071298 | 0 | 2.5854 | 0.00088748 | -0.011779 | 2.21 | 0.00065318 | 0 | 2.46 | 0.00081321 | -0.0112 |  | CFL | Bldg | 2330 | 0.713 | 2210 | 0.653 | 1.11 | 1.25 | -0.0050679 | 2330 | 0.713 | 2210 | 0.653 | 1.11 | 1.25 | -0.00507
CFLBldgSDGESeExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SDG | ESe | Ex | CZ08 | 2.3258 | 0.00071298 | 0 | 2.625 | 0.00089945 | -0.011379 | 2.21 | 0.00065318 | 0 | 2.49 | 0.00082421 | -0.0108 |  | CFL | Bldg | 2330 | 0.713 | 2210 | 0.653 | 1.13 | 1.26 | -0.0048869 | 2330 | 0.713 | 2210 | 0.653 | 1.13 | 1.26 | -0.00489
CFLBldgSDGESeExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SDG | ESe | Ex | CZ10 | 2.3258 | 0.00071298 | 0 | 2.6054 | 0.00089645 | -0.014272 | 2.21 | 0.00065318 | 0 | 2.48 | 0.00082121 | -0.0135 |  | CFL | Bldg | 2330 | 0.713 | 2210 | 0.653 | 1.12 | 1.26 | -0.0061086 | 2330 | 0.713 | 2210 | 0.653 | 1.12 | 1.26 | -0.00611
CFLBldgSDGESeExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SDG | ESe | Ex | CZ14 | 2.3257 | 0.00071295 | 0 | 2.5253 | 0.00086551 | -0.02226 | 2.21 | 0.00065318 | 0 | 2.4 | 0.00079322 | -0.0212 |  | CFL | Bldg | 2330 | 0.713 | 2210 | 0.653 | 1.09 | 1.21 | -0.0095928 | 2330 | 0.713 | 2210 | 0.653 | 1.09 | 1.21 | -0.00959
CFLBldgSDGESeExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SDG | ESe | Ex | CZ15 | 2.3259 | 0.00071305 | 0 | 2.8349 | 0.00089554 | -0.0063491 | 2.21 | 0.00065317 | 0 | 2.69 | 0.00082021 | -0.00604 |  | CFL | Bldg | 2330 | 0.713 | 2210 | 0.653 | 1.22 | 1.26 | -0.002733 | 2330 | 0.713 | 2210 | 0.653 | 1.22 | 1.26 | -0.00273
CFLBldgSDGESeExIOU | Com-Iltg-dWatt-CFL_OSbldg | SDG | ESe | Ex | IOU | 2.3257 | 0.00071298 | 0 | 2.5946 | 0.00089171 | -0.012727 | 2.21 | 0.00065318 | 0 | 2.4687 | 0.00081699 | -0.012077 |  | CFL | Bldg | 2330 | 0.713 | 2210 | 0.653 | 1.12 | 1.25 | -0.0054647 | 2330 | 0.713 | 2210 | 0.653 | 1.12 | 1.25 | -0.00546
CFLBldgSDGESeNewCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SDG | ESe | New | CZ06 | 2.21 | 0.000658 | 0 | 2.43 | 0.000866 | -0.0164 | 2.21 | 0.000658 | 0 | 2.43 | 0.000866 | -0.0164 |  | CFL | Bldg | 2210 | 0.658 | 2210 | 0.658 | 1.1 | 1.32 | -0.0074208 | 2210 | 0.658 | 2210 | 0.658 | 1.1 | 1.32 | -0.00742
CFLBldgSDGESeNewCZ07 | Com-Iltg-dWatt-CFL_OSbldg | SDG | ESe | New | CZ07 | 2.21 | 0.000658 | 0 | 2.39 | 0.000845 | -0.0142 | 2.21 | 0.000658 | 0 | 2.39 | 0.000845 | -0.0142 |  | CFL | Bldg | 2210 | 0.658 | 2210 | 0.658 | 1.08 | 1.28 | -0.0064253 | 2210 | 0.658 | 2210 | 0.658 | 1.08 | 1.28 | -0.00643
CFLBldgSDGESeNewCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SDG | ESe | New | CZ08 | 2.21 | 0.000658 | 0 | 2.46 | 0.000876 | -0.0134 | 2.21 | 0.000658 | 0 | 2.46 | 0.000876 | -0.0134 |  | CFL | Bldg | 2210 | 0.658 | 2210 | 0.658 | 1.11 | 1.33 | -0.0060633 | 2210 | 0.658 | 2210 | 0.658 | 1.11 | 1.33 | -0.00606
CFLBldgSDGESeNewCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SDG | ESe | New | CZ10 | 2.21 | 0.000658 | 0 | 2.47 | 0.000916 | -0.0169 | 2.21 | 0.000658 | 0 | 2.47 | 0.000916 | -0.0169 |  | CFL | Bldg | 2210 | 0.658 | 2210 | 0.658 | 1.12 | 1.39 | -0.0076471 | 2210 | 0.658 | 2210 | 0.658 | 1.12 | 1.39 | -0.00765
CFLBldgSDGESeNewCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SDG | ESe | New | CZ14 | 2.21 | 0.000658 | 0 | 2.43 | 0.0009 | -0.0248 | 2.21 | 0.000658 | 0 | 2.43 | 0.0009 | -0.0248 |  | CFL | Bldg | 2210 | 0.658 | 2210 | 0.658 | 1.1 | 1.37 | -0.011222 | 2210 | 0.658 | 2210 | 0.658 | 1.1 | 1.37 | -0.0112
CFLBldgSDGESeNewCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SDG | ESe | New | CZ15 | 2.21 | 0.000658 | 0 | 2.73 | 0.00091 | -0.00743 | 2.21 | 0.000658 | 0 | 2.73 | 0.00091 | -0.00743 |  | CFL | Bldg | 2210 | 0.658 | 2210 | 0.658 | 1.24 | 1.38 | -0.003362 | 2210 | 0.658 | 2210 | 0.658 | 1.24 | 1.38 | -0.00336
CFLBldgSDGESeNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SDG | ESe | New | IOU | 2.21 | 0.000658 | 0 | 2.423 | 0.0008715 | -0.015222 | 2.21 | 0.000658 | 0 | 2.423 | 0.0008715 | -0.015222 |  | CFL | Bldg | 2210 | 0.658 | 2210 | 0.658 | 1.1 | 1.32 | -0.0068879 | 2210 | 0.658 | 2210 | 0.658 | 1.1 | 1.32 | -0.00689
CFLBldgSDGEUnExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SDG | EUn | Ex | CZ06 | 2.363 | 0.00066387 | 0 | 2.6924 | 0.00083948 | -0.0099734 | 2.26 | 0.00059081 | 0 | 2.58 | 0.00074675 | -0.0095894 |  | CFL | Bldg | 2360 | 0.664 | 2260 | 0.591 | 1.14 | 1.26 | -0.0042431 | 2360 | 0.664 | 2260 | 0.591 | 1.14 | 1.26 | -0.00424
CFLBldgSDGEUnExCZ07 | Com-Iltg-dWatt-CFL_OSbldg | SDG | EUn | Ex | CZ07 | 2.3631 | 0.00066393 | 0 | 2.6825 | 0.00083162 | -0.0089243 | 2.26 | 0.00059081 | 0 | 2.57 | 0.00073975 | -0.0085494 |  | CFL | Bldg | 2360 | 0.664 | 2260 | 0.591 | 1.14 | 1.25 | -0.0037829 | 2360 | 0.664 | 2260 | 0.591 | 1.14 | 1.25 | -0.00378
CFLBldgSDGEUnExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SDG | EUn | Ex | CZ08 | 2.3632 | 0.00066396 | 0 | 2.7025 | 0.0008416 | -0.0096326 | 2.26 | 0.00059081 | 0 | 2.59 | 0.00074875 | -0.0092294 |  | CFL | Bldg | 2360 | 0.664 | 2260 | 0.591 | 1.15 | 1.27 | -0.0040838 | 2360 | 0.664 | 2260 | 0.591 | 1.15 | 1.27 | -0.00408
CFLBldgSDGEUnExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SDG | EUn | Ex | CZ10 | 2.3631 | 0.00066393 | 0 | 2.7025 | 0.00085543 | -0.011369 | 2.26 | 0.00059081 | 0 | 2.59 | 0.00076075 | -0.0109 |  | CFL | Bldg | 2360 | 0.664 | 2260 | 0.591 | 1.15 | 1.29 | -0.004823 | 2360 | 0.664 | 2260 | 0.591 | 1.15 | 1.29 | -0.00482
CFLBldgSDGEUnExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SDG | EUn | Ex | CZ14 | 2.363 | 0.00066387 | 0 | 2.6724 | 0.00084448 | -0.015656 | 2.26 | 0.00059081 | 0 | 2.56 | 0.00075081 | -0.015 |  | CFL | Bldg | 2360 | 0.664 | 2260 | 0.591 | 1.13 | 1.27 | -0.0066372 | 2360 | 0.664 | 2260 | 0.591 | 1.13 | 1.27 | -0.00664
CFLBldgSDGEUnExIOU | Com-Iltg-dWatt-CFL_OSbldg | SDG | EUn | Ex | IOU | 2.3631 | 0.00066393 | 0 | 2.6874 | 0.00083741 | -0.0095455 | 2.26 | 0.00059081 | 0 | 2.5749 | 0.00074486 | -0.0091467 |  | CFL | Bldg | 2360 | 0.664 | 2260 | 0.591 | 1.14 | 1.26 | -0.0040472 | 2360 | 0.664 | 2260 | 0.591 | 1.14 | 1.26 | -0.00405
CFLBldgSDGEUnNewCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SDG | EUn | New | CZ06 | 2.26 | 0.000588 | 0 | 2.61 | 0.00074 | -0.00734 | 2.26 | 0.000588 | 0 | 2.61 | 0.00074 | -0.00734 |  | CFL | Bldg | 2260 | 0.588 | 2260 | 0.588 | 1.15 | 1.26 | -0.0032478 | 2260 | 0.588 | 2260 | 0.588 | 1.15 | 1.26 | -0.00325
CFLBldgSDGEUnNewCZ07 | Com-Iltg-dWatt-CFL_OSbldg | SDG | EUn | New | CZ07 | 2.26 | 0.000588 | 0 | 2.58 | 0.000734 | -0.00655 | 2.26 | 0.000588 | 0 | 2.58 | 0.000734 | -0.00655 |  | CFL | Bldg | 2260 | 0.588 | 2260 | 0.588 | 1.14 | 1.25 | -0.0028982 | 2260 | 0.588 | 2260 | 0.588 | 1.14 | 1.25 | -0.0029
CFLBldgSDGEUnNewCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SDG | EUn | New | CZ08 | 2.26 | 0.000588 | 0 | 2.62 | 0.000748 | -0.00649 | 2.26 | 0.000588 | 0 | 2.62 | 0.000748 | -0.00649 |  | CFL | Bldg | 2260 | 0.588 | 2260 | 0.588 | 1.16 | 1.27 | -0.0028717 | 2260 | 0.588 | 2260 | 0.588 | 1.16 | 1.27 | -0.00287
CFLBldgSDGEUnNewCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SDG | EUn | New | CZ10 | 2.26 | 0.000588 | 0 | 2.65 | 0.000771 | -0.0075 | 2.26 | 0.000588 | 0 | 2.65 | 0.000771 | -0.0075 |  | CFL | Bldg | 2260 | 0.588 | 2260 | 0.588 | 1.17 | 1.31 | -0.0033186 | 2260 | 0.588 | 2260 | 0.588 | 1.17 | 1.31 | -0.00332
CFLBldgSDGEUnNewCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SDG | EUn | New | CZ14 | 2.26 | 0.000588 | 0 | 2.54 | 0.000713 | -0.0124 | 2.26 | 0.000588 | 0 | 2.54 | 0.000713 | -0.0124 |  | CFL | Bldg | 2260 | 0.588 | 2260 | 0.588 | 1.12 | 1.21 | -0.0054867 | 2260 | 0.588 | 2260 | 0.588 | 1.12 | 1.21 | -0.00549
CFLBldgSDGEUnNewCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SDG | EUn | New | CZ15 | 2.26 | 0.000588 | 0 | 2.77 | 0.000779 | -0.00346 | 2.26 | 0.000588 | 0 | 2.77 | 0.000779 | -0.00346 |  | CFL | Bldg | 2260 | 0.588 | 2260 | 0.588 | 1.23 | 1.32 | -0.001531 | 2260 | 0.588 | 2260 | 0.588 | 1.23 | 1.32 | -0.00153
CFLBldgSDGEUnNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SDG | EUn | New | IOU | 2.26 | 0.000588 | 0 | 2.5968 | 0.00074274 | -0.0068073 | 2.26 | 0.000588 | 0 | 2.5968 | 0.00074274 | -0.0068073 |  | CFL | Bldg | 2260 | 0.588 | 2260 | 0.588 | 1.15 | 1.26 | -0.0030121 | 2260 | 0.588 | 2260 | 0.588 | 1.15 | 1.26 | -0.00301
CFLBldgSDGGroExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Gro | Ex | CZ06 | 3.8866 | 0.00049449 | 0 | 3.8775 | 0.00061041 | -0.053258 | 3.85 | 0.00048992 | 0 | 3.85 | 0.000604 | -0.0528 |  | CFL | Bldg | 3890 | 0.494 | 3850 | 0.49 | 1 | 1.23 | -0.013714 | 3890 | 0.494 | 3850 | 0.49 | 1 | 1.23 | -0.0137
CFLBldgSDGGroExCZ07 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Gro | Ex | CZ07 | 3.8866 | 0.00049449 | 0 | 3.8266 | 0.00060141 | -0.057158 | 3.85 | 0.00048992 | 0 | 3.79 | 0.000595 | -0.0567 |  | CFL | Bldg | 3890 | 0.494 | 3850 | 0.49 | 0.984 | 1.21 | -0.014727 | 3890 | 0.494 | 3850 | 0.49 | 0.984 | 1.21 | -0.0147
CFLBldgSDGGroExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Gro | Ex | CZ08 | 3.8866 | 0.00049449 | 0 | 3.9675 | 0.00062641 | -0.048566 | 3.85 | 0.00048992 | 0 | 3.94 | 0.00062 | -0.0482 |  | CFL | Bldg | 3890 | 0.494 | 3850 | 0.49 | 1.02 | 1.27 | -0.012519 | 3890 | 0.494 | 3850 | 0.49 | 1.02 | 1.27 | -0.0125
CFLBldgSDGGroExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Gro | Ex | CZ10 | 3.8866 | 0.00049449 | 0 | 4.0375 | 0.00065741 | -0.045866 | 3.85 | 0.00048992 | 0 | 4.01 | 0.000651 | -0.0455 |  | CFL | Bldg | 3890 | 0.494 | 3850 | 0.49 | 1.04 | 1.33 | -0.011818 | 3890 | 0.494 | 3850 | 0.49 | 1.04 | 1.33 | -0.0118
CFLBldgSDGGroExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Gro | Ex | CZ14 | 3.8867 | 0.0004945 | 0 | 4.0266 | 0.00066833 | -0.046266 | 3.85 | 0.00048992 | 0 | 3.99 | 0.000661 | -0.0459 |  | CFL | Bldg | 3890 | 0.494 | 3850 | 0.49 | 1.04 | 1.35 | -0.011922 | 3890 | 0.494 | 3850 | 0.49 | 1.04 | 1.35 | -0.0119
CFLBldgSDGGroExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Gro | Ex | CZ15 | 3.8866 | 0.00049449 | 0 | 4.3566 | 0.0006554 | -0.026583 | 3.85 | 0.00048992 | 0 | 4.32 | 0.000649 | -0.0264 |  | CFL | Bldg | 3890 | 0.494 | 3850 | 0.49 | 1.12 | 1.32 | -0.0068571 | 3890 | 0.494 | 3850 | 0.49 | 1.12 | 1.32 | -0.00686
CFLBldgSDGGroExIOU | Com-Iltg-dWatt-CFL_OSbldg | SDG | Gro | Ex | IOU | 3.8866 | 0.00049449 | 0 | 3.8916 | 0.00061804 | -0.053582 | 3.85 | 0.00048992 | 0 | 3.8582 | 0.00061162 | -0.053152 |  | CFL | Bldg | 3890 | 0.494 | 3850 | 0.49 | 1 | 1.25 | -0.013806 | 3890 | 0.494 | 3850 | 0.49 | 1 | 1.25 | -0.0138
CFLBldgSDGGroNewCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Gro | New | CZ06 | 3.85 | 0.000489 | 0 | 4.03 | 0.000617 | -0.0439 | 3.85 | 0.000489 | 0 | 4.03 | 0.000617 | -0.0439 |  | CFL | Bldg | 3850 | 0.489 | 3850 | 0.489 | 1.05 | 1.26 | -0.011403 | 3850 | 0.489 | 3850 | 0.489 | 1.05 | 1.26 | -0.0114
CFLBldgSDGGroNewCZ07 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Gro | New | CZ07 | 3.85 | 0.000489 | 0 | 3.99 | 0.000602 | -0.0459 | 3.85 | 0.000489 | 0 | 3.99 | 0.000602 | -0.0459 |  | CFL | Bldg | 3850 | 0.489 | 3850 | 0.489 | 1.04 | 1.23 | -0.011922 | 3850 | 0.489 | 3850 | 0.489 | 1.04 | 1.23 | -0.0119
CFLBldgSDGGroNewCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Gro | New | CZ08 | 3.85 | 0.000489 | 0 | 4.08 | 0.000628 | -0.0384 | 3.85 | 0.000489 | 0 | 4.08 | 0.000628 | -0.0384 |  | CFL | Bldg | 3850 | 0.489 | 3850 | 0.489 | 1.06 | 1.28 | -0.009974 | 3850 | 0.489 | 3850 | 0.489 | 1.06 | 1.28 | -0.00997
CFLBldgSDGGroNewCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Gro | New | CZ10 | 3.85 | 0.000489 | 0 | 4.12 | 0.00069 | -0.0401 | 3.85 | 0.000489 | 0 | 4.12 | 0.00069 | -0.0401 |  | CFL | Bldg | 3850 | 0.489 | 3850 | 0.489 | 1.07 | 1.41 | -0.010416 | 3850 | 0.489 | 3850 | 0.489 | 1.07 | 1.41 | -0.0104
CFLBldgSDGGroNewCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Gro | New | CZ14 | 3.85 | 0.000489 | 0 | 4.13 | 0.000673 | -0.0439 | 3.85 | 0.000489 | 0 | 4.13 | 0.000673 | -0.0439 |  | CFL | Bldg | 3850 | 0.489 | 3850 | 0.489 | 1.07 | 1.38 | -0.011403 | 3850 | 0.489 | 3850 | 0.489 | 1.07 | 1.38 | -0.0114
CFLBldgSDGGroNewCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Gro | New | CZ15 | 3.85 | 0.000489 | 0 | 4.46 | 0.000683 | -0.0227 | 3.85 | 0.000489 | 0 | 4.46 | 0.000683 | -0.0227 |  | CFL | Bldg | 3850 | 0.489 | 3850 | 0.489 | 1.16 | 1.4 | -0.0058961 | 3850 | 0.489 | 3850 | 0.489 | 1.16 | 1.4 | -0.0059
CFLBldgSDGGroNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SDG | Gro | New | IOU | 3.85 | 0.000489 | 0 | 4.0308 | 0.00062772 | -0.043993 | 3.85 | 0.000489 | 0 | 4.0308 | 0.00062772 | -0.043993 |  | CFL | Bldg | 3850 | 0.489 | 3850 | 0.489 | 1.05 | 1.28 | -0.011427 | 3850 | 0.489 | 3850 | 0.489 | 1.05 | 1.28 | -0.0114
CFLBldgSDGHspExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Hsp | Ex | CZ06 | 4.1996 | 0.00071684 | 0 | 4.7992 | 0.0008868 | -0.022596 | 4.1804 | 0.000713 | 0 | 4.78 | 0.00088104 | -0.0225 |  | CFL | Bldg | 4200 | 0.717 | 4180 | 0.713 | 1.14 | 1.24 | -0.0053823 | 4200 | 0.717 | 4180 | 0.713 | 1.14 | 1.24 | -0.00538
CFLBldgSDGHspExCZ07 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Hsp | Ex | CZ07 | 4.1996 | 0.00071684 | 0 | 4.7992 | 0.0008788 | -0.0207 | 4.1804 | 0.000713 | 0 | 4.78 | 0.000874 | -0.0207 |  | CFL | Bldg | 4200 | 0.717 | 4180 | 0.713 | 1.14 | 1.23 | -0.0049517 | 4200 | 0.717 | 4180 | 0.713 | 1.14 | 1.23 | -0.00495
CFLBldgSDGHspExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Hsp | Ex | CZ08 | 4.1996 | 0.00071684 | 0 | 4.8292 | 0.0008848 | -0.022196 | 4.1804 | 0.000713 | 0 | 4.81 | 0.00088 | -0.0221 |  | CFL | Bldg | 4200 | 0.717 | 4180 | 0.713 | 1.15 | 1.23 | -0.0052866 | 4200 | 0.717 | 4180 | 0.713 | 1.15 | 1.23 | -0.00529
CFLBldgSDGHspExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Hsp | Ex | CZ10 | 4.1996 | 0.00071684 | 0 | 4.8192 | 0.0009068 | -0.023696 | 4.1804 | 0.000713 | 0 | 4.8 | 0.00090104 | -0.0236 |  | CFL | Bldg | 4200 | 0.717 | 4180 | 0.713 | 1.15 | 1.26 | -0.0056454 | 4200 | 0.717 | 4180 | 0.713 | 1.15 | 1.26 | -0.00565
CFLBldgSDGHspExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Hsp | Ex | CZ14 | 4.1995 | 0.00071679 | 0 | 4.759 | 0.00090074 | -0.029095 | 4.1805 | 0.000713 | 0 | 4.74 | 0.000896 | -0.029 |  | CFL | Bldg | 4200 | 0.717 | 4180 | 0.713 | 1.13 | 1.26 | -0.0069369 | 4200 | 0.717 | 4180 | 0.713 | 1.13 | 1.26 | -0.00694
CFLBldgSDGHspExIOU | Com-Iltg-dWatt-CFL_OSbldg | SDG | Hsp | Ex | IOU | 4.1996 | 0.00071684 | 0 | 4.8033 | 0.00088321 | -0.021239 | 4.1804 | 0.000713 | 0 | 4.7841 | 0.00087825 | -0.021218 |  | CFL | Bldg | 4200 | 0.717 | 4180 | 0.713 | 1.14 | 1.23 | -0.0050757 | 4200 | 0.717 | 4180 | 0.713 | 1.14 | 1.23 | -0.00508
CFLBldgSDGHspNewCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Hsp | New | CZ06 | 4.19 | 0.000713 | 0 | 4.58 | 0.000852 | -0.0239 | 4.19 | 0.000713 | 0 | 4.58 | 0.000852 | -0.0239 |  | CFL | Bldg | 4190 | 0.713 | 4190 | 0.713 | 1.09 | 1.19 | -0.0057041 | 4190 | 0.713 | 4190 | 0.713 | 1.09 | 1.19 | -0.0057
CFLBldgSDGHspNewCZ07 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Hsp | New | CZ07 | 4.19 | 0.000713 | 0 | 4.6 | 0.000847 | -0.0205 | 4.19 | 0.000713 | 0 | 4.6 | 0.000847 | -0.0205 |  | CFL | Bldg | 4190 | 0.713 | 4190 | 0.713 | 1.1 | 1.19 | -0.0048926 | 4190 | 0.713 | 4190 | 0.713 | 1.1 | 1.19 | -0.00489
CFLBldgSDGHspNewCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Hsp | New | CZ08 | 4.19 | 0.000713 | 0 | 4.62 | 0.000856 | -0.0221 | 4.19 | 0.000713 | 0 | 4.62 | 0.000856 | -0.0221 |  | CFL | Bldg | 4190 | 0.713 | 4190 | 0.713 | 1.1 | 1.2 | -0.0052745 | 4190 | 0.713 | 4190 | 0.713 | 1.1 | 1.2 | -0.00527
CFLBldgSDGHspNewCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Hsp | New | CZ10 | 4.19 | 0.000713 | 0 | 4.62 | 0.000882 | -0.0249 | 4.19 | 0.000713 | 0 | 4.62 | 0.000882 | -0.0249 |  | CFL | Bldg | 4190 | 0.713 | 4190 | 0.713 | 1.1 | 1.24 | -0.0059427 | 4190 | 0.713 | 4190 | 0.713 | 1.1 | 1.24 | -0.00594
CFLBldgSDGHspNewCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Hsp | New | CZ14 | 4.19 | 0.000713 | 0 | 4.56 | 0.000876 | -0.031 | 4.19 | 0.000713 | 0 | 4.56 | 0.000876 | -0.031 |  | CFL | Bldg | 4190 | 0.713 | 4190 | 0.713 | 1.09 | 1.23 | -0.0073986 | 4190 | 0.713 | 4190 | 0.713 | 1.09 | 1.23 | -0.0074
CFLBldgSDGHspNewCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Hsp | New | CZ15 | 4.19 | 0.000713 | 0 | 4.84 | 0.000889 | -0.0201 | 4.19 | 0.000713 | 0 | 4.84 | 0.000889 | -0.0201 |  | CFL | Bldg | 4190 | 0.713 | 4190 | 0.713 | 1.16 | 1.25 | -0.0047971 | 4190 | 0.713 | 4190 | 0.713 | 1.16 | 1.25 | -0.0048
CFLBldgSDGHspNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SDG | Hsp | New | IOU | 4.19 | 0.000713 | 0 | 4.6032 | 0.00085246 | -0.02128 | 4.19 | 0.000713 | 0 | 4.6032 | 0.00085246 | -0.02128 |  | CFL | Bldg | 4190 | 0.713 | 4190 | 0.713 | 1.1 | 1.2 | -0.0050786 | 4190 | 0.713 | 4190 | 0.713 | 1.1 | 1.2 | -0.00508
CFLBldgSDGHtlExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Htl | Ex | CZ06 | 1.6669 | 0.00019859 | 0 | 1.8169 | 0.00024848 | -0.0033838 | 1.649 | 0.000195 | 0 | 1.79 | 0.0002449 | -0.003339 |  | CFL | Bldg | 1670 | 0.199 | 1650 | 0.195 | 1.09 | 1.26 | -0.0020249 | 1670 | 0.199 | 1650 | 0.195 | 1.09 | 1.26 | -0.00202
CFLBldgSDGHtlExCZ07 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Htl | Ex | CZ07 | 1.6669 | 0.00019859 | 0 | 1.8469 | 0.00024648 | -0.0026348 | 1.649 | 0.000195 | 0 | 1.82 | 0.000242 | -0.002599 |  | CFL | Bldg | 1670 | 0.199 | 1650 | 0.195 | 1.1 | 1.24 | -0.0015761 | 1670 | 0.199 | 1650 | 0.195 | 1.1 | 1.24 | -0.00158
CFLBldgSDGHtlExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Htl | Ex | CZ08 | 1.6669 | 0.00019859 | 0 | 1.8369 | 0.00024948 | -0.0030548 | 1.649 | 0.000195 | 0 | 1.81 | 0.0002459 | -0.00301 |  | CFL | Bldg | 1670 | 0.199 | 1650 | 0.195 | 1.1 | 1.26 | -0.0018254 | 1670 | 0.199 | 1650 | 0.195 | 1.1 | 1.26 | -0.00183
CFLBldgSDGHtlExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Htl | Ex | CZ10 | 1.6669 | 0.00019859 | 0 | 1.8159 | 0.00025448 | -0.0035338 | 1.649 | 0.000195 | 0 | 1.789 | 0.00025 | -0.003489 |  | CFL | Bldg | 1670 | 0.199 | 1650 | 0.195 | 1.08 | 1.28 | -0.0021158 | 1670 | 0.199 | 1650 | 0.195 | 1.08 | 1.28 | -0.00212
CFLBldgSDGHtlExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Htl | Ex | CZ14 | 1.6669 | 0.00019859 | 0 | 1.7369 | 0.00025448 | -0.0048217 | 1.649 | 0.000195 | 0 | 1.71 | 0.00025 | -0.00475 |  | CFL | Bldg | 1670 | 0.199 | 1650 | 0.195 | 1.04 | 1.28 | -0.0028806 | 1670 | 0.199 | 1650 | 0.195 | 1.04 | 1.28 | -0.00288
CFLBldgSDGHtlExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Htl | Ex | CZ15 | 1.6669 | 0.00019858 | 0 | 1.9459 | 0.00025638 | -0.0020358 | 1.649 | 0.000195 | 0 | 1.919 | 0.0002519 | -0.002009 |  | CFL | Bldg | 1670 | 0.199 | 1650 | 0.195 | 1.16 | 1.29 | -0.0012183 | 1670 | 0.199 | 1650 | 0.195 | 1.16 | 1.29 | -0.00122
CFLBldgSDGHtlExIOU | Com-Iltg-dWatt-CFL_OSbldg | SDG | Htl | Ex | IOU | 1.6669 | 0.00019859 | 0 | 1.8426 | 0.00024753 | -0.0027708 | 1.649 | 0.000195 | 0 | 1.8157 | 0.0002431 | -0.0027334 |  | CFL | Bldg | 1670 | 0.199 | 1650 | 0.195 | 1.1 | 1.25 | -0.0016577 | 1670 | 0.199 | 1650 | 0.195 | 1.1 | 1.25 | -0.00166
CFLBldgSDGHtlNewCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Htl | New | CZ06 | 1.64 | 0.000195 | 0 | 1.78 | 0.000249 | -0.0031 | 1.64 | 0.000195 | 0 | 1.78 | 0.000249 | -0.0031 |  | CFL | Bldg | 1640 | 0.195 | 1640 | 0.195 | 1.09 | 1.28 | -0.0018902 | 1640 | 0.195 | 1640 | 0.195 | 1.09 | 1.28 | -0.00189
CFLBldgSDGHtlNewCZ07 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Htl | New | CZ07 | 1.64 | 0.000195 | 0 | 1.81 | 0.000245 | -0.00223 | 1.64 | 0.000195 | 0 | 1.81 | 0.000245 | -0.00223 |  | CFL | Bldg | 1640 | 0.195 | 1640 | 0.195 | 1.1 | 1.26 | -0.0013598 | 1640 | 0.195 | 1640 | 0.195 | 1.1 | 1.26 | -0.00136
CFLBldgSDGHtlNewCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Htl | New | CZ08 | 1.64 | 0.000195 | 0 | 1.8 | 0.000251 | -0.00273 | 1.64 | 0.000195 | 0 | 1.8 | 0.000251 | -0.00273 |  | CFL | Bldg | 1640 | 0.195 | 1640 | 0.195 | 1.1 | 1.29 | -0.0016646 | 1640 | 0.195 | 1640 | 0.195 | 1.1 | 1.29 | -0.00166
CFLBldgSDGHtlNewCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Htl | New | CZ10 | 1.64 | 0.000195 | 0 | 1.78 | 0.000263 | -0.00342 | 1.64 | 0.000195 | 0 | 1.78 | 0.000263 | -0.00342 |  | CFL | Bldg | 1640 | 0.195 | 1640 | 0.195 | 1.09 | 1.35 | -0.0020854 | 1640 | 0.195 | 1640 | 0.195 | 1.09 | 1.35 | -0.00209
CFLBldgSDGHtlNewCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Htl | New | CZ14 | 1.64 | 0.000195 | 0 | 1.68 | 0.000258 | -0.00512 | 1.64 | 0.000195 | 0 | 1.68 | 0.000258 | -0.00512 |  | CFL | Bldg | 1640 | 0.195 | 1640 | 0.195 | 1.02 | 1.32 | -0.003122 | 1640 | 0.195 | 1640 | 0.195 | 1.02 | 1.32 | -0.00312
CFLBldgSDGHtlNewCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Htl | New | CZ15 | 1.64 | 0.000195 | 0 | 1.92 | 0.000262 | -0.00172 | 1.64 | 0.000195 | 0 | 1.92 | 0.000262 | -0.00172 |  | CFL | Bldg | 1640 | 0.195 | 1640 | 0.195 | 1.17 | 1.34 | -0.0010488 | 1640 | 0.195 | 1640 | 0.195 | 1.17 | 1.34 | -0.00105
CFLBldgSDGHtlNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SDG | Htl | New | IOU | 1.64 | 0.000195 | 0 | 1.8057 | 0.00024723 | -0.0024073 | 1.64 | 0.000195 | 0 | 1.8057 | 0.00024723 | -0.0024073 |  | CFL | Bldg | 1640 | 0.195 | 1640 | 0.195 | 1.1 | 1.27 | -0.0014678 | 1640 | 0.195 | 1640 | 0.195 | 1.1 | 1.27 | -0.00147
CFLBldgSDGMBTExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SDG | MBT | Ex | CZ06 | 3.0854 | 0.00077861 | 0 | 3.5745 | 0.00093634 | -0.00057017 | 3.04 | 0.000765 | 0 | 3.52 | 0.00092 | -0.000562 |  | CFL | Bldg | 3090 | 0.779 | 3040 | 0.765 | 1.16 | 1.2 | -0.00018487 | 3090 | 0.779 | 3040 | 0.765 | 1.16 | 1.2 | -0.000185
CFLBldgSDGMBTExCZ07 | Com-Iltg-dWatt-CFL_OSbldg | SDG | MBT | Ex | CZ07 | 3.0854 | 0.00077861 | 0 | 3.5845 | 0.00092534 | -0.00015472 | 3.04 | 0.000765 | 0 | 3.53 | 0.000909 | -0.00015291 |  | CFL | Bldg | 3090 | 0.779 | 3040 | 0.765 | 1.16 | 1.19 | -5.0299e-05 | 3090 | 0.779 | 3040 | 0.765 | 1.16 | 1.19 | -5.03e-05
CFLBldgSDGMBTExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SDG | MBT | Ex | CZ08 | 3.0854 | 0.00077861 | 0 | 3.5845 | 0.00097724 | -0.00037044 | 3.04 | 0.000765 | 0 | 3.53 | 0.00096 | -0.000365 |  | CFL | Bldg | 3090 | 0.779 | 3040 | 0.765 | 1.16 | 1.25 | -0.00012007 | 3090 | 0.779 | 3040 | 0.765 | 1.16 | 1.25 | -0.00012
CFLBldgSDGMBTExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SDG | MBT | Ex | CZ10 | 3.0854 | 0.00077861 | 0 | 3.5645 | 0.00099724 | -0.00099852 | 3.04 | 0.000765 | 0 | 3.51 | 0.00098 | -0.000984 |  | CFL | Bldg | 3090 | 0.779 | 3040 | 0.765 | 1.15 | 1.28 | -0.00032368 | 3090 | 0.779 | 3040 | 0.765 | 1.15 | 1.28 | -0.000324
CFLBldgSDGMBTExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SDG | MBT | Ex | CZ14 | 3.0854 | 0.00077861 | 0 | 3.5145 | 0.00098924 | -0.0023863 | 3.04 | 0.000765 | 0 | 3.46 | 0.000972 | -0.00235 |  | CFL | Bldg | 3090 | 0.779 | 3040 | 0.765 | 1.14 | 1.27 | -0.00077303 | 3090 | 0.779 | 3040 | 0.765 | 1.14 | 1.27 | -0.000773
CFLBldgSDGMBTExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SDG | MBT | Ex | CZ15 | 3.0854 | 0.00077861 | 0 | 3.7135 | 0.00099834 | 0 | 3.04 | 0.000765 | 0 | 3.65 | 0.000982 | 0 |  | CFL | Bldg | 3090 | 0.779 | 3040 | 0.765 | 1.2 | 1.28 | 0 | 3090 | 0.779 | 3040 | 0.765 | 1.2 | 1.28 | 0
CFLBldgSDGMBTExIOU | Com-Iltg-dWatt-CFL_OSbldg | SDG | MBT | Ex | IOU | 3.0854 | 0.00077861 | 0 | 3.5778 | 0.00094938 | -0.00044931 | 3.04 | 0.000765 | 0 | 3.5233 | 0.00093274 | -0.00044304 |  | CFL | Bldg | 3090 | 0.779 | 3040 | 0.765 | 1.16 | 1.22 | -0.00014574 | 3090 | 0.779 | 3040 | 0.765 | 1.16 | 1.22 | -0.000146
CFLBldgSDGMBTNewCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SDG | MBT | New | CZ06 | 3.04 | 0.000765 | 0 | 3.41 | 0.000957 | -0.00103 | 3.04 | 0.000765 | 0 | 3.41 | 0.000957 | -0.00103 |  | CFL | Bldg | 3040 | 0.765 | 3040 | 0.765 | 1.12 | 1.25 | -0.00033882 | 3040 | 0.765 | 3040 | 0.765 | 1.12 | 1.25 | -0.000339
CFLBldgSDGMBTNewCZ07 | Com-Iltg-dWatt-CFL_OSbldg | SDG | MBT | New | CZ07 | 3.04 | 0.000765 | 0 | 3.39 | 0.000949 | 0 | 3.04 | 0.000765 | 0 | 3.39 | 0.000949 | 0 |  | CFL | Bldg | 3040 | 0.765 | 3040 | 0.765 | 1.12 | 1.24 | 0 | 3040 | 0.765 | 3040 | 0.765 | 1.12 | 1.24 | 0
CFLBldgSDGMBTNewCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SDG | MBT | New | CZ08 | 3.04 | 0.000765 | 0 | 3.42 | 0.000982 | -0.000823 | 3.04 | 0.000765 | 0 | 3.42 | 0.000982 | -0.000823 |  | CFL | Bldg | 3040 | 0.765 | 3040 | 0.765 | 1.13 | 1.28 | -0.00027072 | 3040 | 0.765 | 3040 | 0.765 | 1.13 | 1.28 | -0.000271
CFLBldgSDGMBTNewCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SDG | MBT | New | CZ10 | 3.04 | 0.000765 | 0 | 3.44 | 0.00102 | -0.00102 | 3.04 | 0.000765 | 0 | 3.44 | 0.00102 | -0.00102 |  | CFL | Bldg | 3040 | 0.765 | 3040 | 0.765 | 1.13 | 1.33 | -0.00033553 | 3040 | 0.765 | 3040 | 0.765 | 1.13 | 1.33 | -0.000336
CFLBldgSDGMBTNewCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SDG | MBT | New | CZ14 | 3.04 | 0.000765 | 0 | 3.4 | 0.00101 | -0.00198 | 3.04 | 0.000765 | 0 | 3.4 | 0.00101 | -0.00198 |  | CFL | Bldg | 3040 | 0.765 | 3040 | 0.765 | 1.12 | 1.32 | -0.00065132 | 3040 | 0.765 | 3040 | 0.765 | 1.12 | 1.32 | -0.000651
CFLBldgSDGMBTNewCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SDG | MBT | New | CZ15 | 3.04 | 0.000765 | 0 | 3.62 | 0.00102 | 0 | 3.04 | 0.000765 | 0 | 3.62 | 0.00102 | 0 |  | CFL | Bldg | 3040 | 0.765 | 3040 | 0.765 | 1.19 | 1.33 | 0 | 3040 | 0.765 | 3040 | 0.765 | 1.19 | 1.33 | 0
CFLBldgSDGMBTNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SDG | MBT | New | IOU | 3.04 | 0.000765 | 0 | 3.4072 | 0.00097226 | -0.00037838 | 3.04 | 0.000765 | 0 | 3.4072 | 0.00097226 | -0.00037838 |  | CFL | Bldg | 3040 | 0.765 | 3040 | 0.765 | 1.12 | 1.27 | -0.00012447 | 3040 | 0.765 | 3040 | 0.765 | 1.12 | 1.27 | -0.000124
CFLBldgSDGMLIExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SDG | MLI | Ex | CZ06 | 2.58 | 0.00077681 | 0 | 2.79 | 0.00092181 | -0.0055491 | 2.58 | 0.00077591 | 0 | 2.79 | 0.00092091 | -0.00554 |  | CFL | Bldg | 2580 | 0.777 | 2580 | 0.776 | 1.08 | 1.19 | -0.0021473 | 2580 | 0.777 | 2580 | 0.776 | 1.08 | 1.19 | -0.00215
CFLBldgSDGMLIExCZ07 | Com-Iltg-dWatt-CFL_OSbldg | SDG | MLI | Ex | CZ07 | 2.58 | 0.00077681 | 0 | 2.79 | 0.00091981 | -0.00286 | 2.58 | 0.00077591 | 0 | 2.79 | 0.000918 | -0.00286 |  | CFL | Bldg | 2580 | 0.777 | 2580 | 0.776 | 1.08 | 1.18 | -0.0011085 | 2580 | 0.777 | 2580 | 0.776 | 1.08 | 1.18 | -0.00111
CFLBldgSDGMLIExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SDG | MLI | Ex | CZ08 | 2.58 | 0.00077681 | 0 | 2.82 | 0.00092081 | -0.0045691 | 2.58 | 0.00077591 | 0 | 2.82 | 0.000919 | -0.00456 |  | CFL | Bldg | 2580 | 0.777 | 2580 | 0.776 | 1.09 | 1.18 | -0.0017674 | 2580 | 0.777 | 2580 | 0.776 | 1.09 | 1.18 | -0.00177
CFLBldgSDGMLIExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SDG | MLI | Ex | CZ10 | 2.58 | 0.00077681 | 0 | 2.81 | 0.00094381 | -0.0062191 | 2.58 | 0.00077591 | 0 | 2.81 | 0.000942 | -0.00621 |  | CFL | Bldg | 2580 | 0.777 | 2580 | 0.776 | 1.09 | 1.21 | -0.002407 | 2580 | 0.777 | 2580 | 0.776 | 1.09 | 1.21 | -0.00241
CFLBldgSDGMLIExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SDG | MLI | Ex | CZ14 | 2.58 | 0.00077681 | 0 | 2.73 | 0.00093282 | -0.0172 | 2.58 | 0.00077591 | 0 | 2.73 | 0.000931 | -0.0172 |  | CFL | Bldg | 2580 | 0.777 | 2580 | 0.776 | 1.06 | 1.2 | -0.0066667 | 2580 | 0.777 | 2580 | 0.776 | 1.06 | 1.2 | -0.00667
CFLBldgSDGMLIExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SDG | MLI | Ex | CZ15 | 2.58 | 0.00077681 | 0 | 3.02 | 0.00093182 | -0.0016291 | 2.58 | 0.00077591 | 0 | 3.02 | 0.00093 | -0.00162 |  | CFL | Bldg | 2580 | 0.777 | 2580 | 0.776 | 1.17 | 1.2 | -0.00062791 | 2580 | 0.777 | 2580 | 0.776 | 1.17 | 1.2 | -0.000628
CFLBldgSDGMLIExIOU | Com-Iltg-dWatt-CFL_OSbldg | SDG | MLI | Ex | IOU | 2.58 | 0.00077681 | 0 | 2.7968 | 0.00092734 | -0.0041334 | 2.58 | 0.00077591 | 0 | 2.7968 | 0.00092556 | -0.0041302 |  | CFL | Bldg | 2580 | 0.777 | 2580 | 0.776 | 1.08 | 1.19 | -0.0016008 | 2580 | 0.777 | 2580 | 0.776 | 1.08 | 1.19 | -0.0016
CFLBldgSDGMLINewCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SDG | MLI | New | CZ06 | 2.58 | 0.000775 | 0 | 2.71 | 0.00091 | -0.01 | 2.58 | 0.000775 | 0 | 2.71 | 0.00091 | -0.01 |  | CFL | Bldg | 2580 | 0.775 | 2580 | 0.775 | 1.05 | 1.17 | -0.003876 | 2580 | 0.775 | 2580 | 0.775 | 1.05 | 1.17 | -0.00388
CFLBldgSDGMLINewCZ07 | Com-Iltg-dWatt-CFL_OSbldg | SDG | MLI | New | CZ07 | 2.58 | 0.000775 | 0 | 2.69 | 0.000908 | -0.00583 | 2.58 | 0.000775 | 0 | 2.69 | 0.000908 | -0.00583 |  | CFL | Bldg | 2580 | 0.775 | 2580 | 0.775 | 1.04 | 1.17 | -0.0022597 | 2580 | 0.775 | 2580 | 0.775 | 1.04 | 1.17 | -0.00226
CFLBldgSDGMLINewCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SDG | MLI | New | CZ08 | 2.58 | 0.000775 | 0 | 2.76 | 0.000916 | -0.00804 | 2.58 | 0.000775 | 0 | 2.76 | 0.000916 | -0.00804 |  | CFL | Bldg | 2580 | 0.775 | 2580 | 0.775 | 1.07 | 1.18 | -0.0031163 | 2580 | 0.775 | 2580 | 0.775 | 1.07 | 1.18 | -0.00312
CFLBldgSDGMLINewCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SDG | MLI | New | CZ10 | 2.58 | 0.000775 | 0 | 2.85 | 0.00102 | -0.0101 | 2.58 | 0.000775 | 0 | 2.85 | 0.00102 | -0.0101 |  | CFL | Bldg | 2580 | 0.775 | 2580 | 0.775 | 1.1 | 1.32 | -0.0039147 | 2580 | 0.775 | 2580 | 0.775 | 1.1 | 1.32 | -0.00391
CFLBldgSDGMLINewCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SDG | MLI | New | CZ14 | 2.58 | 0.000775 | 0 | 2.73 | 0.000953 | -0.0199 | 2.58 | 0.000775 | 0 | 2.73 | 0.000953 | -0.0199 |  | CFL | Bldg | 2580 | 0.775 | 2580 | 0.775 | 1.06 | 1.23 | -0.0077132 | 2580 | 0.775 | 2580 | 0.775 | 1.06 | 1.23 | -0.00771
CFLBldgSDGMLINewCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SDG | MLI | New | CZ15 | 2.58 | 0.000775 | 0 | 3.04 | 0.00104 | -0.00169 | 2.58 | 0.000775 | 0 | 3.04 | 0.00104 | -0.00169 |  | CFL | Bldg | 2580 | 0.775 | 2580 | 0.775 | 1.18 | 1.34 | -0.00065504 | 2580 | 0.775 | 2580 | 0.775 | 1.18 | 1.34 | -0.000655
CFLBldgSDGMLINewIOU | Com-Iltg-dWatt-CFL_OSbldg | SDG | MLI | New | IOU | 2.58 | 0.000775 | 0 | 2.7421 | 0.00094304 | -0.0074268 | 2.58 | 0.000775 | 0 | 2.7421 | 0.00094304 | -0.0074268 |  | CFL | Bldg | 2580 | 0.775 | 2580 | 0.775 | 1.06 | 1.22 | -0.0028786 | 2580 | 0.775 | 2580 | 0.775 | 1.06 | 1.22 | -0.00288
CFLBldgSDGMtlExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Mtl | Ex | CZ06 | 1.3659 | 0.00015048 | 0 | 1.5459 | 0.00018928 | -0.0036297 | 1.33 | 0.000146 | 0 | 1.51 | 0.000183 | -0.00354 |  | CFL | Bldg | 1370 | 0.15 | 1330 | 0.146 | 1.14 | 1.25 | -0.0026617 | 1370 | 0.15 | 1330 | 0.146 | 1.14 | 1.25 | -0.00266
CFLBldgSDGMtlExCZ07 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Mtl | Ex | CZ07 | 1.3659 | 0.00015048 | 0 | 1.5759 | 0.00018738 | -0.0025828 | 1.33 | 0.000146 | 0 | 1.54 | 0.000182 | -0.00252 |  | CFL | Bldg | 1370 | 0.15 | 1330 | 0.146 | 1.16 | 1.25 | -0.0018947 | 1370 | 0.15 | 1330 | 0.146 | 1.16 | 1.25 | -0.00189
CFLBldgSDGMtlExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Mtl | Ex | CZ08 | 1.3659 | 0.00015048 | 0 | 1.5659 | 0.00019138 | -0.0030317 | 1.33 | 0.000146 | 0 | 1.53 | 0.0001851 | -0.00296 |  | CFL | Bldg | 1370 | 0.15 | 1330 | 0.146 | 1.15 | 1.27 | -0.0022256 | 1370 | 0.15 | 1330 | 0.146 | 1.15 | 1.27 | -0.00223
CFLBldgSDGMtlExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Mtl | Ex | CZ10 | 1.3659 | 0.00015048 | 0 | 1.5548 | 0.00019638 | -0.0036197 | 1.33 | 0.000146 | 0 | 1.51 | 0.000191 | -0.00353 |  | CFL | Bldg | 1370 | 0.15 | 1330 | 0.146 | 1.14 | 1.31 | -0.0026541 | 1370 | 0.15 | 1330 | 0.146 | 1.14 | 1.31 | -0.00265
CFLBldgSDGMtlExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Mtl | Ex | CZ14 | 1.3659 | 0.00015048 | 0 | 1.5059 | 0.00019638 | -0.0050955 | 1.33 | 0.000146 | 0 | 1.47 | 0.000191 | -0.00497 |  | CFL | Bldg | 1370 | 0.15 | 1330 | 0.146 | 1.11 | 1.31 | -0.0037368 | 1370 | 0.15 | 1330 | 0.146 | 1.11 | 1.31 | -0.00374
CFLBldgSDGMtlExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Mtl | Ex | CZ15 | 1.3658 | 0.00015048 | 0 | 1.6448 | 0.00019938 | -0.0014759 | 1.33 | 0.000146 | 0 | 1.6 | 0.000194 | -0.00144 |  | CFL | Bldg | 1370 | 0.15 | 1330 | 0.146 | 1.2 | 1.33 | -0.0010827 | 1370 | 0.15 | 1330 | 0.146 | 1.2 | 1.33 | -0.00108
CFLBldgSDGMtlExIOU | Com-Iltg-dWatt-CFL_OSbldg | SDG | Mtl | Ex | IOU | 1.3659 | 0.00015048 | 0 | 1.5725 | 0.00018856 | -0.0027435 | 1.33 | 0.000146 | 0 | 1.5357 | 0.00018313 | -0.0026766 |  | CFL | Bldg | 1370 | 0.15 | 1330 | 0.146 | 1.15 | 1.25 | -0.0020125 | 1370 | 0.15 | 1330 | 0.146 | 1.15 | 1.25 | -0.00201
CFLBldgSDGMtlNewCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Mtl | New | CZ06 | 1.33 | 0.000146 | 0 | 1.5 | 0.000188 | -0.00466 | 1.33 | 0.000146 | 0 | 1.5 | 0.000188 | -0.00466 |  | CFL | Bldg | 1330 | 0.146 | 1330 | 0.146 | 1.13 | 1.29 | -0.0035038 | 1330 | 0.146 | 1330 | 0.146 | 1.13 | 1.29 | -0.0035
CFLBldgSDGMtlNewCZ07 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Mtl | New | CZ07 | 1.33 | 0.000146 | 0 | 1.53 | 0.000185 | -0.00321 | 1.33 | 0.000146 | 0 | 1.53 | 0.000185 | -0.00321 |  | CFL | Bldg | 1330 | 0.146 | 1330 | 0.146 | 1.15 | 1.27 | -0.0024135 | 1330 | 0.146 | 1330 | 0.146 | 1.15 | 1.27 | -0.00241
CFLBldgSDGMtlNewCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Mtl | New | CZ08 | 1.33 | 0.000146 | 0 | 1.52 | 0.00019 | -0.00389 | 1.33 | 0.000146 | 0 | 1.52 | 0.00019 | -0.00389 |  | CFL | Bldg | 1330 | 0.146 | 1330 | 0.146 | 1.14 | 1.3 | -0.0029248 | 1330 | 0.146 | 1330 | 0.146 | 1.14 | 1.3 | -0.00292
CFLBldgSDGMtlNewCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Mtl | New | CZ10 | 1.33 | 0.000146 | 0 | 1.5 | 0.000196 | -0.00488 | 1.33 | 0.000146 | 0 | 1.5 | 0.000196 | -0.00488 |  | CFL | Bldg | 1330 | 0.146 | 1330 | 0.146 | 1.13 | 1.34 | -0.0036692 | 1330 | 0.146 | 1330 | 0.146 | 1.13 | 1.34 | -0.00367
CFLBldgSDGMtlNewCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Mtl | New | CZ14 | 1.33 | 0.000146 | 0 | 1.44 | 0.000196 | -0.00653 | 1.33 | 0.000146 | 0 | 1.44 | 0.000196 | -0.00653 |  | CFL | Bldg | 1330 | 0.146 | 1330 | 0.146 | 1.08 | 1.34 | -0.0049098 | 1330 | 0.146 | 1330 | 0.146 | 1.08 | 1.34 | -0.00491
CFLBldgSDGMtlNewCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Mtl | New | CZ15 | 1.33 | 0.000146 | 0 | 1.61 | 0.0002 | -0.00224 | 1.33 | 0.000146 | 0 | 1.61 | 0.0002 | -0.00224 |  | CFL | Bldg | 1330 | 0.146 | 1330 | 0.146 | 1.21 | 1.37 | -0.0016842 | 1330 | 0.146 | 1330 | 0.146 | 1.21 | 1.37 | -0.00168
CFLBldgSDGMtlNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SDG | Mtl | New | IOU | 1.33 | 0.000146 | 0 | 1.5258 | 0.00018647 | -0.0034599 | 1.33 | 0.000146 | 0 | 1.5258 | 0.00018647 | -0.0034599 |  | CFL | Bldg | 1330 | 0.146 | 1330 | 0.146 | 1.15 | 1.28 | -0.0026014 | 1330 | 0.146 | 1330 | 0.146 | 1.15 | 1.28 | -0.0026
CFLBldgSDGNrsExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Nrs | Ex | CZ06 | 3.5684 | 0.00056464 | 0 | 3.848 | 0.00072852 | -0.03388 | 3.5204 | 0.00055504 | 0 | 3.8 | 0.00071604 | -0.0334 |  | CFL | Bldg | 3570 | 0.565 | 3520 | 0.555 | 1.08 | 1.29 | -0.0094876 | 3570 | 0.565 | 3520 | 0.555 | 1.08 | 1.29 | -0.00949
CFLBldgSDGNrsExCZ07 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Nrs | Ex | CZ07 | 3.5684 | 0.00056464 | 0 | 3.848 | 0.00071556 | -0.029984 | 3.5204 | 0.00055504 | 0 | 3.7904 | 0.00070404 | -0.0296 |  | CFL | Bldg | 3570 | 0.565 | 3520 | 0.555 | 1.08 | 1.27 | -0.0084081 | 3570 | 0.565 | 3520 | 0.555 | 1.08 | 1.27 | -0.00841
CFLBldgSDGNrsExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Nrs | Ex | CZ08 | 3.5684 | 0.00056464 | 0 | 3.888 | 0.00073152 | -0.032584 | 3.5204 | 0.00055504 | 0 | 3.84 | 0.00071904 | -0.0322 |  | CFL | Bldg | 3570 | 0.565 | 3520 | 0.555 | 1.09 | 1.3 | -0.0091467 | 3570 | 0.565 | 3520 | 0.555 | 1.09 | 1.3 | -0.00915
CFLBldgSDGNrsExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Nrs | Ex | CZ10 | 3.5684 | 0.00056464 | 0 | 3.908 | 0.00075452 | -0.034784 | 3.5204 | 0.00055504 | 0 | 3.8504 | 0.00074204 | -0.034304 |  | CFL | Bldg | 3570 | 0.565 | 3520 | 0.555 | 1.09 | 1.34 | -0.0097443 | 3570 | 0.565 | 3520 | 0.555 | 1.09 | 1.34 | -0.00974
CFLBldgSDGNrsExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Nrs | Ex | CZ14 | 3.5679 | 0.00056453 | 0 | 3.8574 | 0.00074638 | -0.040674 | 3.5205 | 0.00055505 | 0 | 3.81 | 0.00073405 | -0.0402 |  | CFL | Bldg | 3570 | 0.565 | 3520 | 0.555 | 1.08 | 1.32 | -0.011419 | 3570 | 0.565 | 3520 | 0.555 | 1.08 | 1.32 | -0.0114
CFLBldgSDGNrsExIOU | Com-Iltg-dWatt-CFL_OSbldg | SDG | Nrs | Ex | IOU | 3.5684 | 0.00056464 | 0 | 3.8582 | 0.00072207 | -0.030875 | 3.5204 | 0.00055504 | 0 | 3.8013 | 0.00071035 | -0.030475 |  | CFL | Bldg | 3570 | 0.565 | 3520 | 0.555 | 1.08 | 1.28 | -0.0086568 | 3570 | 0.565 | 3520 | 0.555 | 1.08 | 1.28 | -0.00866
CFLBldgSDGNrsNewCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Nrs | New | CZ06 | 3.53 | 0.000556 | 0 | 3.67 | 0.000706 | -0.0356 | 3.53 | 0.000556 | 0 | 3.67 | 0.000706 | -0.0356 |  | CFL | Bldg | 3530 | 0.556 | 3530 | 0.556 | 1.04 | 1.27 | -0.010085 | 3530 | 0.556 | 3530 | 0.556 | 1.04 | 1.27 | -0.0101
CFLBldgSDGNrsNewCZ07 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Nrs | New | CZ07 | 3.53 | 0.000556 | 0 | 3.65 | 0.000706 | -0.0332 | 3.53 | 0.000556 | 0 | 3.65 | 0.000706 | -0.0332 |  | CFL | Bldg | 3530 | 0.556 | 3530 | 0.556 | 1.03 | 1.27 | -0.0094051 | 3530 | 0.556 | 3530 | 0.556 | 1.03 | 1.27 | -0.00941
CFLBldgSDGNrsNewCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Nrs | New | CZ08 | 3.53 | 0.000556 | 0 | 3.73 | 0.000709 | -0.034 | 3.53 | 0.000556 | 0 | 3.73 | 0.000709 | -0.034 |  | CFL | Bldg | 3530 | 0.556 | 3530 | 0.556 | 1.06 | 1.28 | -0.0096317 | 3530 | 0.556 | 3530 | 0.556 | 1.06 | 1.28 | -0.00963
CFLBldgSDGNrsNewCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Nrs | New | CZ10 | 3.53 | 0.000556 | 0 | 3.77 | 0.000738 | -0.0349 | 3.53 | 0.000556 | 0 | 3.77 | 0.000738 | -0.0349 |  | CFL | Bldg | 3530 | 0.556 | 3530 | 0.556 | 1.07 | 1.33 | -0.0098867 | 3530 | 0.556 | 3530 | 0.556 | 1.07 | 1.33 | -0.00989
CFLBldgSDGNrsNewCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Nrs | New | CZ14 | 3.53 | 0.000556 | 0 | 3.74 | 0.000716 | -0.043 | 3.53 | 0.000556 | 0 | 3.74 | 0.000716 | -0.043 |  | CFL | Bldg | 3530 | 0.556 | 3530 | 0.556 | 1.06 | 1.29 | -0.012181 | 3530 | 0.556 | 3530 | 0.556 | 1.06 | 1.29 | -0.0122
CFLBldgSDGNrsNewCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Nrs | New | CZ15 | 3.53 | 0.000556 | 0 | 4.05 | 0.000736 | -0.0167 | 3.53 | 0.000556 | 0 | 4.05 | 0.000736 | -0.0167 |  | CFL | Bldg | 3530 | 0.556 | 3530 | 0.556 | 1.15 | 1.32 | -0.0047309 | 3530 | 0.556 | 3530 | 0.556 | 1.15 | 1.32 | -0.00473
CFLBldgSDGNrsNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SDG | Nrs | New | IOU | 3.53 | 0.000556 | 0 | 3.671 | 0.00071063 | -0.03354 | 3.53 | 0.000556 | 0 | 3.671 | 0.00071063 | -0.03354 |  | CFL | Bldg | 3530 | 0.556 | 3530 | 0.556 | 1.04 | 1.28 | -0.0095014 | 3530 | 0.556 | 3530 | 0.556 | 1.04 | 1.28 | -0.0095
CFLBldgSDGOfLExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SDG | OfL | Ex | CZ06 | 2.9935 | 0.00062322 | 0 | 3.4324 | 0.00079473 | -0.0071749 | 2.88 | 0.00059295 | 0 | 3.3095 | 0.00075595 | -0.0069195 |  | CFL | Bldg | 2990 | 0.623 | 2880 | 0.593 | 1.15 | 1.27 | -0.0024026 | 2990 | 0.623 | 2880 | 0.593 | 1.15 | 1.27 | -0.0024
CFLBldgSDGOfLExCZ07 | Com-Iltg-dWatt-CFL_OSbldg | SDG | OfL | Ex | CZ07 | 2.9935 | 0.00062322 | 0 | 3.423 | 0.00078373 | -0.006157 | 2.88 | 0.00059295 | 0 | 3.3 | 0.00074589 | -0.0059395 |  | CFL | Bldg | 2990 | 0.623 | 2880 | 0.593 | 1.15 | 1.26 | -0.0020623 | 2990 | 0.623 | 2880 | 0.593 | 1.15 | 1.26 | -0.00206
CFLBldgSDGOfLExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SDG | OfL | Ex | CZ08 | 2.9935 | 0.00062322 | 0 | 3.443 | 0.00081068 | -0.0069654 | 2.88 | 0.00059295 | 0 | 3.32 | 0.00077095 | -0.0067195 |  | CFL | Bldg | 2990 | 0.623 | 2880 | 0.593 | 1.15 | 1.3 | -0.0023331 | 2990 | 0.623 | 2880 | 0.593 | 1.15 | 1.3 | -0.00233
CFLBldgSDGOfLExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SDG | OfL | Ex | CZ10 | 2.9935 | 0.00062322 | 0 | 3.4424 | 0.00081763 | -0.0079533 | 2.88 | 0.00059295 | 0 | 3.3195 | 0.00077789 | -0.0076695 |  | CFL | Bldg | 2990 | 0.623 | 2880 | 0.593 | 1.15 | 1.31 | -0.002663 | 2990 | 0.623 | 2880 | 0.593 | 1.15 | 1.31 | -0.00266
CFLBldgSDGOfLExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SDG | OfL | Ex | CZ14 | 2.9935 | 0.00062322 | 0 | 3.3925 | 0.00080468 | -0.010978 | 2.88 | 0.00059295 | 0 | 3.2695 | 0.00076495 | -0.0106 |  | CFL | Bldg | 2990 | 0.623 | 2880 | 0.593 | 1.14 | 1.29 | -0.0036806 | 2990 | 0.623 | 2880 | 0.593 | 1.14 | 1.29 | -0.00368
CFLBldgSDGOfLExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SDG | OfL | Ex | CZ15 | 2.9935 | 0.00062321 | 0 | 3.6424 | 0.00082061 | -0.0046097 | 2.88 | 0.00059295 | 0 | 3.51 | 0.00078089 | -0.0044395 |  | CFL | Bldg | 2990 | 0.623 | 2880 | 0.593 | 1.22 | 1.32 | -0.0015415 | 2990 | 0.623 | 2880 | 0.593 | 1.22 | 1.32 | -0.00154
CFLBldgSDGOfLExIOU | Com-Iltg-dWatt-CFL_OSbldg | SDG | OfL | Ex | IOU | 2.9935 | 0.00062322 | 0 | 3.4271 | 0.00079053 | -0.0065253 | 2.88 | 0.00059295 | 0 | 3.3041 | 0.00075229 | -0.0062942 |  | CFL | Bldg | 2990 | 0.623 | 2880 | 0.593 | 1.15 | 1.27 | -0.0021855 | 2990 | 0.623 | 2880 | 0.593 | 1.15 | 1.27 | -0.00219
CFLBldgSDGOfLNewCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SDG | OfL | New | CZ06 | 2.88 | 0.000592 | 0 | 3.3 | 0.000737 | -0.00469 | 2.88 | 0.000592 | 0 | 3.3 | 0.000737 | -0.00469 |  | CFL | Bldg | 2880 | 0.592 | 2880 | 0.592 | 1.15 | 1.24 | -0.0016285 | 2880 | 0.592 | 2880 | 0.592 | 1.15 | 1.24 | -0.00163
CFLBldgSDGOfLNewCZ07 | Com-Iltg-dWatt-CFL_OSbldg | SDG | OfL | New | CZ07 | 2.88 | 0.000592 | 0 | 3.3 | 0.000728 | -0.0038 | 2.88 | 0.000592 | 0 | 3.3 | 0.000728 | -0.0038 |  | CFL | Bldg | 2880 | 0.592 | 2880 | 0.592 | 1.15 | 1.23 | -0.0013194 | 2880 | 0.592 | 2880 | 0.592 | 1.15 | 1.23 | -0.00132
CFLBldgSDGOfLNewCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SDG | OfL | New | CZ08 | 2.88 | 0.000592 | 0 | 3.31 | 0.000747 | -0.00389 | 2.88 | 0.000592 | 0 | 3.31 | 0.000747 | -0.00389 |  | CFL | Bldg | 2880 | 0.592 | 2880 | 0.592 | 1.15 | 1.26 | -0.0013507 | 2880 | 0.592 | 2880 | 0.592 | 1.15 | 1.26 | -0.00135
CFLBldgSDGOfLNewCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SDG | OfL | New | CZ10 | 2.88 | 0.000592 | 0 | 3.33 | 0.00077 | -0.00478 | 2.88 | 0.000592 | 0 | 3.33 | 0.00077 | -0.00478 |  | CFL | Bldg | 2880 | 0.592 | 2880 | 0.592 | 1.16 | 1.3 | -0.0016597 | 2880 | 0.592 | 2880 | 0.592 | 1.16 | 1.3 | -0.00166
CFLBldgSDGOfLNewCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SDG | OfL | New | CZ14 | 2.88 | 0.000592 | 0 | 3.27 | 0.000783 | -0.00751 | 2.88 | 0.000592 | 0 | 3.27 | 0.000783 | -0.00751 |  | CFL | Bldg | 2880 | 0.592 | 2880 | 0.592 | 1.14 | 1.32 | -0.0026076 | 2880 | 0.592 | 2880 | 0.592 | 1.14 | 1.32 | -0.00261
CFLBldgSDGOfLNewCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SDG | OfL | New | CZ15 | 2.88 | 0.000592 | 0 | 3.45 | 0.000766 | -0.00226 | 2.88 | 0.000592 | 0 | 3.45 | 0.000766 | -0.00226 |  | CFL | Bldg | 2880 | 0.592 | 2880 | 0.592 | 1.2 | 1.29 | -0.00078472 | 2880 | 0.592 | 2880 | 0.592 | 1.2 | 1.29 | -0.000785
CFLBldgSDGOfLNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SDG | OfL | New | IOU | 2.88 | 0.000592 | 0 | 3.3055 | 0.00073615 | -0.0040046 | 2.88 | 0.000592 | 0 | 3.3055 | 0.00073615 | -0.0040046 |  | CFL | Bldg | 2880 | 0.592 | 2880 | 0.592 | 1.15 | 1.24 | -0.0013905 | 2880 | 0.592 | 2880 | 0.592 | 1.15 | 1.24 | -0.00139
CFLBldgSDGOfSExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SDG | OfS | Ex | CZ06 | 2.9678 | 0.00067411 | 0 | 3.3964 | 0.00084912 | -0.0023906 | 2.72 | 0.00059405 | 0 | 3.1105 | 0.00074809 | -0.0021905 |  | CFL | Bldg | 2970 | 0.674 | 2720 | 0.594 | 1.14 | 1.26 | -0.00080532 | 2970 | 0.674 | 2720 | 0.594 | 1.14 | 1.26 | -0.000805
CFLBldgSDGOfSExCZ07 | Com-Iltg-dWatt-CFL_OSbldg | SDG | OfS | Ex | CZ07 | 2.9678 | 0.00067411 | 0 | 3.4064 | 0.00084013 | -0.00064943 | 2.72 | 0.00059405 | 0 | 3.1205 | 0.00074005 | -0.00059605 |  | CFL | Bldg | 2970 | 0.674 | 2720 | 0.594 | 1.15 | 1.25 | -0.00021913 | 2970 | 0.674 | 2720 | 0.594 | 1.15 | 1.25 | -0.000219
CFLBldgSDGOfSExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SDG | OfS | Ex | CZ08 | 2.9678 | 0.00067412 | 0 | 3.4164 | 0.00085409 | -0.0020221 | 2.72 | 0.00059405 | 0 | 3.1305 | 0.00075209 | -0.00186 |  | CFL | Bldg | 2970 | 0.674 | 2720 | 0.594 | 1.15 | 1.27 | -0.00068382 | 2970 | 0.674 | 2720 | 0.594 | 1.15 | 1.27 | -0.000684
CFLBldgSDGOfSExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SDG | OfS | Ex | CZ10 | 2.9678 | 0.00067411 | 0 | 3.4064 | 0.00085708 | -0.0030874 | 2.72 | 0.00059405 | 0 | 3.1205 | 0.00075509 | -0.00283 |  | CFL | Bldg | 2970 | 0.674 | 2720 | 0.594 | 1.15 | 1.27 | -0.0010404 | 2970 | 0.674 | 2720 | 0.594 | 1.15 | 1.27 | -0.00104
CFLBldgSDGOfSExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SDG | OfS | Ex | CZ14 | 2.9677 | 0.00067407 | 0 | 3.3168 | 0.00086794 | -0.0074997 | 2.72 | 0.00059405 | 0 | 3.0405 | 0.00076409 | -0.0068805 |  | CFL | Bldg | 2970 | 0.674 | 2720 | 0.594 | 1.12 | 1.29 | -0.0025296 | 2970 | 0.674 | 2720 | 0.594 | 1.12 | 1.29 | -0.00253
CFLBldgSDGOfSExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SDG | OfS | Ex | CZ15 | 2.9681 | 0.00067418 | 0 | 3.6358 | 0.00084922 | -0.00064947 | 2.72 | 0.00059405 | 0 | 3.34 | 0.00074809 | -0.00059605 |  | CFL | Bldg | 2970 | 0.674 | 2720 | 0.594 | 1.23 | 1.26 | -0.00021913 | 2970 | 0.674 | 2720 | 0.594 | 1.23 | 1.26 | -0.000219
CFLBldgSDGOfSExIOU | Com-Iltg-dWatt-CFL_OSbldg | SDG | OfS | Ex | IOU | 2.9678 | 0.00067411 | 0 | 3.4063 | 0.00084368 | -0.0011666 | 2.72 | 0.00059405 | 0 | 3.1204 | 0.00074319 | -0.0010701 |  | CFL | Bldg | 2970 | 0.674 | 2720 | 0.594 | 1.15 | 1.25 | -0.00039343 | 2970 | 0.674 | 2720 | 0.594 | 1.15 | 1.25 | -0.000393
CFLBldgSDGOfSNewCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SDG | OfS | New | CZ06 | 2.72 | 0.000595 | 0 | 2.99 | 0.000737 | -0.00242 | 2.72 | 0.000595 | 0 | 2.99 | 0.000737 | -0.00242 |  | CFL | Bldg | 2720 | 0.595 | 2720 | 0.595 | 1.1 | 1.24 | -0.00088971 | 2720 | 0.595 | 2720 | 0.595 | 1.1 | 1.24 | -0.00089
CFLBldgSDGOfSNewCZ07 | Com-Iltg-dWatt-CFL_OSbldg | SDG | OfS | New | CZ07 | 2.72 | 0.000595 | 0 | 2.98 | 0.000728 | -0.000564 | 2.72 | 0.000595 | 0 | 2.98 | 0.000728 | -0.000564 |  | CFL | Bldg | 2720 | 0.595 | 2720 | 0.595 | 1.1 | 1.22 | -0.00020735 | 2720 | 0.595 | 2720 | 0.595 | 1.1 | 1.22 | -0.000207
CFLBldgSDGOfSNewCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SDG | OfS | New | CZ08 | 2.72 | 0.000595 | 0 | 3 | 0.000745 | -0.00204 | 2.72 | 0.000595 | 0 | 3 | 0.000745 | -0.00204 |  | CFL | Bldg | 2720 | 0.595 | 2720 | 0.595 | 1.1 | 1.25 | -0.00075 | 2720 | 0.595 | 2720 | 0.595 | 1.1 | 1.25 | -0.00075
CFLBldgSDGOfSNewCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SDG | OfS | New | CZ10 | 2.72 | 0.000595 | 0 | 3.04 | 0.000772 | -0.00161 | 2.72 | 0.000595 | 0 | 3.04 | 0.000772 | -0.00161 |  | CFL | Bldg | 2720 | 0.595 | 2720 | 0.595 | 1.12 | 1.3 | -0.00059191 | 2720 | 0.595 | 2720 | 0.595 | 1.12 | 1.3 | -0.000592
CFLBldgSDGOfSNewCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SDG | OfS | New | CZ14 | 2.72 | 0.000595 | 0 | 2.96 | 0.000772 | -0.00616 | 2.72 | 0.000595 | 0 | 2.96 | 0.000772 | -0.00616 |  | CFL | Bldg | 2720 | 0.595 | 2720 | 0.595 | 1.09 | 1.3 | -0.0022647 | 2720 | 0.595 | 2720 | 0.595 | 1.09 | 1.3 | -0.00226
CFLBldgSDGOfSNewCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SDG | OfS | New | CZ15 | 2.72 | 0.000595 | 0 | 3.17 | 0.00078 | 0 | 2.72 | 0.000595 | 0 | 3.17 | 0.00078 | 0 |  | CFL | Bldg | 2720 | 0.595 | 2720 | 0.595 | 1.17 | 1.31 | 0 | 2720 | 0.595 | 2720 | 0.595 | 1.17 | 1.31 | 0
CFLBldgSDGOfSNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SDG | OfS | New | IOU | 2.72 | 0.000595 | 0 | 2.9912 | 0.00073642 | -0.0008386 | 2.72 | 0.000595 | 0 | 2.9912 | 0.00073642 | -0.0008386 |  | CFL | Bldg | 2720 | 0.595 | 2720 | 0.595 | 1.1 | 1.24 | -0.00030831 | 2720 | 0.595 | 2720 | 0.595 | 1.1 | 1.24 | -0.000308
CFLBldgSDGRFFExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SDG | RFF | Ex | CZ06 | 4.81 | 0.000808 | 0 | 5.34 | 0.000987 | -0.0258 | 4.81 | 0.000808 | 0 | 5.34 | 0.000987 | -0.0258 |  | CFL | Bldg | 4810 | 0.808 | 4810 | 0.808 | 1.11 | 1.22 | -0.0053638 | 4810 | 0.808 | 4810 | 0.808 | 1.11 | 1.22 | -0.00536
CFLBldgSDGRFFExCZ07 | Com-Iltg-dWatt-CFL_OSbldg | SDG | RFF | Ex | CZ07 | 4.81 | 0.000808 | 0 | 5.35 | 0.000979 | -0.0231 | 4.81 | 0.000808 | 0 | 5.35 | 0.000979 | -0.0231 |  | CFL | Bldg | 4810 | 0.808 | 4810 | 0.808 | 1.11 | 1.21 | -0.0048025 | 4810 | 0.808 | 4810 | 0.808 | 1.11 | 1.21 | -0.0048
CFLBldgSDGRFFExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SDG | RFF | Ex | CZ08 | 4.81 | 0.000808 | 0 | 5.38 | 0.000978 | -0.0226 | 4.81 | 0.000808 | 0 | 5.38 | 0.000978 | -0.0226 |  | CFL | Bldg | 4810 | 0.808 | 4810 | 0.808 | 1.12 | 1.21 | -0.0046985 | 4810 | 0.808 | 4810 | 0.808 | 1.12 | 1.21 | -0.0047
CFLBldgSDGRFFExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SDG | RFF | Ex | CZ10 | 4.81 | 0.000808 | 0 | 5.38 | 0.000995 | -0.0251 | 4.81 | 0.000808 | 0 | 5.38 | 0.000995 | -0.0251 |  | CFL | Bldg | 4810 | 0.808 | 4810 | 0.808 | 1.12 | 1.23 | -0.0052183 | 4810 | 0.808 | 4810 | 0.808 | 1.12 | 1.23 | -0.00522
CFLBldgSDGRFFExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SDG | RFF | Ex | CZ14 | 4.81 | 0.000808 | 0 | 5.29 | 0.00101 | -0.0355 | 4.81 | 0.000808 | 0 | 5.29 | 0.00101 | -0.0355 |  | CFL | Bldg | 4810 | 0.808 | 4810 | 0.808 | 1.1 | 1.25 | -0.0073805 | 4810 | 0.808 | 4810 | 0.808 | 1.1 | 1.25 | -0.00738
CFLBldgSDGRFFExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SDG | RFF | Ex | CZ15 | 4.81 | 0.000808 | 0 | 5.71 | 0.00101 | -0.0117 | 4.81 | 0.000808 | 0 | 5.71 | 0.00101 | -0.0117 |  | CFL | Bldg | 4810 | 0.808 | 4810 | 0.808 | 1.19 | 1.25 | -0.0024324 | 4810 | 0.808 | 4810 | 0.808 | 1.19 | 1.25 | -0.00243
CFLBldgSDGRFFExIOU | Com-Iltg-dWatt-CFL_OSbldg | SDG | RFF | Ex | IOU | 4.81 | 0.000808 | 0 | 5.3573 | 0.00098294 | -0.023662 | 4.81 | 0.000808 | 0 | 5.3573 | 0.00098294 | -0.023662 |  | CFL | Bldg | 4810 | 0.808 | 4810 | 0.808 | 1.11 | 1.22 | -0.0049193 | 4810 | 0.808 | 4810 | 0.808 | 1.11 | 1.22 | -0.00492
CFLBldgSDGRFFNewCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SDG | RFF | New | CZ06 | 4.81 | 0.000808 | 0 | 5.15 | 0.001 | -0.027 | 4.81 | 0.000808 | 0 | 5.15 | 0.001 | -0.027 |  | CFL | Bldg | 4810 | 0.808 | 4810 | 0.808 | 1.07 | 1.24 | -0.0056133 | 4810 | 0.808 | 4810 | 0.808 | 1.07 | 1.24 | -0.00561
CFLBldgSDGRFFNewCZ07 | Com-Iltg-dWatt-CFL_OSbldg | SDG | RFF | New | CZ07 | 4.81 | 0.000808 | 0 | 5.13 | 0.000993 | -0.0286 | 4.81 | 0.000808 | 0 | 5.13 | 0.000993 | -0.0286 |  | CFL | Bldg | 4810 | 0.808 | 4810 | 0.808 | 1.07 | 1.23 | -0.0059459 | 4810 | 0.808 | 4810 | 0.808 | 1.07 | 1.23 | -0.00595
CFLBldgSDGRFFNewCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SDG | RFF | New | CZ08 | 4.81 | 0.000808 | 0 | 5.17 | 0.000972 | -0.0264 | 4.81 | 0.000808 | 0 | 5.17 | 0.000972 | -0.0264 |  | CFL | Bldg | 4810 | 0.808 | 4810 | 0.808 | 1.07 | 1.2 | -0.0054886 | 4810 | 0.808 | 4810 | 0.808 | 1.07 | 1.2 | -0.00549
CFLBldgSDGRFFNewCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SDG | RFF | New | CZ10 | 4.81 | 0.000808 | 0 | 5.29 | 0.00105 | -0.0308 | 4.81 | 0.000808 | 0 | 5.29 | 0.00105 | -0.0308 |  | CFL | Bldg | 4810 | 0.808 | 4810 | 0.808 | 1.1 | 1.3 | -0.0064033 | 4810 | 0.808 | 4810 | 0.808 | 1.1 | 1.3 | -0.0064
CFLBldgSDGRFFNewCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SDG | RFF | New | CZ14 | 4.81 | 0.000808 | 0 | 5.26 | 0.00105 | -0.0429 | 4.81 | 0.000808 | 0 | 5.26 | 0.00105 | -0.0429 |  | CFL | Bldg | 4810 | 0.808 | 4810 | 0.808 | 1.09 | 1.3 | -0.0089189 | 4810 | 0.808 | 4810 | 0.808 | 1.09 | 1.3 | -0.00892
CFLBldgSDGRFFNewCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SDG | RFF | New | CZ15 | 4.81 | 0.000808 | 0 | 5.66 | 0.00107 | -0.0153 | 4.81 | 0.000808 | 0 | 5.66 | 0.00107 | -0.0153 |  | CFL | Bldg | 4810 | 0.808 | 4810 | 0.808 | 1.18 | 1.32 | -0.0031809 | 4810 | 0.808 | 4810 | 0.808 | 1.18 | 1.32 | -0.00318
CFLBldgSDGRFFNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SDG | RFF | New | IOU | 4.81 | 0.000808 | 0 | 5.1681 | 0.0010054 | -0.028958 | 4.81 | 0.000808 | 0 | 5.1681 | 0.0010054 | -0.028958 |  | CFL | Bldg | 4810 | 0.808 | 4810 | 0.808 | 1.07 | 1.24 | -0.0060203 | 4810 | 0.808 | 4810 | 0.808 | 1.07 | 1.24 | -0.00602
CFLBldgSDGRSDExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SDG | RSD | Ex | CZ06 | 4.83 | 0.0008 | 0 | 5.45 | 0.000994 | -0.023 | 4.83 | 0.0008 | 0 | 5.45 | 0.000994 | -0.023 |  | CFL | Bldg | 4830 | 0.8 | 4830 | 0.8 | 1.13 | 1.24 | -0.0047619 | 4830 | 0.8 | 4830 | 0.8 | 1.13 | 1.24 | -0.00476
CFLBldgSDGRSDExCZ07 | Com-Iltg-dWatt-CFL_OSbldg | SDG | RSD | Ex | CZ07 | 4.83 | 0.0008 | 0 | 5.46 | 0.000998 | -0.0201 | 4.83 | 0.0008 | 0 | 5.46 | 0.000998 | -0.0201 |  | CFL | Bldg | 4830 | 0.8 | 4830 | 0.8 | 1.13 | 1.25 | -0.0041615 | 4830 | 0.8 | 4830 | 0.8 | 1.13 | 1.25 | -0.00416
CFLBldgSDGRSDExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SDG | RSD | Ex | CZ08 | 4.83 | 0.0008 | 0 | 5.49 | 0.00097 | -0.0196 | 4.83 | 0.0008 | 0 | 5.49 | 0.00097 | -0.0196 |  | CFL | Bldg | 4830 | 0.8 | 4830 | 0.8 | 1.14 | 1.21 | -0.004058 | 4830 | 0.8 | 4830 | 0.8 | 1.14 | 1.21 | -0.00406
CFLBldgSDGRSDExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SDG | RSD | Ex | CZ10 | 4.83 | 0.0008 | 0 | 5.47 | 0.000958 | -0.0231 | 4.83 | 0.0008 | 0 | 5.47 | 0.000958 | -0.0231 |  | CFL | Bldg | 4830 | 0.8 | 4830 | 0.8 | 1.13 | 1.2 | -0.0047826 | 4830 | 0.8 | 4830 | 0.8 | 1.13 | 1.2 | -0.00478
CFLBldgSDGRSDExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SDG | RSD | Ex | CZ14 | 4.83 | 0.0008 | 0 | 5.34 | 0.00096 | -0.0359 | 4.83 | 0.0008 | 0 | 5.34 | 0.00096 | -0.0359 |  | CFL | Bldg | 4830 | 0.8 | 4830 | 0.8 | 1.11 | 1.2 | -0.0074327 | 4830 | 0.8 | 4830 | 0.8 | 1.11 | 1.2 | -0.00743
CFLBldgSDGRSDExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SDG | RSD | Ex | CZ15 | 4.83 | 0.0008 | 0 | 5.88 | 0.00102 | -0.00854 | 4.83 | 0.0008 | 0 | 5.88 | 0.00102 | -0.00854 |  | CFL | Bldg | 4830 | 0.8 | 4830 | 0.8 | 1.22 | 1.27 | -0.0017681 | 4830 | 0.8 | 4830 | 0.8 | 1.22 | 1.27 | -0.00177
CFLBldgSDGRSDExIOU | Com-Iltg-dWatt-CFL_OSbldg | SDG | RSD | Ex | IOU | 4.83 | 0.0008 | 0 | 5.4628 | 0.00098812 | -0.020897 | 4.83 | 0.0008 | 0 | 5.4628 | 0.00098812 | -0.020897 |  | CFL | Bldg | 4830 | 0.8 | 4830 | 0.8 | 1.13 | 1.24 | -0.0043266 | 4830 | 0.8 | 4830 | 0.8 | 1.13 | 1.24 | -0.00433
CFLBldgSDGRSDNewCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SDG | RSD | New | CZ06 | 4.83 | 0.0008 | 0 | 5.28 | 0.001 | -0.0277 | 4.83 | 0.0008 | 0 | 5.28 | 0.001 | -0.0277 |  | CFL | Bldg | 4830 | 0.8 | 4830 | 0.8 | 1.09 | 1.25 | -0.005735 | 4830 | 0.8 | 4830 | 0.8 | 1.09 | 1.25 | -0.00574
CFLBldgSDGRSDNewCZ07 | Com-Iltg-dWatt-CFL_OSbldg | SDG | RSD | New | CZ07 | 4.83 | 0.0008 | 0 | 5.25 | 0.001 | -0.0255 | 4.83 | 0.0008 | 0 | 5.25 | 0.001 | -0.0255 |  | CFL | Bldg | 4830 | 0.8 | 4830 | 0.8 | 1.09 | 1.25 | -0.0052795 | 4830 | 0.8 | 4830 | 0.8 | 1.09 | 1.25 | -0.00528
CFLBldgSDGRSDNewCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SDG | RSD | New | CZ08 | 4.83 | 0.0008 | 0 | 5.18 | 0.000871 | -0.0229 | 4.83 | 0.0008 | 0 | 5.18 | 0.000871 | -0.0229 |  | CFL | Bldg | 4830 | 0.8 | 4830 | 0.8 | 1.07 | 1.09 | -0.0047412 | 4830 | 0.8 | 4830 | 0.8 | 1.07 | 1.09 | -0.00474
CFLBldgSDGRSDNewCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SDG | RSD | New | CZ10 | 4.83 | 0.0008 | 0 | 5.39 | 0.00105 | -0.0262 | 4.83 | 0.0008 | 0 | 5.39 | 0.00105 | -0.0262 |  | CFL | Bldg | 4830 | 0.8 | 4830 | 0.8 | 1.12 | 1.31 | -0.0054244 | 4830 | 0.8 | 4830 | 0.8 | 1.12 | 1.31 | -0.00542
CFLBldgSDGRSDNewCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SDG | RSD | New | CZ14 | 4.83 | 0.0008 | 0 | 5.31 | 0.00105 | -0.0388 | 4.83 | 0.0008 | 0 | 5.31 | 0.00105 | -0.0388 |  | CFL | Bldg | 4830 | 0.8 | 4830 | 0.8 | 1.1 | 1.31 | -0.0080331 | 4830 | 0.8 | 4830 | 0.8 | 1.1 | 1.31 | -0.00803
CFLBldgSDGRSDNewCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SDG | RSD | New | CZ15 | 4.83 | 0.0008 | 0 | 5.8 | 0.00108 | -0.0113 | 4.83 | 0.0008 | 0 | 5.8 | 0.00108 | -0.0113 |  | CFL | Bldg | 4830 | 0.8 | 4830 | 0.8 | 1.2 | 1.35 | -0.0023395 | 4830 | 0.8 | 4830 | 0.8 | 1.2 | 1.35 | -0.00234
CFLBldgSDGRSDNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SDG | RSD | New | IOU | 4.83 | 0.0008 | 0 | 5.2806 | 0.0010072 | -0.025687 | 4.83 | 0.0008 | 0 | 5.2806 | 0.0010072 | -0.025687 |  | CFL | Bldg | 4830 | 0.8 | 4830 | 0.8 | 1.09 | 1.26 | -0.0053183 | 4830 | 0.8 | 4830 | 0.8 | 1.09 | 1.26 | -0.00532
CFLBldgSDGRt3ExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Rt3 | Ex | CZ06 | 3.71 | 0.00063085 | 0 | 4.2293 | 0.00079278 | -0.00534 | 3.71 | 0.000629 | 0 | 4.22 | 0.00079 | -0.00534 |  | CFL | Bldg | 3710 | 0.631 | 3710 | 0.629 | 1.14 | 1.26 | -0.0014394 | 3710 | 0.631 | 3710 | 0.629 | 1.14 | 1.26 | -0.00144
CFLBldgSDGRt3ExCZ07 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Rt3 | Ex | CZ07 | 3.71 | 0.00063085 | 0 | 4.2493 | 0.00077785 | -0.00245 | 3.71 | 0.000629 | 0 | 4.24 | 0.000776 | -0.00245 |  | CFL | Bldg | 3710 | 0.631 | 3710 | 0.629 | 1.14 | 1.23 | -0.00066038 | 3710 | 0.631 | 3710 | 0.629 | 1.14 | 1.23 | -0.00066
CFLBldgSDGRt3ExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Rt3 | Ex | CZ08 | 3.71 | 0.00063085 | 0 | 4.24 | 0.00078078 | -0.0046393 | 3.71 | 0.000629 | 0 | 4.24 | 0.000778 | -0.00463 |  | CFL | Bldg | 3710 | 0.631 | 3710 | 0.629 | 1.14 | 1.24 | -0.001248 | 3710 | 0.631 | 3710 | 0.629 | 1.14 | 1.24 | -0.00125
CFLBldgSDGRt3ExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Rt3 | Ex | CZ10 | 3.71 | 0.00063085 | 0 | 4.18 | 0.00079078 | -0.0081593 | 3.71 | 0.000629 | 0 | 4.18 | 0.00078893 | -0.00815 |  | CFL | Bldg | 3710 | 0.631 | 3710 | 0.629 | 1.13 | 1.25 | -0.0021968 | 3710 | 0.631 | 3710 | 0.629 | 1.13 | 1.25 | -0.0022
CFLBldgSDGRt3ExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Rt3 | Ex | CZ14 | 3.71 | 0.00063085 | 0 | 3.98 | 0.00079686 | -0.025093 | 3.71 | 0.000629 | 0 | 3.98 | 0.000795 | -0.025093 |  | CFL | Bldg | 3710 | 0.631 | 3710 | 0.629 | 1.07 | 1.26 | -0.0067636 | 3710 | 0.631 | 3710 | 0.629 | 1.07 | 1.26 | -0.00676
CFLBldgSDGRt3ExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Rt3 | Ex | CZ15 | 3.71 | 0.00063085 | 0 | 4.3292 | 0.00081185 | -0.00207 | 3.71 | 0.000629 | 0 | 4.32 | 0.00081 | -0.00207 |  | CFL | Bldg | 3710 | 0.631 | 3710 | 0.629 | 1.16 | 1.29 | -0.00055795 | 3710 | 0.631 | 3710 | 0.629 | 1.16 | 1.29 | -0.000558
CFLBldgSDGRt3ExIOU | Com-Iltg-dWatt-CFL_OSbldg | SDG | Rt3 | Ex | IOU | 3.71 | 0.00063085 | 0 | 4.2308 | 0.00078174 | -0.0041018 | 3.71 | 0.000629 | 0 | 4.2244 | 0.00077979 | -0.004099 |  | CFL | Bldg | 3710 | 0.631 | 3710 | 0.629 | 1.14 | 1.24 | -0.0011049 | 3710 | 0.631 | 3710 | 0.629 | 1.14 | 1.24 | -0.0011
CFLBldgSDGRt3NewCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Rt3 | New | CZ06 | 3.71 | 0.000629 | 0 | 4.1 | 0.000769 | -0.00793 | 3.71 | 0.000629 | 0 | 4.1 | 0.000769 | -0.00793 |  | CFL | Bldg | 3710 | 0.629 | 3710 | 0.629 | 1.11 | 1.22 | -0.0021375 | 3710 | 0.629 | 3710 | 0.629 | 1.11 | 1.22 | -0.00214
CFLBldgSDGRt3NewCZ07 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Rt3 | New | CZ07 | 3.71 | 0.000629 | 0 | 4.13 | 0.000744 | -0.00378 | 3.71 | 0.000629 | 0 | 4.13 | 0.000744 | -0.00378 |  | CFL | Bldg | 3710 | 0.629 | 3710 | 0.629 | 1.11 | 1.18 | -0.0010189 | 3710 | 0.629 | 3710 | 0.629 | 1.11 | 1.18 | -0.00102
CFLBldgSDGRt3NewCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Rt3 | New | CZ08 | 3.71 | 0.000629 | 0 | 4.14 | 0.000758 | -0.00645 | 3.71 | 0.000629 | 0 | 4.14 | 0.000758 | -0.00645 |  | CFL | Bldg | 3710 | 0.629 | 3710 | 0.629 | 1.12 | 1.21 | -0.0017385 | 3710 | 0.629 | 3710 | 0.629 | 1.12 | 1.21 | -0.00174
CFLBldgSDGRt3NewCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Rt3 | New | CZ10 | 3.71 | 0.000629 | 0 | 4.09 | 0.000783 | -0.0112 | 3.71 | 0.000629 | 0 | 4.09 | 0.000783 | -0.0112 |  | CFL | Bldg | 3710 | 0.629 | 3710 | 0.629 | 1.1 | 1.24 | -0.0030189 | 3710 | 0.629 | 3710 | 0.629 | 1.1 | 1.24 | -0.00302
CFLBldgSDGRt3NewCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Rt3 | New | CZ14 | 3.71 | 0.000629 | 0 | 3.95 | 0.000788 | -0.027 | 3.71 | 0.000629 | 0 | 3.95 | 0.000788 | -0.027 |  | CFL | Bldg | 3710 | 0.629 | 3710 | 0.629 | 1.06 | 1.25 | -0.0072776 | 3710 | 0.629 | 3710 | 0.629 | 1.06 | 1.25 | -0.00728
CFLBldgSDGRt3NewCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Rt3 | New | CZ15 | 3.71 | 0.000629 | 0 | 4.32 | 0.000839 | -0.00168 | 3.71 | 0.000629 | 0 | 4.32 | 0.000839 | -0.00168 |  | CFL | Bldg | 3710 | 0.629 | 3710 | 0.629 | 1.16 | 1.33 | -0.00045283 | 3710 | 0.629 | 3710 | 0.629 | 1.16 | 1.33 | -0.000453
CFLBldgSDGRt3NewIOU | Com-Iltg-dWatt-CFL_OSbldg | SDG | Rt3 | New | IOU | 3.71 | 0.000629 | 0 | 4.1197 | 0.00075533 | -0.005923 | 3.71 | 0.000629 | 0 | 4.1197 | 0.00075533 | -0.005923 |  | CFL | Bldg | 3710 | 0.629 | 3710 | 0.629 | 1.11 | 1.2 | -0.0015965 | 3710 | 0.629 | 3710 | 0.629 | 1.11 | 1.2 | -0.0016
CFLBldgSDGRtLExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SDG | RtL | Ex | CZ06 | 4.3493 | 0.00068893 | 0 | 4.8993 | 0.00086985 | -0.0107 | 4.3493 | 0.000688 | 0 | 4.89 | 0.000868 | -0.0107 |  | CFL | Bldg | 4350 | 0.689 | 4350 | 0.688 | 1.12 | 1.26 | -0.0024602 | 4350 | 0.689 | 4350 | 0.688 | 1.12 | 1.26 | -0.00246
CFLBldgSDGRtLExCZ07 | Com-Iltg-dWatt-CFL_OSbldg | SDG | RtL | Ex | CZ07 | 4.3493 | 0.00068893 | 0 | 4.9293 | 0.00086885 | -0.0076993 | 4.3493 | 0.000688 | 0 | 4.92 | 0.000867 | -0.00769 |  | CFL | Bldg | 4350 | 0.689 | 4350 | 0.688 | 1.13 | 1.26 | -0.0017681 | 4350 | 0.689 | 4350 | 0.688 | 1.13 | 1.26 | -0.00177
CFLBldgSDGRtLExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SDG | RtL | Ex | CZ08 | 4.3493 | 0.00068893 | 0 | 4.91 | 0.00086985 | -0.0092193 | 4.3493 | 0.000688 | 0 | 4.91 | 0.00086893 | -0.00921 |  | CFL | Bldg | 4350 | 0.689 | 4350 | 0.688 | 1.13 | 1.26 | -0.0021176 | 4350 | 0.689 | 4350 | 0.688 | 1.13 | 1.26 | -0.00212
CFLBldgSDGRtLExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SDG | RtL | Ex | CZ10 | 4.3493 | 0.00068893 | 0 | 4.8793 | 0.00088585 | -0.0123 | 4.3493 | 0.000688 | 0 | 4.87 | 0.000884 | -0.0123 |  | CFL | Bldg | 4350 | 0.689 | 4350 | 0.688 | 1.12 | 1.28 | -0.0028281 | 4350 | 0.689 | 4350 | 0.688 | 1.12 | 1.28 | -0.00283
CFLBldgSDGRtLExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SDG | RtL | Ex | CZ14 | 4.3493 | 0.00068893 | 0 | 4.71 | 0.00089785 | -0.0252 | 4.3493 | 0.000688 | 0 | 4.71 | 0.000896 | -0.0252 |  | CFL | Bldg | 4350 | 0.689 | 4350 | 0.688 | 1.08 | 1.3 | -0.0057941 | 4350 | 0.689 | 4350 | 0.688 | 1.08 | 1.3 | -0.00579
CFLBldgSDGRtLExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SDG | RtL | Ex | CZ15 | 4.3492 | 0.00068892 | 0 | 5.09 | 0.00090285 | -0.00439 | 4.3492 | 0.000688 | 0 | 5.09 | 0.000901 | -0.00439 |  | CFL | Bldg | 4350 | 0.689 | 4350 | 0.688 | 1.17 | 1.31 | -0.0010094 | 4350 | 0.689 | 4350 | 0.688 | 1.17 | 1.31 | -0.00101
CFLBldgSDGRtLExIOU | Com-Iltg-dWatt-CFL_OSbldg | SDG | RtL | Ex | IOU | 4.3493 | 0.00068893 | 0 | 4.9147 | 0.00087316 | -0.0090367 | 4.3493 | 0.000688 | 0 | 4.906 | 0.00087136 | -0.00903 |  | CFL | Bldg | 4350 | 0.689 | 4350 | 0.688 | 1.13 | 1.27 | -0.0020762 | 4350 | 0.689 | 4350 | 0.688 | 1.13 | 1.27 | -0.00208
CFLBldgSDGRtLNewCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SDG | RtL | New | CZ06 | 4.34 | 0.000688 | 0 | 4.76 | 0.000875 | -0.0149 | 4.34 | 0.000688 | 0 | 4.76 | 0.000875 | -0.0149 |  | CFL | Bldg | 4340 | 0.688 | 4340 | 0.688 | 1.1 | 1.27 | -0.0034332 | 4340 | 0.688 | 4340 | 0.688 | 1.1 | 1.27 | -0.00343
CFLBldgSDGRtLNewCZ07 | Com-Iltg-dWatt-CFL_OSbldg | SDG | RtL | New | CZ07 | 4.34 | 0.000688 | 0 | 4.74 | 0.000842 | -0.0106 | 4.34 | 0.000688 | 0 | 4.74 | 0.000842 | -0.0106 |  | CFL | Bldg | 4340 | 0.688 | 4340 | 0.688 | 1.09 | 1.22 | -0.0024424 | 4340 | 0.688 | 4340 | 0.688 | 1.09 | 1.22 | -0.00244
CFLBldgSDGRtLNewCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SDG | RtL | New | CZ08 | 4.34 | 0.000688 | 0 | 4.82 | 0.000886 | -0.0126 | 4.34 | 0.000688 | 0 | 4.82 | 0.000886 | -0.0126 |  | CFL | Bldg | 4340 | 0.688 | 4340 | 0.688 | 1.11 | 1.29 | -0.0029032 | 4340 | 0.688 | 4340 | 0.688 | 1.11 | 1.29 | -0.0029
CFLBldgSDGRtLNewCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SDG | RtL | New | CZ10 | 4.34 | 0.000688 | 0 | 4.85 | 0.000932 | -0.0145 | 4.34 | 0.000688 | 0 | 4.85 | 0.000932 | -0.0145 |  | CFL | Bldg | 4340 | 0.688 | 4340 | 0.688 | 1.12 | 1.35 | -0.003341 | 4340 | 0.688 | 4340 | 0.688 | 1.12 | 1.35 | -0.00334
CFLBldgSDGRtLNewCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SDG | RtL | New | CZ14 | 4.34 | 0.000688 | 0 | 4.74 | 0.000925 | -0.0282 | 4.34 | 0.000688 | 0 | 4.74 | 0.000925 | -0.0282 |  | CFL | Bldg | 4340 | 0.688 | 4340 | 0.688 | 1.09 | 1.34 | -0.0064977 | 4340 | 0.688 | 4340 | 0.688 | 1.09 | 1.34 | -0.0065
CFLBldgSDGRtLNewCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SDG | RtL | New | CZ15 | 4.34 | 0.000688 | 0 | 5.13 | 0.000942 | -0.00424 | 4.34 | 0.000688 | 0 | 5.13 | 0.000942 | -0.00424 |  | CFL | Bldg | 4340 | 0.688 | 4340 | 0.688 | 1.18 | 1.37 | -0.00097696 | 4340 | 0.688 | 4340 | 0.688 | 1.18 | 1.37 | -0.000977
CFLBldgSDGRtLNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SDG | RtL | New | IOU | 4.34 | 0.000688 | 0 | 4.7726 | 0.00086797 | -0.011837 | 4.34 | 0.000688 | 0 | 4.7726 | 0.00086797 | -0.011837 |  | CFL | Bldg | 4340 | 0.688 | 4340 | 0.688 | 1.1 | 1.26 | -0.0027275 | 4340 | 0.688 | 4340 | 0.688 | 1.1 | 1.26 | -0.00273
CFLBldgSDGRtSExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SDG | RtS | Ex | CZ06 | 4.01 | 0.0007 | 0 | 4.44 | 0.000876 | -0.00794 | 4.01 | 0.0007 | 0 | 4.44 | 0.000876 | -0.00794 |  | CFL | Bldg | 4010 | 0.7 | 4010 | 0.7 | 1.11 | 1.25 | -0.00198 | 4010 | 0.7 | 4010 | 0.7 | 1.11 | 1.25 | -0.00198
CFLBldgSDGRtSExCZ07 | Com-Iltg-dWatt-CFL_OSbldg | SDG | RtS | Ex | CZ07 | 4.01 | 0.0007 | 0 | 4.45 | 0.000856 | -0.00489 | 4.01 | 0.0007 | 0 | 4.45 | 0.000856 | -0.00489 |  | CFL | Bldg | 4010 | 0.7 | 4010 | 0.7 | 1.11 | 1.22 | -0.0012195 | 4010 | 0.7 | 4010 | 0.7 | 1.11 | 1.22 | -0.00122
CFLBldgSDGRtSExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SDG | RtS | Ex | CZ08 | 4.01 | 0.0007 | 0 | 4.47 | 0.000877 | -0.00674 | 4.01 | 0.0007 | 0 | 4.47 | 0.000877 | -0.00674 |  | CFL | Bldg | 4010 | 0.7 | 4010 | 0.7 | 1.11 | 1.25 | -0.0016808 | 4010 | 0.7 | 4010 | 0.7 | 1.11 | 1.25 | -0.00168
CFLBldgSDGRtSExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SDG | RtS | Ex | CZ10 | 4.01 | 0.0007 | 0 | 4.45 | 0.000885 | -0.00939 | 4.01 | 0.0007 | 0 | 4.45 | 0.000885 | -0.00939 |  | CFL | Bldg | 4010 | 0.7 | 4010 | 0.7 | 1.11 | 1.26 | -0.0023416 | 4010 | 0.7 | 4010 | 0.7 | 1.11 | 1.26 | -0.00234
CFLBldgSDGRtSExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SDG | RtS | Ex | CZ14 | 4.01 | 0.0007 | 0 | 4.32 | 0.000883 | -0.0206 | 4.01 | 0.0007 | 0 | 4.32 | 0.000883 | -0.0206 |  | CFL | Bldg | 4010 | 0.7 | 4010 | 0.7 | 1.08 | 1.26 | -0.0051372 | 4010 | 0.7 | 4010 | 0.7 | 1.08 | 1.26 | -0.00514
CFLBldgSDGRtSExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SDG | RtS | Ex | CZ15 | 4.01 | 0.0007 | 0 | 4.76 | 0.000871 | -0.00244 | 4.01 | 0.0007 | 0 | 4.76 | 0.000871 | -0.00244 |  | CFL | Bldg | 4010 | 0.7 | 4010 | 0.7 | 1.19 | 1.24 | -0.00060848 | 4010 | 0.7 | 4010 | 0.7 | 1.19 | 1.24 | -0.000608
CFLBldgSDGRtSExIOU | Com-Iltg-dWatt-CFL_OSbldg | SDG | RtS | Ex | IOU | 4.01 | 0.0007 | 0 | 4.4509 | 0.0008651 | -0.006223 | 4.01 | 0.0007 | 0 | 4.4509 | 0.0008651 | -0.006223 |  | CFL | Bldg | 4010 | 0.7 | 4010 | 0.7 | 1.11 | 1.24 | -0.0015519 | 4010 | 0.7 | 4010 | 0.7 | 1.11 | 1.24 | -0.00155
CFLBldgSDGRtSNewCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SDG | RtS | New | CZ06 | 4.01 | 0.0007 | 0 | 4.33 | 0.000862 | -0.00999 | 4.01 | 0.0007 | 0 | 4.33 | 0.000862 | -0.00999 |  | CFL | Bldg | 4010 | 0.7 | 4010 | 0.7 | 1.08 | 1.23 | -0.0024913 | 4010 | 0.7 | 4010 | 0.7 | 1.08 | 1.23 | -0.00249
CFLBldgSDGRtSNewCZ07 | Com-Iltg-dWatt-CFL_OSbldg | SDG | RtS | New | CZ07 | 4.01 | 0.0007 | 0 | 4.32 | 0.000851 | -0.0061 | 4.01 | 0.0007 | 0 | 4.32 | 0.000851 | -0.0061 |  | CFL | Bldg | 4010 | 0.7 | 4010 | 0.7 | 1.08 | 1.22 | -0.0015212 | 4010 | 0.7 | 4010 | 0.7 | 1.08 | 1.22 | -0.00152
CFLBldgSDGRtSNewCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SDG | RtS | New | CZ08 | 4.01 | 0.0007 | 0 | 4.37 | 0.000871 | -0.00834 | 4.01 | 0.0007 | 0 | 4.37 | 0.000871 | -0.00834 |  | CFL | Bldg | 4010 | 0.7 | 4010 | 0.7 | 1.09 | 1.24 | -0.0020798 | 4010 | 0.7 | 4010 | 0.7 | 1.09 | 1.24 | -0.00208
CFLBldgSDGRtSNewCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SDG | RtS | New | CZ10 | 4.01 | 0.0007 | 0 | 4.41 | 0.000908 | -0.00999 | 4.01 | 0.0007 | 0 | 4.41 | 0.000908 | -0.00999 |  | CFL | Bldg | 4010 | 0.7 | 4010 | 0.7 | 1.1 | 1.3 | -0.0024913 | 4010 | 0.7 | 4010 | 0.7 | 1.1 | 1.3 | -0.00249
CFLBldgSDGRtSNewCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SDG | RtS | New | CZ14 | 4.01 | 0.0007 | 0 | 4.31 | 0.000895 | -0.022 | 4.01 | 0.0007 | 0 | 4.31 | 0.000895 | -0.022 |  | CFL | Bldg | 4010 | 0.7 | 4010 | 0.7 | 1.07 | 1.28 | -0.0054863 | 4010 | 0.7 | 4010 | 0.7 | 1.07 | 1.28 | -0.00549
CFLBldgSDGRtSNewCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SDG | RtS | New | CZ15 | 4.01 | 0.0007 | 0 | 4.61 | 0.00092 | -0.00193 | 4.01 | 0.0007 | 0 | 4.61 | 0.00092 | -0.00193 |  | CFL | Bldg | 4010 | 0.7 | 4010 | 0.7 | 1.15 | 1.31 | -0.0004813 | 4010 | 0.7 | 4010 | 0.7 | 1.15 | 1.31 | -0.000481
CFLBldgSDGRtSNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SDG | RtS | New | IOU | 4.01 | 0.0007 | 0 | 4.3455 | 0.00086663 | -0.0073348 | 4.01 | 0.0007 | 0 | 4.3455 | 0.00086663 | -0.0073348 |  | CFL | Bldg | 4010 | 0.7 | 4010 | 0.7 | 1.08 | 1.24 | -0.0018291 | 4010 | 0.7 | 4010 | 0.7 | 1.08 | 1.24 | -0.00183
CFLBldgSDGSCnExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SDG | SCn | Ex | CZ06 | 2.7587 | 0.00057427 | 0 | 2.8387 | 0.00073807 | -0.014393 | 2.74 | 0.000564 | 0 | 2.82 | 0.000725 | -0.0143 |  | CFL | Bldg | 2760 | 0.574 | 2740 | 0.564 | 1.03 | 1.29 | -0.005219 | 2760 | 0.574 | 2740 | 0.564 | 1.03 | 1.29 | -0.00522
CFLBldgSDGSCnExCZ07 | Com-Iltg-dWatt-CFL_OSbldg | SDG | SCn | Ex | CZ07 | 2.7587 | 0.00057427 | 0 | 2.7893 | 0.00074207 | -0.011593 | 2.74 | 0.000564 | 0 | 2.78 | 0.000729 | -0.0115 |  | CFL | Bldg | 2760 | 0.574 | 2740 | 0.564 | 1.01 | 1.29 | -0.0041971 | 2760 | 0.574 | 2740 | 0.564 | 1.01 | 1.29 | -0.0042
CFLBldgSDGSCnExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SDG | SCn | Ex | CZ08 | 2.7587 | 0.00057427 | 0 | 2.8787 | 0.00073707 | -0.012293 | 2.74 | 0.000564 | 0 | 2.86 | 0.000724 | -0.0122 |  | CFL | Bldg | 2760 | 0.574 | 2740 | 0.564 | 1.04 | 1.28 | -0.0044526 | 2760 | 0.574 | 2740 | 0.564 | 1.04 | 1.28 | -0.00445
CFLBldgSDGSCnExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SDG | SCn | Ex | CZ10 | 2.7587 | 0.00057427 | 0 | 2.8887 | 0.000747 | -0.015693 | 2.74 | 0.000564 | 0 | 2.87 | 0.000733 | -0.0156 |  | CFL | Bldg | 2760 | 0.574 | 2740 | 0.564 | 1.05 | 1.3 | -0.0056934 | 2760 | 0.574 | 2740 | 0.564 | 1.05 | 1.3 | -0.00569
CFLBldgSDGSCnExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SDG | SCn | Ex | CZ14 | 2.7587 | 0.00057427 | 0 | 2.7987 | 0.00073307 | -0.023193 | 2.74 | 0.000564 | 0 | 2.78 | 0.00072 | -0.0231 |  | CFL | Bldg | 2760 | 0.574 | 2740 | 0.564 | 1.01 | 1.28 | -0.0084307 | 2760 | 0.574 | 2740 | 0.564 | 1.01 | 1.28 | -0.00843
CFLBldgSDGSCnExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SDG | SCn | Ex | CZ15 | 2.7587 | 0.00057427 | 0 | 3.0887 | 0.00073408 | -0.0065174 | 2.74 | 0.000564 | 0 | 3.07 | 0.000721 | -0.00648 |  | CFL | Bldg | 2760 | 0.574 | 2740 | 0.564 | 1.12 | 1.28 | -0.002365 | 2760 | 0.574 | 2740 | 0.564 | 1.12 | 1.28 | -0.00237
CFLBldgSDGSCnExIOU | Com-Iltg-dWatt-CFL_OSbldg | SDG | SCn | Ex | IOU | 2.7587 | 0.00057427 | 0 | 2.8221 | 0.00074333 | -0.012929 | 2.74 | 0.000564 | 0 | 2.8096 | 0.00072998 | -0.012836 |  | CFL | Bldg | 2760 | 0.574 | 2740 | 0.564 | 1.03 | 1.29 | -0.0046845 | 2760 | 0.574 | 2740 | 0.564 | 1.03 | 1.29 | -0.00468
CFLBldgSDGSCnNewCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SDG | SCn | New | CZ06 | 2.74 | 0.000564 | 0 | 2.74 | 0.000675 | -0.0162 | 2.74 | 0.000564 | 0 | 2.74 | 0.000675 | -0.0162 |  | CFL | Bldg | 2740 | 0.564 | 2740 | 0.564 | 1 | 1.2 | -0.0059124 | 2740 | 0.564 | 2740 | 0.564 | 1 | 1.2 | -0.00591
CFLBldgSDGSCnNewCZ07 | Com-Iltg-dWatt-CFL_OSbldg | SDG | SCn | New | CZ07 | 2.74 | 0.000564 | 0 | 2.74 | 0.00069 | -0.0134 | 2.74 | 0.000564 | 0 | 2.74 | 0.00069 | -0.0134 |  | CFL | Bldg | 2740 | 0.564 | 2740 | 0.564 | 1 | 1.22 | -0.0048905 | 2740 | 0.564 | 2740 | 0.564 | 1 | 1.22 | -0.00489
CFLBldgSDGSCnNewCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SDG | SCn | New | CZ08 | 2.74 | 0.000564 | 0 | 2.81 | 0.000685 | -0.0141 | 2.74 | 0.000564 | 0 | 2.81 | 0.000685 | -0.0141 |  | CFL | Bldg | 2740 | 0.564 | 2740 | 0.564 | 1.03 | 1.21 | -0.005146 | 2740 | 0.564 | 2740 | 0.564 | 1.03 | 1.21 | -0.00515
CFLBldgSDGSCnNewCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SDG | SCn | New | CZ10 | 2.74 | 0.000564 | 0 | 2.81 | 0.000702 | -0.0165 | 2.74 | 0.000564 | 0 | 2.81 | 0.000702 | -0.0165 |  | CFL | Bldg | 2740 | 0.564 | 2740 | 0.564 | 1.03 | 1.24 | -0.0060219 | 2740 | 0.564 | 2740 | 0.564 | 1.03 | 1.24 | -0.00602
CFLBldgSDGSCnNewCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SDG | SCn | New | CZ14 | 2.74 | 0.000564 | 0 | 2.76 | 0.000699 | -0.0243 | 2.74 | 0.000564 | 0 | 2.76 | 0.000699 | -0.0243 |  | CFL | Bldg | 2740 | 0.564 | 2740 | 0.564 | 1.01 | 1.24 | -0.0088686 | 2740 | 0.564 | 2740 | 0.564 | 1.01 | 1.24 | -0.00887
CFLBldgSDGSCnNewCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SDG | SCn | New | CZ15 | 2.74 | 0.000564 | 0 | 2.99 | 0.000704 | -0.00513 | 2.74 | 0.000564 | 0 | 2.99 | 0.000704 | -0.00513 |  | CFL | Bldg | 2740 | 0.564 | 2740 | 0.564 | 1.09 | 1.25 | -0.0018723 | 2740 | 0.564 | 2740 | 0.564 | 1.09 | 1.25 | -0.00187
CFLBldgSDGSCnNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SDG | SCn | New | IOU | 2.74 | 0.000564 | 0 | 2.7624 | 0.00069318 | -0.01443 | 2.74 | 0.000564 | 0 | 2.7624 | 0.00069318 | -0.01443 |  | CFL | Bldg | 2740 | 0.564 | 2740 | 0.564 | 1.01 | 1.23 | -0.0052664 | 2740 | 0.564 | 2740 | 0.564 | 1.01 | 1.23 | -0.00527
CFLBldgSDGSUnExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SDG | SUn | Ex | CZ06 | 2.7587 | 0.00057427 | 0 | 2.7587 | 0.00057427 | 0 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 |  | CFL | Bldg | 2760 | 0.574 | 2740 | 0.564 | 1 | 1 | 0 | 2760 | 0.574 | 2740 | 0.564 | 1 | 1 | 0
CFLBldgSDGSUnExCZ07 | Com-Iltg-dWatt-CFL_OSbldg | SDG | SUn | Ex | CZ07 | 2.7587 | 0.00057427 | 0 | 2.7587 | 0.00057427 | 0 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 |  | CFL | Bldg | 2760 | 0.574 | 2740 | 0.564 | 1 | 1 | 0 | 2760 | 0.574 | 2740 | 0.564 | 1 | 1 | 0
CFLBldgSDGSUnExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SDG | SUn | Ex | CZ08 | 2.7587 | 0.00057427 | 0 | 2.7587 | 0.00057427 | 0 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 |  | CFL | Bldg | 2760 | 0.574 | 2740 | 0.564 | 1 | 1 | 0 | 2760 | 0.574 | 2740 | 0.564 | 1 | 1 | 0
CFLBldgSDGSUnExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SDG | SUn | Ex | CZ10 | 2.7587 | 0.00057427 | 0 | 2.7587 | 0.00057427 | 0 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 |  | CFL | Bldg | 2760 | 0.574 | 2740 | 0.564 | 1 | 1 | 0 | 2760 | 0.574 | 2740 | 0.564 | 1 | 1 | 0
CFLBldgSDGSUnExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SDG | SUn | Ex | CZ14 | 2.7587 | 0.00057427 | 0 | 2.7587 | 0.00057427 | 0 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 |  | CFL | Bldg | 2760 | 0.574 | 2740 | 0.564 | 1 | 1 | 0 | 2760 | 0.574 | 2740 | 0.564 | 1 | 1 | 0
CFLBldgSDGSUnExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SDG | SUn | Ex | CZ15 | 2.7587 | 0.00057427 | 0 | 2.7587 | 0.00057427 | 0 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 |  | CFL | Bldg | 2760 | 0.574 | 2740 | 0.564 | 1 | 1 | 0 | 2760 | 0.574 | 2740 | 0.564 | 1 | 1 | 0
CFLBldgSDGSUnExIOU | Com-Iltg-dWatt-CFL_OSbldg | SDG | SUn | Ex | IOU | 2.7587 | 0.00057427 | 0 | 2.7587 | 0.00057427 | 0 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 |  | CFL | Bldg | 2760 | 0.574 | 2740 | 0.564 | 1 | 1 | 0 | 2760 | 0.574 | 2740 | 0.564 | 1 | 1 | 0
CFLBldgSDGSUnNewCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SDG | SUn | New | CZ06 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 |  | CFL | Bldg | 2740 | 0.564 | 2740 | 0.564 | 1 | 1 | 0 | 2740 | 0.564 | 2740 | 0.564 | 1 | 1 | 0
CFLBldgSDGSUnNewCZ07 | Com-Iltg-dWatt-CFL_OSbldg | SDG | SUn | New | CZ07 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 |  | CFL | Bldg | 2740 | 0.564 | 2740 | 0.564 | 1 | 1 | 0 | 2740 | 0.564 | 2740 | 0.564 | 1 | 1 | 0
CFLBldgSDGSUnNewCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SDG | SUn | New | CZ08 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 |  | CFL | Bldg | 2740 | 0.564 | 2740 | 0.564 | 1 | 1 | 0 | 2740 | 0.564 | 2740 | 0.564 | 1 | 1 | 0
CFLBldgSDGSUnNewCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SDG | SUn | New | CZ10 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 |  | CFL | Bldg | 2740 | 0.564 | 2740 | 0.564 | 1 | 1 | 0 | 2740 | 0.564 | 2740 | 0.564 | 1 | 1 | 0
CFLBldgSDGSUnNewCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SDG | SUn | New | CZ14 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 |  | CFL | Bldg | 2740 | 0.564 | 2740 | 0.564 | 1 | 1 | 0 | 2740 | 0.564 | 2740 | 0.564 | 1 | 1 | 0
CFLBldgSDGSUnNewCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SDG | SUn | New | CZ15 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 |  | CFL | Bldg | 2740 | 0.564 | 2740 | 0.564 | 1 | 1 | 0 | 2740 | 0.564 | 2740 | 0.564 | 1 | 1 | 0
CFLBldgSDGSUnNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SDG | SUn | New | IOU | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 | 2.74 | 0.000564 | 0 |  | CFL | Bldg | 2740 | 0.564 | 2740 | 0.564 | 1 | 1 | 0 | 2740 | 0.564 | 2740 | 0.564 | 1 | 1 | 0
CFLBldgSDGWRfExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SDG | WRf | Ex | CZ06 | 4.7242 | 0.00054708 | 0 | 7.4408 | 0.00068583 | 0 | 4.66 | 0.00053608 | 0 | 7.34 | 0.00067208 | 0 |  | CFL | Bldg | 4720 | 0.547 | 4660 | 0.536 | 1.58 | 1.25 | 0 | 4720 | 0.547 | 4660 | 0.536 | 1.58 | 1.25 | 0
CFLBldgSDGWRfExCZ07 | Com-Iltg-dWatt-CFL_OSbldg | SDG | WRf | Ex | CZ07 | 4.7243 | 0.00054711 | 0 | 7.3919 | 0.00068678 | 0 | 4.66 | 0.00053608 | 0 | 7.2908 | 0.000673 | 0 |  | CFL | Bldg | 4720 | 0.547 | 4660 | 0.536 | 1.56 | 1.26 | 0 | 4720 | 0.547 | 4660 | 0.536 | 1.56 | 1.26 | 0
CFLBldgSDGWRfExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SDG | WRf | Ex | CZ10 | 4.7243 | 0.00054711 | 0 | 7.6211 | 0.00069186 | 0 | 4.66 | 0.00053608 | 0 | 7.52 | 0.00067808 | 0 |  | CFL | Bldg | 4720 | 0.547 | 4660 | 0.536 | 1.61 | 1.26 | 0 | 4720 | 0.547 | 4660 | 0.536 | 1.61 | 1.26 | 0
CFLBldgSDGWRfExIOU | Com-Iltg-dWatt-CFL_OSbldg | SDG | WRf | Ex | IOU | 4.7243 | 0.00054711 | 0 | 7.4427 | 0.00068789 | 0 | 4.66 | 0.00053608 | 0 | 7.3416 | 0.00067411 | 0 |  | CFL | Bldg | 4720 | 0.547 | 4660 | 0.536 | 1.58 | 1.26 | 0 | 4720 | 0.547 | 4660 | 0.536 | 1.58 | 1.26 | 0
CFLBldgSDGWRfNewCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SDG | WRf | New | CZ06 | 4.66 | 0.000537 | 0 | 7.07 | 0.000662 | 0 | 4.66 | 0.000537 | 0 | 7.07 | 0.000662 | 0 |  | CFL | Bldg | 4660 | 0.537 | 4660 | 0.537 | 1.52 | 1.23 | 0 | 4660 | 0.537 | 4660 | 0.537 | 1.52 | 1.23 | 0
CFLBldgSDGWRfNewCZ07 | Com-Iltg-dWatt-CFL_OSbldg | SDG | WRf | New | CZ07 | 4.66 | 0.000537 | 0 | 7.13 | 0.000662 | 0 | 4.66 | 0.000537 | 0 | 7.13 | 0.000662 | 0 |  | CFL | Bldg | 4660 | 0.537 | 4660 | 0.537 | 1.53 | 1.23 | 0 | 4660 | 0.537 | 4660 | 0.537 | 1.53 | 1.23 | 0
CFLBldgSDGWRfNewCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SDG | WRf | New | CZ08 | 4.66 | 0.000537 | 0 | 7.03 | 0.000663 | 0 | 4.66 | 0.000537 | 0 | 7.03 | 0.000663 | 0 |  | CFL | Bldg | 4660 | 0.537 | 4660 | 0.537 | 1.51 | 1.23 | 0 | 4660 | 0.537 | 4660 | 0.537 | 1.51 | 1.23 | 0
CFLBldgSDGWRfNewCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SDG | WRf | New | CZ10 | 4.66 | 0.000537 | 0 | 6.86 | 0.000671 | 0 | 4.66 | 0.000537 | 0 | 6.86 | 0.000671 | 0 |  | CFL | Bldg | 4660 | 0.537 | 4660 | 0.537 | 1.47 | 1.25 | 0 | 4660 | 0.537 | 4660 | 0.537 | 1.47 | 1.25 | 0
CFLBldgSDGWRfNewCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SDG | WRf | New | CZ14 | 4.66 | 0.000537 | 0 | 6.61 | 0.000665 | 0 | 4.66 | 0.000537 | 0 | 6.61 | 0.000665 | 0 |  | CFL | Bldg | 4660 | 0.537 | 4660 | 0.537 | 1.42 | 1.24 | 0 | 4660 | 0.537 | 4660 | 0.537 | 1.42 | 1.24 | 0
CFLBldgSDGWRfNewCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SDG | WRf | New | CZ15 | 4.66 | 0.000537 | 0 | 7.09 | 0.000669 | 0 | 4.66 | 0.000537 | 0 | 7.09 | 0.000669 | 0 |  | CFL | Bldg | 4660 | 0.537 | 4660 | 0.537 | 1.52 | 1.25 | 0 | 4660 | 0.537 | 4660 | 0.537 | 1.52 | 1.25 | 0
CFLBldgSDGWRfNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SDG | WRf | New | IOU | 4.66 | 0.000537 | 0 | 7.0702 | 0.00066397 | 0 | 4.66 | 0.000537 | 0 | 7.0702 | 0.00066397 | 0 |  | CFL | Bldg | 4660 | 0.537 | 4660 | 0.537 | 1.52 | 1.24 | 0 | 4660 | 0.537 | 4660 | 0.537 | 1.52 | 1.24 | 0
CFLNonePGEAsmExCZ01 | Com-Iltg-dWatt-CFL_OSnone | PGE | Asm | Ex | CZ01 | 2.3 | 0.000409 | 0 | 2.19 | 0.000474 | -0.0409 | 2.3 | 0.000409 | 0 | 2.19 | 0.000474 | -0.0409 |  | CFL | None | 2300 | 0.409 | 2300 | 0.409 | 0.952 | 1.16 | -0.017783 | 2300 | 0.409 | 2300 | 0.409 | 0.952 | 1.16 | -0.0178
CFLNonePGEAsmExCZ02 | Com-Iltg-dWatt-CFL_OSnone | PGE | Asm | Ex | CZ02 | 2.3 | 0.000409 | 0 | 2.37 | 0.000479 | -0.0237 | 2.3 | 0.000409 | 0 | 2.37 | 0.000479 | -0.0237 |  | CFL | None | 2300 | 0.409 | 2300 | 0.409 | 1.03 | 1.17 | -0.010304 | 2300 | 0.409 | 2300 | 0.409 | 1.03 | 1.17 | -0.0103
CFLNonePGEAsmExCZ03 | Com-Iltg-dWatt-CFL_OSnone | PGE | Asm | Ex | CZ03 | 2.3 | 0.000409 | 0 | 2.35 | 0.000479 | -0.026 | 2.3 | 0.000409 | 0 | 2.35 | 0.000479 | -0.026 |  | CFL | None | 2300 | 0.409 | 2300 | 0.409 | 1.02 | 1.17 | -0.011304 | 2300 | 0.409 | 2300 | 0.409 | 1.02 | 1.17 | -0.0113
CFLNonePGEAsmExCZ04 | Com-Iltg-dWatt-CFL_OSnone | PGE | Asm | Ex | CZ04 | 2.3 | 0.000409 | 0 | 2.41 | 0.000479 | -0.0192 | 2.3 | 0.000409 | 0 | 2.41 | 0.000479 | -0.0192 |  | CFL | None | 2300 | 0.409 | 2300 | 0.409 | 1.05 | 1.17 | -0.0083478 | 2300 | 0.409 | 2300 | 0.409 | 1.05 | 1.17 | -0.00835
CFLNonePGEAsmExCZ05 | Com-Iltg-dWatt-CFL_OSnone | PGE | Asm | Ex | CZ05 | 2.3 | 0.000409 | 0 | 2.36 | 0.00047 | -0.023 | 2.3 | 0.000409 | 0 | 2.36 | 0.00047 | -0.023 |  | CFL | None | 2300 | 0.409 | 2300 | 0.409 | 1.03 | 1.15 | -0.01 | 2300 | 0.409 | 2300 | 0.409 | 1.03 | 1.15 | -0.01
CFLNonePGEAsmExCZ11 | Com-Iltg-dWatt-CFL_OSnone | PGE | Asm | Ex | CZ11 | 2.3 | 0.000409 | 0 | 2.42 | 0.000477 | -0.0204 | 2.3 | 0.000409 | 0 | 2.42 | 0.000477 | -0.0204 |  | CFL | None | 2300 | 0.409 | 2300 | 0.409 | 1.05 | 1.17 | -0.0088696 | 2300 | 0.409 | 2300 | 0.409 | 1.05 | 1.17 | -0.00887
CFLNonePGEAsmExCZ12 | Com-Iltg-dWatt-CFL_OSnone | PGE | Asm | Ex | CZ12 | 2.3 | 0.000409 | 0 | 2.4 | 0.000482 | -0.0215 | 2.3 | 0.000409 | 0 | 2.4 | 0.000482 | -0.0215 |  | CFL | None | 2300 | 0.409 | 2300 | 0.409 | 1.04 | 1.18 | -0.0093478 | 2300 | 0.409 | 2300 | 0.409 | 1.04 | 1.18 | -0.00935
CFLNonePGEAsmExCZ13 | Com-Iltg-dWatt-CFL_OSnone | PGE | Asm | Ex | CZ13 | 2.3 | 0.000409 | 0 | 2.43 | 0.000476 | -0.0198 | 2.3 | 0.000409 | 0 | 2.43 | 0.000476 | -0.0198 |  | CFL | None | 2300 | 0.409 | 2300 | 0.409 | 1.06 | 1.16 | -0.0086087 | 2300 | 0.409 | 2300 | 0.409 | 1.06 | 1.16 | -0.00861
CFLNonePGEAsmExCZ16 | Com-Iltg-dWatt-CFL_OSnone | PGE | Asm | Ex | CZ16 | 2.3 | 0.000409 | 0 | 2.24 | 0.000471 | -0.031 | 2.3 | 0.000409 | 0 | 2.24 | 0.000471 | -0.031 |  | CFL | None | 2300 | 0.409 | 2300 | 0.409 | 0.974 | 1.15 | -0.013478 | 2300 | 0.409 | 2300 | 0.409 | 0.974 | 1.15 | -0.0135
CFLNonePGEAsmExIOU | Com-Iltg-dWatt-CFL_OSnone | PGE | Asm | Ex | IOU | 2.3 | 0.000409 | 0 | 2.3831 | 0.0004788 | -0.02279 | 2.3 | 0.000409 | 0 | 2.3831 | 0.0004788 | -0.02279 |  | CFL | None | 2300 | 0.409 | 2300 | 0.409 | 1.04 | 1.17 | -0.0099088 | 2300 | 0.409 | 2300 | 0.409 | 1.04 | 1.17 | -0.00991
CFLNonePGEAsmNewCZ01 | Com-Iltg-dWatt-CFL_OSnone | PGE | Asm | New | CZ01 | 2.3 | 0.000409 | 0 | 2.2 | 0.000473 | -0.0407 | 2.3 | 0.000409 | 0 | 2.2 | 0.000473 | -0.0407 |  | CFL | None | 2300 | 0.409 | 2300 | 0.409 | 0.957 | 1.16 | -0.017696 | 2300 | 0.409 | 2300 | 0.409 | 0.957 | 1.16 | -0.0177
CFLNonePGEAsmNewCZ02 | Com-Iltg-dWatt-CFL_OSnone | PGE | Asm | New | CZ02 | 2.3 | 0.000409 | 0 | 2.34 | 0.000479 | -0.0258 | 2.3 | 0.000409 | 0 | 2.34 | 0.000479 | -0.0258 |  | CFL | None | 2300 | 0.409 | 2300 | 0.409 | 1.02 | 1.17 | -0.011217 | 2300 | 0.409 | 2300 | 0.409 | 1.02 | 1.17 | -0.0112
CFLNonePGEAsmNewCZ03 | Com-Iltg-dWatt-CFL_OSnone | PGE | Asm | New | CZ03 | 2.3 | 0.000409 | 0 | 2.32 | 0.000472 | -0.0267 | 2.3 | 0.000409 | 0 | 2.32 | 0.000472 | -0.0267 |  | CFL | None | 2300 | 0.409 | 2300 | 0.409 | 1.01 | 1.15 | -0.011609 | 2300 | 0.409 | 2300 | 0.409 | 1.01 | 1.15 | -0.0116
CFLNonePGEAsmNewCZ04 | Com-Iltg-dWatt-CFL_OSnone | PGE | Asm | New | CZ04 | 2.3 | 0.000409 | 0 | 2.38 | 0.000479 | -0.021 | 2.3 | 0.000409 | 0 | 2.38 | 0.000479 | -0.021 |  | CFL | None | 2300 | 0.409 | 2300 | 0.409 | 1.03 | 1.17 | -0.0091304 | 2300 | 0.409 | 2300 | 0.409 | 1.03 | 1.17 | -0.00913
CFLNonePGEAsmNewCZ05 | Com-Iltg-dWatt-CFL_OSnone | PGE | Asm | New | CZ05 | 2.3 | 0.000409 | 0 | 2.34 | 0.000466 | -0.0232 | 2.3 | 0.000409 | 0 | 2.34 | 0.000466 | -0.0232 |  | CFL | None | 2300 | 0.409 | 2300 | 0.409 | 1.02 | 1.14 | -0.010087 | 2300 | 0.409 | 2300 | 0.409 | 1.02 | 1.14 | -0.0101
CFLNonePGEAsmNewCZ11 | Com-Iltg-dWatt-CFL_OSnone | PGE | Asm | New | CZ11 | 2.3 | 0.000409 | 0 | 2.4 | 0.000487 | -0.0221 | 2.3 | 0.000409 | 0 | 2.4 | 0.000487 | -0.0221 |  | CFL | None | 2300 | 0.409 | 2300 | 0.409 | 1.04 | 1.19 | -0.0096087 | 2300 | 0.409 | 2300 | 0.409 | 1.04 | 1.19 | -0.00961
CFLNonePGEAsmNewCZ12 | Com-Iltg-dWatt-CFL_OSnone | PGE | Asm | New | CZ12 | 2.3 | 0.000409 | 0 | 2.38 | 0.000485 | -0.0235 | 2.3 | 0.000409 | 0 | 2.38 | 0.000485 | -0.0235 |  | CFL | None | 2300 | 0.409 | 2300 | 0.409 | 1.03 | 1.19 | -0.010217 | 2300 | 0.409 | 2300 | 0.409 | 1.03 | 1.19 | -0.0102
CFLNonePGEAsmNewCZ13 | Com-Iltg-dWatt-CFL_OSnone | PGE | Asm | New | CZ13 | 2.3 | 0.000409 | 0 | 2.41 | 0.000488 | -0.0213 | 2.3 | 0.000409 | 0 | 2.41 | 0.000488 | -0.0213 |  | CFL | None | 2300 | 0.409 | 2300 | 0.409 | 1.05 | 1.19 | -0.0092609 | 2300 | 0.409 | 2300 | 0.409 | 1.05 | 1.19 | -0.00926
CFLNonePGEAsmNewCZ16 | Com-Iltg-dWatt-CFL_OSnone | PGE | Asm | New | CZ16 | 2.3 | 0.000409 | 0 | 2.25 | 0.00047 | -0.0308 | 2.3 | 0.000409 | 0 | 2.25 | 0.00047 | -0.0308 |  | CFL | None | 2300 | 0.409 | 2300 | 0.409 | 0.978 | 1.15 | -0.013391 | 2300 | 0.409 | 2300 | 0.409 | 0.978 | 1.15 | -0.0134
CFLNonePGEAsmNewIOU | Com-Iltg-dWatt-CFL_OSnone | PGE | Asm | New | IOU | 2.3 | 0.000409 | 0 | 2.366 | 0.00048045 | -0.023694 | 2.3 | 0.000409 | 0 | 2.366 | 0.00048045 | -0.023694 |  | CFL | None | 2300 | 0.409 | 2300 | 0.409 | 1.03 | 1.17 | -0.010302 | 2300 | 0.409 | 2300 | 0.409 | 1.03 | 1.17 | -0.0103
CFLNonePGEComExCZ01 | Com-Iltg-dWatt-CFL_OSnone | PGE | Com | Ex | CZ01 | 3.0038 | 0.00061337 | 0 | 2.9636 | 0.00071616 | -0.035858 | 3.0038 | 0.00061337 | 0 | 2.9636 | 0.00071616 | -0.035858 |  | CFL | None | 3000 | 0.613 | 3000 | 0.613 | 0.987 | 1.17 | -0.011938 | 3000 | 0.613 | 3000 | 0.613 | 0.987 | 1.17 | -0.0119
CFLNonePGEComExCZ02 | Com-Iltg-dWatt-CFL_OSnone | PGE | Com | Ex | CZ02 | 3.0625 | 0.00053803 | 0 | 3.2034 | 0.00065491 | -0.022834 | 3.0625 | 0.00053803 | 0 | 3.2034 | 0.00065491 | -0.022834 |  | CFL | None | 3060 | 0.538 | 3060 | 0.538 | 1.05 | 1.22 | -0.0074561 | 3060 | 0.538 | 3060 | 0.538 | 1.05 | 1.22 | -0.00746
CFLNonePGEComExCZ03 | Com-Iltg-dWatt-CFL_OSnone | PGE | Com | Ex | CZ03 | 3.0067 | 0.00055203 | 0 | 3.1729 | 0.00067498 | -0.020746 | 3.0067 | 0.00055203 | 0 | 3.1729 | 0.00067498 | -0.020746 |  | CFL | None | 3010 | 0.552 | 3010 | 0.552 | 1.06 | 1.22 | -0.0069001 | 3010 | 0.552 | 3010 | 0.552 | 1.06 | 1.22 | -0.0069
CFLNonePGEComExCZ04 | Com-Iltg-dWatt-CFL_OSnone | PGE | Com | Ex | CZ04 | 3.0181 | 0.00062097 | 0 | 3.2261 | 0.00075926 | -0.016885 | 3.0181 | 0.00062097 | 0 | 3.2261 | 0.00075926 | -0.016885 |  | CFL | None | 3020 | 0.621 | 3020 | 0.621 | 1.07 | 1.22 | -0.0055947 | 3020 | 0.621 | 3020 | 0.621 | 1.07 | 1.22 | -0.00559
CFLNonePGEComExCZ05 | Com-Iltg-dWatt-CFL_OSnone | PGE | Com | Ex | CZ05 | 2.9267 | 0.00058612 | 0 | 3.0907 | 0.00070376 | -0.020939 | 2.9267 | 0.00058612 | 0 | 3.0907 | 0.00070376 | -0.020939 |  | CFL | None | 2930 | 0.586 | 2930 | 0.586 | 1.06 | 1.2 | -0.0071547 | 2930 | 0.586 | 2930 | 0.586 | 1.06 | 1.2 | -0.00715
CFLNonePGEComExCZ11 | Com-Iltg-dWatt-CFL_OSnone | PGE | Com | Ex | CZ11 | 3.0747 | 0.00053392 | 0 | 3.2716 | 0.00064729 | -0.020706 | 3.0747 | 0.00053392 | 0 | 3.2716 | 0.00064729 | -0.020706 |  | CFL | None | 3070 | 0.534 | 3070 | 0.534 | 1.06 | 1.21 | -0.0067343 | 3070 | 0.534 | 3070 | 0.534 | 1.06 | 1.21 | -0.00673
CFLNonePGEComExCZ12 | Com-Iltg-dWatt-CFL_OSnone | PGE | Com | Ex | CZ12 | 3.1152 | 0.00055384 | 0 | 3.3066 | 0.00067272 | -0.020356 | 3.1152 | 0.00055384 | 0 | 3.3066 | 0.00067272 | -0.020356 |  | CFL | None | 3120 | 0.554 | 3120 | 0.554 | 1.06 | 1.21 | -0.0065344 | 3120 | 0.554 | 3120 | 0.554 | 1.06 | 1.21 | -0.00653
CFLNonePGEComExCZ13 | Com-Iltg-dWatt-CFL_OSnone | PGE | Com | Ex | CZ13 | 3.1229 | 0.0005416 | 0 | 3.3905 | 0.00065505 | -0.018518 | 3.1229 | 0.0005416 | 0 | 3.3905 | 0.00065505 | -0.018518 |  | CFL | None | 3120 | 0.542 | 3120 | 0.542 | 1.09 | 1.21 | -0.0059299 | 3120 | 0.542 | 3120 | 0.542 | 1.09 | 1.21 | -0.00593
CFLNonePGEComExCZ16 | Com-Iltg-dWatt-CFL_OSnone | PGE | Com | Ex | CZ16 | 2.8458 | 0.00050392 | 0 | 2.7808 | 0.00058854 | -0.030035 | 2.8458 | 0.00050392 | 0 | 2.7808 | 0.00058854 | -0.030035 |  | CFL | None | 2850 | 0.504 | 2850 | 0.504 | 0.977 | 1.17 | -0.010554 | 2850 | 0.504 | 2850 | 0.504 | 0.977 | 1.17 | -0.0106
CFLNonePGEComExIOU | Com-Iltg-dWatt-CFL_OSnone | PGE | Com | Ex | IOU | 3.0495 | 0.00056101 | 0 | 3.2368 | 0.00068281 | -0.020126 | 3.0495 | 0.00056101 | 0 | 3.2368 | 0.00068281 | -0.020126 |  | CFL | None | 3050 | 0.561 | 3050 | 0.561 | 1.06 | 1.22 | -0.0065998 | 3050 | 0.561 | 3050 | 0.561 | 1.06 | 1.22 | -0.0066
CFLNonePGEComNewCZ05 | Com-Iltg-dWatt-CFL_OSnone | PGE | Com | New | CZ05 | 2.8919 | 0.00056886 | 0 | 3.0002 | 0.00068789 | -0.020762 | 2.8919 | 0.00056886 | 0 | 3.0002 | 0.00068789 | -0.020762 |  | CFL | None | 2890 | 0.569 | 2890 | 0.569 | 1.04 | 1.21 | -0.0071793 | 2890 | 0.569 | 2890 | 0.569 | 1.04 | 1.21 | -0.00718
CFLNonePGEComNewCZ11 | Com-Iltg-dWatt-CFL_OSnone | PGE | Com | New | CZ11 | 3.0589 | 0.00054062 | 0 | 3.2431 | 0.00066058 | -0.01996 | 3.0589 | 0.00054062 | 0 | 3.2431 | 0.00066058 | -0.01996 |  | CFL | None | 3060 | 0.541 | 3060 | 0.541 | 1.06 | 1.22 | -0.0065251 | 3060 | 0.541 | 3060 | 0.541 | 1.06 | 1.22 | -0.00653
CFLNonePGEComNewCZ12 | Com-Iltg-dWatt-CFL_OSnone | PGE | Com | New | CZ12 | 3.0998 | 0.00055895 | 0 | 3.2866 | 0.00067892 | -0.019384 | 3.0998 | 0.00055895 | 0 | 3.2866 | 0.00067892 | -0.019384 |  | CFL | None | 3100 | 0.559 | 3100 | 0.559 | 1.06 | 1.21 | -0.0062533 | 3100 | 0.559 | 3100 | 0.559 | 1.06 | 1.21 | -0.00625
CFLNonePGEComNewCZ13 | Com-Iltg-dWatt-CFL_OSnone | PGE | Com | New | CZ13 | 3.1341 | 0.00055223 | 0 | 3.3807 | 0.00066914 | -0.018135 | 3.1341 | 0.00055223 | 0 | 3.3807 | 0.00066914 | -0.018135 |  | CFL | None | 3130 | 0.552 | 3130 | 0.552 | 1.08 | 1.21 | -0.0057863 | 3130 | 0.552 | 3130 | 0.552 | 1.08 | 1.21 | -0.00579
CFLNonePGEComNewCZ16 | Com-Iltg-dWatt-CFL_OSnone | PGE | Com | New | CZ16 | 2.8066 | 0.00050301 | 0 | 2.7368 | 0.00058465 | -0.028132 | 2.8066 | 0.00050301 | 0 | 2.7368 | 0.00058465 | -0.028132 |  | CFL | None | 2810 | 0.503 | 2810 | 0.503 | 0.975 | 1.16 | -0.010023 | 2810 | 0.503 | 2810 | 0.503 | 0.975 | 1.16 | -0.01
CFLNonePGEComNewIOU | Com-Iltg-dWatt-CFL_OSnone | PGE | Com | New | IOU | 3.0788 | 0.00056888 | 0 | 3.2465 | 0.00069068 | -0.019477 | 3.0788 | 0.00056888 | 0 | 3.2465 | 0.00069068 | -0.019477 |  | CFL | None | 3080 | 0.569 | 3080 | 0.569 | 1.05 | 1.21 | -0.0063262 | 3080 | 0.569 | 3080 | 0.569 | 1.05 | 1.21 | -0.00633
CFLNonePGEECCExCZ01 | Com-Iltg-dWatt-CFL_OSnone | PGE | ECC | Ex | CZ01 | 2.42 | 0.000647 | 0 | 2.49 | 0.00079 | -0.0479 | 2.42 | 0.000647 | 0 | 2.49 | 0.00079 | -0.0479 |  | CFL | None | 2420 | 0.647 | 2420 | 0.647 | 1.03 | 1.22 | -0.019793 | 2420 | 0.647 | 2420 | 0.647 | 1.03 | 1.22 | -0.0198
CFLNonePGEECCExCZ02 | Com-Iltg-dWatt-CFL_OSnone | PGE | ECC | Ex | CZ02 | 2.42 | 0.00042 | 0 | 2.63 | 0.000554 | -0.0293 | 2.42 | 0.00042 | 0 | 2.63 | 0.000554 | -0.0293 |  | CFL | None | 2420 | 0.42 | 2420 | 0.42 | 1.09 | 1.32 | -0.012107 | 2420 | 0.42 | 2420 | 0.42 | 1.09 | 1.32 | -0.0121
CFLNonePGEECCExCZ03 | Com-Iltg-dWatt-CFL_OSnone | PGE | ECC | Ex | CZ03 | 2.42 | 0.00042 | 0 | 2.61 | 0.000523 | -0.0305 | 2.42 | 0.00042 | 0 | 2.61 | 0.000523 | -0.0305 |  | CFL | None | 2420 | 0.42 | 2420 | 0.42 | 1.08 | 1.25 | -0.012603 | 2420 | 0.42 | 2420 | 0.42 | 1.08 | 1.25 | -0.0126
CFLNonePGEECCExCZ04 | Com-Iltg-dWatt-CFL_OSnone | PGE | ECC | Ex | CZ04 | 2.42 | 0.000647 | 0 | 2.67 | 0.000841 | -0.0234 | 2.42 | 0.000647 | 0 | 2.67 | 0.000841 | -0.0234 |  | CFL | None | 2420 | 0.647 | 2420 | 0.647 | 1.1 | 1.3 | -0.0096694 | 2420 | 0.647 | 2420 | 0.647 | 1.1 | 1.3 | -0.00967
CFLNonePGEECCExCZ05 | Com-Iltg-dWatt-CFL_OSnone | PGE | ECC | Ex | CZ05 | 2.42 | 0.000647 | 0 | 2.61 | 0.000799 | -0.0298 | 2.42 | 0.000647 | 0 | 2.61 | 0.000799 | -0.0298 |  | CFL | None | 2420 | 0.647 | 2420 | 0.647 | 1.08 | 1.23 | -0.012314 | 2420 | 0.647 | 2420 | 0.647 | 1.08 | 1.23 | -0.0123
CFLNonePGEECCExCZ11 | Com-Iltg-dWatt-CFL_OSnone | PGE | ECC | Ex | CZ11 | 2.42 | 0.00042 | 0 | 2.7 | 0.000523 | -0.0269 | 2.42 | 0.00042 | 0 | 2.7 | 0.000523 | -0.0269 |  | CFL | None | 2420 | 0.42 | 2420 | 0.42 | 1.12 | 1.25 | -0.011116 | 2420 | 0.42 | 2420 | 0.42 | 1.12 | 1.25 | -0.0111
CFLNonePGEECCExCZ12 | Com-Iltg-dWatt-CFL_OSnone | PGE | ECC | Ex | CZ12 | 2.42 | 0.00042 | 0 | 2.68 | 0.000528 | -0.0264 | 2.42 | 0.00042 | 0 | 2.68 | 0.000528 | -0.0264 |  | CFL | None | 2420 | 0.42 | 2420 | 0.42 | 1.11 | 1.26 | -0.010909 | 2420 | 0.42 | 2420 | 0.42 | 1.11 | 1.26 | -0.0109
CFLNonePGEECCExCZ13 | Com-Iltg-dWatt-CFL_OSnone | PGE | ECC | Ex | CZ13 | 2.42 | 0.00042 | 0 | 2.73 | 0.000553 | -0.0233 | 2.42 | 0.00042 | 0 | 2.73 | 0.000553 | -0.0233 |  | CFL | None | 2420 | 0.42 | 2420 | 0.42 | 1.13 | 1.32 | -0.0096281 | 2420 | 0.42 | 2420 | 0.42 | 1.13 | 1.32 | -0.00963
CFLNonePGEECCExCZ16 | Com-Iltg-dWatt-CFL_OSnone | PGE | ECC | Ex | CZ16 | 2.42 | 0.00042 | 0 | 2.55 | 0.000498 | -0.0419 | 2.42 | 0.00042 | 0 | 2.55 | 0.000498 | -0.0419 |  | CFL | None | 2420 | 0.42 | 2420 | 0.42 | 1.05 | 1.19 | -0.017314 | 2420 | 0.42 | 2420 | 0.42 | 1.05 | 1.19 | -0.0173
CFLNonePGEECCExIOU | Com-Iltg-dWatt-CFL_OSnone | PGE | ECC | Ex | IOU | 2.42 | 0.00046328 | 0 | 2.647 | 0.00058624 | -0.028399 | 2.42 | 0.00046328 | 0 | 2.647 | 0.00058624 | -0.028399 |  | CFL | None | 2420 | 0.463 | 2420 | 0.463 | 1.09 | 1.27 | -0.011735 | 2420 | 0.463 | 2420 | 0.463 | 1.09 | 1.27 | -0.0117
CFLNonePGEECCNewCZ01 | Com-Iltg-dWatt-CFL_OSnone | PGE | ECC | New | CZ01 | 2.42 | 0.000647 | 0 | 2.47 | 0.000756 | -0.0494 | 2.42 | 0.000647 | 0 | 2.47 | 0.000756 | -0.0494 |  | CFL | None | 2420 | 0.647 | 2420 | 0.647 | 1.02 | 1.17 | -0.020413 | 2420 | 0.647 | 2420 | 0.647 | 1.02 | 1.17 | -0.0204
CFLNonePGEECCNewCZ02 | Com-Iltg-dWatt-CFL_OSnone | PGE | ECC | New | CZ02 | 2.42 | 0.00042 | 0 | 2.62 | 0.000572 | -0.03 | 2.42 | 0.00042 | 0 | 2.62 | 0.000572 | -0.03 |  | CFL | None | 2420 | 0.42 | 2420 | 0.42 | 1.08 | 1.36 | -0.012397 | 2420 | 0.42 | 2420 | 0.42 | 1.08 | 1.36 | -0.0124
CFLNonePGEECCNewCZ03 | Com-Iltg-dWatt-CFL_OSnone | PGE | ECC | New | CZ03 | 2.42 | 0.00042 | 0 | 2.57 | 0.000551 | -0.0329 | 2.42 | 0.00042 | 0 | 2.57 | 0.000551 | -0.0329 |  | CFL | None | 2420 | 0.42 | 2420 | 0.42 | 1.06 | 1.31 | -0.013595 | 2420 | 0.42 | 2420 | 0.42 | 1.06 | 1.31 | -0.0136
CFLNonePGEECCNewCZ04 | Com-Iltg-dWatt-CFL_OSnone | PGE | ECC | New | CZ04 | 2.42 | 0.000647 | 0 | 2.65 | 0.000822 | -0.0242 | 2.42 | 0.000647 | 0 | 2.65 | 0.000822 | -0.0242 |  | CFL | None | 2420 | 0.647 | 2420 | 0.647 | 1.1 | 1.27 | -0.01 | 2420 | 0.647 | 2420 | 0.647 | 1.1 | 1.27 | -0.01
CFLNonePGEECCNewCZ05 | Com-Iltg-dWatt-CFL_OSnone | PGE | ECC | New | CZ05 | 2.42 | 0.000647 | 0 | 2.57 | 0.000794 | -0.032 | 2.42 | 0.000647 | 0 | 2.57 | 0.000794 | -0.032 |  | CFL | None | 2420 | 0.647 | 2420 | 0.647 | 1.06 | 1.23 | -0.013223 | 2420 | 0.647 | 2420 | 0.647 | 1.06 | 1.23 | -0.0132
CFLNonePGEECCNewCZ11 | Com-Iltg-dWatt-CFL_OSnone | PGE | ECC | New | CZ11 | 2.42 | 0.00042 | 0 | 2.69 | 0.000561 | -0.0252 | 2.42 | 0.00042 | 0 | 2.69 | 0.000561 | -0.0252 |  | CFL | None | 2420 | 0.42 | 2420 | 0.42 | 1.11 | 1.34 | -0.010413 | 2420 | 0.42 | 2420 | 0.42 | 1.11 | 1.34 | -0.0104
CFLNonePGEECCNewCZ12 | Com-Iltg-dWatt-CFL_OSnone | PGE | ECC | New | CZ12 | 2.42 | 0.00042 | 0 | 2.67 | 0.000573 | -0.0257 | 2.42 | 0.00042 | 0 | 2.67 | 0.000573 | -0.0257 |  | CFL | None | 2420 | 0.42 | 2420 | 0.42 | 1.1 | 1.36 | -0.01062 | 2420 | 0.42 | 2420 | 0.42 | 1.1 | 1.36 | -0.0106
CFLNonePGEECCNewCZ13 | Com-Iltg-dWatt-CFL_OSnone | PGE | ECC | New | CZ13 | 2.42 | 0.00042 | 0 | 2.71 | 0.000567 | -0.0219 | 2.42 | 0.00042 | 0 | 2.71 | 0.000567 | -0.0219 |  | CFL | None | 2420 | 0.42 | 2420 | 0.42 | 1.12 | 1.35 | -0.0090496 | 2420 | 0.42 | 2420 | 0.42 | 1.12 | 1.35 | -0.00905
CFLNonePGEECCNewCZ16 | Com-Iltg-dWatt-CFL_OSnone | PGE | ECC | New | CZ16 | 2.42 | 0.00042 | 0 | 2.54 | 0.000544 | -0.0402 | 2.42 | 0.00042 | 0 | 2.54 | 0.000544 | -0.0402 |  | CFL | None | 2420 | 0.42 | 2420 | 0.42 | 1.05 | 1.3 | -0.016612 | 2420 | 0.42 | 2420 | 0.42 | 1.05 | 1.3 | -0.0166
CFLNonePGEECCNewIOU | Com-Iltg-dWatt-CFL_OSnone | PGE | ECC | New | IOU | 2.42 | 0.00046356 | 0 | 2.634 | 0.00060879 | -0.028086 | 2.42 | 0.00046356 | 0 | 2.634 | 0.00060879 | -0.028086 |  | CFL | None | 2420 | 0.464 | 2420 | 0.464 | 1.09 | 1.31 | -0.011606 | 2420 | 0.464 | 2420 | 0.464 | 1.09 | 1.31 | -0.0116
CFLNonePGEEPrExCZ01 | Com-Iltg-dWatt-CFL_OSnone | PGE | EPr | Ex | CZ01 | 2.24 | 0.00063 | 0 | 2.22 | 0.00075 | -0.0403 | 2.24 | 0.00063 | 0 | 2.22 | 0.00075 | -0.0403 |  | CFL | None | 2240 | 0.63 | 2240 | 0.63 | 0.991 | 1.19 | -0.017991 | 2240 | 0.63 | 2240 | 0.63 | 0.991 | 1.19 | -0.018
CFLNonePGEEPrExCZ02 | Com-Iltg-dWatt-CFL_OSnone | PGE | EPr | Ex | CZ02 | 2.24 | 2e-05 | 0 | 2.36 | 2e-05 | -0.0242 | 2.24 | 2e-05 | 0 | 2.36 | 2e-05 | -0.0242 |  | CFL | None | 2240 | 0.02 | 2240 | 0.02 | 1.05 | 1 | -0.010804 | 2240 | 0.02 | 2240 | 0.02 | 1.05 | 1 | -0.0108
CFLNonePGEEPrExCZ03 | Com-Iltg-dWatt-CFL_OSnone | PGE | EPr | Ex | CZ03 | 2.24 | 2e-05 | 0 | 2.38 | 2e-05 | -0.0235 | 2.24 | 2e-05 | 0 | 2.38 | 2e-05 | -0.0235 |  | CFL | None | 2240 | 0.02 | 2240 | 0.02 | 1.06 | 1 | -0.010491 | 2240 | 0.02 | 2240 | 0.02 | 1.06 | 1 | -0.0105
CFLNonePGEEPrExCZ04 | Com-Iltg-dWatt-CFL_OSnone | PGE | EPr | Ex | CZ04 | 2.24 | 0.00063 | 0 | 2.41 | 0.000772 | -0.0186 | 2.24 | 0.00063 | 0 | 2.41 | 0.000772 | -0.0186 |  | CFL | None | 2240 | 0.63 | 2240 | 0.63 | 1.08 | 1.23 | -0.0083036 | 2240 | 0.63 | 2240 | 0.63 | 1.08 | 1.23 | -0.0083
CFLNonePGEEPrExCZ05 | Com-Iltg-dWatt-CFL_OSnone | PGE | EPr | Ex | CZ05 | 2.24 | 0.00063 | 0 | 2.37 | 0.000756 | -0.0222 | 2.24 | 0.00063 | 0 | 2.37 | 0.000756 | -0.0222 |  | CFL | None | 2240 | 0.63 | 2240 | 0.63 | 1.06 | 1.2 | -0.0099107 | 2240 | 0.63 | 2240 | 0.63 | 1.06 | 1.2 | -0.00991
CFLNonePGEEPrExCZ11 | Com-Iltg-dWatt-CFL_OSnone | PGE | EPr | Ex | CZ11 | 2.24 | 2e-05 | 0 | 2.37 | 2e-05 | -0.0222 | 2.24 | 2e-05 | 0 | 2.37 | 2e-05 | -0.0222 |  | CFL | None | 2240 | 0.02 | 2240 | 0.02 | 1.06 | 1 | -0.0099107 | 2240 | 0.02 | 2240 | 0.02 | 1.06 | 1 | -0.00991
CFLNonePGEEPrExCZ12 | Com-Iltg-dWatt-CFL_OSnone | PGE | EPr | Ex | CZ12 | 2.24 | 2e-05 | 0 | 2.37 | 2e-05 | -0.0231 | 2.24 | 2e-05 | 0 | 2.37 | 2e-05 | -0.0231 |  | CFL | None | 2240 | 0.02 | 2240 | 0.02 | 1.06 | 1 | -0.010312 | 2240 | 0.02 | 2240 | 0.02 | 1.06 | 1 | -0.0103
CFLNonePGEEPrExCZ13 | Com-Iltg-dWatt-CFL_OSnone | PGE | EPr | Ex | CZ13 | 2.24 | 2e-05 | 0 | 2.4 | 2e-05 | -0.02 | 2.24 | 2e-05 | 0 | 2.4 | 2e-05 | -0.02 |  | CFL | None | 2240 | 0.02 | 2240 | 0.02 | 1.07 | 1 | -0.0089286 | 2240 | 0.02 | 2240 | 0.02 | 1.07 | 1 | -0.00893
CFLNonePGEEPrExCZ16 | Com-Iltg-dWatt-CFL_OSnone | PGE | EPr | Ex | CZ16 | 2.24 | 2e-05 | 0 | 2.17 | 2e-05 | -0.0399 | 2.24 | 2e-05 | 0 | 2.17 | 2e-05 | -0.0399 |  | CFL | None | 2240 | 0.02 | 2240 | 0.02 | 0.969 | 1 | -0.017813 | 2240 | 0.02 | 2240 | 0.02 | 0.969 | 1 | -0.0178
CFLNonePGEEPrExIOU | Com-Iltg-dWatt-CFL_OSnone | PGE | EPr | Ex | IOU | 2.24 | 0.00012734 | 0 | 2.3796 | 0.00015178 | -0.022378 | 2.24 | 0.00012734 | 0 | 2.3796 | 0.00015178 | -0.022378 |  | CFL | None | 2240 | 0.127 | 2240 | 0.127 | 1.06 | 1.19 | -0.00999 | 2240 | 0.127 | 2240 | 0.127 | 1.06 | 1.19 | -0.00999
CFLNonePGEEPrNewCZ01 | Com-Iltg-dWatt-CFL_OSnone | PGE | EPr | New | CZ01 | 2.24 | 0.00063 | 0 | 2.2 | 0.000725 | -0.0477 | 2.24 | 0.00063 | 0 | 2.2 | 0.000725 | -0.0477 |  | CFL | None | 2240 | 0.63 | 2240 | 0.63 | 0.982 | 1.15 | -0.021295 | 2240 | 0.63 | 2240 | 0.63 | 0.982 | 1.15 | -0.0213
CFLNonePGEEPrNewCZ02 | Com-Iltg-dWatt-CFL_OSnone | PGE | EPr | New | CZ02 | 2.24 | 2e-05 | 0 | 2.33 | 2e-05 | -0.0307 | 2.24 | 2e-05 | 0 | 2.33 | 2e-05 | -0.0307 |  | CFL | None | 2240 | 0.02 | 2240 | 0.02 | 1.04 | 1 | -0.013705 | 2240 | 0.02 | 2240 | 0.02 | 1.04 | 1 | -0.0137
CFLNonePGEEPrNewCZ03 | Com-Iltg-dWatt-CFL_OSnone | PGE | EPr | New | CZ03 | 2.24 | 2e-05 | 0 | 2.31 | 2e-05 | -0.0291 | 2.24 | 2e-05 | 0 | 2.31 | 2e-05 | -0.0291 |  | CFL | None | 2240 | 0.02 | 2240 | 0.02 | 1.03 | 1 | -0.012991 | 2240 | 0.02 | 2240 | 0.02 | 1.03 | 1 | -0.013
CFLNonePGEEPrNewCZ04 | Com-Iltg-dWatt-CFL_OSnone | PGE | EPr | New | CZ04 | 2.24 | 0.00063 | 0 | 2.38 | 0.000818 | -0.0237 | 2.24 | 0.00063 | 0 | 2.38 | 0.000818 | -0.0237 |  | CFL | None | 2240 | 0.63 | 2240 | 0.63 | 1.06 | 1.3 | -0.01058 | 2240 | 0.63 | 2240 | 0.63 | 1.06 | 1.3 | -0.0106
CFLNonePGEEPrNewCZ05 | Com-Iltg-dWatt-CFL_OSnone | PGE | EPr | New | CZ05 | 2.24 | 0.00063 | 0 | 2.33 | 0.000778 | -0.0242 | 2.24 | 0.00063 | 0 | 2.33 | 0.000778 | -0.0242 |  | CFL | None | 2240 | 0.63 | 2240 | 0.63 | 1.04 | 1.23 | -0.010804 | 2240 | 0.63 | 2240 | 0.63 | 1.04 | 1.23 | -0.0108
CFLNonePGEEPrNewCZ11 | Com-Iltg-dWatt-CFL_OSnone | PGE | EPr | New | CZ11 | 2.24 | 2e-05 | 0 | 2.4 | 2e-05 | -0.0269 | 2.24 | 2e-05 | 0 | 2.4 | 2e-05 | -0.0269 |  | CFL | None | 2240 | 0.02 | 2240 | 0.02 | 1.07 | 1 | -0.012009 | 2240 | 0.02 | 2240 | 0.02 | 1.07 | 1 | -0.012
CFLNonePGEEPrNewCZ12 | Com-Iltg-dWatt-CFL_OSnone | PGE | EPr | New | CZ12 | 2.24 | 2e-05 | 0 | 2.38 | 2e-05 | -0.0276 | 2.24 | 2e-05 | 0 | 2.38 | 2e-05 | -0.0276 |  | CFL | None | 2240 | 0.02 | 2240 | 0.02 | 1.06 | 1 | -0.012321 | 2240 | 0.02 | 2240 | 0.02 | 1.06 | 1 | -0.0123
CFLNonePGEEPrNewCZ13 | Com-Iltg-dWatt-CFL_OSnone | PGE | EPr | New | CZ13 | 2.24 | 2e-05 | 0 | 2.42 | 2e-05 | -0.0246 | 2.24 | 2e-05 | 0 | 2.42 | 2e-05 | -0.0246 |  | CFL | None | 2240 | 0.02 | 2240 | 0.02 | 1.08 | 1 | -0.010982 | 2240 | 0.02 | 2240 | 0.02 | 1.08 | 1 | -0.011
CFLNonePGEEPrNewCZ16 | Com-Iltg-dWatt-CFL_OSnone | PGE | EPr | New | CZ16 | 2.24 | 2e-05 | 0 | 2.23 | 2e-05 | -0.0352 | 2.24 | 2e-05 | 0 | 2.23 | 2e-05 | -0.0352 |  | CFL | None | 2240 | 0.02 | 2240 | 0.02 | 0.996 | 1 | -0.015714 | 2240 | 0.02 | 2240 | 0.02 | 0.996 | 1 | -0.0157
CFLNonePGEEPrNewIOU | Com-Iltg-dWatt-CFL_OSnone | PGE | EPr | New | IOU | 2.24 | 0.00010604 | 0 | 2.3718 | 0.00013102 | -0.027066 | 2.24 | 0.00010604 | 0 | 2.3718 | 0.00013102 | -0.027066 |  | CFL | None | 2240 | 0.106 | 2240 | 0.106 | 1.06 | 1.24 | -0.012083 | 2240 | 0.106 | 2240 | 0.106 | 1.06 | 1.24 | -0.0121
CFLNonePGEERCExCZ01 | Com-Iltg-dWatt-CFL_OSnone | PGE | ERC | Ex | CZ01 | 2.6 | 0.000728 | 0 | 2.52 | 0.000864 | -0.0434 | 2.6 | 0.000728 | 0 | 2.52 | 0.000864 | -0.0434 |  | CFL | None | 2600 | 0.728 | 2600 | 0.728 | 0.969 | 1.19 | -0.016692 | 2600 | 0.728 | 2600 | 0.728 | 0.969 | 1.19 | -0.0167
CFLNonePGEERCExCZ02 | Com-Iltg-dWatt-CFL_OSnone | PGE | ERC | Ex | CZ02 | 2.6 | 2.1e-05 | 0 | 2.62 | 2.1e-05 | -0.0312 | 2.6 | 2.1e-05 | 0 | 2.62 | 2.1e-05 | -0.0312 |  | CFL | None | 2600 | 0.021 | 2600 | 0.021 | 1.01 | 1 | -0.012 | 2600 | 0.021 | 2600 | 0.021 | 1.01 | 1 | -0.012
CFLNonePGEERCExCZ03 | Com-Iltg-dWatt-CFL_OSnone | PGE | ERC | Ex | CZ03 | 2.6 | 2.1e-05 | 0 | 2.63 | 2.1e-05 | -0.0291 | 2.6 | 2.1e-05 | 0 | 2.63 | 2.1e-05 | -0.0291 |  | CFL | None | 2600 | 0.021 | 2600 | 0.021 | 1.01 | 1 | -0.011192 | 2600 | 0.021 | 2600 | 0.021 | 1.01 | 1 | -0.0112
CFLNonePGEERCExCZ04 | Com-Iltg-dWatt-CFL_OSnone | PGE | ERC | Ex | CZ04 | 2.6 | 0.000728 | 0 | 2.7 | 0.000874 | -0.0243 | 2.6 | 0.000728 | 0 | 2.7 | 0.000874 | -0.0243 |  | CFL | None | 2600 | 0.728 | 2600 | 0.728 | 1.04 | 1.2 | -0.0093462 | 2600 | 0.728 | 2600 | 0.728 | 1.04 | 1.2 | -0.00935
CFLNonePGEERCExCZ05 | Com-Iltg-dWatt-CFL_OSnone | PGE | ERC | Ex | CZ05 | 2.6 | 0.000728 | 0 | 2.63 | 0.00087 | -0.0288 | 2.6 | 0.000728 | 0 | 2.63 | 0.00087 | -0.0288 |  | CFL | None | 2600 | 0.728 | 2600 | 0.728 | 1.01 | 1.2 | -0.011077 | 2600 | 0.728 | 2600 | 0.728 | 1.01 | 1.2 | -0.0111
CFLNonePGEERCExCZ11 | Com-Iltg-dWatt-CFL_OSnone | PGE | ERC | Ex | CZ11 | 2.6 | 2.1e-05 | 0 | 2.69 | 2.1e-05 | -0.0262 | 2.6 | 2.1e-05 | 0 | 2.69 | 2.1e-05 | -0.0262 |  | CFL | None | 2600 | 0.021 | 2600 | 0.021 | 1.03 | 1 | -0.010077 | 2600 | 0.021 | 2600 | 0.021 | 1.03 | 1 | -0.0101
CFLNonePGEERCExCZ12 | Com-Iltg-dWatt-CFL_OSnone | PGE | ERC | Ex | CZ12 | 2.6 | 2.1e-05 | 0 | 2.68 | 2.1e-05 | -0.0278 | 2.6 | 2.1e-05 | 0 | 2.68 | 2.1e-05 | -0.0278 |  | CFL | None | 2600 | 0.021 | 2600 | 0.021 | 1.03 | 1 | -0.010692 | 2600 | 0.021 | 2600 | 0.021 | 1.03 | 1 | -0.0107
CFLNonePGEERCExCZ13 | Com-Iltg-dWatt-CFL_OSnone | PGE | ERC | Ex | CZ13 | 2.6 | 2.1e-05 | 0 | 2.73 | 2.1e-05 | -0.0248 | 2.6 | 2.1e-05 | 0 | 2.73 | 2.1e-05 | -0.0248 |  | CFL | None | 2600 | 0.021 | 2600 | 0.021 | 1.05 | 1 | -0.0095385 | 2600 | 0.021 | 2600 | 0.021 | 1.05 | 1 | -0.00954
CFLNonePGEERCExCZ16 | Com-Iltg-dWatt-CFL_OSnone | PGE | ERC | Ex | CZ16 | 2.6 | 2.1e-05 | 0 | 2.56 | 2.1e-05 | -0.0418 | 2.6 | 2.1e-05 | 0 | 2.56 | 2.1e-05 | -0.0418 |  | CFL | None | 2600 | 0.021 | 2600 | 0.021 | 0.985 | 1 | -0.016077 | 2600 | 0.021 | 2600 | 0.021 | 0.985 | 1 | -0.0161
CFLNonePGEERCExIOU | Com-Iltg-dWatt-CFL_OSnone | PGE | ERC | Ex | IOU | 2.6 | 0.00014541 | 0 | 2.6694 | 0.00017091 | -0.027622 | 2.6 | 0.00014541 | 0 | 2.6694 | 0.00017091 | -0.027622 |  | CFL | None | 2600 | 0.145 | 2600 | 0.145 | 1.03 | 1.18 | -0.010624 | 2600 | 0.145 | 2600 | 0.145 | 1.03 | 1.18 | -0.0106
CFLNonePGEERCNewCZ01 | Com-Iltg-dWatt-CFL_OSnone | PGE | ERC | New | CZ01 | 2.6 | 0.000728 | 0 | 2.67 | 0.000861 | -0.0511 | 2.6 | 0.000728 | 0 | 2.67 | 0.000861 | -0.0511 |  | CFL | None | 2600 | 0.728 | 2600 | 0.728 | 1.03 | 1.18 | -0.019654 | 2600 | 0.728 | 2600 | 0.728 | 1.03 | 1.18 | -0.0197
CFLNonePGEERCNewCZ02 | Com-Iltg-dWatt-CFL_OSnone | PGE | ERC | New | CZ02 | 2.6 | 2.1e-05 | 0 | 2.79 | 2.1e-05 | -0.0337 | 2.6 | 2.1e-05 | 0 | 2.79 | 2.1e-05 | -0.0337 |  | CFL | None | 2600 | 0.021 | 2600 | 0.021 | 1.07 | 1 | -0.012962 | 2600 | 0.021 | 2600 | 0.021 | 1.07 | 1 | -0.013
CFLNonePGEERCNewCZ03 | Com-Iltg-dWatt-CFL_OSnone | PGE | ERC | New | CZ03 | 2.6 | 2.1e-05 | 0 | 2.79 | 2.1e-05 | -0.0309 | 2.6 | 2.1e-05 | 0 | 2.79 | 2.1e-05 | -0.0309 |  | CFL | None | 2600 | 0.021 | 2600 | 0.021 | 1.07 | 1 | -0.011885 | 2600 | 0.021 | 2600 | 0.021 | 1.07 | 1 | -0.0119
CFLNonePGEERCNewCZ04 | Com-Iltg-dWatt-CFL_OSnone | PGE | ERC | New | CZ04 | 2.6 | 0.000728 | 0 | 2.86 | 0.000919 | -0.0267 | 2.6 | 0.000728 | 0 | 2.86 | 0.000919 | -0.0267 |  | CFL | None | 2600 | 0.728 | 2600 | 0.728 | 1.1 | 1.26 | -0.010269 | 2600 | 0.728 | 2600 | 0.728 | 1.1 | 1.26 | -0.0103
CFLNonePGEERCNewCZ05 | Com-Iltg-dWatt-CFL_OSnone | PGE | ERC | New | CZ05 | 2.6 | 0.000728 | 0 | 2.78 | 0.000933 | -0.0296 | 2.6 | 0.000728 | 0 | 2.78 | 0.000933 | -0.0296 |  | CFL | None | 2600 | 0.728 | 2600 | 0.728 | 1.07 | 1.28 | -0.011385 | 2600 | 0.728 | 2600 | 0.728 | 1.07 | 1.28 | -0.0114
CFLNonePGEERCNewCZ11 | Com-Iltg-dWatt-CFL_OSnone | PGE | ERC | New | CZ11 | 2.6 | 2.1e-05 | 0 | 2.92 | 2.1e-05 | -0.0309 | 2.6 | 2.1e-05 | 0 | 2.92 | 2.1e-05 | -0.0309 |  | CFL | None | 2600 | 0.021 | 2600 | 0.021 | 1.12 | 1 | -0.011885 | 2600 | 0.021 | 2600 | 0.021 | 1.12 | 1 | -0.0119
CFLNonePGEERCNewCZ12 | Com-Iltg-dWatt-CFL_OSnone | PGE | ERC | New | CZ12 | 2.6 | 2.1e-05 | 0 | 2.86 | 2.1e-05 | -0.0314 | 2.6 | 2.1e-05 | 0 | 2.86 | 2.1e-05 | -0.0314 |  | CFL | None | 2600 | 0.021 | 2600 | 0.021 | 1.1 | 1 | -0.012077 | 2600 | 0.021 | 2600 | 0.021 | 1.1 | 1 | -0.0121
CFLNonePGEERCNewCZ13 | Com-Iltg-dWatt-CFL_OSnone | PGE | ERC | New | CZ13 | 2.6 | 2.1e-05 | 0 | 2.91 | 2.1e-05 | -0.0275 | 2.6 | 2.1e-05 | 0 | 2.91 | 2.1e-05 | -0.0275 |  | CFL | None | 2600 | 0.021 | 2600 | 0.021 | 1.12 | 1 | -0.010577 | 2600 | 0.021 | 2600 | 0.021 | 1.12 | 1 | -0.0106
CFLNonePGEERCNewCZ16 | Com-Iltg-dWatt-CFL_OSnone | PGE | ERC | New | CZ16 | 2.6 | 2.1e-05 | 0 | 2.67 | 2.1e-05 | -0.0478 | 2.6 | 2.1e-05 | 0 | 2.67 | 2.1e-05 | -0.0478 |  | CFL | None | 2600 | 0.021 | 2600 | 0.021 | 1.03 | 1 | -0.018385 | 2600 | 0.021 | 2600 | 0.021 | 1.03 | 1 | -0.0184
CFLNonePGEERCNewIOU | Com-Iltg-dWatt-CFL_OSnone | PGE | ERC | New | IOU | 2.6 | 0.00012072 | 0 | 2.8556 | 0.00014733 | -0.030336 | 2.6 | 0.00012072 | 0 | 2.8556 | 0.00014733 | -0.030336 |  | CFL | None | 2600 | 0.121 | 2600 | 0.121 | 1.1 | 1.22 | -0.011668 | 2600 | 0.121 | 2600 | 0.121 | 1.1 | 1.22 | -0.0117
CFLNonePGEESeExCZ01 | Com-Iltg-dWatt-CFL_OSnone | PGE | ESe | Ex | CZ01 | 2.33 | 0.000715 | 0 | 2.26 | 0.000847 | -0.0476 | 2.33 | 0.000715 | 0 | 2.26 | 0.000847 | -0.0476 |  | CFL | None | 2330 | 0.715 | 2330 | 0.715 | 0.97 | 1.18 | -0.020429 | 2330 | 0.715 | 2330 | 0.715 | 0.97 | 1.18 | -0.0204
CFLNonePGEESeExCZ02 | Com-Iltg-dWatt-CFL_OSnone | PGE | ESe | Ex | CZ02 | 2.33 | 2e-05 | 0 | 2.43 | 2e-05 | -0.0298 | 2.33 | 2e-05 | 0 | 2.43 | 2e-05 | -0.0298 |  | CFL | None | 2330 | 0.02 | 2330 | 0.02 | 1.04 | 1 | -0.01279 | 2330 | 0.02 | 2330 | 0.02 | 1.04 | 1 | -0.0128
CFLNonePGEESeExCZ03 | Com-Iltg-dWatt-CFL_OSnone | PGE | ESe | Ex | CZ03 | 2.33 | 2e-05 | 0 | 2.42 | 2e-05 | -0.0308 | 2.33 | 2e-05 | 0 | 2.42 | 2e-05 | -0.0308 |  | CFL | None | 2330 | 0.02 | 2330 | 0.02 | 1.04 | 1 | -0.013219 | 2330 | 0.02 | 2330 | 0.02 | 1.04 | 1 | -0.0132
CFLNonePGEESeExCZ04 | Com-Iltg-dWatt-CFL_OSnone | PGE | ESe | Ex | CZ04 | 2.33 | 0.000715 | 0 | 2.48 | 0.000867 | -0.0238 | 2.33 | 0.000715 | 0 | 2.48 | 0.000867 | -0.0238 |  | CFL | None | 2330 | 0.715 | 2330 | 0.715 | 1.06 | 1.21 | -0.010215 | 2330 | 0.715 | 2330 | 0.715 | 1.06 | 1.21 | -0.0102
CFLNonePGEESeExCZ05 | Com-Iltg-dWatt-CFL_OSnone | PGE | ESe | Ex | CZ05 | 2.33 | 0.000715 | 0 | 2.43 | 0.000847 | -0.0282 | 2.33 | 0.000715 | 0 | 2.43 | 0.000847 | -0.0282 |  | CFL | None | 2330 | 0.715 | 2330 | 0.715 | 1.04 | 1.18 | -0.012103 | 2330 | 0.715 | 2330 | 0.715 | 1.04 | 1.18 | -0.0121
CFLNonePGEESeExCZ11 | Com-Iltg-dWatt-CFL_OSnone | PGE | ESe | Ex | CZ11 | 2.33 | 2e-05 | 0 | 2.48 | 2e-05 | -0.0263 | 2.33 | 2e-05 | 0 | 2.48 | 2e-05 | -0.0263 |  | CFL | None | 2330 | 0.02 | 2330 | 0.02 | 1.06 | 1 | -0.011288 | 2330 | 0.02 | 2330 | 0.02 | 1.06 | 1 | -0.0113
CFLNonePGEESeExCZ12 | Com-Iltg-dWatt-CFL_OSnone | PGE | ESe | Ex | CZ12 | 2.33 | 2e-05 | 0 | 2.46 | 2e-05 | -0.0275 | 2.33 | 2e-05 | 0 | 2.46 | 2e-05 | -0.0275 |  | CFL | None | 2330 | 0.02 | 2330 | 0.02 | 1.06 | 1 | -0.011803 | 2330 | 0.02 | 2330 | 0.02 | 1.06 | 1 | -0.0118
CFLNonePGEESeExCZ13 | Com-Iltg-dWatt-CFL_OSnone | PGE | ESe | Ex | CZ13 | 2.33 | 2e-05 | 0 | 2.5 | 2e-05 | -0.024 | 2.33 | 2e-05 | 0 | 2.5 | 2e-05 | -0.024 |  | CFL | None | 2330 | 0.02 | 2330 | 0.02 | 1.07 | 1 | -0.0103 | 2330 | 0.02 | 2330 | 0.02 | 1.07 | 1 | -0.0103
CFLNonePGEESeExCZ16 | Com-Iltg-dWatt-CFL_OSnone | PGE | ESe | Ex | CZ16 | 2.33 | 2e-05 | 0 | 2.28 | 2e-05 | -0.0413 | 2.33 | 2e-05 | 0 | 2.28 | 2e-05 | -0.0413 |  | CFL | None | 2330 | 0.02 | 2330 | 0.02 | 0.979 | 1 | -0.017725 | 2330 | 0.02 | 2330 | 0.02 | 0.979 | 1 | -0.0177
CFLNonePGEESeExIOU | Com-Iltg-dWatt-CFL_OSnone | PGE | ESe | Ex | IOU | 2.33 | 0.00014229 | 0 | 2.4529 | 0.00016844 | -0.027763 | 2.33 | 0.00014229 | 0 | 2.4529 | 0.00016844 | -0.027763 |  | CFL | None | 2330 | 0.142 | 2330 | 0.142 | 1.05 | 1.18 | -0.011915 | 2330 | 0.142 | 2330 | 0.142 | 1.05 | 1.18 | -0.0119
CFLNonePGEESeNewCZ01 | Com-Iltg-dWatt-CFL_OSnone | PGE | ESe | New | CZ01 | 2.33 | 0.000715 | 0 | 2.3 | 0.000822 | -0.0375 | 2.33 | 0.000715 | 0 | 2.3 | 0.000822 | -0.0375 |  | CFL | None | 2330 | 0.715 | 2330 | 0.715 | 0.987 | 1.15 | -0.016094 | 2330 | 0.715 | 2330 | 0.715 | 0.987 | 1.15 | -0.0161
CFLNonePGEESeNewCZ02 | Com-Iltg-dWatt-CFL_OSnone | PGE | ESe | New | CZ02 | 2.33 | 2e-05 | 0 | 2.45 | 2e-05 | -0.0345 | 2.33 | 2e-05 | 0 | 2.45 | 2e-05 | -0.0345 |  | CFL | None | 2330 | 0.02 | 2330 | 0.02 | 1.05 | 1 | -0.014807 | 2330 | 0.02 | 2330 | 0.02 | 1.05 | 1 | -0.0148
CFLNonePGEESeNewCZ03 | Com-Iltg-dWatt-CFL_OSnone | PGE | ESe | New | CZ03 | 2.33 | 2e-05 | 0 | 2.42 | 2e-05 | -0.0303 | 2.33 | 2e-05 | 0 | 2.42 | 2e-05 | -0.0303 |  | CFL | None | 2330 | 0.02 | 2330 | 0.02 | 1.04 | 1 | -0.013004 | 2330 | 0.02 | 2330 | 0.02 | 1.04 | 1 | -0.013
CFLNonePGEESeNewCZ04 | Com-Iltg-dWatt-CFL_OSnone | PGE | ESe | New | CZ04 | 2.33 | 0.000715 | 0 | 2.49 | 0.000931 | -0.0275 | 2.33 | 0.000715 | 0 | 2.49 | 0.000931 | -0.0275 |  | CFL | None | 2330 | 0.715 | 2330 | 0.715 | 1.07 | 1.3 | -0.011803 | 2330 | 0.715 | 2330 | 0.715 | 1.07 | 1.3 | -0.0118
CFLNonePGEESeNewCZ05 | Com-Iltg-dWatt-CFL_OSnone | PGE | ESe | New | CZ05 | 2.33 | 0.000715 | 0 | 2.41 | 0.000866 | -0.0263 | 2.33 | 0.000715 | 0 | 2.41 | 0.000866 | -0.0263 |  | CFL | None | 2330 | 0.715 | 2330 | 0.715 | 1.03 | 1.21 | -0.011288 | 2330 | 0.715 | 2330 | 0.715 | 1.03 | 1.21 | -0.0113
CFLNonePGEESeNewCZ11 | Com-Iltg-dWatt-CFL_OSnone | PGE | ESe | New | CZ11 | 2.33 | 2e-05 | 0 | 2.54 | 2e-05 | -0.0298 | 2.33 | 2e-05 | 0 | 2.54 | 2e-05 | -0.0298 |  | CFL | None | 2330 | 0.02 | 2330 | 0.02 | 1.09 | 1 | -0.01279 | 2330 | 0.02 | 2330 | 0.02 | 1.09 | 1 | -0.0128
CFLNonePGEESeNewCZ12 | Com-Iltg-dWatt-CFL_OSnone | PGE | ESe | New | CZ12 | 2.33 | 2e-05 | 0 | 2.51 | 2e-05 | -0.0308 | 2.33 | 2e-05 | 0 | 2.51 | 2e-05 | -0.0308 |  | CFL | None | 2330 | 0.02 | 2330 | 0.02 | 1.08 | 1 | -0.013219 | 2330 | 0.02 | 2330 | 0.02 | 1.08 | 1 | -0.0132
CFLNonePGEESeNewCZ13 | Com-Iltg-dWatt-CFL_OSnone | PGE | ESe | New | CZ13 | 2.33 | 2e-05 | 0 | 2.56 | 2e-05 | -0.0277 | 2.33 | 2e-05 | 0 | 2.56 | 2e-05 | -0.0277 |  | CFL | None | 2330 | 0.02 | 2330 | 0.02 | 1.1 | 1 | -0.011888 | 2330 | 0.02 | 2330 | 0.02 | 1.1 | 1 | -0.0119
CFLNonePGEESeNewCZ16 | Com-Iltg-dWatt-CFL_OSnone | PGE | ESe | New | CZ16 | 2.33 | 2e-05 | 0 | 2.33 | 2e-05 | -0.0345 | 2.33 | 2e-05 | 0 | 2.33 | 2e-05 | -0.0345 |  | CFL | None | 2330 | 0.02 | 2330 | 0.02 | 1 | 1 | -0.014807 | 2330 | 0.02 | 2330 | 0.02 | 1 | 1 | -0.0148
CFLNonePGEESeNewIOU | Com-Iltg-dWatt-CFL_OSnone | PGE | ESe | New | IOU | 2.33 | 0.00011803 | 0 | 2.4972 | 0.00014641 | -0.029778 | 2.33 | 0.00011803 | 0 | 2.4972 | 0.00014641 | -0.029778 |  | CFL | None | 2330 | 0.118 | 2330 | 0.118 | 1.07 | 1.24 | -0.01278 | 2330 | 0.118 | 2330 | 0.118 | 1.07 | 1.24 | -0.0128
CFLNonePGEEUnExCZ01 | Com-Iltg-dWatt-CFL_OSnone | PGE | EUn | Ex | CZ01 | 2.37 | 0.000669 | 0 | 2.5 | 0.000821 | -0.0251 | 2.37 | 0.000669 | 0 | 2.5 | 0.000821 | -0.0251 |  | CFL | None | 2370 | 0.669 | 2370 | 0.669 | 1.05 | 1.23 | -0.010591 | 2370 | 0.669 | 2370 | 0.669 | 1.05 | 1.23 | -0.0106
CFLNonePGEEUnExCZ02 | Com-Iltg-dWatt-CFL_OSnone | PGE | EUn | Ex | CZ02 | 2.37 | 0.000439 | 0 | 2.6 | 0.000544 | -0.0184 | 2.37 | 0.000439 | 0 | 2.6 | 0.000544 | -0.0184 |  | CFL | None | 2370 | 0.439 | 2370 | 0.439 | 1.1 | 1.24 | -0.0077637 | 2370 | 0.439 | 2370 | 0.439 | 1.1 | 1.24 | -0.00776
CFLNonePGEEUnExCZ03 | Com-Iltg-dWatt-CFL_OSnone | PGE | EUn | Ex | CZ03 | 2.37 | 0.000439 | 0 | 2.6 | 0.000531 | -0.0176 | 2.37 | 0.000439 | 0 | 2.6 | 0.000531 | -0.0176 |  | CFL | None | 2370 | 0.439 | 2370 | 0.439 | 1.1 | 1.21 | -0.0074262 | 2370 | 0.439 | 2370 | 0.439 | 1.1 | 1.21 | -0.00743
CFLNonePGEEUnExCZ04 | Com-Iltg-dWatt-CFL_OSnone | PGE | EUn | Ex | CZ04 | 2.37 | 0.000669 | 0 | 2.64 | 0.000855 | -0.0143 | 2.37 | 0.000669 | 0 | 2.64 | 0.000855 | -0.0143 |  | CFL | None | 2370 | 0.669 | 2370 | 0.669 | 1.11 | 1.28 | -0.0060338 | 2370 | 0.669 | 2370 | 0.669 | 1.11 | 1.28 | -0.00603
CFLNonePGEEUnExCZ05 | Com-Iltg-dWatt-CFL_OSnone | PGE | EUn | Ex | CZ05 | 2.37 | 0.000669 | 0 | 2.59 | 0.000814 | -0.0168 | 2.37 | 0.000669 | 0 | 2.59 | 0.000814 | -0.0168 |  | CFL | None | 2370 | 0.669 | 2370 | 0.669 | 1.09 | 1.22 | -0.0070886 | 2370 | 0.669 | 2370 | 0.669 | 1.09 | 1.22 | -0.00709
CFLNonePGEEUnExCZ11 | Com-Iltg-dWatt-CFL_OSnone | PGE | EUn | Ex | CZ11 | 2.37 | 0.000439 | 0 | 2.65 | 0.000553 | -0.0165 | 2.37 | 0.000439 | 0 | 2.65 | 0.000553 | -0.0165 |  | CFL | None | 2370 | 0.439 | 2370 | 0.439 | 1.12 | 1.26 | -0.006962 | 2370 | 0.439 | 2370 | 0.439 | 1.12 | 1.26 | -0.00696
CFLNonePGEEUnExCZ12 | Com-Iltg-dWatt-CFL_OSnone | PGE | EUn | Ex | CZ12 | 2.37 | 0.000439 | 0 | 2.64 | 0.000549 | -0.0164 | 2.37 | 0.000439 | 0 | 2.64 | 0.000549 | -0.0164 |  | CFL | None | 2370 | 0.439 | 2370 | 0.439 | 1.11 | 1.25 | -0.0069198 | 2370 | 0.439 | 2370 | 0.439 | 1.11 | 1.25 | -0.00692
CFLNonePGEEUnExCZ13 | Com-Iltg-dWatt-CFL_OSnone | PGE | EUn | Ex | CZ13 | 2.37 | 0.000439 | 0 | 2.67 | 0.000558 | -0.0144 | 2.37 | 0.000439 | 0 | 2.67 | 0.000558 | -0.0144 |  | CFL | None | 2370 | 0.439 | 2370 | 0.439 | 1.13 | 1.27 | -0.0060759 | 2370 | 0.439 | 2370 | 0.439 | 1.13 | 1.27 | -0.00608
CFLNonePGEEUnExCZ16 | Com-Iltg-dWatt-CFL_OSnone | PGE | EUn | Ex | CZ16 | 2.37 | 0.000439 | 0 | 2.52 | 0.00053 | -0.0258 | 2.37 | 0.000439 | 0 | 2.52 | 0.00053 | -0.0258 |  | CFL | None | 2370 | 0.439 | 2370 | 0.439 | 1.06 | 1.21 | -0.010886 | 2370 | 0.439 | 2370 | 0.439 | 1.06 | 1.21 | -0.0109
CFLNonePGEEUnExIOU | Com-Iltg-dWatt-CFL_OSnone | PGE | EUn | Ex | IOU | 2.37 | 0.00048286 | 0 | 2.6192 | 0.00059792 | -0.016846 | 2.37 | 0.00048286 | 0 | 2.6192 | 0.00059792 | -0.016846 |  | CFL | None | 2370 | 0.483 | 2370 | 0.483 | 1.11 | 1.24 | -0.0071079 | 2370 | 0.483 | 2370 | 0.483 | 1.11 | 1.24 | -0.00711
CFLNonePGEEUnNewCZ01 | Com-Iltg-dWatt-CFL_OSnone | PGE | EUn | New | CZ01 | 2.37 | 0.000669 | 0 | 2.48 | 0.000785 | -0.0228 | 2.37 | 0.000669 | 0 | 2.48 | 0.000785 | -0.0228 |  | CFL | None | 2370 | 0.669 | 2370 | 0.669 | 1.05 | 1.17 | -0.0096203 | 2370 | 0.669 | 2370 | 0.669 | 1.05 | 1.17 | -0.00962
CFLNonePGEEUnNewCZ02 | Com-Iltg-dWatt-CFL_OSnone | PGE | EUn | New | CZ02 | 2.37 | 0.000439 | 0 | 2.62 | 0.000572 | -0.0184 | 2.37 | 0.000439 | 0 | 2.62 | 0.000572 | -0.0184 |  | CFL | None | 2370 | 0.439 | 2370 | 0.439 | 1.11 | 1.3 | -0.0077637 | 2370 | 0.439 | 2370 | 0.439 | 1.11 | 1.3 | -0.00776
CFLNonePGEEUnNewCZ03 | Com-Iltg-dWatt-CFL_OSnone | PGE | EUn | New | CZ03 | 2.37 | 0.000439 | 0 | 2.57 | 0.000554 | -0.0136 | 2.37 | 0.000439 | 0 | 2.57 | 0.000554 | -0.0136 |  | CFL | None | 2370 | 0.439 | 2370 | 0.439 | 1.08 | 1.26 | -0.0057384 | 2370 | 0.439 | 2370 | 0.439 | 1.08 | 1.26 | -0.00574
CFLNonePGEEUnNewCZ04 | Com-Iltg-dWatt-CFL_OSnone | PGE | EUn | New | CZ04 | 2.37 | 0.000669 | 0 | 2.64 | 0.00084 | -0.0122 | 2.37 | 0.000669 | 0 | 2.64 | 0.00084 | -0.0122 |  | CFL | None | 2370 | 0.669 | 2370 | 0.669 | 1.11 | 1.26 | -0.0051477 | 2370 | 0.669 | 2370 | 0.669 | 1.11 | 1.26 | -0.00515
CFLNonePGEEUnNewCZ05 | Com-Iltg-dWatt-CFL_OSnone | PGE | EUn | New | CZ05 | 2.37 | 0.000669 | 0 | 2.57 | 0.000805 | -0.0148 | 2.37 | 0.000669 | 0 | 2.57 | 0.000805 | -0.0148 |  | CFL | None | 2370 | 0.669 | 2370 | 0.669 | 1.08 | 1.2 | -0.0062447 | 2370 | 0.669 | 2370 | 0.669 | 1.08 | 1.2 | -0.00624
CFLNonePGEEUnNewCZ11 | Com-Iltg-dWatt-CFL_OSnone | PGE | EUn | New | CZ11 | 2.37 | 0.000439 | 0 | 2.69 | 0.000569 | -0.0137 | 2.37 | 0.000439 | 0 | 2.69 | 0.000569 | -0.0137 |  | CFL | None | 2370 | 0.439 | 2370 | 0.439 | 1.14 | 1.3 | -0.0057806 | 2370 | 0.439 | 2370 | 0.439 | 1.14 | 1.3 | -0.00578
CFLNonePGEEUnNewCZ12 | Com-Iltg-dWatt-CFL_OSnone | PGE | EUn | New | CZ12 | 2.37 | 0.000439 | 0 | 2.67 | 0.000571 | -0.0149 | 2.37 | 0.000439 | 0 | 2.67 | 0.000571 | -0.0149 |  | CFL | None | 2370 | 0.439 | 2370 | 0.439 | 1.13 | 1.3 | -0.0062869 | 2370 | 0.439 | 2370 | 0.439 | 1.13 | 1.3 | -0.00629
CFLNonePGEEUnNewCZ13 | Com-Iltg-dWatt-CFL_OSnone | PGE | EUn | New | CZ13 | 2.37 | 0.000439 | 0 | 2.74 | 0.000595 | -0.0154 | 2.37 | 0.000439 | 0 | 2.74 | 0.000595 | -0.0154 |  | CFL | None | 2370 | 0.439 | 2370 | 0.439 | 1.16 | 1.36 | -0.0064979 | 2370 | 0.439 | 2370 | 0.439 | 1.16 | 1.36 | -0.0065
CFLNonePGEEUnNewCZ16 | Com-Iltg-dWatt-CFL_OSnone | PGE | EUn | New | CZ16 | 2.37 | 0.000439 | 0 | 2.52 | 0.000548 | -0.0246 | 2.37 | 0.000439 | 0 | 2.52 | 0.000548 | -0.0246 |  | CFL | None | 2370 | 0.439 | 2370 | 0.439 | 1.06 | 1.25 | -0.01038 | 2370 | 0.439 | 2370 | 0.439 | 1.06 | 1.25 | -0.0104
CFLNonePGEEUnNewIOU | Com-Iltg-dWatt-CFL_OSnone | PGE | EUn | New | IOU | 2.37 | 0.00048313 | 0 | 2.6384 | 0.00061823 | -0.014612 | 2.37 | 0.00048313 | 0 | 2.6384 | 0.00061823 | -0.014612 |  | CFL | None | 2370 | 0.483 | 2370 | 0.483 | 1.11 | 1.28 | -0.0061656 | 2370 | 0.483 | 2370 | 0.483 | 1.11 | 1.28 | -0.00617
CFLNonePGEGroExCZ01 | Com-Iltg-dWatt-CFL_OSnone | PGE | Gro | Ex | CZ01 | 3.89 | 0.000495 | 0 | 3.13 | 0.000462 | -0.0684 | 3.89 | 0.000495 | 0 | 3.13 | 0.000462 | -0.0684 |  | CFL | None | 3890 | 0.495 | 3890 | 0.495 | 0.805 | 0.933 | -0.017584 | 3890 | 0.495 | 3890 | 0.495 | 0.805 | 0.933 | -0.0176
CFLNonePGEGroExCZ02 | Com-Iltg-dWatt-CFL_OSnone | PGE | Gro | Ex | CZ02 | 3.89 | 0.000495 | 0 | 3.52 | 0.000663 | -0.0533 | 3.89 | 0.000495 | 0 | 3.52 | 0.000663 | -0.0533 |  | CFL | None | 3890 | 0.495 | 3890 | 0.495 | 0.905 | 1.34 | -0.013702 | 3890 | 0.495 | 3890 | 0.495 | 0.905 | 1.34 | -0.0137
CFLNonePGEGroExCZ03 | Com-Iltg-dWatt-CFL_OSnone | PGE | Gro | Ex | CZ03 | 3.89 | 0.000495 | 0 | 3.36 | 0.000625 | -0.0607 | 3.89 | 0.000495 | 0 | 3.36 | 0.000625 | -0.0607 |  | CFL | None | 3890 | 0.495 | 3890 | 0.495 | 0.864 | 1.26 | -0.015604 | 3890 | 0.495 | 3890 | 0.495 | 0.864 | 1.26 | -0.0156
CFLNonePGEGroExCZ04 | Com-Iltg-dWatt-CFL_OSnone | PGE | Gro | Ex | CZ04 | 3.89 | 0.000495 | 0 | 3.59 | 0.000629 | -0.0513 | 3.89 | 0.000495 | 0 | 3.59 | 0.000629 | -0.0513 |  | CFL | None | 3890 | 0.495 | 3890 | 0.495 | 0.923 | 1.27 | -0.013188 | 3890 | 0.495 | 3890 | 0.495 | 0.923 | 1.27 | -0.0132
CFLNonePGEGroExCZ05 | Com-Iltg-dWatt-CFL_OSnone | PGE | Gro | Ex | CZ05 | 3.89 | 0.000495 | 0 | 3.33 | 0.000607 | -0.0607 | 3.89 | 0.000495 | 0 | 3.33 | 0.000607 | -0.0607 |  | CFL | None | 3890 | 0.495 | 3890 | 0.495 | 0.856 | 1.23 | -0.015604 | 3890 | 0.495 | 3890 | 0.495 | 0.856 | 1.23 | -0.0156
CFLNonePGEGroExCZ11 | Com-Iltg-dWatt-CFL_OSnone | PGE | Gro | Ex | CZ11 | 3.89 | 0.000495 | 0 | 3.81 | 0.00066 | -0.0436 | 3.89 | 0.000495 | 0 | 3.81 | 0.00066 | -0.0436 |  | CFL | None | 3890 | 0.495 | 3890 | 0.495 | 0.979 | 1.33 | -0.011208 | 3890 | 0.495 | 3890 | 0.495 | 0.979 | 1.33 | -0.0112
CFLNonePGEGroExCZ12 | Com-Iltg-dWatt-CFL_OSnone | PGE | Gro | Ex | CZ12 | 3.89 | 0.000495 | 0 | 3.7 | 0.000655 | -0.0474 | 3.89 | 0.000495 | 0 | 3.7 | 0.000655 | -0.0474 |  | CFL | None | 3890 | 0.495 | 3890 | 0.495 | 0.951 | 1.32 | -0.012185 | 3890 | 0.495 | 3890 | 0.495 | 0.951 | 1.32 | -0.0122
CFLNonePGEGroExCZ13 | Com-Iltg-dWatt-CFL_OSnone | PGE | Gro | Ex | CZ13 | 3.89 | 0.000495 | 0 | 3.84 | 0.000655 | -0.0412 | 3.89 | 0.000495 | 0 | 3.84 | 0.000655 | -0.0412 |  | CFL | None | 3890 | 0.495 | 3890 | 0.495 | 0.987 | 1.32 | -0.010591 | 3890 | 0.495 | 3890 | 0.495 | 0.987 | 1.32 | -0.0106
CFLNonePGEGroExCZ16 | Com-Iltg-dWatt-CFL_OSnone | PGE | Gro | Ex | CZ16 | 3.89 | 0.000495 | 0 | 3.35 | 0.00062 | -0.0564 | 3.89 | 0.000495 | 0 | 3.35 | 0.00062 | -0.0564 |  | CFL | None | 3890 | 0.495 | 3890 | 0.495 | 0.861 | 1.25 | -0.014499 | 3890 | 0.495 | 3890 | 0.495 | 0.861 | 1.25 | -0.0145
CFLNonePGEGroExIOU | Com-Iltg-dWatt-CFL_OSnone | PGE | Gro | Ex | IOU | 3.89 | 0.000495 | 0 | 3.5875 | 0.00064058 | -0.051474 | 3.89 | 0.000495 | 0 | 3.5875 | 0.00064058 | -0.051474 |  | CFL | None | 3890 | 0.495 | 3890 | 0.495 | 0.922 | 1.29 | -0.013232 | 3890 | 0.495 | 3890 | 0.495 | 0.922 | 1.29 | -0.0132
CFLNonePGEGroNewCZ01 | Com-Iltg-dWatt-CFL_OSnone | PGE | Gro | New | CZ01 | 3.89 | 0.000495 | 0 | 3.22 | 0.000583 | -0.0727 | 3.89 | 0.000495 | 0 | 3.22 | 0.000583 | -0.0727 |  | CFL | None | 3890 | 0.495 | 3890 | 0.495 | 0.828 | 1.18 | -0.018689 | 3890 | 0.495 | 3890 | 0.495 | 0.828 | 1.18 | -0.0187
CFLNonePGEGroNewCZ02 | Com-Iltg-dWatt-CFL_OSnone | PGE | Gro | New | CZ02 | 3.89 | 0.000495 | 0 | 3.66 | 0.000688 | -0.0533 | 3.89 | 0.000495 | 0 | 3.66 | 0.000688 | -0.0533 |  | CFL | None | 3890 | 0.495 | 3890 | 0.495 | 0.941 | 1.39 | -0.013702 | 3890 | 0.495 | 3890 | 0.495 | 0.941 | 1.39 | -0.0137
CFLNonePGEGroNewCZ03 | Com-Iltg-dWatt-CFL_OSnone | PGE | Gro | New | CZ03 | 3.89 | 0.000495 | 0 | 3.47 | 0.000647 | -0.0599 | 3.89 | 0.000495 | 0 | 3.47 | 0.000647 | -0.0599 |  | CFL | None | 3890 | 0.495 | 3890 | 0.495 | 0.892 | 1.31 | -0.015398 | 3890 | 0.495 | 3890 | 0.495 | 0.892 | 1.31 | -0.0154
CFLNonePGEGroNewCZ04 | Com-Iltg-dWatt-CFL_OSnone | PGE | Gro | New | CZ04 | 3.89 | 0.000495 | 0 | 3.76 | 0.000646 | -0.049 | 3.89 | 0.000495 | 0 | 3.76 | 0.000646 | -0.049 |  | CFL | None | 3890 | 0.495 | 3890 | 0.495 | 0.967 | 1.31 | -0.012596 | 3890 | 0.495 | 3890 | 0.495 | 0.967 | 1.31 | -0.0126
CFLNonePGEGroNewCZ05 | Com-Iltg-dWatt-CFL_OSnone | PGE | Gro | New | CZ05 | 3.89 | 0.000495 | 0 | 3.47 | 0.000626 | -0.0595 | 3.89 | 0.000495 | 0 | 3.47 | 0.000626 | -0.0595 |  | CFL | None | 3890 | 0.495 | 3890 | 0.495 | 0.892 | 1.26 | -0.015296 | 3890 | 0.495 | 3890 | 0.495 | 0.892 | 1.26 | -0.0153
CFLNonePGEGroNewCZ11 | Com-Iltg-dWatt-CFL_OSnone | PGE | Gro | New | CZ11 | 3.89 | 0.000495 | 0 | 3.94 | 0.000693 | -0.0424 | 3.89 | 0.000495 | 0 | 3.94 | 0.000693 | -0.0424 |  | CFL | None | 3890 | 0.495 | 3890 | 0.495 | 1.01 | 1.4 | -0.0109 | 3890 | 0.495 | 3890 | 0.495 | 1.01 | 1.4 | -0.0109
CFLNonePGEGroNewCZ12 | Com-Iltg-dWatt-CFL_OSnone | PGE | Gro | New | CZ12 | 3.89 | 0.000495 | 0 | 3.85 | 0.000694 | -0.0471 | 3.89 | 0.000495 | 0 | 3.85 | 0.000694 | -0.0471 |  | CFL | None | 3890 | 0.495 | 3890 | 0.495 | 0.99 | 1.4 | -0.012108 | 3890 | 0.495 | 3890 | 0.495 | 0.99 | 1.4 | -0.0121
CFLNonePGEGroNewCZ13 | Com-Iltg-dWatt-CFL_OSnone | PGE | Gro | New | CZ13 | 3.89 | 0.000495 | 0 | 3.97 | 0.000672 | -0.0401 | 3.89 | 0.000495 | 0 | 3.97 | 0.000672 | -0.0401 |  | CFL | None | 3890 | 0.495 | 3890 | 0.495 | 1.02 | 1.36 | -0.010308 | 3890 | 0.495 | 3890 | 0.495 | 1.02 | 1.36 | -0.0103
CFLNonePGEGroNewCZ16 | Com-Iltg-dWatt-CFL_OSnone | PGE | Gro | New | CZ16 | 3.89 | 0.000495 | 0 | 3.51 | 0.00063 | -0.0552 | 3.89 | 0.000495 | 0 | 3.51 | 0.00063 | -0.0552 |  | CFL | None | 3890 | 0.495 | 3890 | 0.495 | 0.902 | 1.27 | -0.01419 | 3890 | 0.495 | 3890 | 0.495 | 0.902 | 1.27 | -0.0142
CFLNonePGEGroNewIOU | Com-Iltg-dWatt-CFL_OSnone | PGE | Gro | New | IOU | 3.89 | 0.000495 | 0 | 3.7618 | 0.00067027 | -0.049133 | 3.89 | 0.000495 | 0 | 3.7618 | 0.00067027 | -0.049133 |  | CFL | None | 3890 | 0.495 | 3890 | 0.495 | 0.967 | 1.35 | -0.012631 | 3890 | 0.495 | 3890 | 0.495 | 0.967 | 1.35 | -0.0126
CFLNonePGEHspExCZ01 | Com-Iltg-dWatt-CFL_OSnone | PGE | Hsp | Ex | CZ01 | 4.2 | 0.000717 | 0 | 4.5 | 0.000822 | -0.0369 | 4.2 | 0.000717 | 0 | 4.5 | 0.000822 | -0.0369 |  | CFL | None | 4200 | 0.717 | 4200 | 0.717 | 1.07 | 1.15 | -0.0087857 | 4200 | 0.717 | 4200 | 0.717 | 1.07 | 1.15 | -0.00879
CFLNonePGEHspExCZ02 | Com-Iltg-dWatt-CFL_OSnone | PGE | Hsp | Ex | CZ02 | 4.2 | 0.000717 | 0 | 4.62 | 0.000881 | -0.0288 | 4.2 | 0.000717 | 0 | 4.62 | 0.000881 | -0.0288 |  | CFL | None | 4200 | 0.717 | 4200 | 0.717 | 1.1 | 1.23 | -0.0068571 | 4200 | 0.717 | 4200 | 0.717 | 1.1 | 1.23 | -0.00686
CFLNonePGEHspExCZ03 | Com-Iltg-dWatt-CFL_OSnone | PGE | Hsp | Ex | CZ03 | 4.2 | 0.000717 | 0 | 4.65 | 0.00086 | -0.0273 | 4.2 | 0.000717 | 0 | 4.65 | 0.00086 | -0.0273 |  | CFL | None | 4200 | 0.717 | 4200 | 0.717 | 1.11 | 1.2 | -0.0065 | 4200 | 0.717 | 4200 | 0.717 | 1.11 | 1.2 | -0.0065
CFLNonePGEHspExCZ04 | Com-Iltg-dWatt-CFL_OSnone | PGE | Hsp | Ex | CZ04 | 4.2 | 0.000717 | 0 | 4.65 | 0.000874 | -0.026 | 4.2 | 0.000717 | 0 | 4.65 | 0.000874 | -0.026 |  | CFL | None | 4200 | 0.717 | 4200 | 0.717 | 1.11 | 1.22 | -0.0061905 | 4200 | 0.717 | 4200 | 0.717 | 1.11 | 1.22 | -0.00619
CFLNonePGEHspExCZ05 | Com-Iltg-dWatt-CFL_OSnone | PGE | Hsp | Ex | CZ05 | 4.2 | 0.000717 | 0 | 4.57 | 0.000845 | -0.029 | 4.2 | 0.000717 | 0 | 4.57 | 0.000845 | -0.029 |  | CFL | None | 4200 | 0.717 | 4200 | 0.717 | 1.09 | 1.18 | -0.0069048 | 4200 | 0.717 | 4200 | 0.717 | 1.09 | 1.18 | -0.0069
CFLNonePGEHspExCZ11 | Com-Iltg-dWatt-CFL_OSnone | PGE | Hsp | Ex | CZ11 | 4.2 | 0.000717 | 0 | 4.67 | 0.000887 | -0.0271 | 4.2 | 0.000717 | 0 | 4.67 | 0.000887 | -0.0271 |  | CFL | None | 4200 | 0.717 | 4200 | 0.717 | 1.11 | 1.24 | -0.0064524 | 4200 | 0.717 | 4200 | 0.717 | 1.11 | 1.24 | -0.00645
CFLNonePGEHspExCZ12 | Com-Iltg-dWatt-CFL_OSnone | PGE | Hsp | Ex | CZ12 | 4.2 | 0.000717 | 0 | 4.66 | 0.000885 | -0.0264 | 4.2 | 0.000717 | 0 | 4.66 | 0.000885 | -0.0264 |  | CFL | None | 4200 | 0.717 | 4200 | 0.717 | 1.11 | 1.23 | -0.0062857 | 4200 | 0.717 | 4200 | 0.717 | 1.11 | 1.23 | -0.00629
CFLNonePGEHspExCZ13 | Com-Iltg-dWatt-CFL_OSnone | PGE | Hsp | Ex | CZ13 | 4.2 | 0.000717 | 0 | 4.69 | 0.000883 | -0.0255 | 4.2 | 0.000717 | 0 | 4.69 | 0.000883 | -0.0255 |  | CFL | None | 4200 | 0.717 | 4200 | 0.717 | 1.12 | 1.23 | -0.0060714 | 4200 | 0.717 | 4200 | 0.717 | 1.12 | 1.23 | -0.00607
CFLNonePGEHspExCZ16 | Com-Iltg-dWatt-CFL_OSnone | PGE | Hsp | Ex | CZ16 | 4.2 | 0.000717 | 0 | 4.42 | 0.000857 | -0.0418 | 4.2 | 0.000717 | 0 | 4.42 | 0.000857 | -0.0418 |  | CFL | None | 4200 | 0.717 | 4200 | 0.717 | 1.05 | 1.2 | -0.0099524 | 4200 | 0.717 | 4200 | 0.717 | 1.05 | 1.2 | -0.00995
CFLNonePGEHspExIOU | Com-Iltg-dWatt-CFL_OSnone | PGE | Hsp | Ex | IOU | 4.2 | 0.000717 | 0 | 4.6531 | 0.00087415 | -0.026965 | 4.2 | 0.000717 | 0 | 4.6531 | 0.00087415 | -0.026965 |  | CFL | None | 4200 | 0.717 | 4200 | 0.717 | 1.11 | 1.22 | -0.0064202 | 4200 | 0.717 | 4200 | 0.717 | 1.11 | 1.22 | -0.00642
CFLNonePGEHspNewCZ01 | Com-Iltg-dWatt-CFL_OSnone | PGE | Hsp | New | CZ01 | 4.2 | 0.000717 | 0 | 4.3 | 0.000783 | -0.0391 | 4.2 | 0.000717 | 0 | 4.3 | 0.000783 | -0.0391 |  | CFL | None | 4200 | 0.717 | 4200 | 0.717 | 1.02 | 1.09 | -0.0093095 | 4200 | 0.717 | 4200 | 0.717 | 1.02 | 1.09 | -0.00931
CFLNonePGEHspNewCZ02 | Com-Iltg-dWatt-CFL_OSnone | PGE | Hsp | New | CZ02 | 4.2 | 0.000717 | 0 | 4.45 | 0.000858 | -0.0313 | 4.2 | 0.000717 | 0 | 4.45 | 0.000858 | -0.0313 |  | CFL | None | 4200 | 0.717 | 4200 | 0.717 | 1.06 | 1.2 | -0.0074524 | 4200 | 0.717 | 4200 | 0.717 | 1.06 | 1.2 | -0.00745
CFLNonePGEHspNewCZ03 | Com-Iltg-dWatt-CFL_OSnone | PGE | Hsp | New | CZ03 | 4.2 | 0.000717 | 0 | 4.43 | 0.000836 | -0.0281 | 4.2 | 0.000717 | 0 | 4.43 | 0.000836 | -0.0281 |  | CFL | None | 4200 | 0.717 | 4200 | 0.717 | 1.05 | 1.17 | -0.0066905 | 4200 | 0.717 | 4200 | 0.717 | 1.05 | 1.17 | -0.00669
CFLNonePGEHspNewCZ04 | Com-Iltg-dWatt-CFL_OSnone | PGE | Hsp | New | CZ04 | 4.2 | 0.000717 | 0 | 4.49 | 0.00085 | -0.0273 | 4.2 | 0.000717 | 0 | 4.49 | 0.00085 | -0.0273 |  | CFL | None | 4200 | 0.717 | 4200 | 0.717 | 1.07 | 1.19 | -0.0065 | 4200 | 0.717 | 4200 | 0.717 | 1.07 | 1.19 | -0.0065
CFLNonePGEHspNewCZ05 | Com-Iltg-dWatt-CFL_OSnone | PGE | Hsp | New | CZ05 | 4.2 | 0.000717 | 0 | 4.41 | 0.000825 | -0.0315 | 4.2 | 0.000717 | 0 | 4.41 | 0.000825 | -0.0315 |  | CFL | None | 4200 | 0.717 | 4200 | 0.717 | 1.05 | 1.15 | -0.0075 | 4200 | 0.717 | 4200 | 0.717 | 1.05 | 1.15 | -0.0075
CFLNonePGEHspNewCZ11 | Com-Iltg-dWatt-CFL_OSnone | PGE | Hsp | New | CZ11 | 4.2 | 0.000717 | 0 | 4.55 | 0.000863 | -0.0291 | 4.2 | 0.000717 | 0 | 4.55 | 0.000863 | -0.0291 |  | CFL | None | 4200 | 0.717 | 4200 | 0.717 | 1.08 | 1.2 | -0.0069286 | 4200 | 0.717 | 4200 | 0.717 | 1.08 | 1.2 | -0.00693
CFLNonePGEHspNewCZ12 | Com-Iltg-dWatt-CFL_OSnone | PGE | Hsp | New | CZ12 | 4.2 | 0.000717 | 0 | 4.52 | 0.000863 | -0.0283 | 4.2 | 0.000717 | 0 | 4.52 | 0.000863 | -0.0283 |  | CFL | None | 4200 | 0.717 | 4200 | 0.717 | 1.08 | 1.2 | -0.0067381 | 4200 | 0.717 | 4200 | 0.717 | 1.08 | 1.2 | -0.00674
CFLNonePGEHspNewCZ13 | Com-Iltg-dWatt-CFL_OSnone | PGE | Hsp | New | CZ13 | 4.2 | 0.000717 | 0 | 4.56 | 0.00086 | -0.0276 | 4.2 | 0.000717 | 0 | 4.56 | 0.00086 | -0.0276 |  | CFL | None | 4200 | 0.717 | 4200 | 0.717 | 1.09 | 1.2 | -0.0065714 | 4200 | 0.717 | 4200 | 0.717 | 1.09 | 1.2 | -0.00657
CFLNonePGEHspNewCZ16 | Com-Iltg-dWatt-CFL_OSnone | PGE | Hsp | New | CZ16 | 4.2 | 0.000717 | 0 | 4.25 | 0.000834 | -0.0466 | 4.2 | 0.000717 | 0 | 4.25 | 0.000834 | -0.0466 |  | CFL | None | 4200 | 0.717 | 4200 | 0.717 | 1.01 | 1.16 | -0.011095 | 4200 | 0.717 | 4200 | 0.717 | 1.01 | 1.16 | -0.0111
CFLNonePGEHspNewIOU | Com-Iltg-dWatt-CFL_OSnone | PGE | Hsp | New | IOU | 4.2 | 0.000717 | 0 | 4.4933 | 0.0008523 | -0.028543 | 4.2 | 0.000717 | 0 | 4.4933 | 0.0008523 | -0.028543 |  | CFL | None | 4200 | 0.717 | 4200 | 0.717 | 1.07 | 1.19 | -0.0067959 | 4200 | 0.717 | 4200 | 0.717 | 1.07 | 1.19 | -0.0068
CFLNonePGEHtlExCZ01 | Com-Iltg-dWatt-CFL_OSnone | PGE | Htl | Ex | CZ01 | 1.67 | 0.000199 | 0 | 1.51 | 0.000238 | -0.00878 | 1.67 | 0.000199 | 0 | 1.51 | 0.000238 | -0.00878 |  | CFL | None | 1670 | 0.199 | 1670 | 0.199 | 0.904 | 1.2 | -0.0052575 | 1670 | 0.199 | 1670 | 0.199 | 0.904 | 1.2 | -0.00526
CFLNonePGEHtlExCZ02 | Com-Iltg-dWatt-CFL_OSnone | PGE | Htl | Ex | CZ02 | 1.67 | 0.000199 | 0 | 1.65 | 0.000247 | -0.00639 | 1.67 | 0.000199 | 0 | 1.65 | 0.000247 | -0.00639 |  | CFL | None | 1670 | 0.199 | 1670 | 0.199 | 0.988 | 1.24 | -0.0038263 | 1670 | 0.199 | 1670 | 0.199 | 0.988 | 1.24 | -0.00383
CFLNonePGEHtlExCZ03 | Com-Iltg-dWatt-CFL_OSnone | PGE | Htl | Ex | CZ03 | 1.67 | 0.000199 | 0 | 1.67 | 0.000244 | -0.00615 | 1.67 | 0.000199 | 0 | 1.67 | 0.000244 | -0.00615 |  | CFL | None | 1670 | 0.199 | 1670 | 0.199 | 1 | 1.23 | -0.0036826 | 1670 | 0.199 | 1670 | 0.199 | 1 | 1.23 | -0.00368
CFLNonePGEHtlExCZ04 | Com-Iltg-dWatt-CFL_OSnone | PGE | Htl | Ex | CZ04 | 1.67 | 0.000199 | 0 | 1.71 | 0.000247 | -0.00517 | 1.67 | 0.000199 | 0 | 1.71 | 0.000247 | -0.00517 |  | CFL | None | 1670 | 0.199 | 1670 | 0.199 | 1.02 | 1.24 | -0.0030958 | 1670 | 0.199 | 1670 | 0.199 | 1.02 | 1.24 | -0.0031
CFLNonePGEHtlExCZ05 | Com-Iltg-dWatt-CFL_OSnone | PGE | Htl | Ex | CZ05 | 1.67 | 0.000199 | 0 | 1.65 | 0.000241 | -0.00637 | 1.67 | 0.000199 | 0 | 1.65 | 0.000241 | -0.00637 |  | CFL | None | 1670 | 0.199 | 1670 | 0.199 | 0.988 | 1.21 | -0.0038144 | 1670 | 0.199 | 1670 | 0.199 | 0.988 | 1.21 | -0.00381
CFLNonePGEHtlExCZ11 | Com-Iltg-dWatt-CFL_OSnone | PGE | Htl | Ex | CZ11 | 1.67 | 0.000199 | 0 | 1.73 | 0.000251 | -0.00558 | 1.67 | 0.000199 | 0 | 1.73 | 0.000251 | -0.00558 |  | CFL | None | 1670 | 0.199 | 1670 | 0.199 | 1.04 | 1.26 | -0.0033413 | 1670 | 0.199 | 1670 | 0.199 | 1.04 | 1.26 | -0.00334
CFLNonePGEHtlExCZ12 | Com-Iltg-dWatt-CFL_OSnone | PGE | Htl | Ex | CZ12 | 1.67 | 0.000199 | 0 | 1.7 | 0.00025 | -0.00568 | 1.67 | 0.000199 | 0 | 1.7 | 0.00025 | -0.00568 |  | CFL | None | 1670 | 0.199 | 1670 | 0.199 | 1.02 | 1.26 | -0.0034012 | 1670 | 0.199 | 1670 | 0.199 | 1.02 | 1.26 | -0.0034
CFLNonePGEHtlExCZ13 | Com-Iltg-dWatt-CFL_OSnone | PGE | Htl | Ex | CZ13 | 1.67 | 0.000199 | 0 | 1.75 | 0.000249 | -0.0052 | 1.67 | 0.000199 | 0 | 1.75 | 0.000249 | -0.0052 |  | CFL | None | 1670 | 0.199 | 1670 | 0.199 | 1.05 | 1.25 | -0.0031138 | 1670 | 0.199 | 1670 | 0.199 | 1.05 | 1.25 | -0.00311
CFLNonePGEHtlExCZ16 | Com-Iltg-dWatt-CFL_OSnone | PGE | Htl | Ex | CZ16 | 1.67 | 0.000199 | 0 | 1.53 | 0.000243 | -0.00886 | 1.67 | 0.000199 | 0 | 1.53 | 0.000243 | -0.00886 |  | CFL | None | 1670 | 0.199 | 1670 | 0.199 | 0.916 | 1.22 | -0.0053054 | 1670 | 0.199 | 1670 | 0.199 | 0.916 | 1.22 | -0.00531
CFLNonePGEHtlExIOU | Com-Iltg-dWatt-CFL_OSnone | PGE | Htl | Ex | IOU | 1.67 | 0.000199 | 0 | 1.6816 | 0.00024583 | -0.0059569 | 1.67 | 0.000199 | 0 | 1.6816 | 0.00024583 | -0.0059569 |  | CFL | None | 1670 | 0.199 | 1670 | 0.199 | 1.01 | 1.24 | -0.003567 | 1670 | 0.199 | 1670 | 0.199 | 1.01 | 1.24 | -0.00357
CFLNonePGEHtlNewCZ01 | Com-Iltg-dWatt-CFL_OSnone | PGE | Htl | New | CZ01 | 1.67 | 0.000199 | 0 | 1.48 | 0.000237 | -0.00971 | 1.67 | 0.000199 | 0 | 1.48 | 0.000237 | -0.00971 |  | CFL | None | 1670 | 0.199 | 1670 | 0.199 | 0.886 | 1.19 | -0.0058144 | 1670 | 0.199 | 1670 | 0.199 | 0.886 | 1.19 | -0.00581
CFLNonePGEHtlNewCZ02 | Com-Iltg-dWatt-CFL_OSnone | PGE | Htl | New | CZ02 | 1.67 | 0.000199 | 0 | 1.63 | 0.000253 | -0.00759 | 1.67 | 0.000199 | 0 | 1.63 | 0.000253 | -0.00759 |  | CFL | None | 1670 | 0.199 | 1670 | 0.199 | 0.976 | 1.27 | -0.0045449 | 1670 | 0.199 | 1670 | 0.199 | 0.976 | 1.27 | -0.00454
CFLNonePGEHtlNewCZ03 | Com-Iltg-dWatt-CFL_OSnone | PGE | Htl | New | CZ03 | 1.67 | 0.000199 | 0 | 1.63 | 0.000245 | -0.00694 | 1.67 | 0.000199 | 0 | 1.63 | 0.000245 | -0.00694 |  | CFL | None | 1670 | 0.199 | 1670 | 0.199 | 0.976 | 1.23 | -0.0041557 | 1670 | 0.199 | 1670 | 0.199 | 0.976 | 1.23 | -0.00416
CFLNonePGEHtlNewCZ04 | Com-Iltg-dWatt-CFL_OSnone | PGE | Htl | New | CZ04 | 1.67 | 0.000199 | 0 | 1.7 | 0.000253 | -0.00599 | 1.67 | 0.000199 | 0 | 1.7 | 0.000253 | -0.00599 |  | CFL | None | 1670 | 0.199 | 1670 | 0.199 | 1.02 | 1.27 | -0.0035868 | 1670 | 0.199 | 1670 | 0.199 | 1.02 | 1.27 | -0.00359
CFLNonePGEHtlNewCZ05 | Com-Iltg-dWatt-CFL_OSnone | PGE | Htl | New | CZ05 | 1.67 | 0.000199 | 0 | 1.62 | 0.000243 | -0.00737 | 1.67 | 0.000199 | 0 | 1.62 | 0.000243 | -0.00737 |  | CFL | None | 1670 | 0.199 | 1670 | 0.199 | 0.97 | 1.22 | -0.0044132 | 1670 | 0.199 | 1670 | 0.199 | 0.97 | 1.22 | -0.00441
CFLNonePGEHtlNewCZ11 | Com-Iltg-dWatt-CFL_OSnone | PGE | Htl | New | CZ11 | 1.67 | 0.000199 | 0 | 1.71 | 0.000254 | -0.00659 | 1.67 | 0.000199 | 0 | 1.71 | 0.000254 | -0.00659 |  | CFL | None | 1670 | 0.199 | 1670 | 0.199 | 1.02 | 1.28 | -0.0039461 | 1670 | 0.199 | 1670 | 0.199 | 1.02 | 1.28 | -0.00395
CFLNonePGEHtlNewCZ12 | Com-Iltg-dWatt-CFL_OSnone | PGE | Htl | New | CZ12 | 1.67 | 0.000199 | 0 | 1.69 | 0.000254 | -0.00665 | 1.67 | 0.000199 | 0 | 1.69 | 0.000254 | -0.00665 |  | CFL | None | 1670 | 0.199 | 1670 | 0.199 | 1.01 | 1.28 | -0.003982 | 1670 | 0.199 | 1670 | 0.199 | 1.01 | 1.28 | -0.00398
CFLNonePGEHtlNewCZ13 | Com-Iltg-dWatt-CFL_OSnone | PGE | Htl | New | CZ13 | 1.67 | 0.000199 | 0 | 1.73 | 0.000252 | -0.00604 | 1.67 | 0.000199 | 0 | 1.73 | 0.000252 | -0.00604 |  | CFL | None | 1670 | 0.199 | 1670 | 0.199 | 1.04 | 1.27 | -0.0036168 | 1670 | 0.199 | 1670 | 0.199 | 1.04 | 1.27 | -0.00362
CFLNonePGEHtlNewCZ16 | Com-Iltg-dWatt-CFL_OSnone | PGE | Htl | New | CZ16 | 1.67 | 0.000199 | 0 | 1.51 | 0.000245 | -0.0109 | 1.67 | 0.000199 | 0 | 1.51 | 0.000245 | -0.0109 |  | CFL | None | 1670 | 0.199 | 1670 | 0.199 | 0.904 | 1.23 | -0.0065269 | 1670 | 0.199 | 1670 | 0.199 | 0.904 | 1.23 | -0.00653
CFLNonePGEHtlNewIOU | Com-Iltg-dWatt-CFL_OSnone | PGE | Htl | New | IOU | 1.67 | 0.000199 | 0 | 1.6647 | 0.00024995 | -0.0068082 | 1.67 | 0.000199 | 0 | 1.6647 | 0.00024995 | -0.0068082 |  | CFL | None | 1670 | 0.199 | 1670 | 0.199 | 0.997 | 1.26 | -0.0040768 | 1670 | 0.199 | 1670 | 0.199 | 0.997 | 1.26 | -0.00408
CFLNonePGEMBTExCZ01 | Com-Iltg-dWatt-CFL_OSnone | PGE | MBT | Ex | CZ01 | 3.09 | 0.00078 | 0 | 3.33 | 0.00092 | -0.00355 | 3.09 | 0.00078 | 0 | 3.33 | 0.00092 | -0.00355 |  | CFL | None | 3090 | 0.78 | 3090 | 0.78 | 1.08 | 1.18 | -0.0011489 | 3090 | 0.78 | 3090 | 0.78 | 1.08 | 1.18 | -0.00115
CFLNonePGEMBTExCZ02 | Com-Iltg-dWatt-CFL_OSnone | PGE | MBT | Ex | CZ02 | 3.09 | 0.00078 | 0 | 3.43 | 0.00092 | -0.00179 | 3.09 | 0.00078 | 0 | 3.43 | 0.00092 | -0.00179 |  | CFL | None | 3090 | 0.78 | 3090 | 0.78 | 1.11 | 1.18 | -0.00057929 | 3090 | 0.78 | 3090 | 0.78 | 1.11 | 1.18 | -0.000579
CFLNonePGEMBTExCZ03 | Com-Iltg-dWatt-CFL_OSnone | PGE | MBT | Ex | CZ03 | 3.09 | 0.00078 | 0 | 3.45 | 0.000923 | -0.00156 | 3.09 | 0.00078 | 0 | 3.45 | 0.000923 | -0.00156 |  | CFL | None | 3090 | 0.78 | 3090 | 0.78 | 1.12 | 1.18 | -0.00050485 | 3090 | 0.78 | 3090 | 0.78 | 1.12 | 1.18 | -0.000505
CFLNonePGEMBTExCZ04 | Com-Iltg-dWatt-CFL_OSnone | PGE | MBT | Ex | CZ04 | 3.09 | 0.00078 | 0 | 3.45 | 0.000934 | -0.0012 | 3.09 | 0.00078 | 0 | 3.45 | 0.000934 | -0.0012 |  | CFL | None | 3090 | 0.78 | 3090 | 0.78 | 1.12 | 1.2 | -0.00038835 | 3090 | 0.78 | 3090 | 0.78 | 1.12 | 1.2 | -0.000388
CFLNonePGEMBTExCZ05 | Com-Iltg-dWatt-CFL_OSnone | PGE | MBT | Ex | CZ05 | 3.09 | 0.00078 | 0 | 3.43 | 0.000924 | -0.000979 | 3.09 | 0.00078 | 0 | 3.43 | 0.000924 | -0.000979 |  | CFL | None | 3090 | 0.78 | 3090 | 0.78 | 1.11 | 1.18 | -0.00031683 | 3090 | 0.78 | 3090 | 0.78 | 1.11 | 1.18 | -0.000317
CFLNonePGEMBTExCZ11 | Com-Iltg-dWatt-CFL_OSnone | PGE | MBT | Ex | CZ11 | 3.09 | 0.00078 | 0 | 3.45 | 0.000939 | -0.00192 | 3.09 | 0.00078 | 0 | 3.45 | 0.000939 | -0.00192 |  | CFL | None | 3090 | 0.78 | 3090 | 0.78 | 1.12 | 1.2 | -0.00062136 | 3090 | 0.78 | 3090 | 0.78 | 1.12 | 1.2 | -0.000621
CFLNonePGEMBTExCZ12 | Com-Iltg-dWatt-CFL_OSnone | PGE | MBT | Ex | CZ12 | 3.09 | 0.00078 | 0 | 3.43 | 0.000914 | -0.00188 | 3.09 | 0.00078 | 0 | 3.43 | 0.000914 | -0.00188 |  | CFL | None | 3090 | 0.78 | 3090 | 0.78 | 1.11 | 1.17 | -0.00060841 | 3090 | 0.78 | 3090 | 0.78 | 1.11 | 1.17 | -0.000608
CFLNonePGEMBTExCZ13 | Com-Iltg-dWatt-CFL_OSnone | PGE | MBT | Ex | CZ13 | 3.09 | 0.00078 | 0 | 3.46 | 0.000916 | -0.00158 | 3.09 | 0.00078 | 0 | 3.46 | 0.000916 | -0.00158 |  | CFL | None | 3090 | 0.78 | 3090 | 0.78 | 1.12 | 1.17 | -0.00051133 | 3090 | 0.78 | 3090 | 0.78 | 1.12 | 1.17 | -0.000511
CFLNonePGEMBTExCZ16 | Com-Iltg-dWatt-CFL_OSnone | PGE | MBT | Ex | CZ16 | 3.09 | 0.00078 | 0 | 3.31 | 0.000899 | -0.00822 | 3.09 | 0.00078 | 0 | 3.31 | 0.000899 | -0.00822 |  | CFL | None | 3090 | 0.78 | 3090 | 0.78 | 1.07 | 1.15 | -0.0026602 | 3090 | 0.78 | 3090 | 0.78 | 1.07 | 1.15 | -0.00266
CFLNonePGEMBTExIOU | Com-Iltg-dWatt-CFL_OSnone | PGE | MBT | Ex | IOU | 3.09 | 0.00078 | 0 | 3.4432 | 0.00092275 | -0.001665 | 3.09 | 0.00078 | 0 | 3.4432 | 0.00092275 | -0.001665 |  | CFL | None | 3090 | 0.78 | 3090 | 0.78 | 1.11 | 1.18 | -0.00053883 | 3090 | 0.78 | 3090 | 0.78 | 1.11 | 1.18 | -0.000539
CFLNonePGEMBTNewCZ01 | Com-Iltg-dWatt-CFL_OSnone | PGE | MBT | New | CZ01 | 3.09 | 0.00078 | 0 | 3.16 | 0.000883 | -0.00343 | 3.09 | 0.00078 | 0 | 3.16 | 0.000883 | -0.00343 |  | CFL | None | 3090 | 0.78 | 3090 | 0.78 | 1.02 | 1.13 | -0.00111 | 3090 | 0.78 | 3090 | 0.78 | 1.02 | 1.13 | -0.00111
CFLNonePGEMBTNewCZ02 | Com-Iltg-dWatt-CFL_OSnone | PGE | MBT | New | CZ02 | 3.09 | 0.00078 | 0 | 3.3 | 0.000958 | -0.00162 | 3.09 | 0.00078 | 0 | 3.3 | 0.000958 | -0.00162 |  | CFL | None | 3090 | 0.78 | 3090 | 0.78 | 1.07 | 1.23 | -0.00052427 | 3090 | 0.78 | 3090 | 0.78 | 1.07 | 1.23 | -0.000524
CFLNonePGEMBTNewCZ03 | Com-Iltg-dWatt-CFL_OSnone | PGE | MBT | New | CZ03 | 3.09 | 0.00078 | 0 | 3.27 | 0.000929 | -0.00154 | 3.09 | 0.00078 | 0 | 3.27 | 0.000929 | -0.00154 |  | CFL | None | 3090 | 0.78 | 3090 | 0.78 | 1.06 | 1.19 | -0.00049838 | 3090 | 0.78 | 3090 | 0.78 | 1.06 | 1.19 | -0.000498
CFLNonePGEMBTNewCZ04 | Com-Iltg-dWatt-CFL_OSnone | PGE | MBT | New | CZ04 | 3.09 | 0.00078 | 0 | 3.33 | 0.000949 | -0.00123 | 3.09 | 0.00078 | 0 | 3.33 | 0.000949 | -0.00123 |  | CFL | None | 3090 | 0.78 | 3090 | 0.78 | 1.08 | 1.22 | -0.00039806 | 3090 | 0.78 | 3090 | 0.78 | 1.08 | 1.22 | -0.000398
CFLNonePGEMBTNewCZ05 | Com-Iltg-dWatt-CFL_OSnone | PGE | MBT | New | CZ05 | 3.09 | 0.00078 | 0 | 3.28 | 0.000924 | -0.000819 | 3.09 | 0.00078 | 0 | 3.28 | 0.000924 | -0.000819 |  | CFL | None | 3090 | 0.78 | 3090 | 0.78 | 1.06 | 1.18 | -0.00026505 | 3090 | 0.78 | 3090 | 0.78 | 1.06 | 1.18 | -0.000265
CFLNonePGEMBTNewCZ11 | Com-Iltg-dWatt-CFL_OSnone | PGE | MBT | New | CZ11 | 3.09 | 0.00078 | 0 | 3.36 | 0.000967 | -0.0017 | 3.09 | 0.00078 | 0 | 3.36 | 0.000967 | -0.0017 |  | CFL | None | 3090 | 0.78 | 3090 | 0.78 | 1.09 | 1.24 | -0.00055016 | 3090 | 0.78 | 3090 | 0.78 | 1.09 | 1.24 | -0.00055
CFLNonePGEMBTNewCZ12 | Com-Iltg-dWatt-CFL_OSnone | PGE | MBT | New | CZ12 | 3.09 | 0.00078 | 0 | 3.34 | 0.000959 | -0.00147 | 3.09 | 0.00078 | 0 | 3.34 | 0.000959 | -0.00147 |  | CFL | None | 3090 | 0.78 | 3090 | 0.78 | 1.08 | 1.23 | -0.00047573 | 3090 | 0.78 | 3090 | 0.78 | 1.08 | 1.23 | -0.000476
CFLNonePGEMBTNewCZ13 | Com-Iltg-dWatt-CFL_OSnone | PGE | MBT | New | CZ13 | 3.09 | 0.00078 | 0 | 3.37 | 0.000956 | -0.00137 | 3.09 | 0.00078 | 0 | 3.37 | 0.000956 | -0.00137 |  | CFL | None | 3090 | 0.78 | 3090 | 0.78 | 1.09 | 1.23 | -0.00044337 | 3090 | 0.78 | 3090 | 0.78 | 1.09 | 1.23 | -0.000443
CFLNonePGEMBTNewCZ16 | Com-Iltg-dWatt-CFL_OSnone | PGE | MBT | New | CZ16 | 3.09 | 0.00078 | 0 | 3.23 | 0.000925 | -0.00636 | 3.09 | 0.00078 | 0 | 3.23 | 0.000925 | -0.00636 |  | CFL | None | 3090 | 0.78 | 3090 | 0.78 | 1.05 | 1.19 | -0.0020583 | 3090 | 0.78 | 3090 | 0.78 | 1.05 | 1.19 | -0.00206
CFLNonePGEMBTNewIOU | Com-Iltg-dWatt-CFL_OSnone | PGE | MBT | New | IOU | 3.09 | 0.00078 | 0 | 3.3217 | 0.00094831 | -0.0015217 | 3.09 | 0.00078 | 0 | 3.3217 | 0.00094831 | -0.0015217 |  | CFL | None | 3090 | 0.78 | 3090 | 0.78 | 1.07 | 1.22 | -0.00049247 | 3090 | 0.78 | 3090 | 0.78 | 1.07 | 1.22 | -0.000492
CFLNonePGEMLIExCZ01 | Com-Iltg-dWatt-CFL_OSnone | PGE | MLI | Ex | CZ01 | 2.58 | 0.000777 | 0 | 2.52 | 0.000884 | -0.0297 | 2.58 | 0.000777 | 0 | 2.52 | 0.000884 | -0.0297 |  | CFL | None | 2580 | 0.777 | 2580 | 0.777 | 0.977 | 1.14 | -0.011512 | 2580 | 0.777 | 2580 | 0.777 | 0.977 | 1.14 | -0.0115
CFLNonePGEMLIExCZ02 | Com-Iltg-dWatt-CFL_OSnone | PGE | MLI | Ex | CZ02 | 2.58 | 0.000777 | 0 | 2.69 | 0.000901 | -0.0147 | 2.58 | 0.000777 | 0 | 2.69 | 0.000901 | -0.0147 |  | CFL | None | 2580 | 0.777 | 2580 | 0.777 | 1.04 | 1.16 | -0.0056977 | 2580 | 0.777 | 2580 | 0.777 | 1.04 | 1.16 | -0.0057
CFLNonePGEMLIExCZ03 | Com-Iltg-dWatt-CFL_OSnone | PGE | MLI | Ex | CZ03 | 2.58 | 0.000777 | 0 | 2.69 | 0.000901 | -0.0136 | 2.58 | 0.000777 | 0 | 2.69 | 0.000901 | -0.0136 |  | CFL | None | 2580 | 0.777 | 2580 | 0.777 | 1.04 | 1.16 | -0.0052713 | 2580 | 0.777 | 2580 | 0.777 | 1.04 | 1.16 | -0.00527
CFLNonePGEMLIExCZ04 | Com-Iltg-dWatt-CFL_OSnone | PGE | MLI | Ex | CZ04 | 2.58 | 0.000777 | 0 | 2.72 | 0.000897 | -0.011 | 2.58 | 0.000777 | 0 | 2.72 | 0.000897 | -0.011 |  | CFL | None | 2580 | 0.777 | 2580 | 0.777 | 1.05 | 1.15 | -0.0042636 | 2580 | 0.777 | 2580 | 0.777 | 1.05 | 1.15 | -0.00426
CFLNonePGEMLIExCZ05 | Com-Iltg-dWatt-CFL_OSnone | PGE | MLI | Ex | CZ05 | 2.58 | 0.000777 | 0 | 2.68 | 0.0009 | -0.0126 | 2.58 | 0.000777 | 0 | 2.68 | 0.0009 | -0.0126 |  | CFL | None | 2580 | 0.777 | 2580 | 0.777 | 1.04 | 1.16 | -0.0048837 | 2580 | 0.777 | 2580 | 0.777 | 1.04 | 1.16 | -0.00488
CFLNonePGEMLIExCZ11 | Com-Iltg-dWatt-CFL_OSnone | PGE | MLI | Ex | CZ11 | 2.58 | 0.000777 | 0 | 2.7 | 0.0009 | -0.0154 | 2.58 | 0.000777 | 0 | 2.7 | 0.0009 | -0.0154 |  | CFL | None | 2580 | 0.777 | 2580 | 0.777 | 1.05 | 1.16 | -0.005969 | 2580 | 0.777 | 2580 | 0.777 | 1.05 | 1.16 | -0.00597
CFLNonePGEMLIExCZ12 | Com-Iltg-dWatt-CFL_OSnone | PGE | MLI | Ex | CZ12 | 2.58 | 0.000777 | 0 | 2.7 | 0.000905 | -0.0149 | 2.58 | 0.000777 | 0 | 2.7 | 0.000905 | -0.0149 |  | CFL | None | 2580 | 0.777 | 2580 | 0.777 | 1.05 | 1.16 | -0.0057752 | 2580 | 0.777 | 2580 | 0.777 | 1.05 | 1.16 | -0.00578
CFLNonePGEMLIExCZ13 | Com-Iltg-dWatt-CFL_OSnone | PGE | MLI | Ex | CZ13 | 2.58 | 0.000777 | 0 | 2.73 | 0.00089 | -0.0134 | 2.58 | 0.000777 | 0 | 2.73 | 0.00089 | -0.0134 |  | CFL | None | 2580 | 0.777 | 2580 | 0.777 | 1.06 | 1.15 | -0.0051938 | 2580 | 0.777 | 2580 | 0.777 | 1.06 | 1.15 | -0.00519
CFLNonePGEMLIExCZ16 | Com-Iltg-dWatt-CFL_OSnone | PGE | MLI | Ex | CZ16 | 2.58 | 0.000777 | 0 | 2.54 | 0.000883 | -0.031 | 2.58 | 0.000777 | 0 | 2.54 | 0.000883 | -0.031 |  | CFL | None | 2580 | 0.777 | 2580 | 0.777 | 0.984 | 1.14 | -0.012016 | 2580 | 0.777 | 2580 | 0.777 | 0.984 | 1.14 | -0.012
CFLNonePGEMLIExIOU | Com-Iltg-dWatt-CFL_OSnone | PGE | MLI | Ex | IOU | 2.58 | 0.000777 | 0 | 2.6998 | 0.00089931 | -0.013793 | 2.58 | 0.000777 | 0 | 2.6998 | 0.00089931 | -0.013793 |  | CFL | None | 2580 | 0.777 | 2580 | 0.777 | 1.05 | 1.16 | -0.005346 | 2580 | 0.777 | 2580 | 0.777 | 1.05 | 1.16 | -0.00535
CFLNonePGEMLINewCZ01 | Com-Iltg-dWatt-CFL_OSnone | PGE | MLI | New | CZ01 | 2.58 | 0.000777 | 0 | 2.45 | 0.000845 | -0.0395 | 2.58 | 0.000777 | 0 | 2.45 | 0.000845 | -0.0395 |  | CFL | None | 2580 | 0.777 | 2580 | 0.777 | 0.95 | 1.09 | -0.01531 | 2580 | 0.777 | 2580 | 0.777 | 0.95 | 1.09 | -0.0153
CFLNonePGEMLINewCZ02 | Com-Iltg-dWatt-CFL_OSnone | PGE | MLI | New | CZ02 | 2.58 | 0.000777 | 0 | 2.6 | 0.000896 | -0.0218 | 2.58 | 0.000777 | 0 | 2.6 | 0.000896 | -0.0218 |  | CFL | None | 2580 | 0.777 | 2580 | 0.777 | 1.01 | 1.15 | -0.0084496 | 2580 | 0.777 | 2580 | 0.777 | 1.01 | 1.15 | -0.00845
CFLNonePGEMLINewCZ03 | Com-Iltg-dWatt-CFL_OSnone | PGE | MLI | New | CZ03 | 2.58 | 0.000777 | 0 | 2.56 | 0.000905 | -0.0214 | 2.58 | 0.000777 | 0 | 2.56 | 0.000905 | -0.0214 |  | CFL | None | 2580 | 0.777 | 2580 | 0.777 | 0.992 | 1.16 | -0.0082946 | 2580 | 0.777 | 2580 | 0.777 | 0.992 | 1.16 | -0.00829
CFLNonePGEMLINewCZ04 | Com-Iltg-dWatt-CFL_OSnone | PGE | MLI | New | CZ04 | 2.58 | 0.000777 | 0 | 2.63 | 0.000894 | -0.0172 | 2.58 | 0.000777 | 0 | 2.63 | 0.000894 | -0.0172 |  | CFL | None | 2580 | 0.777 | 2580 | 0.777 | 1.02 | 1.15 | -0.0066667 | 2580 | 0.777 | 2580 | 0.777 | 1.02 | 1.15 | -0.00667
CFLNonePGEMLINewCZ05 | Com-Iltg-dWatt-CFL_OSnone | PGE | MLI | New | CZ05 | 2.58 | 0.000777 | 0 | 2.56 | 0.00089 | -0.0208 | 2.58 | 0.000777 | 0 | 2.56 | 0.00089 | -0.0208 |  | CFL | None | 2580 | 0.777 | 2580 | 0.777 | 0.992 | 1.15 | -0.008062 | 2580 | 0.777 | 2580 | 0.777 | 0.992 | 1.15 | -0.00806
CFLNonePGEMLINewCZ11 | Com-Iltg-dWatt-CFL_OSnone | PGE | MLI | New | CZ11 | 2.58 | 0.000777 | 0 | 2.7 | 0.000928 | -0.0183 | 2.58 | 0.000777 | 0 | 2.7 | 0.000928 | -0.0183 |  | CFL | None | 2580 | 0.777 | 2580 | 0.777 | 1.05 | 1.19 | -0.007093 | 2580 | 0.777 | 2580 | 0.777 | 1.05 | 1.19 | -0.00709
CFLNonePGEMLINewCZ12 | Com-Iltg-dWatt-CFL_OSnone | PGE | MLI | New | CZ12 | 2.58 | 0.000777 | 0 | 2.66 | 0.000916 | -0.0199 | 2.58 | 0.000777 | 0 | 2.66 | 0.000916 | -0.0199 |  | CFL | None | 2580 | 0.777 | 2580 | 0.777 | 1.03 | 1.18 | -0.0077132 | 2580 | 0.777 | 2580 | 0.777 | 1.03 | 1.18 | -0.00771
CFLNonePGEMLINewCZ13 | Com-Iltg-dWatt-CFL_OSnone | PGE | MLI | New | CZ13 | 2.58 | 0.000777 | 0 | 2.73 | 0.000934 | -0.0173 | 2.58 | 0.000777 | 0 | 2.73 | 0.000934 | -0.0173 |  | CFL | None | 2580 | 0.777 | 2580 | 0.777 | 1.06 | 1.2 | -0.0067054 | 2580 | 0.777 | 2580 | 0.777 | 1.06 | 1.2 | -0.00671
CFLNonePGEMLINewCZ16 | Com-Iltg-dWatt-CFL_OSnone | PGE | MLI | New | CZ16 | 2.58 | 0.000777 | 0 | 2.53 | 0.000883 | -0.0335 | 2.58 | 0.000777 | 0 | 2.53 | 0.000883 | -0.0335 |  | CFL | None | 2580 | 0.777 | 2580 | 0.777 | 0.981 | 1.14 | -0.012984 | 2580 | 0.777 | 2580 | 0.777 | 0.981 | 1.14 | -0.013
CFLNonePGEMLINewIOU | Com-Iltg-dWatt-CFL_OSnone | PGE | MLI | New | IOU | 2.58 | 0.000777 | 0 | 2.6368 | 0.00091066 | -0.019682 | 2.58 | 0.000777 | 0 | 2.6368 | 0.00091066 | -0.019682 |  | CFL | None | 2580 | 0.777 | 2580 | 0.777 | 1.02 | 1.17 | -0.0076287 | 2580 | 0.777 | 2580 | 0.777 | 1.02 | 1.17 | -0.00763
CFLNonePGEMtlExCZ01 | Com-Iltg-dWatt-CFL_OSnone | PGE | Mtl | Ex | CZ01 | 1.37 | 0.000151 | 0 | 1.35 | 0.00018 | -0.0118 | 1.37 | 0.000151 | 0 | 1.35 | 0.00018 | -0.0118 |  | CFL | None | 1370 | 0.151 | 1370 | 0.151 | 0.985 | 1.19 | -0.0086131 | 1370 | 0.151 | 1370 | 0.151 | 0.985 | 1.19 | -0.00861
CFLNonePGEMtlExCZ02 | Com-Iltg-dWatt-CFL_OSnone | PGE | Mtl | Ex | CZ02 | 1.37 | 0.000151 | 0 | 1.43 | 0.000186 | -0.00782 | 1.37 | 0.000151 | 0 | 1.43 | 0.000186 | -0.00782 |  | CFL | None | 1370 | 0.151 | 1370 | 0.151 | 1.04 | 1.23 | -0.005708 | 1370 | 0.151 | 1370 | 0.151 | 1.04 | 1.23 | -0.00571
CFLNonePGEMtlExCZ03 | Com-Iltg-dWatt-CFL_OSnone | PGE | Mtl | Ex | CZ03 | 1.37 | 0.000151 | 0 | 1.44 | 0.000182 | -0.00758 | 1.37 | 0.000151 | 0 | 1.44 | 0.000182 | -0.00758 |  | CFL | None | 1370 | 0.151 | 1370 | 0.151 | 1.05 | 1.21 | -0.0055328 | 1370 | 0.151 | 1370 | 0.151 | 1.05 | 1.21 | -0.00553
CFLNonePGEMtlExCZ04 | Com-Iltg-dWatt-CFL_OSnone | PGE | Mtl | Ex | CZ04 | 1.37 | 0.000151 | 0 | 1.46 | 0.000185 | -0.00627 | 1.37 | 0.000151 | 0 | 1.46 | 0.000185 | -0.00627 |  | CFL | None | 1370 | 0.151 | 1370 | 0.151 | 1.07 | 1.23 | -0.0045766 | 1370 | 0.151 | 1370 | 0.151 | 1.07 | 1.23 | -0.00458
CFLNonePGEMtlExCZ05 | Com-Iltg-dWatt-CFL_OSnone | PGE | Mtl | Ex | CZ05 | 1.37 | 0.000151 | 0 | 1.42 | 0.000181 | -0.00798 | 1.37 | 0.000151 | 0 | 1.42 | 0.000181 | -0.00798 |  | CFL | None | 1370 | 0.151 | 1370 | 0.151 | 1.04 | 1.2 | -0.0058248 | 1370 | 0.151 | 1370 | 0.151 | 1.04 | 1.2 | -0.00582
CFLNonePGEMtlExCZ11 | Com-Iltg-dWatt-CFL_OSnone | PGE | Mtl | Ex | CZ11 | 1.37 | 0.000151 | 0 | 1.47 | 0.000188 | -0.00658 | 1.37 | 0.000151 | 0 | 1.47 | 0.000188 | -0.00658 |  | CFL | None | 1370 | 0.151 | 1370 | 0.151 | 1.07 | 1.25 | -0.0048029 | 1370 | 0.151 | 1370 | 0.151 | 1.07 | 1.25 | -0.0048
CFLNonePGEMtlExCZ12 | Com-Iltg-dWatt-CFL_OSnone | PGE | Mtl | Ex | CZ12 | 1.37 | 0.000151 | 0 | 1.46 | 0.000188 | -0.00695 | 1.37 | 0.000151 | 0 | 1.46 | 0.000188 | -0.00695 |  | CFL | None | 1370 | 0.151 | 1370 | 0.151 | 1.07 | 1.25 | -0.005073 | 1370 | 0.151 | 1370 | 0.151 | 1.07 | 1.25 | -0.00507
CFLNonePGEMtlExCZ13 | Com-Iltg-dWatt-CFL_OSnone | PGE | Mtl | Ex | CZ13 | 1.37 | 0.000151 | 0 | 1.49 | 0.000188 | -0.00616 | 1.37 | 0.000151 | 0 | 1.49 | 0.000188 | -0.00616 |  | CFL | None | 1370 | 0.151 | 1370 | 0.151 | 1.09 | 1.25 | -0.0044964 | 1370 | 0.151 | 1370 | 0.151 | 1.09 | 1.25 | -0.0045
CFLNonePGEMtlExCZ16 | Com-Iltg-dWatt-CFL_OSnone | PGE | Mtl | Ex | CZ16 | 1.37 | 0.000151 | 0 | 1.34 | 0.000181 | -0.0105 | 1.37 | 0.000151 | 0 | 1.34 | 0.000181 | -0.0105 |  | CFL | None | 1370 | 0.151 | 1370 | 0.151 | 0.978 | 1.2 | -0.0076642 | 1370 | 0.151 | 1370 | 0.151 | 0.978 | 1.2 | -0.00766
CFLNonePGEMtlExIOU | Com-Iltg-dWatt-CFL_OSnone | PGE | Mtl | Ex | IOU | 1.37 | 0.000151 | 0 | 1.446 | 0.00018413 | -0.0072997 | 1.37 | 0.000151 | 0 | 1.446 | 0.00018413 | -0.0072997 |  | CFL | None | 1370 | 0.151 | 1370 | 0.151 | 1.06 | 1.22 | -0.0053283 | 1370 | 0.151 | 1370 | 0.151 | 1.06 | 1.22 | -0.00533
CFLNonePGEMtlNewCZ01 | Com-Iltg-dWatt-CFL_OSnone | PGE | Mtl | New | CZ01 | 1.37 | 0.000151 | 0 | 1.29 | 0.00018 | -0.0152 | 1.37 | 0.000151 | 0 | 1.29 | 0.00018 | -0.0152 |  | CFL | None | 1370 | 0.151 | 1370 | 0.151 | 0.942 | 1.19 | -0.011095 | 1370 | 0.151 | 1370 | 0.151 | 0.942 | 1.19 | -0.0111
CFLNonePGEMtlNewCZ02 | Com-Iltg-dWatt-CFL_OSnone | PGE | Mtl | New | CZ02 | 1.37 | 0.000151 | 0 | 1.4 | 0.000191 | -0.0103 | 1.37 | 0.000151 | 0 | 1.4 | 0.000191 | -0.0103 |  | CFL | None | 1370 | 0.151 | 1370 | 0.151 | 1.02 | 1.26 | -0.0075182 | 1370 | 0.151 | 1370 | 0.151 | 1.02 | 1.26 | -0.00752
CFLNonePGEMtlNewCZ03 | Com-Iltg-dWatt-CFL_OSnone | PGE | Mtl | New | CZ03 | 1.37 | 0.000151 | 0 | 1.41 | 0.000185 | -0.00964 | 1.37 | 0.000151 | 0 | 1.41 | 0.000185 | -0.00964 |  | CFL | None | 1370 | 0.151 | 1370 | 0.151 | 1.03 | 1.23 | -0.0070365 | 1370 | 0.151 | 1370 | 0.151 | 1.03 | 1.23 | -0.00704
CFLNonePGEMtlNewCZ04 | Com-Iltg-dWatt-CFL_OSnone | PGE | Mtl | New | CZ04 | 1.37 | 0.000151 | 0 | 1.45 | 0.000189 | -0.00812 | 1.37 | 0.000151 | 0 | 1.45 | 0.000189 | -0.00812 |  | CFL | None | 1370 | 0.151 | 1370 | 0.151 | 1.06 | 1.25 | -0.005927 | 1370 | 0.151 | 1370 | 0.151 | 1.06 | 1.25 | -0.00593
CFLNonePGEMtlNewCZ05 | Com-Iltg-dWatt-CFL_OSnone | PGE | Mtl | New | CZ05 | 1.37 | 0.000151 | 0 | 1.39 | 0.000183 | -0.0108 | 1.37 | 0.000151 | 0 | 1.39 | 0.000183 | -0.0108 |  | CFL | None | 1370 | 0.151 | 1370 | 0.151 | 1.01 | 1.21 | -0.0078832 | 1370 | 0.151 | 1370 | 0.151 | 1.01 | 1.21 | -0.00788
CFLNonePGEMtlNewCZ11 | Com-Iltg-dWatt-CFL_OSnone | PGE | Mtl | New | CZ11 | 1.37 | 0.000151 | 0 | 1.46 | 0.000193 | -0.00821 | 1.37 | 0.000151 | 0 | 1.46 | 0.000193 | -0.00821 |  | CFL | None | 1370 | 0.151 | 1370 | 0.151 | 1.07 | 1.28 | -0.0059927 | 1370 | 0.151 | 1370 | 0.151 | 1.07 | 1.28 | -0.00599
CFLNonePGEMtlNewCZ12 | Com-Iltg-dWatt-CFL_OSnone | PGE | Mtl | New | CZ12 | 1.37 | 0.000151 | 0 | 1.45 | 0.000192 | -0.00858 | 1.37 | 0.000151 | 0 | 1.45 | 0.000192 | -0.00858 |  | CFL | None | 1370 | 0.151 | 1370 | 0.151 | 1.06 | 1.27 | -0.0062628 | 1370 | 0.151 | 1370 | 0.151 | 1.06 | 1.27 | -0.00626
CFLNonePGEMtlNewCZ13 | Com-Iltg-dWatt-CFL_OSnone | PGE | Mtl | New | CZ13 | 1.37 | 0.000151 | 0 | 1.47 | 0.000191 | -0.00772 | 1.37 | 0.000151 | 0 | 1.47 | 0.000191 | -0.00772 |  | CFL | None | 1370 | 0.151 | 1370 | 0.151 | 1.07 | 1.26 | -0.005635 | 1370 | 0.151 | 1370 | 0.151 | 1.07 | 1.26 | -0.00564
CFLNonePGEMtlNewCZ16 | Com-Iltg-dWatt-CFL_OSnone | PGE | Mtl | New | CZ16 | 1.37 | 0.000151 | 0 | 1.32 | 0.000184 | -0.0121 | 1.37 | 0.000151 | 0 | 1.32 | 0.000184 | -0.0121 |  | CFL | None | 1370 | 0.151 | 1370 | 0.151 | 0.964 | 1.22 | -0.0088321 | 1370 | 0.151 | 1370 | 0.151 | 0.964 | 1.22 | -0.00883
CFLNonePGEMtlNewIOU | Com-Iltg-dWatt-CFL_OSnone | PGE | Mtl | New | IOU | 1.37 | 0.000151 | 0 | 1.4285 | 0.00018851 | -0.0091488 | 1.37 | 0.000151 | 0 | 1.4285 | 0.00018851 | -0.0091488 |  | CFL | None | 1370 | 0.151 | 1370 | 0.151 | 1.04 | 1.25 | -0.0066779 | 1370 | 0.151 | 1370 | 0.151 | 1.04 | 1.25 | -0.00668
CFLNonePGENrsExCZ01 | Com-Iltg-dWatt-CFL_OSnone | PGE | Nrs | Ex | CZ01 | 3.57 | 0.000565 | 0 | 3.51 | 0.000645 | -0.0722 | 3.57 | 0.000565 | 0 | 3.51 | 0.000645 | -0.0722 |  | CFL | None | 3570 | 0.565 | 3570 | 0.565 | 0.983 | 1.14 | -0.020224 | 3570 | 0.565 | 3570 | 0.565 | 0.983 | 1.14 | -0.0202
CFLNonePGENrsExCZ02 | Com-Iltg-dWatt-CFL_OSnone | PGE | Nrs | Ex | CZ02 | 3.57 | 0.000565 | 0 | 3.7 | 0.00071 | -0.0522 | 3.57 | 0.000565 | 0 | 3.7 | 0.00071 | -0.0522 |  | CFL | None | 3570 | 0.565 | 3570 | 0.565 | 1.04 | 1.26 | -0.014622 | 3570 | 0.565 | 3570 | 0.565 | 1.04 | 1.26 | -0.0146
CFLNonePGENrsExCZ03 | Com-Iltg-dWatt-CFL_OSnone | PGE | Nrs | Ex | CZ03 | 3.57 | 0.000565 | 0 | 3.66 | 0.000688 | -0.0529 | 3.57 | 0.000565 | 0 | 3.66 | 0.000688 | -0.0529 |  | CFL | None | 3570 | 0.565 | 3570 | 0.565 | 1.03 | 1.22 | -0.014818 | 3570 | 0.565 | 3570 | 0.565 | 1.03 | 1.22 | -0.0148
CFLNonePGENrsExCZ04 | Com-Iltg-dWatt-CFL_OSnone | PGE | Nrs | Ex | CZ04 | 3.57 | 0.000565 | 0 | 3.75 | 0.000704 | -0.0447 | 3.57 | 0.000565 | 0 | 3.75 | 0.000704 | -0.0447 |  | CFL | None | 3570 | 0.565 | 3570 | 0.565 | 1.05 | 1.25 | -0.012521 | 3570 | 0.565 | 3570 | 0.565 | 1.05 | 1.25 | -0.0125
CFLNonePGENrsExCZ05 | Com-Iltg-dWatt-CFL_OSnone | PGE | Nrs | Ex | CZ05 | 3.57 | 0.000565 | 0 | 3.63 | 0.00067 | -0.0543 | 3.57 | 0.000565 | 0 | 3.63 | 0.00067 | -0.0543 |  | CFL | None | 3570 | 0.565 | 3570 | 0.565 | 1.02 | 1.19 | -0.01521 | 3570 | 0.565 | 3570 | 0.565 | 1.02 | 1.19 | -0.0152
CFLNonePGENrsExCZ11 | Com-Iltg-dWatt-CFL_OSnone | PGE | Nrs | Ex | CZ11 | 3.57 | 0.000565 | 0 | 3.8 | 0.000715 | -0.0432 | 3.57 | 0.000565 | 0 | 3.8 | 0.000715 | -0.0432 |  | CFL | None | 3570 | 0.565 | 3570 | 0.565 | 1.06 | 1.27 | -0.012101 | 3570 | 0.565 | 3570 | 0.565 | 1.06 | 1.27 | -0.0121
CFLNonePGENrsExCZ12 | Com-Iltg-dWatt-CFL_OSnone | PGE | Nrs | Ex | CZ12 | 3.57 | 0.000565 | 0 | 3.77 | 0.000712 | -0.0454 | 3.57 | 0.000565 | 0 | 3.77 | 0.000712 | -0.0454 |  | CFL | None | 3570 | 0.565 | 3570 | 0.565 | 1.06 | 1.26 | -0.012717 | 3570 | 0.565 | 3570 | 0.565 | 1.06 | 1.26 | -0.0127
CFLNonePGENrsExCZ13 | Com-Iltg-dWatt-CFL_OSnone | PGE | Nrs | Ex | CZ13 | 3.57 | 0.000565 | 0 | 3.82 | 0.000712 | -0.0414 | 3.57 | 0.000565 | 0 | 3.82 | 0.000712 | -0.0414 |  | CFL | None | 3570 | 0.565 | 3570 | 0.565 | 1.07 | 1.26 | -0.011597 | 3570 | 0.565 | 3570 | 0.565 | 1.07 | 1.26 | -0.0116
CFLNonePGENrsExCZ16 | Com-Iltg-dWatt-CFL_OSnone | PGE | Nrs | Ex | CZ16 | 3.57 | 0.000565 | 0 | 3.59 | 0.000684 | -0.0629 | 3.57 | 0.000565 | 0 | 3.59 | 0.000684 | -0.0629 |  | CFL | None | 3570 | 0.565 | 3570 | 0.565 | 1.01 | 1.21 | -0.017619 | 3570 | 0.565 | 3570 | 0.565 | 1.01 | 1.21 | -0.0176
CFLNonePGENrsExIOU | Com-Iltg-dWatt-CFL_OSnone | PGE | Nrs | Ex | IOU | 3.57 | 0.000565 | 0 | 3.7329 | 0.00070234 | -0.047858 | 3.57 | 0.000565 | 0 | 3.7329 | 0.00070234 | -0.047858 |  | CFL | None | 3570 | 0.565 | 3570 | 0.565 | 1.05 | 1.24 | -0.013406 | 3570 | 0.565 | 3570 | 0.565 | 1.05 | 1.24 | -0.0134
CFLNonePGENrsNewCZ01 | Com-Iltg-dWatt-CFL_OSnone | PGE | Nrs | New | CZ01 | 3.57 | 0.000565 | 0 | 3.39 | 0.000617 | -0.0786 | 3.57 | 0.000565 | 0 | 3.39 | 0.000617 | -0.0786 |  | CFL | None | 3570 | 0.565 | 3570 | 0.565 | 0.95 | 1.09 | -0.022017 | 3570 | 0.565 | 3570 | 0.565 | 0.95 | 1.09 | -0.022
CFLNonePGENrsNewCZ02 | Com-Iltg-dWatt-CFL_OSnone | PGE | Nrs | New | CZ02 | 3.57 | 0.000565 | 0 | 3.58 | 0.000706 | -0.0554 | 3.57 | 0.000565 | 0 | 3.58 | 0.000706 | -0.0554 |  | CFL | None | 3570 | 0.565 | 3570 | 0.565 | 1 | 1.25 | -0.015518 | 3570 | 0.565 | 3570 | 0.565 | 1 | 1.25 | -0.0155
CFLNonePGENrsNewCZ03 | Com-Iltg-dWatt-CFL_OSnone | PGE | Nrs | New | CZ03 | 3.57 | 0.000565 | 0 | 3.51 | 0.000694 | -0.0579 | 3.57 | 0.000565 | 0 | 3.51 | 0.000694 | -0.0579 |  | CFL | None | 3570 | 0.565 | 3570 | 0.565 | 0.983 | 1.23 | -0.016218 | 3570 | 0.565 | 3570 | 0.565 | 0.983 | 1.23 | -0.0162
CFLNonePGENrsNewCZ04 | Com-Iltg-dWatt-CFL_OSnone | PGE | Nrs | New | CZ04 | 3.57 | 0.000565 | 0 | 3.66 | 0.000706 | -0.0468 | 3.57 | 0.000565 | 0 | 3.66 | 0.000706 | -0.0468 |  | CFL | None | 3570 | 0.565 | 3570 | 0.565 | 1.03 | 1.25 | -0.013109 | 3570 | 0.565 | 3570 | 0.565 | 1.03 | 1.25 | -0.0131
CFLNonePGENrsNewCZ05 | Com-Iltg-dWatt-CFL_OSnone | PGE | Nrs | New | CZ05 | 3.57 | 0.000565 | 0 | 3.51 | 0.00067 | -0.06 | 3.57 | 0.000565 | 0 | 3.51 | 0.00067 | -0.06 |  | CFL | None | 3570 | 0.565 | 3570 | 0.565 | 0.983 | 1.19 | -0.016807 | 3570 | 0.565 | 3570 | 0.565 | 0.983 | 1.19 | -0.0168
CFLNonePGENrsNewCZ11 | Com-Iltg-dWatt-CFL_OSnone | PGE | Nrs | New | CZ11 | 3.57 | 0.000565 | 0 | 3.75 | 0.000716 | -0.0447 | 3.57 | 0.000565 | 0 | 3.75 | 0.000716 | -0.0447 |  | CFL | None | 3570 | 0.565 | 3570 | 0.565 | 1.05 | 1.27 | -0.012521 | 3570 | 0.565 | 3570 | 0.565 | 1.05 | 1.27 | -0.0125
CFLNonePGENrsNewCZ12 | Com-Iltg-dWatt-CFL_OSnone | PGE | Nrs | New | CZ12 | 3.57 | 0.000565 | 0 | 3.7 | 0.000718 | -0.0468 | 3.57 | 0.000565 | 0 | 3.7 | 0.000718 | -0.0468 |  | CFL | None | 3570 | 0.565 | 3570 | 0.565 | 1.04 | 1.27 | -0.013109 | 3570 | 0.565 | 3570 | 0.565 | 1.04 | 1.27 | -0.0131
CFLNonePGENrsNewCZ13 | Com-Iltg-dWatt-CFL_OSnone | PGE | Nrs | New | CZ13 | 3.57 | 0.000565 | 0 | 3.76 | 0.000716 | -0.0425 | 3.57 | 0.000565 | 0 | 3.76 | 0.000716 | -0.0425 |  | CFL | None | 3570 | 0.565 | 3570 | 0.565 | 1.05 | 1.27 | -0.011905 | 3570 | 0.565 | 3570 | 0.565 | 1.05 | 1.27 | -0.0119
CFLNonePGENrsNewCZ16 | Com-Iltg-dWatt-CFL_OSnone | PGE | Nrs | New | CZ16 | 3.57 | 0.000565 | 0 | 3.52 | 0.000685 | -0.0661 | 3.57 | 0.000565 | 0 | 3.52 | 0.000685 | -0.0661 |  | CFL | None | 3570 | 0.565 | 3570 | 0.565 | 0.986 | 1.21 | -0.018515 | 3570 | 0.565 | 3570 | 0.565 | 0.986 | 1.21 | -0.0185
CFLNonePGENrsNewIOU | Com-Iltg-dWatt-CFL_OSnone | PGE | Nrs | New | IOU | 3.57 | 0.000565 | 0 | 3.6468 | 0.00070717 | -0.049862 | 3.57 | 0.000565 | 0 | 3.6468 | 0.00070717 | -0.049862 |  | CFL | None | 3570 | 0.565 | 3570 | 0.565 | 1.02 | 1.25 | -0.013967 | 3570 | 0.565 | 3570 | 0.565 | 1.02 | 1.25 | -0.014
CFLNonePGEOfLExCZ01 | Com-Iltg-dWatt-CFL_OSnone | PGE | OfL | Ex | CZ01 | 3 | 0.000625 | 0 | 3.2 | 0.000793 | -0.0278 | 3 | 0.000625 | 0 | 3.2 | 0.000793 | -0.0278 |  | CFL | None | 3000 | 0.625 | 3000 | 0.625 | 1.07 | 1.27 | -0.0092667 | 3000 | 0.625 | 3000 | 0.625 | 1.07 | 1.27 | -0.00927
CFLNonePGEOfLExCZ02 | Com-Iltg-dWatt-CFL_OSnone | PGE | OfL | Ex | CZ02 | 3 | 0.000625 | 0 | 3.29 | 0.000835 | -0.0207 | 3 | 0.000625 | 0 | 3.29 | 0.000835 | -0.0207 |  | CFL | None | 3000 | 0.625 | 3000 | 0.625 | 1.1 | 1.34 | -0.0069 | 3000 | 0.625 | 3000 | 0.625 | 1.1 | 1.34 | -0.0069
CFLNonePGEOfLExCZ03 | Com-Iltg-dWatt-CFL_OSnone | PGE | OfL | Ex | CZ03 | 3 | 0.000625 | 0 | 3.28 | 0.000813 | -0.0192 | 3 | 0.000625 | 0 | 3.28 | 0.000813 | -0.0192 |  | CFL | None | 3000 | 0.625 | 3000 | 0.625 | 1.09 | 1.3 | -0.0064 | 3000 | 0.625 | 3000 | 0.625 | 1.09 | 1.3 | -0.0064
CFLNonePGEOfLExCZ04 | Com-Iltg-dWatt-CFL_OSnone | PGE | OfL | Ex | CZ04 | 3 | 0.000625 | 0 | 3.32 | 0.000817 | -0.0174 | 3 | 0.000625 | 0 | 3.32 | 0.000817 | -0.0174 |  | CFL | None | 3000 | 0.625 | 3000 | 0.625 | 1.11 | 1.31 | -0.0058 | 3000 | 0.625 | 3000 | 0.625 | 1.11 | 1.31 | -0.0058
CFLNonePGEOfLExCZ05 | Com-Iltg-dWatt-CFL_OSnone | PGE | OfL | Ex | CZ05 | 3 | 0.000625 | 0 | 3.28 | 0.000795 | -0.019 | 3 | 0.000625 | 0 | 3.28 | 0.000795 | -0.019 |  | CFL | None | 3000 | 0.625 | 3000 | 0.625 | 1.09 | 1.27 | -0.0063333 | 3000 | 0.625 | 3000 | 0.625 | 1.09 | 1.27 | -0.00633
CFLNonePGEOfLExCZ11 | Com-Iltg-dWatt-CFL_OSnone | PGE | OfL | Ex | CZ11 | 3 | 0.000625 | 0 | 3.37 | 0.000834 | -0.0199 | 3 | 0.000625 | 0 | 3.37 | 0.000834 | -0.0199 |  | CFL | None | 3000 | 0.625 | 3000 | 0.625 | 1.12 | 1.33 | -0.0066333 | 3000 | 0.625 | 3000 | 0.625 | 1.12 | 1.33 | -0.00663
CFLNonePGEOfLExCZ12 | Com-Iltg-dWatt-CFL_OSnone | PGE | OfL | Ex | CZ12 | 3 | 0.000625 | 0 | 3.32 | 0.000826 | -0.0191 | 3 | 0.000625 | 0 | 3.32 | 0.000826 | -0.0191 |  | CFL | None | 3000 | 0.625 | 3000 | 0.625 | 1.11 | 1.32 | -0.0063667 | 3000 | 0.625 | 3000 | 0.625 | 1.11 | 1.32 | -0.00637
CFLNonePGEOfLExCZ13 | Com-Iltg-dWatt-CFL_OSnone | PGE | OfL | Ex | CZ13 | 3 | 0.000625 | 0 | 3.4 | 0.000837 | -0.018 | 3 | 0.000625 | 0 | 3.4 | 0.000837 | -0.018 |  | CFL | None | 3000 | 0.625 | 3000 | 0.625 | 1.13 | 1.34 | -0.006 | 3000 | 0.625 | 3000 | 0.625 | 1.13 | 1.34 | -0.006
CFLNonePGEOfLExCZ16 | Com-Iltg-dWatt-CFL_OSnone | PGE | OfL | Ex | CZ16 | 3 | 0.000625 | 0 | 3.12 | 0.000804 | -0.0354 | 3 | 0.000625 | 0 | 3.12 | 0.000804 | -0.0354 |  | CFL | None | 3000 | 0.625 | 3000 | 0.625 | 1.04 | 1.29 | -0.0118 | 3000 | 0.625 | 3000 | 0.625 | 1.04 | 1.29 | -0.0118
CFLNonePGEOfLExIOU | Com-Iltg-dWatt-CFL_OSnone | PGE | OfL | Ex | IOU | 3 | 0.000625 | 0 | 3.3031 | 0.00081828 | -0.018885 | 3 | 0.000625 | 0 | 3.3031 | 0.00081828 | -0.018885 |  | CFL | None | 3000 | 0.625 | 3000 | 0.625 | 1.1 | 1.31 | -0.0062951 | 3000 | 0.625 | 3000 | 0.625 | 1.1 | 1.31 | -0.0063
CFLNonePGEOfLNewCZ01 | Com-Iltg-dWatt-CFL_OSnone | PGE | OfL | New | CZ01 | 3 | 0.000625 | 0 | 3.18 | 0.000761 | -0.0181 | 3 | 0.000625 | 0 | 3.18 | 0.000761 | -0.0181 |  | CFL | None | 3000 | 0.625 | 3000 | 0.625 | 1.06 | 1.22 | -0.0060333 | 3000 | 0.625 | 3000 | 0.625 | 1.06 | 1.22 | -0.00603
CFLNonePGEOfLNewCZ02 | Com-Iltg-dWatt-CFL_OSnone | PGE | OfL | New | CZ02 | 3 | 0.000625 | 0 | 3.31 | 0.000774 | -0.012 | 3 | 0.000625 | 0 | 3.31 | 0.000774 | -0.012 |  | CFL | None | 3000 | 0.625 | 3000 | 0.625 | 1.1 | 1.24 | -0.004 | 3000 | 0.625 | 3000 | 0.625 | 1.1 | 1.24 | -0.004
CFLNonePGEOfLNewCZ03 | Com-Iltg-dWatt-CFL_OSnone | PGE | OfL | New | CZ03 | 3 | 0.000625 | 0 | 3.29 | 0.000772 | -0.0119 | 3 | 0.000625 | 0 | 3.29 | 0.000772 | -0.0119 |  | CFL | None | 3000 | 0.625 | 3000 | 0.625 | 1.1 | 1.24 | -0.0039667 | 3000 | 0.625 | 3000 | 0.625 | 1.1 | 1.24 | -0.00397
CFLNonePGEOfLNewCZ04 | Com-Iltg-dWatt-CFL_OSnone | PGE | OfL | New | CZ04 | 3 | 0.000625 | 0 | 3.33 | 0.000776 | -0.011 | 3 | 0.000625 | 0 | 3.33 | 0.000776 | -0.011 |  | CFL | None | 3000 | 0.625 | 3000 | 0.625 | 1.11 | 1.24 | -0.0036667 | 3000 | 0.625 | 3000 | 0.625 | 1.11 | 1.24 | -0.00367
CFLNonePGEOfLNewCZ05 | Com-Iltg-dWatt-CFL_OSnone | PGE | OfL | New | CZ05 | 3 | 0.000625 | 0 | 3.28 | 0.000756 | -0.00947 | 3 | 0.000625 | 0 | 3.28 | 0.000756 | -0.00947 |  | CFL | None | 3000 | 0.625 | 3000 | 0.625 | 1.09 | 1.21 | -0.0031567 | 3000 | 0.625 | 3000 | 0.625 | 1.09 | 1.21 | -0.00316
CFLNonePGEOfLNewCZ11 | Com-Iltg-dWatt-CFL_OSnone | PGE | OfL | New | CZ11 | 3 | 0.000625 | 0 | 3.35 | 0.000782 | -0.0104 | 3 | 0.000625 | 0 | 3.35 | 0.000782 | -0.0104 |  | CFL | None | 3000 | 0.625 | 3000 | 0.625 | 1.12 | 1.25 | -0.0034667 | 3000 | 0.625 | 3000 | 0.625 | 1.12 | 1.25 | -0.00347
CFLNonePGEOfLNewCZ12 | Com-Iltg-dWatt-CFL_OSnone | PGE | OfL | New | CZ12 | 3 | 0.000625 | 0 | 3.33 | 0.000779 | -0.0117 | 3 | 0.000625 | 0 | 3.33 | 0.000779 | -0.0117 |  | CFL | None | 3000 | 0.625 | 3000 | 0.625 | 1.11 | 1.25 | -0.0039 | 3000 | 0.625 | 3000 | 0.625 | 1.11 | 1.25 | -0.0039
CFLNonePGEOfLNewCZ13 | Com-Iltg-dWatt-CFL_OSnone | PGE | OfL | New | CZ13 | 3 | 0.000625 | 0 | 3.36 | 0.000781 | -0.0102 | 3 | 0.000625 | 0 | 3.36 | 0.000781 | -0.0102 |  | CFL | None | 3000 | 0.625 | 3000 | 0.625 | 1.12 | 1.25 | -0.0034 | 3000 | 0.625 | 3000 | 0.625 | 1.12 | 1.25 | -0.0034
CFLNonePGEOfLNewCZ16 | Com-Iltg-dWatt-CFL_OSnone | PGE | OfL | New | CZ16 | 3 | 0.000625 | 0 | 3.2 | 0.000766 | -0.0254 | 3 | 0.000625 | 0 | 3.2 | 0.000766 | -0.0254 |  | CFL | None | 3000 | 0.625 | 3000 | 0.625 | 1.07 | 1.23 | -0.0084667 | 3000 | 0.625 | 3000 | 0.625 | 1.07 | 1.23 | -0.00847
CFLNonePGEOfLNewIOU | Com-Iltg-dWatt-CFL_OSnone | PGE | OfL | New | IOU | 3 | 0.000625 | 0 | 3.3148 | 0.00077515 | -0.01149 | 3 | 0.000625 | 0 | 3.3148 | 0.00077515 | -0.01149 |  | CFL | None | 3000 | 0.625 | 3000 | 0.625 | 1.1 | 1.24 | -0.0038301 | 3000 | 0.625 | 3000 | 0.625 | 1.1 | 1.24 | -0.00383
CFLNonePGEOfSExCZ01 | Com-Iltg-dWatt-CFL_OSnone | PGE | OfS | Ex | CZ01 | 2.98 | 0.000678 | 0 | 2.99 | 0.000804 | -0.0186 | 2.98 | 0.000678 | 0 | 2.99 | 0.000804 | -0.0186 |  | CFL | None | 2980 | 0.678 | 2980 | 0.678 | 1 | 1.19 | -0.0062416 | 2980 | 0.678 | 2980 | 0.678 | 1 | 1.19 | -0.00624
CFLNonePGEOfSExCZ02 | Com-Iltg-dWatt-CFL_OSnone | PGE | OfS | Ex | CZ02 | 2.98 | 0.000678 | 0 | 3.12 | 0.000828 | -0.0121 | 2.98 | 0.000678 | 0 | 3.12 | 0.000828 | -0.0121 |  | CFL | None | 2980 | 0.678 | 2980 | 0.678 | 1.05 | 1.22 | -0.0040604 | 2980 | 0.678 | 2980 | 0.678 | 1.05 | 1.22 | -0.00406
CFLNonePGEOfSExCZ03 | Com-Iltg-dWatt-CFL_OSnone | PGE | OfS | Ex | CZ03 | 2.98 | 0.000678 | 0 | 3.11 | 0.000827 | -0.0103 | 2.98 | 0.000678 | 0 | 3.11 | 0.000827 | -0.0103 |  | CFL | None | 2980 | 0.678 | 2980 | 0.678 | 1.04 | 1.22 | -0.0034564 | 2980 | 0.678 | 2980 | 0.678 | 1.04 | 1.22 | -0.00346
CFLNonePGEOfSExCZ04 | Com-Iltg-dWatt-CFL_OSnone | PGE | OfS | Ex | CZ04 | 2.98 | 0.000678 | 0 | 3.17 | 0.000831 | -0.00825 | 2.98 | 0.000678 | 0 | 3.17 | 0.000831 | -0.00825 |  | CFL | None | 2980 | 0.678 | 2980 | 0.678 | 1.06 | 1.23 | -0.0027685 | 2980 | 0.678 | 2980 | 0.678 | 1.06 | 1.23 | -0.00277
CFLNonePGEOfSExCZ05 | Com-Iltg-dWatt-CFL_OSnone | PGE | OfS | Ex | CZ05 | 2.98 | 0.000678 | 0 | 3.13 | 0.000811 | -0.00857 | 2.98 | 0.000678 | 0 | 3.13 | 0.000811 | -0.00857 |  | CFL | None | 2980 | 0.678 | 2980 | 0.678 | 1.05 | 1.2 | -0.0028758 | 2980 | 0.678 | 2980 | 0.678 | 1.05 | 1.2 | -0.00288
CFLNonePGEOfSExCZ11 | Com-Iltg-dWatt-CFL_OSnone | PGE | OfS | Ex | CZ11 | 2.98 | 0.000678 | 0 | 3.18 | 0.000829 | -0.0127 | 2.98 | 0.000678 | 0 | 3.18 | 0.000829 | -0.0127 |  | CFL | None | 2980 | 0.678 | 2980 | 0.678 | 1.07 | 1.22 | -0.0042617 | 2980 | 0.678 | 2980 | 0.678 | 1.07 | 1.22 | -0.00426
CFLNonePGEOfSExCZ12 | Com-Iltg-dWatt-CFL_OSnone | PGE | OfS | Ex | CZ12 | 2.98 | 0.000678 | 0 | 3.16 | 0.000831 | -0.0123 | 2.98 | 0.000678 | 0 | 3.16 | 0.000831 | -0.0123 |  | CFL | None | 2980 | 0.678 | 2980 | 0.678 | 1.06 | 1.23 | -0.0041275 | 2980 | 0.678 | 2980 | 0.678 | 1.06 | 1.23 | -0.00413
CFLNonePGEOfSExCZ13 | Com-Iltg-dWatt-CFL_OSnone | PGE | OfS | Ex | CZ13 | 2.98 | 0.000678 | 0 | 3.19 | 0.000822 | -0.0116 | 2.98 | 0.000678 | 0 | 3.19 | 0.000822 | -0.0116 |  | CFL | None | 2980 | 0.678 | 2980 | 0.678 | 1.07 | 1.21 | -0.0038926 | 2980 | 0.678 | 2980 | 0.678 | 1.07 | 1.21 | -0.00389
CFLNonePGEOfSExCZ16 | Com-Iltg-dWatt-CFL_OSnone | PGE | OfS | Ex | CZ16 | 2.98 | 0.000678 | 0 | 2.95 | 0.000814 | -0.023 | 2.98 | 0.000678 | 0 | 2.95 | 0.000814 | -0.023 |  | CFL | None | 2980 | 0.678 | 2980 | 0.678 | 0.99 | 1.2 | -0.0077181 | 2980 | 0.678 | 2980 | 0.678 | 0.99 | 1.2 | -0.00772
CFLNonePGEOfSExIOU | Com-Iltg-dWatt-CFL_OSnone | PGE | OfS | Ex | IOU | 2.98 | 0.000678 | 0 | 3.1507 | 0.0008271 | -0.011083 | 2.98 | 0.000678 | 0 | 3.1507 | 0.0008271 | -0.011083 |  | CFL | None | 2980 | 0.678 | 2980 | 0.678 | 1.06 | 1.22 | -0.0037191 | 2980 | 0.678 | 2980 | 0.678 | 1.06 | 1.22 | -0.00372
CFLNonePGEOfSNewCZ01 | Com-Iltg-dWatt-CFL_OSnone | PGE | OfS | New | CZ01 | 2.98 | 0.000678 | 0 | 2.92 | 0.000797 | -0.0172 | 2.98 | 0.000678 | 0 | 2.92 | 0.000797 | -0.0172 |  | CFL | None | 2980 | 0.678 | 2980 | 0.678 | 0.98 | 1.18 | -0.0057718 | 2980 | 0.678 | 2980 | 0.678 | 0.98 | 1.18 | -0.00577
CFLNonePGEOfSNewCZ02 | Com-Iltg-dWatt-CFL_OSnone | PGE | OfS | New | CZ02 | 2.98 | 0.000678 | 0 | 3.11 | 0.000843 | -0.00926 | 2.98 | 0.000678 | 0 | 3.11 | 0.000843 | -0.00926 |  | CFL | None | 2980 | 0.678 | 2980 | 0.678 | 1.04 | 1.24 | -0.0031074 | 2980 | 0.678 | 2980 | 0.678 | 1.04 | 1.24 | -0.00311
CFLNonePGEOfSNewCZ03 | Com-Iltg-dWatt-CFL_OSnone | PGE | OfS | New | CZ03 | 2.98 | 0.000678 | 0 | 3.06 | 0.000823 | -0.0101 | 2.98 | 0.000678 | 0 | 3.06 | 0.000823 | -0.0101 |  | CFL | None | 2980 | 0.678 | 2980 | 0.678 | 1.03 | 1.21 | -0.0033893 | 2980 | 0.678 | 2980 | 0.678 | 1.03 | 1.21 | -0.00339
CFLNonePGEOfSNewCZ04 | Com-Iltg-dWatt-CFL_OSnone | PGE | OfS | New | CZ04 | 2.98 | 0.000678 | 0 | 3.14 | 0.000839 | -0.00738 | 2.98 | 0.000678 | 0 | 3.14 | 0.000839 | -0.00738 |  | CFL | None | 2980 | 0.678 | 2980 | 0.678 | 1.05 | 1.24 | -0.0024765 | 2980 | 0.678 | 2980 | 0.678 | 1.05 | 1.24 | -0.00248
CFLNonePGEOfSNewCZ05 | Com-Iltg-dWatt-CFL_OSnone | PGE | OfS | New | CZ05 | 2.98 | 0.000678 | 0 | 3.08 | 0.00081 | -0.00801 | 2.98 | 0.000678 | 0 | 3.08 | 0.00081 | -0.00801 |  | CFL | None | 2980 | 0.678 | 2980 | 0.678 | 1.03 | 1.19 | -0.0026879 | 2980 | 0.678 | 2980 | 0.678 | 1.03 | 1.19 | -0.00269
CFLNonePGEOfSNewCZ11 | Com-Iltg-dWatt-CFL_OSnone | PGE | OfS | New | CZ11 | 2.98 | 0.000678 | 0 | 3.17 | 0.000851 | -0.0102 | 2.98 | 0.000678 | 0 | 3.17 | 0.000851 | -0.0102 |  | CFL | None | 2980 | 0.678 | 2980 | 0.678 | 1.06 | 1.26 | -0.0034228 | 2980 | 0.678 | 2980 | 0.678 | 1.06 | 1.26 | -0.00342
CFLNonePGEOfSNewCZ12 | Com-Iltg-dWatt-CFL_OSnone | PGE | OfS | New | CZ12 | 2.98 | 0.000678 | 0 | 3.15 | 0.000847 | -0.00991 | 2.98 | 0.000678 | 0 | 3.15 | 0.000847 | -0.00991 |  | CFL | None | 2980 | 0.678 | 2980 | 0.678 | 1.06 | 1.25 | -0.0033255 | 2980 | 0.678 | 2980 | 0.678 | 1.06 | 1.25 | -0.00333
CFLNonePGEOfSNewCZ13 | Com-Iltg-dWatt-CFL_OSnone | PGE | OfS | New | CZ13 | 2.98 | 0.000678 | 0 | 3.18 | 0.000842 | -0.00944 | 2.98 | 0.000678 | 0 | 3.18 | 0.000842 | -0.00944 |  | CFL | None | 2980 | 0.678 | 2980 | 0.678 | 1.07 | 1.24 | -0.0031678 | 2980 | 0.678 | 2980 | 0.678 | 1.07 | 1.24 | -0.00317
CFLNonePGEOfSNewCZ16 | Com-Iltg-dWatt-CFL_OSnone | PGE | OfS | New | CZ16 | 2.98 | 0.000678 | 0 | 2.95 | 0.00082 | -0.0214 | 2.98 | 0.000678 | 0 | 2.95 | 0.00082 | -0.0214 |  | CFL | None | 2980 | 0.678 | 2980 | 0.678 | 0.99 | 1.21 | -0.0071812 | 2980 | 0.678 | 2980 | 0.678 | 0.99 | 1.21 | -0.00718
CFLNonePGEOfSNewIOU | Com-Iltg-dWatt-CFL_OSnone | PGE | OfS | New | IOU | 2.98 | 0.000678 | 0 | 3.1274 | 0.00083758 | -0.0095312 | 2.98 | 0.000678 | 0 | 3.1274 | 0.00083758 | -0.0095312 |  | CFL | None | 2980 | 0.678 | 2980 | 0.678 | 1.05 | 1.24 | -0.0031984 | 2980 | 0.678 | 2980 | 0.678 | 1.05 | 1.24 | -0.0032
CFLNonePGERFFExCZ01 | Com-Iltg-dWatt-CFL_OSnone | PGE | RFF | Ex | CZ01 | 4.81 | 0.000808 | 0 | 4.69 | 0.000918 | -0.0567 | 4.81 | 0.000808 | 0 | 4.69 | 0.000918 | -0.0567 |  | CFL | None | 4810 | 0.808 | 4810 | 0.808 | 0.975 | 1.14 | -0.011788 | 4810 | 0.808 | 4810 | 0.808 | 0.975 | 1.14 | -0.0118
CFLNonePGERFFExCZ02 | Com-Iltg-dWatt-CFL_OSnone | PGE | RFF | Ex | CZ02 | 4.81 | 0.000808 | 0 | 4.97 | 0.000938 | -0.0368 | 4.81 | 0.000808 | 0 | 4.97 | 0.000938 | -0.0368 |  | CFL | None | 4810 | 0.808 | 4810 | 0.808 | 1.03 | 1.16 | -0.0076507 | 4810 | 0.808 | 4810 | 0.808 | 1.03 | 1.16 | -0.00765
CFLNonePGERFFExCZ03 | Com-Iltg-dWatt-CFL_OSnone | PGE | RFF | Ex | CZ03 | 4.81 | 0.000808 | 0 | 4.91 | 0.000932 | -0.039 | 4.81 | 0.000808 | 0 | 4.91 | 0.000932 | -0.039 |  | CFL | None | 4810 | 0.808 | 4810 | 0.808 | 1.02 | 1.15 | -0.0081081 | 4810 | 0.808 | 4810 | 0.808 | 1.02 | 1.15 | -0.00811
CFLNonePGERFFExCZ04 | Com-Iltg-dWatt-CFL_OSnone | PGE | RFF | Ex | CZ04 | 4.81 | 0.000808 | 0 | 5.04 | 0.000937 | -0.031 | 4.81 | 0.000808 | 0 | 5.04 | 0.000937 | -0.031 |  | CFL | None | 4810 | 0.808 | 4810 | 0.808 | 1.05 | 1.16 | -0.0064449 | 4810 | 0.808 | 4810 | 0.808 | 1.05 | 1.16 | -0.00644
CFLNonePGERFFExCZ05 | Com-Iltg-dWatt-CFL_OSnone | PGE | RFF | Ex | CZ05 | 4.81 | 0.000808 | 0 | 4.89 | 0.000923 | -0.0394 | 4.81 | 0.000808 | 0 | 4.89 | 0.000923 | -0.0394 |  | CFL | None | 4810 | 0.808 | 4810 | 0.808 | 1.02 | 1.14 | -0.0081913 | 4810 | 0.808 | 4810 | 0.808 | 1.02 | 1.14 | -0.00819
CFLNonePGERFFExCZ11 | Com-Iltg-dWatt-CFL_OSnone | PGE | RFF | Ex | CZ11 | 4.81 | 0.000808 | 0 | 5.07 | 0.000956 | -0.0303 | 4.81 | 0.000808 | 0 | 5.07 | 0.000956 | -0.0303 |  | CFL | None | 4810 | 0.808 | 4810 | 0.808 | 1.05 | 1.18 | -0.0062994 | 4810 | 0.808 | 4810 | 0.808 | 1.05 | 1.18 | -0.0063
CFLNonePGERFFExCZ12 | Com-Iltg-dWatt-CFL_OSnone | PGE | RFF | Ex | CZ12 | 4.81 | 0.000808 | 0 | 5.04 | 0.000946 | -0.0317 | 4.81 | 0.000808 | 0 | 5.04 | 0.000946 | -0.0317 |  | CFL | None | 4810 | 0.808 | 4810 | 0.808 | 1.05 | 1.17 | -0.0065904 | 4810 | 0.808 | 4810 | 0.808 | 1.05 | 1.17 | -0.00659
CFLNonePGERFFExCZ13 | Com-Iltg-dWatt-CFL_OSnone | PGE | RFF | Ex | CZ13 | 4.81 | 0.000808 | 0 | 5.08 | 0.000942 | -0.029 | 4.81 | 0.000808 | 0 | 5.08 | 0.000942 | -0.029 |  | CFL | None | 4810 | 0.808 | 4810 | 0.808 | 1.06 | 1.17 | -0.0060291 | 4810 | 0.808 | 4810 | 0.808 | 1.06 | 1.17 | -0.00603
CFLNonePGERFFExCZ16 | Com-Iltg-dWatt-CFL_OSnone | PGE | RFF | Ex | CZ16 | 4.81 | 0.000808 | 0 | 4.72 | 0.000929 | -0.0553 | 4.81 | 0.000808 | 0 | 4.72 | 0.000929 | -0.0553 |  | CFL | None | 4810 | 0.808 | 4810 | 0.808 | 0.981 | 1.15 | -0.011497 | 4810 | 0.808 | 4810 | 0.808 | 0.981 | 1.15 | -0.0115
CFLNonePGERFFExIOU | Com-Iltg-dWatt-CFL_OSnone | PGE | RFF | Ex | IOU | 4.81 | 0.000808 | 0 | 4.9886 | 0.00093854 | -0.034654 | 4.81 | 0.000808 | 0 | 4.9886 | 0.00093854 | -0.034654 |  | CFL | None | 4810 | 0.808 | 4810 | 0.808 | 1.04 | 1.16 | -0.0072047 | 4810 | 0.808 | 4810 | 0.808 | 1.04 | 1.16 | -0.0072
CFLNonePGERFFNewCZ01 | Com-Iltg-dWatt-CFL_OSnone | PGE | RFF | New | CZ01 | 4.81 | 0.000808 | 0 | 4.52 | 0.000879 | -0.0596 | 4.81 | 0.000808 | 0 | 4.52 | 0.000879 | -0.0596 |  | CFL | None | 4810 | 0.808 | 4810 | 0.808 | 0.94 | 1.09 | -0.012391 | 4810 | 0.808 | 4810 | 0.808 | 0.94 | 1.09 | -0.0124
CFLNonePGERFFNewCZ02 | Com-Iltg-dWatt-CFL_OSnone | PGE | RFF | New | CZ02 | 4.81 | 0.000808 | 0 | 4.86 | 0.000974 | -0.0437 | 4.81 | 0.000808 | 0 | 4.86 | 0.000974 | -0.0437 |  | CFL | None | 4810 | 0.808 | 4810 | 0.808 | 1.01 | 1.21 | -0.0090852 | 4810 | 0.808 | 4810 | 0.808 | 1.01 | 1.21 | -0.00909
CFLNonePGERFFNewCZ03 | Com-Iltg-dWatt-CFL_OSnone | PGE | RFF | New | CZ03 | 4.81 | 0.000808 | 0 | 4.76 | 0.000945 | -0.0445 | 4.81 | 0.000808 | 0 | 4.76 | 0.000945 | -0.0445 |  | CFL | None | 4810 | 0.808 | 4810 | 0.808 | 0.99 | 1.17 | -0.0092516 | 4810 | 0.808 | 4810 | 0.808 | 0.99 | 1.17 | -0.00925
CFLNonePGERFFNewCZ04 | Com-Iltg-dWatt-CFL_OSnone | PGE | RFF | New | CZ04 | 4.81 | 0.000808 | 0 | 4.94 | 0.000964 | -0.0368 | 4.81 | 0.000808 | 0 | 4.94 | 0.000964 | -0.0368 |  | CFL | None | 4810 | 0.808 | 4810 | 0.808 | 1.03 | 1.19 | -0.0076507 | 4810 | 0.808 | 4810 | 0.808 | 1.03 | 1.19 | -0.00765
CFLNonePGERFFNewCZ05 | Com-Iltg-dWatt-CFL_OSnone | PGE | RFF | New | CZ05 | 4.81 | 0.000808 | 0 | 4.76 | 0.000932 | -0.0394 | 4.81 | 0.000808 | 0 | 4.76 | 0.000932 | -0.0394 |  | CFL | None | 4810 | 0.808 | 4810 | 0.808 | 0.99 | 1.15 | -0.0081913 | 4810 | 0.808 | 4810 | 0.808 | 0.99 | 1.15 | -0.00819
CFLNonePGERFFNewCZ11 | Com-Iltg-dWatt-CFL_OSnone | PGE | RFF | New | CZ11 | 4.81 | 0.000808 | 0 | 5.05 | 0.000996 | -0.0332 | 4.81 | 0.000808 | 0 | 5.05 | 0.000996 | -0.0332 |  | CFL | None | 4810 | 0.808 | 4810 | 0.808 | 1.05 | 1.23 | -0.0069023 | 4810 | 0.808 | 4810 | 0.808 | 1.05 | 1.23 | -0.0069
CFLNonePGERFFNewCZ12 | Com-Iltg-dWatt-CFL_OSnone | PGE | RFF | New | CZ12 | 4.81 | 0.000808 | 0 | 5 | 0.000986 | -0.039 | 4.81 | 0.000808 | 0 | 5 | 0.000986 | -0.039 |  | CFL | None | 4810 | 0.808 | 4810 | 0.808 | 1.04 | 1.22 | -0.0081081 | 4810 | 0.808 | 4810 | 0.808 | 1.04 | 1.22 | -0.00811
CFLNonePGERFFNewCZ13 | Com-Iltg-dWatt-CFL_OSnone | PGE | RFF | New | CZ13 | 4.81 | 0.000808 | 0 | 5.06 | 0.000984 | -0.0346 | 4.81 | 0.000808 | 0 | 5.06 | 0.000984 | -0.0346 |  | CFL | None | 4810 | 0.808 | 4810 | 0.808 | 1.05 | 1.22 | -0.0071933 | 4810 | 0.808 | 4810 | 0.808 | 1.05 | 1.22 | -0.00719
CFLNonePGERFFNewCZ16 | Com-Iltg-dWatt-CFL_OSnone | PGE | RFF | New | CZ16 | 4.81 | 0.000808 | 0 | 4.68 | 0.000952 | -0.0615 | 4.81 | 0.000808 | 0 | 4.68 | 0.000952 | -0.0615 |  | CFL | None | 4810 | 0.808 | 4810 | 0.808 | 0.973 | 1.18 | -0.012786 | 4810 | 0.808 | 4810 | 0.808 | 0.973 | 1.18 | -0.0128
CFLNonePGERFFNewIOU | Com-Iltg-dWatt-CFL_OSnone | PGE | RFF | New | IOU | 4.81 | 0.000808 | 0 | 4.9059 | 0.000967 | -0.040184 | 4.81 | 0.000808 | 0 | 4.9059 | 0.000967 | -0.040184 |  | CFL | None | 4810 | 0.808 | 4810 | 0.808 | 1.02 | 1.2 | -0.0083542 | 4810 | 0.808 | 4810 | 0.808 | 1.02 | 1.2 | -0.00835
CFLNonePGERSDExCZ01 | Com-Iltg-dWatt-CFL_OSnone | PGE | RSD | Ex | CZ01 | 4.83 | 0.0008 | 0 | 4.63 | 0.000938 | -0.0603 | 4.83 | 0.0008 | 0 | 4.63 | 0.000938 | -0.0603 |  | CFL | None | 4830 | 0.8 | 4830 | 0.8 | 0.959 | 1.17 | -0.012484 | 4830 | 0.8 | 4830 | 0.8 | 0.959 | 1.17 | -0.0125
CFLNonePGERSDExCZ02 | Com-Iltg-dWatt-CFL_OSnone | PGE | RSD | Ex | CZ02 | 4.83 | 0.0008 | 0 | 5 | 0.000938 | -0.0354 | 4.83 | 0.0008 | 0 | 5 | 0.000938 | -0.0354 |  | CFL | None | 4830 | 0.8 | 4830 | 0.8 | 1.04 | 1.17 | -0.0073292 | 4830 | 0.8 | 4830 | 0.8 | 1.04 | 1.17 | -0.00733
CFLNonePGERSDExCZ03 | Com-Iltg-dWatt-CFL_OSnone | PGE | RSD | Ex | CZ03 | 4.83 | 0.0008 | 0 | 4.94 | 0.000939 | -0.0396 | 4.83 | 0.0008 | 0 | 4.94 | 0.000939 | -0.0396 |  | CFL | None | 4830 | 0.8 | 4830 | 0.8 | 1.02 | 1.17 | -0.0081988 | 4830 | 0.8 | 4830 | 0.8 | 1.02 | 1.17 | -0.0082
CFLNonePGERSDExCZ04 | Com-Iltg-dWatt-CFL_OSnone | PGE | RSD | Ex | CZ04 | 4.83 | 0.0008 | 0 | 5.09 | 0.000942 | -0.0294 | 4.83 | 0.0008 | 0 | 5.09 | 0.000942 | -0.0294 |  | CFL | None | 4830 | 0.8 | 4830 | 0.8 | 1.05 | 1.18 | -0.006087 | 4830 | 0.8 | 4830 | 0.8 | 1.05 | 1.18 | -0.00609
CFLNonePGERSDExCZ05 | Com-Iltg-dWatt-CFL_OSnone | PGE | RSD | Ex | CZ05 | 4.83 | 0.0008 | 0 | 4.95 | 0.000932 | -0.0382 | 4.83 | 0.0008 | 0 | 4.95 | 0.000932 | -0.0382 |  | CFL | None | 4830 | 0.8 | 4830 | 0.8 | 1.02 | 1.17 | -0.0079089 | 4830 | 0.8 | 4830 | 0.8 | 1.02 | 1.17 | -0.00791
CFLNonePGERSDExCZ11 | Com-Iltg-dWatt-CFL_OSnone | PGE | RSD | Ex | CZ11 | 4.83 | 0.0008 | 0 | 5.11 | 0.000947 | -0.0306 | 4.83 | 0.0008 | 0 | 5.11 | 0.000947 | -0.0306 |  | CFL | None | 4830 | 0.8 | 4830 | 0.8 | 1.06 | 1.18 | -0.0063354 | 4830 | 0.8 | 4830 | 0.8 | 1.06 | 1.18 | -0.00634
CFLNonePGERSDExCZ12 | Com-Iltg-dWatt-CFL_OSnone | PGE | RSD | Ex | CZ12 | 4.83 | 0.0008 | 0 | 5.06 | 0.000917 | -0.0316 | 4.83 | 0.0008 | 0 | 5.06 | 0.000917 | -0.0316 |  | CFL | None | 4830 | 0.8 | 4830 | 0.8 | 1.05 | 1.15 | -0.0065424 | 4830 | 0.8 | 4830 | 0.8 | 1.05 | 1.15 | -0.00654
CFLNonePGERSDExCZ13 | Com-Iltg-dWatt-CFL_OSnone | PGE | RSD | Ex | CZ13 | 4.83 | 0.0008 | 0 | 5.14 | 0.000943 | -0.029 | 4.83 | 0.0008 | 0 | 5.14 | 0.000943 | -0.029 |  | CFL | None | 4830 | 0.8 | 4830 | 0.8 | 1.06 | 1.18 | -0.0060041 | 4830 | 0.8 | 4830 | 0.8 | 1.06 | 1.18 | -0.006
CFLNonePGERSDExCZ16 | Com-Iltg-dWatt-CFL_OSnone | PGE | RSD | Ex | CZ16 | 4.83 | 0.0008 | 0 | 4.71 | 0.000916 | -0.0541 | 4.83 | 0.0008 | 0 | 4.71 | 0.000916 | -0.0541 |  | CFL | None | 4830 | 0.8 | 4830 | 0.8 | 0.975 | 1.15 | -0.011201 | 4830 | 0.8 | 4830 | 0.8 | 0.975 | 1.15 | -0.0112
CFLNonePGERSDExIOU | Com-Iltg-dWatt-CFL_OSnone | PGE | RSD | Ex | IOU | 4.83 | 0.0008 | 0 | 5.0232 | 0.00093527 | -0.034529 | 4.83 | 0.0008 | 0 | 5.0232 | 0.00093527 | -0.034529 |  | CFL | None | 4830 | 0.8 | 4830 | 0.8 | 1.04 | 1.17 | -0.007149 | 4830 | 0.8 | 4830 | 0.8 | 1.04 | 1.17 | -0.00715
CFLNonePGERSDNewCZ01 | Com-Iltg-dWatt-CFL_OSnone | PGE | RSD | New | CZ01 | 4.83 | 0.0008 | 0 | 4.61 | 0.00091 | -0.0146 | 4.83 | 0.0008 | 0 | 4.61 | 0.00091 | -0.0146 |  | CFL | None | 4830 | 0.8 | 4830 | 0.8 | 0.954 | 1.14 | -0.0030228 | 4830 | 0.8 | 4830 | 0.8 | 0.954 | 1.14 | -0.00302
CFLNonePGERSDNewCZ02 | Com-Iltg-dWatt-CFL_OSnone | PGE | RSD | New | CZ02 | 4.83 | 0.0008 | 0 | 4.94 | 0.000974 | -0.0393 | 4.83 | 0.0008 | 0 | 4.94 | 0.000974 | -0.0393 |  | CFL | None | 4830 | 0.8 | 4830 | 0.8 | 1.02 | 1.22 | -0.0081366 | 4830 | 0.8 | 4830 | 0.8 | 1.02 | 1.22 | -0.00814
CFLNonePGERSDNewCZ03 | Com-Iltg-dWatt-CFL_OSnone | PGE | RSD | New | CZ03 | 4.83 | 0.0008 | 0 | 4.8 | 0.000928 | -0.0492 | 4.83 | 0.0008 | 0 | 4.8 | 0.000928 | -0.0492 |  | CFL | None | 4830 | 0.8 | 4830 | 0.8 | 0.994 | 1.16 | -0.010186 | 4830 | 0.8 | 4830 | 0.8 | 0.994 | 1.16 | -0.0102
CFLNonePGERSDNewCZ04 | Com-Iltg-dWatt-CFL_OSnone | PGE | RSD | New | CZ04 | 4.83 | 0.0008 | 0 | 5.03 | 0.000974 | -0.0329 | 4.83 | 0.0008 | 0 | 5.03 | 0.000974 | -0.0329 |  | CFL | None | 4830 | 0.8 | 4830 | 0.8 | 1.04 | 1.22 | -0.0068116 | 4830 | 0.8 | 4830 | 0.8 | 1.04 | 1.22 | -0.00681
CFLNonePGERSDNewCZ05 | Com-Iltg-dWatt-CFL_OSnone | PGE | RSD | New | CZ05 | 4.83 | 0.0008 | 0 | 4.84 | 0.000938 | -0.0422 | 4.83 | 0.0008 | 0 | 4.84 | 0.000938 | -0.0422 |  | CFL | None | 4830 | 0.8 | 4830 | 0.8 | 1 | 1.17 | -0.0087371 | 4830 | 0.8 | 4830 | 0.8 | 1 | 1.17 | -0.00874
CFLNonePGERSDNewCZ11 | Com-Iltg-dWatt-CFL_OSnone | PGE | RSD | New | CZ11 | 4.83 | 0.0008 | 0 | 5.1 | 0.000994 | -0.0339 | 4.83 | 0.0008 | 0 | 5.1 | 0.000994 | -0.0339 |  | CFL | None | 4830 | 0.8 | 4830 | 0.8 | 1.06 | 1.24 | -0.0070186 | 4830 | 0.8 | 4830 | 0.8 | 1.06 | 1.24 | -0.00702
CFLNonePGERSDNewCZ12 | Com-Iltg-dWatt-CFL_OSnone | PGE | RSD | New | CZ12 | 4.83 | 0.0008 | 0 | 5.02 | 0.000958 | -0.0341 | 4.83 | 0.0008 | 0 | 5.02 | 0.000958 | -0.0341 |  | CFL | None | 4830 | 0.8 | 4830 | 0.8 | 1.04 | 1.2 | -0.00706 | 4830 | 0.8 | 4830 | 0.8 | 1.04 | 1.2 | -0.00706
CFLNonePGERSDNewCZ13 | Com-Iltg-dWatt-CFL_OSnone | PGE | RSD | New | CZ13 | 4.83 | 0.0008 | 0 | 5.12 | 0.000992 | -0.0324 | 4.83 | 0.0008 | 0 | 5.12 | 0.000992 | -0.0324 |  | CFL | None | 4830 | 0.8 | 4830 | 0.8 | 1.06 | 1.24 | -0.0067081 | 4830 | 0.8 | 4830 | 0.8 | 1.06 | 1.24 | -0.00671
CFLNonePGERSDNewCZ16 | Com-Iltg-dWatt-CFL_OSnone | PGE | RSD | New | CZ16 | 4.83 | 0.0008 | 0 | 4.68 | 0.000943 | -0.0452 | 4.83 | 0.0008 | 0 | 4.68 | 0.000943 | -0.0452 |  | CFL | None | 4830 | 0.8 | 4830 | 0.8 | 0.969 | 1.18 | -0.0093582 | 4830 | 0.8 | 4830 | 0.8 | 0.969 | 1.18 | -0.00936
CFLNonePGERSDNewIOU | Com-Iltg-dWatt-CFL_OSnone | PGE | RSD | New | IOU | 4.83 | 0.0008 | 0 | 4.955 | 0.00095805 | -0.038862 | 4.83 | 0.0008 | 0 | 4.955 | 0.00095805 | -0.038862 |  | CFL | None | 4830 | 0.8 | 4830 | 0.8 | 1.03 | 1.2 | -0.008046 | 4830 | 0.8 | 4830 | 0.8 | 1.03 | 1.2 | -0.00805
CFLNonePGERt3ExCZ01 | Com-Iltg-dWatt-CFL_OSnone | PGE | Rt3 | Ex | CZ01 | 3.71 | 0.000631 | 0 | 3.56 | 0.000782 | -0.0545 | 3.71 | 0.000631 | 0 | 3.56 | 0.000782 | -0.0545 |  | CFL | None | 3710 | 0.631 | 3710 | 0.631 | 0.96 | 1.24 | -0.01469 | 3710 | 0.631 | 3710 | 0.631 | 0.96 | 1.24 | -0.0147
CFLNonePGERt3ExCZ02 | Com-Iltg-dWatt-CFL_OSnone | PGE | Rt3 | Ex | CZ02 | 3.71 | 0.000631 | 0 | 3.9 | 0.000767 | -0.0277 | 3.71 | 0.000631 | 0 | 3.9 | 0.000767 | -0.0277 |  | CFL | None | 3710 | 0.631 | 3710 | 0.631 | 1.05 | 1.22 | -0.0074663 | 3710 | 0.631 | 3710 | 0.631 | 1.05 | 1.22 | -0.00747
CFLNonePGERt3ExCZ03 | Com-Iltg-dWatt-CFL_OSnone | PGE | Rt3 | Ex | CZ03 | 3.71 | 0.000631 | 0 | 3.92 | 0.000772 | -0.0266 | 3.71 | 0.000631 | 0 | 3.92 | 0.000772 | -0.0266 |  | CFL | None | 3710 | 0.631 | 3710 | 0.631 | 1.06 | 1.22 | -0.0071698 | 3710 | 0.631 | 3710 | 0.631 | 1.06 | 1.22 | -0.00717
CFLNonePGERt3ExCZ04 | Com-Iltg-dWatt-CFL_OSnone | PGE | Rt3 | Ex | CZ04 | 3.71 | 0.000631 | 0 | 3.99 | 0.000771 | -0.0183 | 3.71 | 0.000631 | 0 | 3.99 | 0.000771 | -0.0183 |  | CFL | None | 3710 | 0.631 | 3710 | 0.631 | 1.08 | 1.22 | -0.0049326 | 3710 | 0.631 | 3710 | 0.631 | 1.08 | 1.22 | -0.00493
CFLNonePGERt3ExCZ05 | Com-Iltg-dWatt-CFL_OSnone | PGE | Rt3 | Ex | CZ05 | 3.71 | 0.000631 | 0 | 3.93 | 0.000764 | -0.022 | 3.71 | 0.000631 | 0 | 3.93 | 0.000764 | -0.022 |  | CFL | None | 3710 | 0.631 | 3710 | 0.631 | 1.06 | 1.21 | -0.0059299 | 3710 | 0.631 | 3710 | 0.631 | 1.06 | 1.21 | -0.00593
CFLNonePGERt3ExCZ11 | Com-Iltg-dWatt-CFL_OSnone | PGE | Rt3 | Ex | CZ11 | 3.71 | 0.000631 | 0 | 3.92 | 0.000774 | -0.0263 | 3.71 | 0.000631 | 0 | 3.92 | 0.000774 | -0.0263 |  | CFL | None | 3710 | 0.631 | 3710 | 0.631 | 1.06 | 1.23 | -0.0070889 | 3710 | 0.631 | 3710 | 0.631 | 1.06 | 1.23 | -0.00709
CFLNonePGERt3ExCZ12 | Com-Iltg-dWatt-CFL_OSnone | PGE | Rt3 | Ex | CZ12 | 3.71 | 0.000631 | 0 | 3.93 | 0.000778 | -0.0256 | 3.71 | 0.000631 | 0 | 3.93 | 0.000778 | -0.0256 |  | CFL | None | 3710 | 0.631 | 3710 | 0.631 | 1.06 | 1.23 | -0.0069003 | 3710 | 0.631 | 3710 | 0.631 | 1.06 | 1.23 | -0.0069
CFLNonePGERt3ExCZ13 | Com-Iltg-dWatt-CFL_OSnone | PGE | Rt3 | Ex | CZ13 | 3.71 | 0.000631 | 0 | 3.95 | 0.000772 | -0.0242 | 3.71 | 0.000631 | 0 | 3.95 | 0.000772 | -0.0242 |  | CFL | None | 3710 | 0.631 | 3710 | 0.631 | 1.06 | 1.22 | -0.0065229 | 3710 | 0.631 | 3710 | 0.631 | 1.06 | 1.22 | -0.00652
CFLNonePGERt3ExCZ16 | Com-Iltg-dWatt-CFL_OSnone | PGE | Rt3 | Ex | CZ16 | 3.71 | 0.000631 | 0 | 3.61 | 0.000755 | -0.0508 | 3.71 | 0.000631 | 0 | 3.61 | 0.000755 | -0.0508 |  | CFL | None | 3710 | 0.631 | 3710 | 0.631 | 0.973 | 1.2 | -0.013693 | 3710 | 0.631 | 3710 | 0.631 | 0.973 | 1.2 | -0.0137
CFLNonePGERt3ExIOU | Com-Iltg-dWatt-CFL_OSnone | PGE | Rt3 | Ex | IOU | 3.71 | 0.000631 | 0 | 3.9306 | 0.00077288 | -0.025173 | 3.71 | 0.000631 | 0 | 3.9306 | 0.00077288 | -0.025173 |  | CFL | None | 3710 | 0.631 | 3710 | 0.631 | 1.06 | 1.22 | -0.0067851 | 3710 | 0.631 | 3710 | 0.631 | 1.06 | 1.22 | -0.00679
CFLNonePGERt3NewCZ01 | Com-Iltg-dWatt-CFL_OSnone | PGE | Rt3 | New | CZ01 | 3.71 | 0.000631 | 0 | 3.49 | 0.000769 | -0.0601 | 3.71 | 0.000631 | 0 | 3.49 | 0.000769 | -0.0601 |  | CFL | None | 3710 | 0.631 | 3710 | 0.631 | 0.941 | 1.22 | -0.016199 | 3710 | 0.631 | 3710 | 0.631 | 0.941 | 1.22 | -0.0162
CFLNonePGERt3NewCZ02 | Com-Iltg-dWatt-CFL_OSnone | PGE | Rt3 | New | CZ02 | 3.71 | 0.000631 | 0 | 3.8 | 0.00075 | -0.0324 | 3.71 | 0.000631 | 0 | 3.8 | 0.00075 | -0.0324 |  | CFL | None | 3710 | 0.631 | 3710 | 0.631 | 1.02 | 1.19 | -0.0087332 | 3710 | 0.631 | 3710 | 0.631 | 1.02 | 1.19 | -0.00873
CFLNonePGERt3NewCZ03 | Com-Iltg-dWatt-CFL_OSnone | PGE | Rt3 | New | CZ03 | 3.71 | 0.000631 | 0 | 3.76 | 0.000755 | -0.0329 | 3.71 | 0.000631 | 0 | 3.76 | 0.000755 | -0.0329 |  | CFL | None | 3710 | 0.631 | 3710 | 0.631 | 1.01 | 1.2 | -0.0088679 | 3710 | 0.631 | 3710 | 0.631 | 1.01 | 1.2 | -0.00887
CFLNonePGERt3NewCZ04 | Com-Iltg-dWatt-CFL_OSnone | PGE | Rt3 | New | CZ04 | 3.71 | 0.000631 | 0 | 3.87 | 0.00076 | -0.0236 | 3.71 | 0.000631 | 0 | 3.87 | 0.00076 | -0.0236 |  | CFL | None | 3710 | 0.631 | 3710 | 0.631 | 1.04 | 1.2 | -0.0063612 | 3710 | 0.631 | 3710 | 0.631 | 1.04 | 1.2 | -0.00636
CFLNonePGERt3NewCZ05 | Com-Iltg-dWatt-CFL_OSnone | PGE | Rt3 | New | CZ05 | 3.71 | 0.000631 | 0 | 3.8 | 0.000752 | -0.0274 | 3.71 | 0.000631 | 0 | 3.8 | 0.000752 | -0.0274 |  | CFL | None | 3710 | 0.631 | 3710 | 0.631 | 1.02 | 1.19 | -0.0073854 | 3710 | 0.631 | 3710 | 0.631 | 1.02 | 1.19 | -0.00739
CFLNonePGERt3NewCZ11 | Com-Iltg-dWatt-CFL_OSnone | PGE | Rt3 | New | CZ11 | 3.71 | 0.000631 | 0 | 3.89 | 0.000777 | -0.0279 | 3.71 | 0.000631 | 0 | 3.89 | 0.000777 | -0.0279 |  | CFL | None | 3710 | 0.631 | 3710 | 0.631 | 1.05 | 1.23 | -0.0075202 | 3710 | 0.631 | 3710 | 0.631 | 1.05 | 1.23 | -0.00752
CFLNonePGERt3NewCZ12 | Com-Iltg-dWatt-CFL_OSnone | PGE | Rt3 | New | CZ12 | 3.71 | 0.000631 | 0 | 3.87 | 0.000774 | -0.0298 | 3.71 | 0.000631 | 0 | 3.87 | 0.000774 | -0.0298 |  | CFL | None | 3710 | 0.631 | 3710 | 0.631 | 1.04 | 1.23 | -0.0080323 | 3710 | 0.631 | 3710 | 0.631 | 1.04 | 1.23 | -0.00803
CFLNonePGERt3NewCZ13 | Com-Iltg-dWatt-CFL_OSnone | PGE | Rt3 | New | CZ13 | 3.71 | 0.000631 | 0 | 3.91 | 0.000769 | -0.0268 | 3.71 | 0.000631 | 0 | 3.91 | 0.000769 | -0.0268 |  | CFL | None | 3710 | 0.631 | 3710 | 0.631 | 1.05 | 1.22 | -0.0072237 | 3710 | 0.631 | 3710 | 0.631 | 1.05 | 1.22 | -0.00722
CFLNonePGERt3NewCZ16 | Com-Iltg-dWatt-CFL_OSnone | PGE | Rt3 | New | CZ16 | 3.71 | 0.000631 | 0 | 3.54 | 0.000694 | -0.0486 | 3.71 | 0.000631 | 0 | 3.54 | 0.000694 | -0.0486 |  | CFL | None | 3710 | 0.631 | 3710 | 0.631 | 0.954 | 1.1 | -0.0131 | 3710 | 0.631 | 3710 | 0.631 | 0.954 | 1.1 | -0.0131
CFLNonePGERt3NewIOU | Com-Iltg-dWatt-CFL_OSnone | PGE | Rt3 | New | IOU | 3.71 | 0.000631 | 0 | 3.8399 | 0.00076428 | -0.029557 | 3.71 | 0.000631 | 0 | 3.8399 | 0.00076428 | -0.029557 |  | CFL | None | 3710 | 0.631 | 3710 | 0.631 | 1.04 | 1.21 | -0.0079669 | 3710 | 0.631 | 3710 | 0.631 | 1.04 | 1.21 | -0.00797
CFLNonePGERtLExCZ01 | Com-Iltg-dWatt-CFL_OSnone | PGE | RtL | Ex | CZ01 | 4.35 | 0.000689 | 0 | 4.22 | 0.000839 | -0.0587 | 4.35 | 0.000689 | 0 | 4.22 | 0.000839 | -0.0587 |  | CFL | None | 4350 | 0.689 | 4350 | 0.689 | 0.97 | 1.22 | -0.013494 | 4350 | 0.689 | 4350 | 0.689 | 0.97 | 1.22 | -0.0135
CFLNonePGERtLExCZ02 | Com-Iltg-dWatt-CFL_OSnone | PGE | RtL | Ex | CZ02 | 4.35 | 0.000689 | 0 | 4.57 | 0.000837 | -0.0305 | 4.35 | 0.000689 | 0 | 4.57 | 0.000837 | -0.0305 |  | CFL | None | 4350 | 0.689 | 4350 | 0.689 | 1.05 | 1.21 | -0.0070115 | 4350 | 0.689 | 4350 | 0.689 | 1.05 | 1.21 | -0.00701
CFLNonePGERtLExCZ03 | Com-Iltg-dWatt-CFL_OSnone | PGE | RtL | Ex | CZ03 | 4.35 | 0.000689 | 0 | 4.6 | 0.000833 | -0.0287 | 4.35 | 0.000689 | 0 | 4.6 | 0.000833 | -0.0287 |  | CFL | None | 4350 | 0.689 | 4350 | 0.689 | 1.06 | 1.21 | -0.0065977 | 4350 | 0.689 | 4350 | 0.689 | 1.06 | 1.21 | -0.0066
CFLNonePGERtLExCZ04 | Com-Iltg-dWatt-CFL_OSnone | PGE | RtL | Ex | CZ04 | 4.35 | 0.000689 | 0 | 4.67 | 0.000838 | -0.0214 | 4.35 | 0.000689 | 0 | 4.67 | 0.000838 | -0.0214 |  | CFL | None | 4350 | 0.689 | 4350 | 0.689 | 1.07 | 1.22 | -0.0049195 | 4350 | 0.689 | 4350 | 0.689 | 1.07 | 1.22 | -0.00492
CFLNonePGERtLExCZ05 | Com-Iltg-dWatt-CFL_OSnone | PGE | RtL | Ex | CZ05 | 4.35 | 0.000689 | 0 | 4.58 | 0.000823 | -0.0284 | 4.35 | 0.000689 | 0 | 4.58 | 0.000823 | -0.0284 |  | CFL | None | 4350 | 0.689 | 4350 | 0.689 | 1.05 | 1.19 | -0.0065287 | 4350 | 0.689 | 4350 | 0.689 | 1.05 | 1.19 | -0.00653
CFLNonePGERtLExCZ11 | Com-Iltg-dWatt-CFL_OSnone | PGE | RtL | Ex | CZ11 | 4.35 | 0.000689 | 0 | 4.6 | 0.000845 | -0.0291 | 4.35 | 0.000689 | 0 | 4.6 | 0.000845 | -0.0291 |  | CFL | None | 4350 | 0.689 | 4350 | 0.689 | 1.06 | 1.23 | -0.0066897 | 4350 | 0.689 | 4350 | 0.689 | 1.06 | 1.23 | -0.00669
CFLNonePGERtLExCZ12 | Com-Iltg-dWatt-CFL_OSnone | PGE | RtL | Ex | CZ12 | 4.35 | 0.000689 | 0 | 4.61 | 0.000853 | -0.0266 | 4.35 | 0.000689 | 0 | 4.61 | 0.000853 | -0.0266 |  | CFL | None | 4350 | 0.689 | 4350 | 0.689 | 1.06 | 1.24 | -0.0061149 | 4350 | 0.689 | 4350 | 0.689 | 1.06 | 1.24 | -0.00611
CFLNonePGERtLExCZ13 | Com-Iltg-dWatt-CFL_OSnone | PGE | RtL | Ex | CZ13 | 4.35 | 0.000689 | 0 | 4.64 | 0.000846 | -0.0257 | 4.35 | 0.000689 | 0 | 4.64 | 0.000846 | -0.0257 |  | CFL | None | 4350 | 0.689 | 4350 | 0.689 | 1.07 | 1.23 | -0.005908 | 4350 | 0.689 | 4350 | 0.689 | 1.07 | 1.23 | -0.00591
CFLNonePGERtLExCZ16 | Com-Iltg-dWatt-CFL_OSnone | PGE | RtL | Ex | CZ16 | 4.35 | 0.000689 | 0 | 4.23 | 0.000812 | -0.0578 | 4.35 | 0.000689 | 0 | 4.23 | 0.000812 | -0.0578 |  | CFL | None | 4350 | 0.689 | 4350 | 0.689 | 0.972 | 1.18 | -0.013287 | 4350 | 0.689 | 4350 | 0.689 | 0.972 | 1.18 | -0.0133
CFLNonePGERtLExIOU | Com-Iltg-dWatt-CFL_OSnone | PGE | RtL | Ex | IOU | 4.35 | 0.000689 | 0 | 4.6102 | 0.00084089 | -0.027301 | 4.35 | 0.000689 | 0 | 4.6102 | 0.00084089 | -0.027301 |  | CFL | None | 4350 | 0.689 | 4350 | 0.689 | 1.06 | 1.22 | -0.0062761 | 4350 | 0.689 | 4350 | 0.689 | 1.06 | 1.22 | -0.00628
CFLNonePGERtLNewCZ01 | Com-Iltg-dWatt-CFL_OSnone | PGE | RtL | New | CZ01 | 4.35 | 0.000689 | 0 | 4.19 | 0.000822 | -0.0652 | 4.35 | 0.000689 | 0 | 4.19 | 0.000822 | -0.0652 |  | CFL | None | 4350 | 0.689 | 4350 | 0.689 | 0.963 | 1.19 | -0.014989 | 4350 | 0.689 | 4350 | 0.689 | 0.963 | 1.19 | -0.015
CFLNonePGERtLNewCZ02 | Com-Iltg-dWatt-CFL_OSnone | PGE | RtL | New | CZ02 | 4.35 | 0.000689 | 0 | 4.52 | 0.000877 | -0.0347 | 4.35 | 0.000689 | 0 | 4.52 | 0.000877 | -0.0347 |  | CFL | None | 4350 | 0.689 | 4350 | 0.689 | 1.04 | 1.27 | -0.007977 | 4350 | 0.689 | 4350 | 0.689 | 1.04 | 1.27 | -0.00798
CFLNonePGERtLNewCZ03 | Com-Iltg-dWatt-CFL_OSnone | PGE | RtL | New | CZ03 | 4.35 | 0.000689 | 0 | 4.47 | 0.000852 | -0.0324 | 4.35 | 0.000689 | 0 | 4.47 | 0.000852 | -0.0324 |  | CFL | None | 4350 | 0.689 | 4350 | 0.689 | 1.03 | 1.24 | -0.0074483 | 4350 | 0.689 | 4350 | 0.689 | 1.03 | 1.24 | -0.00745
CFLNonePGERtLNewCZ04 | Com-Iltg-dWatt-CFL_OSnone | PGE | RtL | New | CZ04 | 4.35 | 0.000689 | 0 | 4.61 | 0.000867 | -0.0246 | 4.35 | 0.000689 | 0 | 4.61 | 0.000867 | -0.0246 |  | CFL | None | 4350 | 0.689 | 4350 | 0.689 | 1.06 | 1.26 | -0.0056552 | 4350 | 0.689 | 4350 | 0.689 | 1.06 | 1.26 | -0.00566
CFLNonePGERtLNewCZ05 | Com-Iltg-dWatt-CFL_OSnone | PGE | RtL | New | CZ05 | 4.35 | 0.000689 | 0 | 4.47 | 0.000832 | -0.0337 | 4.35 | 0.000689 | 0 | 4.47 | 0.000832 | -0.0337 |  | CFL | None | 4350 | 0.689 | 4350 | 0.689 | 1.03 | 1.21 | -0.0077471 | 4350 | 0.689 | 4350 | 0.689 | 1.03 | 1.21 | -0.00775
CFLNonePGERtLNewCZ11 | Com-Iltg-dWatt-CFL_OSnone | PGE | RtL | New | CZ11 | 4.35 | 0.000689 | 0 | 4.64 | 0.000881 | -0.031 | 4.35 | 0.000689 | 0 | 4.64 | 0.000881 | -0.031 |  | CFL | None | 4350 | 0.689 | 4350 | 0.689 | 1.07 | 1.28 | -0.0071264 | 4350 | 0.689 | 4350 | 0.689 | 1.07 | 1.28 | -0.00713
CFLNonePGERtLNewCZ12 | Com-Iltg-dWatt-CFL_OSnone | PGE | RtL | New | CZ12 | 4.35 | 0.000689 | 0 | 4.62 | 0.00089 | -0.0305 | 4.35 | 0.000689 | 0 | 4.62 | 0.00089 | -0.0305 |  | CFL | None | 4350 | 0.689 | 4350 | 0.689 | 1.06 | 1.29 | -0.0070115 | 4350 | 0.689 | 4350 | 0.689 | 1.06 | 1.29 | -0.00701
CFLNonePGERtLNewCZ13 | Com-Iltg-dWatt-CFL_OSnone | PGE | RtL | New | CZ13 | 4.35 | 0.000689 | 0 | 4.67 | 0.000883 | -0.029 | 4.35 | 0.000689 | 0 | 4.67 | 0.000883 | -0.029 |  | CFL | None | 4350 | 0.689 | 4350 | 0.689 | 1.07 | 1.28 | -0.0066667 | 4350 | 0.689 | 4350 | 0.689 | 1.07 | 1.28 | -0.00667
CFLNonePGERtLNewCZ16 | Com-Iltg-dWatt-CFL_OSnone | PGE | RtL | New | CZ16 | 4.35 | 0.000689 | 0 | 4.26 | 0.000842 | -0.0609 | 4.35 | 0.000689 | 0 | 4.26 | 0.000842 | -0.0609 |  | CFL | None | 4350 | 0.689 | 4350 | 0.689 | 0.979 | 1.22 | -0.014 | 4350 | 0.689 | 4350 | 0.689 | 0.979 | 1.22 | -0.014
CFLNonePGERtLNewIOU | Com-Iltg-dWatt-CFL_OSnone | PGE | RtL | New | IOU | 4.35 | 0.000689 | 0 | 4.5758 | 0.00087242 | -0.03072 | 4.35 | 0.000689 | 0 | 4.5758 | 0.00087242 | -0.03072 |  | CFL | None | 4350 | 0.689 | 4350 | 0.689 | 1.05 | 1.27 | -0.007062 | 4350 | 0.689 | 4350 | 0.689 | 1.05 | 1.27 | -0.00706
CFLNonePGERtSExCZ01 | Com-Iltg-dWatt-CFL_OSnone | PGE | RtS | Ex | CZ01 | 4.01 | 0.0007 | 0 | 3.88 | 0.000827 | -0.0481 | 4.01 | 0.0007 | 0 | 3.88 | 0.000827 | -0.0481 |  | CFL | None | 4010 | 0.7 | 4010 | 0.7 | 0.968 | 1.18 | -0.011995 | 4010 | 0.7 | 4010 | 0.7 | 0.968 | 1.18 | -0.012
CFLNonePGERtSExCZ02 | Com-Iltg-dWatt-CFL_OSnone | PGE | RtS | Ex | CZ02 | 4.01 | 0.0007 | 0 | 4.18 | 0.000835 | -0.0263 | 4.01 | 0.0007 | 0 | 4.18 | 0.000835 | -0.0263 |  | CFL | None | 4010 | 0.7 | 4010 | 0.7 | 1.04 | 1.19 | -0.0065586 | 4010 | 0.7 | 4010 | 0.7 | 1.04 | 1.19 | -0.00656
CFLNonePGERtSExCZ03 | Com-Iltg-dWatt-CFL_OSnone | PGE | RtS | Ex | CZ03 | 4.01 | 0.0007 | 0 | 4.18 | 0.000848 | -0.0248 | 4.01 | 0.0007 | 0 | 4.18 | 0.000848 | -0.0248 |  | CFL | None | 4010 | 0.7 | 4010 | 0.7 | 1.04 | 1.21 | -0.0061845 | 4010 | 0.7 | 4010 | 0.7 | 1.04 | 1.21 | -0.00618
CFLNonePGERtSExCZ04 | Com-Iltg-dWatt-CFL_OSnone | PGE | RtS | Ex | CZ04 | 4.01 | 0.0007 | 0 | 4.26 | 0.000848 | -0.0186 | 4.01 | 0.0007 | 0 | 4.26 | 0.000848 | -0.0186 |  | CFL | None | 4010 | 0.7 | 4010 | 0.7 | 1.06 | 1.21 | -0.0046384 | 4010 | 0.7 | 4010 | 0.7 | 1.06 | 1.21 | -0.00464
CFLNonePGERtSExCZ05 | Com-Iltg-dWatt-CFL_OSnone | PGE | RtS | Ex | CZ05 | 4.01 | 0.0007 | 0 | 4.18 | 0.000834 | -0.0218 | 4.01 | 0.0007 | 0 | 4.18 | 0.000834 | -0.0218 |  | CFL | None | 4010 | 0.7 | 4010 | 0.7 | 1.04 | 1.19 | -0.0054364 | 4010 | 0.7 | 4010 | 0.7 | 1.04 | 1.19 | -0.00544
CFLNonePGERtSExCZ11 | Com-Iltg-dWatt-CFL_OSnone | PGE | RtS | Ex | CZ11 | 4.01 | 0.0007 | 0 | 4.21 | 0.000857 | -0.0248 | 4.01 | 0.0007 | 0 | 4.21 | 0.000857 | -0.0248 |  | CFL | None | 4010 | 0.7 | 4010 | 0.7 | 1.05 | 1.22 | -0.0061845 | 4010 | 0.7 | 4010 | 0.7 | 1.05 | 1.22 | -0.00618
CFLNonePGERtSExCZ12 | Com-Iltg-dWatt-CFL_OSnone | PGE | RtS | Ex | CZ12 | 4.01 | 0.0007 | 0 | 4.2 | 0.000844 | -0.0256 | 4.01 | 0.0007 | 0 | 4.2 | 0.000844 | -0.0256 |  | CFL | None | 4010 | 0.7 | 4010 | 0.7 | 1.05 | 1.21 | -0.006384 | 4010 | 0.7 | 4010 | 0.7 | 1.05 | 1.21 | -0.00638
CFLNonePGERtSExCZ13 | Com-Iltg-dWatt-CFL_OSnone | PGE | RtS | Ex | CZ13 | 4.01 | 0.0007 | 0 | 4.23 | 0.000849 | -0.0232 | 4.01 | 0.0007 | 0 | 4.23 | 0.000849 | -0.0232 |  | CFL | None | 4010 | 0.7 | 4010 | 0.7 | 1.05 | 1.21 | -0.0057855 | 4010 | 0.7 | 4010 | 0.7 | 1.05 | 1.21 | -0.00579
CFLNonePGERtSExCZ16 | Com-Iltg-dWatt-CFL_OSnone | PGE | RtS | Ex | CZ16 | 4.01 | 0.0007 | 0 | 3.93 | 0.000832 | -0.0449 | 4.01 | 0.0007 | 0 | 3.93 | 0.000832 | -0.0449 |  | CFL | None | 4010 | 0.7 | 4010 | 0.7 | 0.98 | 1.19 | -0.011197 | 4010 | 0.7 | 4010 | 0.7 | 0.98 | 1.19 | -0.0112
CFLNonePGERtSExIOU | Com-Iltg-dWatt-CFL_OSnone | PGE | RtS | Ex | IOU | 4.01 | 0.0007 | 0 | 4.2007 | 0.0008462 | -0.024223 | 4.01 | 0.0007 | 0 | 4.2007 | 0.0008462 | -0.024223 |  | CFL | None | 4010 | 0.7 | 4010 | 0.7 | 1.05 | 1.21 | -0.0060407 | 4010 | 0.7 | 4010 | 0.7 | 1.05 | 1.21 | -0.00604
CFLNonePGERtSNewCZ01 | Com-Iltg-dWatt-CFL_OSnone | PGE | RtS | New | CZ01 | 4.01 | 0.0007 | 0 | 3.86 | 0.000815 | -0.0538 | 4.01 | 0.0007 | 0 | 3.86 | 0.000815 | -0.0538 |  | CFL | None | 4010 | 0.7 | 4010 | 0.7 | 0.963 | 1.16 | -0.013416 | 4010 | 0.7 | 4010 | 0.7 | 0.963 | 1.16 | -0.0134
CFLNonePGERtSNewCZ02 | Com-Iltg-dWatt-CFL_OSnone | PGE | RtS | New | CZ02 | 4.01 | 0.0007 | 0 | 4.13 | 0.000855 | -0.029 | 4.01 | 0.0007 | 0 | 4.13 | 0.000855 | -0.029 |  | CFL | None | 4010 | 0.7 | 4010 | 0.7 | 1.03 | 1.22 | -0.0072319 | 4010 | 0.7 | 4010 | 0.7 | 1.03 | 1.22 | -0.00723
CFLNonePGERtSNewCZ03 | Com-Iltg-dWatt-CFL_OSnone | PGE | RtS | New | CZ03 | 4.01 | 0.0007 | 0 | 4.07 | 0.000839 | -0.0276 | 4.01 | 0.0007 | 0 | 4.07 | 0.000839 | -0.0276 |  | CFL | None | 4010 | 0.7 | 4010 | 0.7 | 1.01 | 1.2 | -0.0068828 | 4010 | 0.7 | 4010 | 0.7 | 1.01 | 1.2 | -0.00688
CFLNonePGERtSNewCZ04 | Com-Iltg-dWatt-CFL_OSnone | PGE | RtS | New | CZ04 | 4.01 | 0.0007 | 0 | 4.19 | 0.000847 | -0.0208 | 4.01 | 0.0007 | 0 | 4.19 | 0.000847 | -0.0208 |  | CFL | None | 4010 | 0.7 | 4010 | 0.7 | 1.04 | 1.21 | -0.005187 | 4010 | 0.7 | 4010 | 0.7 | 1.04 | 1.21 | -0.00519
CFLNonePGERtSNewCZ05 | Com-Iltg-dWatt-CFL_OSnone | PGE | RtS | New | CZ05 | 4.01 | 0.0007 | 0 | 4.09 | 0.000825 | -0.0246 | 4.01 | 0.0007 | 0 | 4.09 | 0.000825 | -0.0246 |  | CFL | None | 4010 | 0.7 | 4010 | 0.7 | 1.02 | 1.18 | -0.0061347 | 4010 | 0.7 | 4010 | 0.7 | 1.02 | 1.18 | -0.00613
CFLNonePGERtSNewCZ11 | Com-Iltg-dWatt-CFL_OSnone | PGE | RtS | New | CZ11 | 4.01 | 0.0007 | 0 | 4.23 | 0.000871 | -0.0251 | 4.01 | 0.0007 | 0 | 4.23 | 0.000871 | -0.0251 |  | CFL | None | 4010 | 0.7 | 4010 | 0.7 | 1.05 | 1.24 | -0.0062594 | 4010 | 0.7 | 4010 | 0.7 | 1.05 | 1.24 | -0.00626
CFLNonePGERtSNewCZ12 | Com-Iltg-dWatt-CFL_OSnone | PGE | RtS | New | CZ12 | 4.01 | 0.0007 | 0 | 4.2 | 0.000862 | -0.0267 | 4.01 | 0.0007 | 0 | 4.2 | 0.000862 | -0.0267 |  | CFL | None | 4010 | 0.7 | 4010 | 0.7 | 1.05 | 1.23 | -0.0066584 | 4010 | 0.7 | 4010 | 0.7 | 1.05 | 1.23 | -0.00666
CFLNonePGERtSNewCZ13 | Com-Iltg-dWatt-CFL_OSnone | PGE | RtS | New | CZ13 | 4.01 | 0.0007 | 0 | 4.24 | 0.000861 | -0.0242 | 4.01 | 0.0007 | 0 | 4.24 | 0.000861 | -0.0242 |  | CFL | None | 4010 | 0.7 | 4010 | 0.7 | 1.06 | 1.23 | -0.0060349 | 4010 | 0.7 | 4010 | 0.7 | 1.06 | 1.23 | -0.00603
CFLNonePGERtSNewCZ16 | Com-Iltg-dWatt-CFL_OSnone | PGE | RtS | New | CZ16 | 4.01 | 0.0007 | 0 | 3.92 | 0.000832 | -0.0481 | 4.01 | 0.0007 | 0 | 3.92 | 0.000832 | -0.0481 |  | CFL | None | 4010 | 0.7 | 4010 | 0.7 | 0.978 | 1.19 | -0.011995 | 4010 | 0.7 | 4010 | 0.7 | 0.978 | 1.19 | -0.012
CFLNonePGERtSNewIOU | Com-Iltg-dWatt-CFL_OSnone | PGE | RtS | New | IOU | 4.01 | 0.0007 | 0 | 4.1637 | 0.00085277 | -0.026004 | 4.01 | 0.0007 | 0 | 4.1637 | 0.00085277 | -0.026004 |  | CFL | None | 4010 | 0.7 | 4010 | 0.7 | 1.04 | 1.22 | -0.0064847 | 4010 | 0.7 | 4010 | 0.7 | 1.04 | 1.22 | -0.00648
CFLNonePGESCnExCZ01 | Com-Iltg-dWatt-CFL_OSnone | PGE | SCn | Ex | CZ01 | 2.76 | 0.000575 | 0 | 2.34 | 0.000575 | -0.0464 | 2.76 | 0.000575 | 0 | 2.34 | 0.000575 | -0.0464 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 0.848 | 1 | -0.016812 | 2760 | 0.575 | 2760 | 0.575 | 0.848 | 1 | -0.0168
CFLNonePGESCnExCZ02 | Com-Iltg-dWatt-CFL_OSnone | PGE | SCn | Ex | CZ02 | 2.76 | 0.000575 | 0 | 2.65 | 0.000717 | -0.0247 | 2.76 | 0.000575 | 0 | 2.65 | 0.000717 | -0.0247 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 0.96 | 1.25 | -0.0089493 | 2760 | 0.575 | 2760 | 0.575 | 0.96 | 1.25 | -0.00895
CFLNonePGESCnExCZ03 | Com-Iltg-dWatt-CFL_OSnone | PGE | SCn | Ex | CZ03 | 2.76 | 0.000575 | 0 | 2.56 | 0.000759 | -0.027 | 2.76 | 0.000575 | 0 | 2.56 | 0.000759 | -0.027 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 0.928 | 1.32 | -0.0097826 | 2760 | 0.575 | 2760 | 0.575 | 0.928 | 1.32 | -0.00978
CFLNonePGESCnExCZ04 | Com-Iltg-dWatt-CFL_OSnone | PGE | SCn | Ex | CZ04 | 2.76 | 0.000575 | 0 | 2.71 | 0.000718 | -0.0215 | 2.76 | 0.000575 | 0 | 2.71 | 0.000718 | -0.0215 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 0.982 | 1.25 | -0.0077899 | 2760 | 0.575 | 2760 | 0.575 | 0.982 | 1.25 | -0.00779
CFLNonePGESCnExCZ05 | Com-Iltg-dWatt-CFL_OSnone | PGE | SCn | Ex | CZ05 | 2.76 | 0.000575 | 0 | 2.54 | 0.000685 | -0.0268 | 2.76 | 0.000575 | 0 | 2.54 | 0.000685 | -0.0268 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 0.92 | 1.19 | -0.0097101 | 2760 | 0.575 | 2760 | 0.575 | 0.92 | 1.19 | -0.00971
CFLNonePGESCnExCZ11 | Com-Iltg-dWatt-CFL_OSnone | PGE | SCn | Ex | CZ11 | 2.76 | 0.000575 | 0 | 2.71 | 0.000699 | -0.0228 | 2.76 | 0.000575 | 0 | 2.71 | 0.000699 | -0.0228 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 0.982 | 1.22 | -0.0082609 | 2760 | 0.575 | 2760 | 0.575 | 0.982 | 1.22 | -0.00826
CFLNonePGESCnExCZ12 | Com-Iltg-dWatt-CFL_OSnone | PGE | SCn | Ex | CZ12 | 2.76 | 0.000575 | 0 | 2.72 | 0.000708 | -0.023 | 2.76 | 0.000575 | 0 | 2.72 | 0.000708 | -0.023 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 0.986 | 1.23 | -0.0083333 | 2760 | 0.575 | 2760 | 0.575 | 0.986 | 1.23 | -0.00833
CFLNonePGESCnExCZ13 | Com-Iltg-dWatt-CFL_OSnone | PGE | SCn | Ex | CZ13 | 2.76 | 0.000575 | 0 | 2.74 | 0.000696 | -0.0204 | 2.76 | 0.000575 | 0 | 2.74 | 0.000696 | -0.0204 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 0.993 | 1.21 | -0.0073913 | 2760 | 0.575 | 2760 | 0.575 | 0.993 | 1.21 | -0.00739
CFLNonePGESCnExCZ16 | Com-Iltg-dWatt-CFL_OSnone | PGE | SCn | Ex | CZ16 | 2.76 | 0.000575 | 0 | 2.46 | 0.000683 | -0.0323 | 2.76 | 0.000575 | 0 | 2.46 | 0.000683 | -0.0323 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 0.891 | 1.19 | -0.011703 | 2760 | 0.575 | 2760 | 0.575 | 0.891 | 1.19 | -0.0117
CFLNonePGESCnExIOU | Com-Iltg-dWatt-CFL_OSnone | PGE | SCn | Ex | IOU | 2.76 | 0.000575 | 0 | 2.6549 | 0.00072353 | -0.024199 | 2.76 | 0.000575 | 0 | 2.6549 | 0.00072353 | -0.024199 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 0.962 | 1.26 | -0.0087678 | 2760 | 0.575 | 2760 | 0.575 | 0.962 | 1.26 | -0.00877
CFLNonePGESCnNewCZ01 | Com-Iltg-dWatt-CFL_OSnone | PGE | SCn | New | CZ01 | 2.76 | 0.000575 | 0 | 2.37 | 0.000575 | -0.05 | 2.76 | 0.000575 | 0 | 2.37 | 0.000575 | -0.05 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 0.859 | 1 | -0.018116 | 2760 | 0.575 | 2760 | 0.575 | 0.859 | 1 | -0.0181
CFLNonePGESCnNewCZ02 | Com-Iltg-dWatt-CFL_OSnone | PGE | SCn | New | CZ02 | 2.76 | 0.000575 | 0 | 2.64 | 0.000696 | -0.0261 | 2.76 | 0.000575 | 0 | 2.64 | 0.000696 | -0.0261 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 0.957 | 1.21 | -0.0094565 | 2760 | 0.575 | 2760 | 0.575 | 0.957 | 1.21 | -0.00946
CFLNonePGESCnNewCZ03 | Com-Iltg-dWatt-CFL_OSnone | PGE | SCn | New | CZ03 | 2.76 | 0.000575 | 0 | 2.56 | 0.000719 | -0.0293 | 2.76 | 0.000575 | 0 | 2.56 | 0.000719 | -0.0293 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 0.928 | 1.25 | -0.010616 | 2760 | 0.575 | 2760 | 0.575 | 0.928 | 1.25 | -0.0106
CFLNonePGESCnNewCZ04 | Com-Iltg-dWatt-CFL_OSnone | PGE | SCn | New | CZ04 | 2.76 | 0.000575 | 0 | 2.7 | 0.000691 | -0.0233 | 2.76 | 0.000575 | 0 | 2.7 | 0.000691 | -0.0233 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 0.978 | 1.2 | -0.008442 | 2760 | 0.575 | 2760 | 0.575 | 0.978 | 1.2 | -0.00844
CFLNonePGESCnNewCZ05 | Com-Iltg-dWatt-CFL_OSnone | PGE | SCn | New | CZ05 | 2.76 | 0.000575 | 0 | 2.53 | 0.000687 | -0.0296 | 2.76 | 0.000575 | 0 | 2.53 | 0.000687 | -0.0296 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 0.917 | 1.19 | -0.010725 | 2760 | 0.575 | 2760 | 0.575 | 0.917 | 1.19 | -0.0107
CFLNonePGESCnNewCZ11 | Com-Iltg-dWatt-CFL_OSnone | PGE | SCn | New | CZ11 | 2.76 | 0.000575 | 0 | 2.69 | 0.000683 | -0.0239 | 2.76 | 0.000575 | 0 | 2.69 | 0.000683 | -0.0239 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 0.975 | 1.19 | -0.0086594 | 2760 | 0.575 | 2760 | 0.575 | 0.975 | 1.19 | -0.00866
CFLNonePGESCnNewCZ12 | Com-Iltg-dWatt-CFL_OSnone | PGE | SCn | New | CZ12 | 2.76 | 0.000575 | 0 | 2.7 | 0.000687 | -0.0242 | 2.76 | 0.000575 | 0 | 2.7 | 0.000687 | -0.0242 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 0.978 | 1.19 | -0.0087681 | 2760 | 0.575 | 2760 | 0.575 | 0.978 | 1.19 | -0.00877
CFLNonePGESCnNewCZ13 | Com-Iltg-dWatt-CFL_OSnone | PGE | SCn | New | CZ13 | 2.76 | 0.000575 | 0 | 2.68 | 0.000669 | -0.021 | 2.76 | 0.000575 | 0 | 2.68 | 0.000669 | -0.021 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 0.971 | 1.16 | -0.0076087 | 2760 | 0.575 | 2760 | 0.575 | 0.971 | 1.16 | -0.00761
CFLNonePGESCnNewCZ16 | Com-Iltg-dWatt-CFL_OSnone | PGE | SCn | New | CZ16 | 2.76 | 0.000575 | 0 | 2.45 | 0.000664 | -0.034 | 2.76 | 0.000575 | 0 | 2.45 | 0.000664 | -0.034 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 0.888 | 1.15 | -0.012319 | 2760 | 0.575 | 2760 | 0.575 | 0.888 | 1.15 | -0.0123
CFLNonePGESCnNewIOU | Com-Iltg-dWatt-CFL_OSnone | PGE | SCn | New | IOU | 2.76 | 0.000575 | 0 | 2.6535 | 0.00069026 | -0.02507 | 2.76 | 0.000575 | 0 | 2.6535 | 0.00069026 | -0.02507 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 0.961 | 1.2 | -0.0090833 | 2760 | 0.575 | 2760 | 0.575 | 0.961 | 1.2 | -0.00908
CFLNonePGESUnExCZ01 | Com-Iltg-dWatt-CFL_OSnone | PGE | SUn | Ex | CZ01 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0 | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0
CFLNonePGESUnExCZ02 | Com-Iltg-dWatt-CFL_OSnone | PGE | SUn | Ex | CZ02 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0 | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0
CFLNonePGESUnExCZ03 | Com-Iltg-dWatt-CFL_OSnone | PGE | SUn | Ex | CZ03 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0 | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0
CFLNonePGESUnExCZ04 | Com-Iltg-dWatt-CFL_OSnone | PGE | SUn | Ex | CZ04 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0 | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0
CFLNonePGESUnExCZ05 | Com-Iltg-dWatt-CFL_OSnone | PGE | SUn | Ex | CZ05 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0 | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0
CFLNonePGESUnExCZ11 | Com-Iltg-dWatt-CFL_OSnone | PGE | SUn | Ex | CZ11 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0 | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0
CFLNonePGESUnExCZ12 | Com-Iltg-dWatt-CFL_OSnone | PGE | SUn | Ex | CZ12 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0 | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0
CFLNonePGESUnExCZ13 | Com-Iltg-dWatt-CFL_OSnone | PGE | SUn | Ex | CZ13 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0 | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0
CFLNonePGESUnExCZ16 | Com-Iltg-dWatt-CFL_OSnone | PGE | SUn | Ex | CZ16 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0 | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0
CFLNonePGESUnExIOU | Com-Iltg-dWatt-CFL_OSnone | PGE | SUn | Ex | IOU | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0 | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0
CFLNonePGESUnNewCZ01 | Com-Iltg-dWatt-CFL_OSnone | PGE | SUn | New | CZ01 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0 | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0
CFLNonePGESUnNewCZ02 | Com-Iltg-dWatt-CFL_OSnone | PGE | SUn | New | CZ02 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0 | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0
CFLNonePGESUnNewCZ03 | Com-Iltg-dWatt-CFL_OSnone | PGE | SUn | New | CZ03 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0 | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0
CFLNonePGESUnNewCZ04 | Com-Iltg-dWatt-CFL_OSnone | PGE | SUn | New | CZ04 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0 | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0
CFLNonePGESUnNewCZ05 | Com-Iltg-dWatt-CFL_OSnone | PGE | SUn | New | CZ05 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0 | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0
CFLNonePGESUnNewCZ11 | Com-Iltg-dWatt-CFL_OSnone | PGE | SUn | New | CZ11 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0 | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0
CFLNonePGESUnNewCZ12 | Com-Iltg-dWatt-CFL_OSnone | PGE | SUn | New | CZ12 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0 | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0
CFLNonePGESUnNewCZ13 | Com-Iltg-dWatt-CFL_OSnone | PGE | SUn | New | CZ13 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0 | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0
CFLNonePGESUnNewCZ16 | Com-Iltg-dWatt-CFL_OSnone | PGE | SUn | New | CZ16 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0 | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0
CFLNonePGESUnNewIOU | Com-Iltg-dWatt-CFL_OSnone | PGE | SUn | New | IOU | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0 | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0
CFLNonePGEWRfExCZ01 | Com-Iltg-dWatt-CFL_OSnone | PGE | WRf | Ex | CZ01 | 4.73 | 0.000548 | 0 | 7.56 | 0.000773 | 0 | 4.73 | 0.000548 | 0 | 7.56 | 0.000773 | 0 |  | CFL | None | 4730 | 0.548 | 4730 | 0.548 | 1.6 | 1.41 | 0 | 4730 | 0.548 | 4730 | 0.548 | 1.6 | 1.41 | 0
CFLNonePGEWRfExCZ02 | Com-Iltg-dWatt-CFL_OSnone | PGE | WRf | Ex | CZ02 | 4.73 | 0.000548 | 0 | 7.67 | 0.000696 | 0 | 4.73 | 0.000548 | 0 | 7.67 | 0.000696 | 0 |  | CFL | None | 4730 | 0.548 | 4730 | 0.548 | 1.62 | 1.27 | 0 | 4730 | 0.548 | 4730 | 0.548 | 1.62 | 1.27 | 0
CFLNonePGEWRfExCZ03 | Com-Iltg-dWatt-CFL_OSnone | PGE | WRf | Ex | CZ03 | 4.73 | 0.000548 | 0 | 7.65 | 0.000725 | 0 | 4.73 | 0.000548 | 0 | 7.65 | 0.000725 | 0 |  | CFL | None | 4730 | 0.548 | 4730 | 0.548 | 1.62 | 1.32 | 0 | 4730 | 0.548 | 4730 | 0.548 | 1.62 | 1.32 | 0
CFLNonePGEWRfExCZ04 | Com-Iltg-dWatt-CFL_OSnone | PGE | WRf | Ex | CZ04 | 4.73 | 0.000548 | 0 | 7.67 | 0.0007 | 0 | 4.73 | 0.000548 | 0 | 7.67 | 0.0007 | 0 |  | CFL | None | 4730 | 0.548 | 4730 | 0.548 | 1.62 | 1.28 | 0 | 4730 | 0.548 | 4730 | 0.548 | 1.62 | 1.28 | 0
CFLNonePGEWRfExCZ05 | Com-Iltg-dWatt-CFL_OSnone | PGE | WRf | Ex | CZ05 | 4.73 | 0.000548 | 0 | 7.51 | 0.000721 | 0 | 4.73 | 0.000548 | 0 | 7.51 | 0.000721 | 0 |  | CFL | None | 4730 | 0.548 | 4730 | 0.548 | 1.59 | 1.32 | 0 | 4730 | 0.548 | 4730 | 0.548 | 1.59 | 1.32 | 0
CFLNonePGEWRfExCZ11 | Com-Iltg-dWatt-CFL_OSnone | PGE | WRf | Ex | CZ11 | 4.73 | 0.000548 | 0 | 7.63 | 0.000717 | 0 | 4.73 | 0.000548 | 0 | 7.63 | 0.000717 | 0 |  | CFL | None | 4730 | 0.548 | 4730 | 0.548 | 1.61 | 1.31 | 0 | 4730 | 0.548 | 4730 | 0.548 | 1.61 | 1.31 | 0
CFLNonePGEWRfExCZ12 | Com-Iltg-dWatt-CFL_OSnone | PGE | WRf | Ex | CZ12 | 4.73 | 0.000548 | 0 | 7.59 | 0.000703 | 0 | 4.73 | 0.000548 | 0 | 7.59 | 0.000703 | 0 |  | CFL | None | 4730 | 0.548 | 4730 | 0.548 | 1.6 | 1.28 | 0 | 4730 | 0.548 | 4730 | 0.548 | 1.6 | 1.28 | 0
CFLNonePGEWRfExCZ13 | Com-Iltg-dWatt-CFL_OSnone | PGE | WRf | Ex | CZ13 | 4.73 | 0.000548 | 0 | 7.69 | 0.000692 | 0 | 4.73 | 0.000548 | 0 | 7.69 | 0.000692 | 0 |  | CFL | None | 4730 | 0.548 | 4730 | 0.548 | 1.63 | 1.26 | 0 | 4730 | 0.548 | 4730 | 0.548 | 1.63 | 1.26 | 0
CFLNonePGEWRfExCZ16 | Com-Iltg-dWatt-CFL_OSnone | PGE | WRf | Ex | CZ16 | 4.73 | 0.000548 | 0 | 6.91 | 0.000753 | 0 | 4.73 | 0.000548 | 0 | 6.91 | 0.000753 | 0 |  | CFL | None | 4730 | 0.548 | 4730 | 0.548 | 1.46 | 1.37 | 0 | 4730 | 0.548 | 4730 | 0.548 | 1.46 | 1.37 | 0
CFLNonePGEWRfExIOU | Com-Iltg-dWatt-CFL_OSnone | PGE | WRf | Ex | IOU | 4.73 | 0.000548 | 0 | 7.6449 | 0.00070847 | 0 | 4.73 | 0.000548 | 0 | 7.6449 | 0.00070847 | 0 |  | CFL | None | 4730 | 0.548 | 4730 | 0.548 | 1.62 | 1.29 | 0 | 4730 | 0.548 | 4730 | 0.548 | 1.62 | 1.29 | 0
CFLNonePGEWRfNewCZ01 | Com-Iltg-dWatt-CFL_OSnone | PGE | WRf | New | CZ01 | 4.73 | 0.000548 | 0 | 6.28 | 0.0011 | 0 | 4.73 | 0.000548 | 0 | 6.28 | 0.0011 | 0 |  | CFL | None | 4730 | 0.548 | 4730 | 0.548 | 1.33 | 2.01 | 0 | 4730 | 0.548 | 4730 | 0.548 | 1.33 | 2.01 | 0
CFLNonePGEWRfNewCZ02 | Com-Iltg-dWatt-CFL_OSnone | PGE | WRf | New | CZ02 | 4.73 | 0.000548 | 0 | 6.65 | 0.000741 | 0 | 4.73 | 0.000548 | 0 | 6.65 | 0.000741 | 0 |  | CFL | None | 4730 | 0.548 | 4730 | 0.548 | 1.41 | 1.35 | 0 | 4730 | 0.548 | 4730 | 0.548 | 1.41 | 1.35 | 0
CFLNonePGEWRfNewCZ03 | Com-Iltg-dWatt-CFL_OSnone | PGE | WRf | New | CZ03 | 4.73 | 0.000548 | 0 | 6.71 | 0.0011 | 0 | 4.73 | 0.000548 | 0 | 6.71 | 0.0011 | 0 |  | CFL | None | 4730 | 0.548 | 4730 | 0.548 | 1.42 | 2.01 | 0 | 4730 | 0.548 | 4730 | 0.548 | 1.42 | 2.01 | 0
CFLNonePGEWRfNewCZ04 | Com-Iltg-dWatt-CFL_OSnone | PGE | WRf | New | CZ04 | 4.73 | 0.000548 | 0 | 6.83 | 0.000803 | 0 | 4.73 | 0.000548 | 0 | 6.83 | 0.000803 | 0 |  | CFL | None | 4730 | 0.548 | 4730 | 0.548 | 1.44 | 1.47 | 0 | 4730 | 0.548 | 4730 | 0.548 | 1.44 | 1.47 | 0
CFLNonePGEWRfNewCZ05 | Com-Iltg-dWatt-CFL_OSnone | PGE | WRf | New | CZ05 | 4.73 | 0.000548 | 0 | 6.65 | 0.0011 | 0 | 4.73 | 0.000548 | 0 | 6.65 | 0.0011 | 0 |  | CFL | None | 4730 | 0.548 | 4730 | 0.548 | 1.41 | 2.01 | 0 | 4730 | 0.548 | 4730 | 0.548 | 1.41 | 2.01 | 0
CFLNonePGEWRfNewCZ11 | Com-Iltg-dWatt-CFL_OSnone | PGE | WRf | New | CZ11 | 4.73 | 0.000548 | 0 | 6.81 | 0.000865 | 0 | 4.73 | 0.000548 | 0 | 6.81 | 0.000865 | 0 |  | CFL | None | 4730 | 0.548 | 4730 | 0.548 | 1.44 | 1.58 | 0 | 4730 | 0.548 | 4730 | 0.548 | 1.44 | 1.58 | 0
CFLNonePGEWRfNewCZ12 | Com-Iltg-dWatt-CFL_OSnone | PGE | WRf | New | CZ12 | 4.73 | 0.000548 | 0 | 6.79 | 0.00075 | 0 | 4.73 | 0.000548 | 0 | 6.79 | 0.00075 | 0 |  | CFL | None | 4730 | 0.548 | 4730 | 0.548 | 1.44 | 1.37 | 0 | 4730 | 0.548 | 4730 | 0.548 | 1.44 | 1.37 | 0
CFLNonePGEWRfNewCZ13 | Com-Iltg-dWatt-CFL_OSnone | PGE | WRf | New | CZ13 | 4.73 | 0.000548 | 0 | 6.94 | 0.000685 | 0 | 4.73 | 0.000548 | 0 | 6.94 | 0.000685 | 0 |  | CFL | None | 4730 | 0.548 | 4730 | 0.548 | 1.47 | 1.25 | 0 | 4730 | 0.548 | 4730 | 0.548 | 1.47 | 1.25 | 0
CFLNonePGEWRfNewCZ16 | Com-Iltg-dWatt-CFL_OSnone | PGE | WRf | New | CZ16 | 4.73 | 0.000548 | 0 | 6.23 | 0.0011 | 0 | 4.73 | 0.000548 | 0 | 6.23 | 0.0011 | 0 |  | CFL | None | 4730 | 0.548 | 4730 | 0.548 | 1.32 | 2.01 | 0 | 4730 | 0.548 | 4730 | 0.548 | 1.32 | 2.01 | 0
CFLNonePGEWRfNewIOU | Com-Iltg-dWatt-CFL_OSnone | PGE | WRf | New | IOU | 4.73 | 0.000548 | 0 | 6.8161 | 0.00082273 | 0 | 4.73 | 0.000548 | 0 | 6.8161 | 0.00082273 | 0 |  | CFL | None | 4730 | 0.548 | 4730 | 0.548 | 1.44 | 1.5 | 0 | 4730 | 0.548 | 4730 | 0.548 | 1.44 | 1.5 | 0
CFLNoneSCEAsmExCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | Asm | Ex | CZ05 | 2.3 | 0.000409 | 0 | 2.41 | 0.00049 | -0.0224 | 2.3 | 0.000409 | 0 | 2.41 | 0.00049 | -0.0224 |  | CFL | None | 2300 | 0.409 | 2300 | 0.409 | 1.05 | 1.2 | -0.0097391 | 2300 | 0.409 | 2300 | 0.409 | 1.05 | 1.2 | -0.00974
CFLNoneSCEAsmExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | Asm | Ex | CZ06 | 2.3 | 0.000409 | 0 | 2.57 | 0.00051 | -0.0106 | 2.3 | 0.000409 | 0 | 2.57 | 0.00051 | -0.0106 |  | CFL | None | 2300 | 0.409 | 2300 | 0.409 | 1.12 | 1.25 | -0.0046087 | 2300 | 0.409 | 2300 | 0.409 | 1.12 | 1.25 | -0.00461
CFLNoneSCEAsmExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | Asm | Ex | CZ08 | 2.3 | 0.000409 | 0 | 2.58 | 0.000496 | -0.00961 | 2.3 | 0.000409 | 0 | 2.58 | 0.000496 | -0.00961 |  | CFL | None | 2300 | 0.409 | 2300 | 0.409 | 1.12 | 1.21 | -0.0041783 | 2300 | 0.409 | 2300 | 0.409 | 1.12 | 1.21 | -0.00418
CFLNoneSCEAsmExCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | Asm | Ex | CZ09 | 2.3 | 0.000409 | 0 | 2.56 | 0.000508 | -0.0115 | 2.3 | 0.000409 | 0 | 2.56 | 0.000508 | -0.0115 |  | CFL | None | 2300 | 0.409 | 2300 | 0.409 | 1.11 | 1.24 | -0.005 | 2300 | 0.409 | 2300 | 0.409 | 1.11 | 1.24 | -0.005
CFLNoneSCEAsmExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | Asm | Ex | CZ10 | 2.3 | 0.000409 | 0 | 2.49 | 0.000491 | -0.0127 | 2.3 | 0.000409 | 0 | 2.49 | 0.000491 | -0.0127 |  | CFL | None | 2300 | 0.409 | 2300 | 0.409 | 1.08 | 1.2 | -0.0055217 | 2300 | 0.409 | 2300 | 0.409 | 1.08 | 1.2 | -0.00552
CFLNoneSCEAsmExCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | Asm | Ex | CZ13 | 2.3 | 0.000409 | 0 | 2.47 | 0.000496 | -0.0198 | 2.3 | 0.000409 | 0 | 2.47 | 0.000496 | -0.0198 |  | CFL | None | 2300 | 0.409 | 2300 | 0.409 | 1.07 | 1.21 | -0.0086087 | 2300 | 0.409 | 2300 | 0.409 | 1.07 | 1.21 | -0.00861
CFLNoneSCEAsmExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | Asm | Ex | CZ14 | 2.3 | 0.000409 | 0 | 2.46 | 0.000464 | -0.0196 | 2.3 | 0.000409 | 0 | 2.46 | 0.000464 | -0.0196 |  | CFL | None | 2300 | 0.409 | 2300 | 0.409 | 1.07 | 1.13 | -0.0085217 | 2300 | 0.409 | 2300 | 0.409 | 1.07 | 1.13 | -0.00852
CFLNoneSCEAsmExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | Asm | Ex | CZ15 | 2.3 | 0.000409 | 0 | 2.82 | 0.000479 | -0.00561 | 2.3 | 0.000409 | 0 | 2.82 | 0.000479 | -0.00561 |  | CFL | None | 2300 | 0.409 | 2300 | 0.409 | 1.23 | 1.17 | -0.0024391 | 2300 | 0.409 | 2300 | 0.409 | 1.23 | 1.17 | -0.00244
CFLNoneSCEAsmExCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | Asm | Ex | CZ16 | 2.3 | 0.000409 | 0 | 2.27 | 0.000487 | -0.0308 | 2.3 | 0.000409 | 0 | 2.27 | 0.000487 | -0.0308 |  | CFL | None | 2300 | 0.409 | 2300 | 0.409 | 0.987 | 1.19 | -0.013391 | 2300 | 0.409 | 2300 | 0.409 | 0.987 | 1.19 | -0.0134
CFLNoneSCEAsmExIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | Asm | Ex | IOU | 2.3 | 0.000409 | 0 | 2.56 | 0.00049761 | -0.011485 | 2.3 | 0.000409 | 0 | 2.56 | 0.00049761 | -0.011485 |  | CFL | None | 2300 | 0.409 | 2300 | 0.409 | 1.11 | 1.22 | -0.0049936 | 2300 | 0.409 | 2300 | 0.409 | 1.11 | 1.22 | -0.00499
CFLNoneSCEAsmNewCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | Asm | New | CZ05 | 2.3 | 0.000409 | 0 | 2.38 | 0.000483 | -0.0227 | 2.3 | 0.000409 | 0 | 2.38 | 0.000483 | -0.0227 |  | CFL | None | 2300 | 0.409 | 2300 | 0.409 | 1.03 | 1.18 | -0.0098696 | 2300 | 0.409 | 2300 | 0.409 | 1.03 | 1.18 | -0.00987
CFLNoneSCEAsmNewCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | Asm | New | CZ06 | 2.3 | 0.000409 | 0 | 2.48 | 0.000501 | -0.0145 | 2.3 | 0.000409 | 0 | 2.48 | 0.000501 | -0.0145 |  | CFL | None | 2300 | 0.409 | 2300 | 0.409 | 1.08 | 1.22 | -0.0063043 | 2300 | 0.409 | 2300 | 0.409 | 1.08 | 1.22 | -0.0063
CFLNoneSCEAsmNewCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | Asm | New | CZ08 | 2.3 | 0.000409 | 0 | 2.51 | 0.000494 | -0.0112 | 2.3 | 0.000409 | 0 | 2.51 | 0.000494 | -0.0112 |  | CFL | None | 2300 | 0.409 | 2300 | 0.409 | 1.09 | 1.21 | -0.0048696 | 2300 | 0.409 | 2300 | 0.409 | 1.09 | 1.21 | -0.00487
CFLNoneSCEAsmNewCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | Asm | New | CZ09 | 2.3 | 0.000409 | 0 | 2.51 | 0.000523 | -0.0135 | 2.3 | 0.000409 | 0 | 2.51 | 0.000523 | -0.0135 |  | CFL | None | 2300 | 0.409 | 2300 | 0.409 | 1.09 | 1.28 | -0.0058696 | 2300 | 0.409 | 2300 | 0.409 | 1.09 | 1.28 | -0.00587
CFLNoneSCEAsmNewCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | Asm | New | CZ10 | 2.3 | 0.000409 | 0 | 2.49 | 0.000506 | -0.0133 | 2.3 | 0.000409 | 0 | 2.49 | 0.000506 | -0.0133 |  | CFL | None | 2300 | 0.409 | 2300 | 0.409 | 1.08 | 1.24 | -0.0057826 | 2300 | 0.409 | 2300 | 0.409 | 1.08 | 1.24 | -0.00578
CFLNoneSCEAsmNewCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | Asm | New | CZ13 | 2.3 | 0.000409 | 0 | 2.46 | 0.00051 | -0.021 | 2.3 | 0.000409 | 0 | 2.46 | 0.00051 | -0.021 |  | CFL | None | 2300 | 0.409 | 2300 | 0.409 | 1.07 | 1.25 | -0.0091304 | 2300 | 0.409 | 2300 | 0.409 | 1.07 | 1.25 | -0.00913
CFLNoneSCEAsmNewCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | Asm | New | CZ14 | 2.3 | 0.000409 | 0 | 2.44 | 0.000486 | -0.0207 | 2.3 | 0.000409 | 0 | 2.44 | 0.000486 | -0.0207 |  | CFL | None | 2300 | 0.409 | 2300 | 0.409 | 1.06 | 1.19 | -0.009 | 2300 | 0.409 | 2300 | 0.409 | 1.06 | 1.19 | -0.009
CFLNoneSCEAsmNewCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | Asm | New | CZ15 | 2.3 | 0.000409 | 0 | 2.75 | 0.00051 | -0.00639 | 2.3 | 0.000409 | 0 | 2.75 | 0.00051 | -0.00639 |  | CFL | None | 2300 | 0.409 | 2300 | 0.409 | 1.2 | 1.25 | -0.0027783 | 2300 | 0.409 | 2300 | 0.409 | 1.2 | 1.25 | -0.00278
CFLNoneSCEAsmNewCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | Asm | New | CZ16 | 2.3 | 0.000409 | 0 | 2.28 | 0.000488 | -0.0306 | 2.3 | 0.000409 | 0 | 2.28 | 0.000488 | -0.0306 |  | CFL | None | 2300 | 0.409 | 2300 | 0.409 | 0.991 | 1.19 | -0.013304 | 2300 | 0.409 | 2300 | 0.409 | 0.991 | 1.19 | -0.0133
CFLNoneSCEAsmNewIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | Asm | New | IOU | 2.3 | 0.000409 | 0 | 2.5136 | 0.00050319 | -0.013393 | 2.3 | 0.000409 | 0 | 2.5136 | 0.00050319 | -0.013393 |  | CFL | None | 2300 | 0.409 | 2300 | 0.409 | 1.09 | 1.23 | -0.0058231 | 2300 | 0.409 | 2300 | 0.409 | 1.09 | 1.23 | -0.00582
CFLNoneSCEComExCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | Com | Ex | CZ05 | 3.4308 | 0.00063012 | 0 | 3.6686 | 0.00078351 | -0.027052 | 3.4308 | 0.00063012 | 0 | 3.6686 | 0.00078351 | -0.027052 |  | CFL | None | 3430 | 0.63 | 3430 | 0.63 | 1.07 | 1.24 | -0.007885 | 3430 | 0.63 | 3430 | 0.63 | 1.07 | 1.24 | -0.00789
CFLNoneSCEComExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | Com | Ex | CZ06 | 3.0917 | 0.00061606 | 0 | 3.4814 | 0.00077388 | -0.011707 | 3.0917 | 0.00061606 | 0 | 3.4814 | 0.00077388 | -0.011707 |  | CFL | None | 3090 | 0.616 | 3090 | 0.616 | 1.13 | 1.26 | -0.0037866 | 3090 | 0.616 | 3090 | 0.616 | 1.13 | 1.26 | -0.00379
CFLNoneSCEComExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | Com | Ex | CZ08 | 3.0424 | 0.00062326 | 0 | 3.4156 | 0.00077949 | -0.010312 | 3.0424 | 0.00062326 | 0 | 3.4156 | 0.00077949 | -0.010312 |  | CFL | None | 3040 | 0.623 | 3040 | 0.623 | 1.12 | 1.25 | -0.0033896 | 3040 | 0.623 | 3040 | 0.623 | 1.12 | 1.25 | -0.00339
CFLNoneSCEComExCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | Com | Ex | CZ09 | 3.081 | 0.00062332 | 0 | 3.4677 | 0.00079611 | -0.01222 | 3.081 | 0.00062332 | 0 | 3.4677 | 0.00079611 | -0.01222 |  | CFL | None | 3080 | 0.623 | 3080 | 0.623 | 1.13 | 1.28 | -0.0039661 | 3080 | 0.623 | 3080 | 0.623 | 1.13 | 1.28 | -0.00397
CFLNoneSCEComExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | Com | Ex | CZ10 | 3.1402 | 0.00062945 | 0 | 3.425 | 0.00077791 | -0.01194 | 3.1402 | 0.00062945 | 0 | 3.425 | 0.00077791 | -0.01194 |  | CFL | None | 3140 | 0.629 | 3140 | 0.629 | 1.09 | 1.24 | -0.0038023 | 3140 | 0.629 | 3140 | 0.629 | 1.09 | 1.24 | -0.0038
CFLNoneSCEComExCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | Com | Ex | CZ13 | 3.2038 | 0.00053736 | 0 | 3.5919 | 0.0006708 | -0.018595 | 3.2038 | 0.00053736 | 0 | 3.5919 | 0.0006708 | -0.018595 |  | CFL | None | 3200 | 0.537 | 3200 | 0.537 | 1.12 | 1.25 | -0.0058042 | 3200 | 0.537 | 3200 | 0.537 | 1.12 | 1.25 | -0.0058
CFLNoneSCEComExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | Com | Ex | CZ14 | 3.1508 | 0.0006376 | 0 | 3.4193 | 0.0008036 | -0.020586 | 3.1508 | 0.0006376 | 0 | 3.4193 | 0.0008036 | -0.020586 |  | CFL | None | 3150 | 0.638 | 3150 | 0.638 | 1.09 | 1.26 | -0.0065334 | 3150 | 0.638 | 3150 | 0.638 | 1.09 | 1.26 | -0.00653
CFLNoneSCEComExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | Com | Ex | CZ15 | 2.889 | 0.0005809 | 0 | 3.4106 | 0.0007321 | -0.0048919 | 2.889 | 0.0005809 | 0 | 3.4106 | 0.0007321 | -0.0048919 |  | CFL | None | 2890 | 0.581 | 2890 | 0.581 | 1.18 | 1.26 | -0.0016933 | 2890 | 0.581 | 2890 | 0.581 | 1.18 | 1.26 | -0.00169
CFLNoneSCEComExCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | Com | Ex | CZ16 | 2.8381 | 0.00049944 | 0 | 2.8573 | 0.00060587 | -0.032137 | 2.8381 | 0.00049944 | 0 | 2.8573 | 0.00060587 | -0.032137 |  | CFL | None | 2840 | 0.499 | 2840 | 0.499 | 1.01 | 1.21 | -0.011323 | 2840 | 0.499 | 2840 | 0.499 | 1.01 | 1.21 | -0.0113
CFLNoneSCEComExIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | Com | Ex | IOU | 3.0771 | 0.00061759 | 0 | 3.4352 | 0.00077392 | -0.011973 | 3.0771 | 0.00061759 | 0 | 3.4352 | 0.00077392 | -0.011973 |  | CFL | None | 3080 | 0.618 | 3080 | 0.618 | 1.12 | 1.25 | -0.003891 | 3080 | 0.618 | 3080 | 0.618 | 1.12 | 1.25 | -0.00389
CFLNoneSCEComNewCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | Com | New | CZ05 | 3.535 | 0.00064039 | 0 | 3.6471 | 0.0007832 | -0.028769 | 3.535 | 0.00064039 | 0 | 3.6471 | 0.0007832 | -0.028769 |  | CFL | None | 3530 | 0.64 | 3530 | 0.64 | 1.03 | 1.22 | -0.0081384 | 3530 | 0.64 | 3530 | 0.64 | 1.03 | 1.22 | -0.00814
CFLNoneSCEComNewCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | Com | New | CZ06 | 3.2122 | 0.00062426 | 0 | 3.5132 | 0.00076692 | -0.012096 | 3.2122 | 0.00062426 | 0 | 3.5132 | 0.00076692 | -0.012096 |  | CFL | None | 3210 | 0.624 | 3210 | 0.624 | 1.09 | 1.23 | -0.0037657 | 3210 | 0.624 | 3210 | 0.624 | 1.09 | 1.23 | -0.00377
CFLNoneSCEComNewCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | Com | New | CZ08 | 3.1344 | 0.00062589 | 0 | 3.424 | 0.0007632 | -0.010091 | 3.1344 | 0.00062589 | 0 | 3.424 | 0.0007632 | -0.010091 |  | CFL | None | 3130 | 0.626 | 3130 | 0.626 | 1.09 | 1.22 | -0.0032194 | 3130 | 0.626 | 3130 | 0.626 | 1.09 | 1.22 | -0.00322
CFLNoneSCEComNewCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | Com | New | CZ09 | 3.1659 | 0.00062206 | 0 | 3.4896 | 0.00079825 | -0.01143 | 3.1659 | 0.00062206 | 0 | 3.4896 | 0.00079825 | -0.01143 |  | CFL | None | 3170 | 0.622 | 3170 | 0.622 | 1.1 | 1.28 | -0.0036103 | 3170 | 0.622 | 3170 | 0.622 | 1.1 | 1.28 | -0.00361
CFLNoneSCEComNewCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | Com | New | CZ10 | 3.0648 | 0.00061625 | 0 | 3.2942 | 0.00076322 | -0.010982 | 3.0648 | 0.00061625 | 0 | 3.2942 | 0.00076322 | -0.010982 |  | CFL | None | 3060 | 0.616 | 3060 | 0.616 | 1.07 | 1.24 | -0.0035832 | 3060 | 0.616 | 3060 | 0.616 | 1.07 | 1.24 | -0.00358
CFLNoneSCEComNewCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | Com | New | CZ13 | 3.2602 | 0.00055486 | 0 | 3.6444 | 0.00069915 | -0.018291 | 3.2602 | 0.00055486 | 0 | 3.6444 | 0.00069915 | -0.018291 |  | CFL | None | 3260 | 0.555 | 3260 | 0.555 | 1.12 | 1.26 | -0.0056104 | 3260 | 0.555 | 3260 | 0.555 | 1.12 | 1.26 | -0.00561
CFLNoneSCEComNewCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | Com | New | CZ14 | 3.183 | 0.0006309 | 0 | 3.4501 | 0.00081047 | -0.020808 | 3.183 | 0.0006309 | 0 | 3.4501 | 0.00081047 | -0.020808 |  | CFL | None | 3180 | 0.631 | 3180 | 0.631 | 1.08 | 1.28 | -0.0065372 | 3180 | 0.631 | 3180 | 0.631 | 1.08 | 1.28 | -0.00654
CFLNoneSCEComNewCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | Com | New | CZ15 | 2.8781 | 0.00058627 | 0 | 3.3863 | 0.00077121 | -0.0040414 | 2.8781 | 0.00058627 | 0 | 3.3863 | 0.00077121 | -0.0040414 |  | CFL | None | 2880 | 0.586 | 2880 | 0.586 | 1.18 | 1.32 | -0.0014042 | 2880 | 0.586 | 2880 | 0.586 | 1.18 | 1.32 | -0.0014
CFLNoneSCEComNewCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | Com | New | CZ16 | 2.8492 | 0.00052896 | 0 | 2.863 | 0.00064578 | -0.030643 | 2.8492 | 0.00052896 | 0 | 2.863 | 0.00064578 | -0.030643 |  | CFL | None | 2850 | 0.529 | 2850 | 0.529 | 1 | 1.22 | -0.010755 | 2850 | 0.529 | 2850 | 0.529 | 1 | 1.22 | -0.0108
CFLNoneSCEComNewIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | Com | New | IOU | 3.1082 | 0.00061504 | 0 | 3.3887 | 0.00076514 | -0.011719 | 3.1082 | 0.00061504 | 0 | 3.3887 | 0.00076514 | -0.011719 |  | CFL | None | 3110 | 0.615 | 3110 | 0.615 | 1.09 | 1.24 | -0.0037705 | 3110 | 0.615 | 3110 | 0.615 | 1.09 | 1.24 | -0.00377
CFLNoneSCEECCExCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | ECC | Ex | CZ05 | 2.42 | 0.000647 | 0 | 2.61 | 0.0008 | -0.0286 | 2.42 | 0.000647 | 0 | 2.61 | 0.0008 | -0.0286 |  | CFL | None | 2420 | 0.647 | 2420 | 0.647 | 1.08 | 1.24 | -0.011818 | 2420 | 0.647 | 2420 | 0.647 | 1.08 | 1.24 | -0.0118
CFLNoneSCEECCExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | ECC | Ex | CZ06 | 2.42 | 0.000647 | 0 | 2.78 | 0.000831 | -0.0135 | 2.42 | 0.000647 | 0 | 2.78 | 0.000831 | -0.0135 |  | CFL | None | 2420 | 0.647 | 2420 | 0.647 | 1.15 | 1.28 | -0.0055785 | 2420 | 0.647 | 2420 | 0.647 | 1.15 | 1.28 | -0.00558
CFLNoneSCEECCExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | ECC | Ex | CZ08 | 2.42 | 0.000647 | 0 | 2.8 | 0.000827 | -0.0123 | 2.42 | 0.000647 | 0 | 2.8 | 0.000827 | -0.0123 |  | CFL | None | 2420 | 0.647 | 2420 | 0.647 | 1.16 | 1.28 | -0.0050826 | 2420 | 0.647 | 2420 | 0.647 | 1.16 | 1.28 | -0.00508
CFLNoneSCEECCExCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | ECC | Ex | CZ09 | 2.42 | 0.000647 | 0 | 2.79 | 0.000844 | -0.0141 | 2.42 | 0.000647 | 0 | 2.79 | 0.000844 | -0.0141 |  | CFL | None | 2420 | 0.647 | 2420 | 0.647 | 1.15 | 1.3 | -0.0058264 | 2420 | 0.647 | 2420 | 0.647 | 1.15 | 1.3 | -0.00583
CFLNoneSCEECCExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | ECC | Ex | CZ10 | 2.42 | 0.000647 | 0 | 2.76 | 0.000835 | -0.0138 | 2.42 | 0.000647 | 0 | 2.76 | 0.000835 | -0.0138 |  | CFL | None | 2420 | 0.647 | 2420 | 0.647 | 1.14 | 1.29 | -0.0057025 | 2420 | 0.647 | 2420 | 0.647 | 1.14 | 1.29 | -0.0057
CFLNoneSCEECCExCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | ECC | Ex | CZ13 | 2.42 | 0.00042 | 0 | 2.71 | 0.000544 | -0.0212 | 2.42 | 0.00042 | 0 | 2.71 | 0.000544 | -0.0212 |  | CFL | None | 2420 | 0.42 | 2420 | 0.42 | 1.12 | 1.3 | -0.0087603 | 2420 | 0.42 | 2420 | 0.42 | 1.12 | 1.3 | -0.00876
CFLNoneSCEECCExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | ECC | Ex | CZ14 | 2.42 | 0.000647 | 0 | 2.7 | 0.000822 | -0.022 | 2.42 | 0.000647 | 0 | 2.7 | 0.000822 | -0.022 |  | CFL | None | 2420 | 0.647 | 2420 | 0.647 | 1.12 | 1.27 | -0.0090909 | 2420 | 0.647 | 2420 | 0.647 | 1.12 | 1.27 | -0.00909
CFLNoneSCEECCExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | ECC | Ex | CZ15 | 2.42 | 0.000647 | 0 | 2.97 | 0.000824 | -0.0061 | 2.42 | 0.000647 | 0 | 2.97 | 0.000824 | -0.0061 |  | CFL | None | 2420 | 0.647 | 2420 | 0.647 | 1.23 | 1.27 | -0.0025207 | 2420 | 0.647 | 2420 | 0.647 | 1.23 | 1.27 | -0.00252
CFLNoneSCEECCExCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | ECC | Ex | CZ16 | 2.42 | 0.00042 | 0 | 2.52 | 0.000517 | -0.0399 | 2.42 | 0.00042 | 0 | 2.52 | 0.000517 | -0.0399 |  | CFL | None | 2420 | 0.42 | 2420 | 0.42 | 1.04 | 1.23 | -0.016488 | 2420 | 0.42 | 2420 | 0.42 | 1.04 | 1.23 | -0.0165
CFLNoneSCEECCExIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | ECC | Ex | IOU | 2.42 | 0.0006253 | 0 | 2.7689 | 0.000801 | -0.015316 | 2.42 | 0.0006253 | 0 | 2.7689 | 0.000801 | -0.015316 |  | CFL | None | 2420 | 0.625 | 2420 | 0.625 | 1.14 | 1.28 | -0.0063289 | 2420 | 0.625 | 2420 | 0.625 | 1.14 | 1.28 | -0.00633
CFLNoneSCEECCNewCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | ECC | New | CZ05 | 2.42 | 0.000647 | 0 | 2.57 | 0.000818 | -0.0332 | 2.42 | 0.000647 | 0 | 2.57 | 0.000818 | -0.0332 |  | CFL | None | 2420 | 0.647 | 2420 | 0.647 | 1.06 | 1.26 | -0.013719 | 2420 | 0.647 | 2420 | 0.647 | 1.06 | 1.26 | -0.0137
CFLNoneSCEECCNewCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | ECC | New | CZ06 | 2.42 | 0.000647 | 0 | 2.72 | 0.000837 | -0.0172 | 2.42 | 0.000647 | 0 | 2.72 | 0.000837 | -0.0172 |  | CFL | None | 2420 | 0.647 | 2420 | 0.647 | 1.12 | 1.29 | -0.0071074 | 2420 | 0.647 | 2420 | 0.647 | 1.12 | 1.29 | -0.00711
CFLNoneSCEECCNewCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | ECC | New | CZ08 | 2.42 | 0.000647 | 0 | 2.74 | 0.000837 | -0.0122 | 2.42 | 0.000647 | 0 | 2.74 | 0.000837 | -0.0122 |  | CFL | None | 2420 | 0.647 | 2420 | 0.647 | 1.13 | 1.29 | -0.0050413 | 2420 | 0.647 | 2420 | 0.647 | 1.13 | 1.29 | -0.00504
CFLNoneSCEECCNewCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | ECC | New | CZ09 | 2.42 | 0.000647 | 0 | 2.74 | 0.00086 | -0.0142 | 2.42 | 0.000647 | 0 | 2.74 | 0.00086 | -0.0142 |  | CFL | None | 2420 | 0.647 | 2420 | 0.647 | 1.13 | 1.33 | -0.0058678 | 2420 | 0.647 | 2420 | 0.647 | 1.13 | 1.33 | -0.00587
CFLNoneSCEECCNewCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | ECC | New | CZ10 | 2.42 | 0.000647 | 0 | 2.76 | 0.000869 | -0.0141 | 2.42 | 0.000647 | 0 | 2.76 | 0.000869 | -0.0141 |  | CFL | None | 2420 | 0.647 | 2420 | 0.647 | 1.14 | 1.34 | -0.0058264 | 2420 | 0.647 | 2420 | 0.647 | 1.14 | 1.34 | -0.00583
CFLNoneSCEECCNewCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | ECC | New | CZ13 | 2.42 | 0.00042 | 0 | 2.74 | 0.000591 | -0.022 | 2.42 | 0.00042 | 0 | 2.74 | 0.000591 | -0.022 |  | CFL | None | 2420 | 0.42 | 2420 | 0.42 | 1.13 | 1.41 | -0.0090909 | 2420 | 0.42 | 2420 | 0.42 | 1.13 | 1.41 | -0.00909
CFLNoneSCEECCNewCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | ECC | New | CZ14 | 2.42 | 0.000647 | 0 | 2.73 | 0.000842 | -0.0229 | 2.42 | 0.000647 | 0 | 2.73 | 0.000842 | -0.0229 |  | CFL | None | 2420 | 0.647 | 2420 | 0.647 | 1.13 | 1.3 | -0.0094628 | 2420 | 0.647 | 2420 | 0.647 | 1.13 | 1.3 | -0.00946
CFLNoneSCEECCNewCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | ECC | New | CZ15 | 2.42 | 0.000647 | 0 | 2.94 | 0.000866 | -0.0054 | 2.42 | 0.000647 | 0 | 2.94 | 0.000866 | -0.0054 |  | CFL | None | 2420 | 0.647 | 2420 | 0.647 | 1.21 | 1.34 | -0.0022314 | 2420 | 0.647 | 2420 | 0.647 | 1.21 | 1.34 | -0.00223
CFLNoneSCEECCNewCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | ECC | New | CZ16 | 2.42 | 0.00042 | 0 | 2.54 | 0.000565 | -0.0412 | 2.42 | 0.00042 | 0 | 2.54 | 0.000565 | -0.0412 |  | CFL | None | 2420 | 0.42 | 2420 | 0.42 | 1.05 | 1.35 | -0.017025 | 2420 | 0.42 | 2420 | 0.42 | 1.05 | 1.35 | -0.017
CFLNoneSCEECCNewIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | ECC | New | IOU | 2.42 | 0.00060985 | 0 | 2.7263 | 0.00080289 | -0.017731 | 2.42 | 0.00060985 | 0 | 2.7263 | 0.00080289 | -0.017731 |  | CFL | None | 2420 | 0.61 | 2420 | 0.61 | 1.13 | 1.32 | -0.007327 | 2420 | 0.61 | 2420 | 0.61 | 1.13 | 1.32 | -0.00733
CFLNoneSCEEPrExCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | EPr | Ex | CZ05 | 2.24 | 0.00063 | 0 | 2.43 | 0.000798 | -0.0203 | 2.24 | 0.00063 | 0 | 2.43 | 0.000798 | -0.0203 |  | CFL | None | 2240 | 0.63 | 2240 | 0.63 | 1.08 | 1.27 | -0.0090625 | 2240 | 0.63 | 2240 | 0.63 | 1.08 | 1.27 | -0.00906
CFLNoneSCEEPrExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | EPr | Ex | CZ06 | 2.24 | 0.00063 | 0 | 2.59 | 0.000813 | -0.01 | 2.24 | 0.00063 | 0 | 2.59 | 0.000813 | -0.01 |  | CFL | None | 2240 | 0.63 | 2240 | 0.63 | 1.16 | 1.29 | -0.0044643 | 2240 | 0.63 | 2240 | 0.63 | 1.16 | 1.29 | -0.00446
CFLNoneSCEEPrExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | EPr | Ex | CZ08 | 2.24 | 0.00063 | 0 | 2.62 | 0.000824 | -0.00838 | 2.24 | 0.00063 | 0 | 2.62 | 0.000824 | -0.00838 |  | CFL | None | 2240 | 0.63 | 2240 | 0.63 | 1.17 | 1.31 | -0.0037411 | 2240 | 0.63 | 2240 | 0.63 | 1.17 | 1.31 | -0.00374
CFLNoneSCEEPrExCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | EPr | Ex | CZ09 | 2.24 | 0.00063 | 0 | 2.58 | 0.000821 | -0.0104 | 2.24 | 0.00063 | 0 | 2.58 | 0.000821 | -0.0104 |  | CFL | None | 2240 | 0.63 | 2240 | 0.63 | 1.15 | 1.3 | -0.0046429 | 2240 | 0.63 | 2240 | 0.63 | 1.15 | 1.3 | -0.00464
CFLNoneSCEEPrExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | EPr | Ex | CZ10 | 2.24 | 0.00063 | 0 | 2.51 | 0.000802 | -0.0114 | 2.24 | 0.00063 | 0 | 2.51 | 0.000802 | -0.0114 |  | CFL | None | 2240 | 0.63 | 2240 | 0.63 | 1.12 | 1.27 | -0.0050893 | 2240 | 0.63 | 2240 | 0.63 | 1.12 | 1.27 | -0.00509
CFLNoneSCEEPrExCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | EPr | Ex | CZ13 | 2.24 | 2e-05 | 0 | 2.45 | 2e-05 | -0.0186 | 2.24 | 2e-05 | 0 | 2.45 | 2e-05 | -0.0186 |  | CFL | None | 2240 | 0.02 | 2240 | 0.02 | 1.09 | 1 | -0.0083036 | 2240 | 0.02 | 2240 | 0.02 | 1.09 | 1 | -0.0083
CFLNoneSCEEPrExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | EPr | Ex | CZ14 | 2.24 | 0.00063 | 0 | 2.43 | 0.000806 | -0.0185 | 2.24 | 0.00063 | 0 | 2.43 | 0.000806 | -0.0185 |  | CFL | None | 2240 | 0.63 | 2240 | 0.63 | 1.08 | 1.28 | -0.0082589 | 2240 | 0.63 | 2240 | 0.63 | 1.08 | 1.28 | -0.00826
CFLNoneSCEEPrExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | EPr | Ex | CZ15 | 2.24 | 0.00063 | 0 | 2.69 | 0.000807 | -0.00484 | 2.24 | 0.00063 | 0 | 2.69 | 0.000807 | -0.00484 |  | CFL | None | 2240 | 0.63 | 2240 | 0.63 | 1.2 | 1.28 | -0.0021607 | 2240 | 0.63 | 2240 | 0.63 | 1.2 | 1.28 | -0.00216
CFLNoneSCEEPrExCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | EPr | Ex | CZ16 | 2.24 | 2e-05 | 0 | 2.17 | 2e-05 | -0.0367 | 2.24 | 2e-05 | 0 | 2.17 | 2e-05 | -0.0367 |  | CFL | None | 2240 | 0.02 | 2240 | 0.02 | 0.969 | 1 | -0.016384 | 2240 | 0.02 | 2240 | 0.02 | 0.969 | 1 | -0.0164
CFLNoneSCEEPrExIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | EPr | Ex | IOU | 2.24 | 0.00058982 | 0 | 2.5585 | 0.00076282 | -0.011226 | 2.24 | 0.00058982 | 0 | 2.5585 | 0.00076282 | -0.011226 |  | CFL | None | 2240 | 0.59 | 2240 | 0.59 | 1.14 | 1.29 | -0.0050115 | 2240 | 0.59 | 2240 | 0.59 | 1.14 | 1.29 | -0.00501
CFLNoneSCEEPrNewCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | EPr | New | CZ05 | 2.24 | 0.00063 | 0 | 2.34 | 0.000812 | -0.0222 | 2.24 | 0.00063 | 0 | 2.34 | 0.000812 | -0.0222 |  | CFL | None | 2240 | 0.63 | 2240 | 0.63 | 1.04 | 1.29 | -0.0099107 | 2240 | 0.63 | 2240 | 0.63 | 1.04 | 1.29 | -0.00991
CFLNoneSCEEPrNewCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | EPr | New | CZ06 | 2.24 | 0.00063 | 0 | 2.47 | 0.000848 | -0.0141 | 2.24 | 0.00063 | 0 | 2.47 | 0.000848 | -0.0141 |  | CFL | None | 2240 | 0.63 | 2240 | 0.63 | 1.1 | 1.35 | -0.0062946 | 2240 | 0.63 | 2240 | 0.63 | 1.1 | 1.35 | -0.00629
CFLNoneSCEEPrNewCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | EPr | New | CZ08 | 2.24 | 0.00063 | 0 | 2.5 | 0.000872 | -0.0121 | 2.24 | 0.00063 | 0 | 2.5 | 0.000872 | -0.0121 |  | CFL | None | 2240 | 0.63 | 2240 | 0.63 | 1.12 | 1.38 | -0.0054018 | 2240 | 0.63 | 2240 | 0.63 | 1.12 | 1.38 | -0.0054
CFLNoneSCEEPrNewCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | EPr | New | CZ09 | 2.24 | 0.00063 | 0 | 2.49 | 0.00089 | -0.0137 | 2.24 | 0.00063 | 0 | 2.49 | 0.00089 | -0.0137 |  | CFL | None | 2240 | 0.63 | 2240 | 0.63 | 1.11 | 1.41 | -0.0061161 | 2240 | 0.63 | 2240 | 0.63 | 1.11 | 1.41 | -0.00612
CFLNoneSCEEPrNewCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | EPr | New | CZ10 | 2.24 | 0.00063 | 0 | 2.51 | 0.000904 | -0.0145 | 2.24 | 0.00063 | 0 | 2.51 | 0.000904 | -0.0145 |  | CFL | None | 2240 | 0.63 | 2240 | 0.63 | 1.12 | 1.43 | -0.0064732 | 2240 | 0.63 | 2240 | 0.63 | 1.12 | 1.43 | -0.00647
CFLNoneSCEEPrNewCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | EPr | New | CZ13 | 2.24 | 2e-05 | 0 | 2.45 | 2e-05 | -0.0228 | 2.24 | 2e-05 | 0 | 2.45 | 2e-05 | -0.0228 |  | CFL | None | 2240 | 0.02 | 2240 | 0.02 | 1.09 | 1 | -0.010179 | 2240 | 0.02 | 2240 | 0.02 | 1.09 | 1 | -0.0102
CFLNoneSCEEPrNewCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | EPr | New | CZ14 | 2.24 | 0.00063 | 0 | 2.46 | 0.000885 | -0.0228 | 2.24 | 0.00063 | 0 | 2.46 | 0.000885 | -0.0228 |  | CFL | None | 2240 | 0.63 | 2240 | 0.63 | 1.1 | 1.4 | -0.010179 | 2240 | 0.63 | 2240 | 0.63 | 1.1 | 1.4 | -0.0102
CFLNoneSCEEPrNewCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | EPr | New | CZ15 | 2.24 | 0.00063 | 0 | 2.73 | 0.000915 | -0.00636 | 2.24 | 0.00063 | 0 | 2.73 | 0.000915 | -0.00636 |  | CFL | None | 2240 | 0.63 | 2240 | 0.63 | 1.22 | 1.45 | -0.0028393 | 2240 | 0.63 | 2240 | 0.63 | 1.22 | 1.45 | -0.00284
CFLNoneSCEEPrNewCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | EPr | New | CZ16 | 2.24 | 2e-05 | 0 | 2.2 | 2e-05 | -0.0327 | 2.24 | 2e-05 | 0 | 2.2 | 2e-05 | -0.0327 |  | CFL | None | 2240 | 0.02 | 2240 | 0.02 | 0.982 | 1 | -0.014598 | 2240 | 0.02 | 2240 | 0.02 | 0.982 | 1 | -0.0146
CFLNoneSCEEPrNewIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | EPr | New | IOU | 2.24 | 0.00056165 | 0 | 2.4869 | 0.00078866 | -0.015555 | 2.24 | 0.00056165 | 0 | 2.4869 | 0.00078866 | -0.015555 |  | CFL | None | 2240 | 0.562 | 2240 | 0.562 | 1.11 | 1.4 | -0.0069441 | 2240 | 0.562 | 2240 | 0.562 | 1.11 | 1.4 | -0.00694
CFLNoneSCEERCExCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | ERC | Ex | CZ05 | 2.6 | 0.000728 | 0 | 2.7 | 0.00091 | -0.0265 | 2.6 | 0.000728 | 0 | 2.7 | 0.00091 | -0.0265 |  | CFL | None | 2600 | 0.728 | 2600 | 0.728 | 1.04 | 1.25 | -0.010192 | 2600 | 0.728 | 2600 | 0.728 | 1.04 | 1.25 | -0.0102
CFLNoneSCEERCExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | ERC | Ex | CZ06 | 2.6 | 0.000728 | 0 | 2.85 | 0.000914 | -0.016 | 2.6 | 0.000728 | 0 | 2.85 | 0.000914 | -0.016 |  | CFL | None | 2600 | 0.728 | 2600 | 0.728 | 1.1 | 1.26 | -0.0061538 | 2600 | 0.728 | 2600 | 0.728 | 1.1 | 1.26 | -0.00615
CFLNoneSCEERCExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | ERC | Ex | CZ08 | 2.6 | 0.000728 | 0 | 2.89 | 0.000925 | -0.014 | 2.6 | 0.000728 | 0 | 2.89 | 0.000925 | -0.014 |  | CFL | None | 2600 | 0.728 | 2600 | 0.728 | 1.11 | 1.27 | -0.0053846 | 2600 | 0.728 | 2600 | 0.728 | 1.11 | 1.27 | -0.00538
CFLNoneSCEERCExCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | ERC | Ex | CZ09 | 2.6 | 0.000728 | 0 | 2.89 | 0.000917 | -0.0158 | 2.6 | 0.000728 | 0 | 2.89 | 0.000917 | -0.0158 |  | CFL | None | 2600 | 0.728 | 2600 | 0.728 | 1.11 | 1.26 | -0.0060769 | 2600 | 0.728 | 2600 | 0.728 | 1.11 | 1.26 | -0.00608
CFLNoneSCEERCExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | ERC | Ex | CZ10 | 2.6 | 0.000728 | 0 | 2.86 | 0.000914 | -0.0162 | 2.6 | 0.000728 | 0 | 2.86 | 0.000914 | -0.0162 |  | CFL | None | 2600 | 0.728 | 2600 | 0.728 | 1.1 | 1.26 | -0.0062308 | 2600 | 0.728 | 2600 | 0.728 | 1.1 | 1.26 | -0.00623
CFLNoneSCEERCExCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | ERC | Ex | CZ13 | 2.6 | 2.1e-05 | 0 | 2.8 | 2.1e-05 | -0.0228 | 2.6 | 2.1e-05 | 0 | 2.8 | 2.1e-05 | -0.0228 |  | CFL | None | 2600 | 0.021 | 2600 | 0.021 | 1.08 | 1 | -0.0087692 | 2600 | 0.021 | 2600 | 0.021 | 1.08 | 1 | -0.00877
CFLNoneSCEERCExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | ERC | Ex | CZ14 | 2.6 | 0.000728 | 0 | 2.84 | 0.000927 | -0.0215 | 2.6 | 0.000728 | 0 | 2.84 | 0.000927 | -0.0215 |  | CFL | None | 2600 | 0.728 | 2600 | 0.728 | 1.09 | 1.27 | -0.0082692 | 2600 | 0.728 | 2600 | 0.728 | 1.09 | 1.27 | -0.00827
CFLNoneSCEERCExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | ERC | Ex | CZ15 | 2.6 | 0.000728 | 0 | 3.07 | 0.00094 | -0.00784 | 2.6 | 0.000728 | 0 | 3.07 | 0.00094 | -0.00784 |  | CFL | None | 2600 | 0.728 | 2600 | 0.728 | 1.18 | 1.29 | -0.0030154 | 2600 | 0.728 | 2600 | 0.728 | 1.18 | 1.29 | -0.00302
CFLNoneSCEERCExCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | ERC | Ex | CZ16 | 2.6 | 2.1e-05 | 0 | 2.58 | 2.1e-05 | -0.0384 | 2.6 | 2.1e-05 | 0 | 2.58 | 2.1e-05 | -0.0384 |  | CFL | None | 2600 | 0.021 | 2600 | 0.021 | 0.992 | 1 | -0.014769 | 2600 | 0.021 | 2600 | 0.021 | 0.992 | 1 | -0.0148
CFLNoneSCEERCExIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | ERC | Ex | IOU | 2.6 | 0.00068143 | 0 | 2.8657 | 0.00086029 | -0.01637 | 2.6 | 0.00068143 | 0 | 2.8657 | 0.00086029 | -0.01637 |  | CFL | None | 2600 | 0.681 | 2600 | 0.681 | 1.1 | 1.26 | -0.0062962 | 2600 | 0.681 | 2600 | 0.681 | 1.1 | 1.26 | -0.0063
CFLNoneSCEERCNewCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | ERC | New | CZ05 | 2.6 | 0.000728 | 0 | 2.82 | 0.00098 | -0.0273 | 2.6 | 0.000728 | 0 | 2.82 | 0.00098 | -0.0273 |  | CFL | None | 2600 | 0.728 | 2600 | 0.728 | 1.08 | 1.35 | -0.0105 | 2600 | 0.728 | 2600 | 0.728 | 1.08 | 1.35 | -0.0105
CFLNoneSCEERCNewCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | ERC | New | CZ06 | 2.6 | 0.000728 | 0 | 2.96 | 0.000937 | -0.0175 | 2.6 | 0.000728 | 0 | 2.96 | 0.000937 | -0.0175 |  | CFL | None | 2600 | 0.728 | 2600 | 0.728 | 1.14 | 1.29 | -0.0067308 | 2600 | 0.728 | 2600 | 0.728 | 1.14 | 1.29 | -0.00673
CFLNoneSCEERCNewCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | ERC | New | CZ08 | 2.6 | 0.000728 | 0 | 3.01 | 0.00096 | -0.0152 | 2.6 | 0.000728 | 0 | 3.01 | 0.00096 | -0.0152 |  | CFL | None | 2600 | 0.728 | 2600 | 0.728 | 1.16 | 1.32 | -0.0058462 | 2600 | 0.728 | 2600 | 0.728 | 1.16 | 1.32 | -0.00585
CFLNoneSCEERCNewCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | ERC | New | CZ09 | 2.6 | 0.000728 | 0 | 3.01 | 0.000986 | -0.0164 | 2.6 | 0.000728 | 0 | 3.01 | 0.000986 | -0.0164 |  | CFL | None | 2600 | 0.728 | 2600 | 0.728 | 1.16 | 1.35 | -0.0063077 | 2600 | 0.728 | 2600 | 0.728 | 1.16 | 1.35 | -0.00631
CFLNoneSCEERCNewCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | ERC | New | CZ10 | 2.6 | 0.000728 | 0 | 3.02 | 0.001 | -0.0173 | 2.6 | 0.000728 | 0 | 3.02 | 0.001 | -0.0173 |  | CFL | None | 2600 | 0.728 | 2600 | 0.728 | 1.16 | 1.37 | -0.0066538 | 2600 | 0.728 | 2600 | 0.728 | 1.16 | 1.37 | -0.00665
CFLNoneSCEERCNewCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | ERC | New | CZ13 | 2.6 | 2.1e-05 | 0 | 2.98 | 2.1e-05 | -0.0253 | 2.6 | 2.1e-05 | 0 | 2.98 | 2.1e-05 | -0.0253 |  | CFL | None | 2600 | 0.021 | 2600 | 0.021 | 1.15 | 1 | -0.0097308 | 2600 | 0.021 | 2600 | 0.021 | 1.15 | 1 | -0.00973
CFLNoneSCEERCNewCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | ERC | New | CZ14 | 2.6 | 0.000728 | 0 | 2.98 | 0.000989 | -0.0251 | 2.6 | 0.000728 | 0 | 2.98 | 0.000989 | -0.0251 |  | CFL | None | 2600 | 0.728 | 2600 | 0.728 | 1.15 | 1.36 | -0.0096538 | 2600 | 0.728 | 2600 | 0.728 | 1.15 | 1.36 | -0.00965
CFLNoneSCEERCNewCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | ERC | New | CZ15 | 2.6 | 0.000728 | 0 | 3.3 | 0.00101 | -0.00867 | 2.6 | 0.000728 | 0 | 3.3 | 0.00101 | -0.00867 |  | CFL | None | 2600 | 0.728 | 2600 | 0.728 | 1.27 | 1.39 | -0.0033346 | 2600 | 0.728 | 2600 | 0.728 | 1.27 | 1.39 | -0.00333
CFLNoneSCEERCNewCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | ERC | New | CZ16 | 2.6 | 2.1e-05 | 0 | 2.67 | 2.1e-05 | -0.0444 | 2.6 | 2.1e-05 | 0 | 2.67 | 2.1e-05 | -0.0444 |  | CFL | None | 2600 | 0.021 | 2600 | 0.021 | 1.03 | 1 | -0.017077 | 2600 | 0.021 | 2600 | 0.021 | 1.03 | 1 | -0.0171
CFLNoneSCEERCNewIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | ERC | New | IOU | 2.6 | 0.00064878 | 0 | 2.9981 | 0.0008721 | -0.018755 | 2.6 | 0.00064878 | 0 | 2.9981 | 0.0008721 | -0.018755 |  | CFL | None | 2600 | 0.649 | 2600 | 0.649 | 1.15 | 1.34 | -0.0072133 | 2600 | 0.649 | 2600 | 0.649 | 1.15 | 1.34 | -0.00721
CFLNoneSCEESeExCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | ESe | Ex | CZ05 | 2.33 | 0.000715 | 0 | 2.47 | 0.000886 | -0.0261 | 2.33 | 0.000715 | 0 | 2.47 | 0.000886 | -0.0261 |  | CFL | None | 2330 | 0.715 | 2330 | 0.715 | 1.06 | 1.24 | -0.011202 | 2330 | 0.715 | 2330 | 0.715 | 1.06 | 1.24 | -0.0112
CFLNoneSCEESeExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | ESe | Ex | CZ06 | 2.33 | 0.000715 | 0 | 2.66 | 0.000922 | -0.0138 | 2.33 | 0.000715 | 0 | 2.66 | 0.000922 | -0.0138 |  | CFL | None | 2330 | 0.715 | 2330 | 0.715 | 1.14 | 1.29 | -0.0059227 | 2330 | 0.715 | 2330 | 0.715 | 1.14 | 1.29 | -0.00592
CFLNoneSCEESeExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | ESe | Ex | CZ08 | 2.33 | 0.000715 | 0 | 2.68 | 0.000917 | -0.012 | 2.33 | 0.000715 | 0 | 2.68 | 0.000917 | -0.012 |  | CFL | None | 2330 | 0.715 | 2330 | 0.715 | 1.15 | 1.28 | -0.0051502 | 2330 | 0.715 | 2330 | 0.715 | 1.15 | 1.28 | -0.00515
CFLNoneSCEESeExCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | ESe | Ex | CZ09 | 2.33 | 0.000715 | 0 | 2.66 | 0.000918 | -0.0138 | 2.33 | 0.000715 | 0 | 2.66 | 0.000918 | -0.0138 |  | CFL | None | 2330 | 0.715 | 2330 | 0.715 | 1.14 | 1.28 | -0.0059227 | 2330 | 0.715 | 2330 | 0.715 | 1.14 | 1.28 | -0.00592
CFLNoneSCEESeExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | ESe | Ex | CZ10 | 2.33 | 0.000715 | 0 | 2.59 | 0.000904 | -0.015 | 2.33 | 0.000715 | 0 | 2.59 | 0.000904 | -0.015 |  | CFL | None | 2330 | 0.715 | 2330 | 0.715 | 1.11 | 1.26 | -0.0064378 | 2330 | 0.715 | 2330 | 0.715 | 1.11 | 1.26 | -0.00644
CFLNoneSCEESeExCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | ESe | Ex | CZ13 | 2.33 | 2e-05 | 0 | 2.55 | 2e-05 | -0.0226 | 2.33 | 2e-05 | 0 | 2.55 | 2e-05 | -0.0226 |  | CFL | None | 2330 | 0.02 | 2330 | 0.02 | 1.09 | 1 | -0.0096996 | 2330 | 0.02 | 2330 | 0.02 | 1.09 | 1 | -0.0097
CFLNoneSCEESeExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | ESe | Ex | CZ14 | 2.33 | 0.000715 | 0 | 2.53 | 0.000875 | -0.0229 | 2.33 | 0.000715 | 0 | 2.53 | 0.000875 | -0.0229 |  | CFL | None | 2330 | 0.715 | 2330 | 0.715 | 1.09 | 1.22 | -0.0098283 | 2330 | 0.715 | 2330 | 0.715 | 1.09 | 1.22 | -0.00983
CFLNoneSCEESeExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | ESe | Ex | CZ15 | 2.33 | 0.000715 | 0 | 2.82 | 0.000901 | -0.00681 | 2.33 | 0.000715 | 0 | 2.82 | 0.000901 | -0.00681 |  | CFL | None | 2330 | 0.715 | 2330 | 0.715 | 1.21 | 1.26 | -0.0029227 | 2330 | 0.715 | 2330 | 0.715 | 1.21 | 1.26 | -0.00292
CFLNoneSCEESeExCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | ESe | Ex | CZ16 | 2.33 | 2e-05 | 0 | 2.27 | 2e-05 | -0.0389 | 2.33 | 2e-05 | 0 | 2.27 | 2e-05 | -0.0389 |  | CFL | None | 2330 | 0.02 | 2330 | 0.02 | 0.974 | 1 | -0.016695 | 2330 | 0.02 | 2330 | 0.02 | 0.974 | 1 | -0.0167
CFLNoneSCEESeExIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | ESe | Ex | IOU | 2.33 | 0.00066922 | 0 | 2.6337 | 0.00085379 | -0.014832 | 2.33 | 0.00066922 | 0 | 2.6337 | 0.00085379 | -0.014832 |  | CFL | None | 2330 | 0.669 | 2330 | 0.669 | 1.13 | 1.28 | -0.0063658 | 2330 | 0.669 | 2330 | 0.669 | 1.13 | 1.28 | -0.00637
CFLNoneSCEESeNewCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | ESe | New | CZ05 | 2.33 | 0.000715 | 0 | 2.43 | 0.000898 | -0.0242 | 2.33 | 0.000715 | 0 | 2.43 | 0.000898 | -0.0242 |  | CFL | None | 2330 | 0.715 | 2330 | 0.715 | 1.04 | 1.26 | -0.010386 | 2330 | 0.715 | 2330 | 0.715 | 1.04 | 1.26 | -0.0104
CFLNoneSCEESeNewCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | ESe | New | CZ06 | 2.33 | 0.000715 | 0 | 2.57 | 0.000952 | -0.0173 | 2.33 | 0.000715 | 0 | 2.57 | 0.000952 | -0.0173 |  | CFL | None | 2330 | 0.715 | 2330 | 0.715 | 1.1 | 1.33 | -0.0074249 | 2330 | 0.715 | 2330 | 0.715 | 1.1 | 1.33 | -0.00742
CFLNoneSCEESeNewCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | ESe | New | CZ08 | 2.33 | 0.000715 | 0 | 2.6 | 0.000962 | -0.0142 | 2.33 | 0.000715 | 0 | 2.6 | 0.000962 | -0.0142 |  | CFL | None | 2330 | 0.715 | 2330 | 0.715 | 1.12 | 1.35 | -0.0060944 | 2330 | 0.715 | 2330 | 0.715 | 1.12 | 1.35 | -0.00609
CFLNoneSCEESeNewCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | ESe | New | CZ09 | 2.33 | 0.000715 | 0 | 2.6 | 0.000996 | -0.0166 | 2.33 | 0.000715 | 0 | 2.6 | 0.000996 | -0.0166 |  | CFL | None | 2330 | 0.715 | 2330 | 0.715 | 1.12 | 1.39 | -0.0071245 | 2330 | 0.715 | 2330 | 0.715 | 1.12 | 1.39 | -0.00712
CFLNoneSCEESeNewCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | ESe | New | CZ10 | 2.33 | 0.000715 | 0 | 2.62 | 0.00101 | -0.0178 | 2.33 | 0.000715 | 0 | 2.62 | 0.00101 | -0.0178 |  | CFL | None | 2330 | 0.715 | 2330 | 0.715 | 1.12 | 1.41 | -0.0076395 | 2330 | 0.715 | 2330 | 0.715 | 1.12 | 1.41 | -0.00764
CFLNoneSCEESeNewCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | ESe | New | CZ13 | 2.33 | 2e-05 | 0 | 2.61 | 2e-05 | -0.0261 | 2.33 | 2e-05 | 0 | 2.61 | 2e-05 | -0.0261 |  | CFL | None | 2330 | 0.02 | 2330 | 0.02 | 1.12 | 1 | -0.011202 | 2330 | 0.02 | 2330 | 0.02 | 1.12 | 1 | -0.0112
CFLNoneSCEESeNewCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | ESe | New | CZ14 | 2.33 | 0.000715 | 0 | 2.58 | 0.000989 | -0.0259 | 2.33 | 0.000715 | 0 | 2.58 | 0.000989 | -0.0259 |  | CFL | None | 2330 | 0.715 | 2330 | 0.715 | 1.11 | 1.38 | -0.011116 | 2330 | 0.715 | 2330 | 0.715 | 1.11 | 1.38 | -0.0111
CFLNoneSCEESeNewCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | ESe | New | CZ15 | 2.33 | 0.000715 | 0 | 2.9 | 0.001 | -0.00776 | 2.33 | 0.000715 | 0 | 2.9 | 0.001 | -0.00776 |  | CFL | None | 2330 | 0.715 | 2330 | 0.715 | 1.24 | 1.4 | -0.0033305 | 2330 | 0.715 | 2330 | 0.715 | 1.24 | 1.4 | -0.00333
CFLNoneSCEESeNewCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | ESe | New | CZ16 | 2.33 | 2e-05 | 0 | 2.32 | 2e-05 | -0.0324 | 2.33 | 2e-05 | 0 | 2.32 | 2e-05 | -0.0324 |  | CFL | None | 2330 | 0.02 | 2330 | 0.02 | 0.996 | 1 | -0.013906 | 2330 | 0.02 | 2330 | 0.02 | 0.996 | 1 | -0.0139
CFLNoneSCEESeNewIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | ESe | New | IOU | 2.33 | 0.00063712 | 0 | 2.6001 | 0.00087837 | -0.018328 | 2.33 | 0.00063712 | 0 | 2.6001 | 0.00087837 | -0.018328 |  | CFL | None | 2330 | 0.637 | 2330 | 0.637 | 1.12 | 1.38 | -0.007866 | 2330 | 0.637 | 2330 | 0.637 | 1.12 | 1.38 | -0.00787
CFLNoneSCEEUnExCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | EUn | Ex | CZ05 | 2.37 | 0.000669 | 0 | 2.62 | 0.000814 | -0.0168 | 2.37 | 0.000669 | 0 | 2.62 | 0.000814 | -0.0168 |  | CFL | None | 2370 | 0.669 | 2370 | 0.669 | 1.11 | 1.22 | -0.0070886 | 2370 | 0.669 | 2370 | 0.669 | 1.11 | 1.22 | -0.00709
CFLNoneSCEEUnExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | EUn | Ex | CZ06 | 2.37 | 0.000669 | 0 | 2.74 | 0.000848 | -0.00966 | 2.37 | 0.000669 | 0 | 2.74 | 0.000848 | -0.00966 |  | CFL | None | 2370 | 0.669 | 2370 | 0.669 | 1.16 | 1.27 | -0.0040759 | 2370 | 0.669 | 2370 | 0.669 | 1.16 | 1.27 | -0.00408
CFLNoneSCEEUnExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | EUn | Ex | CZ08 | 2.37 | 0.000669 | 0 | 2.75 | 0.00085 | -0.00933 | 2.37 | 0.000669 | 0 | 2.75 | 0.00085 | -0.00933 |  | CFL | None | 2370 | 0.669 | 2370 | 0.669 | 1.16 | 1.27 | -0.0039367 | 2370 | 0.669 | 2370 | 0.669 | 1.16 | 1.27 | -0.00394
CFLNoneSCEEUnExCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | EUn | Ex | CZ09 | 2.37 | 0.000669 | 0 | 2.74 | 0.000861 | -0.0105 | 2.37 | 0.000669 | 0 | 2.74 | 0.000861 | -0.0105 |  | CFL | None | 2370 | 0.669 | 2370 | 0.669 | 1.16 | 1.29 | -0.0044304 | 2370 | 0.669 | 2370 | 0.669 | 1.16 | 1.29 | -0.00443
CFLNoneSCEEUnExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | EUn | Ex | CZ10 | 2.37 | 0.000669 | 0 | 2.72 | 0.000856 | -0.00968 | 2.37 | 0.000669 | 0 | 2.72 | 0.000856 | -0.00968 |  | CFL | None | 2370 | 0.669 | 2370 | 0.669 | 1.15 | 1.28 | -0.0040844 | 2370 | 0.669 | 2370 | 0.669 | 1.15 | 1.28 | -0.00408
CFLNoneSCEEUnExCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | EUn | Ex | CZ13 | 2.37 | 0.000439 | 0 | 2.67 | 0.000553 | -0.013 | 2.37 | 0.000439 | 0 | 2.67 | 0.000553 | -0.013 |  | CFL | None | 2370 | 0.439 | 2370 | 0.439 | 1.13 | 1.26 | -0.0054852 | 2370 | 0.439 | 2370 | 0.439 | 1.13 | 1.26 | -0.00549
CFLNoneSCEEUnExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | EUn | Ex | CZ14 | 2.37 | 0.000669 | 0 | 2.67 | 0.000849 | -0.0142 | 2.37 | 0.000669 | 0 | 2.67 | 0.000849 | -0.0142 |  | CFL | None | 2370 | 0.669 | 2370 | 0.669 | 1.13 | 1.27 | -0.0059916 | 2370 | 0.669 | 2370 | 0.669 | 1.13 | 1.27 | -0.00599
CFLNoneSCEEUnExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | EUn | Ex | CZ15 | 2.37 | 0.000669 | 0 | 2.84 | 0.000858 | -0.00511 | 2.37 | 0.000669 | 0 | 2.84 | 0.000858 | -0.00511 |  | CFL | None | 2370 | 0.669 | 2370 | 0.669 | 1.2 | 1.28 | -0.0021561 | 2370 | 0.669 | 2370 | 0.669 | 1.2 | 1.28 | -0.00216
CFLNoneSCEEUnExCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | EUn | Ex | CZ16 | 2.37 | 0.000439 | 0 | 2.49 | 0.000535 | -0.0275 | 2.37 | 0.000439 | 0 | 2.49 | 0.000535 | -0.0275 |  | CFL | None | 2370 | 0.439 | 2370 | 0.439 | 1.05 | 1.22 | -0.011603 | 2370 | 0.439 | 2370 | 0.439 | 1.05 | 1.22 | -0.0116
CFLNoneSCEEUnExIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | EUn | Ex | IOU | 2.37 | 0.00064701 | 0 | 2.7223 | 0.00082164 | -0.011016 | 2.37 | 0.00064701 | 0 | 2.7223 | 0.00082164 | -0.011016 |  | CFL | None | 2370 | 0.647 | 2370 | 0.647 | 1.15 | 1.27 | -0.0046482 | 2370 | 0.647 | 2370 | 0.647 | 1.15 | 1.27 | -0.00465
CFLNoneSCEEUnNewCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | EUn | New | CZ05 | 2.37 | 0.000669 | 0 | 2.57 | 0.000828 | -0.0155 | 2.37 | 0.000669 | 0 | 2.57 | 0.000828 | -0.0155 |  | CFL | None | 2370 | 0.669 | 2370 | 0.669 | 1.08 | 1.24 | -0.0065401 | 2370 | 0.669 | 2370 | 0.669 | 1.08 | 1.24 | -0.00654
CFLNoneSCEEUnNewCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | EUn | New | CZ06 | 2.37 | 0.000669 | 0 | 2.71 | 0.000849 | -0.00701 | 2.37 | 0.000669 | 0 | 2.71 | 0.000849 | -0.00701 |  | CFL | None | 2370 | 0.669 | 2370 | 0.669 | 1.14 | 1.27 | -0.0029578 | 2370 | 0.669 | 2370 | 0.669 | 1.14 | 1.27 | -0.00296
CFLNoneSCEEUnNewCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | EUn | New | CZ08 | 2.37 | 0.000669 | 0 | 2.74 | 0.000861 | -0.0062 | 2.37 | 0.000669 | 0 | 2.74 | 0.000861 | -0.0062 |  | CFL | None | 2370 | 0.669 | 2370 | 0.669 | 1.16 | 1.29 | -0.002616 | 2370 | 0.669 | 2370 | 0.669 | 1.16 | 1.29 | -0.00262
CFLNoneSCEEUnNewCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | EUn | New | CZ09 | 2.37 | 0.000669 | 0 | 2.75 | 0.000889 | -0.00715 | 2.37 | 0.000669 | 0 | 2.75 | 0.000889 | -0.00715 |  | CFL | None | 2370 | 0.669 | 2370 | 0.669 | 1.16 | 1.33 | -0.0030169 | 2370 | 0.669 | 2370 | 0.669 | 1.16 | 1.33 | -0.00302
CFLNoneSCEEUnNewCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | EUn | New | CZ10 | 2.37 | 0.000669 | 0 | 2.76 | 0.000892 | -0.00757 | 2.37 | 0.000669 | 0 | 2.76 | 0.000892 | -0.00757 |  | CFL | None | 2370 | 0.669 | 2370 | 0.669 | 1.16 | 1.33 | -0.0031941 | 2370 | 0.669 | 2370 | 0.669 | 1.16 | 1.33 | -0.00319
CFLNoneSCEEUnNewCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | EUn | New | CZ13 | 2.37 | 0.000439 | 0 | 2.77 | 0.000631 | -0.0155 | 2.37 | 0.000439 | 0 | 2.77 | 0.000631 | -0.0155 |  | CFL | None | 2370 | 0.439 | 2370 | 0.439 | 1.17 | 1.44 | -0.0065401 | 2370 | 0.439 | 2370 | 0.439 | 1.17 | 1.44 | -0.00654
CFLNoneSCEEUnNewCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | EUn | New | CZ14 | 2.37 | 0.000669 | 0 | 2.62 | 0.000815 | -0.0127 | 2.37 | 0.000669 | 0 | 2.62 | 0.000815 | -0.0127 |  | CFL | None | 2370 | 0.669 | 2370 | 0.669 | 1.11 | 1.22 | -0.0053586 | 2370 | 0.669 | 2370 | 0.669 | 1.11 | 1.22 | -0.00536
CFLNoneSCEEUnNewCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | EUn | New | CZ15 | 2.37 | 0.000669 | 0 | 2.91 | 0.000906 | -0.00324 | 2.37 | 0.000669 | 0 | 2.91 | 0.000906 | -0.00324 |  | CFL | None | 2370 | 0.669 | 2370 | 0.669 | 1.23 | 1.35 | -0.0013671 | 2370 | 0.669 | 2370 | 0.669 | 1.23 | 1.35 | -0.00137
CFLNoneSCEEUnNewCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | EUn | New | CZ16 | 2.37 | 0.000439 | 0 | 2.5 | 0.000567 | -0.0277 | 2.37 | 0.000439 | 0 | 2.5 | 0.000567 | -0.0277 |  | CFL | None | 2370 | 0.439 | 2370 | 0.439 | 1.05 | 1.29 | -0.011688 | 2370 | 0.439 | 2370 | 0.439 | 1.05 | 1.29 | -0.0117
CFLNoneSCEEUnNewIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | EUn | New | IOU | 2.37 | 0.00063136 | 0 | 2.7139 | 0.00082088 | -0.0098409 | 2.37 | 0.00063136 | 0 | 2.7139 | 0.00082088 | -0.0098409 |  | CFL | None | 2370 | 0.631 | 2370 | 0.631 | 1.15 | 1.3 | -0.0041523 | 2370 | 0.631 | 2370 | 0.631 | 1.15 | 1.3 | -0.00415
CFLNoneSCEGroExCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | Gro | Ex | CZ05 | 3.89 | 0.000495 | 0 | 3.73 | 0.000619 | -0.0677 | 3.89 | 0.000495 | 0 | 3.73 | 0.000619 | -0.0677 |  | CFL | None | 3890 | 0.495 | 3890 | 0.495 | 0.959 | 1.25 | -0.017404 | 3890 | 0.495 | 3890 | 0.495 | 0.959 | 1.25 | -0.0174
CFLNoneSCEGroExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | Gro | Ex | CZ06 | 3.89 | 0.000495 | 0 | 3.94 | 0.000623 | -0.0544 | 3.89 | 0.000495 | 0 | 3.94 | 0.000623 | -0.0544 |  | CFL | None | 3890 | 0.495 | 3890 | 0.495 | 1.01 | 1.26 | -0.013985 | 3890 | 0.495 | 3890 | 0.495 | 1.01 | 1.26 | -0.014
CFLNoneSCEGroExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | Gro | Ex | CZ08 | 3.89 | 0.000495 | 0 | 4.04 | 0.000641 | -0.0494 | 3.89 | 0.000495 | 0 | 4.04 | 0.000641 | -0.0494 |  | CFL | None | 3890 | 0.495 | 3890 | 0.495 | 1.04 | 1.29 | -0.012699 | 3890 | 0.495 | 3890 | 0.495 | 1.04 | 1.29 | -0.0127
CFLNoneSCEGroExCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | Gro | Ex | CZ09 | 3.89 | 0.000495 | 0 | 4.08 | 0.000647 | -0.0482 | 3.89 | 0.000495 | 0 | 4.08 | 0.000647 | -0.0482 |  | CFL | None | 3890 | 0.495 | 3890 | 0.495 | 1.05 | 1.31 | -0.012391 | 3890 | 0.495 | 3890 | 0.495 | 1.05 | 1.31 | -0.0124
CFLNoneSCEGroExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | Gro | Ex | CZ10 | 3.89 | 0.000495 | 0 | 4.07 | 0.000662 | -0.0471 | 3.89 | 0.000495 | 0 | 4.07 | 0.000662 | -0.0471 |  | CFL | None | 3890 | 0.495 | 3890 | 0.495 | 1.05 | 1.34 | -0.012108 | 3890 | 0.495 | 3890 | 0.495 | 1.05 | 1.34 | -0.0121
CFLNoneSCEGroExCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | Gro | Ex | CZ13 | 3.89 | 0.000495 | 0 | 4.08 | 0.000654 | -0.0463 | 3.89 | 0.000495 | 0 | 4.08 | 0.000654 | -0.0463 |  | CFL | None | 3890 | 0.495 | 3890 | 0.495 | 1.05 | 1.32 | -0.011902 | 3890 | 0.495 | 3890 | 0.495 | 1.05 | 1.32 | -0.0119
CFLNoneSCEGroExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | Gro | Ex | CZ14 | 3.89 | 0.000495 | 0 | 4.06 | 0.000675 | -0.0474 | 3.89 | 0.000495 | 0 | 4.06 | 0.000675 | -0.0474 |  | CFL | None | 3890 | 0.495 | 3890 | 0.495 | 1.04 | 1.36 | -0.012185 | 3890 | 0.495 | 3890 | 0.495 | 1.04 | 1.36 | -0.0122
CFLNoneSCEGroExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | Gro | Ex | CZ15 | 3.89 | 0.000495 | 0 | 4.38 | 0.00066 | -0.0272 | 3.89 | 0.000495 | 0 | 4.38 | 0.00066 | -0.0272 |  | CFL | None | 3890 | 0.495 | 3890 | 0.495 | 1.13 | 1.33 | -0.0069923 | 3890 | 0.495 | 3890 | 0.495 | 1.13 | 1.33 | -0.00699
CFLNoneSCEGroExCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | Gro | Ex | CZ16 | 3.89 | 0.000495 | 0 | 3.69 | 0.000624 | -0.0634 | 3.89 | 0.000495 | 0 | 3.69 | 0.000624 | -0.0634 |  | CFL | None | 3890 | 0.495 | 3890 | 0.495 | 0.949 | 1.26 | -0.016298 | 3890 | 0.495 | 3890 | 0.495 | 0.949 | 1.26 | -0.0163
CFLNoneSCEGroExIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | Gro | Ex | IOU | 3.89 | 0.000495 | 0 | 4.0355 | 0.00064494 | -0.049263 | 3.89 | 0.000495 | 0 | 4.0355 | 0.00064494 | -0.049263 |  | CFL | None | 3890 | 0.495 | 3890 | 0.495 | 1.04 | 1.3 | -0.012664 | 3890 | 0.495 | 3890 | 0.495 | 1.04 | 1.3 | -0.0127
CFLNoneSCEGroNewCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | Gro | New | CZ05 | 3.89 | 0.000495 | 0 | 3.82 | 0.000625 | -0.0649 | 3.89 | 0.000495 | 0 | 3.82 | 0.000625 | -0.0649 |  | CFL | None | 3890 | 0.495 | 3890 | 0.495 | 0.982 | 1.26 | -0.016684 | 3890 | 0.495 | 3890 | 0.495 | 0.982 | 1.26 | -0.0167
CFLNoneSCEGroNewCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | Gro | New | CZ06 | 3.89 | 0.000495 | 0 | 4.1 | 0.000628 | -0.0463 | 3.89 | 0.000495 | 0 | 4.1 | 0.000628 | -0.0463 |  | CFL | None | 3890 | 0.495 | 3890 | 0.495 | 1.05 | 1.27 | -0.011902 | 3890 | 0.495 | 3890 | 0.495 | 1.05 | 1.27 | -0.0119
CFLNoneSCEGroNewCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | Gro | New | CZ08 | 3.89 | 0.000495 | 0 | 4.15 | 0.00064 | -0.0404 | 3.89 | 0.000495 | 0 | 4.15 | 0.00064 | -0.0404 |  | CFL | None | 3890 | 0.495 | 3890 | 0.495 | 1.07 | 1.29 | -0.010386 | 3890 | 0.495 | 3890 | 0.495 | 1.07 | 1.29 | -0.0104
CFLNoneSCEGroNewCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | Gro | New | CZ09 | 3.89 | 0.000495 | 0 | 4.16 | 0.000676 | -0.0428 | 3.89 | 0.000495 | 0 | 4.16 | 0.000676 | -0.0428 |  | CFL | None | 3890 | 0.495 | 3890 | 0.495 | 1.07 | 1.37 | -0.011003 | 3890 | 0.495 | 3890 | 0.495 | 1.07 | 1.37 | -0.011
CFLNoneSCEGroNewCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | Gro | New | CZ10 | 3.89 | 0.000495 | 0 | 4.19 | 0.000704 | -0.042 | 3.89 | 0.000495 | 0 | 4.19 | 0.000704 | -0.042 |  | CFL | None | 3890 | 0.495 | 3890 | 0.495 | 1.08 | 1.42 | -0.010797 | 3890 | 0.495 | 3890 | 0.495 | 1.08 | 1.42 | -0.0108
CFLNoneSCEGroNewCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | Gro | New | CZ13 | 3.89 | 0.000495 | 0 | 4.2 | 0.000679 | -0.0439 | 3.89 | 0.000495 | 0 | 4.2 | 0.000679 | -0.0439 |  | CFL | None | 3890 | 0.495 | 3890 | 0.495 | 1.08 | 1.37 | -0.011285 | 3890 | 0.495 | 3890 | 0.495 | 1.08 | 1.37 | -0.0113
CFLNoneSCEGroNewCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | Gro | New | CZ14 | 3.89 | 0.000495 | 0 | 4.21 | 0.000687 | -0.0463 | 3.89 | 0.000495 | 0 | 4.21 | 0.000687 | -0.0463 |  | CFL | None | 3890 | 0.495 | 3890 | 0.495 | 1.08 | 1.39 | -0.011902 | 3890 | 0.495 | 3890 | 0.495 | 1.08 | 1.39 | -0.0119
CFLNoneSCEGroNewCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | Gro | New | CZ15 | 3.89 | 0.000495 | 0 | 4.53 | 0.000699 | -0.0239 | 3.89 | 0.000495 | 0 | 4.53 | 0.000699 | -0.0239 |  | CFL | None | 3890 | 0.495 | 3890 | 0.495 | 1.16 | 1.41 | -0.006144 | 3890 | 0.495 | 3890 | 0.495 | 1.16 | 1.41 | -0.00614
CFLNoneSCEGroNewCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | Gro | New | CZ16 | 3.89 | 0.000495 | 0 | 3.82 | 0.000638 | -0.0603 | 3.89 | 0.000495 | 0 | 3.82 | 0.000638 | -0.0603 |  | CFL | None | 3890 | 0.495 | 3890 | 0.495 | 0.982 | 1.29 | -0.015501 | 3890 | 0.495 | 3890 | 0.495 | 0.982 | 1.29 | -0.0155
CFLNoneSCEGroNewIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | Gro | New | IOU | 3.89 | 0.000495 | 0 | 4.1686 | 0.00066953 | -0.042543 | 3.89 | 0.000495 | 0 | 4.1686 | 0.00066953 | -0.042543 |  | CFL | None | 3890 | 0.495 | 3890 | 0.495 | 1.07 | 1.35 | -0.010937 | 3890 | 0.495 | 3890 | 0.495 | 1.07 | 1.35 | -0.0109
CFLNoneSCEHspExCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | Hsp | Ex | CZ05 | 4.2 | 0.000717 | 0 | 4.71 | 0.000873 | -0.0296 | 4.2 | 0.000717 | 0 | 4.71 | 0.000873 | -0.0296 |  | CFL | None | 4200 | 0.717 | 4200 | 0.717 | 1.12 | 1.22 | -0.0070476 | 4200 | 0.717 | 4200 | 0.717 | 1.12 | 1.22 | -0.00705
CFLNoneSCEHspExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | Hsp | Ex | CZ06 | 4.2 | 0.000717 | 0 | 4.86 | 0.000896 | -0.0221 | 4.2 | 0.000717 | 0 | 4.86 | 0.000896 | -0.0221 |  | CFL | None | 4200 | 0.717 | 4200 | 0.717 | 1.16 | 1.25 | -0.0052619 | 4200 | 0.717 | 4200 | 0.717 | 1.16 | 1.25 | -0.00526
CFLNoneSCEHspExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | Hsp | Ex | CZ08 | 4.2 | 0.000717 | 0 | 4.89 | 0.000895 | -0.0217 | 4.2 | 0.000717 | 0 | 4.89 | 0.000895 | -0.0217 |  | CFL | None | 4200 | 0.717 | 4200 | 0.717 | 1.16 | 1.25 | -0.0051667 | 4200 | 0.717 | 4200 | 0.717 | 1.16 | 1.25 | -0.00517
CFLNoneSCEHspExCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | Hsp | Ex | CZ09 | 4.2 | 0.000717 | 0 | 4.91 | 0.000919 | -0.022 | 4.2 | 0.000717 | 0 | 4.91 | 0.000919 | -0.022 |  | CFL | None | 4200 | 0.717 | 4200 | 0.717 | 1.17 | 1.28 | -0.0052381 | 4200 | 0.717 | 4200 | 0.717 | 1.17 | 1.28 | -0.00524
CFLNoneSCEHspExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | Hsp | Ex | CZ10 | 4.2 | 0.000717 | 0 | 4.78 | 0.000907 | -0.0237 | 4.2 | 0.000717 | 0 | 4.78 | 0.000907 | -0.0237 |  | CFL | None | 4200 | 0.717 | 4200 | 0.717 | 1.14 | 1.26 | -0.0056429 | 4200 | 0.717 | 4200 | 0.717 | 1.14 | 1.26 | -0.00564
CFLNoneSCEHspExCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | Hsp | Ex | CZ13 | 4.2 | 0.000717 | 0 | 4.75 | 0.000904 | -0.027 | 4.2 | 0.000717 | 0 | 4.75 | 0.000904 | -0.027 |  | CFL | None | 4200 | 0.717 | 4200 | 0.717 | 1.13 | 1.26 | -0.0064286 | 4200 | 0.717 | 4200 | 0.717 | 1.13 | 1.26 | -0.00643
CFLNoneSCEHspExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | Hsp | Ex | CZ14 | 4.2 | 0.000717 | 0 | 4.75 | 0.000905 | -0.0289 | 4.2 | 0.000717 | 0 | 4.75 | 0.000905 | -0.0289 |  | CFL | None | 4200 | 0.717 | 4200 | 0.717 | 1.13 | 1.26 | -0.006881 | 4200 | 0.717 | 4200 | 0.717 | 1.13 | 1.26 | -0.00688
CFLNoneSCEHspExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | Hsp | Ex | CZ15 | 4.2 | 0.000717 | 0 | 4.97 | 0.000916 | -0.0189 | 4.2 | 0.000717 | 0 | 4.97 | 0.000916 | -0.0189 |  | CFL | None | 4200 | 0.717 | 4200 | 0.717 | 1.18 | 1.28 | -0.0045 | 4200 | 0.717 | 4200 | 0.717 | 1.18 | 1.28 | -0.0045
CFLNoneSCEHspExCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | Hsp | Ex | CZ16 | 4.2 | 0.000717 | 0 | 4.44 | 0.000878 | -0.0396 | 4.2 | 0.000717 | 0 | 4.44 | 0.000878 | -0.0396 |  | CFL | None | 4200 | 0.717 | 4200 | 0.717 | 1.06 | 1.22 | -0.0094286 | 4200 | 0.717 | 4200 | 0.717 | 1.06 | 1.22 | -0.00943
CFLNoneSCEHspExIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | Hsp | Ex | IOU | 4.2 | 0.000717 | 0 | 4.8498 | 0.00090111 | -0.022939 | 4.2 | 0.000717 | 0 | 4.8498 | 0.00090111 | -0.022939 |  | CFL | None | 4200 | 0.717 | 4200 | 0.717 | 1.15 | 1.26 | -0.0054618 | 4200 | 0.717 | 4200 | 0.717 | 1.15 | 1.26 | -0.00546
CFLNoneSCEHspNewCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | Hsp | New | CZ05 | 4.2 | 0.000717 | 0 | 4.43 | 0.000847 | -0.0314 | 4.2 | 0.000717 | 0 | 4.43 | 0.000847 | -0.0314 |  | CFL | None | 4200 | 0.717 | 4200 | 0.717 | 1.05 | 1.18 | -0.0074762 | 4200 | 0.717 | 4200 | 0.717 | 1.05 | 1.18 | -0.00748
CFLNoneSCEHspNewCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | Hsp | New | CZ06 | 4.2 | 0.000717 | 0 | 4.6 | 0.000863 | -0.0241 | 4.2 | 0.000717 | 0 | 4.6 | 0.000863 | -0.0241 |  | CFL | None | 4200 | 0.717 | 4200 | 0.717 | 1.1 | 1.2 | -0.0057381 | 4200 | 0.717 | 4200 | 0.717 | 1.1 | 1.2 | -0.00574
CFLNoneSCEHspNewCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | Hsp | New | CZ08 | 4.2 | 0.000717 | 0 | 4.65 | 0.000868 | -0.0222 | 4.2 | 0.000717 | 0 | 4.65 | 0.000868 | -0.0222 |  | CFL | None | 4200 | 0.717 | 4200 | 0.717 | 1.11 | 1.21 | -0.0052857 | 4200 | 0.717 | 4200 | 0.717 | 1.11 | 1.21 | -0.00529
CFLNoneSCEHspNewCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | Hsp | New | CZ09 | 4.2 | 0.000717 | 0 | 4.67 | 0.000891 | -0.0226 | 4.2 | 0.000717 | 0 | 4.67 | 0.000891 | -0.0226 |  | CFL | None | 4200 | 0.717 | 4200 | 0.717 | 1.11 | 1.24 | -0.005381 | 4200 | 0.717 | 4200 | 0.717 | 1.11 | 1.24 | -0.00538
CFLNoneSCEHspNewCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | Hsp | New | CZ10 | 4.2 | 0.000717 | 0 | 4.65 | 0.000896 | -0.0248 | 4.2 | 0.000717 | 0 | 4.65 | 0.000896 | -0.0248 |  | CFL | None | 4200 | 0.717 | 4200 | 0.717 | 1.11 | 1.25 | -0.0059048 | 4200 | 0.717 | 4200 | 0.717 | 1.11 | 1.25 | -0.0059
CFLNoneSCEHspNewCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | Hsp | New | CZ13 | 4.2 | 0.000717 | 0 | 4.63 | 0.000891 | -0.028 | 4.2 | 0.000717 | 0 | 4.63 | 0.000891 | -0.028 |  | CFL | None | 4200 | 0.717 | 4200 | 0.717 | 1.1 | 1.24 | -0.0066667 | 4200 | 0.717 | 4200 | 0.717 | 1.1 | 1.24 | -0.00667
CFLNoneSCEHspNewCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | Hsp | New | CZ14 | 4.2 | 0.000717 | 0 | 4.57 | 0.000889 | -0.0309 | 4.2 | 0.000717 | 0 | 4.57 | 0.000889 | -0.0309 |  | CFL | None | 4200 | 0.717 | 4200 | 0.717 | 1.09 | 1.24 | -0.0073571 | 4200 | 0.717 | 4200 | 0.717 | 1.09 | 1.24 | -0.00736
CFLNoneSCEHspNewCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | Hsp | New | CZ15 | 4.2 | 0.000717 | 0 | 4.87 | 0.000903 | -0.02 | 4.2 | 0.000717 | 0 | 4.87 | 0.000903 | -0.02 |  | CFL | None | 4200 | 0.717 | 4200 | 0.717 | 1.16 | 1.26 | -0.0047619 | 4200 | 0.717 | 4200 | 0.717 | 1.16 | 1.26 | -0.00476
CFLNoneSCEHspNewCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | Hsp | New | CZ16 | 4.2 | 0.000717 | 0 | 4.24 | 0.000858 | -0.0445 | 4.2 | 0.000717 | 0 | 4.24 | 0.000858 | -0.0445 |  | CFL | None | 4200 | 0.717 | 4200 | 0.717 | 1.01 | 1.2 | -0.010595 | 4200 | 0.717 | 4200 | 0.717 | 1.01 | 1.2 | -0.0106
CFLNoneSCEHspNewIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | Hsp | New | IOU | 4.2 | 0.000717 | 0 | 4.6343 | 0.0008801 | -0.024552 | 4.2 | 0.000717 | 0 | 4.6343 | 0.0008801 | -0.024552 |  | CFL | None | 4200 | 0.717 | 4200 | 0.717 | 1.1 | 1.23 | -0.0058458 | 4200 | 0.717 | 4200 | 0.717 | 1.1 | 1.23 | -0.00585
CFLNoneSCEHtlExCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | Htl | Ex | CZ05 | 1.67 | 0.000199 | 0 | 1.68 | 0.00025 | -0.00502 | 1.67 | 0.000199 | 0 | 1.68 | 0.00025 | -0.00502 |  | CFL | None | 1670 | 0.199 | 1670 | 0.199 | 1.01 | 1.26 | -0.003006 | 1670 | 0.199 | 1670 | 0.199 | 1.01 | 1.26 | -0.00301
CFLNoneSCEHtlExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | Htl | Ex | CZ06 | 1.67 | 0.000199 | 0 | 1.85 | 0.000252 | -0.00319 | 1.67 | 0.000199 | 0 | 1.85 | 0.000252 | -0.00319 |  | CFL | None | 1670 | 0.199 | 1670 | 0.199 | 1.11 | 1.27 | -0.0019102 | 1670 | 0.199 | 1670 | 0.199 | 1.11 | 1.27 | -0.00191
CFLNoneSCEHtlExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | Htl | Ex | CZ08 | 1.67 | 0.000199 | 0 | 1.87 | 0.000254 | -0.00289 | 1.67 | 0.000199 | 0 | 1.87 | 0.000254 | -0.00289 |  | CFL | None | 1670 | 0.199 | 1670 | 0.199 | 1.12 | 1.28 | -0.0017305 | 1670 | 0.199 | 1670 | 0.199 | 1.12 | 1.28 | -0.00173
CFLNoneSCEHtlExCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | Htl | Ex | CZ09 | 1.67 | 0.000199 | 0 | 1.86 | 0.000258 | -0.00308 | 1.67 | 0.000199 | 0 | 1.86 | 0.000258 | -0.00308 |  | CFL | None | 1670 | 0.199 | 1670 | 0.199 | 1.11 | 1.3 | -0.0018443 | 1670 | 0.199 | 1670 | 0.199 | 1.11 | 1.3 | -0.00184
CFLNoneSCEHtlExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | Htl | Ex | CZ10 | 1.67 | 0.000199 | 0 | 1.81 | 0.000256 | -0.00319 | 1.67 | 0.000199 | 0 | 1.81 | 0.000256 | -0.00319 |  | CFL | None | 1670 | 0.199 | 1670 | 0.199 | 1.08 | 1.29 | -0.0019102 | 1670 | 0.199 | 1670 | 0.199 | 1.08 | 1.29 | -0.00191
CFLNoneSCEHtlExCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | Htl | Ex | CZ13 | 1.67 | 0.000199 | 0 | 1.76 | 0.000255 | -0.00436 | 1.67 | 0.000199 | 0 | 1.76 | 0.000255 | -0.00436 |  | CFL | None | 1670 | 0.199 | 1670 | 0.199 | 1.05 | 1.28 | -0.0026108 | 1670 | 0.199 | 1670 | 0.199 | 1.05 | 1.28 | -0.00261
CFLNoneSCEHtlExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | Htl | Ex | CZ14 | 1.67 | 0.000199 | 0 | 1.74 | 0.000257 | -0.00441 | 1.67 | 0.000199 | 0 | 1.74 | 0.000257 | -0.00441 |  | CFL | None | 1670 | 0.199 | 1670 | 0.199 | 1.04 | 1.29 | -0.0026407 | 1670 | 0.199 | 1670 | 0.199 | 1.04 | 1.29 | -0.00264
CFLNoneSCEHtlExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | Htl | Ex | CZ15 | 1.67 | 0.000199 | 0 | 1.95 | 0.000258 | -0.00176 | 1.67 | 0.000199 | 0 | 1.95 | 0.000258 | -0.00176 |  | CFL | None | 1670 | 0.199 | 1670 | 0.199 | 1.17 | 1.3 | -0.0010539 | 1670 | 0.199 | 1670 | 0.199 | 1.17 | 1.3 | -0.00105
CFLNoneSCEHtlExCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | Htl | Ex | CZ16 | 1.67 | 0.000199 | 0 | 1.53 | 0.00025 | -0.00717 | 1.67 | 0.000199 | 0 | 1.53 | 0.00025 | -0.00717 |  | CFL | None | 1670 | 0.199 | 1670 | 0.199 | 0.916 | 1.26 | -0.0042934 | 1670 | 0.199 | 1670 | 0.199 | 0.916 | 1.26 | -0.00429
CFLNoneSCEHtlExIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | Htl | Ex | IOU | 1.67 | 0.000199 | 0 | 1.8517 | 0.00025455 | -0.0031023 | 1.67 | 0.000199 | 0 | 1.8517 | 0.00025455 | -0.0031023 |  | CFL | None | 1670 | 0.199 | 1670 | 0.199 | 1.11 | 1.28 | -0.0018577 | 1670 | 0.199 | 1670 | 0.199 | 1.11 | 1.28 | -0.00186
CFLNoneSCEHtlNewCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | Htl | New | CZ05 | 1.67 | 0.000199 | 0 | 1.61 | 0.000252 | -0.00527 | 1.67 | 0.000199 | 0 | 1.61 | 0.000252 | -0.00527 |  | CFL | None | 1670 | 0.199 | 1670 | 0.199 | 0.964 | 1.27 | -0.0031557 | 1670 | 0.199 | 1670 | 0.199 | 0.964 | 1.27 | -0.00316
CFLNoneSCEHtlNewCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | Htl | New | CZ06 | 1.67 | 0.000199 | 0 | 1.81 | 0.000256 | -0.00289 | 1.67 | 0.000199 | 0 | 1.81 | 0.000256 | -0.00289 |  | CFL | None | 1670 | 0.199 | 1670 | 0.199 | 1.08 | 1.29 | -0.0017305 | 1670 | 0.199 | 1670 | 0.199 | 1.08 | 1.29 | -0.00173
CFLNoneSCEHtlNewCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | Htl | New | CZ08 | 1.67 | 0.000199 | 0 | 1.84 | 0.000258 | -0.00254 | 1.67 | 0.000199 | 0 | 1.84 | 0.000258 | -0.00254 |  | CFL | None | 1670 | 0.199 | 1670 | 0.199 | 1.1 | 1.3 | -0.001521 | 1670 | 0.199 | 1670 | 0.199 | 1.1 | 1.3 | -0.00152
CFLNoneSCEHtlNewCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | Htl | New | CZ09 | 1.67 | 0.000199 | 0 | 1.82 | 0.000263 | -0.00289 | 1.67 | 0.000199 | 0 | 1.82 | 0.000263 | -0.00289 |  | CFL | None | 1670 | 0.199 | 1670 | 0.199 | 1.09 | 1.32 | -0.0017305 | 1670 | 0.199 | 1670 | 0.199 | 1.09 | 1.32 | -0.00173
CFLNoneSCEHtlNewCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | Htl | New | CZ10 | 1.67 | 0.000199 | 0 | 1.81 | 0.000271 | -0.00321 | 1.67 | 0.000199 | 0 | 1.81 | 0.000271 | -0.00321 |  | CFL | None | 1670 | 0.199 | 1670 | 0.199 | 1.08 | 1.36 | -0.0019222 | 1670 | 0.199 | 1670 | 0.199 | 1.08 | 1.36 | -0.00192
CFLNoneSCEHtlNewCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | Htl | New | CZ13 | 1.67 | 0.000199 | 0 | 1.74 | 0.000263 | -0.0044 | 1.67 | 0.000199 | 0 | 1.74 | 0.000263 | -0.0044 |  | CFL | None | 1670 | 0.199 | 1670 | 0.199 | 1.04 | 1.32 | -0.0026347 | 1670 | 0.199 | 1670 | 0.199 | 1.04 | 1.32 | -0.00263
CFLNoneSCEHtlNewCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | Htl | New | CZ14 | 1.67 | 0.000199 | 0 | 1.71 | 0.000265 | -0.00483 | 1.67 | 0.000199 | 0 | 1.71 | 0.000265 | -0.00483 |  | CFL | None | 1670 | 0.199 | 1670 | 0.199 | 1.02 | 1.33 | -0.0028922 | 1670 | 0.199 | 1670 | 0.199 | 1.02 | 1.33 | -0.00289
CFLNoneSCEHtlNewCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | Htl | New | CZ15 | 1.67 | 0.000199 | 0 | 1.96 | 0.00027 | -0.0016 | 1.67 | 0.000199 | 0 | 1.96 | 0.00027 | -0.0016 |  | CFL | None | 1670 | 0.199 | 1670 | 0.199 | 1.17 | 1.36 | -0.00095808 | 1670 | 0.199 | 1670 | 0.199 | 1.17 | 1.36 | -0.000958
CFLNoneSCEHtlNewCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | Htl | New | CZ16 | 1.67 | 0.000199 | 0 | 1.47 | 0.000255 | -0.00819 | 1.67 | 0.000199 | 0 | 1.47 | 0.000255 | -0.00819 |  | CFL | None | 1670 | 0.199 | 1670 | 0.199 | 0.88 | 1.28 | -0.0049042 | 1670 | 0.199 | 1670 | 0.199 | 0.88 | 1.28 | -0.0049
CFLNoneSCEHtlNewIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | Htl | New | IOU | 1.67 | 0.000199 | 0 | 1.8304 | 0.00026296 | -0.0029422 | 1.67 | 0.000199 | 0 | 1.8304 | 0.00026296 | -0.0029422 |  | CFL | None | 1670 | 0.199 | 1670 | 0.199 | 1.1 | 1.32 | -0.0017618 | 1670 | 0.199 | 1670 | 0.199 | 1.1 | 1.32 | -0.00176
CFLNoneSCEMBTExCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | MBT | Ex | CZ05 | 3.09 | 0.00078 | 0 | 3.54 | 0.00097 | -0.00131 | 3.09 | 0.00078 | 0 | 3.54 | 0.00097 | -0.00131 |  | CFL | None | 3090 | 0.78 | 3090 | 0.78 | 1.15 | 1.24 | -0.00042395 | 3090 | 0.78 | 3090 | 0.78 | 1.15 | 1.24 | -0.000424
CFLNoneSCEMBTExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | MBT | Ex | CZ06 | 3.09 | 0.00078 | 0 | 3.62 | 0.000945 | -0.000565 | 3.09 | 0.00078 | 0 | 3.62 | 0.000945 | -0.000565 |  | CFL | None | 3090 | 0.78 | 3090 | 0.78 | 1.17 | 1.21 | -0.00018285 | 3090 | 0.78 | 3090 | 0.78 | 1.17 | 1.21 | -0.000183
CFLNoneSCEMBTExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | MBT | Ex | CZ08 | 3.09 | 0.00078 | 0 | 3.64 | 0.000981 | -0.000211 | 3.09 | 0.00078 | 0 | 3.64 | 0.000981 | -0.000211 |  | CFL | None | 3090 | 0.78 | 3090 | 0.78 | 1.18 | 1.26 | -6.8285e-05 | 3090 | 0.78 | 3090 | 0.78 | 1.18 | 1.26 | -6.83e-05
CFLNoneSCEMBTExCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | MBT | Ex | CZ09 | 3.09 | 0.00078 | 0 | 3.63 | 0.000984 | -0.000868 | 3.09 | 0.00078 | 0 | 3.63 | 0.000984 | -0.000868 |  | CFL | None | 3090 | 0.78 | 3090 | 0.78 | 1.17 | 1.26 | -0.00028091 | 3090 | 0.78 | 3090 | 0.78 | 1.17 | 1.26 | -0.000281
CFLNoneSCEMBTExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | MBT | Ex | CZ10 | 3.09 | 0.00078 | 0 | 3.52 | 0.000985 | -0.00097 | 3.09 | 0.00078 | 0 | 3.52 | 0.000985 | -0.00097 |  | CFL | None | 3090 | 0.78 | 3090 | 0.78 | 1.14 | 1.26 | -0.00031392 | 3090 | 0.78 | 3090 | 0.78 | 1.14 | 1.26 | -0.000314
CFLNoneSCEMBTExCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | MBT | Ex | CZ13 | 3.09 | 0.00078 | 0 | 3.52 | 0.000952 | -0.00202 | 3.09 | 0.00078 | 0 | 3.52 | 0.000952 | -0.00202 |  | CFL | None | 3090 | 0.78 | 3090 | 0.78 | 1.14 | 1.22 | -0.00065372 | 3090 | 0.78 | 3090 | 0.78 | 1.14 | 1.22 | -0.000654
CFLNoneSCEMBTExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | MBT | Ex | CZ14 | 3.09 | 0.00078 | 0 | 3.52 | 0.000984 | -0.00233 | 3.09 | 0.00078 | 0 | 3.52 | 0.000984 | -0.00233 |  | CFL | None | 3090 | 0.78 | 3090 | 0.78 | 1.14 | 1.26 | -0.00075405 | 3090 | 0.78 | 3090 | 0.78 | 1.14 | 1.26 | -0.000754
CFLNoneSCEMBTExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | MBT | Ex | CZ15 | 3.09 | 0.00078 | 0 | 3.66 | 0.000988 | 0 | 3.09 | 0.00078 | 0 | 3.66 | 0.000988 | 0 |  | CFL | None | 3090 | 0.78 | 3090 | 0.78 | 1.18 | 1.27 | 0 | 3090 | 0.78 | 3090 | 0.78 | 1.18 | 1.27 | 0
CFLNoneSCEMBTExCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | MBT | Ex | CZ16 | 3.09 | 0.00078 | 0 | 3.31 | 0.000929 | -0.00819 | 3.09 | 0.00078 | 0 | 3.31 | 0.000929 | -0.00819 |  | CFL | None | 3090 | 0.78 | 3090 | 0.78 | 1.07 | 1.19 | -0.0026505 | 3090 | 0.78 | 3090 | 0.78 | 1.07 | 1.19 | -0.00265
CFLNoneSCEMBTExIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | MBT | Ex | IOU | 3.09 | 0.00078 | 0 | 3.6008 | 0.00097292 | -0.00080034 | 3.09 | 0.00078 | 0 | 3.6008 | 0.00097292 | -0.00080034 |  | CFL | None | 3090 | 0.78 | 3090 | 0.78 | 1.17 | 1.25 | -0.00025901 | 3090 | 0.78 | 3090 | 0.78 | 1.17 | 1.25 | -0.000259
CFLNoneSCEMBTNewCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | MBT | New | CZ05 | 3.09 | 0.00078 | 0 | 3.33 | 0.000963 | -0.00106 | 3.09 | 0.00078 | 0 | 3.33 | 0.000963 | -0.00106 |  | CFL | None | 3090 | 0.78 | 3090 | 0.78 | 1.08 | 1.23 | -0.00034304 | 3090 | 0.78 | 3090 | 0.78 | 1.08 | 1.23 | -0.000343
CFLNoneSCEMBTNewCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | MBT | New | CZ06 | 3.09 | 0.00078 | 0 | 3.45 | 0.000969 | -0.00101 | 3.09 | 0.00078 | 0 | 3.45 | 0.000969 | -0.00101 |  | CFL | None | 3090 | 0.78 | 3090 | 0.78 | 1.12 | 1.24 | -0.00032686 | 3090 | 0.78 | 3090 | 0.78 | 1.12 | 1.24 | -0.000327
CFLNoneSCEMBTNewCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | MBT | New | CZ08 | 3.09 | 0.00078 | 0 | 3.47 | 0.000994 | -0.000812 | 3.09 | 0.00078 | 0 | 3.47 | 0.000994 | -0.000812 |  | CFL | None | 3090 | 0.78 | 3090 | 0.78 | 1.12 | 1.27 | -0.00026278 | 3090 | 0.78 | 3090 | 0.78 | 1.12 | 1.27 | -0.000263
CFLNoneSCEMBTNewCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | MBT | New | CZ09 | 3.09 | 0.00078 | 0 | 3.46 | 0.00102 | -0.000955 | 3.09 | 0.00078 | 0 | 3.46 | 0.00102 | -0.000955 |  | CFL | None | 3090 | 0.78 | 3090 | 0.78 | 1.12 | 1.31 | -0.00030906 | 3090 | 0.78 | 3090 | 0.78 | 1.12 | 1.31 | -0.000309
CFLNoneSCEMBTNewCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | MBT | New | CZ10 | 3.09 | 0.00078 | 0 | 3.48 | 0.00103 | -0.00101 | 3.09 | 0.00078 | 0 | 3.48 | 0.00103 | -0.00101 |  | CFL | None | 3090 | 0.78 | 3090 | 0.78 | 1.13 | 1.32 | -0.00032686 | 3090 | 0.78 | 3090 | 0.78 | 1.13 | 1.32 | -0.000327
CFLNoneSCEMBTNewCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | MBT | New | CZ13 | 3.09 | 0.00078 | 0 | 3.44 | 0.001 | -0.00177 | 3.09 | 0.00078 | 0 | 3.44 | 0.001 | -0.00177 |  | CFL | None | 3090 | 0.78 | 3090 | 0.78 | 1.11 | 1.28 | -0.00057282 | 3090 | 0.78 | 3090 | 0.78 | 1.11 | 1.28 | -0.000573
CFLNoneSCEMBTNewCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | MBT | New | CZ14 | 3.09 | 0.00078 | 0 | 3.44 | 0.00102 | -0.00195 | 3.09 | 0.00078 | 0 | 3.44 | 0.00102 | -0.00195 |  | CFL | None | 3090 | 0.78 | 3090 | 0.78 | 1.11 | 1.31 | -0.00063107 | 3090 | 0.78 | 3090 | 0.78 | 1.11 | 1.31 | -0.000631
CFLNoneSCEMBTNewCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | MBT | New | CZ15 | 3.09 | 0.00078 | 0 | 3.66 | 0.00103 | 0 | 3.09 | 0.00078 | 0 | 3.66 | 0.00103 | 0 |  | CFL | None | 3090 | 0.78 | 3090 | 0.78 | 1.18 | 1.32 | 0 | 3090 | 0.78 | 3090 | 0.78 | 1.18 | 1.32 | 0
CFLNoneSCEMBTNewCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | MBT | New | CZ16 | 3.09 | 0.00078 | 0 | 3.27 | 0.000963 | -0.00664 | 3.09 | 0.00078 | 0 | 3.27 | 0.000963 | -0.00664 |  | CFL | None | 3090 | 0.78 | 3090 | 0.78 | 1.06 | 1.23 | -0.0021489 | 3090 | 0.78 | 3090 | 0.78 | 1.06 | 1.23 | -0.00215
CFLNoneSCEMBTNewIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | MBT | New | IOU | 3.09 | 0.00078 | 0 | 3.4812 | 0.0010082 | -0.0010933 | 3.09 | 0.00078 | 0 | 3.4812 | 0.0010082 | -0.0010933 |  | CFL | None | 3090 | 0.78 | 3090 | 0.78 | 1.13 | 1.29 | -0.00035382 | 3090 | 0.78 | 3090 | 0.78 | 1.13 | 1.29 | -0.000354
CFLNoneSCEMLIExCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | MLI | Ex | CZ05 | 2.58 | 0.000777 | 0 | 2.72 | 0.00094 | -0.0125 | 2.58 | 0.000777 | 0 | 2.72 | 0.00094 | -0.0125 |  | CFL | None | 2580 | 0.777 | 2580 | 0.777 | 1.05 | 1.21 | -0.004845 | 2580 | 0.777 | 2580 | 0.777 | 1.05 | 1.21 | -0.00485
CFLNoneSCEMLIExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | MLI | Ex | CZ06 | 2.58 | 0.000777 | 0 | 2.87 | 0.000924 | -0.00433 | 2.58 | 0.000777 | 0 | 2.87 | 0.000924 | -0.00433 |  | CFL | None | 2580 | 0.777 | 2580 | 0.777 | 1.11 | 1.19 | -0.0016783 | 2580 | 0.777 | 2580 | 0.777 | 1.11 | 1.19 | -0.00168
CFLNoneSCEMLIExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | MLI | Ex | CZ08 | 2.58 | 0.000777 | 0 | 2.88 | 0.000922 | -0.00356 | 2.58 | 0.000777 | 0 | 2.88 | 0.000922 | -0.00356 |  | CFL | None | 2580 | 0.777 | 2580 | 0.777 | 1.12 | 1.19 | -0.0013798 | 2580 | 0.777 | 2580 | 0.777 | 1.12 | 1.19 | -0.00138
CFLNoneSCEMLIExCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | MLI | Ex | CZ09 | 2.58 | 0.000777 | 0 | 2.87 | 0.000943 | -0.00488 | 2.58 | 0.000777 | 0 | 2.87 | 0.000943 | -0.00488 |  | CFL | None | 2580 | 0.777 | 2580 | 0.777 | 1.11 | 1.21 | -0.0018915 | 2580 | 0.777 | 2580 | 0.777 | 1.11 | 1.21 | -0.00189
CFLNoneSCEMLIExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | MLI | Ex | CZ10 | 2.58 | 0.000777 | 0 | 2.78 | 0.000936 | -0.00627 | 2.58 | 0.000777 | 0 | 2.78 | 0.000936 | -0.00627 |  | CFL | None | 2580 | 0.777 | 2580 | 0.777 | 1.08 | 1.2 | -0.0024302 | 2580 | 0.777 | 2580 | 0.777 | 1.08 | 1.2 | -0.00243
CFLNoneSCEMLIExCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | MLI | Ex | CZ13 | 2.58 | 0.000777 | 0 | 2.76 | 0.000924 | -0.0139 | 2.58 | 0.000777 | 0 | 2.76 | 0.000924 | -0.0139 |  | CFL | None | 2580 | 0.777 | 2580 | 0.777 | 1.07 | 1.19 | -0.0053876 | 2580 | 0.777 | 2580 | 0.777 | 1.07 | 1.19 | -0.00539
CFLNoneSCEMLIExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | MLI | Ex | CZ14 | 2.58 | 0.000777 | 0 | 2.73 | 0.000929 | -0.016 | 2.58 | 0.000777 | 0 | 2.73 | 0.000929 | -0.016 |  | CFL | None | 2580 | 0.777 | 2580 | 0.777 | 1.06 | 1.2 | -0.0062016 | 2580 | 0.777 | 2580 | 0.777 | 1.06 | 1.2 | -0.0062
CFLNoneSCEMLIExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | MLI | Ex | CZ15 | 2.58 | 0.000777 | 0 | 2.97 | 0.000925 | -0.00161 | 2.58 | 0.000777 | 0 | 2.97 | 0.000925 | -0.00161 |  | CFL | None | 2580 | 0.777 | 2580 | 0.777 | 1.15 | 1.19 | -0.00062403 | 2580 | 0.777 | 2580 | 0.777 | 1.15 | 1.19 | -0.000624
CFLNoneSCEMLIExCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | MLI | Ex | CZ16 | 2.58 | 0.000777 | 0 | 2.54 | 0.000915 | -0.0312 | 2.58 | 0.000777 | 0 | 2.54 | 0.000915 | -0.0312 |  | CFL | None | 2580 | 0.777 | 2580 | 0.777 | 0.984 | 1.18 | -0.012093 | 2580 | 0.777 | 2580 | 0.777 | 0.984 | 1.18 | -0.0121
CFLNoneSCEMLIExIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | MLI | Ex | IOU | 2.58 | 0.000777 | 0 | 2.8489 | 0.00092828 | -0.0055919 | 2.58 | 0.000777 | 0 | 2.8489 | 0.00092828 | -0.0055919 |  | CFL | None | 2580 | 0.777 | 2580 | 0.777 | 1.1 | 1.19 | -0.0021674 | 2580 | 0.777 | 2580 | 0.777 | 1.1 | 1.19 | -0.00217
CFLNoneSCEMLINewCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | MLI | New | CZ05 | 2.58 | 0.000777 | 0 | 2.57 | 0.000925 | -0.0206 | 2.58 | 0.000777 | 0 | 2.57 | 0.000925 | -0.0206 |  | CFL | None | 2580 | 0.777 | 2580 | 0.777 | 0.996 | 1.19 | -0.0079845 | 2580 | 0.777 | 2580 | 0.777 | 0.996 | 1.19 | -0.00798
CFLNoneSCEMLINewCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | MLI | New | CZ06 | 2.58 | 0.000777 | 0 | 2.71 | 0.000908 | -0.00931 | 2.58 | 0.000777 | 0 | 2.71 | 0.000908 | -0.00931 |  | CFL | None | 2580 | 0.777 | 2580 | 0.777 | 1.05 | 1.17 | -0.0036085 | 2580 | 0.777 | 2580 | 0.777 | 1.05 | 1.17 | -0.00361
CFLNoneSCEMLINewCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | MLI | New | CZ08 | 2.58 | 0.000777 | 0 | 2.75 | 0.000913 | -0.00751 | 2.58 | 0.000777 | 0 | 2.75 | 0.000913 | -0.00751 |  | CFL | None | 2580 | 0.777 | 2580 | 0.777 | 1.07 | 1.18 | -0.0029109 | 2580 | 0.777 | 2580 | 0.777 | 1.07 | 1.18 | -0.00291
CFLNoneSCEMLINewCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | MLI | New | CZ09 | 2.58 | 0.000777 | 0 | 2.82 | 0.000998 | -0.00864 | 2.58 | 0.000777 | 0 | 2.82 | 0.000998 | -0.00864 |  | CFL | None | 2580 | 0.777 | 2580 | 0.777 | 1.09 | 1.28 | -0.0033488 | 2580 | 0.777 | 2580 | 0.777 | 1.09 | 1.28 | -0.00335
CFLNoneSCEMLINewCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | MLI | New | CZ10 | 2.58 | 0.000777 | 0 | 2.84 | 0.00102 | -0.00944 | 2.58 | 0.000777 | 0 | 2.84 | 0.00102 | -0.00944 |  | CFL | None | 2580 | 0.777 | 2580 | 0.777 | 1.1 | 1.31 | -0.0036589 | 2580 | 0.777 | 2580 | 0.777 | 1.1 | 1.31 | -0.00366
CFLNoneSCEMLINewCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | MLI | New | CZ13 | 2.58 | 0.000777 | 0 | 2.78 | 0.000977 | -0.0171 | 2.58 | 0.000777 | 0 | 2.78 | 0.000977 | -0.0171 |  | CFL | None | 2580 | 0.777 | 2580 | 0.777 | 1.08 | 1.26 | -0.0066279 | 2580 | 0.777 | 2580 | 0.777 | 1.08 | 1.26 | -0.00663
CFLNoneSCEMLINewCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | MLI | New | CZ14 | 2.58 | 0.000777 | 0 | 2.73 | 0.000949 | -0.0186 | 2.58 | 0.000777 | 0 | 2.73 | 0.000949 | -0.0186 |  | CFL | None | 2580 | 0.777 | 2580 | 0.777 | 1.06 | 1.22 | -0.0072093 | 2580 | 0.777 | 2580 | 0.777 | 1.06 | 1.22 | -0.00721
CFLNoneSCEMLINewCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | MLI | New | CZ15 | 2.58 | 0.000777 | 0 | 3.03 | 0.00103 | -0.00158 | 2.58 | 0.000777 | 0 | 3.03 | 0.00103 | -0.00158 |  | CFL | None | 2580 | 0.777 | 2580 | 0.777 | 1.17 | 1.33 | -0.0006124 | 2580 | 0.777 | 2580 | 0.777 | 1.17 | 1.33 | -0.000612
CFLNoneSCEMLINewCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | MLI | New | CZ16 | 2.58 | 0.000777 | 0 | 2.54 | 0.000914 | -0.033 | 2.58 | 0.000777 | 0 | 2.54 | 0.000914 | -0.033 |  | CFL | None | 2580 | 0.777 | 2580 | 0.777 | 0.984 | 1.18 | -0.012791 | 2580 | 0.777 | 2580 | 0.777 | 0.984 | 1.18 | -0.0128
CFLNoneSCEMLINewIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | MLI | New | IOU | 2.58 | 0.000777 | 0 | 2.8022 | 0.00096985 | -0.0094527 | 2.58 | 0.000777 | 0 | 2.8022 | 0.00096985 | -0.0094527 |  | CFL | None | 2580 | 0.777 | 2580 | 0.777 | 1.09 | 1.25 | -0.0036638 | 2580 | 0.777 | 2580 | 0.777 | 1.09 | 1.25 | -0.00366
CFLNoneSCEMtlExCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | Mtl | Ex | CZ05 | 1.37 | 0.000151 | 0 | 1.46 | 0.00019 | -0.00654 | 1.37 | 0.000151 | 0 | 1.46 | 0.00019 | -0.00654 |  | CFL | None | 1370 | 0.151 | 1370 | 0.151 | 1.07 | 1.26 | -0.0047737 | 1370 | 0.151 | 1370 | 0.151 | 1.07 | 1.26 | -0.00477
CFLNoneSCEMtlExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | Mtl | Ex | CZ06 | 1.37 | 0.000151 | 0 | 1.57 | 0.000191 | -0.0034 | 1.37 | 0.000151 | 0 | 1.57 | 0.000191 | -0.0034 |  | CFL | None | 1370 | 0.151 | 1370 | 0.151 | 1.15 | 1.26 | -0.0024818 | 1370 | 0.151 | 1370 | 0.151 | 1.15 | 1.26 | -0.00248
CFLNoneSCEMtlExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | Mtl | Ex | CZ08 | 1.37 | 0.000151 | 0 | 1.59 | 0.000193 | -0.00283 | 1.37 | 0.000151 | 0 | 1.59 | 0.000193 | -0.00283 |  | CFL | None | 1370 | 0.151 | 1370 | 0.151 | 1.16 | 1.28 | -0.0020657 | 1370 | 0.151 | 1370 | 0.151 | 1.16 | 1.28 | -0.00207
CFLNoneSCEMtlExCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | Mtl | Ex | CZ09 | 1.37 | 0.000151 | 0 | 1.58 | 0.000198 | -0.00319 | 1.37 | 0.000151 | 0 | 1.58 | 0.000198 | -0.00319 |  | CFL | None | 1370 | 0.151 | 1370 | 0.151 | 1.15 | 1.31 | -0.0023285 | 1370 | 0.151 | 1370 | 0.151 | 1.15 | 1.31 | -0.00233
CFLNoneSCEMtlExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | Mtl | Ex | CZ10 | 1.37 | 0.000151 | 0 | 1.55 | 0.000198 | -0.00357 | 1.37 | 0.000151 | 0 | 1.55 | 0.000198 | -0.00357 |  | CFL | None | 1370 | 0.151 | 1370 | 0.151 | 1.13 | 1.31 | -0.0026058 | 1370 | 0.151 | 1370 | 0.151 | 1.13 | 1.31 | -0.00261
CFLNoneSCEMtlExCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | Mtl | Ex | CZ13 | 1.37 | 0.000151 | 0 | 1.53 | 0.000197 | -0.00505 | 1.37 | 0.000151 | 0 | 1.53 | 0.000197 | -0.00505 |  | CFL | None | 1370 | 0.151 | 1370 | 0.151 | 1.12 | 1.3 | -0.0036861 | 1370 | 0.151 | 1370 | 0.151 | 1.12 | 1.3 | -0.00369
CFLNoneSCEMtlExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | Mtl | Ex | CZ14 | 1.37 | 0.000151 | 0 | 1.51 | 0.000198 | -0.0049 | 1.37 | 0.000151 | 0 | 1.51 | 0.000198 | -0.0049 |  | CFL | None | 1370 | 0.151 | 1370 | 0.151 | 1.1 | 1.31 | -0.0035766 | 1370 | 0.151 | 1370 | 0.151 | 1.1 | 1.31 | -0.00358
CFLNoneSCEMtlExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | Mtl | Ex | CZ15 | 1.37 | 0.000151 | 0 | 1.65 | 0.000201 | -0.00145 | 1.37 | 0.000151 | 0 | 1.65 | 0.000201 | -0.00145 |  | CFL | None | 1370 | 0.151 | 1370 | 0.151 | 1.2 | 1.33 | -0.0010584 | 1370 | 0.151 | 1370 | 0.151 | 1.2 | 1.33 | -0.00106
CFLNoneSCEMtlExCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | Mtl | Ex | CZ16 | 1.37 | 0.000151 | 0 | 1.36 | 0.00019 | -0.00869 | 1.37 | 0.000151 | 0 | 1.36 | 0.00019 | -0.00869 |  | CFL | None | 1370 | 0.151 | 1370 | 0.151 | 0.993 | 1.26 | -0.0063431 | 1370 | 0.151 | 1370 | 0.151 | 0.993 | 1.26 | -0.00634
CFLNoneSCEMtlExIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | Mtl | Ex | IOU | 1.37 | 0.000151 | 0 | 1.5761 | 0.00019456 | -0.0032372 | 1.37 | 0.000151 | 0 | 1.5761 | 0.00019456 | -0.0032372 |  | CFL | None | 1370 | 0.151 | 1370 | 0.151 | 1.15 | 1.29 | -0.0023629 | 1370 | 0.151 | 1370 | 0.151 | 1.15 | 1.29 | -0.00236
CFLNoneSCEMtlNewCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | Mtl | New | CZ05 | 1.37 | 0.000151 | 0 | 1.41 | 0.000191 | -0.00879 | 1.37 | 0.000151 | 0 | 1.41 | 0.000191 | -0.00879 |  | CFL | None | 1370 | 0.151 | 1370 | 0.151 | 1.03 | 1.26 | -0.0064161 | 1370 | 0.151 | 1370 | 0.151 | 1.03 | 1.26 | -0.00642
CFLNoneSCEMtlNewCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | Mtl | New | CZ06 | 1.37 | 0.000151 | 0 | 1.55 | 0.000195 | -0.00465 | 1.37 | 0.000151 | 0 | 1.55 | 0.000195 | -0.00465 |  | CFL | None | 1370 | 0.151 | 1370 | 0.151 | 1.13 | 1.29 | -0.0033942 | 1370 | 0.151 | 1370 | 0.151 | 1.13 | 1.29 | -0.00339
CFLNoneSCEMtlNewCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | Mtl | New | CZ08 | 1.37 | 0.000151 | 0 | 1.57 | 0.000198 | -0.00387 | 1.37 | 0.000151 | 0 | 1.57 | 0.000198 | -0.00387 |  | CFL | None | 1370 | 0.151 | 1370 | 0.151 | 1.15 | 1.31 | -0.0028248 | 1370 | 0.151 | 1370 | 0.151 | 1.15 | 1.31 | -0.00282
CFLNoneSCEMtlNewCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | Mtl | New | CZ09 | 1.37 | 0.000151 | 0 | 1.57 | 0.000203 | -0.0039 | 1.37 | 0.000151 | 0 | 1.57 | 0.000203 | -0.0039 |  | CFL | None | 1370 | 0.151 | 1370 | 0.151 | 1.15 | 1.34 | -0.0028467 | 1370 | 0.151 | 1370 | 0.151 | 1.15 | 1.34 | -0.00285
CFLNoneSCEMtlNewCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | Mtl | New | CZ10 | 1.37 | 0.000151 | 0 | 1.55 | 0.000204 | -0.00483 | 1.37 | 0.000151 | 0 | 1.55 | 0.000204 | -0.00483 |  | CFL | None | 1370 | 0.151 | 1370 | 0.151 | 1.13 | 1.35 | -0.0035255 | 1370 | 0.151 | 1370 | 0.151 | 1.13 | 1.35 | -0.00353
CFLNoneSCEMtlNewCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | Mtl | New | CZ13 | 1.37 | 0.000151 | 0 | 1.51 | 0.000202 | -0.00624 | 1.37 | 0.000151 | 0 | 1.51 | 0.000202 | -0.00624 |  | CFL | None | 1370 | 0.151 | 1370 | 0.151 | 1.1 | 1.34 | -0.0045547 | 1370 | 0.151 | 1370 | 0.151 | 1.1 | 1.34 | -0.00455
CFLNoneSCEMtlNewCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | Mtl | New | CZ14 | 1.37 | 0.000151 | 0 | 1.49 | 0.000204 | -0.00649 | 1.37 | 0.000151 | 0 | 1.49 | 0.000204 | -0.00649 |  | CFL | None | 1370 | 0.151 | 1370 | 0.151 | 1.09 | 1.35 | -0.0047372 | 1370 | 0.151 | 1370 | 0.151 | 1.09 | 1.35 | -0.00474
CFLNoneSCEMtlNewCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | Mtl | New | CZ15 | 1.37 | 0.000151 | 0 | 1.66 | 0.000209 | -0.00225 | 1.37 | 0.000151 | 0 | 1.66 | 0.000209 | -0.00225 |  | CFL | None | 1370 | 0.151 | 1370 | 0.151 | 1.21 | 1.38 | -0.0016423 | 1370 | 0.151 | 1370 | 0.151 | 1.21 | 1.38 | -0.00164
CFLNoneSCEMtlNewCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | Mtl | New | CZ16 | 1.37 | 0.000151 | 0 | 1.33 | 0.000193 | -0.0101 | 1.37 | 0.000151 | 0 | 1.33 | 0.000193 | -0.0101 |  | CFL | None | 1370 | 0.151 | 1370 | 0.151 | 0.971 | 1.28 | -0.0073723 | 1370 | 0.151 | 1370 | 0.151 | 0.971 | 1.28 | -0.00737
CFLNoneSCEMtlNewIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | Mtl | New | IOU | 1.37 | 0.000151 | 0 | 1.5689 | 0.00020158 | -0.0042343 | 1.37 | 0.000151 | 0 | 1.5689 | 0.00020158 | -0.0042343 |  | CFL | None | 1370 | 0.151 | 1370 | 0.151 | 1.15 | 1.33 | -0.0030907 | 1370 | 0.151 | 1370 | 0.151 | 1.15 | 1.33 | -0.00309
CFLNoneSCENrsExCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | Nrs | Ex | CZ05 | 3.57 | 0.000565 | 0 | 3.65 | 0.000697 | -0.0522 | 3.57 | 0.000565 | 0 | 3.65 | 0.000697 | -0.0522 |  | CFL | None | 3570 | 0.565 | 3570 | 0.565 | 1.02 | 1.23 | -0.014622 | 3570 | 0.565 | 3570 | 0.565 | 1.02 | 1.23 | -0.0146
CFLNoneSCENrsExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | Nrs | Ex | CZ06 | 3.57 | 0.000565 | 0 | 3.89 | 0.00073 | -0.0345 | 3.57 | 0.000565 | 0 | 3.89 | 0.00073 | -0.0345 |  | CFL | None | 3570 | 0.565 | 3570 | 0.565 | 1.09 | 1.29 | -0.0096639 | 3570 | 0.565 | 3570 | 0.565 | 1.09 | 1.29 | -0.00966
CFLNoneSCENrsExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | Nrs | Ex | CZ08 | 3.57 | 0.000565 | 0 | 3.93 | 0.000733 | -0.0333 | 3.57 | 0.000565 | 0 | 3.93 | 0.000733 | -0.0333 |  | CFL | None | 3570 | 0.565 | 3570 | 0.565 | 1.1 | 1.3 | -0.0093277 | 3570 | 0.565 | 3570 | 0.565 | 1.1 | 1.3 | -0.00933
CFLNoneSCENrsExCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | Nrs | Ex | CZ09 | 3.57 | 0.000565 | 0 | 3.94 | 0.000755 | -0.034 | 3.57 | 0.000565 | 0 | 3.94 | 0.000755 | -0.034 |  | CFL | None | 3570 | 0.565 | 3570 | 0.565 | 1.1 | 1.34 | -0.0095238 | 3570 | 0.565 | 3570 | 0.565 | 1.1 | 1.34 | -0.00952
CFLNoneSCENrsExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | Nrs | Ex | CZ10 | 3.57 | 0.000565 | 0 | 3.8893 | 0.000754 | -0.034 | 3.57 | 0.000565 | 0 | 3.8893 | 0.000754 | -0.034 |  | CFL | None | 3570 | 0.565 | 3570 | 0.565 | 1.09 | 1.33 | -0.0095238 | 3570 | 0.565 | 3570 | 0.565 | 1.09 | 1.33 | -0.00952
CFLNoneSCENrsExCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | Nrs | Ex | CZ13 | 3.57 | 0.000565 | 0 | 3.85 | 0.000746 | -0.0393 | 3.57 | 0.000565 | 0 | 3.85 | 0.000746 | -0.0393 |  | CFL | None | 3570 | 0.565 | 3570 | 0.565 | 1.08 | 1.32 | -0.011008 | 3570 | 0.565 | 3570 | 0.565 | 1.08 | 1.32 | -0.011
CFLNoneSCENrsExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | Nrs | Ex | CZ14 | 3.57 | 0.000565 | 0 | 3.86 | 0.000746 | -0.0407 | 3.57 | 0.000565 | 0 | 3.86 | 0.000746 | -0.0407 |  | CFL | None | 3570 | 0.565 | 3570 | 0.565 | 1.08 | 1.32 | -0.011401 | 3570 | 0.565 | 3570 | 0.565 | 1.08 | 1.32 | -0.0114
CFLNoneSCENrsExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | Nrs | Ex | CZ15 | 3.57 | 0.000565 | 0 | 4.15 | 0.00076 | -0.0204 | 3.57 | 0.000565 | 0 | 4.15 | 0.00076 | -0.0204 |  | CFL | None | 3570 | 0.565 | 3570 | 0.565 | 1.16 | 1.35 | -0.0057143 | 3570 | 0.565 | 3570 | 0.565 | 1.16 | 1.35 | -0.00571
CFLNoneSCENrsExCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | Nrs | Ex | CZ16 | 3.57 | 0.000565 | 0 | 3.56 | 0.000713 | -0.0593 | 3.57 | 0.000565 | 0 | 3.56 | 0.000713 | -0.0593 |  | CFL | None | 3570 | 0.565 | 3570 | 0.565 | 0.997 | 1.26 | -0.016611 | 3570 | 0.565 | 3570 | 0.565 | 0.997 | 1.26 | -0.0166
CFLNoneSCENrsExIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | Nrs | Ex | IOU | 3.57 | 0.000565 | 0 | 3.9041 | 0.00073917 | -0.034693 | 3.57 | 0.000565 | 0 | 3.9041 | 0.00073917 | -0.034693 |  | CFL | None | 3570 | 0.565 | 3570 | 0.565 | 1.09 | 1.31 | -0.0097179 | 3570 | 0.565 | 3570 | 0.565 | 1.09 | 1.31 | -0.00972
CFLNoneSCENrsNewCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | Nrs | New | CZ05 | 3.57 | 0.000565 | 0 | 3.5 | 0.000688 | -0.0582 | 3.57 | 0.000565 | 0 | 3.5 | 0.000688 | -0.0582 |  | CFL | None | 3570 | 0.565 | 3570 | 0.565 | 0.98 | 1.22 | -0.016303 | 3570 | 0.565 | 3570 | 0.565 | 0.98 | 1.22 | -0.0163
CFLNoneSCENrsNewCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | Nrs | New | CZ06 | 3.57 | 0.000565 | 0 | 3.72 | 0.000719 | -0.0357 | 3.57 | 0.000565 | 0 | 3.72 | 0.000719 | -0.0357 |  | CFL | None | 3570 | 0.565 | 3570 | 0.565 | 1.04 | 1.27 | -0.01 | 3570 | 0.565 | 3570 | 0.565 | 1.04 | 1.27 | -0.01
CFLNoneSCENrsNewCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | Nrs | New | CZ08 | 3.57 | 0.000565 | 0 | 3.78 | 0.000722 | -0.0341 | 3.57 | 0.000565 | 0 | 3.78 | 0.000722 | -0.0341 |  | CFL | None | 3570 | 0.565 | 3570 | 0.565 | 1.06 | 1.28 | -0.0095518 | 3570 | 0.565 | 3570 | 0.565 | 1.06 | 1.28 | -0.00955
CFLNoneSCENrsNewCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | Nrs | New | CZ09 | 3.57 | 0.000565 | 0 | 3.8 | 0.000748 | -0.0344 | 3.57 | 0.000565 | 0 | 3.8 | 0.000748 | -0.0344 |  | CFL | None | 3570 | 0.565 | 3570 | 0.565 | 1.06 | 1.32 | -0.0096359 | 3570 | 0.565 | 3570 | 0.565 | 1.06 | 1.32 | -0.00964
CFLNoneSCENrsNewCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | Nrs | New | CZ10 | 3.57 | 0.000565 | 0 | 3.82 | 0.00075 | -0.035 | 3.57 | 0.000565 | 0 | 3.82 | 0.00075 | -0.035 |  | CFL | None | 3570 | 0.565 | 3570 | 0.565 | 1.07 | 1.33 | -0.0098039 | 3570 | 0.565 | 3570 | 0.565 | 1.07 | 1.33 | -0.0098
CFLNoneSCENrsNewCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | Nrs | New | CZ13 | 3.57 | 0.000565 | 0 | 3.79 | 0.000743 | -0.0414 | 3.57 | 0.000565 | 0 | 3.79 | 0.000743 | -0.0414 |  | CFL | None | 3570 | 0.565 | 3570 | 0.565 | 1.06 | 1.32 | -0.011597 | 3570 | 0.565 | 3570 | 0.565 | 1.06 | 1.32 | -0.0116
CFLNoneSCENrsNewCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | Nrs | New | CZ14 | 3.57 | 0.000565 | 0 | 3.79 | 0.000731 | -0.0432 | 3.57 | 0.000565 | 0 | 3.79 | 0.000731 | -0.0432 |  | CFL | None | 3570 | 0.565 | 3570 | 0.565 | 1.06 | 1.29 | -0.012101 | 3570 | 0.565 | 3570 | 0.565 | 1.06 | 1.29 | -0.0121
CFLNoneSCENrsNewCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | Nrs | New | CZ15 | 3.57 | 0.000565 | 0 | 4.11 | 0.000751 | -0.0168 | 3.57 | 0.000565 | 0 | 4.11 | 0.000751 | -0.0168 |  | CFL | None | 3570 | 0.565 | 3570 | 0.565 | 1.15 | 1.33 | -0.0047059 | 3570 | 0.565 | 3570 | 0.565 | 1.15 | 1.33 | -0.00471
CFLNoneSCENrsNewCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | Nrs | New | CZ16 | 3.57 | 0.000565 | 0 | 3.51 | 0.000706 | -0.0643 | 3.57 | 0.000565 | 0 | 3.51 | 0.000706 | -0.0643 |  | CFL | None | 3570 | 0.565 | 3570 | 0.565 | 0.983 | 1.25 | -0.018011 | 3570 | 0.565 | 3570 | 0.565 | 0.983 | 1.25 | -0.018
CFLNoneSCENrsNewIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | Nrs | New | IOU | 3.57 | 0.000565 | 0 | 3.7859 | 0.00073374 | -0.035694 | 3.57 | 0.000565 | 0 | 3.7859 | 0.00073374 | -0.035694 |  | CFL | None | 3570 | 0.565 | 3570 | 0.565 | 1.06 | 1.3 | -0.0099984 | 3570 | 0.565 | 3570 | 0.565 | 1.06 | 1.3 | -0.01
CFLNoneSCEOfLExCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | OfL | Ex | CZ05 | 3 | 0.000625 | 0 | 3.3201 | 0.000809 | -0.020701 | 3 | 0.000625 | 0 | 3.3201 | 0.000809 | -0.020701 |  | CFL | None | 3000 | 0.625 | 3000 | 0.625 | 1.11 | 1.29 | -0.0069003 | 3000 | 0.625 | 3000 | 0.625 | 1.11 | 1.29 | -0.0069
CFLNoneSCEOfLExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | OfL | Ex | CZ06 | 3 | 0.000625 | 0 | 3.46 | 0.000831 | -0.0134 | 3 | 0.000625 | 0 | 3.46 | 0.000831 | -0.0134 |  | CFL | None | 3000 | 0.625 | 3000 | 0.625 | 1.15 | 1.33 | -0.0044667 | 3000 | 0.625 | 3000 | 0.625 | 1.15 | 1.33 | -0.00447
CFLNoneSCEOfLExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | OfL | Ex | CZ08 | 3 | 0.000625 | 0 | 3.49 | 0.000849 | -0.0128 | 3 | 0.000625 | 0 | 3.49 | 0.000849 | -0.0128 |  | CFL | None | 3000 | 0.625 | 3000 | 0.625 | 1.16 | 1.36 | -0.0042667 | 3000 | 0.625 | 3000 | 0.625 | 1.16 | 1.36 | -0.00427
CFLNoneSCEOfLExCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | OfL | Ex | CZ09 | 3 | 0.000625 | 0 | 3.47 | 0.000849 | -0.0152 | 3 | 0.000625 | 0 | 3.47 | 0.000849 | -0.0152 |  | CFL | None | 3000 | 0.625 | 3000 | 0.625 | 1.16 | 1.36 | -0.0050667 | 3000 | 0.625 | 3000 | 0.625 | 1.16 | 1.36 | -0.00507
CFLNoneSCEOfLExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | OfL | Ex | CZ10 | 3 | 0.000625 | 0 | 3.47 | 0.000844 | -0.0123 | 3 | 0.000625 | 0 | 3.47 | 0.000844 | -0.0123 |  | CFL | None | 3000 | 0.625 | 3000 | 0.625 | 1.16 | 1.35 | -0.0041 | 3000 | 0.625 | 3000 | 0.625 | 1.16 | 1.35 | -0.0041
CFLNoneSCEOfLExCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | OfL | Ex | CZ13 | 3 | 0.000625 | 0 | 3.45 | 0.000826 | -0.018009 | 3 | 0.000625 | 0 | 3.45 | 0.000826 | -0.018009 |  | CFL | None | 3000 | 0.625 | 3000 | 0.625 | 1.15 | 1.32 | -0.006003 | 3000 | 0.625 | 3000 | 0.625 | 1.15 | 1.32 | -0.006
CFLNoneSCEOfLExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | OfL | Ex | CZ14 | 3 | 0.000625 | 0 | 3.41 | 0.000841 | -0.0174 | 3 | 0.000625 | 0 | 3.41 | 0.000841 | -0.0174 |  | CFL | None | 3000 | 0.625 | 3000 | 0.625 | 1.14 | 1.35 | -0.0058 | 3000 | 0.625 | 3000 | 0.625 | 1.14 | 1.35 | -0.0058
CFLNoneSCEOfLExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | OfL | Ex | CZ15 | 3 | 0.000625 | 0 | 3.67 | 0.000839 | -0.00767 | 3 | 0.000625 | 0 | 3.67 | 0.000839 | -0.00767 |  | CFL | None | 3000 | 0.625 | 3000 | 0.625 | 1.22 | 1.34 | -0.0025567 | 3000 | 0.625 | 3000 | 0.625 | 1.22 | 1.34 | -0.00256
CFLNoneSCEOfLExCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | OfL | Ex | CZ16 | 3 | 0.000625 | 0 | 3.1705 | 0.000793 | -0.0318 | 3 | 0.000625 | 0 | 3.1705 | 0.000793 | -0.0318 |  | CFL | None | 3000 | 0.625 | 3000 | 0.625 | 1.06 | 1.27 | -0.0106 | 3000 | 0.625 | 3000 | 0.625 | 1.06 | 1.27 | -0.0106
CFLNoneSCEOfLExIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | OfL | Ex | IOU | 3 | 0.000625 | 0 | 3.4742 | 0.00084217 | -0.013656 | 3 | 0.000625 | 0 | 3.4742 | 0.00084217 | -0.013656 |  | CFL | None | 3000 | 0.625 | 3000 | 0.625 | 1.16 | 1.35 | -0.0045519 | 3000 | 0.625 | 3000 | 0.625 | 1.16 | 1.35 | -0.00455
CFLNoneSCEOfLNewCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | OfL | New | CZ05 | 3 | 0.000625 | 0 | 3.31 | 0.000775 | -0.00974 | 3 | 0.000625 | 0 | 3.31 | 0.000775 | -0.00974 |  | CFL | None | 3000 | 0.625 | 3000 | 0.625 | 1.1 | 1.24 | -0.0032467 | 3000 | 0.625 | 3000 | 0.625 | 1.1 | 1.24 | -0.00325
CFLNoneSCEOfLNewCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | OfL | New | CZ06 | 3 | 0.000625 | 0 | 3.45 | 0.000788 | -0.0065 | 3 | 0.000625 | 0 | 3.45 | 0.000788 | -0.0065 |  | CFL | None | 3000 | 0.625 | 3000 | 0.625 | 1.15 | 1.26 | -0.0021667 | 3000 | 0.625 | 3000 | 0.625 | 1.15 | 1.26 | -0.00217
CFLNoneSCEOfLNewCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | OfL | New | CZ08 | 3 | 0.000625 | 0 | 3.46 | 0.000798 | -0.00566 | 3 | 0.000625 | 0 | 3.46 | 0.000798 | -0.00566 |  | CFL | None | 3000 | 0.625 | 3000 | 0.625 | 1.15 | 1.28 | -0.0018867 | 3000 | 0.625 | 3000 | 0.625 | 1.15 | 1.28 | -0.00189
CFLNoneSCEOfLNewCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | OfL | New | CZ09 | 3 | 0.000625 | 0 | 3.45 | 0.000822 | -0.00791 | 3 | 0.000625 | 0 | 3.45 | 0.000822 | -0.00791 |  | CFL | None | 3000 | 0.625 | 3000 | 0.625 | 1.15 | 1.32 | -0.0026367 | 3000 | 0.625 | 3000 | 0.625 | 1.15 | 1.32 | -0.00264
CFLNoneSCEOfLNewCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | OfL | New | CZ10 | 3 | 0.000625 | 0 | 3.47 | 0.000825 | -0.00686 | 3 | 0.000625 | 0 | 3.47 | 0.000825 | -0.00686 |  | CFL | None | 3000 | 0.625 | 3000 | 0.625 | 1.16 | 1.32 | -0.0022867 | 3000 | 0.625 | 3000 | 0.625 | 1.16 | 1.32 | -0.00229
CFLNoneSCEOfLNewCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | OfL | New | CZ13 | 3 | 0.000625 | 0 | 3.4 | 0.000803 | -0.0102 | 3 | 0.000625 | 0 | 3.4 | 0.000803 | -0.0102 |  | CFL | None | 3000 | 0.625 | 3000 | 0.625 | 1.13 | 1.28 | -0.0034 | 3000 | 0.625 | 3000 | 0.625 | 1.13 | 1.28 | -0.0034
CFLNoneSCEOfLNewCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | OfL | New | CZ14 | 3 | 0.000625 | 0 | 3.42 | 0.000834 | -0.00902 | 3 | 0.000625 | 0 | 3.42 | 0.000834 | -0.00902 |  | CFL | None | 3000 | 0.625 | 3000 | 0.625 | 1.14 | 1.33 | -0.0030067 | 3000 | 0.625 | 3000 | 0.625 | 1.14 | 1.33 | -0.00301
CFLNoneSCEOfLNewCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | OfL | New | CZ15 | 3 | 0.000625 | 0 | 3.61 | 0.000817 | -0.00333 | 3 | 0.000625 | 0 | 3.61 | 0.000817 | -0.00333 |  | CFL | None | 3000 | 0.625 | 3000 | 0.625 | 1.2 | 1.31 | -0.00111 | 3000 | 0.625 | 3000 | 0.625 | 1.2 | 1.31 | -0.00111
CFLNoneSCEOfLNewCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | OfL | New | CZ16 | 3 | 0.000625 | 0 | 3.22 | 0.000784 | -0.025 | 3 | 0.000625 | 0 | 3.22 | 0.000784 | -0.025 |  | CFL | None | 3000 | 0.625 | 3000 | 0.625 | 1.07 | 1.25 | -0.0083333 | 3000 | 0.625 | 3000 | 0.625 | 1.07 | 1.25 | -0.00833
CFLNoneSCEOfLNewIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | OfL | New | IOU | 3 | 0.000625 | 0 | 3.4592 | 0.00080883 | -0.0069623 | 3 | 0.000625 | 0 | 3.4592 | 0.00080883 | -0.0069623 |  | CFL | None | 3000 | 0.625 | 3000 | 0.625 | 1.15 | 1.29 | -0.0023208 | 3000 | 0.625 | 3000 | 0.625 | 1.15 | 1.29 | -0.00232
CFLNoneSCEOfSExCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | OfS | Ex | CZ05 | 2.98 | 0.000678 | 0 | 3.24 | 0.000852 | -0.00932 | 2.98 | 0.000678 | 0 | 3.24 | 0.000852 | -0.00932 |  | CFL | None | 2980 | 0.678 | 2980 | 0.678 | 1.09 | 1.26 | -0.0031275 | 2980 | 0.678 | 2980 | 0.678 | 1.09 | 1.26 | -0.00313
CFLNoneSCEOfSExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | OfS | Ex | CZ06 | 2.98 | 0.000678 | 0 | 3.39 | 0.000864 | -0.0045 | 2.98 | 0.000678 | 0 | 3.39 | 0.000864 | -0.0045 |  | CFL | None | 2980 | 0.678 | 2980 | 0.678 | 1.14 | 1.27 | -0.0015101 | 2980 | 0.678 | 2980 | 0.678 | 1.14 | 1.27 | -0.00151
CFLNoneSCEOfSExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | OfS | Ex | CZ08 | 2.98 | 0.000678 | 0 | 3.41 | 0.000869 | -0.00408 | 2.98 | 0.000678 | 0 | 3.41 | 0.000869 | -0.00408 |  | CFL | None | 2980 | 0.678 | 2980 | 0.678 | 1.14 | 1.28 | -0.0013691 | 2980 | 0.678 | 2980 | 0.678 | 1.14 | 1.28 | -0.00137
CFLNoneSCEOfSExCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | OfS | Ex | CZ09 | 2.98 | 0.000678 | 0 | 3.4 | 0.000877 | -0.00506 | 2.98 | 0.000678 | 0 | 3.4 | 0.000877 | -0.00506 |  | CFL | None | 2980 | 0.678 | 2980 | 0.678 | 1.14 | 1.29 | -0.001698 | 2980 | 0.678 | 2980 | 0.678 | 1.14 | 1.29 | -0.0017
CFLNoneSCEOfSExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | OfS | Ex | CZ10 | 2.98 | 0.000678 | 0 | 3.35 | 0.00087 | -0.00473 | 2.98 | 0.000678 | 0 | 3.35 | 0.00087 | -0.00473 |  | CFL | None | 2980 | 0.678 | 2980 | 0.678 | 1.12 | 1.28 | -0.0015872 | 2980 | 0.678 | 2980 | 0.678 | 1.12 | 1.28 | -0.00159
CFLNoneSCEOfSExCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | OfS | Ex | CZ13 | 2.98 | 0.000678 | 0 | 3.28 | 0.000864 | -0.0112 | 2.98 | 0.000678 | 0 | 3.28 | 0.000864 | -0.0112 |  | CFL | None | 2980 | 0.678 | 2980 | 0.678 | 1.1 | 1.27 | -0.0037584 | 2980 | 0.678 | 2980 | 0.678 | 1.1 | 1.27 | -0.00376
CFLNoneSCEOfSExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | OfS | Ex | CZ14 | 2.98 | 0.000678 | 0 | 3.29 | 0.000881 | -0.00887 | 2.98 | 0.000678 | 0 | 3.29 | 0.000881 | -0.00887 |  | CFL | None | 2980 | 0.678 | 2980 | 0.678 | 1.1 | 1.3 | -0.0029765 | 2980 | 0.678 | 2980 | 0.678 | 1.1 | 1.3 | -0.00298
CFLNoneSCEOfSExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | OfS | Ex | CZ15 | 2.98 | 0.000678 | 0 | 3.58 | 0.000862 | -0.00141 | 2.98 | 0.000678 | 0 | 3.58 | 0.000862 | -0.00141 |  | CFL | None | 2980 | 0.678 | 2980 | 0.678 | 1.2 | 1.27 | -0.00047315 | 2980 | 0.678 | 2980 | 0.678 | 1.2 | 1.27 | -0.000473
CFLNoneSCEOfSExCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | OfS | Ex | CZ16 | 2.98 | 0.000678 | 0 | 2.99 | 0.000848 | -0.0211 | 2.98 | 0.000678 | 0 | 2.99 | 0.000848 | -0.0211 |  | CFL | None | 2980 | 0.678 | 2980 | 0.678 | 1 | 1.25 | -0.0070805 | 2980 | 0.678 | 2980 | 0.678 | 1 | 1.25 | -0.00708
CFLNoneSCEOfSExIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | OfS | Ex | IOU | 2.98 | 0.000678 | 0 | 3.384 | 0.00086855 | -0.0050799 | 2.98 | 0.000678 | 0 | 3.384 | 0.00086855 | -0.0050799 |  | CFL | None | 2980 | 0.678 | 2980 | 0.678 | 1.14 | 1.28 | -0.0017047 | 2980 | 0.678 | 2980 | 0.678 | 1.14 | 1.28 | -0.0017
CFLNoneSCEOfSNewCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | OfS | New | CZ05 | 2.98 | 0.000678 | 0 | 3.11 | 0.000839 | -0.00842 | 2.98 | 0.000678 | 0 | 3.11 | 0.000839 | -0.00842 |  | CFL | None | 2980 | 0.678 | 2980 | 0.678 | 1.04 | 1.24 | -0.0028255 | 2980 | 0.678 | 2980 | 0.678 | 1.04 | 1.24 | -0.00283
CFLNoneSCEOfSNewCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | OfS | New | CZ06 | 2.98 | 0.000678 | 0 | 3.28 | 0.00085 | -0.00339 | 2.98 | 0.000678 | 0 | 3.28 | 0.00085 | -0.00339 |  | CFL | None | 2980 | 0.678 | 2980 | 0.678 | 1.1 | 1.25 | -0.0011376 | 2980 | 0.678 | 2980 | 0.678 | 1.1 | 1.25 | -0.00114
CFLNoneSCEOfSNewCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | OfS | New | CZ08 | 2.98 | 0.000678 | 0 | 3.3 | 0.000861 | -0.00301 | 2.98 | 0.000678 | 0 | 3.3 | 0.000861 | -0.00301 |  | CFL | None | 2980 | 0.678 | 2980 | 0.678 | 1.11 | 1.27 | -0.0010101 | 2980 | 0.678 | 2980 | 0.678 | 1.11 | 1.27 | -0.00101
CFLNoneSCEOfSNewCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | OfS | New | CZ09 | 2.98 | 0.000678 | 0 | 3.3 | 0.000883 | -0.00339 | 2.98 | 0.000678 | 0 | 3.3 | 0.000883 | -0.00339 |  | CFL | None | 2980 | 0.678 | 2980 | 0.678 | 1.11 | 1.3 | -0.0011376 | 2980 | 0.678 | 2980 | 0.678 | 1.11 | 1.3 | -0.00114
CFLNoneSCEOfSNewCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | OfS | New | CZ10 | 2.98 | 0.000678 | 0 | 3.34 | 0.000894 | -0.00239 | 2.98 | 0.000678 | 0 | 3.34 | 0.000894 | -0.00239 |  | CFL | None | 2980 | 0.678 | 2980 | 0.678 | 1.12 | 1.32 | -0.00080201 | 2980 | 0.678 | 2980 | 0.678 | 1.12 | 1.32 | -0.000802
CFLNoneSCEOfSNewCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | OfS | New | CZ13 | 2.98 | 0.000678 | 0 | 3.24 | 0.000878 | -0.00893 | 2.98 | 0.000678 | 0 | 3.24 | 0.000878 | -0.00893 |  | CFL | None | 2980 | 0.678 | 2980 | 0.678 | 1.09 | 1.29 | -0.0029966 | 2980 | 0.678 | 2980 | 0.678 | 1.09 | 1.29 | -0.003
CFLNoneSCEOfSNewCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | OfS | New | CZ14 | 2.98 | 0.000678 | 0 | 3.26 | 0.000893 | -0.00744 | 2.98 | 0.000678 | 0 | 3.26 | 0.000893 | -0.00744 |  | CFL | None | 2980 | 0.678 | 2980 | 0.678 | 1.09 | 1.32 | -0.0024966 | 2980 | 0.678 | 2980 | 0.678 | 1.09 | 1.32 | -0.0025
CFLNoneSCEOfSNewCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | OfS | New | CZ15 | 2.98 | 0.000678 | 0 | 3.49 | 0.000903 | -0.000223 | 2.98 | 0.000678 | 0 | 3.49 | 0.000903 | -0.000223 |  | CFL | None | 2980 | 0.678 | 2980 | 0.678 | 1.17 | 1.33 | -7.4832e-05 | 2980 | 0.678 | 2980 | 0.678 | 1.17 | 1.33 | -7.48e-05
CFLNoneSCEOfSNewCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | OfS | New | CZ16 | 2.98 | 0.000678 | 0 | 2.98 | 0.000851 | -0.0199 | 2.98 | 0.000678 | 0 | 2.98 | 0.000851 | -0.0199 |  | CFL | None | 2980 | 0.678 | 2980 | 0.678 | 1 | 1.26 | -0.0066779 | 2980 | 0.678 | 2980 | 0.678 | 1 | 1.26 | -0.00668
CFLNoneSCEOfSNewIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | OfS | New | IOU | 2.98 | 0.000678 | 0 | 3.3122 | 0.00087597 | -0.0034739 | 2.98 | 0.000678 | 0 | 3.3122 | 0.00087597 | -0.0034739 |  | CFL | None | 2980 | 0.678 | 2980 | 0.678 | 1.11 | 1.29 | -0.0011657 | 2980 | 0.678 | 2980 | 0.678 | 1.11 | 1.29 | -0.00117
CFLNoneSCERFFExCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | RFF | Ex | CZ05 | 4.81 | 0.000808 | 0 | 5 | 0.000957 | -0.0449 | 4.81 | 0.000808 | 0 | 5 | 0.000957 | -0.0449 |  | CFL | None | 4810 | 0.808 | 4810 | 0.808 | 1.04 | 1.18 | -0.0093347 | 4810 | 0.808 | 4810 | 0.808 | 1.04 | 1.18 | -0.00933
CFLNoneSCERFFExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | RFF | Ex | CZ06 | 4.81 | 0.000808 | 0 | 5.24 | 0.000978 | -0.0251 | 4.81 | 0.000808 | 0 | 5.24 | 0.000978 | -0.0251 |  | CFL | None | 4810 | 0.808 | 4810 | 0.808 | 1.09 | 1.21 | -0.0052183 | 4810 | 0.808 | 4810 | 0.808 | 1.09 | 1.21 | -0.00522
CFLNoneSCERFFExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | RFF | Ex | CZ08 | 4.81 | 0.000808 | 0 | 5.29 | 0.00097 | -0.0221 | 4.81 | 0.000808 | 0 | 5.29 | 0.00097 | -0.0221 |  | CFL | None | 4810 | 0.808 | 4810 | 0.808 | 1.1 | 1.2 | -0.0045946 | 4810 | 0.808 | 4810 | 0.808 | 1.1 | 1.2 | -0.00459
CFLNoneSCERFFExCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | RFF | Ex | CZ09 | 4.81 | 0.000808 | 0 | 5.3 | 0.00099 | -0.0231 | 4.81 | 0.000808 | 0 | 5.3 | 0.00099 | -0.0231 |  | CFL | None | 4810 | 0.808 | 4810 | 0.808 | 1.1 | 1.23 | -0.0048025 | 4810 | 0.808 | 4810 | 0.808 | 1.1 | 1.23 | -0.0048
CFLNoneSCERFFExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | RFF | Ex | CZ10 | 4.81 | 0.000808 | 0 | 5.2 | 0.000974 | -0.0256 | 4.81 | 0.000808 | 0 | 5.2 | 0.000974 | -0.0256 |  | CFL | None | 4810 | 0.808 | 4810 | 0.808 | 1.08 | 1.21 | -0.0053222 | 4810 | 0.808 | 4810 | 0.808 | 1.08 | 1.21 | -0.00532
CFLNoneSCERFFExCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | RFF | Ex | CZ13 | 4.81 | 0.000808 | 0 | 5.2 | 0.00098 | -0.0338 | 4.81 | 0.000808 | 0 | 5.2 | 0.00098 | -0.0338 |  | CFL | None | 4810 | 0.808 | 4810 | 0.808 | 1.08 | 1.21 | -0.007027 | 4810 | 0.808 | 4810 | 0.808 | 1.08 | 1.21 | -0.00703
CFLNoneSCERFFExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | RFF | Ex | CZ14 | 4.81 | 0.000808 | 0 | 5.16 | 0.000991 | -0.0357 | 4.81 | 0.000808 | 0 | 5.16 | 0.000991 | -0.0357 |  | CFL | None | 4810 | 0.808 | 4810 | 0.808 | 1.07 | 1.23 | -0.007422 | 4810 | 0.808 | 4810 | 0.808 | 1.07 | 1.23 | -0.00742
CFLNoneSCERFFExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | RFF | Ex | CZ15 | 4.81 | 0.000808 | 0 | 5.52 | 0.000987 | -0.012 | 4.81 | 0.000808 | 0 | 5.52 | 0.000987 | -0.012 |  | CFL | None | 4810 | 0.808 | 4810 | 0.808 | 1.15 | 1.22 | -0.0024948 | 4810 | 0.808 | 4810 | 0.808 | 1.15 | 1.22 | -0.00249
CFLNoneSCERFFExCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | RFF | Ex | CZ16 | 4.81 | 0.000808 | 0 | 4.81 | 0.000959 | -0.0649 | 4.81 | 0.000808 | 0 | 4.81 | 0.000959 | -0.0649 |  | CFL | None | 4810 | 0.808 | 4810 | 0.808 | 1 | 1.19 | -0.013493 | 4810 | 0.808 | 4810 | 0.808 | 1 | 1.19 | -0.0135
CFLNoneSCERFFExIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | RFF | Ex | IOU | 4.81 | 0.000808 | 0 | 5.2521 | 0.00097739 | -0.025009 | 4.81 | 0.000808 | 0 | 5.2521 | 0.00097739 | -0.025009 |  | CFL | None | 4810 | 0.808 | 4810 | 0.808 | 1.09 | 1.21 | -0.0051993 | 4810 | 0.808 | 4810 | 0.808 | 1.09 | 1.21 | -0.0052
CFLNoneSCERFFNewCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | RFF | New | CZ05 | 4.81 | 0.000808 | 0 | 4.93 | 0.000971 | -0.0436 | 4.81 | 0.000808 | 0 | 4.93 | 0.000971 | -0.0436 |  | CFL | None | 4810 | 0.808 | 4810 | 0.808 | 1.02 | 1.2 | -0.0090644 | 4810 | 0.808 | 4810 | 0.808 | 1.02 | 1.2 | -0.00906
CFLNoneSCERFFNewCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | RFF | New | CZ06 | 4.81 | 0.000808 | 0 | 5.16 | 0.000999 | -0.0259 | 4.81 | 0.000808 | 0 | 5.16 | 0.000999 | -0.0259 |  | CFL | None | 4810 | 0.808 | 4810 | 0.808 | 1.07 | 1.24 | -0.0053846 | 4810 | 0.808 | 4810 | 0.808 | 1.07 | 1.24 | -0.00538
CFLNoneSCERFFNewCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | RFF | New | CZ08 | 4.81 | 0.000808 | 0 | 5.17 | 0.00097 | -0.0255 | 4.81 | 0.000808 | 0 | 5.17 | 0.00097 | -0.0255 |  | CFL | None | 4810 | 0.808 | 4810 | 0.808 | 1.07 | 1.2 | -0.0053015 | 4810 | 0.808 | 4810 | 0.808 | 1.07 | 1.2 | -0.0053
CFLNoneSCERFFNewCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | RFF | New | CZ09 | 4.81 | 0.000808 | 0 | 5.27 | 0.00104 | -0.0285 | 4.81 | 0.000808 | 0 | 5.27 | 0.00104 | -0.0285 |  | CFL | None | 4810 | 0.808 | 4810 | 0.808 | 1.1 | 1.29 | -0.0059252 | 4810 | 0.808 | 4810 | 0.808 | 1.1 | 1.29 | -0.00593
CFLNoneSCERFFNewCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | RFF | New | CZ10 | 4.81 | 0.000808 | 0 | 5.29 | 0.00104 | -0.0296 | 4.81 | 0.000808 | 0 | 5.29 | 0.00104 | -0.0296 |  | CFL | None | 4810 | 0.808 | 4810 | 0.808 | 1.1 | 1.29 | -0.0061538 | 4810 | 0.808 | 4810 | 0.808 | 1.1 | 1.29 | -0.00615
CFLNoneSCERFFNewCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | RFF | New | CZ13 | 4.81 | 0.000808 | 0 | 5.28 | 0.00104 | -0.0388 | 4.81 | 0.000808 | 0 | 5.28 | 0.00104 | -0.0388 |  | CFL | None | 4810 | 0.808 | 4810 | 0.808 | 1.1 | 1.29 | -0.0080665 | 4810 | 0.808 | 4810 | 0.808 | 1.1 | 1.29 | -0.00807
CFLNoneSCERFFNewCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | RFF | New | CZ14 | 4.81 | 0.000808 | 0 | 5.27 | 0.00105 | -0.0413 | 4.81 | 0.000808 | 0 | 5.27 | 0.00105 | -0.0413 |  | CFL | None | 4810 | 0.808 | 4810 | 0.808 | 1.1 | 1.3 | -0.0085863 | 4810 | 0.808 | 4810 | 0.808 | 1.1 | 1.3 | -0.00859
CFLNoneSCERFFNewCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | RFF | New | CZ15 | 4.81 | 0.000808 | 0 | 5.65 | 0.00106 | -0.0147 | 4.81 | 0.000808 | 0 | 5.65 | 0.00106 | -0.0147 |  | CFL | None | 4810 | 0.808 | 4810 | 0.808 | 1.17 | 1.31 | -0.0030561 | 4810 | 0.808 | 4810 | 0.808 | 1.17 | 1.31 | -0.00306
CFLNoneSCERFFNewCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | RFF | New | CZ16 | 4.81 | 0.000808 | 0 | 4.87 | 0.000998 | -0.0697 | 4.81 | 0.000808 | 0 | 4.87 | 0.000998 | -0.0697 |  | CFL | None | 4810 | 0.808 | 4810 | 0.808 | 1.01 | 1.24 | -0.014491 | 4810 | 0.808 | 4810 | 0.808 | 1.01 | 1.24 | -0.0145
CFLNoneSCERFFNewIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | RFF | New | IOU | 4.81 | 0.000808 | 0 | 5.24 | 0.0010151 | -0.028553 | 4.81 | 0.000808 | 0 | 5.24 | 0.0010151 | -0.028553 |  | CFL | None | 4810 | 0.808 | 4810 | 0.808 | 1.09 | 1.26 | -0.0059362 | 4810 | 0.808 | 4810 | 0.808 | 1.09 | 1.26 | -0.00594
CFLNoneSCERSDExCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | RSD | Ex | CZ05 | 4.83 | 0.0008 | 0 | 5.07 | 0.000973 | -0.0434 | 4.83 | 0.0008 | 0 | 5.07 | 0.000973 | -0.0434 |  | CFL | None | 4830 | 0.8 | 4830 | 0.8 | 1.05 | 1.22 | -0.0089855 | 4830 | 0.8 | 4830 | 0.8 | 1.05 | 1.22 | -0.00899
CFLNoneSCERSDExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | RSD | Ex | CZ06 | 4.83 | 0.0008 | 0 | 5.37 | 0.000985 | -0.0223 | 4.83 | 0.0008 | 0 | 5.37 | 0.000985 | -0.0223 |  | CFL | None | 4830 | 0.8 | 4830 | 0.8 | 1.11 | 1.23 | -0.004617 | 4830 | 0.8 | 4830 | 0.8 | 1.11 | 1.23 | -0.00462
CFLNoneSCERSDExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | RSD | Ex | CZ08 | 4.83 | 0.0008 | 0 | 5.41 | 0.00096 | -0.019 | 4.83 | 0.0008 | 0 | 5.41 | 0.00096 | -0.019 |  | CFL | None | 4830 | 0.8 | 4830 | 0.8 | 1.12 | 1.2 | -0.0039337 | 4830 | 0.8 | 4830 | 0.8 | 1.12 | 1.2 | -0.00393
CFLNoneSCERSDExCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | RSD | Ex | CZ09 | 4.83 | 0.0008 | 0 | 5.41 | 0.000976 | -0.0216 | 4.83 | 0.0008 | 0 | 5.41 | 0.000976 | -0.0216 |  | CFL | None | 4830 | 0.8 | 4830 | 0.8 | 1.12 | 1.22 | -0.004472 | 4830 | 0.8 | 4830 | 0.8 | 1.12 | 1.22 | -0.00447
CFLNoneSCERSDExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | RSD | Ex | CZ10 | 4.83 | 0.0008 | 0 | 5.31 | 0.000946 | -0.0228 | 4.83 | 0.0008 | 0 | 5.31 | 0.000946 | -0.0228 |  | CFL | None | 4830 | 0.8 | 4830 | 0.8 | 1.1 | 1.18 | -0.0047205 | 4830 | 0.8 | 4830 | 0.8 | 1.1 | 1.18 | -0.00472
CFLNoneSCERSDExCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | RSD | Ex | CZ13 | 4.83 | 0.0008 | 0 | 5.28 | 0.000985 | -0.0335 | 4.83 | 0.0008 | 0 | 5.28 | 0.000985 | -0.0335 |  | CFL | None | 4830 | 0.8 | 4830 | 0.8 | 1.09 | 1.23 | -0.0069358 | 4830 | 0.8 | 4830 | 0.8 | 1.09 | 1.23 | -0.00694
CFLNoneSCERSDExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | RSD | Ex | CZ14 | 4.83 | 0.0008 | 0 | 5.23 | 0.000948 | -0.0347 | 4.83 | 0.0008 | 0 | 5.23 | 0.000948 | -0.0347 |  | CFL | None | 4830 | 0.8 | 4830 | 0.8 | 1.08 | 1.19 | -0.0071843 | 4830 | 0.8 | 4830 | 0.8 | 1.08 | 1.19 | -0.00718
CFLNoneSCERSDExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | RSD | Ex | CZ15 | 4.83 | 0.0008 | 0 | 5.68 | 0.001 | -0.00859 | 4.83 | 0.0008 | 0 | 5.68 | 0.001 | -0.00859 |  | CFL | None | 4830 | 0.8 | 4830 | 0.8 | 1.18 | 1.25 | -0.0017785 | 4830 | 0.8 | 4830 | 0.8 | 1.18 | 1.25 | -0.00178
CFLNoneSCERSDExCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | RSD | Ex | CZ16 | 4.83 | 0.0008 | 0 | 4.85 | 0.000948 | -0.0618 | 4.83 | 0.0008 | 0 | 4.85 | 0.000948 | -0.0618 |  | CFL | None | 4830 | 0.8 | 4830 | 0.8 | 1 | 1.19 | -0.012795 | 4830 | 0.8 | 4830 | 0.8 | 1 | 1.19 | -0.0128
CFLNoneSCERSDExIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | RSD | Ex | IOU | 4.83 | 0.0008 | 0 | 5.3677 | 0.00096639 | -0.022424 | 4.83 | 0.0008 | 0 | 5.3677 | 0.00096639 | -0.022424 |  | CFL | None | 4830 | 0.8 | 4830 | 0.8 | 1.11 | 1.21 | -0.0046427 | 4830 | 0.8 | 4830 | 0.8 | 1.11 | 1.21 | -0.00464
CFLNoneSCERSDNewCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | RSD | New | CZ05 | 4.83 | 0.0008 | 0 | 5 | 0.000982 | -0.0472 | 4.83 | 0.0008 | 0 | 5 | 0.000982 | -0.0472 |  | CFL | None | 4830 | 0.8 | 4830 | 0.8 | 1.04 | 1.23 | -0.0097723 | 4830 | 0.8 | 4830 | 0.8 | 1.04 | 1.23 | -0.00977
CFLNoneSCERSDNewCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | RSD | New | CZ06 | 4.83 | 0.0008 | 0 | 5.28 | 0.000998 | -0.0266 | 4.83 | 0.0008 | 0 | 5.28 | 0.000998 | -0.0266 |  | CFL | None | 4830 | 0.8 | 4830 | 0.8 | 1.09 | 1.25 | -0.0055072 | 4830 | 0.8 | 4830 | 0.8 | 1.09 | 1.25 | -0.00551
CFLNoneSCERSDNewCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | RSD | New | CZ08 | 4.83 | 0.0008 | 0 | 5.19 | 0.00087 | -0.0222 | 4.83 | 0.0008 | 0 | 5.19 | 0.00087 | -0.0222 |  | CFL | None | 4830 | 0.8 | 4830 | 0.8 | 1.07 | 1.09 | -0.0045963 | 4830 | 0.8 | 4830 | 0.8 | 1.07 | 1.09 | -0.0046
CFLNoneSCERSDNewCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | RSD | New | CZ09 | 4.83 | 0.0008 | 0 | 5.37 | 0.00105 | -0.0246 | 4.83 | 0.0008 | 0 | 5.37 | 0.00105 | -0.0246 |  | CFL | None | 4830 | 0.8 | 4830 | 0.8 | 1.11 | 1.31 | -0.0050932 | 4830 | 0.8 | 4830 | 0.8 | 1.11 | 1.31 | -0.00509
CFLNoneSCERSDNewCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | RSD | New | CZ10 | 4.83 | 0.0008 | 0 | 5.39 | 0.00105 | -0.0252 | 4.83 | 0.0008 | 0 | 5.39 | 0.00105 | -0.0252 |  | CFL | None | 4830 | 0.8 | 4830 | 0.8 | 1.12 | 1.31 | -0.0052174 | 4830 | 0.8 | 4830 | 0.8 | 1.12 | 1.31 | -0.00522
CFLNoneSCERSDNewCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | RSD | New | CZ13 | 4.83 | 0.0008 | 0 | 5.34 | 0.00105 | -0.0364 | 4.83 | 0.0008 | 0 | 5.34 | 0.00105 | -0.0364 |  | CFL | None | 4830 | 0.8 | 4830 | 0.8 | 1.11 | 1.31 | -0.0075362 | 4830 | 0.8 | 4830 | 0.8 | 1.11 | 1.31 | -0.00754
CFLNoneSCERSDNewCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | RSD | New | CZ14 | 4.83 | 0.0008 | 0 | 5.32 | 0.00105 | -0.0374 | 4.83 | 0.0008 | 0 | 5.32 | 0.00105 | -0.0374 |  | CFL | None | 4830 | 0.8 | 4830 | 0.8 | 1.1 | 1.31 | -0.0077433 | 4830 | 0.8 | 4830 | 0.8 | 1.1 | 1.31 | -0.00774
CFLNoneSCERSDNewCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | RSD | New | CZ15 | 4.83 | 0.0008 | 0 | 5.79 | 0.00108 | -0.0109 | 4.83 | 0.0008 | 0 | 5.79 | 0.00108 | -0.0109 |  | CFL | None | 4830 | 0.8 | 4830 | 0.8 | 1.2 | 1.35 | -0.0022567 | 4830 | 0.8 | 4830 | 0.8 | 1.2 | 1.35 | -0.00226
CFLNoneSCERSDNewCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | RSD | New | CZ16 | 4.83 | 0.0008 | 0 | 4.89 | 0.00099 | -0.0512 | 4.83 | 0.0008 | 0 | 4.89 | 0.00099 | -0.0512 |  | CFL | None | 4830 | 0.8 | 4830 | 0.8 | 1.01 | 1.24 | -0.0106 | 4830 | 0.8 | 4830 | 0.8 | 1.01 | 1.24 | -0.0106
CFLNoneSCERSDNewIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | RSD | New | IOU | 4.83 | 0.0008 | 0 | 5.3221 | 0.0009961 | -0.025391 | 4.83 | 0.0008 | 0 | 5.3221 | 0.0009961 | -0.025391 |  | CFL | None | 4830 | 0.8 | 4830 | 0.8 | 1.1 | 1.25 | -0.005257 | 4830 | 0.8 | 4830 | 0.8 | 1.1 | 1.25 | -0.00526
CFLNoneSCERt3ExCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | Rt3 | Ex | CZ05 | 3.71 | 0.000631 | 0 | 3.99 | 0.000797 | -0.0208 | 3.71 | 0.000631 | 0 | 3.99 | 0.000797 | -0.0208 |  | CFL | None | 3710 | 0.631 | 3710 | 0.631 | 1.08 | 1.26 | -0.0056065 | 3710 | 0.631 | 3710 | 0.631 | 1.08 | 1.26 | -0.00561
CFLNoneSCERt3ExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | Rt3 | Ex | CZ06 | 3.71 | 0.000631 | 0 | 4.28 | 0.000798 | -0.00538 | 3.71 | 0.000631 | 0 | 4.28 | 0.000798 | -0.00538 |  | CFL | None | 3710 | 0.631 | 3710 | 0.631 | 1.15 | 1.26 | -0.0014501 | 3710 | 0.631 | 3710 | 0.631 | 1.15 | 1.26 | -0.00145
CFLNoneSCERt3ExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | Rt3 | Ex | CZ08 | 3.71 | 0.000631 | 0 | 4.29 | 0.000786 | -0.00471 | 3.71 | 0.000631 | 0 | 4.29 | 0.000786 | -0.00471 |  | CFL | None | 3710 | 0.631 | 3710 | 0.631 | 1.16 | 1.25 | -0.0012695 | 3710 | 0.631 | 3710 | 0.631 | 1.16 | 1.25 | -0.00127
CFLNoneSCERt3ExCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | Rt3 | Ex | CZ09 | 3.71 | 0.000631 | 0 | 4.23 | 0.000796 | -0.00723 | 3.71 | 0.000631 | 0 | 4.23 | 0.000796 | -0.00723 |  | CFL | None | 3710 | 0.631 | 3710 | 0.631 | 1.14 | 1.26 | -0.0019488 | 3710 | 0.631 | 3710 | 0.631 | 1.14 | 1.26 | -0.00195
CFLNoneSCERt3ExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | Rt3 | Ex | CZ10 | 3.71 | 0.000631 | 0 | 4.13 | 0.000785 | -0.00846 | 3.71 | 0.000631 | 0 | 4.13 | 0.000785 | -0.00846 |  | CFL | None | 3710 | 0.631 | 3710 | 0.631 | 1.11 | 1.24 | -0.0022803 | 3710 | 0.631 | 3710 | 0.631 | 1.11 | 1.24 | -0.00228
CFLNoneSCERt3ExCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | Rt3 | Ex | CZ13 | 3.71 | 0.000631 | 0 | 4.03 | 0.000803 | -0.0231 | 3.71 | 0.000631 | 0 | 4.03 | 0.000803 | -0.0231 |  | CFL | None | 3710 | 0.631 | 3710 | 0.631 | 1.09 | 1.27 | -0.0062264 | 3710 | 0.631 | 3710 | 0.631 | 1.09 | 1.27 | -0.00623
CFLNoneSCERt3ExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | Rt3 | Ex | CZ14 | 3.71 | 0.000631 | 0 | 3.97 | 0.000795 | -0.0248 | 3.71 | 0.000631 | 0 | 3.97 | 0.000795 | -0.0248 |  | CFL | None | 3710 | 0.631 | 3710 | 0.631 | 1.07 | 1.26 | -0.0066846 | 3710 | 0.631 | 3710 | 0.631 | 1.07 | 1.26 | -0.00668
CFLNoneSCERt3ExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | Rt3 | Ex | CZ15 | 3.71 | 0.000631 | 0 | 4.28 | 0.000808 | -0.00214 | 3.71 | 0.000631 | 0 | 4.28 | 0.000808 | -0.00214 |  | CFL | None | 3710 | 0.631 | 3710 | 0.631 | 1.15 | 1.28 | -0.00057682 | 3710 | 0.631 | 3710 | 0.631 | 1.15 | 1.28 | -0.000577
CFLNoneSCERt3ExCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | Rt3 | Ex | CZ16 | 3.71 | 0.000631 | 0 | 3.63 | 0.000781 | -0.0479 | 3.71 | 0.000631 | 0 | 3.63 | 0.000781 | -0.0479 |  | CFL | None | 3710 | 0.631 | 3710 | 0.631 | 0.978 | 1.24 | -0.012911 | 3710 | 0.631 | 3710 | 0.631 | 0.978 | 1.24 | -0.0129
CFLNoneSCERt3ExIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | Rt3 | Ex | IOU | 3.71 | 0.000631 | 0 | 4.2167 | 0.00079173 | -0.0077409 | 3.71 | 0.000631 | 0 | 4.2167 | 0.00079173 | -0.0077409 |  | CFL | None | 3710 | 0.631 | 3710 | 0.631 | 1.14 | 1.25 | -0.0020865 | 3710 | 0.631 | 3710 | 0.631 | 1.14 | 1.25 | -0.00209
CFLNoneSCERt3NewCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | Rt3 | New | CZ05 | 3.71 | 0.000631 | 0 | 3.84 | 0.00078 | -0.0257 | 3.71 | 0.000631 | 0 | 3.84 | 0.00078 | -0.0257 |  | CFL | None | 3710 | 0.631 | 3710 | 0.631 | 1.04 | 1.24 | -0.0069272 | 3710 | 0.631 | 3710 | 0.631 | 1.04 | 1.24 | -0.00693
CFLNoneSCERt3NewCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | Rt3 | New | CZ06 | 3.71 | 0.000631 | 0 | 4.11 | 0.000772 | -0.00775 | 3.71 | 0.000631 | 0 | 4.11 | 0.000772 | -0.00775 |  | CFL | None | 3710 | 0.631 | 3710 | 0.631 | 1.11 | 1.22 | -0.0020889 | 3710 | 0.631 | 3710 | 0.631 | 1.11 | 1.22 | -0.00209
CFLNoneSCERt3NewCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | Rt3 | New | CZ08 | 3.71 | 0.000631 | 0 | 4.15 | 0.000762 | -0.00634 | 3.71 | 0.000631 | 0 | 4.15 | 0.000762 | -0.00634 |  | CFL | None | 3710 | 0.631 | 3710 | 0.631 | 1.12 | 1.21 | -0.0017089 | 3710 | 0.631 | 3710 | 0.631 | 1.12 | 1.21 | -0.00171
CFLNoneSCERt3NewCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | Rt3 | New | CZ09 | 3.71 | 0.000631 | 0 | 4.1 | 0.00078 | -0.00953 | 3.71 | 0.000631 | 0 | 4.1 | 0.00078 | -0.00953 |  | CFL | None | 3710 | 0.631 | 3710 | 0.631 | 1.11 | 1.24 | -0.0025687 | 3710 | 0.631 | 3710 | 0.631 | 1.11 | 1.24 | -0.00257
CFLNoneSCERt3NewCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | Rt3 | New | CZ10 | 3.71 | 0.000631 | 0 | 4.11 | 0.000787 | -0.011 | 3.71 | 0.000631 | 0 | 4.11 | 0.000787 | -0.011 |  | CFL | None | 3710 | 0.631 | 3710 | 0.631 | 1.11 | 1.25 | -0.002965 | 3710 | 0.631 | 3710 | 0.631 | 1.11 | 1.25 | -0.00297
CFLNoneSCERt3NewCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | Rt3 | New | CZ13 | 3.71 | 0.000631 | 0 | 3.98 | 0.000801 | -0.0252 | 3.71 | 0.000631 | 0 | 3.98 | 0.000801 | -0.0252 |  | CFL | None | 3710 | 0.631 | 3710 | 0.631 | 1.07 | 1.27 | -0.0067925 | 3710 | 0.631 | 3710 | 0.631 | 1.07 | 1.27 | -0.00679
CFLNoneSCERt3NewCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | Rt3 | New | CZ14 | 3.71 | 0.000631 | 0 | 3.97 | 0.000793 | -0.0262 | 3.71 | 0.000631 | 0 | 3.97 | 0.000793 | -0.0262 |  | CFL | None | 3710 | 0.631 | 3710 | 0.631 | 1.07 | 1.26 | -0.007062 | 3710 | 0.631 | 3710 | 0.631 | 1.07 | 1.26 | -0.00706
CFLNoneSCERt3NewCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | Rt3 | New | CZ15 | 3.71 | 0.000631 | 0 | 4.33 | 0.000843 | -0.00168 | 3.71 | 0.000631 | 0 | 4.33 | 0.000843 | -0.00168 |  | CFL | None | 3710 | 0.631 | 3710 | 0.631 | 1.17 | 1.34 | -0.00045283 | 3710 | 0.631 | 3710 | 0.631 | 1.17 | 1.34 | -0.000453
CFLNoneSCERt3NewCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | Rt3 | New | CZ16 | 3.71 | 0.000631 | 0 | 3.58 | 0.000712 | -0.0456 | 3.71 | 0.000631 | 0 | 3.58 | 0.000712 | -0.0456 |  | CFL | None | 3710 | 0.631 | 3710 | 0.631 | 0.965 | 1.13 | -0.012291 | 3710 | 0.631 | 3710 | 0.631 | 0.965 | 1.13 | -0.0123
CFLNoneSCERt3NewIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | Rt3 | New | IOU | 3.71 | 0.000631 | 0 | 4.109 | 0.00078041 | -0.01048 | 3.71 | 0.000631 | 0 | 4.109 | 0.00078041 | -0.01048 |  | CFL | None | 3710 | 0.631 | 3710 | 0.631 | 1.11 | 1.24 | -0.0028249 | 3710 | 0.631 | 3710 | 0.631 | 1.11 | 1.24 | -0.00282
CFLNoneSCERtLExCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | RtL | Ex | CZ05 | 4.35 | 0.000689 | 0 | 4.66 | 0.000858 | -0.0261 | 4.35 | 0.000689 | 0 | 4.66 | 0.000858 | -0.0261 |  | CFL | None | 4350 | 0.689 | 4350 | 0.689 | 1.07 | 1.25 | -0.006 | 4350 | 0.689 | 4350 | 0.689 | 1.07 | 1.25 | -0.006
CFLNoneSCERtLExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | RtL | Ex | CZ06 | 4.35 | 0.000689 | 0 | 4.95 | 0.000872 | -0.0105 | 4.35 | 0.000689 | 0 | 4.95 | 0.000872 | -0.0105 |  | CFL | None | 4350 | 0.689 | 4350 | 0.689 | 1.14 | 1.27 | -0.0024138 | 4350 | 0.689 | 4350 | 0.689 | 1.14 | 1.27 | -0.00241
CFLNoneSCERtLExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | RtL | Ex | CZ08 | 4.35 | 0.000689 | 0 | 4.96 | 0.000873 | -0.00905 | 4.35 | 0.000689 | 0 | 4.96 | 0.000873 | -0.00905 |  | CFL | None | 4350 | 0.689 | 4350 | 0.689 | 1.14 | 1.27 | -0.0020805 | 4350 | 0.689 | 4350 | 0.689 | 1.14 | 1.27 | -0.00208
CFLNoneSCERtLExCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | RtL | Ex | CZ09 | 4.35 | 0.000689 | 0 | 4.91 | 0.000894 | -0.0109 | 4.35 | 0.000689 | 0 | 4.91 | 0.000894 | -0.0109 |  | CFL | None | 4350 | 0.689 | 4350 | 0.689 | 1.13 | 1.3 | -0.0025057 | 4350 | 0.689 | 4350 | 0.689 | 1.13 | 1.3 | -0.00251
CFLNoneSCERtLExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | RtL | Ex | CZ10 | 4.35 | 0.000689 | 0 | 4.83 | 0.000883 | -0.012 | 4.35 | 0.000689 | 0 | 4.83 | 0.000883 | -0.012 |  | CFL | None | 4350 | 0.689 | 4350 | 0.689 | 1.11 | 1.28 | -0.0027586 | 4350 | 0.689 | 4350 | 0.689 | 1.11 | 1.28 | -0.00276
CFLNoneSCERtLExCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | RtL | Ex | CZ13 | 4.35 | 0.000689 | 0 | 4.74 | 0.000889 | -0.0237 | 4.35 | 0.000689 | 0 | 4.74 | 0.000889 | -0.0237 |  | CFL | None | 4350 | 0.689 | 4350 | 0.689 | 1.09 | 1.29 | -0.0054483 | 4350 | 0.689 | 4350 | 0.689 | 1.09 | 1.29 | -0.00545
CFLNoneSCERtLExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | RtL | Ex | CZ14 | 4.35 | 0.000689 | 0 | 4.7 | 0.000896 | -0.0246 | 4.35 | 0.000689 | 0 | 4.7 | 0.000896 | -0.0246 |  | CFL | None | 4350 | 0.689 | 4350 | 0.689 | 1.08 | 1.3 | -0.0056552 | 4350 | 0.689 | 4350 | 0.689 | 1.08 | 1.3 | -0.00566
CFLNoneSCERtLExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | RtL | Ex | CZ15 | 4.35 | 0.000689 | 0 | 5.05 | 0.000899 | -0.00424 | 4.35 | 0.000689 | 0 | 5.05 | 0.000899 | -0.00424 |  | CFL | None | 4350 | 0.689 | 4350 | 0.689 | 1.16 | 1.3 | -0.00097471 | 4350 | 0.689 | 4350 | 0.689 | 1.16 | 1.3 | -0.000975
CFLNoneSCERtLExCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | RtL | Ex | CZ16 | 4.35 | 0.000689 | 0 | 4.27 | 0.000847 | -0.0544 | 4.35 | 0.000689 | 0 | 4.27 | 0.000847 | -0.0544 |  | CFL | None | 4350 | 0.689 | 4350 | 0.689 | 0.982 | 1.23 | -0.012506 | 4350 | 0.689 | 4350 | 0.689 | 0.982 | 1.23 | -0.0125
CFLNoneSCERtLExIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | RtL | Ex | IOU | 4.35 | 0.000689 | 0 | 4.901 | 0.00087993 | -0.011666 | 4.35 | 0.000689 | 0 | 4.901 | 0.00087993 | -0.011666 |  | CFL | None | 4350 | 0.689 | 4350 | 0.689 | 1.13 | 1.28 | -0.0026818 | 4350 | 0.689 | 4350 | 0.689 | 1.13 | 1.28 | -0.00268
CFLNoneSCERtLNewCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | RtL | New | CZ05 | 4.35 | 0.000689 | 0 | 4.52 | 0.000863 | -0.0311 | 4.35 | 0.000689 | 0 | 4.52 | 0.000863 | -0.0311 |  | CFL | None | 4350 | 0.689 | 4350 | 0.689 | 1.04 | 1.25 | -0.0071494 | 4350 | 0.689 | 4350 | 0.689 | 1.04 | 1.25 | -0.00715
CFLNoneSCERtLNewCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | RtL | New | CZ06 | 4.35 | 0.000689 | 0 | 4.77 | 0.000878 | -0.0144 | 4.35 | 0.000689 | 0 | 4.77 | 0.000878 | -0.0144 |  | CFL | None | 4350 | 0.689 | 4350 | 0.689 | 1.1 | 1.27 | -0.0033103 | 4350 | 0.689 | 4350 | 0.689 | 1.1 | 1.27 | -0.00331
CFLNoneSCERtLNewCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | RtL | New | CZ08 | 4.35 | 0.000689 | 0 | 4.83 | 0.00089 | -0.0122 | 4.35 | 0.000689 | 0 | 4.83 | 0.00089 | -0.0122 |  | CFL | None | 4350 | 0.689 | 4350 | 0.689 | 1.11 | 1.29 | -0.0028046 | 4350 | 0.689 | 4350 | 0.689 | 1.11 | 1.29 | -0.0028
CFLNoneSCERtLNewCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | RtL | New | CZ09 | 4.35 | 0.000689 | 0 | 4.84 | 0.000933 | -0.0121 | 4.35 | 0.000689 | 0 | 4.84 | 0.000933 | -0.0121 |  | CFL | None | 4350 | 0.689 | 4350 | 0.689 | 1.11 | 1.35 | -0.0027816 | 4350 | 0.689 | 4350 | 0.689 | 1.11 | 1.35 | -0.00278
CFLNoneSCERtLNewCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | RtL | New | CZ10 | 4.35 | 0.000689 | 0 | 4.86 | 0.000936 | -0.0141 | 4.35 | 0.000689 | 0 | 4.86 | 0.000936 | -0.0141 |  | CFL | None | 4350 | 0.689 | 4350 | 0.689 | 1.12 | 1.36 | -0.0032414 | 4350 | 0.689 | 4350 | 0.689 | 1.12 | 1.36 | -0.00324
CFLNoneSCERtLNewCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | RtL | New | CZ13 | 4.35 | 0.000689 | 0 | 4.76 | 0.000927 | -0.0267 | 4.35 | 0.000689 | 0 | 4.76 | 0.000927 | -0.0267 |  | CFL | None | 4350 | 0.689 | 4350 | 0.689 | 1.09 | 1.35 | -0.0061379 | 4350 | 0.689 | 4350 | 0.689 | 1.09 | 1.35 | -0.00614
CFLNoneSCERtLNewCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | RtL | New | CZ14 | 4.35 | 0.000689 | 0 | 4.75 | 0.000929 | -0.0273 | 4.35 | 0.000689 | 0 | 4.75 | 0.000929 | -0.0273 |  | CFL | None | 4350 | 0.689 | 4350 | 0.689 | 1.09 | 1.35 | -0.0062759 | 4350 | 0.689 | 4350 | 0.689 | 1.09 | 1.35 | -0.00628
CFLNoneSCERtLNewCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | RtL | New | CZ15 | 4.35 | 0.000689 | 0 | 5.14 | 0.000946 | -0.00414 | 4.35 | 0.000689 | 0 | 5.14 | 0.000946 | -0.00414 |  | CFL | None | 4350 | 0.689 | 4350 | 0.689 | 1.18 | 1.37 | -0.00095172 | 4350 | 0.689 | 4350 | 0.689 | 1.18 | 1.37 | -0.000952
CFLNoneSCERtLNewCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | RtL | New | CZ16 | 4.35 | 0.000689 | 0 | 4.3 | 0.000876 | -0.0565 | 4.35 | 0.000689 | 0 | 4.3 | 0.000876 | -0.0565 |  | CFL | None | 4350 | 0.689 | 4350 | 0.689 | 0.989 | 1.27 | -0.012989 | 4350 | 0.689 | 4350 | 0.689 | 0.989 | 1.27 | -0.013
CFLNoneSCERtLNewIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | RtL | New | IOU | 4.35 | 0.000689 | 0 | 4.8304 | 0.00091354 | -0.014693 | 4.35 | 0.000689 | 0 | 4.8304 | 0.00091354 | -0.014693 |  | CFL | None | 4350 | 0.689 | 4350 | 0.689 | 1.11 | 1.33 | -0.0033778 | 4350 | 0.689 | 4350 | 0.689 | 1.11 | 1.33 | -0.00338
CFLNoneSCERtSExCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | RtS | Ex | CZ05 | 4.01 | 0.0007 | 0 | 4.24 | 0.00087 | -0.021 | 4.01 | 0.0007 | 0 | 4.24 | 0.00087 | -0.021 |  | CFL | None | 4010 | 0.7 | 4010 | 0.7 | 1.06 | 1.24 | -0.0052369 | 4010 | 0.7 | 4010 | 0.7 | 1.06 | 1.24 | -0.00524
CFLNoneSCERtSExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | RtS | Ex | CZ06 | 4.01 | 0.0007 | 0 | 4.49 | 0.000879 | -0.0077 | 4.01 | 0.0007 | 0 | 4.49 | 0.000879 | -0.0077 |  | CFL | None | 4010 | 0.7 | 4010 | 0.7 | 1.12 | 1.26 | -0.0019202 | 4010 | 0.7 | 4010 | 0.7 | 1.12 | 1.26 | -0.00192
CFLNoneSCERtSExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | RtS | Ex | CZ08 | 4.01 | 0.0007 | 0 | 4.51 | 0.000881 | -0.00658 | 4.01 | 0.0007 | 0 | 4.51 | 0.000881 | -0.00658 |  | CFL | None | 4010 | 0.7 | 4010 | 0.7 | 1.12 | 1.26 | -0.0016409 | 4010 | 0.7 | 4010 | 0.7 | 1.12 | 1.26 | -0.00164
CFLNoneSCERtSExCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | RtS | Ex | CZ09 | 4.01 | 0.0007 | 0 | 4.48 | 0.000894 | -0.00834 | 4.01 | 0.0007 | 0 | 4.48 | 0.000894 | -0.00834 |  | CFL | None | 4010 | 0.7 | 4010 | 0.7 | 1.12 | 1.28 | -0.0020798 | 4010 | 0.7 | 4010 | 0.7 | 1.12 | 1.28 | -0.00208
CFLNoneSCERtSExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | RtS | Ex | CZ10 | 4.01 | 0.0007 | 0 | 4.4 | 0.00088 | -0.00935 | 4.01 | 0.0007 | 0 | 4.4 | 0.00088 | -0.00935 |  | CFL | None | 4010 | 0.7 | 4010 | 0.7 | 1.1 | 1.26 | -0.0023317 | 4010 | 0.7 | 4010 | 0.7 | 1.1 | 1.26 | -0.00233
CFLNoneSCERtSExCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | RtS | Ex | CZ13 | 4.01 | 0.0007 | 0 | 4.32 | 0.000888 | -0.0221 | 4.01 | 0.0007 | 0 | 4.32 | 0.000888 | -0.0221 |  | CFL | None | 4010 | 0.7 | 4010 | 0.7 | 1.08 | 1.27 | -0.0055112 | 4010 | 0.7 | 4010 | 0.7 | 1.08 | 1.27 | -0.00551
CFLNoneSCERtSExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | RtS | Ex | CZ14 | 4.01 | 0.0007 | 0 | 4.31 | 0.000883 | -0.0203 | 4.01 | 0.0007 | 0 | 4.31 | 0.000883 | -0.0203 |  | CFL | None | 4010 | 0.7 | 4010 | 0.7 | 1.07 | 1.26 | -0.0050623 | 4010 | 0.7 | 4010 | 0.7 | 1.07 | 1.26 | -0.00506
CFLNoneSCERtSExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | RtS | Ex | CZ15 | 4.01 | 0.0007 | 0 | 4.7 | 0.000873 | -0.0024 | 4.01 | 0.0007 | 0 | 4.7 | 0.000873 | -0.0024 |  | CFL | None | 4010 | 0.7 | 4010 | 0.7 | 1.17 | 1.25 | -0.0005985 | 4010 | 0.7 | 4010 | 0.7 | 1.17 | 1.25 | -0.000599
CFLNoneSCERtSExCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | RtS | Ex | CZ16 | 4.01 | 0.0007 | 0 | 3.96 | 0.000864 | -0.0425 | 4.01 | 0.0007 | 0 | 3.96 | 0.000864 | -0.0425 |  | CFL | None | 4010 | 0.7 | 4010 | 0.7 | 0.988 | 1.23 | -0.010599 | 4010 | 0.7 | 4010 | 0.7 | 0.988 | 1.23 | -0.0106
CFLNoneSCERtSExIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | RtS | Ex | IOU | 4.01 | 0.0007 | 0 | 4.4634 | 0.00088209 | -0.0089415 | 4.01 | 0.0007 | 0 | 4.4634 | 0.00088209 | -0.0089415 |  | CFL | None | 4010 | 0.7 | 4010 | 0.7 | 1.11 | 1.26 | -0.0022298 | 4010 | 0.7 | 4010 | 0.7 | 1.11 | 1.26 | -0.00223
CFLNoneSCERtSNewCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | RtS | New | CZ05 | 4.01 | 0.0007 | 0 | 4.12 | 0.000851 | -0.0234 | 4.01 | 0.0007 | 0 | 4.12 | 0.000851 | -0.0234 |  | CFL | None | 4010 | 0.7 | 4010 | 0.7 | 1.03 | 1.22 | -0.0058354 | 4010 | 0.7 | 4010 | 0.7 | 1.03 | 1.22 | -0.00584
CFLNoneSCERtSNewCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | RtS | New | CZ06 | 4.01 | 0.0007 | 0 | 4.34 | 0.000862 | -0.00979 | 4.01 | 0.0007 | 0 | 4.34 | 0.000862 | -0.00979 |  | CFL | None | 4010 | 0.7 | 4010 | 0.7 | 1.08 | 1.23 | -0.0024414 | 4010 | 0.7 | 4010 | 0.7 | 1.08 | 1.23 | -0.00244
CFLNoneSCERtSNewCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | RtS | New | CZ08 | 4.01 | 0.0007 | 0 | 4.38 | 0.000872 | -0.00818 | 4.01 | 0.0007 | 0 | 4.38 | 0.000872 | -0.00818 |  | CFL | None | 4010 | 0.7 | 4010 | 0.7 | 1.09 | 1.25 | -0.0020399 | 4010 | 0.7 | 4010 | 0.7 | 1.09 | 1.25 | -0.00204
CFLNoneSCERtSNewCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | RtS | New | CZ09 | 4.01 | 0.0007 | 0 | 4.37 | 0.000895 | -0.00943 | 4.01 | 0.0007 | 0 | 4.37 | 0.000895 | -0.00943 |  | CFL | None | 4010 | 0.7 | 4010 | 0.7 | 1.09 | 1.28 | -0.0023516 | 4010 | 0.7 | 4010 | 0.7 | 1.09 | 1.28 | -0.00235
CFLNoneSCERtSNewCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | RtS | New | CZ10 | 4.01 | 0.0007 | 0 | 4.41 | 0.000909 | -0.00979 | 4.01 | 0.0007 | 0 | 4.41 | 0.000909 | -0.00979 |  | CFL | None | 4010 | 0.7 | 4010 | 0.7 | 1.1 | 1.3 | -0.0024414 | 4010 | 0.7 | 4010 | 0.7 | 1.1 | 1.3 | -0.00244
CFLNoneSCERtSNewCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | RtS | New | CZ13 | 4.01 | 0.0007 | 0 | 4.3 | 0.000896 | -0.0228 | 4.01 | 0.0007 | 0 | 4.3 | 0.000896 | -0.0228 |  | CFL | None | 4010 | 0.7 | 4010 | 0.7 | 1.07 | 1.28 | -0.0056858 | 4010 | 0.7 | 4010 | 0.7 | 1.07 | 1.28 | -0.00569
CFLNoneSCERtSNewCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | RtS | New | CZ14 | 4.01 | 0.0007 | 0 | 4.31 | 0.000897 | -0.0214 | 4.01 | 0.0007 | 0 | 4.31 | 0.000897 | -0.0214 |  | CFL | None | 4010 | 0.7 | 4010 | 0.7 | 1.07 | 1.28 | -0.0053367 | 4010 | 0.7 | 4010 | 0.7 | 1.07 | 1.28 | -0.00534
CFLNoneSCERtSNewCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | RtS | New | CZ15 | 4.01 | 0.0007 | 0 | 4.62 | 0.000923 | -0.00195 | 4.01 | 0.0007 | 0 | 4.62 | 0.000923 | -0.00195 |  | CFL | None | 4010 | 0.7 | 4010 | 0.7 | 1.15 | 1.32 | -0.00048628 | 4010 | 0.7 | 4010 | 0.7 | 1.15 | 1.32 | -0.000486
CFLNoneSCERtSNewCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | RtS | New | CZ16 | 4.01 | 0.0007 | 0 | 3.94 | 0.00086 | -0.0453 | 4.01 | 0.0007 | 0 | 3.94 | 0.00086 | -0.0453 |  | CFL | None | 4010 | 0.7 | 4010 | 0.7 | 0.983 | 1.23 | -0.011297 | 4010 | 0.7 | 4010 | 0.7 | 0.983 | 1.23 | -0.0113
CFLNoneSCERtSNewIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | RtS | New | IOU | 4.01 | 0.0007 | 0 | 4.3799 | 0.00088921 | -0.01053 | 4.01 | 0.0007 | 0 | 4.3799 | 0.00088921 | -0.01053 |  | CFL | None | 4010 | 0.7 | 4010 | 0.7 | 1.09 | 1.27 | -0.002626 | 4010 | 0.7 | 4010 | 0.7 | 1.09 | 1.27 | -0.00263
CFLNoneSCEs_AgrExCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_Agr | Ex | CZ05 | 2.66 | 0.0007572 | 0 | 2.824 | 0.0009224 | -0.011866 | 2.66 | 0.0007572 | 0 | 2.824 | 0.0009224 | -0.011866 |  | CFL | None | 2660 | 0.757 | 2660 | 0.757 | 1.06 | 1.22 | -0.0044609 | 2660 | 0.757 | 2660 | 0.757 | 1.06 | 1.22 | -0.00446
CFLNoneSCEs_AgrExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_Agr | Ex | CZ06 | 2.66 | 0.0007572 | 0 | 2.974 | 0.000912 | -0.004364 | 2.66 | 0.0007572 | 0 | 2.974 | 0.000912 | -0.004364 |  | CFL | None | 2660 | 0.757 | 2660 | 0.757 | 1.12 | 1.2 | -0.0016406 | 2660 | 0.757 | 2660 | 0.757 | 1.12 | 1.2 | -0.00164
CFLNoneSCEs_AgrExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_Agr | Ex | CZ08 | 2.66 | 0.0007572 | 0 | 2.988 | 0.0009114 | -0.003664 | 2.66 | 0.0007572 | 0 | 2.988 | 0.0009114 | -0.003664 |  | CFL | None | 2660 | 0.757 | 2660 | 0.757 | 1.12 | 1.2 | -0.0013774 | 2660 | 0.757 | 2660 | 0.757 | 1.12 | 1.2 | -0.00138
CFLNoneSCEs_AgrExCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_Agr | Ex | CZ09 | 2.66 | 0.0007572 | 0 | 2.976 | 0.0009298 | -0.004918 | 2.66 | 0.0007572 | 0 | 2.976 | 0.0009298 | -0.004918 |  | CFL | None | 2660 | 0.757 | 2660 | 0.757 | 1.12 | 1.23 | -0.0018489 | 2660 | 0.757 | 2660 | 0.757 | 1.12 | 1.23 | -0.00185
CFLNoneSCEs_AgrExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_Agr | Ex | CZ10 | 2.66 | 0.0007572 | 0 | 2.894 | 0.0009228 | -0.005964 | 2.66 | 0.0007572 | 0 | 2.894 | 0.0009228 | -0.005964 |  | CFL | None | 2660 | 0.757 | 2660 | 0.757 | 1.09 | 1.22 | -0.0022421 | 2660 | 0.757 | 2660 | 0.757 | 1.09 | 1.22 | -0.00224
CFLNoneSCEs_AgrExCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_Agr | Ex | CZ13 | 2.66 | 0.0007572 | 0 | 2.866 | 0.000912 | -0.01336 | 2.66 | 0.0007572 | 0 | 2.866 | 0.000912 | -0.01336 |  | CFL | None | 2660 | 0.757 | 2660 | 0.757 | 1.08 | 1.2 | -0.0050226 | 2660 | 0.757 | 2660 | 0.757 | 1.08 | 1.2 | -0.00502
CFLNoneSCEs_AgrExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_Agr | Ex | CZ14 | 2.66 | 0.0007572 | 0 | 2.842 | 0.0009194 | -0.014576 | 2.66 | 0.0007572 | 0 | 2.842 | 0.0009194 | -0.014576 |  | CFL | None | 2660 | 0.757 | 2660 | 0.757 | 1.07 | 1.21 | -0.0054797 | 2660 | 0.757 | 2660 | 0.757 | 1.07 | 1.21 | -0.00548
CFLNoneSCEs_AgrExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_Agr | Ex | CZ15 | 2.66 | 0.0007572 | 0 | 3.094 | 0.0009124 | -0.00157 | 2.66 | 0.0007572 | 0 | 3.094 | 0.0009124 | -0.00157 |  | CFL | None | 2660 | 0.757 | 2660 | 0.757 | 1.16 | 1.2 | -0.00059023 | 2660 | 0.757 | 2660 | 0.757 | 1.16 | 1.2 | -0.00059
CFLNoneSCEs_AgrExCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_Agr | Ex | CZ16 | 2.66 | 0.0007572 | 0 | 2.63 | 0.0009016 | -0.02918 | 2.66 | 0.0007572 | 0 | 2.63 | 0.0009016 | -0.02918 |  | CFL | None | 2660 | 0.757 | 2660 | 0.757 | 0.989 | 1.19 | -0.01097 | 2660 | 0.757 | 2660 | 0.757 | 0.989 | 1.19 | -0.011
CFLNoneSCEs_AgrExIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | s_Agr | Ex | IOU | 2.66 | 0.0007572 | 0 | 2.9567 | 0.00091633 | -0.0054902 | 2.66 | 0.0007572 | 0 | 2.9567 | 0.00091633 | -0.0054902 |  | CFL | None | 2660 | 0.757 | 2660 | 0.757 | 1.11 | 1.21 | -0.002064 | 2660 | 0.757 | 2660 | 0.757 | 1.11 | 1.21 | -0.00206
CFLNoneSCEs_CliExCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_Cli | Ex | CZ05 | 3.275 | 0.0006215 | 0 | 3.445 | 0.0007745 | -0.030715 | 3.275 | 0.0006215 | 0 | 3.445 | 0.0007745 | -0.030715 |  | CFL | None | 3280 | 0.622 | 3280 | 0.622 | 1.05 | 1.25 | -0.0093786 | 3280 | 0.622 | 3280 | 0.622 | 1.05 | 1.25 | -0.00938
CFLNoneSCEs_CliExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_Cli | Ex | CZ06 | 3.275 | 0.0006215 | 0 | 3.635 | 0.000797 | -0.0195 | 3.275 | 0.0006215 | 0 | 3.635 | 0.000797 | -0.0195 |  | CFL | None | 3280 | 0.622 | 3280 | 0.622 | 1.11 | 1.28 | -0.0059542 | 3280 | 0.622 | 3280 | 0.622 | 1.11 | 1.28 | -0.00595
CFLNoneSCEs_CliExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_Cli | Ex | CZ08 | 3.275 | 0.0006215 | 0 | 3.67 | 0.000801 | -0.01869 | 3.275 | 0.0006215 | 0 | 3.67 | 0.000801 | -0.01869 |  | CFL | None | 3280 | 0.622 | 3280 | 0.622 | 1.12 | 1.29 | -0.0057069 | 3280 | 0.622 | 3280 | 0.622 | 1.12 | 1.29 | -0.00571
CFLNoneSCEs_CliExCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_Cli | Ex | CZ09 | 3.275 | 0.0006215 | 0 | 3.67 | 0.000816 | -0.019535 | 3.275 | 0.0006215 | 0 | 3.67 | 0.000816 | -0.019535 |  | CFL | None | 3280 | 0.622 | 3280 | 0.622 | 1.12 | 1.31 | -0.0059649 | 3280 | 0.622 | 3280 | 0.622 | 1.12 | 1.31 | -0.00596
CFLNoneSCEs_CliExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_Cli | Ex | CZ10 | 3.275 | 0.0006215 | 0 | 3.615 | 0.000812 | -0.01937 | 3.275 | 0.0006215 | 0 | 3.615 | 0.000812 | -0.01937 |  | CFL | None | 3280 | 0.622 | 3280 | 0.622 | 1.1 | 1.31 | -0.0059145 | 3280 | 0.622 | 3280 | 0.622 | 1.1 | 1.31 | -0.00591
CFLNoneSCEs_CliExCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_Cli | Ex | CZ13 | 3.275 | 0.0006215 | 0 | 3.57 | 0.000805 | -0.02525 | 3.275 | 0.0006215 | 0 | 3.57 | 0.000805 | -0.02525 |  | CFL | None | 3280 | 0.622 | 3280 | 0.622 | 1.09 | 1.3 | -0.0077099 | 3280 | 0.622 | 3280 | 0.622 | 1.09 | 1.3 | -0.00771
CFLNoneSCEs_CliExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_Cli | Ex | CZ14 | 3.275 | 0.0006215 | 0 | 3.575 | 0.0008135 | -0.02479 | 3.275 | 0.0006215 | 0 | 3.575 | 0.0008135 | -0.02479 |  | CFL | None | 3280 | 0.622 | 3280 | 0.622 | 1.09 | 1.31 | -0.0075695 | 3280 | 0.622 | 3280 | 0.622 | 1.09 | 1.31 | -0.00757
CFLNoneSCEs_CliExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_Cli | Ex | CZ15 | 3.275 | 0.0006215 | 0 | 3.87 | 0.000811 | -0.010905 | 3.275 | 0.0006215 | 0 | 3.87 | 0.000811 | -0.010905 |  | CFL | None | 3280 | 0.622 | 3280 | 0.622 | 1.18 | 1.3 | -0.0033298 | 3280 | 0.622 | 3280 | 0.622 | 1.18 | 1.3 | -0.00333
CFLNoneSCEs_CliExCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_Cli | Ex | CZ16 | 3.275 | 0.0006215 | 0 | 3.275 | 0.0007805 | -0.0402 | 3.275 | 0.0006215 | 0 | 3.275 | 0.0007805 | -0.0402 |  | CFL | None | 3280 | 0.622 | 3280 | 0.622 | 1 | 1.26 | -0.012275 | 3280 | 0.622 | 3280 | 0.622 | 1 | 1.26 | -0.0123
CFLNoneSCEs_CliExIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | s_Cli | Ex | IOU | 3.275 | 0.0006215 | 0 | 3.6424 | 0.00080386 | -0.019887 | 3.275 | 0.0006215 | 0 | 3.6424 | 0.00080386 | -0.019887 |  | CFL | None | 3280 | 0.622 | 3280 | 0.622 | 1.11 | 1.29 | -0.0060725 | 3280 | 0.622 | 3280 | 0.622 | 1.11 | 1.29 | -0.00607
CFLNoneSCEs_FStExCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_FSt | Ex | CZ05 | 3.95 | 0.0005975 | 0 | 3.985 | 0.0007445 | -0.04435 | 3.95 | 0.0005975 | 0 | 3.985 | 0.0007445 | -0.04435 |  | CFL | None | 3950 | 0.598 | 3950 | 0.598 | 1.01 | 1.25 | -0.011228 | 3950 | 0.598 | 3950 | 0.598 | 1.01 | 1.25 | -0.0112
CFLNoneSCEs_FStExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_FSt | Ex | CZ06 | 3.95 | 0.0005975 | 0 | 4.21 | 0.000751 | -0.0311 | 3.95 | 0.0005975 | 0 | 4.21 | 0.000751 | -0.0311 |  | CFL | None | 3950 | 0.598 | 3950 | 0.598 | 1.07 | 1.26 | -0.0078734 | 3950 | 0.598 | 3950 | 0.598 | 1.07 | 1.26 | -0.00787
CFLNoneSCEs_FStExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_FSt | Ex | CZ08 | 3.95 | 0.0005975 | 0 | 4.275 | 0.000761 | -0.02799 | 3.95 | 0.0005975 | 0 | 4.275 | 0.000761 | -0.02799 |  | CFL | None | 3950 | 0.598 | 3950 | 0.598 | 1.08 | 1.27 | -0.0070861 | 3950 | 0.598 | 3950 | 0.598 | 1.08 | 1.27 | -0.00709
CFLNoneSCEs_FStExCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_FSt | Ex | CZ09 | 3.95 | 0.0005975 | 0 | 4.28 | 0.0007705 | -0.02827 | 3.95 | 0.0005975 | 0 | 4.28 | 0.0007705 | -0.02827 |  | CFL | None | 3950 | 0.598 | 3950 | 0.598 | 1.08 | 1.29 | -0.007157 | 3950 | 0.598 | 3950 | 0.598 | 1.08 | 1.29 | -0.00716
CFLNoneSCEs_FStExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_FSt | Ex | CZ10 | 3.95 | 0.0005975 | 0 | 4.235 | 0.000771 | -0.02822 | 3.95 | 0.0005975 | 0 | 4.235 | 0.000771 | -0.02822 |  | CFL | None | 3950 | 0.598 | 3950 | 0.598 | 1.07 | 1.29 | -0.0071443 | 3950 | 0.598 | 3950 | 0.598 | 1.07 | 1.29 | -0.00714
CFLNoneSCEs_FStExCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_FSt | Ex | CZ13 | 3.95 | 0.0005975 | 0 | 4.2 | 0.000771 | -0.0342 | 3.95 | 0.0005975 | 0 | 4.2 | 0.000771 | -0.0342 |  | CFL | None | 3950 | 0.598 | 3950 | 0.598 | 1.06 | 1.29 | -0.0086582 | 3950 | 0.598 | 3950 | 0.598 | 1.06 | 1.29 | -0.00866
CFLNoneSCEs_FStExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_FSt | Ex | CZ14 | 3.95 | 0.0005975 | 0 | 4.185 | 0.000779 | -0.0339 | 3.95 | 0.0005975 | 0 | 4.185 | 0.000779 | -0.0339 |  | CFL | None | 3950 | 0.598 | 3950 | 0.598 | 1.06 | 1.3 | -0.0085823 | 3950 | 0.598 | 3950 | 0.598 | 1.06 | 1.3 | -0.00858
CFLNoneSCEs_FStExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_FSt | Ex | CZ15 | 3.95 | 0.0005975 | 0 | 4.54 | 0.0007665 | -0.0148 | 3.95 | 0.0005975 | 0 | 4.54 | 0.0007665 | -0.0148 |  | CFL | None | 3950 | 0.598 | 3950 | 0.598 | 1.15 | 1.28 | -0.0037468 | 3950 | 0.598 | 3950 | 0.598 | 1.15 | 1.28 | -0.00375
CFLNoneSCEs_FStExCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_FSt | Ex | CZ16 | 3.95 | 0.0005975 | 0 | 3.83 | 0.000744 | -0.05295 | 3.95 | 0.0005975 | 0 | 3.83 | 0.000744 | -0.05295 |  | CFL | None | 3950 | 0.598 | 3950 | 0.598 | 0.97 | 1.25 | -0.013405 | 3950 | 0.598 | 3950 | 0.598 | 0.97 | 1.25 | -0.0134
CFLNoneSCEs_FStExIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | s_FSt | Ex | IOU | 3.95 | 0.0005975 | 0 | 4.2483 | 0.00076351 | -0.029114 | 3.95 | 0.0005975 | 0 | 4.2483 | 0.00076351 | -0.029114 |  | CFL | None | 3950 | 0.598 | 3950 | 0.598 | 1.08 | 1.28 | -0.0073706 | 3950 | 0.598 | 3950 | 0.598 | 1.08 | 1.28 | -0.00737
CFLNoneSCEs_IndExCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_Ind | Ex | CZ05 | 2.835 | 0.0007785 | 0 | 3.13 | 0.000955 | -0.006905 | 2.835 | 0.0007785 | 0 | 3.13 | 0.000955 | -0.006905 |  | CFL | None | 2840 | 0.778 | 2840 | 0.778 | 1.1 | 1.23 | -0.0024356 | 2840 | 0.778 | 2840 | 0.778 | 1.1 | 1.23 | -0.00244
CFLNoneSCEs_IndExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_Ind | Ex | CZ06 | 2.835 | 0.0007785 | 0 | 3.245 | 0.0009345 | -0.0024475 | 2.835 | 0.0007785 | 0 | 3.245 | 0.0009345 | -0.0024475 |  | CFL | None | 2840 | 0.778 | 2840 | 0.778 | 1.14 | 1.2 | -0.00086332 | 2840 | 0.778 | 2840 | 0.778 | 1.14 | 1.2 | -0.000863
CFLNoneSCEs_IndExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_Ind | Ex | CZ08 | 2.835 | 0.0007785 | 0 | 3.26 | 0.0009515 | -0.0018855 | 2.835 | 0.0007785 | 0 | 3.26 | 0.0009515 | -0.0018855 |  | CFL | None | 2840 | 0.778 | 2840 | 0.778 | 1.15 | 1.22 | -0.00066508 | 2840 | 0.778 | 2840 | 0.778 | 1.15 | 1.22 | -0.000665
CFLNoneSCEs_IndExCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_Ind | Ex | CZ09 | 2.835 | 0.0007785 | 0 | 3.25 | 0.0009635 | -0.002874 | 2.835 | 0.0007785 | 0 | 3.25 | 0.0009635 | -0.002874 |  | CFL | None | 2840 | 0.778 | 2840 | 0.778 | 1.15 | 1.24 | -0.0010138 | 2840 | 0.778 | 2840 | 0.778 | 1.15 | 1.24 | -0.00101
CFLNoneSCEs_IndExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_Ind | Ex | CZ10 | 2.835 | 0.0007785 | 0 | 3.15 | 0.0009605 | -0.00362 | 2.835 | 0.0007785 | 0 | 3.15 | 0.0009605 | -0.00362 |  | CFL | None | 2840 | 0.778 | 2840 | 0.778 | 1.11 | 1.23 | -0.0012769 | 2840 | 0.778 | 2840 | 0.778 | 1.11 | 1.23 | -0.00128
CFLNoneSCEs_IndExCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_Ind | Ex | CZ13 | 2.835 | 0.0007785 | 0 | 3.14 | 0.000938 | -0.00796 | 2.835 | 0.0007785 | 0 | 3.14 | 0.000938 | -0.00796 |  | CFL | None | 2840 | 0.778 | 2840 | 0.778 | 1.11 | 1.2 | -0.0028078 | 2840 | 0.778 | 2840 | 0.778 | 1.11 | 1.2 | -0.00281
CFLNoneSCEs_IndExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_Ind | Ex | CZ14 | 2.835 | 0.0007785 | 0 | 3.125 | 0.0009565 | -0.009165 | 2.835 | 0.0007785 | 0 | 3.125 | 0.0009565 | -0.009165 |  | CFL | None | 2840 | 0.778 | 2840 | 0.778 | 1.1 | 1.23 | -0.0032328 | 2840 | 0.778 | 2840 | 0.778 | 1.1 | 1.23 | -0.00323
CFLNoneSCEs_IndExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_Ind | Ex | CZ15 | 2.835 | 0.0007785 | 0 | 3.315 | 0.0009565 | -0.000805 | 2.835 | 0.0007785 | 0 | 3.315 | 0.0009565 | -0.000805 |  | CFL | None | 2840 | 0.778 | 2840 | 0.778 | 1.17 | 1.23 | -0.00028395 | 2840 | 0.778 | 2840 | 0.778 | 1.17 | 1.23 | -0.000284
CFLNoneSCEs_IndExCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_Ind | Ex | CZ16 | 2.835 | 0.0007785 | 0 | 2.925 | 0.000922 | -0.019695 | 2.835 | 0.0007785 | 0 | 2.925 | 0.000922 | -0.019695 |  | CFL | None | 2840 | 0.778 | 2840 | 0.778 | 1.03 | 1.18 | -0.0069471 | 2840 | 0.778 | 2840 | 0.778 | 1.03 | 1.18 | -0.00695
CFLNoneSCEs_IndExIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | s_Ind | Ex | IOU | 2.835 | 0.0007785 | 0 | 3.2248 | 0.0009506 | -0.0031961 | 2.835 | 0.0007785 | 0 | 3.2248 | 0.0009506 | -0.0031961 |  | CFL | None | 2840 | 0.778 | 2840 | 0.778 | 1.14 | 1.22 | -0.0011274 | 2840 | 0.778 | 2840 | 0.778 | 1.14 | 1.22 | -0.00113
CFLNoneSCEs_MiCExCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_MiC | Ex | CZ05 | 3.94 | 0.000726 | 0 | 4.1867 | 0.00089833 | -0.024577 | 3.94 | 0.000726 | 0 | 4.1867 | 0.00089833 | -0.024577 |  | CFL | None | 3940 | 0.726 | 3940 | 0.726 | 1.06 | 1.24 | -0.0062377 | 3940 | 0.726 | 3940 | 0.726 | 1.06 | 1.24 | -0.00624
CFLNoneSCEs_MiCExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_MiC | Ex | CZ06 | 3.94 | 0.000726 | 0 | 4.4167 | 0.00090933 | -0.0115 | 3.94 | 0.000726 | 0 | 4.4167 | 0.00090933 | -0.0115 |  | CFL | None | 3940 | 0.726 | 3940 | 0.726 | 1.12 | 1.25 | -0.0029188 | 3940 | 0.726 | 3940 | 0.726 | 1.12 | 1.25 | -0.00292
CFLNoneSCEs_MiCExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_MiC | Ex | CZ08 | 3.94 | 0.000726 | 0 | 4.4467 | 0.00090333 | -0.0098867 | 3.94 | 0.000726 | 0 | 4.4467 | 0.00090333 | -0.0098867 |  | CFL | None | 3940 | 0.726 | 3940 | 0.726 | 1.13 | 1.24 | -0.0025093 | 3940 | 0.726 | 3940 | 0.726 | 1.13 | 1.24 | -0.00251
CFLNoneSCEs_MiCExCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_MiC | Ex | CZ09 | 3.94 | 0.000726 | 0 | 4.43 | 0.00091567 | -0.01167 | 3.94 | 0.000726 | 0 | 4.43 | 0.00091567 | -0.01167 |  | CFL | None | 3940 | 0.726 | 3940 | 0.726 | 1.12 | 1.26 | -0.0029619 | 3940 | 0.726 | 3940 | 0.726 | 1.12 | 1.26 | -0.00296
CFLNoneSCEs_MiCExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_MiC | Ex | CZ10 | 3.94 | 0.000726 | 0 | 4.3567 | 0.00089867 | -0.012293 | 3.94 | 0.000726 | 0 | 4.3567 | 0.00089867 | -0.012293 |  | CFL | None | 3940 | 0.726 | 3940 | 0.726 | 1.11 | 1.24 | -0.0031201 | 3940 | 0.726 | 3940 | 0.726 | 1.11 | 1.24 | -0.00312
CFLNoneSCEs_MiCExCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_MiC | Ex | CZ13 | 3.94 | 0.000726 | 0 | 4.3 | 0.00091233 | -0.022267 | 3.94 | 0.000726 | 0 | 4.3 | 0.00091233 | -0.022267 |  | CFL | None | 3940 | 0.726 | 3940 | 0.726 | 1.09 | 1.26 | -0.0056514 | 3940 | 0.726 | 3940 | 0.726 | 1.09 | 1.26 | -0.00565
CFLNoneSCEs_MiCExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_MiC | Ex | CZ14 | 3.94 | 0.000726 | 0 | 4.28 | 0.000904 | -0.021327 | 3.94 | 0.000726 | 0 | 4.28 | 0.000904 | -0.021327 |  | CFL | None | 3940 | 0.726 | 3940 | 0.726 | 1.09 | 1.25 | -0.0054129 | 3940 | 0.726 | 3940 | 0.726 | 1.09 | 1.25 | -0.00541
CFLNoneSCEs_MiCExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_MiC | Ex | CZ15 | 3.94 | 0.000726 | 0 | 4.6567 | 0.00091167 | -0.0041367 | 3.94 | 0.000726 | 0 | 4.6567 | 0.00091167 | -0.0041367 |  | CFL | None | 3940 | 0.726 | 3940 | 0.726 | 1.18 | 1.26 | -0.0010499 | 3940 | 0.726 | 3940 | 0.726 | 1.18 | 1.26 | -0.00105
CFLNoneSCEs_MiCExCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_MiC | Ex | CZ16 | 3.94 | 0.000726 | 0 | 3.9367 | 0.00088667 | -0.0418 | 3.94 | 0.000726 | 0 | 3.9367 | 0.00088667 | -0.0418 |  | CFL | None | 3940 | 0.726 | 3940 | 0.726 | 0.999 | 1.22 | -0.010609 | 3940 | 0.726 | 3940 | 0.726 | 0.999 | 1.22 | -0.0106
CFLNoneSCEs_MiCExIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | s_MiC | Ex | IOU | 3.94 | 0.000726 | 0 | 4.4073 | 0.00090568 | -0.012151 | 3.94 | 0.000726 | 0 | 4.4073 | 0.00090568 | -0.012151 |  | CFL | None | 3940 | 0.726 | 3940 | 0.726 | 1.12 | 1.25 | -0.003084 | 3940 | 0.726 | 3940 | 0.726 | 1.12 | 1.25 | -0.00308
CFLNoneSCEs_TCUExCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_TCU | Ex | CZ05 | 2.816 | 0.000646 | 0 | 2.924 | 0.000779 | -0.014046 | 2.816 | 0.000646 | 0 | 2.924 | 0.000779 | -0.014046 |  | CFL | None | 2820 | 0.646 | 2820 | 0.646 | 1.04 | 1.21 | -0.0049879 | 2820 | 0.646 | 2820 | 0.646 | 1.04 | 1.21 | -0.00499
CFLNoneSCEs_TCUExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_TCU | Ex | CZ06 | 2.816 | 0.000646 | 0 | 3.066 | 0.000788 | -0.007306 | 2.816 | 0.000646 | 0 | 3.066 | 0.000788 | -0.007306 |  | CFL | None | 2820 | 0.646 | 2820 | 0.646 | 1.09 | 1.22 | -0.0025945 | 2820 | 0.646 | 2820 | 0.646 | 1.09 | 1.22 | -0.00259
CFLNoneSCEs_TCUExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_TCU | Ex | CZ08 | 2.816 | 0.000646 | 0 | 3.09 | 0.0007916 | -0.006548 | 2.816 | 0.000646 | 0 | 3.09 | 0.0007916 | -0.006548 |  | CFL | None | 2820 | 0.646 | 2820 | 0.646 | 1.1 | 1.23 | -0.0023253 | 2820 | 0.646 | 2820 | 0.646 | 1.1 | 1.23 | -0.00233
CFLNoneSCEs_TCUExCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_TCU | Ex | CZ09 | 2.816 | 0.000646 | 0 | 3.078 | 0.0008002 | -0.00799 | 2.816 | 0.000646 | 0 | 3.078 | 0.0008002 | -0.00799 |  | CFL | None | 2820 | 0.646 | 2820 | 0.646 | 1.09 | 1.24 | -0.0028374 | 2820 | 0.646 | 2820 | 0.646 | 1.09 | 1.24 | -0.00284
CFLNoneSCEs_TCUExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_TCU | Ex | CZ10 | 2.816 | 0.000646 | 0 | 3.046 | 0.0007946 | -0.007842 | 2.816 | 0.000646 | 0 | 3.046 | 0.0007946 | -0.007842 |  | CFL | None | 2820 | 0.646 | 2820 | 0.646 | 1.08 | 1.23 | -0.0027848 | 2820 | 0.646 | 2820 | 0.646 | 1.08 | 1.23 | -0.00278
CFLNoneSCEs_TCUExCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_TCU | Ex | CZ13 | 2.816 | 0.000646 | 0 | 3.016 | 0.0007854 | -0.0129 | 2.816 | 0.000646 | 0 | 3.016 | 0.0007854 | -0.0129 |  | CFL | None | 2820 | 0.646 | 2820 | 0.646 | 1.07 | 1.22 | -0.004581 | 2820 | 0.646 | 2820 | 0.646 | 1.07 | 1.22 | -0.00458
CFLNoneSCEs_TCUExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_TCU | Ex | CZ14 | 2.816 | 0.000646 | 0 | 3 | 0.0007926 | -0.013136 | 2.816 | 0.000646 | 0 | 3 | 0.0007926 | -0.013136 |  | CFL | None | 2820 | 0.646 | 2820 | 0.646 | 1.07 | 1.23 | -0.0046648 | 2820 | 0.646 | 2820 | 0.646 | 1.07 | 1.23 | -0.00466
CFLNoneSCEs_TCUExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_TCU | Ex | CZ15 | 2.816 | 0.000646 | 0 | 3.212 | 0.0007884 | -0.003388 | 2.816 | 0.000646 | 0 | 3.212 | 0.0007884 | -0.003388 |  | CFL | None | 2820 | 0.646 | 2820 | 0.646 | 1.14 | 1.22 | -0.0012031 | 2820 | 0.646 | 2820 | 0.646 | 1.14 | 1.22 | -0.0012
CFLNoneSCEs_TCUExCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_TCU | Ex | CZ16 | 2.816 | 0.000646 | 0 | 2.798 | 0.0007696 | -0.02356 | 2.816 | 0.000646 | 0 | 2.798 | 0.0007696 | -0.02356 |  | CFL | None | 2820 | 0.646 | 2820 | 0.646 | 0.994 | 1.19 | -0.0083665 | 2820 | 0.646 | 2820 | 0.646 | 0.994 | 1.19 | -0.00837
CFLNoneSCEs_TCUExIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | s_TCU | Ex | IOU | 2.816 | 0.000646 | 0 | 3.0701 | 0.00079204 | -0.0077303 | 2.816 | 0.000646 | 0 | 3.0701 | 0.00079204 | -0.0077303 |  | CFL | None | 2820 | 0.646 | 2820 | 0.646 | 1.09 | 1.23 | -0.0027451 | 2820 | 0.646 | 2820 | 0.646 | 1.09 | 1.23 | -0.00275
CFLNoneSCESCnExCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | SCn | Ex | CZ05 | 2.76 | 0.000575 | 0 | 2.57 | 0.000719 | -0.0276 | 2.76 | 0.000575 | 0 | 2.57 | 0.000719 | -0.0276 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 0.931 | 1.25 | -0.01 | 2760 | 0.575 | 2760 | 0.575 | 0.931 | 1.25 | -0.01
CFLNoneSCESCnExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | SCn | Ex | CZ06 | 2.76 | 0.000575 | 0 | 2.86 | 0.000746 | -0.0143 | 2.76 | 0.000575 | 0 | 2.86 | 0.000746 | -0.0143 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 1.04 | 1.3 | -0.0051812 | 2760 | 0.575 | 2760 | 0.575 | 1.04 | 1.3 | -0.00518
CFLNoneSCESCnExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | SCn | Ex | CZ08 | 2.76 | 0.000575 | 0 | 2.91 | 0.000743 | -0.0123 | 2.76 | 0.000575 | 0 | 2.91 | 0.000743 | -0.0123 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 1.05 | 1.29 | -0.0044565 | 2760 | 0.575 | 2760 | 0.575 | 1.05 | 1.29 | -0.00446
CFLNoneSCESCnExCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | SCn | Ex | CZ09 | 2.76 | 0.000575 | 0 | 2.89 | 0.000757 | -0.0148 | 2.76 | 0.000575 | 0 | 2.89 | 0.000757 | -0.0148 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 1.05 | 1.32 | -0.0053623 | 2760 | 0.575 | 2760 | 0.575 | 1.05 | 1.32 | -0.00536
CFLNoneSCESCnExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | SCn | Ex | CZ10 | 2.76 | 0.000575 | 0 | 2.87 | 0.000748 | -0.0159 | 2.76 | 0.000575 | 0 | 2.87 | 0.000748 | -0.0159 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 1.04 | 1.3 | -0.0057609 | 2760 | 0.575 | 2760 | 0.575 | 1.04 | 1.3 | -0.00576
CFLNoneSCESCnExCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | SCn | Ex | CZ13 | 2.76 | 0.000575 | 0 | 2.82 | 0.000738 | -0.0213 | 2.76 | 0.000575 | 0 | 2.82 | 0.000738 | -0.0213 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 1.02 | 1.28 | -0.0077174 | 2760 | 0.575 | 2760 | 0.575 | 1.02 | 1.28 | -0.00772
CFLNoneSCESCnExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | SCn | Ex | CZ14 | 2.76 | 0.000575 | 0 | 2.8 | 0.000737 | -0.0234 | 2.76 | 0.000575 | 0 | 2.8 | 0.000737 | -0.0234 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 1.01 | 1.28 | -0.0084783 | 2760 | 0.575 | 2760 | 0.575 | 1.01 | 1.28 | -0.00848
CFLNoneSCESCnExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | SCn | Ex | CZ15 | 2.76 | 0.000575 | 0 | 3.07 | 0.000741 | -0.00625 | 2.76 | 0.000575 | 0 | 3.07 | 0.000741 | -0.00625 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 1.11 | 1.29 | -0.0022645 | 2760 | 0.575 | 2760 | 0.575 | 1.11 | 1.29 | -0.00226
CFLNoneSCESCnExCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | SCn | Ex | CZ16 | 2.76 | 0.000575 | 0 | 2.53 | 0.000717 | -0.0337 | 2.76 | 0.000575 | 0 | 2.53 | 0.000717 | -0.0337 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 0.917 | 1.25 | -0.01221 | 2760 | 0.575 | 2760 | 0.575 | 0.917 | 1.25 | -0.0122
CFLNoneSCESCnExIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | SCn | Ex | IOU | 2.76 | 0.000575 | 0 | 2.8846 | 0.00074618 | -0.014319 | 2.76 | 0.000575 | 0 | 2.8846 | 0.00074618 | -0.014319 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 1.05 | 1.3 | -0.005188 | 2760 | 0.575 | 2760 | 0.575 | 1.05 | 1.3 | -0.00519
CFLNoneSCESCnNewCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | SCn | New | CZ05 | 2.76 | 0.000575 | 0 | 2.57 | 0.000722 | -0.0304 | 2.76 | 0.000575 | 0 | 2.57 | 0.000722 | -0.0304 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 0.931 | 1.26 | -0.011014 | 2760 | 0.575 | 2760 | 0.575 | 0.931 | 1.26 | -0.011
CFLNoneSCESCnNewCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | SCn | New | CZ06 | 2.76 | 0.000575 | 0 | 2.77 | 0.000692 | -0.0162 | 2.76 | 0.000575 | 0 | 2.77 | 0.000692 | -0.0162 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 1 | 1.2 | -0.0058696 | 2760 | 0.575 | 2760 | 0.575 | 1 | 1.2 | -0.00587
CFLNoneSCESCnNewCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | SCn | New | CZ08 | 2.76 | 0.000575 | 0 | 2.83 | 0.000702 | -0.0141 | 2.76 | 0.000575 | 0 | 2.83 | 0.000702 | -0.0141 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 1.03 | 1.22 | -0.0051087 | 2760 | 0.575 | 2760 | 0.575 | 1.03 | 1.22 | -0.00511
CFLNoneSCESCnNewCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | SCn | New | CZ09 | 2.76 | 0.000575 | 0 | 2.84 | 0.000725 | -0.0151 | 2.76 | 0.000575 | 0 | 2.84 | 0.000725 | -0.0151 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 1.03 | 1.26 | -0.005471 | 2760 | 0.575 | 2760 | 0.575 | 1.03 | 1.26 | -0.00547
CFLNoneSCESCnNewCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | SCn | New | CZ10 | 2.76 | 0.000575 | 0 | 2.84 | 0.000719 | -0.0165 | 2.76 | 0.000575 | 0 | 2.84 | 0.000719 | -0.0165 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 1.03 | 1.25 | -0.0059783 | 2760 | 0.575 | 2760 | 0.575 | 1.03 | 1.25 | -0.00598
CFLNoneSCESCnNewCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | SCn | New | CZ13 | 2.76 | 0.000575 | 0 | 2.76 | 0.0007 | -0.0217 | 2.76 | 0.000575 | 0 | 2.76 | 0.0007 | -0.0217 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 1 | 1.22 | -0.0078623 | 2760 | 0.575 | 2760 | 0.575 | 1 | 1.22 | -0.00786
CFLNoneSCESCnNewCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | SCn | New | CZ14 | 2.76 | 0.000575 | 0 | 2.79 | 0.000716 | -0.0243 | 2.76 | 0.000575 | 0 | 2.79 | 0.000716 | -0.0243 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 1.01 | 1.25 | -0.0088043 | 2760 | 0.575 | 2760 | 0.575 | 1.01 | 1.25 | -0.0088
CFLNoneSCESCnNewCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | SCn | New | CZ15 | 2.76 | 0.000575 | 0 | 3.02 | 0.000722 | -0.00514 | 2.76 | 0.000575 | 0 | 3.02 | 0.000722 | -0.00514 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 1.09 | 1.26 | -0.0018623 | 2760 | 0.575 | 2760 | 0.575 | 1.09 | 1.26 | -0.00186
CFLNoneSCESCnNewCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | SCn | New | CZ16 | 2.76 | 0.000575 | 0 | 2.51 | 0.000692 | -0.0351 | 2.76 | 0.000575 | 0 | 2.51 | 0.000692 | -0.0351 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 0.909 | 1.2 | -0.012717 | 2760 | 0.575 | 2760 | 0.575 | 0.909 | 1.2 | -0.0127
CFLNoneSCESCnNewIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | SCn | New | IOU | 2.76 | 0.000575 | 0 | 2.8295 | 0.00071359 | -0.016221 | 2.76 | 0.000575 | 0 | 2.8295 | 0.00071359 | -0.016221 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 1.03 | 1.24 | -0.005877 | 2760 | 0.575 | 2760 | 0.575 | 1.03 | 1.24 | -0.00588
CFLNoneSCESUnExCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | SUn | Ex | CZ05 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0 | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0
CFLNoneSCESUnExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | SUn | Ex | CZ06 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0 | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0
CFLNoneSCESUnExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | SUn | Ex | CZ08 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0 | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0
CFLNoneSCESUnExCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | SUn | Ex | CZ09 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0 | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0
CFLNoneSCESUnExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | SUn | Ex | CZ10 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0 | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0
CFLNoneSCESUnExCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | SUn | Ex | CZ13 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0 | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0
CFLNoneSCESUnExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | SUn | Ex | CZ14 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0 | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0
CFLNoneSCESUnExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | SUn | Ex | CZ15 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0 | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0
CFLNoneSCESUnExCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | SUn | Ex | CZ16 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0 | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0
CFLNoneSCESUnExIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | SUn | Ex | IOU | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0 | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0
CFLNoneSCESUnNewCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | SUn | New | CZ05 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0 | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0
CFLNoneSCESUnNewCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | SUn | New | CZ06 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0 | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0
CFLNoneSCESUnNewCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | SUn | New | CZ08 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0 | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0
CFLNoneSCESUnNewCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | SUn | New | CZ09 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0 | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0
CFLNoneSCESUnNewCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | SUn | New | CZ10 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0 | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0
CFLNoneSCESUnNewCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | SUn | New | CZ13 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0 | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0
CFLNoneSCESUnNewCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | SUn | New | CZ14 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0 | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0
CFLNoneSCESUnNewCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | SUn | New | CZ15 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0 | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0
CFLNoneSCESUnNewCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | SUn | New | CZ16 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0 | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0
CFLNoneSCESUnNewIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | SUn | New | IOU | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0 | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0
CFLNoneSCEWRfExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | WRf | Ex | CZ06 | 4.73 | 0.000548 | 0 | 7.37 | 0.000688 | 0 | 4.73 | 0.000548 | 0 | 7.37 | 0.000688 | 0 |  | CFL | None | 4730 | 0.548 | 4730 | 0.548 | 1.56 | 1.26 | 0 | 4730 | 0.548 | 4730 | 0.548 | 1.56 | 1.26 | 0
CFLNoneSCEWRfExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | WRf | Ex | CZ08 | 4.73 | 0.000548 | 0 | 7.46 | 0.000689 | 0 | 4.73 | 0.000548 | 0 | 7.46 | 0.000689 | 0 |  | CFL | None | 4730 | 0.548 | 4730 | 0.548 | 1.58 | 1.26 | 0 | 4730 | 0.548 | 4730 | 0.548 | 1.58 | 1.26 | 0
CFLNoneSCEWRfExCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | WRf | Ex | CZ09 | 4.73 | 0.000548 | 0 | 7.57 | 0.000706 | 0 | 4.73 | 0.000548 | 0 | 7.57 | 0.000706 | 0 |  | CFL | None | 4730 | 0.548 | 4730 | 0.548 | 1.6 | 1.29 | 0 | 4730 | 0.548 | 4730 | 0.548 | 1.6 | 1.29 | 0
CFLNoneSCEWRfExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | WRf | Ex | CZ10 | 4.73 | 0.000548 | 0 | 7.62 | 0.000693 | 0 | 4.73 | 0.000548 | 0 | 7.62 | 0.000693 | 0 |  | CFL | None | 4730 | 0.548 | 4730 | 0.548 | 1.61 | 1.26 | 0 | 4730 | 0.548 | 4730 | 0.548 | 1.61 | 1.26 | 0
CFLNoneSCEWRfExCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | WRf | Ex | CZ13 | 4.73 | 0.000548 | 0 | 7.63 | 0.000691 | 0 | 4.73 | 0.000548 | 0 | 7.63 | 0.000691 | 0 |  | CFL | None | 4730 | 0.548 | 4730 | 0.548 | 1.61 | 1.26 | 0 | 4730 | 0.548 | 4730 | 0.548 | 1.61 | 1.26 | 0
CFLNoneSCEWRfExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | WRf | Ex | CZ14 | 4.73 | 0.000548 | 0 | 7.45 | 0.000689 | 0 | 4.73 | 0.000548 | 0 | 7.45 | 0.000689 | 0 |  | CFL | None | 4730 | 0.548 | 4730 | 0.548 | 1.58 | 1.26 | 0 | 4730 | 0.548 | 4730 | 0.548 | 1.58 | 1.26 | 0
CFLNoneSCEWRfExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | WRf | Ex | CZ15 | 4.73 | 0.000548 | 0 | 7.85 | 0.000693 | 0 | 4.73 | 0.000548 | 0 | 7.85 | 0.000693 | 0 |  | CFL | None | 4730 | 0.548 | 4730 | 0.548 | 1.66 | 1.26 | 0 | 4730 | 0.548 | 4730 | 0.548 | 1.66 | 1.26 | 0
CFLNoneSCEWRfExCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | WRf | Ex | CZ16 | 4.73 | 0.000548 | 0 | 6.89 | 0.000777 | 0 | 4.73 | 0.000548 | 0 | 6.89 | 0.000777 | 0 |  | CFL | None | 4730 | 0.548 | 4730 | 0.548 | 1.46 | 1.42 | 0 | 4730 | 0.548 | 4730 | 0.548 | 1.46 | 1.42 | 0
CFLNoneSCEWRfExIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | WRf | Ex | IOU | 4.73 | 0.000548 | 0 | 7.5062 | 0.0006917 | 0 | 4.73 | 0.000548 | 0 | 7.5062 | 0.0006917 | 0 |  | CFL | None | 4730 | 0.548 | 4730 | 0.548 | 1.59 | 1.26 | 0 | 4730 | 0.548 | 4730 | 0.548 | 1.59 | 1.26 | 0
CFLNoneSCEWRfNewCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | WRf | New | CZ05 | 4.73 | 0.000548 | 0 | 6.65 | 0.0011 | 0 | 4.73 | 0.000548 | 0 | 6.65 | 0.0011 | 0 |  | CFL | None | 4730 | 0.548 | 4730 | 0.548 | 1.41 | 2.01 | 0 | 4730 | 0.548 | 4730 | 0.548 | 1.41 | 2.01 | 0
CFLNoneSCEWRfNewCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | WRf | New | CZ06 | 4.73 | 0.000548 | 0 | 7.17 | 0.000676 | 0 | 4.73 | 0.000548 | 0 | 7.17 | 0.000676 | 0 |  | CFL | None | 4730 | 0.548 | 4730 | 0.548 | 1.52 | 1.23 | 0 | 4730 | 0.548 | 4730 | 0.548 | 1.52 | 1.23 | 0
CFLNoneSCEWRfNewCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | WRf | New | CZ08 | 4.73 | 0.000548 | 0 | 7.13 | 0.000677 | 0 | 4.73 | 0.000548 | 0 | 7.13 | 0.000677 | 0 |  | CFL | None | 4730 | 0.548 | 4730 | 0.548 | 1.51 | 1.24 | 0 | 4730 | 0.548 | 4730 | 0.548 | 1.51 | 1.24 | 0
CFLNoneSCEWRfNewCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | WRf | New | CZ09 | 4.73 | 0.000548 | 0 | 6.98 | 0.000703 | 0 | 4.73 | 0.000548 | 0 | 6.98 | 0.000703 | 0 |  | CFL | None | 4730 | 0.548 | 4730 | 0.548 | 1.48 | 1.28 | 0 | 4730 | 0.548 | 4730 | 0.548 | 1.48 | 1.28 | 0
CFLNoneSCEWRfNewCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | WRf | New | CZ10 | 4.73 | 0.000548 | 0 | 6.96 | 0.000685 | 0 | 4.73 | 0.000548 | 0 | 6.96 | 0.000685 | 0 |  | CFL | None | 4730 | 0.548 | 4730 | 0.548 | 1.47 | 1.25 | 0 | 4730 | 0.548 | 4730 | 0.548 | 1.47 | 1.25 | 0
CFLNoneSCEWRfNewCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | WRf | New | CZ13 | 4.73 | 0.000548 | 0 | 6.94 | 0.000685 | 0 | 4.73 | 0.000548 | 0 | 6.94 | 0.000685 | 0 |  | CFL | None | 4730 | 0.548 | 4730 | 0.548 | 1.47 | 1.25 | 0 | 4730 | 0.548 | 4730 | 0.548 | 1.47 | 1.25 | 0
CFLNoneSCEWRfNewCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | WRf | New | CZ14 | 4.73 | 0.000548 | 0 | 6.7 | 0.000679 | 0 | 4.73 | 0.000548 | 0 | 6.7 | 0.000679 | 0 |  | CFL | None | 4730 | 0.548 | 4730 | 0.548 | 1.42 | 1.24 | 0 | 4730 | 0.548 | 4730 | 0.548 | 1.42 | 1.24 | 0
CFLNoneSCEWRfNewCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | WRf | New | CZ15 | 4.73 | 0.000548 | 0 | 7.19 | 0.000683 | 0 | 4.73 | 0.000548 | 0 | 7.19 | 0.000683 | 0 |  | CFL | None | 4730 | 0.548 | 4730 | 0.548 | 1.52 | 1.25 | 0 | 4730 | 0.548 | 4730 | 0.548 | 1.52 | 1.25 | 0
CFLNoneSCEWRfNewCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | WRf | New | CZ16 | 4.73 | 0.000548 | 0 | 6.23 | 0.0011 | 0 | 4.73 | 0.000548 | 0 | 6.23 | 0.0011 | 0 |  | CFL | None | 4730 | 0.548 | 4730 | 0.548 | 1.32 | 2.01 | 0 | 4730 | 0.548 | 4730 | 0.548 | 1.32 | 2.01 | 0
CFLNoneSCEWRfNewIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | WRf | New | IOU | 4.73 | 0.000548 | 0 | 7.037 | 0.00068495 | 0 | 4.73 | 0.000548 | 0 | 7.037 | 0.00068495 | 0 |  | CFL | None | 4730 | 0.548 | 4730 | 0.548 | 1.49 | 1.25 | 0 | 4730 | 0.548 | 4730 | 0.548 | 1.49 | 1.25 | 0
CFLNoneSDGAsmExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SDG | Asm | Ex | CZ06 | 2.3 | 0.000409 | 0 | 2.52 | 0.000508 | -0.012 | 2.3 | 0.000409 | 0 | 2.52 | 0.000508 | -0.012 |  | CFL | None | 2300 | 0.409 | 2300 | 0.409 | 1.1 | 1.24 | -0.0052174 | 2300 | 0.409 | 2300 | 0.409 | 1.1 | 1.24 | -0.00522
CFLNoneSDGAsmExCZ07 | Com-Iltg-dWatt-CFL_OSnone | SDG | Asm | Ex | CZ07 | 2.3 | 0.000409 | 0 | 2.53 | 0.000507 | -0.011 | 2.3 | 0.000409 | 0 | 2.53 | 0.000507 | -0.011 |  | CFL | None | 2300 | 0.409 | 2300 | 0.409 | 1.1 | 1.24 | -0.0047826 | 2300 | 0.409 | 2300 | 0.409 | 1.1 | 1.24 | -0.00478
CFLNoneSDGAsmExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SDG | Asm | Ex | CZ08 | 2.3 | 0.000409 | 0 | 2.54 | 0.000493 | -0.0105 | 2.3 | 0.000409 | 0 | 2.54 | 0.000493 | -0.0105 |  | CFL | None | 2300 | 0.409 | 2300 | 0.409 | 1.1 | 1.21 | -0.0045652 | 2300 | 0.409 | 2300 | 0.409 | 1.1 | 1.21 | -0.00457
CFLNoneSDGAsmExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SDG | Asm | Ex | CZ10 | 2.3 | 0.000409 | 0 | 2.52 | 0.000497 | -0.0133 | 2.3 | 0.000409 | 0 | 2.52 | 0.000497 | -0.0133 |  | CFL | None | 2300 | 0.409 | 2300 | 0.409 | 1.1 | 1.22 | -0.0057826 | 2300 | 0.409 | 2300 | 0.409 | 1.1 | 1.22 | -0.00578
CFLNoneSDGAsmExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SDG | Asm | Ex | CZ14 | 2.3 | 0.000409 | 0 | 2.46 | 0.000465 | -0.021 | 2.3 | 0.000409 | 0 | 2.46 | 0.000465 | -0.021 |  | CFL | None | 2300 | 0.409 | 2300 | 0.409 | 1.07 | 1.14 | -0.0091304 | 2300 | 0.409 | 2300 | 0.409 | 1.07 | 1.14 | -0.00913
CFLNoneSDGAsmExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SDG | Asm | Ex | CZ15 | 2.3 | 0.000409 | 0 | 2.88 | 0.000484 | -0.00586 | 2.3 | 0.000409 | 0 | 2.88 | 0.000484 | -0.00586 |  | CFL | None | 2300 | 0.409 | 2300 | 0.409 | 1.25 | 1.18 | -0.0025478 | 2300 | 0.409 | 2300 | 0.409 | 1.25 | 1.18 | -0.00255
CFLNoneSDGAsmExIOU | Com-Iltg-dWatt-CFL_OSnone | SDG | Asm | Ex | IOU | 2.3 | 0.000409 | 0 | 2.5273 | 0.00050325 | -0.0118 | 2.3 | 0.000409 | 0 | 2.5273 | 0.00050325 | -0.0118 |  | CFL | None | 2300 | 0.409 | 2300 | 0.409 | 1.1 | 1.23 | -0.0051302 | 2300 | 0.409 | 2300 | 0.409 | 1.1 | 1.23 | -0.00513
CFLNoneSDGAsmNewCZ06 | Com-Iltg-dWatt-CFL_OSnone | SDG | Asm | New | CZ06 | 2.3 | 0.000409 | 0 | 2.48 | 0.000504 | -0.0155 | 2.3 | 0.000409 | 0 | 2.48 | 0.000504 | -0.0155 |  | CFL | None | 2300 | 0.409 | 2300 | 0.409 | 1.08 | 1.23 | -0.0067391 | 2300 | 0.409 | 2300 | 0.409 | 1.08 | 1.23 | -0.00674
CFLNoneSDGAsmNewCZ07 | Com-Iltg-dWatt-CFL_OSnone | SDG | Asm | New | CZ07 | 2.3 | 0.000409 | 0 | 2.5 | 0.000502 | -0.0136 | 2.3 | 0.000409 | 0 | 2.5 | 0.000502 | -0.0136 |  | CFL | None | 2300 | 0.409 | 2300 | 0.409 | 1.09 | 1.23 | -0.005913 | 2300 | 0.409 | 2300 | 0.409 | 1.09 | 1.23 | -0.00591
CFLNoneSDGAsmNewCZ08 | Com-Iltg-dWatt-CFL_OSnone | SDG | Asm | New | CZ08 | 2.3 | 0.000409 | 0 | 2.52 | 0.000498 | -0.012 | 2.3 | 0.000409 | 0 | 2.52 | 0.000498 | -0.012 |  | CFL | None | 2300 | 0.409 | 2300 | 0.409 | 1.1 | 1.22 | -0.0052174 | 2300 | 0.409 | 2300 | 0.409 | 1.1 | 1.22 | -0.00522
CFLNoneSDGAsmNewCZ10 | Com-Iltg-dWatt-CFL_OSnone | SDG | Asm | New | CZ10 | 2.3 | 0.000409 | 0 | 2.5 | 0.00051 | -0.0143 | 2.3 | 0.000409 | 0 | 2.5 | 0.00051 | -0.0143 |  | CFL | None | 2300 | 0.409 | 2300 | 0.409 | 1.09 | 1.25 | -0.0062174 | 2300 | 0.409 | 2300 | 0.409 | 1.09 | 1.25 | -0.00622
CFLNoneSDGAsmNewCZ14 | Com-Iltg-dWatt-CFL_OSnone | SDG | Asm | New | CZ14 | 2.3 | 0.000409 | 0 | 2.44 | 0.000489 | -0.0222 | 2.3 | 0.000409 | 0 | 2.44 | 0.000489 | -0.0222 |  | CFL | None | 2300 | 0.409 | 2300 | 0.409 | 1.06 | 1.2 | -0.0096522 | 2300 | 0.409 | 2300 | 0.409 | 1.06 | 1.2 | -0.00965
CFLNoneSDGAsmNewCZ15 | Com-Iltg-dWatt-CFL_OSnone | SDG | Asm | New | CZ15 | 2.3 | 0.000409 | 0 | 2.77 | 0.000513 | -0.00688 | 2.3 | 0.000409 | 0 | 2.77 | 0.000513 | -0.00688 |  | CFL | None | 2300 | 0.409 | 2300 | 0.409 | 1.2 | 1.25 | -0.0029913 | 2300 | 0.409 | 2300 | 0.409 | 1.2 | 1.25 | -0.00299
CFLNoneSDGAsmNewIOU | Com-Iltg-dWatt-CFL_OSnone | SDG | Asm | New | IOU | 2.3 | 0.000409 | 0 | 2.5 | 0.00050432 | -0.013903 | 2.3 | 0.000409 | 0 | 2.5 | 0.00050432 | -0.013903 |  | CFL | None | 2300 | 0.409 | 2300 | 0.409 | 1.09 | 1.23 | -0.0060449 | 2300 | 0.409 | 2300 | 0.409 | 1.09 | 1.23 | -0.00604
CFLNoneSDGComExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SDG | Com | Ex | CZ06 | 3.0724 | 0.00059158 | 0 | 3.3795 | 0.00073278 | -0.01312 | 3.0724 | 0.00059158 | 0 | 3.3795 | 0.00073278 | -0.01312 |  | CFL | None | 3070 | 0.592 | 3070 | 0.592 | 1.1 | 1.24 | -0.0042701 | 3070 | 0.592 | 3070 | 0.592 | 1.1 | 1.24 | -0.00427
CFLNoneSDGComExCZ07 | Com-Iltg-dWatt-CFL_OSnone | SDG | Com | Ex | CZ07 | 3.045 | 0.00060438 | 0 | 3.3839 | 0.00074352 | -0.0092872 | 3.045 | 0.00060438 | 0 | 3.3839 | 0.00074352 | -0.0092872 |  | CFL | None | 3050 | 0.604 | 3050 | 0.604 | 1.11 | 1.23 | -0.0030499 | 3050 | 0.604 | 3050 | 0.604 | 1.11 | 1.23 | -0.00305
CFLNoneSDGComExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SDG | Com | Ex | CZ08 | 3.3663 | 0.00065207 | 0 | 3.772 | 0.00081618 | -0.010838 | 3.3663 | 0.00065207 | 0 | 3.772 | 0.00081618 | -0.010838 |  | CFL | None | 3370 | 0.652 | 3370 | 0.652 | 1.12 | 1.25 | -0.0032196 | 3370 | 0.652 | 3370 | 0.652 | 1.12 | 1.25 | -0.00322
CFLNoneSDGComExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SDG | Com | Ex | CZ10 | 3.0767 | 0.00062805 | 0 | 3.4069 | 0.00078856 | -0.011815 | 3.0767 | 0.00062805 | 0 | 3.4069 | 0.00078856 | -0.011815 |  | CFL | None | 3080 | 0.628 | 3080 | 0.628 | 1.11 | 1.26 | -0.0038403 | 3080 | 0.628 | 3080 | 0.628 | 1.11 | 1.26 | -0.00384
CFLNoneSDGComExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SDG | Com | Ex | CZ14 | 2.6613 | 0.00058124 | 0 | 2.9024 | 0.00072636 | -0.014696 | 2.6613 | 0.00058124 | 0 | 2.9024 | 0.00072636 | -0.014696 |  | CFL | None | 2660 | 0.581 | 2660 | 0.581 | 1.09 | 1.25 | -0.0055221 | 2660 | 0.581 | 2660 | 0.581 | 1.09 | 1.25 | -0.00552
CFLNoneSDGComExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SDG | Com | Ex | CZ15 | 2.3494 | 0.0004603 | 0 | 2.7826 | 0.00057932 | -0.0034952 | 2.3494 | 0.0004603 | 0 | 2.7826 | 0.00057932 | -0.0034952 |  | CFL | None | 2350 | 0.46 | 2350 | 0.46 | 1.18 | 1.26 | -0.0014877 | 2350 | 0.46 | 2350 | 0.46 | 1.18 | 1.26 | -0.00149
CFLNoneSDGComExIOU | Com-Iltg-dWatt-CFL_OSnone | SDG | Com | Ex | IOU | 3.0593 | 0.00061043 | 0 | 3.3969 | 0.00075527 | -0.010049 | 3.0593 | 0.00061043 | 0 | 3.3969 | 0.00075527 | -0.010049 |  | CFL | None | 3060 | 0.61 | 3060 | 0.61 | 1.11 | 1.24 | -0.0032848 | 3060 | 0.61 | 3060 | 0.61 | 1.11 | 1.24 | -0.00328
CFLNoneSDGComNewCZ06 | Com-Iltg-dWatt-CFL_OSnone | SDG | Com | New | CZ06 | 3.0023 | 0.00055818 | 0 | 3.2511 | 0.00068761 | -0.013397 | 3.0023 | 0.00055818 | 0 | 3.2511 | 0.00068761 | -0.013397 |  | CFL | None | 3000 | 0.558 | 3000 | 0.558 | 1.08 | 1.23 | -0.0044624 | 3000 | 0.558 | 3000 | 0.558 | 1.08 | 1.23 | -0.00446
CFLNoneSDGComNewCZ07 | Com-Iltg-dWatt-CFL_OSnone | SDG | Com | New | CZ07 | 2.9688 | 0.00057738 | 0 | 3.2336 | 0.00070107 | -0.0091598 | 2.9688 | 0.00057738 | 0 | 3.2336 | 0.00070107 | -0.0091598 |  | CFL | None | 2970 | 0.577 | 2970 | 0.577 | 1.09 | 1.21 | -0.0030854 | 2970 | 0.577 | 2970 | 0.577 | 1.09 | 1.21 | -0.00309
CFLNoneSDGComNewCZ08 | Com-Iltg-dWatt-CFL_OSnone | SDG | Com | New | CZ08 | 3.4184 | 0.0006455 | 0 | 3.7576 | 0.00080308 | -0.011201 | 3.4184 | 0.0006455 | 0 | 3.7576 | 0.00080308 | -0.011201 |  | CFL | None | 3420 | 0.645 | 3420 | 0.645 | 1.1 | 1.24 | -0.0032768 | 3420 | 0.645 | 3420 | 0.645 | 1.1 | 1.24 | -0.00328
CFLNoneSDGComNewCZ10 | Com-Iltg-dWatt-CFL_OSnone | SDG | Com | New | CZ10 | 3.0689 | 0.00061566 | 0 | 3.3743 | 0.00079473 | -0.011989 | 3.0689 | 0.00061566 | 0 | 3.3743 | 0.00079473 | -0.011989 |  | CFL | None | 3070 | 0.616 | 3070 | 0.616 | 1.1 | 1.29 | -0.0039067 | 3070 | 0.616 | 3070 | 0.616 | 1.1 | 1.29 | -0.00391
CFLNoneSDGComNewCZ14 | Com-Iltg-dWatt-CFL_OSnone | SDG | Com | New | CZ14 | 2.5807 | 0.00054577 | 0 | 2.7949 | 0.00069841 | -0.014461 | 2.5807 | 0.00054577 | 0 | 2.7949 | 0.00069841 | -0.014461 |  | CFL | None | 2580 | 0.546 | 2580 | 0.546 | 1.08 | 1.28 | -0.0056033 | 2580 | 0.546 | 2580 | 0.546 | 1.08 | 1.28 | -0.0056
CFLNoneSDGComNewCZ15 | Com-Iltg-dWatt-CFL_OSnone | SDG | Com | New | CZ15 | 2.1978 | 0.00040498 | 0 | 2.5866 | 0.00053239 | -0.0031178 | 2.1978 | 0.00040498 | 0 | 2.5866 | 0.00053239 | -0.0031178 |  | CFL | None | 2200 | 0.405 | 2200 | 0.405 | 1.18 | 1.31 | -0.0014186 | 2200 | 0.405 | 2200 | 0.405 | 1.18 | 1.31 | -0.00142
CFLNoneSDGComNewIOU | Com-Iltg-dWatt-CFL_OSnone | SDG | Com | New | IOU | 3.0014 | 0.0005869 | 0 | 3.2772 | 0.00072472 | -0.010023 | 3.0014 | 0.0005869 | 0 | 3.2772 | 0.00072472 | -0.010023 |  | CFL | None | 3000 | 0.587 | 3000 | 0.587 | 1.09 | 1.23 | -0.0033394 | 3000 | 0.587 | 3000 | 0.587 | 1.09 | 1.23 | -0.00334
CFLNoneSDGECCExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SDG | ECC | Ex | CZ06 | 2.42 | 0.000647 | 0 | 2.71 | 0.000826 | -0.0141 | 2.42 | 0.000647 | 0 | 2.71 | 0.000826 | -0.0141 |  | CFL | None | 2420 | 0.647 | 2420 | 0.647 | 1.12 | 1.28 | -0.0058264 | 2420 | 0.647 | 2420 | 0.647 | 1.12 | 1.28 | -0.00583
CFLNoneSDGECCExCZ07 | Com-Iltg-dWatt-CFL_OSnone | SDG | ECC | Ex | CZ07 | 2.42 | 0.000647 | 0 | 2.74 | 0.000824 | -0.0116 | 2.42 | 0.000647 | 0 | 2.74 | 0.000824 | -0.0116 |  | CFL | None | 2420 | 0.647 | 2420 | 0.647 | 1.13 | 1.27 | -0.0047934 | 2420 | 0.647 | 2420 | 0.647 | 1.13 | 1.27 | -0.00479
CFLNoneSDGECCExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SDG | ECC | Ex | CZ08 | 2.42 | 0.000647 | 0 | 2.75 | 0.000822 | -0.0126 | 2.42 | 0.000647 | 0 | 2.75 | 0.000822 | -0.0126 |  | CFL | None | 2420 | 0.647 | 2420 | 0.647 | 1.14 | 1.27 | -0.0052066 | 2420 | 0.647 | 2420 | 0.647 | 1.14 | 1.27 | -0.00521
CFLNoneSDGECCExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SDG | ECC | Ex | CZ10 | 2.42 | 0.000647 | 0 | 2.74 | 0.000838 | -0.015 | 2.42 | 0.000647 | 0 | 2.74 | 0.000838 | -0.015 |  | CFL | None | 2420 | 0.647 | 2420 | 0.647 | 1.13 | 1.3 | -0.0061983 | 2420 | 0.647 | 2420 | 0.647 | 1.13 | 1.3 | -0.0062
CFLNoneSDGECCExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SDG | ECC | Ex | CZ14 | 2.42 | 0.000647 | 0 | 2.68 | 0.000826 | -0.0226 | 2.42 | 0.000647 | 0 | 2.68 | 0.000826 | -0.0226 |  | CFL | None | 2420 | 0.647 | 2420 | 0.647 | 1.11 | 1.28 | -0.0093388 | 2420 | 0.647 | 2420 | 0.647 | 1.11 | 1.28 | -0.00934
CFLNoneSDGECCExIOU | Com-Iltg-dWatt-CFL_OSnone | SDG | ECC | Ex | IOU | 2.42 | 0.000647 | 0 | 2.7396 | 0.00082729 | -0.012478 | 2.42 | 0.000647 | 0 | 2.7396 | 0.00082729 | -0.012478 |  | CFL | None | 2420 | 0.647 | 2420 | 0.647 | 1.13 | 1.28 | -0.0051562 | 2420 | 0.647 | 2420 | 0.647 | 1.13 | 1.28 | -0.00516
CFLNoneSDGECCNewCZ06 | Com-Iltg-dWatt-CFL_OSnone | SDG | ECC | New | CZ06 | 2.42 | 0.000647 | 0 | 2.72 | 0.00083 | -0.0171 | 2.42 | 0.000647 | 0 | 2.72 | 0.00083 | -0.0171 |  | CFL | None | 2420 | 0.647 | 2420 | 0.647 | 1.12 | 1.28 | -0.0070661 | 2420 | 0.647 | 2420 | 0.647 | 1.12 | 1.28 | -0.00707
CFLNoneSDGECCNewCZ07 | Com-Iltg-dWatt-CFL_OSnone | SDG | ECC | New | CZ07 | 2.42 | 0.000647 | 0 | 2.72 | 0.000837 | -0.0129 | 2.42 | 0.000647 | 0 | 2.72 | 0.000837 | -0.0129 |  | CFL | None | 2420 | 0.647 | 2420 | 0.647 | 1.12 | 1.29 | -0.0053306 | 2420 | 0.647 | 2420 | 0.647 | 1.12 | 1.29 | -0.00533
CFLNoneSDGECCNewCZ08 | Com-Iltg-dWatt-CFL_OSnone | SDG | ECC | New | CZ08 | 2.42 | 0.000647 | 0 | 2.74 | 0.000829 | -0.0125 | 2.42 | 0.000647 | 0 | 2.74 | 0.000829 | -0.0125 |  | CFL | None | 2420 | 0.647 | 2420 | 0.647 | 1.13 | 1.28 | -0.0051653 | 2420 | 0.647 | 2420 | 0.647 | 1.13 | 1.28 | -0.00517
CFLNoneSDGECCNewCZ10 | Com-Iltg-dWatt-CFL_OSnone | SDG | ECC | New | CZ10 | 2.42 | 0.000647 | 0 | 2.76 | 0.000855 | -0.0143 | 2.42 | 0.000647 | 0 | 2.76 | 0.000855 | -0.0143 |  | CFL | None | 2420 | 0.647 | 2420 | 0.647 | 1.14 | 1.32 | -0.0059091 | 2420 | 0.647 | 2420 | 0.647 | 1.14 | 1.32 | -0.00591
CFLNoneSDGECCNewCZ14 | Com-Iltg-dWatt-CFL_OSnone | SDG | ECC | New | CZ14 | 2.42 | 0.000647 | 0 | 2.73 | 0.000828 | -0.0225 | 2.42 | 0.000647 | 0 | 2.73 | 0.000828 | -0.0225 |  | CFL | None | 2420 | 0.647 | 2420 | 0.647 | 1.13 | 1.28 | -0.0092975 | 2420 | 0.647 | 2420 | 0.647 | 1.13 | 1.28 | -0.0093
CFLNoneSDGECCNewCZ15 | Com-Iltg-dWatt-CFL_OSnone | SDG | ECC | New | CZ15 | 2.42 | 0.000647 | 0 | 2.92 | 0.000848 | -0.00559 | 2.42 | 0.000647 | 0 | 2.92 | 0.000848 | -0.00559 |  | CFL | None | 2420 | 0.647 | 2420 | 0.647 | 1.21 | 1.31 | -0.0023099 | 2420 | 0.647 | 2420 | 0.647 | 1.21 | 1.31 | -0.00231
CFLNoneSDGECCNewIOU | Com-Iltg-dWatt-CFL_OSnone | SDG | ECC | New | IOU | 2.42 | 0.000647 | 0 | 2.7296 | 0.00084107 | -0.013297 | 2.42 | 0.000647 | 0 | 2.7296 | 0.00084107 | -0.013297 |  | CFL | None | 2420 | 0.647 | 2420 | 0.647 | 1.13 | 1.3 | -0.0054948 | 2420 | 0.647 | 2420 | 0.647 | 1.13 | 1.3 | -0.00549
CFLNoneSDGEPrExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SDG | EPr | Ex | CZ06 | 2.24 | 0.00063 | 0 | 2.53 | 0.000804 | -0.0104 | 2.24 | 0.00063 | 0 | 2.53 | 0.000804 | -0.0104 |  | CFL | None | 2240 | 0.63 | 2240 | 0.63 | 1.13 | 1.28 | -0.0046429 | 2240 | 0.63 | 2240 | 0.63 | 1.13 | 1.28 | -0.00464
CFLNoneSDGEPrExCZ07 | Com-Iltg-dWatt-CFL_OSnone | SDG | EPr | Ex | CZ07 | 2.24 | 0.00063 | 0 | 2.53 | 0.000811 | -0.00961 | 2.24 | 0.00063 | 0 | 2.53 | 0.000811 | -0.00961 |  | CFL | None | 2240 | 0.63 | 2240 | 0.63 | 1.13 | 1.29 | -0.0042902 | 2240 | 0.63 | 2240 | 0.63 | 1.13 | 1.29 | -0.00429
CFLNoneSDGEPrExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SDG | EPr | Ex | CZ08 | 2.24 | 0.00063 | 0 | 2.56 | 0.000811 | -0.00878 | 2.24 | 0.00063 | 0 | 2.56 | 0.000811 | -0.00878 |  | CFL | None | 2240 | 0.63 | 2240 | 0.63 | 1.14 | 1.29 | -0.0039196 | 2240 | 0.63 | 2240 | 0.63 | 1.14 | 1.29 | -0.00392
CFLNoneSDGEPrExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SDG | EPr | Ex | CZ10 | 2.24 | 0.00063 | 0 | 2.54 | 0.000804 | -0.011 | 2.24 | 0.00063 | 0 | 2.54 | 0.000804 | -0.011 |  | CFL | None | 2240 | 0.63 | 2240 | 0.63 | 1.13 | 1.28 | -0.0049107 | 2240 | 0.63 | 2240 | 0.63 | 1.13 | 1.28 | -0.00491
CFLNoneSDGEPrExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SDG | EPr | Ex | CZ14 | 2.24 | 0.00063 | 0 | 2.43 | 0.000805 | -0.0184 | 2.24 | 0.00063 | 0 | 2.43 | 0.000805 | -0.0184 |  | CFL | None | 2240 | 0.63 | 2240 | 0.63 | 1.08 | 1.28 | -0.0082143 | 2240 | 0.63 | 2240 | 0.63 | 1.08 | 1.28 | -0.00821
CFLNoneSDGEPrExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SDG | EPr | Ex | CZ15 | 2.24 | 0.00063 | 0 | 2.72 | 0.000808 | -0.00468 | 2.24 | 0.00063 | 0 | 2.72 | 0.000808 | -0.00468 |  | CFL | None | 2240 | 0.63 | 2240 | 0.63 | 1.21 | 1.28 | -0.0020893 | 2240 | 0.63 | 2240 | 0.63 | 1.21 | 1.28 | -0.00209
CFLNoneSDGEPrExIOU | Com-Iltg-dWatt-CFL_OSnone | SDG | EPr | Ex | IOU | 2.24 | 0.00063 | 0 | 2.5345 | 0.00080832 | -0.010122 | 2.24 | 0.00063 | 0 | 2.5345 | 0.00080832 | -0.010122 |  | CFL | None | 2240 | 0.63 | 2240 | 0.63 | 1.13 | 1.28 | -0.0045188 | 2240 | 0.63 | 2240 | 0.63 | 1.13 | 1.28 | -0.00452
CFLNoneSDGEPrNewCZ06 | Com-Iltg-dWatt-CFL_OSnone | SDG | EPr | New | CZ06 | 2.24 | 0.00063 | 0 | 2.46 | 0.000842 | -0.0142 | 2.24 | 0.00063 | 0 | 2.46 | 0.000842 | -0.0142 |  | CFL | None | 2240 | 0.63 | 2240 | 0.63 | 1.1 | 1.34 | -0.0063393 | 2240 | 0.63 | 2240 | 0.63 | 1.1 | 1.34 | -0.00634
CFLNoneSDGEPrNewCZ07 | Com-Iltg-dWatt-CFL_OSnone | SDG | EPr | New | CZ07 | 2.24 | 0.00063 | 0 | 2.43 | 0.000834 | -0.0132 | 2.24 | 0.00063 | 0 | 2.43 | 0.000834 | -0.0132 |  | CFL | None | 2240 | 0.63 | 2240 | 0.63 | 1.08 | 1.32 | -0.0058929 | 2240 | 0.63 | 2240 | 0.63 | 1.08 | 1.32 | -0.00589
CFLNoneSDGEPrNewCZ08 | Com-Iltg-dWatt-CFL_OSnone | SDG | EPr | New | CZ08 | 2.24 | 0.00063 | 0 | 2.5 | 0.000866 | -0.0122 | 2.24 | 0.00063 | 0 | 2.5 | 0.000866 | -0.0122 |  | CFL | None | 2240 | 0.63 | 2240 | 0.63 | 1.12 | 1.37 | -0.0054464 | 2240 | 0.63 | 2240 | 0.63 | 1.12 | 1.37 | -0.00545
CFLNoneSDGEPrNewCZ10 | Com-Iltg-dWatt-CFL_OSnone | SDG | EPr | New | CZ10 | 2.24 | 0.00063 | 0 | 2.5 | 0.000896 | -0.0147 | 2.24 | 0.00063 | 0 | 2.5 | 0.000896 | -0.0147 |  | CFL | None | 2240 | 0.63 | 2240 | 0.63 | 1.12 | 1.42 | -0.0065625 | 2240 | 0.63 | 2240 | 0.63 | 1.12 | 1.42 | -0.00656
CFLNoneSDGEPrNewCZ14 | Com-Iltg-dWatt-CFL_OSnone | SDG | EPr | New | CZ14 | 2.24 | 0.00063 | 0 | 2.45 | 0.000878 | -0.0231 | 2.24 | 0.00063 | 0 | 2.45 | 0.000878 | -0.0231 |  | CFL | None | 2240 | 0.63 | 2240 | 0.63 | 1.09 | 1.39 | -0.010312 | 2240 | 0.63 | 2240 | 0.63 | 1.09 | 1.39 | -0.0103
CFLNoneSDGEPrNewCZ15 | Com-Iltg-dWatt-CFL_OSnone | SDG | EPr | New | CZ15 | 2.24 | 0.00063 | 0 | 2.71 | 0.000908 | -0.00643 | 2.24 | 0.00063 | 0 | 2.71 | 0.000908 | -0.00643 |  | CFL | None | 2240 | 0.63 | 2240 | 0.63 | 1.21 | 1.44 | -0.0028705 | 2240 | 0.63 | 2240 | 0.63 | 1.21 | 1.44 | -0.00287
CFLNoneSDGEPrNewIOU | Com-Iltg-dWatt-CFL_OSnone | SDG | EPr | New | IOU | 2.24 | 0.00063 | 0 | 2.4589 | 0.00085691 | -0.013756 | 2.24 | 0.00063 | 0 | 2.4589 | 0.00085691 | -0.013756 |  | CFL | None | 2240 | 0.63 | 2240 | 0.63 | 1.1 | 1.36 | -0.0061409 | 2240 | 0.63 | 2240 | 0.63 | 1.1 | 1.36 | -0.00614
CFLNoneSDGERCExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SDG | ERC | Ex | CZ06 | 2.6 | 0.000728 | 0 | 2.84 | 0.000906 | -0.016 | 2.6 | 0.000728 | 0 | 2.84 | 0.000906 | -0.016 |  | CFL | None | 2600 | 0.728 | 2600 | 0.728 | 1.09 | 1.24 | -0.0061538 | 2600 | 0.728 | 2600 | 0.728 | 1.09 | 1.24 | -0.00615
CFLNoneSDGERCExCZ07 | Com-Iltg-dWatt-CFL_OSnone | SDG | ERC | Ex | CZ07 | 2.6 | 0.000728 | 0 | 2.9 | 0.000904 | -0.0128 | 2.6 | 0.000728 | 0 | 2.9 | 0.000904 | -0.0128 |  | CFL | None | 2600 | 0.728 | 2600 | 0.728 | 1.12 | 1.24 | -0.0049231 | 2600 | 0.728 | 2600 | 0.728 | 1.12 | 1.24 | -0.00492
CFLNoneSDGERCExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SDG | ERC | Ex | CZ08 | 2.6 | 0.000728 | 0 | 2.88 | 0.000916 | -0.014 | 2.6 | 0.000728 | 0 | 2.88 | 0.000916 | -0.014 |  | CFL | None | 2600 | 0.728 | 2600 | 0.728 | 1.11 | 1.26 | -0.0053846 | 2600 | 0.728 | 2600 | 0.728 | 1.11 | 1.26 | -0.00538
CFLNoneSDGERCExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SDG | ERC | Ex | CZ10 | 2.6 | 0.000728 | 0 | 2.85 | 0.000911 | -0.0164 | 2.6 | 0.000728 | 0 | 2.85 | 0.000911 | -0.0164 |  | CFL | None | 2600 | 0.728 | 2600 | 0.728 | 1.1 | 1.25 | -0.0063077 | 2600 | 0.728 | 2600 | 0.728 | 1.1 | 1.25 | -0.00631
CFLNoneSDGERCExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SDG | ERC | Ex | CZ14 | 2.6 | 0.000728 | 0 | 2.83 | 0.000925 | -0.0217 | 2.6 | 0.000728 | 0 | 2.83 | 0.000925 | -0.0217 |  | CFL | None | 2600 | 0.728 | 2600 | 0.728 | 1.09 | 1.27 | -0.0083462 | 2600 | 0.728 | 2600 | 0.728 | 1.09 | 1.27 | -0.00835
CFLNoneSDGERCExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SDG | ERC | Ex | CZ15 | 2.6 | 0.000728 | 0 | 3.06 | 0.000938 | -0.00794 | 2.6 | 0.000728 | 0 | 3.06 | 0.000938 | -0.00794 |  | CFL | None | 2600 | 0.728 | 2600 | 0.728 | 1.18 | 1.29 | -0.0030538 | 2600 | 0.728 | 2600 | 0.728 | 1.18 | 1.29 | -0.00305
CFLNoneSDGERCExIOU | Com-Iltg-dWatt-CFL_OSnone | SDG | ERC | Ex | IOU | 2.6 | 0.000728 | 0 | 2.8795 | 0.00090731 | -0.014262 | 2.6 | 0.000728 | 0 | 2.8795 | 0.00090731 | -0.014262 |  | CFL | None | 2600 | 0.728 | 2600 | 0.728 | 1.11 | 1.25 | -0.0054854 | 2600 | 0.728 | 2600 | 0.728 | 1.11 | 1.25 | -0.00549
CFLNoneSDGERCNewCZ06 | Com-Iltg-dWatt-CFL_OSnone | SDG | ERC | New | CZ06 | 2.6 | 0.000728 | 0 | 2.96 | 0.000932 | -0.0177 | 2.6 | 0.000728 | 0 | 2.96 | 0.000932 | -0.0177 |  | CFL | None | 2600 | 0.728 | 2600 | 0.728 | 1.14 | 1.28 | -0.0068077 | 2600 | 0.728 | 2600 | 0.728 | 1.14 | 1.28 | -0.00681
CFLNoneSDGERCNewCZ07 | Com-Iltg-dWatt-CFL_OSnone | SDG | ERC | New | CZ07 | 2.6 | 0.000728 | 0 | 2.97 | 0.000918 | -0.0137 | 2.6 | 0.000728 | 0 | 2.97 | 0.000918 | -0.0137 |  | CFL | None | 2600 | 0.728 | 2600 | 0.728 | 1.14 | 1.26 | -0.0052692 | 2600 | 0.728 | 2600 | 0.728 | 1.14 | 1.26 | -0.00527
CFLNoneSDGERCNewCZ08 | Com-Iltg-dWatt-CFL_OSnone | SDG | ERC | New | CZ08 | 2.6 | 0.000728 | 0 | 2.99 | 0.000954 | -0.0154 | 2.6 | 0.000728 | 0 | 2.99 | 0.000954 | -0.0154 |  | CFL | None | 2600 | 0.728 | 2600 | 0.728 | 1.15 | 1.31 | -0.0059231 | 2600 | 0.728 | 2600 | 0.728 | 1.15 | 1.31 | -0.00592
CFLNoneSDGERCNewCZ10 | Com-Iltg-dWatt-CFL_OSnone | SDG | ERC | New | CZ10 | 2.6 | 0.000728 | 0 | 3.01 | 0.000997 | -0.0175 | 2.6 | 0.000728 | 0 | 3.01 | 0.000997 | -0.0175 |  | CFL | None | 2600 | 0.728 | 2600 | 0.728 | 1.16 | 1.37 | -0.0067308 | 2600 | 0.728 | 2600 | 0.728 | 1.16 | 1.37 | -0.00673
CFLNoneSDGERCNewCZ14 | Com-Iltg-dWatt-CFL_OSnone | SDG | ERC | New | CZ14 | 2.6 | 0.000728 | 0 | 2.97 | 0.000982 | -0.0254 | 2.6 | 0.000728 | 0 | 2.97 | 0.000982 | -0.0254 |  | CFL | None | 2600 | 0.728 | 2600 | 0.728 | 1.14 | 1.35 | -0.0097692 | 2600 | 0.728 | 2600 | 0.728 | 1.14 | 1.35 | -0.00977
CFLNoneSDGERCNewCZ15 | Com-Iltg-dWatt-CFL_OSnone | SDG | ERC | New | CZ15 | 2.6 | 0.000728 | 0 | 3.28 | 0.000998 | -0.00877 | 2.6 | 0.000728 | 0 | 3.28 | 0.000998 | -0.00877 |  | CFL | None | 2600 | 0.728 | 2600 | 0.728 | 1.26 | 1.37 | -0.0033731 | 2600 | 0.728 | 2600 | 0.728 | 1.26 | 1.37 | -0.00337
CFLNoneSDGERCNewIOU | Com-Iltg-dWatt-CFL_OSnone | SDG | ERC | New | IOU | 2.6 | 0.000728 | 0 | 2.9844 | 0.00094715 | -0.01532 | 2.6 | 0.000728 | 0 | 2.9844 | 0.00094715 | -0.01532 |  | CFL | None | 2600 | 0.728 | 2600 | 0.728 | 1.15 | 1.3 | -0.0058923 | 2600 | 0.728 | 2600 | 0.728 | 1.15 | 1.3 | -0.00589
CFLNoneSDGESeExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SDG | ESe | Ex | CZ06 | 2.33 | 0.000715 | 0 | 2.6 | 0.000907 | -0.0134 | 2.33 | 0.000715 | 0 | 2.6 | 0.000907 | -0.0134 |  | CFL | None | 2330 | 0.715 | 2330 | 0.715 | 1.12 | 1.27 | -0.0057511 | 2330 | 0.715 | 2330 | 0.715 | 1.12 | 1.27 | -0.00575
CFLNoneSDGESeExCZ07 | Com-Iltg-dWatt-CFL_OSnone | SDG | ESe | Ex | CZ07 | 2.33 | 0.000715 | 0 | 2.59 | 0.00089 | -0.0118 | 2.33 | 0.000715 | 0 | 2.59 | 0.00089 | -0.0118 |  | CFL | None | 2330 | 0.715 | 2330 | 0.715 | 1.11 | 1.24 | -0.0050644 | 2330 | 0.715 | 2330 | 0.715 | 1.11 | 1.24 | -0.00506
CFLNoneSDGESeExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SDG | ESe | Ex | CZ08 | 2.33 | 0.000715 | 0 | 2.63 | 0.000902 | -0.0114 | 2.33 | 0.000715 | 0 | 2.63 | 0.000902 | -0.0114 |  | CFL | None | 2330 | 0.715 | 2330 | 0.715 | 1.13 | 1.26 | -0.0048927 | 2330 | 0.715 | 2330 | 0.715 | 1.13 | 1.26 | -0.00489
CFLNoneSDGESeExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SDG | ESe | Ex | CZ10 | 2.33 | 0.000715 | 0 | 2.61 | 0.000899 | -0.0143 | 2.33 | 0.000715 | 0 | 2.61 | 0.000899 | -0.0143 |  | CFL | None | 2330 | 0.715 | 2330 | 0.715 | 1.12 | 1.26 | -0.0061373 | 2330 | 0.715 | 2330 | 0.715 | 1.12 | 1.26 | -0.00614
CFLNoneSDGESeExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SDG | ESe | Ex | CZ14 | 2.33 | 0.000715 | 0 | 2.53 | 0.000868 | -0.0223 | 2.33 | 0.000715 | 0 | 2.53 | 0.000868 | -0.0223 |  | CFL | None | 2330 | 0.715 | 2330 | 0.715 | 1.09 | 1.21 | -0.0095708 | 2330 | 0.715 | 2330 | 0.715 | 1.09 | 1.21 | -0.00957
CFLNoneSDGESeExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SDG | ESe | Ex | CZ15 | 2.33 | 0.000715 | 0 | 2.84 | 0.000898 | -0.00636 | 2.33 | 0.000715 | 0 | 2.84 | 0.000898 | -0.00636 |  | CFL | None | 2330 | 0.715 | 2330 | 0.715 | 1.22 | 1.26 | -0.0027296 | 2330 | 0.715 | 2330 | 0.715 | 1.22 | 1.26 | -0.00273
CFLNoneSDGESeExIOU | Com-Iltg-dWatt-CFL_OSnone | SDG | ESe | Ex | IOU | 2.33 | 0.000715 | 0 | 2.5993 | 0.00089424 | -0.012751 | 2.33 | 0.000715 | 0 | 2.5993 | 0.00089424 | -0.012751 |  | CFL | None | 2330 | 0.715 | 2330 | 0.715 | 1.12 | 1.25 | -0.0054724 | 2330 | 0.715 | 2330 | 0.715 | 1.12 | 1.25 | -0.00547
CFLNoneSDGESeNewCZ06 | Com-Iltg-dWatt-CFL_OSnone | SDG | ESe | New | CZ06 | 2.33 | 0.000715 | 0 | 2.56 | 0.000941 | -0.0173 | 2.33 | 0.000715 | 0 | 2.56 | 0.000941 | -0.0173 |  | CFL | None | 2330 | 0.715 | 2330 | 0.715 | 1.1 | 1.32 | -0.0074249 | 2330 | 0.715 | 2330 | 0.715 | 1.1 | 1.32 | -0.00742
CFLNoneSDGESeNewCZ07 | Com-Iltg-dWatt-CFL_OSnone | SDG | ESe | New | CZ07 | 2.33 | 0.000715 | 0 | 2.52 | 0.000919 | -0.015 | 2.33 | 0.000715 | 0 | 2.52 | 0.000919 | -0.015 |  | CFL | None | 2330 | 0.715 | 2330 | 0.715 | 1.08 | 1.29 | -0.0064378 | 2330 | 0.715 | 2330 | 0.715 | 1.08 | 1.29 | -0.00644
CFLNoneSDGESeNewCZ08 | Com-Iltg-dWatt-CFL_OSnone | SDG | ESe | New | CZ08 | 2.33 | 0.000715 | 0 | 2.59 | 0.000952 | -0.0142 | 2.33 | 0.000715 | 0 | 2.59 | 0.000952 | -0.0142 |  | CFL | None | 2330 | 0.715 | 2330 | 0.715 | 1.11 | 1.33 | -0.0060944 | 2330 | 0.715 | 2330 | 0.715 | 1.11 | 1.33 | -0.00609
CFLNoneSDGESeNewCZ10 | Com-Iltg-dWatt-CFL_OSnone | SDG | ESe | New | CZ10 | 2.33 | 0.000715 | 0 | 2.61 | 0.000995 | -0.0179 | 2.33 | 0.000715 | 0 | 2.61 | 0.000995 | -0.0179 |  | CFL | None | 2330 | 0.715 | 2330 | 0.715 | 1.12 | 1.39 | -0.0076824 | 2330 | 0.715 | 2330 | 0.715 | 1.12 | 1.39 | -0.00768
CFLNoneSDGESeNewCZ14 | Com-Iltg-dWatt-CFL_OSnone | SDG | ESe | New | CZ14 | 2.33 | 0.000715 | 0 | 2.57 | 0.000978 | -0.0261 | 2.33 | 0.000715 | 0 | 2.57 | 0.000978 | -0.0261 |  | CFL | None | 2330 | 0.715 | 2330 | 0.715 | 1.1 | 1.37 | -0.011202 | 2330 | 0.715 | 2330 | 0.715 | 1.1 | 1.37 | -0.0112
CFLNoneSDGESeNewCZ15 | Com-Iltg-dWatt-CFL_OSnone | SDG | ESe | New | CZ15 | 2.33 | 0.000715 | 0 | 2.87 | 0.00099 | -0.00783 | 2.33 | 0.000715 | 0 | 2.87 | 0.00099 | -0.00783 |  | CFL | None | 2330 | 0.715 | 2330 | 0.715 | 1.23 | 1.38 | -0.0033605 | 2330 | 0.715 | 2330 | 0.715 | 1.23 | 1.38 | -0.00336
CFLNoneSDGESeNewIOU | Com-Iltg-dWatt-CFL_OSnone | SDG | ESe | New | IOU | 2.33 | 0.000715 | 0 | 2.5564 | 0.00094733 | -0.016096 | 2.33 | 0.000715 | 0 | 2.5564 | 0.00094733 | -0.016096 |  | CFL | None | 2330 | 0.715 | 2330 | 0.715 | 1.1 | 1.32 | -0.0069081 | 2330 | 0.715 | 2330 | 0.715 | 1.1 | 1.32 | -0.00691
CFLNoneSDGEUnExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SDG | EUn | Ex | CZ06 | 2.37 | 0.000669 | 0 | 2.7 | 0.000846 | -0.01 | 2.37 | 0.000669 | 0 | 2.7 | 0.000846 | -0.01 |  | CFL | None | 2370 | 0.669 | 2370 | 0.669 | 1.14 | 1.26 | -0.0042194 | 2370 | 0.669 | 2370 | 0.669 | 1.14 | 1.26 | -0.00422
CFLNoneSDGEUnExCZ07 | Com-Iltg-dWatt-CFL_OSnone | SDG | EUn | Ex | CZ07 | 2.37 | 0.000669 | 0 | 2.69 | 0.000838 | -0.0089504 | 2.37 | 0.000669 | 0 | 2.69 | 0.000838 | -0.0089504 |  | CFL | None | 2370 | 0.669 | 2370 | 0.669 | 1.14 | 1.25 | -0.0037765 | 2370 | 0.669 | 2370 | 0.669 | 1.14 | 1.25 | -0.00378
CFLNoneSDGEUnExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SDG | EUn | Ex | CZ08 | 2.37 | 0.000669 | 0 | 2.71 | 0.000848 | -0.00966 | 2.37 | 0.000669 | 0 | 2.71 | 0.000848 | -0.00966 |  | CFL | None | 2370 | 0.669 | 2370 | 0.669 | 1.14 | 1.27 | -0.0040759 | 2370 | 0.669 | 2370 | 0.669 | 1.14 | 1.27 | -0.00408
CFLNoneSDGEUnExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SDG | EUn | Ex | CZ10 | 2.37 | 0.000669 | 0 | 2.71 | 0.000862 | -0.0114 | 2.37 | 0.000669 | 0 | 2.71 | 0.000862 | -0.0114 |  | CFL | None | 2370 | 0.669 | 2370 | 0.669 | 1.14 | 1.29 | -0.0048101 | 2370 | 0.669 | 2370 | 0.669 | 1.14 | 1.29 | -0.00481
CFLNoneSDGEUnExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SDG | EUn | Ex | CZ14 | 2.37 | 0.000669 | 0 | 2.68 | 0.000851 | -0.0157 | 2.37 | 0.000669 | 0 | 2.68 | 0.000851 | -0.0157 |  | CFL | None | 2370 | 0.669 | 2370 | 0.669 | 1.13 | 1.27 | -0.0066245 | 2370 | 0.669 | 2370 | 0.669 | 1.13 | 1.27 | -0.00662
CFLNoneSDGEUnExIOU | Com-Iltg-dWatt-CFL_OSnone | SDG | EUn | Ex | IOU | 2.37 | 0.000669 | 0 | 2.6949 | 0.00084384 | -0.0095729 | 2.37 | 0.000669 | 0 | 2.6949 | 0.00084384 | -0.0095729 |  | CFL | None | 2370 | 0.669 | 2370 | 0.669 | 1.14 | 1.26 | -0.0040392 | 2370 | 0.669 | 2370 | 0.669 | 1.14 | 1.26 | -0.00404
CFLNoneSDGEUnNewCZ06 | Com-Iltg-dWatt-CFL_OSnone | SDG | EUn | New | CZ06 | 2.37 | 0.000669 | 0 | 2.73 | 0.000842 | -0.00769 | 2.37 | 0.000669 | 0 | 2.73 | 0.000842 | -0.00769 |  | CFL | None | 2370 | 0.669 | 2370 | 0.669 | 1.15 | 1.26 | -0.0032447 | 2370 | 0.669 | 2370 | 0.669 | 1.15 | 1.26 | -0.00324
CFLNoneSDGEUnNewCZ07 | Com-Iltg-dWatt-CFL_OSnone | SDG | EUn | New | CZ07 | 2.37 | 0.000669 | 0 | 2.7 | 0.000836 | -0.00686 | 2.37 | 0.000669 | 0 | 2.7 | 0.000836 | -0.00686 |  | CFL | None | 2370 | 0.669 | 2370 | 0.669 | 1.14 | 1.25 | -0.0028945 | 2370 | 0.669 | 2370 | 0.669 | 1.14 | 1.25 | -0.00289
CFLNoneSDGEUnNewCZ08 | Com-Iltg-dWatt-CFL_OSnone | SDG | EUn | New | CZ08 | 2.37 | 0.000669 | 0 | 2.75 | 0.000851 | -0.00679 | 2.37 | 0.000669 | 0 | 2.75 | 0.000851 | -0.00679 |  | CFL | None | 2370 | 0.669 | 2370 | 0.669 | 1.16 | 1.27 | -0.002865 | 2370 | 0.669 | 2370 | 0.669 | 1.16 | 1.27 | -0.00287
CFLNoneSDGEUnNewCZ10 | Com-Iltg-dWatt-CFL_OSnone | SDG | EUn | New | CZ10 | 2.37 | 0.000669 | 0 | 2.77 | 0.000878 | -0.00786 | 2.37 | 0.000669 | 0 | 2.77 | 0.000878 | -0.00786 |  | CFL | None | 2370 | 0.669 | 2370 | 0.669 | 1.17 | 1.31 | -0.0033165 | 2370 | 0.669 | 2370 | 0.669 | 1.17 | 1.31 | -0.00332
CFLNoneSDGEUnNewCZ14 | Com-Iltg-dWatt-CFL_OSnone | SDG | EUn | New | CZ14 | 2.37 | 0.000669 | 0 | 2.66 | 0.000811 | -0.013 | 2.37 | 0.000669 | 0 | 2.66 | 0.000811 | -0.013 |  | CFL | None | 2370 | 0.669 | 2370 | 0.669 | 1.12 | 1.21 | -0.0054852 | 2370 | 0.669 | 2370 | 0.669 | 1.12 | 1.21 | -0.00549
CFLNoneSDGEUnNewCZ15 | Com-Iltg-dWatt-CFL_OSnone | SDG | EUn | New | CZ15 | 2.37 | 0.000669 | 0 | 2.9 | 0.000886 | -0.00362 | 2.37 | 0.000669 | 0 | 2.9 | 0.000886 | -0.00362 |  | CFL | None | 2370 | 0.669 | 2370 | 0.669 | 1.22 | 1.32 | -0.0015274 | 2370 | 0.669 | 2370 | 0.669 | 1.22 | 1.32 | -0.00153
CFLNoneSDGEUnNewIOU | Com-Iltg-dWatt-CFL_OSnone | SDG | EUn | New | IOU | 2.37 | 0.000669 | 0 | 2.7168 | 0.0008459 | -0.0071306 | 2.37 | 0.000669 | 0 | 2.7168 | 0.0008459 | -0.0071306 |  | CFL | None | 2370 | 0.669 | 2370 | 0.669 | 1.15 | 1.26 | -0.0030087 | 2370 | 0.669 | 2370 | 0.669 | 1.15 | 1.26 | -0.00301
CFLNoneSDGGroExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SDG | Gro | Ex | CZ06 | 3.89 | 0.000495 | 0 | 3.88 | 0.000611 | -0.0533 | 3.89 | 0.000495 | 0 | 3.88 | 0.000611 | -0.0533 |  | CFL | None | 3890 | 0.495 | 3890 | 0.495 | 0.997 | 1.23 | -0.013702 | 3890 | 0.495 | 3890 | 0.495 | 0.997 | 1.23 | -0.0137
CFLNoneSDGGroExCZ07 | Com-Iltg-dWatt-CFL_OSnone | SDG | Gro | Ex | CZ07 | 3.89 | 0.000495 | 0 | 3.83 | 0.000602 | -0.0572 | 3.89 | 0.000495 | 0 | 3.83 | 0.000602 | -0.0572 |  | CFL | None | 3890 | 0.495 | 3890 | 0.495 | 0.985 | 1.22 | -0.014704 | 3890 | 0.495 | 3890 | 0.495 | 0.985 | 1.22 | -0.0147
CFLNoneSDGGroExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SDG | Gro | Ex | CZ08 | 3.89 | 0.000495 | 0 | 3.97 | 0.000627 | -0.0486 | 3.89 | 0.000495 | 0 | 3.97 | 0.000627 | -0.0486 |  | CFL | None | 3890 | 0.495 | 3890 | 0.495 | 1.02 | 1.27 | -0.012494 | 3890 | 0.495 | 3890 | 0.495 | 1.02 | 1.27 | -0.0125
CFLNoneSDGGroExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SDG | Gro | Ex | CZ10 | 3.89 | 0.000495 | 0 | 4.04 | 0.000658 | -0.0459 | 3.89 | 0.000495 | 0 | 4.04 | 0.000658 | -0.0459 |  | CFL | None | 3890 | 0.495 | 3890 | 0.495 | 1.04 | 1.33 | -0.011799 | 3890 | 0.495 | 3890 | 0.495 | 1.04 | 1.33 | -0.0118
CFLNoneSDGGroExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SDG | Gro | Ex | CZ14 | 3.89 | 0.000495 | 0 | 4.03 | 0.000669 | -0.0463 | 3.89 | 0.000495 | 0 | 4.03 | 0.000669 | -0.0463 |  | CFL | None | 3890 | 0.495 | 3890 | 0.495 | 1.04 | 1.35 | -0.011902 | 3890 | 0.495 | 3890 | 0.495 | 1.04 | 1.35 | -0.0119
CFLNoneSDGGroExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SDG | Gro | Ex | CZ15 | 3.89 | 0.000495 | 0 | 4.36 | 0.000656 | -0.0266 | 3.89 | 0.000495 | 0 | 4.36 | 0.000656 | -0.0266 |  | CFL | None | 3890 | 0.495 | 3890 | 0.495 | 1.12 | 1.33 | -0.006838 | 3890 | 0.495 | 3890 | 0.495 | 1.12 | 1.33 | -0.00684
CFLNoneSDGGroExIOU | Com-Iltg-dWatt-CFL_OSnone | SDG | Gro | Ex | IOU | 3.89 | 0.000495 | 0 | 3.8946 | 0.00061863 | -0.053622 | 3.89 | 0.000495 | 0 | 3.8946 | 0.00061863 | -0.053622 |  | CFL | None | 3890 | 0.495 | 3890 | 0.495 | 1 | 1.25 | -0.013784 | 3890 | 0.495 | 3890 | 0.495 | 1 | 1.25 | -0.0138
CFLNoneSDGGroNewCZ06 | Com-Iltg-dWatt-CFL_OSnone | SDG | Gro | New | CZ06 | 3.89 | 0.000495 | 0 | 4.06 | 0.000624 | -0.0443 | 3.89 | 0.000495 | 0 | 4.06 | 0.000624 | -0.0443 |  | CFL | None | 3890 | 0.495 | 3890 | 0.495 | 1.04 | 1.26 | -0.011388 | 3890 | 0.495 | 3890 | 0.495 | 1.04 | 1.26 | -0.0114
CFLNoneSDGGroNewCZ07 | Com-Iltg-dWatt-CFL_OSnone | SDG | Gro | New | CZ07 | 3.89 | 0.000495 | 0 | 4.03 | 0.000609 | -0.0463 | 3.89 | 0.000495 | 0 | 4.03 | 0.000609 | -0.0463 |  | CFL | None | 3890 | 0.495 | 3890 | 0.495 | 1.04 | 1.23 | -0.011902 | 3890 | 0.495 | 3890 | 0.495 | 1.04 | 1.23 | -0.0119
CFLNoneSDGGroNewCZ08 | Com-Iltg-dWatt-CFL_OSnone | SDG | Gro | New | CZ08 | 3.89 | 0.000495 | 0 | 4.11 | 0.000635 | -0.0387 | 3.89 | 0.000495 | 0 | 4.11 | 0.000635 | -0.0387 |  | CFL | None | 3890 | 0.495 | 3890 | 0.495 | 1.06 | 1.28 | -0.0099486 | 3890 | 0.495 | 3890 | 0.495 | 1.06 | 1.28 | -0.00995
CFLNoneSDGGroNewCZ10 | Com-Iltg-dWatt-CFL_OSnone | SDG | Gro | New | CZ10 | 3.89 | 0.000495 | 0 | 4.16 | 0.000698 | -0.0404 | 3.89 | 0.000495 | 0 | 4.16 | 0.000698 | -0.0404 |  | CFL | None | 3890 | 0.495 | 3890 | 0.495 | 1.07 | 1.41 | -0.010386 | 3890 | 0.495 | 3890 | 0.495 | 1.07 | 1.41 | -0.0104
CFLNoneSDGGroNewCZ14 | Com-Iltg-dWatt-CFL_OSnone | SDG | Gro | New | CZ14 | 3.89 | 0.000495 | 0 | 4.17 | 0.00068 | -0.0443 | 3.89 | 0.000495 | 0 | 4.17 | 0.00068 | -0.0443 |  | CFL | None | 3890 | 0.495 | 3890 | 0.495 | 1.07 | 1.37 | -0.011388 | 3890 | 0.495 | 3890 | 0.495 | 1.07 | 1.37 | -0.0114
CFLNoneSDGGroNewCZ15 | Com-Iltg-dWatt-CFL_OSnone | SDG | Gro | New | CZ15 | 3.89 | 0.000495 | 0 | 4.5 | 0.000691 | -0.0229 | 3.89 | 0.000495 | 0 | 4.5 | 0.000691 | -0.0229 |  | CFL | None | 3890 | 0.495 | 3890 | 0.495 | 1.16 | 1.4 | -0.0058869 | 3890 | 0.495 | 3890 | 0.495 | 1.16 | 1.4 | -0.00589
CFLNoneSDGGroNewIOU | Com-Iltg-dWatt-CFL_OSnone | SDG | Gro | New | IOU | 3.89 | 0.000495 | 0 | 4.07 | 0.00063499 | -0.044363 | 3.89 | 0.000495 | 0 | 4.07 | 0.00063499 | -0.044363 |  | CFL | None | 3890 | 0.495 | 3890 | 0.495 | 1.05 | 1.28 | -0.011404 | 3890 | 0.495 | 3890 | 0.495 | 1.05 | 1.28 | -0.0114
CFLNoneSDGHspExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SDG | Hsp | Ex | CZ06 | 4.2 | 0.000717 | 0 | 4.8 | 0.000887 | -0.0226 | 4.2 | 0.000717 | 0 | 4.8 | 0.000887 | -0.0226 |  | CFL | None | 4200 | 0.717 | 4200 | 0.717 | 1.14 | 1.24 | -0.005381 | 4200 | 0.717 | 4200 | 0.717 | 1.14 | 1.24 | -0.00538
CFLNoneSDGHspExCZ07 | Com-Iltg-dWatt-CFL_OSnone | SDG | Hsp | Ex | CZ07 | 4.2 | 0.000717 | 0 | 4.8 | 0.000879 | -0.0207 | 4.2 | 0.000717 | 0 | 4.8 | 0.000879 | -0.0207 |  | CFL | None | 4200 | 0.717 | 4200 | 0.717 | 1.14 | 1.23 | -0.0049286 | 4200 | 0.717 | 4200 | 0.717 | 1.14 | 1.23 | -0.00493
CFLNoneSDGHspExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SDG | Hsp | Ex | CZ08 | 4.2 | 0.000717 | 0 | 4.83 | 0.000885 | -0.0222 | 4.2 | 0.000717 | 0 | 4.83 | 0.000885 | -0.0222 |  | CFL | None | 4200 | 0.717 | 4200 | 0.717 | 1.15 | 1.23 | -0.0052857 | 4200 | 0.717 | 4200 | 0.717 | 1.15 | 1.23 | -0.00529
CFLNoneSDGHspExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SDG | Hsp | Ex | CZ10 | 4.2 | 0.000717 | 0 | 4.82 | 0.000907 | -0.0237 | 4.2 | 0.000717 | 0 | 4.82 | 0.000907 | -0.0237 |  | CFL | None | 4200 | 0.717 | 4200 | 0.717 | 1.15 | 1.26 | -0.0056429 | 4200 | 0.717 | 4200 | 0.717 | 1.15 | 1.26 | -0.00564
CFLNoneSDGHspExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SDG | Hsp | Ex | CZ14 | 4.2 | 0.000717 | 0 | 4.76 | 0.000901 | -0.0291 | 4.2 | 0.000717 | 0 | 4.76 | 0.000901 | -0.0291 |  | CFL | None | 4200 | 0.717 | 4200 | 0.717 | 1.13 | 1.26 | -0.0069286 | 4200 | 0.717 | 4200 | 0.717 | 1.13 | 1.26 | -0.00693
CFLNoneSDGHspExIOU | Com-Iltg-dWatt-CFL_OSnone | SDG | Hsp | Ex | IOU | 4.2 | 0.000717 | 0 | 4.8041 | 0.00088341 | -0.021239 | 4.2 | 0.000717 | 0 | 4.8041 | 0.00088341 | -0.021239 |  | CFL | None | 4200 | 0.717 | 4200 | 0.717 | 1.14 | 1.23 | -0.005057 | 4200 | 0.717 | 4200 | 0.717 | 1.14 | 1.23 | -0.00506
CFLNoneSDGHspNewCZ06 | Com-Iltg-dWatt-CFL_OSnone | SDG | Hsp | New | CZ06 | 4.2 | 0.000717 | 0 | 4.59 | 0.000857 | -0.024 | 4.2 | 0.000717 | 0 | 4.59 | 0.000857 | -0.024 |  | CFL | None | 4200 | 0.717 | 4200 | 0.717 | 1.09 | 1.2 | -0.0057143 | 4200 | 0.717 | 4200 | 0.717 | 1.09 | 1.2 | -0.00571
CFLNoneSDGHspNewCZ07 | Com-Iltg-dWatt-CFL_OSnone | SDG | Hsp | New | CZ07 | 4.2 | 0.000717 | 0 | 4.61 | 0.000852 | -0.0205 | 4.2 | 0.000717 | 0 | 4.61 | 0.000852 | -0.0205 |  | CFL | None | 4200 | 0.717 | 4200 | 0.717 | 1.1 | 1.19 | -0.004881 | 4200 | 0.717 | 4200 | 0.717 | 1.1 | 1.19 | -0.00488
CFLNoneSDGHspNewCZ08 | Com-Iltg-dWatt-CFL_OSnone | SDG | Hsp | New | CZ08 | 4.2 | 0.000717 | 0 | 4.64 | 0.000861 | -0.0222 | 4.2 | 0.000717 | 0 | 4.64 | 0.000861 | -0.0222 |  | CFL | None | 4200 | 0.717 | 4200 | 0.717 | 1.1 | 1.2 | -0.0052857 | 4200 | 0.717 | 4200 | 0.717 | 1.1 | 1.2 | -0.00529
CFLNoneSDGHspNewCZ10 | Com-Iltg-dWatt-CFL_OSnone | SDG | Hsp | New | CZ10 | 4.2 | 0.000717 | 0 | 4.64 | 0.000888 | -0.025 | 4.2 | 0.000717 | 0 | 4.64 | 0.000888 | -0.025 |  | CFL | None | 4200 | 0.717 | 4200 | 0.717 | 1.1 | 1.24 | -0.0059524 | 4200 | 0.717 | 4200 | 0.717 | 1.1 | 1.24 | -0.00595
CFLNoneSDGHspNewCZ14 | Com-Iltg-dWatt-CFL_OSnone | SDG | Hsp | New | CZ14 | 4.2 | 0.000717 | 0 | 4.57 | 0.000881 | -0.0311 | 4.2 | 0.000717 | 0 | 4.57 | 0.000881 | -0.0311 |  | CFL | None | 4200 | 0.717 | 4200 | 0.717 | 1.09 | 1.23 | -0.0074048 | 4200 | 0.717 | 4200 | 0.717 | 1.09 | 1.23 | -0.0074
CFLNoneSDGHspNewCZ15 | Com-Iltg-dWatt-CFL_OSnone | SDG | Hsp | New | CZ15 | 4.2 | 0.000717 | 0 | 4.86 | 0.000894 | -0.0202 | 4.2 | 0.000717 | 0 | 4.86 | 0.000894 | -0.0202 |  | CFL | None | 4200 | 0.717 | 4200 | 0.717 | 1.16 | 1.25 | -0.0048095 | 4200 | 0.717 | 4200 | 0.717 | 1.16 | 1.25 | -0.00481
CFLNoneSDGHspNewIOU | Com-Iltg-dWatt-CFL_OSnone | SDG | Hsp | New | IOU | 4.2 | 0.000717 | 0 | 4.615 | 0.0008576 | -0.021301 | 4.2 | 0.000717 | 0 | 4.615 | 0.0008576 | -0.021301 |  | CFL | None | 4200 | 0.717 | 4200 | 0.717 | 1.1 | 1.2 | -0.0050715 | 4200 | 0.717 | 4200 | 0.717 | 1.1 | 1.2 | -0.00507
CFLNoneSDGHtlExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SDG | Htl | Ex | CZ06 | 1.67 | 0.000199 | 0 | 1.82 | 0.000249 | -0.00339 | 1.67 | 0.000199 | 0 | 1.82 | 0.000249 | -0.00339 |  | CFL | None | 1670 | 0.199 | 1670 | 0.199 | 1.09 | 1.25 | -0.0020299 | 1670 | 0.199 | 1670 | 0.199 | 1.09 | 1.25 | -0.00203
CFLNoneSDGHtlExCZ07 | Com-Iltg-dWatt-CFL_OSnone | SDG | Htl | Ex | CZ07 | 1.67 | 0.000199 | 0 | 1.85 | 0.000247 | -0.00264 | 1.67 | 0.000199 | 0 | 1.85 | 0.000247 | -0.00264 |  | CFL | None | 1670 | 0.199 | 1670 | 0.199 | 1.11 | 1.24 | -0.0015808 | 1670 | 0.199 | 1670 | 0.199 | 1.11 | 1.24 | -0.00158
CFLNoneSDGHtlExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SDG | Htl | Ex | CZ08 | 1.67 | 0.000199 | 0 | 1.84 | 0.00025 | -0.00306 | 1.67 | 0.000199 | 0 | 1.84 | 0.00025 | -0.00306 |  | CFL | None | 1670 | 0.199 | 1670 | 0.199 | 1.1 | 1.26 | -0.0018323 | 1670 | 0.199 | 1670 | 0.199 | 1.1 | 1.26 | -0.00183
CFLNoneSDGHtlExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SDG | Htl | Ex | CZ10 | 1.67 | 0.000199 | 0 | 1.8197 | 0.000255 | -0.00354 | 1.67 | 0.000199 | 0 | 1.8197 | 0.000255 | -0.00354 |  | CFL | None | 1670 | 0.199 | 1670 | 0.199 | 1.09 | 1.28 | -0.0021198 | 1670 | 0.199 | 1670 | 0.199 | 1.09 | 1.28 | -0.00212
CFLNoneSDGHtlExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SDG | Htl | Ex | CZ14 | 1.67 | 0.000199 | 0 | 1.74 | 0.000255 | -0.00483 | 1.67 | 0.000199 | 0 | 1.74 | 0.000255 | -0.00483 |  | CFL | None | 1670 | 0.199 | 1670 | 0.199 | 1.04 | 1.28 | -0.0028922 | 1670 | 0.199 | 1670 | 0.199 | 1.04 | 1.28 | -0.00289
CFLNoneSDGHtlExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SDG | Htl | Ex | CZ15 | 1.67 | 0.000199 | 0 | 1.95 | 0.000257 | -0.00204 | 1.67 | 0.000199 | 0 | 1.95 | 0.000257 | -0.00204 |  | CFL | None | 1670 | 0.199 | 1670 | 0.199 | 1.17 | 1.29 | -0.0012216 | 1670 | 0.199 | 1670 | 0.199 | 1.17 | 1.29 | -0.00122
CFLNoneSDGHtlExIOU | Com-Iltg-dWatt-CFL_OSnone | SDG | Htl | Ex | IOU | 1.67 | 0.000199 | 0 | 1.8458 | 0.00024805 | -0.0027762 | 1.67 | 0.000199 | 0 | 1.8458 | 0.00024805 | -0.0027762 |  | CFL | None | 1670 | 0.199 | 1670 | 0.199 | 1.11 | 1.25 | -0.0016624 | 1670 | 0.199 | 1670 | 0.199 | 1.11 | 1.25 | -0.00166
CFLNoneSDGHtlNewCZ06 | Com-Iltg-dWatt-CFL_OSnone | SDG | Htl | New | CZ06 | 1.67 | 0.000199 | 0 | 1.81 | 0.000254 | -0.00316 | 1.67 | 0.000199 | 0 | 1.81 | 0.000254 | -0.00316 |  | CFL | None | 1670 | 0.199 | 1670 | 0.199 | 1.08 | 1.28 | -0.0018922 | 1670 | 0.199 | 1670 | 0.199 | 1.08 | 1.28 | -0.00189
CFLNoneSDGHtlNewCZ07 | Com-Iltg-dWatt-CFL_OSnone | SDG | Htl | New | CZ07 | 1.67 | 0.000199 | 0 | 1.84 | 0.00025 | -0.00227 | 1.67 | 0.000199 | 0 | 1.84 | 0.00025 | -0.00227 |  | CFL | None | 1670 | 0.199 | 1670 | 0.199 | 1.1 | 1.26 | -0.0013593 | 1670 | 0.199 | 1670 | 0.199 | 1.1 | 1.26 | -0.00136
CFLNoneSDGHtlNewCZ08 | Com-Iltg-dWatt-CFL_OSnone | SDG | Htl | New | CZ08 | 1.67 | 0.000199 | 0 | 1.83 | 0.000256 | -0.00278 | 1.67 | 0.000199 | 0 | 1.83 | 0.000256 | -0.00278 |  | CFL | None | 1670 | 0.199 | 1670 | 0.199 | 1.1 | 1.29 | -0.0016647 | 1670 | 0.199 | 1670 | 0.199 | 1.1 | 1.29 | -0.00166
CFLNoneSDGHtlNewCZ10 | Com-Iltg-dWatt-CFL_OSnone | SDG | Htl | New | CZ10 | 1.67 | 0.000199 | 0 | 1.81 | 0.000268 | -0.00348 | 1.67 | 0.000199 | 0 | 1.81 | 0.000268 | -0.00348 |  | CFL | None | 1670 | 0.199 | 1670 | 0.199 | 1.08 | 1.35 | -0.0020838 | 1670 | 0.199 | 1670 | 0.199 | 1.08 | 1.35 | -0.00208
CFLNoneSDGHtlNewCZ14 | Com-Iltg-dWatt-CFL_OSnone | SDG | Htl | New | CZ14 | 1.67 | 0.000199 | 0 | 1.71 | 0.000263 | -0.00522 | 1.67 | 0.000199 | 0 | 1.71 | 0.000263 | -0.00522 |  | CFL | None | 1670 | 0.199 | 1670 | 0.199 | 1.02 | 1.32 | -0.0031257 | 1670 | 0.199 | 1670 | 0.199 | 1.02 | 1.32 | -0.00313
CFLNoneSDGHtlNewCZ15 | Com-Iltg-dWatt-CFL_OSnone | SDG | Htl | New | CZ15 | 1.67 | 0.000199 | 0 | 1.96 | 0.000267 | -0.00176 | 1.67 | 0.000199 | 0 | 1.96 | 0.000267 | -0.00176 |  | CFL | None | 1670 | 0.199 | 1670 | 0.199 | 1.17 | 1.34 | -0.0010539 | 1670 | 0.199 | 1670 | 0.199 | 1.17 | 1.34 | -0.00105
CFLNoneSDGHtlNewIOU | Com-Iltg-dWatt-CFL_OSnone | SDG | Htl | New | IOU | 1.67 | 0.000199 | 0 | 1.8358 | 0.00025223 | -0.0024507 | 1.67 | 0.000199 | 0 | 1.8358 | 0.00025223 | -0.0024507 |  | CFL | None | 1670 | 0.199 | 1670 | 0.199 | 1.1 | 1.27 | -0.0014675 | 1670 | 0.199 | 1670 | 0.199 | 1.1 | 1.27 | -0.00147
CFLNoneSDGMBTExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SDG | MBT | Ex | CZ06 | 3.09 | 0.00078 | 0 | 3.58 | 0.000938 | -0.0005711 | 3.09 | 0.00078 | 0 | 3.58 | 0.000938 | -0.0005711 |  | CFL | None | 3090 | 0.78 | 3090 | 0.78 | 1.16 | 1.2 | -0.00018482 | 3090 | 0.78 | 3090 | 0.78 | 1.16 | 1.2 | -0.000185
CFLNoneSDGMBTExCZ07 | Com-Iltg-dWatt-CFL_OSnone | SDG | MBT | Ex | CZ07 | 3.09 | 0.00078 | 0 | 3.59 | 0.000927 | -0.000155 | 3.09 | 0.00078 | 0 | 3.59 | 0.000927 | -0.000155 |  | CFL | None | 3090 | 0.78 | 3090 | 0.78 | 1.16 | 1.19 | -5.0162e-05 | 3090 | 0.78 | 3090 | 0.78 | 1.16 | 1.19 | -5.02e-05
CFLNoneSDGMBTExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SDG | MBT | Ex | CZ08 | 3.09 | 0.00078 | 0 | 3.59 | 0.000979 | -0.000371 | 3.09 | 0.00078 | 0 | 3.59 | 0.000979 | -0.000371 |  | CFL | None | 3090 | 0.78 | 3090 | 0.78 | 1.16 | 1.26 | -0.00012006 | 3090 | 0.78 | 3090 | 0.78 | 1.16 | 1.26 | -0.00012
CFLNoneSDGMBTExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SDG | MBT | Ex | CZ10 | 3.09 | 0.00078 | 0 | 3.57 | 0.000999 | -0.001 | 3.09 | 0.00078 | 0 | 3.57 | 0.000999 | -0.001 |  | CFL | None | 3090 | 0.78 | 3090 | 0.78 | 1.16 | 1.28 | -0.00032362 | 3090 | 0.78 | 3090 | 0.78 | 1.16 | 1.28 | -0.000324
CFLNoneSDGMBTExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SDG | MBT | Ex | CZ14 | 3.09 | 0.00078 | 0 | 3.52 | 0.000991 | -0.00239 | 3.09 | 0.00078 | 0 | 3.52 | 0.000991 | -0.00239 |  | CFL | None | 3090 | 0.78 | 3090 | 0.78 | 1.14 | 1.27 | -0.00077346 | 3090 | 0.78 | 3090 | 0.78 | 1.14 | 1.27 | -0.000773
CFLNoneSDGMBTExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SDG | MBT | Ex | CZ15 | 3.09 | 0.00078 | 0 | 3.72 | 0.001 | 0 | 3.09 | 0.00078 | 0 | 3.72 | 0.001 | 0 |  | CFL | None | 3090 | 0.78 | 3090 | 0.78 | 1.2 | 1.28 | 0 | 3090 | 0.78 | 3090 | 0.78 | 1.2 | 1.28 | 0
CFLNoneSDGMBTExIOU | Com-Iltg-dWatt-CFL_OSnone | SDG | MBT | Ex | IOU | 3.09 | 0.00078 | 0 | 3.5833 | 0.00095108 | -0.00045001 | 3.09 | 0.00078 | 0 | 3.5833 | 0.00095108 | -0.00045001 |  | CFL | None | 3090 | 0.78 | 3090 | 0.78 | 1.16 | 1.22 | -0.00014563 | 3090 | 0.78 | 3090 | 0.78 | 1.16 | 1.22 | -0.000146
CFLNoneSDGMBTNewCZ06 | Com-Iltg-dWatt-CFL_OSnone | SDG | MBT | New | CZ06 | 3.09 | 0.00078 | 0 | 3.47 | 0.000976 | -0.00105 | 3.09 | 0.00078 | 0 | 3.47 | 0.000976 | -0.00105 |  | CFL | None | 3090 | 0.78 | 3090 | 0.78 | 1.12 | 1.25 | -0.00033981 | 3090 | 0.78 | 3090 | 0.78 | 1.12 | 1.25 | -0.00034
CFLNoneSDGMBTNewCZ07 | Com-Iltg-dWatt-CFL_OSnone | SDG | MBT | New | CZ07 | 3.09 | 0.00078 | 0 | 3.45 | 0.000967 | 0 | 3.09 | 0.00078 | 0 | 3.45 | 0.000967 | 0 |  | CFL | None | 3090 | 0.78 | 3090 | 0.78 | 1.12 | 1.24 | 0 | 3090 | 0.78 | 3090 | 0.78 | 1.12 | 1.24 | 0
CFLNoneSDGMBTNewCZ08 | Com-Iltg-dWatt-CFL_OSnone | SDG | MBT | New | CZ08 | 3.09 | 0.00078 | 0 | 3.48 | 0.001 | -0.000837 | 3.09 | 0.00078 | 0 | 3.48 | 0.001 | -0.000837 |  | CFL | None | 3090 | 0.78 | 3090 | 0.78 | 1.13 | 1.28 | -0.00027087 | 3090 | 0.78 | 3090 | 0.78 | 1.13 | 1.28 | -0.000271
CFLNoneSDGMBTNewCZ10 | Com-Iltg-dWatt-CFL_OSnone | SDG | MBT | New | CZ10 | 3.09 | 0.00078 | 0 | 3.49 | 0.00104 | -0.00104 | 3.09 | 0.00078 | 0 | 3.49 | 0.00104 | -0.00104 |  | CFL | None | 3090 | 0.78 | 3090 | 0.78 | 1.13 | 1.33 | -0.00033657 | 3090 | 0.78 | 3090 | 0.78 | 1.13 | 1.33 | -0.000337
CFLNoneSDGMBTNewCZ14 | Com-Iltg-dWatt-CFL_OSnone | SDG | MBT | New | CZ14 | 3.09 | 0.00078 | 0 | 3.46 | 0.00103 | -0.00202 | 3.09 | 0.00078 | 0 | 3.46 | 0.00103 | -0.00202 |  | CFL | None | 3090 | 0.78 | 3090 | 0.78 | 1.12 | 1.32 | -0.00065372 | 3090 | 0.78 | 3090 | 0.78 | 1.12 | 1.32 | -0.000654
CFLNoneSDGMBTNewCZ15 | Com-Iltg-dWatt-CFL_OSnone | SDG | MBT | New | CZ15 | 3.09 | 0.00078 | 0 | 3.68 | 0.00104 | 0 | 3.09 | 0.00078 | 0 | 3.68 | 0.00104 | 0 |  | CFL | None | 3090 | 0.78 | 3090 | 0.78 | 1.19 | 1.33 | 0 | 3090 | 0.78 | 3090 | 0.78 | 1.19 | 1.33 | 0
CFLNoneSDGMBTNewIOU | Com-Iltg-dWatt-CFL_OSnone | SDG | MBT | New | IOU | 3.09 | 0.00078 | 0 | 3.4642 | 0.00099093 | -0.00038576 | 3.09 | 0.00078 | 0 | 3.4642 | 0.00099093 | -0.00038576 |  | CFL | None | 3090 | 0.78 | 3090 | 0.78 | 1.12 | 1.27 | -0.00012484 | 3090 | 0.78 | 3090 | 0.78 | 1.12 | 1.27 | -0.000125
CFLNoneSDGMLIExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SDG | MLI | Ex | CZ06 | 2.58 | 0.000777 | 0 | 2.79 | 0.000922 | -0.00555 | 2.58 | 0.000777 | 0 | 2.79 | 0.000922 | -0.00555 |  | CFL | None | 2580 | 0.777 | 2580 | 0.777 | 1.08 | 1.19 | -0.0021512 | 2580 | 0.777 | 2580 | 0.777 | 1.08 | 1.19 | -0.00215
CFLNoneSDGMLIExCZ07 | Com-Iltg-dWatt-CFL_OSnone | SDG | MLI | Ex | CZ07 | 2.58 | 0.000777 | 0 | 2.79 | 0.00092 | -0.00286 | 2.58 | 0.000777 | 0 | 2.79 | 0.00092 | -0.00286 |  | CFL | None | 2580 | 0.777 | 2580 | 0.777 | 1.08 | 1.18 | -0.0011085 | 2580 | 0.777 | 2580 | 0.777 | 1.08 | 1.18 | -0.00111
CFLNoneSDGMLIExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SDG | MLI | Ex | CZ08 | 2.58 | 0.000777 | 0 | 2.82 | 0.000921 | -0.00457 | 2.58 | 0.000777 | 0 | 2.82 | 0.000921 | -0.00457 |  | CFL | None | 2580 | 0.777 | 2580 | 0.777 | 1.09 | 1.19 | -0.0017713 | 2580 | 0.777 | 2580 | 0.777 | 1.09 | 1.19 | -0.00177
CFLNoneSDGMLIExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SDG | MLI | Ex | CZ10 | 2.58 | 0.000777 | 0 | 2.81 | 0.000944 | -0.00622 | 2.58 | 0.000777 | 0 | 2.81 | 0.000944 | -0.00622 |  | CFL | None | 2580 | 0.777 | 2580 | 0.777 | 1.09 | 1.21 | -0.0024109 | 2580 | 0.777 | 2580 | 0.777 | 1.09 | 1.21 | -0.00241
CFLNoneSDGMLIExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SDG | MLI | Ex | CZ14 | 2.58 | 0.000777 | 0 | 2.73 | 0.000933 | -0.0172 | 2.58 | 0.000777 | 0 | 2.73 | 0.000933 | -0.0172 |  | CFL | None | 2580 | 0.777 | 2580 | 0.777 | 1.06 | 1.2 | -0.0066667 | 2580 | 0.777 | 2580 | 0.777 | 1.06 | 1.2 | -0.00667
CFLNoneSDGMLIExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SDG | MLI | Ex | CZ15 | 2.58 | 0.000777 | 0 | 3.02 | 0.000932 | -0.00163 | 2.58 | 0.000777 | 0 | 3.02 | 0.000932 | -0.00163 |  | CFL | None | 2580 | 0.777 | 2580 | 0.777 | 1.17 | 1.2 | -0.00063178 | 2580 | 0.777 | 2580 | 0.777 | 1.17 | 1.2 | -0.000632
CFLNoneSDGMLIExIOU | Com-Iltg-dWatt-CFL_OSnone | SDG | MLI | Ex | IOU | 2.58 | 0.000777 | 0 | 2.7968 | 0.00092753 | -0.0041338 | 2.58 | 0.000777 | 0 | 2.7968 | 0.00092753 | -0.0041338 |  | CFL | None | 2580 | 0.777 | 2580 | 0.777 | 1.08 | 1.19 | -0.0016022 | 2580 | 0.777 | 2580 | 0.777 | 1.08 | 1.19 | -0.0016
CFLNoneSDGMLINewCZ06 | Com-Iltg-dWatt-CFL_OSnone | SDG | MLI | New | CZ06 | 2.58 | 0.000777 | 0 | 2.71 | 0.000912 | -0.01 | 2.58 | 0.000777 | 0 | 2.71 | 0.000912 | -0.01 |  | CFL | None | 2580 | 0.777 | 2580 | 0.777 | 1.05 | 1.17 | -0.003876 | 2580 | 0.777 | 2580 | 0.777 | 1.05 | 1.17 | -0.00388
CFLNoneSDGMLINewCZ07 | Com-Iltg-dWatt-CFL_OSnone | SDG | MLI | New | CZ07 | 2.58 | 0.000777 | 0 | 2.7 | 0.00091 | -0.00583 | 2.58 | 0.000777 | 0 | 2.7 | 0.00091 | -0.00583 |  | CFL | None | 2580 | 0.777 | 2580 | 0.777 | 1.05 | 1.17 | -0.0022597 | 2580 | 0.777 | 2580 | 0.777 | 1.05 | 1.17 | -0.00226
CFLNoneSDGMLINewCZ08 | Com-Iltg-dWatt-CFL_OSnone | SDG | MLI | New | CZ08 | 2.58 | 0.000777 | 0 | 2.76 | 0.000918 | -0.00805 | 2.58 | 0.000777 | 0 | 2.76 | 0.000918 | -0.00805 |  | CFL | None | 2580 | 0.777 | 2580 | 0.777 | 1.07 | 1.18 | -0.0031202 | 2580 | 0.777 | 2580 | 0.777 | 1.07 | 1.18 | -0.00312
CFLNoneSDGMLINewCZ10 | Com-Iltg-dWatt-CFL_OSnone | SDG | MLI | New | CZ10 | 2.58 | 0.000777 | 0 | 2.85 | 0.00102 | -0.0101 | 2.58 | 0.000777 | 0 | 2.85 | 0.00102 | -0.0101 |  | CFL | None | 2580 | 0.777 | 2580 | 0.777 | 1.1 | 1.31 | -0.0039147 | 2580 | 0.777 | 2580 | 0.777 | 1.1 | 1.31 | -0.00391
CFLNoneSDGMLINewCZ14 | Com-Iltg-dWatt-CFL_OSnone | SDG | MLI | New | CZ14 | 2.58 | 0.000777 | 0 | 2.73 | 0.000955 | -0.0199 | 2.58 | 0.000777 | 0 | 2.73 | 0.000955 | -0.0199 |  | CFL | None | 2580 | 0.777 | 2580 | 0.777 | 1.06 | 1.23 | -0.0077132 | 2580 | 0.777 | 2580 | 0.777 | 1.06 | 1.23 | -0.00771
CFLNoneSDGMLINewCZ15 | Com-Iltg-dWatt-CFL_OSnone | SDG | MLI | New | CZ15 | 2.58 | 0.000777 | 0 | 3.05 | 0.00104 | -0.00169 | 2.58 | 0.000777 | 0 | 3.05 | 0.00104 | -0.00169 |  | CFL | None | 2580 | 0.777 | 2580 | 0.777 | 1.18 | 1.34 | -0.00065504 | 2580 | 0.777 | 2580 | 0.777 | 1.18 | 1.34 | -0.000655
CFLNoneSDGMLINewIOU | Com-Iltg-dWatt-CFL_OSnone | SDG | MLI | New | IOU | 2.58 | 0.000777 | 0 | 2.7484 | 0.00094443 | -0.007427 | 2.58 | 0.000777 | 0 | 2.7484 | 0.00094443 | -0.007427 |  | CFL | None | 2580 | 0.777 | 2580 | 0.777 | 1.07 | 1.22 | -0.0028787 | 2580 | 0.777 | 2580 | 0.777 | 1.07 | 1.22 | -0.00288
CFLNoneSDGMtlExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SDG | Mtl | Ex | CZ06 | 1.37 | 0.000151 | 0 | 1.55 | 0.00019 | -0.00364 | 1.37 | 0.000151 | 0 | 1.55 | 0.00019 | -0.00364 |  | CFL | None | 1370 | 0.151 | 1370 | 0.151 | 1.13 | 1.26 | -0.0026569 | 1370 | 0.151 | 1370 | 0.151 | 1.13 | 1.26 | -0.00266
CFLNoneSDGMtlExCZ07 | Com-Iltg-dWatt-CFL_OSnone | SDG | Mtl | Ex | CZ07 | 1.37 | 0.000151 | 0 | 1.58 | 0.000188 | -0.00259 | 1.37 | 0.000151 | 0 | 1.58 | 0.000188 | -0.00259 |  | CFL | None | 1370 | 0.151 | 1370 | 0.151 | 1.15 | 1.25 | -0.0018905 | 1370 | 0.151 | 1370 | 0.151 | 1.15 | 1.25 | -0.00189
CFLNoneSDGMtlExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SDG | Mtl | Ex | CZ08 | 1.37 | 0.000151 | 0 | 1.57 | 0.000192 | -0.00304 | 1.37 | 0.000151 | 0 | 1.57 | 0.000192 | -0.00304 |  | CFL | None | 1370 | 0.151 | 1370 | 0.151 | 1.15 | 1.27 | -0.002219 | 1370 | 0.151 | 1370 | 0.151 | 1.15 | 1.27 | -0.00222
CFLNoneSDGMtlExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SDG | Mtl | Ex | CZ10 | 1.37 | 0.000151 | 0 | 1.56 | 0.000197 | -0.00363 | 1.37 | 0.000151 | 0 | 1.56 | 0.000197 | -0.00363 |  | CFL | None | 1370 | 0.151 | 1370 | 0.151 | 1.14 | 1.3 | -0.0026496 | 1370 | 0.151 | 1370 | 0.151 | 1.14 | 1.3 | -0.00265
CFLNoneSDGMtlExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SDG | Mtl | Ex | CZ14 | 1.37 | 0.000151 | 0 | 1.51 | 0.000197 | -0.00511 | 1.37 | 0.000151 | 0 | 1.51 | 0.000197 | -0.00511 |  | CFL | None | 1370 | 0.151 | 1370 | 0.151 | 1.1 | 1.3 | -0.0037299 | 1370 | 0.151 | 1370 | 0.151 | 1.1 | 1.3 | -0.00373
CFLNoneSDGMtlExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SDG | Mtl | Ex | CZ15 | 1.37 | 0.000151 | 0 | 1.65 | 0.0002 | -0.00148 | 1.37 | 0.000151 | 0 | 1.65 | 0.0002 | -0.00148 |  | CFL | None | 1370 | 0.151 | 1370 | 0.151 | 1.2 | 1.32 | -0.0010803 | 1370 | 0.151 | 1370 | 0.151 | 1.2 | 1.32 | -0.00108
CFLNoneSDGMtlExIOU | Com-Iltg-dWatt-CFL_OSnone | SDG | Mtl | Ex | IOU | 1.37 | 0.000151 | 0 | 1.5768 | 0.00018918 | -0.0027512 | 1.37 | 0.000151 | 0 | 1.5768 | 0.00018918 | -0.0027512 |  | CFL | None | 1370 | 0.151 | 1370 | 0.151 | 1.15 | 1.25 | -0.0020082 | 1370 | 0.151 | 1370 | 0.151 | 1.15 | 1.25 | -0.00201
CFLNoneSDGMtlNewCZ06 | Com-Iltg-dWatt-CFL_OSnone | SDG | Mtl | New | CZ06 | 1.37 | 0.000151 | 0 | 1.54 | 0.000194 | -0.0048 | 1.37 | 0.000151 | 0 | 1.54 | 0.000194 | -0.0048 |  | CFL | None | 1370 | 0.151 | 1370 | 0.151 | 1.12 | 1.28 | -0.0035036 | 1370 | 0.151 | 1370 | 0.151 | 1.12 | 1.28 | -0.0035
CFLNoneSDGMtlNewCZ07 | Com-Iltg-dWatt-CFL_OSnone | SDG | Mtl | New | CZ07 | 1.37 | 0.000151 | 0 | 1.57 | 0.000191 | -0.0033 | 1.37 | 0.000151 | 0 | 1.57 | 0.000191 | -0.0033 |  | CFL | None | 1370 | 0.151 | 1370 | 0.151 | 1.15 | 1.26 | -0.0024088 | 1370 | 0.151 | 1370 | 0.151 | 1.15 | 1.26 | -0.00241
CFLNoneSDGMtlNewCZ08 | Com-Iltg-dWatt-CFL_OSnone | SDG | Mtl | New | CZ08 | 1.37 | 0.000151 | 0 | 1.57 | 0.000197 | -0.004 | 1.37 | 0.000151 | 0 | 1.57 | 0.000197 | -0.004 |  | CFL | None | 1370 | 0.151 | 1370 | 0.151 | 1.15 | 1.3 | -0.0029197 | 1370 | 0.151 | 1370 | 0.151 | 1.15 | 1.3 | -0.00292
CFLNoneSDGMtlNewCZ10 | Com-Iltg-dWatt-CFL_OSnone | SDG | Mtl | New | CZ10 | 1.37 | 0.000151 | 0 | 1.54 | 0.000203 | -0.00501 | 1.37 | 0.000151 | 0 | 1.54 | 0.000203 | -0.00501 |  | CFL | None | 1370 | 0.151 | 1370 | 0.151 | 1.12 | 1.34 | -0.0036569 | 1370 | 0.151 | 1370 | 0.151 | 1.12 | 1.34 | -0.00366
CFLNoneSDGMtlNewCZ14 | Com-Iltg-dWatt-CFL_OSnone | SDG | Mtl | New | CZ14 | 1.37 | 0.000151 | 0 | 1.48 | 0.000202 | -0.00671 | 1.37 | 0.000151 | 0 | 1.48 | 0.000202 | -0.00671 |  | CFL | None | 1370 | 0.151 | 1370 | 0.151 | 1.08 | 1.34 | -0.0048978 | 1370 | 0.151 | 1370 | 0.151 | 1.08 | 1.34 | -0.0049
CFLNoneSDGMtlNewCZ15 | Com-Iltg-dWatt-CFL_OSnone | SDG | Mtl | New | CZ15 | 1.37 | 0.000151 | 0 | 1.65 | 0.000207 | -0.0023 | 1.37 | 0.000151 | 0 | 1.65 | 0.000207 | -0.0023 |  | CFL | None | 1370 | 0.151 | 1370 | 0.151 | 1.2 | 1.37 | -0.0016788 | 1370 | 0.151 | 1370 | 0.151 | 1.2 | 1.37 | -0.00168
CFLNoneSDGMtlNewIOU | Com-Iltg-dWatt-CFL_OSnone | SDG | Mtl | New | IOU | 1.37 | 0.000151 | 0 | 1.5658 | 0.00019258 | -0.0035566 | 1.37 | 0.000151 | 0 | 1.5658 | 0.00019258 | -0.0035566 |  | CFL | None | 1370 | 0.151 | 1370 | 0.151 | 1.14 | 1.28 | -0.0025961 | 1370 | 0.151 | 1370 | 0.151 | 1.14 | 1.28 | -0.0026
CFLNoneSDGNrsExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SDG | Nrs | Ex | CZ06 | 3.57 | 0.000565 | 0 | 3.85 | 0.000729 | -0.033897 | 3.57 | 0.000565 | 0 | 3.85 | 0.000729 | -0.033897 |  | CFL | None | 3570 | 0.565 | 3570 | 0.565 | 1.08 | 1.29 | -0.009495 | 3570 | 0.565 | 3570 | 0.565 | 1.08 | 1.29 | -0.0095
CFLNoneSDGNrsExCZ07 | Com-Iltg-dWatt-CFL_OSnone | SDG | Nrs | Ex | CZ07 | 3.57 | 0.000565 | 0 | 3.8497 | 0.000716 | -0.03 | 3.57 | 0.000565 | 0 | 3.8497 | 0.000716 | -0.03 |  | CFL | None | 3570 | 0.565 | 3570 | 0.565 | 1.08 | 1.27 | -0.0084034 | 3570 | 0.565 | 3570 | 0.565 | 1.08 | 1.27 | -0.0084
CFLNoneSDGNrsExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SDG | Nrs | Ex | CZ08 | 3.57 | 0.000565 | 0 | 3.89 | 0.000732 | -0.0326 | 3.57 | 0.000565 | 0 | 3.89 | 0.000732 | -0.0326 |  | CFL | None | 3570 | 0.565 | 3570 | 0.565 | 1.09 | 1.3 | -0.0091317 | 3570 | 0.565 | 3570 | 0.565 | 1.09 | 1.3 | -0.00913
CFLNoneSDGNrsExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SDG | Nrs | Ex | CZ10 | 3.57 | 0.000565 | 0 | 3.91 | 0.000755 | -0.0348 | 3.57 | 0.000565 | 0 | 3.91 | 0.000755 | -0.0348 |  | CFL | None | 3570 | 0.565 | 3570 | 0.565 | 1.1 | 1.34 | -0.0097479 | 3570 | 0.565 | 3570 | 0.565 | 1.1 | 1.34 | -0.00975
CFLNoneSDGNrsExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SDG | Nrs | Ex | CZ14 | 3.57 | 0.000565 | 0 | 3.86 | 0.000747 | -0.0407 | 3.57 | 0.000565 | 0 | 3.86 | 0.000747 | -0.0407 |  | CFL | None | 3570 | 0.565 | 3570 | 0.565 | 1.08 | 1.32 | -0.011401 | 3570 | 0.565 | 3570 | 0.565 | 1.08 | 1.32 | -0.0114
CFLNoneSDGNrsExIOU | Com-Iltg-dWatt-CFL_OSnone | SDG | Nrs | Ex | IOU | 3.57 | 0.000565 | 0 | 3.86 | 0.00072252 | -0.030891 | 3.57 | 0.000565 | 0 | 3.86 | 0.00072252 | -0.030891 |  | CFL | None | 3570 | 0.565 | 3570 | 0.565 | 1.08 | 1.28 | -0.008653 | 3570 | 0.565 | 3570 | 0.565 | 1.08 | 1.28 | -0.00865
CFLNoneSDGNrsNewCZ06 | Com-Iltg-dWatt-CFL_OSnone | SDG | Nrs | New | CZ06 | 3.57 | 0.000565 | 0 | 3.72 | 0.000718 | -0.0361 | 3.57 | 0.000565 | 0 | 3.72 | 0.000718 | -0.0361 |  | CFL | None | 3570 | 0.565 | 3570 | 0.565 | 1.04 | 1.27 | -0.010112 | 3570 | 0.565 | 3570 | 0.565 | 1.04 | 1.27 | -0.0101
CFLNoneSDGNrsNewCZ07 | Com-Iltg-dWatt-CFL_OSnone | SDG | Nrs | New | CZ07 | 3.57 | 0.000565 | 0 | 3.69 | 0.000718 | -0.0337 | 3.57 | 0.000565 | 0 | 3.69 | 0.000718 | -0.0337 |  | CFL | None | 3570 | 0.565 | 3570 | 0.565 | 1.03 | 1.27 | -0.0094398 | 3570 | 0.565 | 3570 | 0.565 | 1.03 | 1.27 | -0.00944
CFLNoneSDGNrsNewCZ08 | Com-Iltg-dWatt-CFL_OSnone | SDG | Nrs | New | CZ08 | 3.57 | 0.000565 | 0 | 3.78 | 0.00072 | -0.0344 | 3.57 | 0.000565 | 0 | 3.78 | 0.00072 | -0.0344 |  | CFL | None | 3570 | 0.565 | 3570 | 0.565 | 1.06 | 1.27 | -0.0096359 | 3570 | 0.565 | 3570 | 0.565 | 1.06 | 1.27 | -0.00964
CFLNoneSDGNrsNewCZ10 | Com-Iltg-dWatt-CFL_OSnone | SDG | Nrs | New | CZ10 | 3.57 | 0.000565 | 0 | 3.82 | 0.00075 | -0.0354 | 3.57 | 0.000565 | 0 | 3.82 | 0.00075 | -0.0354 |  | CFL | None | 3570 | 0.565 | 3570 | 0.565 | 1.07 | 1.33 | -0.009916 | 3570 | 0.565 | 3570 | 0.565 | 1.07 | 1.33 | -0.00992
CFLNoneSDGNrsNewCZ14 | Com-Iltg-dWatt-CFL_OSnone | SDG | Nrs | New | CZ14 | 3.57 | 0.000565 | 0 | 3.79 | 0.000728 | -0.0436 | 3.57 | 0.000565 | 0 | 3.79 | 0.000728 | -0.0436 |  | CFL | None | 3570 | 0.565 | 3570 | 0.565 | 1.06 | 1.29 | -0.012213 | 3570 | 0.565 | 3570 | 0.565 | 1.06 | 1.29 | -0.0122
CFLNoneSDGNrsNewCZ15 | Com-Iltg-dWatt-CFL_OSnone | SDG | Nrs | New | CZ15 | 3.57 | 0.000565 | 0 | 4.1 | 0.000749 | -0.0169 | 3.57 | 0.000565 | 0 | 4.1 | 0.000749 | -0.0169 |  | CFL | None | 3570 | 0.565 | 3570 | 0.565 | 1.15 | 1.33 | -0.0047339 | 3570 | 0.565 | 3570 | 0.565 | 1.15 | 1.33 | -0.00473
CFLNoneSDGNrsNewIOU | Com-Iltg-dWatt-CFL_OSnone | SDG | Nrs | New | IOU | 3.57 | 0.000565 | 0 | 3.7131 | 0.00072259 | -0.034035 | 3.57 | 0.000565 | 0 | 3.7131 | 0.00072259 | -0.034035 |  | CFL | None | 3570 | 0.565 | 3570 | 0.565 | 1.04 | 1.28 | -0.0095337 | 3570 | 0.565 | 3570 | 0.565 | 1.04 | 1.28 | -0.00953
CFLNoneSDGOfLExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SDG | OfL | Ex | CZ06 | 3 | 0.000625 | 0 | 3.44 | 0.000797 | -0.0071958 | 3 | 0.000625 | 0 | 3.44 | 0.000797 | -0.0071958 |  | CFL | None | 3000 | 0.625 | 3000 | 0.625 | 1.15 | 1.28 | -0.0023986 | 3000 | 0.625 | 3000 | 0.625 | 1.15 | 1.28 | -0.0024
CFLNoneSDGOfLExCZ07 | Com-Iltg-dWatt-CFL_OSnone | SDG | OfL | Ex | CZ07 | 3 | 0.000625 | 0 | 3.4358 | 0.000786 | -0.0061758 | 3 | 0.000625 | 0 | 3.4358 | 0.000786 | -0.0061758 |  | CFL | None | 3000 | 0.625 | 3000 | 0.625 | 1.15 | 1.26 | -0.0020586 | 3000 | 0.625 | 3000 | 0.625 | 1.15 | 1.26 | -0.00206
CFLNoneSDGOfLExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SDG | OfL | Ex | CZ08 | 3 | 0.000625 | 0 | 3.4558 | 0.000813 | -0.0069858 | 3 | 0.000625 | 0 | 3.4558 | 0.000813 | -0.0069858 |  | CFL | None | 3000 | 0.625 | 3000 | 0.625 | 1.15 | 1.3 | -0.0023286 | 3000 | 0.625 | 3000 | 0.625 | 1.15 | 1.3 | -0.00233
CFLNoneSDGOfLExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SDG | OfL | Ex | CZ10 | 3 | 0.000625 | 0 | 3.45 | 0.00082 | -0.0079758 | 3 | 0.000625 | 0 | 3.45 | 0.00082 | -0.0079758 |  | CFL | None | 3000 | 0.625 | 3000 | 0.625 | 1.15 | 1.31 | -0.0026586 | 3000 | 0.625 | 3000 | 0.625 | 1.15 | 1.31 | -0.00266
CFLNoneSDGOfLExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SDG | OfL | Ex | CZ14 | 3 | 0.000625 | 0 | 3.4 | 0.000807 | -0.011 | 3 | 0.000625 | 0 | 3.4 | 0.000807 | -0.011 |  | CFL | None | 3000 | 0.625 | 3000 | 0.625 | 1.13 | 1.29 | -0.0036667 | 3000 | 0.625 | 3000 | 0.625 | 1.13 | 1.29 | -0.00367
CFLNoneSDGOfLExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SDG | OfL | Ex | CZ15 | 3 | 0.000625 | 0 | 3.6514 | 0.000823 | -0.00462 | 3 | 0.000625 | 0 | 3.6514 | 0.000823 | -0.00462 |  | CFL | None | 3000 | 0.625 | 3000 | 0.625 | 1.22 | 1.32 | -0.00154 | 3000 | 0.625 | 3000 | 0.625 | 1.22 | 1.32 | -0.00154
CFLNoneSDGOfLExIOU | Com-Iltg-dWatt-CFL_OSnone | SDG | OfL | Ex | IOU | 3 | 0.000625 | 0 | 3.4389 | 0.00079282 | -0.0065448 | 3 | 0.000625 | 0 | 3.4389 | 0.00079282 | -0.0065448 |  | CFL | None | 3000 | 0.625 | 3000 | 0.625 | 1.15 | 1.27 | -0.0021816 | 3000 | 0.625 | 3000 | 0.625 | 1.15 | 1.27 | -0.00218
CFLNoneSDGOfLNewCZ06 | Com-Iltg-dWatt-CFL_OSnone | SDG | OfL | New | CZ06 | 3 | 0.000625 | 0 | 3.44 | 0.000778 | -0.00489 | 3 | 0.000625 | 0 | 3.44 | 0.000778 | -0.00489 |  | CFL | None | 3000 | 0.625 | 3000 | 0.625 | 1.15 | 1.24 | -0.00163 | 3000 | 0.625 | 3000 | 0.625 | 1.15 | 1.24 | -0.00163
CFLNoneSDGOfLNewCZ07 | Com-Iltg-dWatt-CFL_OSnone | SDG | OfL | New | CZ07 | 3 | 0.000625 | 0 | 3.43 | 0.000769 | -0.00396 | 3 | 0.000625 | 0 | 3.43 | 0.000769 | -0.00396 |  | CFL | None | 3000 | 0.625 | 3000 | 0.625 | 1.14 | 1.23 | -0.00132 | 3000 | 0.625 | 3000 | 0.625 | 1.14 | 1.23 | -0.00132
CFLNoneSDGOfLNewCZ08 | Com-Iltg-dWatt-CFL_OSnone | SDG | OfL | New | CZ08 | 3 | 0.000625 | 0 | 3.45 | 0.000789 | -0.00405 | 3 | 0.000625 | 0 | 3.45 | 0.000789 | -0.00405 |  | CFL | None | 3000 | 0.625 | 3000 | 0.625 | 1.15 | 1.26 | -0.00135 | 3000 | 0.625 | 3000 | 0.625 | 1.15 | 1.26 | -0.00135
CFLNoneSDGOfLNewCZ10 | Com-Iltg-dWatt-CFL_OSnone | SDG | OfL | New | CZ10 | 3 | 0.000625 | 0 | 3.46 | 0.000813 | -0.00498 | 3 | 0.000625 | 0 | 3.46 | 0.000813 | -0.00498 |  | CFL | None | 3000 | 0.625 | 3000 | 0.625 | 1.15 | 1.3 | -0.00166 | 3000 | 0.625 | 3000 | 0.625 | 1.15 | 1.3 | -0.00166
CFLNoneSDGOfLNewCZ14 | Com-Iltg-dWatt-CFL_OSnone | SDG | OfL | New | CZ14 | 3 | 0.000625 | 0 | 3.4 | 0.000827 | -0.00782 | 3 | 0.000625 | 0 | 3.4 | 0.000827 | -0.00782 |  | CFL | None | 3000 | 0.625 | 3000 | 0.625 | 1.13 | 1.32 | -0.0026067 | 3000 | 0.625 | 3000 | 0.625 | 1.13 | 1.32 | -0.00261
CFLNoneSDGOfLNewCZ15 | Com-Iltg-dWatt-CFL_OSnone | SDG | OfL | New | CZ15 | 3 | 0.000625 | 0 | 3.59 | 0.000809 | -0.00235 | 3 | 0.000625 | 0 | 3.59 | 0.000809 | -0.00235 |  | CFL | None | 3000 | 0.625 | 3000 | 0.625 | 1.2 | 1.29 | -0.00078333 | 3000 | 0.625 | 3000 | 0.625 | 1.2 | 1.29 | -0.000783
CFLNoneSDGOfLNewIOU | Com-Iltg-dWatt-CFL_OSnone | SDG | OfL | New | IOU | 3 | 0.000625 | 0 | 3.4359 | 0.00077753 | -0.004173 | 3 | 0.000625 | 0 | 3.4359 | 0.00077753 | -0.004173 |  | CFL | None | 3000 | 0.625 | 3000 | 0.625 | 1.15 | 1.24 | -0.001391 | 3000 | 0.625 | 3000 | 0.625 | 1.15 | 1.24 | -0.00139
CFLNoneSDGOfSExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SDG | OfS | Ex | CZ06 | 2.98 | 0.000678 | 0 | 3.41 | 0.000854 | -0.0024 | 2.98 | 0.000678 | 0 | 3.41 | 0.000854 | -0.0024 |  | CFL | None | 2980 | 0.678 | 2980 | 0.678 | 1.14 | 1.26 | -0.00080537 | 2980 | 0.678 | 2980 | 0.678 | 1.14 | 1.26 | -0.000805
CFLNoneSDGOfSExCZ07 | Com-Iltg-dWatt-CFL_OSnone | SDG | OfS | Ex | CZ07 | 2.98 | 0.000678 | 0 | 3.42 | 0.000845 | -0.00065205 | 2.98 | 0.000678 | 0 | 3.42 | 0.000845 | -0.00065205 |  | CFL | None | 2980 | 0.678 | 2980 | 0.678 | 1.15 | 1.25 | -0.00021881 | 2980 | 0.678 | 2980 | 0.678 | 1.15 | 1.25 | -0.000219
CFLNoneSDGOfSExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SDG | OfS | Ex | CZ08 | 2.98 | 0.000678 | 0 | 3.43 | 0.000859 | -0.00203 | 2.98 | 0.000678 | 0 | 3.43 | 0.000859 | -0.00203 |  | CFL | None | 2980 | 0.678 | 2980 | 0.678 | 1.15 | 1.27 | -0.00068121 | 2980 | 0.678 | 2980 | 0.678 | 1.15 | 1.27 | -0.000681
CFLNoneSDGOfSExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SDG | OfS | Ex | CZ10 | 2.98 | 0.000678 | 0 | 3.42 | 0.000862 | -0.0031 | 2.98 | 0.000678 | 0 | 3.42 | 0.000862 | -0.0031 |  | CFL | None | 2980 | 0.678 | 2980 | 0.678 | 1.15 | 1.27 | -0.0010403 | 2980 | 0.678 | 2980 | 0.678 | 1.15 | 1.27 | -0.00104
CFLNoneSDGOfSExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SDG | OfS | Ex | CZ14 | 2.98 | 0.000678 | 0 | 3.33 | 0.000873 | -0.00753 | 2.98 | 0.000678 | 0 | 3.33 | 0.000873 | -0.00753 |  | CFL | None | 2980 | 0.678 | 2980 | 0.678 | 1.12 | 1.29 | -0.0025268 | 2980 | 0.678 | 2980 | 0.678 | 1.12 | 1.29 | -0.00253
CFLNoneSDGOfSExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SDG | OfS | Ex | CZ15 | 2.98 | 0.000678 | 0 | 3.65 | 0.000854 | -0.00065211 | 2.98 | 0.000678 | 0 | 3.65 | 0.000854 | -0.00065211 |  | CFL | None | 2980 | 0.678 | 2980 | 0.678 | 1.22 | 1.26 | -0.00021883 | 2980 | 0.678 | 2980 | 0.678 | 1.22 | 1.26 | -0.000219
CFLNoneSDGOfSExIOU | Com-Iltg-dWatt-CFL_OSnone | SDG | OfS | Ex | IOU | 2.98 | 0.000678 | 0 | 3.4199 | 0.00084856 | -0.0011714 | 2.98 | 0.000678 | 0 | 3.4199 | 0.00084856 | -0.0011714 |  | CFL | None | 2980 | 0.678 | 2980 | 0.678 | 1.15 | 1.25 | -0.00039308 | 2980 | 0.678 | 2980 | 0.678 | 1.15 | 1.25 | -0.000393
CFLNoneSDGOfSNewCZ06 | Com-Iltg-dWatt-CFL_OSnone | SDG | OfS | New | CZ06 | 2.98 | 0.000678 | 0 | 3.26 | 0.00084 | -0.00264 | 2.98 | 0.000678 | 0 | 3.26 | 0.00084 | -0.00264 |  | CFL | None | 2980 | 0.678 | 2980 | 0.678 | 1.09 | 1.24 | -0.00088591 | 2980 | 0.678 | 2980 | 0.678 | 1.09 | 1.24 | -0.000886
CFLNoneSDGOfSNewCZ07 | Com-Iltg-dWatt-CFL_OSnone | SDG | OfS | New | CZ07 | 2.98 | 0.000678 | 0 | 3.26 | 0.000829 | -0.000616 | 2.98 | 0.000678 | 0 | 3.26 | 0.000829 | -0.000616 |  | CFL | None | 2980 | 0.678 | 2980 | 0.678 | 1.09 | 1.22 | -0.00020671 | 2980 | 0.678 | 2980 | 0.678 | 1.09 | 1.22 | -0.000207
CFLNoneSDGOfSNewCZ08 | Com-Iltg-dWatt-CFL_OSnone | SDG | OfS | New | CZ08 | 2.98 | 0.000678 | 0 | 3.28 | 0.00085 | -0.00223 | 2.98 | 0.000678 | 0 | 3.28 | 0.00085 | -0.00223 |  | CFL | None | 2980 | 0.678 | 2980 | 0.678 | 1.1 | 1.25 | -0.00074832 | 2980 | 0.678 | 2980 | 0.678 | 1.1 | 1.25 | -0.000748
CFLNoneSDGOfSNewCZ10 | Com-Iltg-dWatt-CFL_OSnone | SDG | OfS | New | CZ10 | 2.98 | 0.000678 | 0 | 3.32 | 0.000879 | -0.00176 | 2.98 | 0.000678 | 0 | 3.32 | 0.000879 | -0.00176 |  | CFL | None | 2980 | 0.678 | 2980 | 0.678 | 1.11 | 1.3 | -0.0005906 | 2980 | 0.678 | 2980 | 0.678 | 1.11 | 1.3 | -0.000591
CFLNoneSDGOfSNewCZ14 | Com-Iltg-dWatt-CFL_OSnone | SDG | OfS | New | CZ14 | 2.98 | 0.000678 | 0 | 3.24 | 0.00088 | -0.00673 | 2.98 | 0.000678 | 0 | 3.24 | 0.00088 | -0.00673 |  | CFL | None | 2980 | 0.678 | 2980 | 0.678 | 1.09 | 1.3 | -0.0022584 | 2980 | 0.678 | 2980 | 0.678 | 1.09 | 1.3 | -0.00226
CFLNoneSDGOfSNewCZ15 | Com-Iltg-dWatt-CFL_OSnone | SDG | OfS | New | CZ15 | 2.98 | 0.000678 | 0 | 3.47 | 0.00089 | 0 | 2.98 | 0.000678 | 0 | 3.47 | 0.00089 | 0 |  | CFL | None | 2980 | 0.678 | 2980 | 0.678 | 1.16 | 1.31 | 0 | 2980 | 0.678 | 2980 | 0.678 | 1.16 | 1.31 | 0
CFLNoneSDGOfSNewIOU | Com-Iltg-dWatt-CFL_OSnone | SDG | OfS | New | IOU | 2.98 | 0.000678 | 0 | 3.271 | 0.00083863 | -0.00091617 | 2.98 | 0.000678 | 0 | 3.271 | 0.00083863 | -0.00091617 |  | CFL | None | 2980 | 0.678 | 2980 | 0.678 | 1.1 | 1.24 | -0.00030744 | 2980 | 0.678 | 2980 | 0.678 | 1.1 | 1.24 | -0.000307
CFLNoneSDGRFFExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SDG | RFF | Ex | CZ06 | 4.81 | 0.000808 | 0 | 5.34 | 0.000987 | -0.0258 | 4.81 | 0.000808 | 0 | 5.34 | 0.000987 | -0.0258 |  | CFL | None | 4810 | 0.808 | 4810 | 0.808 | 1.11 | 1.22 | -0.0053638 | 4810 | 0.808 | 4810 | 0.808 | 1.11 | 1.22 | -0.00536
CFLNoneSDGRFFExCZ07 | Com-Iltg-dWatt-CFL_OSnone | SDG | RFF | Ex | CZ07 | 4.81 | 0.000808 | 0 | 5.35 | 0.000979 | -0.0231 | 4.81 | 0.000808 | 0 | 5.35 | 0.000979 | -0.0231 |  | CFL | None | 4810 | 0.808 | 4810 | 0.808 | 1.11 | 1.21 | -0.0048025 | 4810 | 0.808 | 4810 | 0.808 | 1.11 | 1.21 | -0.0048
CFLNoneSDGRFFExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SDG | RFF | Ex | CZ08 | 4.81 | 0.000808 | 0 | 5.38 | 0.000978 | -0.0226 | 4.81 | 0.000808 | 0 | 5.38 | 0.000978 | -0.0226 |  | CFL | None | 4810 | 0.808 | 4810 | 0.808 | 1.12 | 1.21 | -0.0046985 | 4810 | 0.808 | 4810 | 0.808 | 1.12 | 1.21 | -0.0047
CFLNoneSDGRFFExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SDG | RFF | Ex | CZ10 | 4.81 | 0.000808 | 0 | 5.3855 | 0.000995 | -0.025155 | 4.81 | 0.000808 | 0 | 5.3855 | 0.000995 | -0.025155 |  | CFL | None | 4810 | 0.808 | 4810 | 0.808 | 1.12 | 1.23 | -0.0052298 | 4810 | 0.808 | 4810 | 0.808 | 1.12 | 1.23 | -0.00523
CFLNoneSDGRFFExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SDG | RFF | Ex | CZ14 | 4.81 | 0.000808 | 0 | 5.29 | 0.00101 | -0.0355 | 4.81 | 0.000808 | 0 | 5.29 | 0.00101 | -0.0355 |  | CFL | None | 4810 | 0.808 | 4810 | 0.808 | 1.1 | 1.25 | -0.0073805 | 4810 | 0.808 | 4810 | 0.808 | 1.1 | 1.25 | -0.00738
CFLNoneSDGRFFExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SDG | RFF | Ex | CZ15 | 4.81 | 0.000808 | 0 | 5.71 | 0.00101 | -0.0117 | 4.81 | 0.000808 | 0 | 5.71 | 0.00101 | -0.0117 |  | CFL | None | 4810 | 0.808 | 4810 | 0.808 | 1.19 | 1.25 | -0.0024324 | 4810 | 0.808 | 4810 | 0.808 | 1.19 | 1.25 | -0.00243
CFLNoneSDGRFFExIOU | Com-Iltg-dWatt-CFL_OSnone | SDG | RFF | Ex | IOU | 4.81 | 0.000808 | 0 | 5.3585 | 0.00098294 | -0.023674 | 4.81 | 0.000808 | 0 | 5.3585 | 0.00098294 | -0.023674 |  | CFL | None | 4810 | 0.808 | 4810 | 0.808 | 1.11 | 1.22 | -0.0049218 | 4810 | 0.808 | 4810 | 0.808 | 1.11 | 1.22 | -0.00492
CFLNoneSDGRFFNewCZ06 | Com-Iltg-dWatt-CFL_OSnone | SDG | RFF | New | CZ06 | 4.81 | 0.000808 | 0 | 5.15 | 0.001 | -0.027 | 4.81 | 0.000808 | 0 | 5.15 | 0.001 | -0.027 |  | CFL | None | 4810 | 0.808 | 4810 | 0.808 | 1.07 | 1.24 | -0.0056133 | 4810 | 0.808 | 4810 | 0.808 | 1.07 | 1.24 | -0.00561
CFLNoneSDGRFFNewCZ07 | Com-Iltg-dWatt-CFL_OSnone | SDG | RFF | New | CZ07 | 4.81 | 0.000808 | 0 | 5.13 | 0.000993 | -0.0286 | 4.81 | 0.000808 | 0 | 5.13 | 0.000993 | -0.0286 |  | CFL | None | 4810 | 0.808 | 4810 | 0.808 | 1.07 | 1.23 | -0.0059459 | 4810 | 0.808 | 4810 | 0.808 | 1.07 | 1.23 | -0.00595
CFLNoneSDGRFFNewCZ08 | Com-Iltg-dWatt-CFL_OSnone | SDG | RFF | New | CZ08 | 4.81 | 0.000808 | 0 | 5.17 | 0.000972 | -0.0264 | 4.81 | 0.000808 | 0 | 5.17 | 0.000972 | -0.0264 |  | CFL | None | 4810 | 0.808 | 4810 | 0.808 | 1.07 | 1.2 | -0.0054886 | 4810 | 0.808 | 4810 | 0.808 | 1.07 | 1.2 | -0.00549
CFLNoneSDGRFFNewCZ10 | Com-Iltg-dWatt-CFL_OSnone | SDG | RFF | New | CZ10 | 4.81 | 0.000808 | 0 | 5.29 | 0.00105 | -0.0308 | 4.81 | 0.000808 | 0 | 5.29 | 0.00105 | -0.0308 |  | CFL | None | 4810 | 0.808 | 4810 | 0.808 | 1.1 | 1.3 | -0.0064033 | 4810 | 0.808 | 4810 | 0.808 | 1.1 | 1.3 | -0.0064
CFLNoneSDGRFFNewCZ14 | Com-Iltg-dWatt-CFL_OSnone | SDG | RFF | New | CZ14 | 4.81 | 0.000808 | 0 | 5.26 | 0.00105 | -0.0429 | 4.81 | 0.000808 | 0 | 5.26 | 0.00105 | -0.0429 |  | CFL | None | 4810 | 0.808 | 4810 | 0.808 | 1.09 | 1.3 | -0.0089189 | 4810 | 0.808 | 4810 | 0.808 | 1.09 | 1.3 | -0.00892
CFLNoneSDGRFFNewCZ15 | Com-Iltg-dWatt-CFL_OSnone | SDG | RFF | New | CZ15 | 4.81 | 0.000808 | 0 | 5.66 | 0.00107 | -0.0153 | 4.81 | 0.000808 | 0 | 5.66 | 0.00107 | -0.0153 |  | CFL | None | 4810 | 0.808 | 4810 | 0.808 | 1.18 | 1.32 | -0.0031809 | 4810 | 0.808 | 4810 | 0.808 | 1.18 | 1.32 | -0.00318
CFLNoneSDGRFFNewIOU | Com-Iltg-dWatt-CFL_OSnone | SDG | RFF | New | IOU | 4.81 | 0.000808 | 0 | 5.1681 | 0.0010054 | -0.028958 | 4.81 | 0.000808 | 0 | 5.1681 | 0.0010054 | -0.028958 |  | CFL | None | 4810 | 0.808 | 4810 | 0.808 | 1.07 | 1.24 | -0.0060203 | 4810 | 0.808 | 4810 | 0.808 | 1.07 | 1.24 | -0.00602
CFLNoneSDGRSDExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SDG | RSD | Ex | CZ06 | 4.83 | 0.0008 | 0 | 5.4513 | 0.000994 | -0.023 | 4.83 | 0.0008 | 0 | 5.4513 | 0.000994 | -0.023 |  | CFL | None | 4830 | 0.8 | 4830 | 0.8 | 1.13 | 1.24 | -0.0047619 | 4830 | 0.8 | 4830 | 0.8 | 1.13 | 1.24 | -0.00476
CFLNoneSDGRSDExCZ07 | Com-Iltg-dWatt-CFL_OSnone | SDG | RSD | Ex | CZ07 | 4.83 | 0.0008 | 0 | 5.46 | 0.000998 | -0.0201 | 4.83 | 0.0008 | 0 | 5.46 | 0.000998 | -0.0201 |  | CFL | None | 4830 | 0.8 | 4830 | 0.8 | 1.13 | 1.25 | -0.0041615 | 4830 | 0.8 | 4830 | 0.8 | 1.13 | 1.25 | -0.00416
CFLNoneSDGRSDExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SDG | RSD | Ex | CZ08 | 4.83 | 0.0008 | 0 | 5.4913 | 0.00097 | -0.0196 | 4.83 | 0.0008 | 0 | 5.4913 | 0.00097 | -0.0196 |  | CFL | None | 4830 | 0.8 | 4830 | 0.8 | 1.14 | 1.21 | -0.004058 | 4830 | 0.8 | 4830 | 0.8 | 1.14 | 1.21 | -0.00406
CFLNoneSDGRSDExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SDG | RSD | Ex | CZ10 | 4.83 | 0.0008 | 0 | 5.47 | 0.000958 | -0.0231 | 4.83 | 0.0008 | 0 | 5.47 | 0.000958 | -0.0231 |  | CFL | None | 4830 | 0.8 | 4830 | 0.8 | 1.13 | 1.2 | -0.0047826 | 4830 | 0.8 | 4830 | 0.8 | 1.13 | 1.2 | -0.00478
CFLNoneSDGRSDExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SDG | RSD | Ex | CZ14 | 4.83 | 0.0008 | 0 | 5.34 | 0.00096 | -0.0359 | 4.83 | 0.0008 | 0 | 5.34 | 0.00096 | -0.0359 |  | CFL | None | 4830 | 0.8 | 4830 | 0.8 | 1.11 | 1.2 | -0.0074327 | 4830 | 0.8 | 4830 | 0.8 | 1.11 | 1.2 | -0.00743
CFLNoneSDGRSDExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SDG | RSD | Ex | CZ15 | 4.83 | 0.0008 | 0 | 5.88 | 0.00102 | -0.0085422 | 4.83 | 0.0008 | 0 | 5.88 | 0.00102 | -0.0085422 |  | CFL | None | 4830 | 0.8 | 4830 | 0.8 | 1.22 | 1.27 | -0.0017686 | 4830 | 0.8 | 4830 | 0.8 | 1.22 | 1.27 | -0.00177
CFLNoneSDGRSDExIOU | Com-Iltg-dWatt-CFL_OSnone | SDG | RSD | Ex | IOU | 4.83 | 0.0008 | 0 | 5.4629 | 0.00098812 | -0.020897 | 4.83 | 0.0008 | 0 | 5.4629 | 0.00098812 | -0.020897 |  | CFL | None | 4830 | 0.8 | 4830 | 0.8 | 1.13 | 1.24 | -0.0043266 | 4830 | 0.8 | 4830 | 0.8 | 1.13 | 1.24 | -0.00433
CFLNoneSDGRSDNewCZ06 | Com-Iltg-dWatt-CFL_OSnone | SDG | RSD | New | CZ06 | 4.83 | 0.0008 | 0 | 5.28 | 0.001 | -0.0277 | 4.83 | 0.0008 | 0 | 5.28 | 0.001 | -0.0277 |  | CFL | None | 4830 | 0.8 | 4830 | 0.8 | 1.09 | 1.25 | -0.005735 | 4830 | 0.8 | 4830 | 0.8 | 1.09 | 1.25 | -0.00574
CFLNoneSDGRSDNewCZ07 | Com-Iltg-dWatt-CFL_OSnone | SDG | RSD | New | CZ07 | 4.83 | 0.0008 | 0 | 5.26 | 0.001 | -0.0255 | 4.83 | 0.0008 | 0 | 5.26 | 0.001 | -0.0255 |  | CFL | None | 4830 | 0.8 | 4830 | 0.8 | 1.09 | 1.25 | -0.0052795 | 4830 | 0.8 | 4830 | 0.8 | 1.09 | 1.25 | -0.00528
CFLNoneSDGRSDNewCZ08 | Com-Iltg-dWatt-CFL_OSnone | SDG | RSD | New | CZ08 | 4.83 | 0.0008 | 0 | 5.19 | 0.000871 | -0.0229 | 4.83 | 0.0008 | 0 | 5.19 | 0.000871 | -0.0229 |  | CFL | None | 4830 | 0.8 | 4830 | 0.8 | 1.07 | 1.09 | -0.0047412 | 4830 | 0.8 | 4830 | 0.8 | 1.07 | 1.09 | -0.00474
CFLNoneSDGRSDNewCZ10 | Com-Iltg-dWatt-CFL_OSnone | SDG | RSD | New | CZ10 | 4.83 | 0.0008 | 0 | 5.4 | 0.00105 | -0.0262 | 4.83 | 0.0008 | 0 | 5.4 | 0.00105 | -0.0262 |  | CFL | None | 4830 | 0.8 | 4830 | 0.8 | 1.12 | 1.31 | -0.0054244 | 4830 | 0.8 | 4830 | 0.8 | 1.12 | 1.31 | -0.00542
CFLNoneSDGRSDNewCZ14 | Com-Iltg-dWatt-CFL_OSnone | SDG | RSD | New | CZ14 | 4.83 | 0.0008 | 0 | 5.31 | 0.00105 | -0.0388 | 4.83 | 0.0008 | 0 | 5.31 | 0.00105 | -0.0388 |  | CFL | None | 4830 | 0.8 | 4830 | 0.8 | 1.1 | 1.31 | -0.0080331 | 4830 | 0.8 | 4830 | 0.8 | 1.1 | 1.31 | -0.00803
CFLNoneSDGRSDNewCZ15 | Com-Iltg-dWatt-CFL_OSnone | SDG | RSD | New | CZ15 | 4.83 | 0.0008 | 0 | 5.8 | 0.00108 | -0.0113 | 4.83 | 0.0008 | 0 | 5.8 | 0.00108 | -0.0113 |  | CFL | None | 4830 | 0.8 | 4830 | 0.8 | 1.2 | 1.35 | -0.0023395 | 4830 | 0.8 | 4830 | 0.8 | 1.2 | 1.35 | -0.00234
CFLNoneSDGRSDNewIOU | Com-Iltg-dWatt-CFL_OSnone | SDG | RSD | New | IOU | 4.83 | 0.0008 | 0 | 5.2901 | 0.0010072 | -0.025687 | 4.83 | 0.0008 | 0 | 5.2901 | 0.0010072 | -0.025687 |  | CFL | None | 4830 | 0.8 | 4830 | 0.8 | 1.1 | 1.26 | -0.0053183 | 4830 | 0.8 | 4830 | 0.8 | 1.1 | 1.26 | -0.00532
CFLNoneSDGRt3ExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SDG | Rt3 | Ex | CZ06 | 3.71 | 0.000631 | 0 | 4.23 | 0.000793 | -0.00534 | 3.71 | 0.000631 | 0 | 4.23 | 0.000793 | -0.00534 |  | CFL | None | 3710 | 0.631 | 3710 | 0.631 | 1.14 | 1.26 | -0.0014394 | 3710 | 0.631 | 3710 | 0.631 | 1.14 | 1.26 | -0.00144
CFLNoneSDGRt3ExCZ07 | Com-Iltg-dWatt-CFL_OSnone | SDG | Rt3 | Ex | CZ07 | 3.71 | 0.000631 | 0 | 4.25 | 0.000778 | -0.00245 | 3.71 | 0.000631 | 0 | 4.25 | 0.000778 | -0.00245 |  | CFL | None | 3710 | 0.631 | 3710 | 0.631 | 1.15 | 1.23 | -0.00066038 | 3710 | 0.631 | 3710 | 0.631 | 1.15 | 1.23 | -0.00066
CFLNoneSDGRt3ExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SDG | Rt3 | Ex | CZ08 | 3.71 | 0.000631 | 0 | 4.24 | 0.000781 | -0.00464 | 3.71 | 0.000631 | 0 | 4.24 | 0.000781 | -0.00464 |  | CFL | None | 3710 | 0.631 | 3710 | 0.631 | 1.14 | 1.24 | -0.0012507 | 3710 | 0.631 | 3710 | 0.631 | 1.14 | 1.24 | -0.00125
CFLNoneSDGRt3ExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SDG | Rt3 | Ex | CZ10 | 3.71 | 0.000631 | 0 | 4.18 | 0.000791 | -0.00816 | 3.71 | 0.000631 | 0 | 4.18 | 0.000791 | -0.00816 |  | CFL | None | 3710 | 0.631 | 3710 | 0.631 | 1.13 | 1.25 | -0.0021995 | 3710 | 0.631 | 3710 | 0.631 | 1.13 | 1.25 | -0.0022
CFLNoneSDGRt3ExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SDG | Rt3 | Ex | CZ14 | 3.71 | 0.000631 | 0 | 3.98 | 0.000797 | -0.0251 | 3.71 | 0.000631 | 0 | 3.98 | 0.000797 | -0.0251 |  | CFL | None | 3710 | 0.631 | 3710 | 0.631 | 1.07 | 1.26 | -0.0067655 | 3710 | 0.631 | 3710 | 0.631 | 1.07 | 1.26 | -0.00677
CFLNoneSDGRt3ExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SDG | Rt3 | Ex | CZ15 | 3.71 | 0.000631 | 0 | 4.33 | 0.000812 | -0.00207 | 3.71 | 0.000631 | 0 | 4.33 | 0.000812 | -0.00207 |  | CFL | None | 3710 | 0.631 | 3710 | 0.631 | 1.17 | 1.29 | -0.00055795 | 3710 | 0.631 | 3710 | 0.631 | 1.17 | 1.29 | -0.000558
CFLNoneSDGRt3ExIOU | Com-Iltg-dWatt-CFL_OSnone | SDG | Rt3 | Ex | IOU | 3.71 | 0.000631 | 0 | 4.2313 | 0.00078191 | -0.0041021 | 3.71 | 0.000631 | 0 | 4.2313 | 0.00078191 | -0.0041021 |  | CFL | None | 3710 | 0.631 | 3710 | 0.631 | 1.14 | 1.24 | -0.0011057 | 3710 | 0.631 | 3710 | 0.631 | 1.14 | 1.24 | -0.00111
CFLNoneSDGRt3NewCZ06 | Com-Iltg-dWatt-CFL_OSnone | SDG | Rt3 | New | CZ06 | 3.71 | 0.000631 | 0 | 4.11 | 0.000771 | -0.00794 | 3.71 | 0.000631 | 0 | 4.11 | 0.000771 | -0.00794 |  | CFL | None | 3710 | 0.631 | 3710 | 0.631 | 1.11 | 1.22 | -0.0021402 | 3710 | 0.631 | 3710 | 0.631 | 1.11 | 1.22 | -0.00214
CFLNoneSDGRt3NewCZ07 | Com-Iltg-dWatt-CFL_OSnone | SDG | Rt3 | New | CZ07 | 3.71 | 0.000631 | 0 | 4.14 | 0.000746 | -0.00378 | 3.71 | 0.000631 | 0 | 4.14 | 0.000746 | -0.00378 |  | CFL | None | 3710 | 0.631 | 3710 | 0.631 | 1.12 | 1.18 | -0.0010189 | 3710 | 0.631 | 3710 | 0.631 | 1.12 | 1.18 | -0.00102
CFLNoneSDGRt3NewCZ08 | Com-Iltg-dWatt-CFL_OSnone | SDG | Rt3 | New | CZ08 | 3.71 | 0.000631 | 0 | 4.14 | 0.00076 | -0.00646 | 3.71 | 0.000631 | 0 | 4.14 | 0.00076 | -0.00646 |  | CFL | None | 3710 | 0.631 | 3710 | 0.631 | 1.12 | 1.2 | -0.0017412 | 3710 | 0.631 | 3710 | 0.631 | 1.12 | 1.2 | -0.00174
CFLNoneSDGRt3NewCZ10 | Com-Iltg-dWatt-CFL_OSnone | SDG | Rt3 | New | CZ10 | 3.71 | 0.000631 | 0 | 4.1 | 0.000786 | -0.0112 | 3.71 | 0.000631 | 0 | 4.1 | 0.000786 | -0.0112 |  | CFL | None | 3710 | 0.631 | 3710 | 0.631 | 1.11 | 1.25 | -0.0030189 | 3710 | 0.631 | 3710 | 0.631 | 1.11 | 1.25 | -0.00302
CFLNoneSDGRt3NewCZ14 | Com-Iltg-dWatt-CFL_OSnone | SDG | Rt3 | New | CZ14 | 3.71 | 0.000631 | 0 | 3.96 | 0.00079 | -0.027 | 3.71 | 0.000631 | 0 | 3.96 | 0.00079 | -0.027 |  | CFL | None | 3710 | 0.631 | 3710 | 0.631 | 1.07 | 1.25 | -0.0072776 | 3710 | 0.631 | 3710 | 0.631 | 1.07 | 1.25 | -0.00728
CFLNoneSDGRt3NewCZ15 | Com-Iltg-dWatt-CFL_OSnone | SDG | Rt3 | New | CZ15 | 3.71 | 0.000631 | 0 | 4.33 | 0.000841 | -0.00168 | 3.71 | 0.000631 | 0 | 4.33 | 0.000841 | -0.00168 |  | CFL | None | 3710 | 0.631 | 3710 | 0.631 | 1.17 | 1.33 | -0.00045283 | 3710 | 0.631 | 3710 | 0.631 | 1.17 | 1.33 | -0.000453
CFLNoneSDGRt3NewIOU | Com-Iltg-dWatt-CFL_OSnone | SDG | Rt3 | New | IOU | 3.71 | 0.000631 | 0 | 4.1291 | 0.00075758 | -0.0059239 | 3.71 | 0.000631 | 0 | 4.1291 | 0.00075758 | -0.0059239 |  | CFL | None | 3710 | 0.631 | 3710 | 0.631 | 1.11 | 1.2 | -0.0015967 | 3710 | 0.631 | 3710 | 0.631 | 1.11 | 1.2 | -0.0016
CFLNoneSDGRtLExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SDG | RtL | Ex | CZ06 | 4.35 | 0.000689 | 0 | 4.9 | 0.00087 | -0.0107 | 4.35 | 0.000689 | 0 | 4.9 | 0.00087 | -0.0107 |  | CFL | None | 4350 | 0.689 | 4350 | 0.689 | 1.13 | 1.26 | -0.0024598 | 4350 | 0.689 | 4350 | 0.689 | 1.13 | 1.26 | -0.00246
CFLNoneSDGRtLExCZ07 | Com-Iltg-dWatt-CFL_OSnone | SDG | RtL | Ex | CZ07 | 4.35 | 0.000689 | 0 | 4.93 | 0.000869 | -0.0077 | 4.35 | 0.000689 | 0 | 4.93 | 0.000869 | -0.0077 |  | CFL | None | 4350 | 0.689 | 4350 | 0.689 | 1.13 | 1.26 | -0.0017701 | 4350 | 0.689 | 4350 | 0.689 | 1.13 | 1.26 | -0.00177
CFLNoneSDGRtLExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SDG | RtL | Ex | CZ08 | 4.35 | 0.000689 | 0 | 4.9137 | 0.00087 | -0.00922 | 4.35 | 0.000689 | 0 | 4.9137 | 0.00087 | -0.00922 |  | CFL | None | 4350 | 0.689 | 4350 | 0.689 | 1.13 | 1.26 | -0.0021195 | 4350 | 0.689 | 4350 | 0.689 | 1.13 | 1.26 | -0.00212
CFLNoneSDGRtLExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SDG | RtL | Ex | CZ10 | 4.35 | 0.000689 | 0 | 4.88 | 0.000886 | -0.0123 | 4.35 | 0.000689 | 0 | 4.88 | 0.000886 | -0.0123 |  | CFL | None | 4350 | 0.689 | 4350 | 0.689 | 1.12 | 1.29 | -0.0028276 | 4350 | 0.689 | 4350 | 0.689 | 1.12 | 1.29 | -0.00283
CFLNoneSDGRtLExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SDG | RtL | Ex | CZ14 | 4.35 | 0.000689 | 0 | 4.71 | 0.000898 | -0.0252 | 4.35 | 0.000689 | 0 | 4.71 | 0.000898 | -0.0252 |  | CFL | None | 4350 | 0.689 | 4350 | 0.689 | 1.08 | 1.3 | -0.0057931 | 4350 | 0.689 | 4350 | 0.689 | 1.08 | 1.3 | -0.00579
CFLNoneSDGRtLExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SDG | RtL | Ex | CZ15 | 4.35 | 0.000689 | 0 | 5.09 | 0.000903 | -0.00439 | 4.35 | 0.000689 | 0 | 5.09 | 0.000903 | -0.00439 |  | CFL | None | 4350 | 0.689 | 4350 | 0.689 | 1.17 | 1.31 | -0.0010092 | 4350 | 0.689 | 4350 | 0.689 | 1.17 | 1.31 | -0.00101
CFLNoneSDGRtLExIOU | Com-Iltg-dWatt-CFL_OSnone | SDG | RtL | Ex | IOU | 4.35 | 0.000689 | 0 | 4.9156 | 0.0008733 | -0.0090372 | 4.35 | 0.000689 | 0 | 4.9156 | 0.0008733 | -0.0090372 |  | CFL | None | 4350 | 0.689 | 4350 | 0.689 | 1.13 | 1.27 | -0.0020775 | 4350 | 0.689 | 4350 | 0.689 | 1.13 | 1.27 | -0.00208
CFLNoneSDGRtLNewCZ06 | Com-Iltg-dWatt-CFL_OSnone | SDG | RtL | New | CZ06 | 4.35 | 0.000689 | 0 | 4.76 | 0.000876 | -0.0149 | 4.35 | 0.000689 | 0 | 4.76 | 0.000876 | -0.0149 |  | CFL | None | 4350 | 0.689 | 4350 | 0.689 | 1.09 | 1.27 | -0.0034253 | 4350 | 0.689 | 4350 | 0.689 | 1.09 | 1.27 | -0.00343
CFLNoneSDGRtLNewCZ07 | Com-Iltg-dWatt-CFL_OSnone | SDG | RtL | New | CZ07 | 4.35 | 0.000689 | 0 | 4.74 | 0.000844 | -0.0107 | 4.35 | 0.000689 | 0 | 4.74 | 0.000844 | -0.0107 |  | CFL | None | 4350 | 0.689 | 4350 | 0.689 | 1.09 | 1.22 | -0.0024598 | 4350 | 0.689 | 4350 | 0.689 | 1.09 | 1.22 | -0.00246
CFLNoneSDGRtLNewCZ08 | Com-Iltg-dWatt-CFL_OSnone | SDG | RtL | New | CZ08 | 4.35 | 0.000689 | 0 | 4.82 | 0.000888 | -0.0126 | 4.35 | 0.000689 | 0 | 4.82 | 0.000888 | -0.0126 |  | CFL | None | 4350 | 0.689 | 4350 | 0.689 | 1.11 | 1.29 | -0.0028966 | 4350 | 0.689 | 4350 | 0.689 | 1.11 | 1.29 | -0.0029
CFLNoneSDGRtLNewCZ10 | Com-Iltg-dWatt-CFL_OSnone | SDG | RtL | New | CZ10 | 4.35 | 0.000689 | 0 | 4.86 | 0.000934 | -0.0145 | 4.35 | 0.000689 | 0 | 4.86 | 0.000934 | -0.0145 |  | CFL | None | 4350 | 0.689 | 4350 | 0.689 | 1.12 | 1.36 | -0.0033333 | 4350 | 0.689 | 4350 | 0.689 | 1.12 | 1.36 | -0.00333
CFLNoneSDGRtLNewCZ14 | Com-Iltg-dWatt-CFL_OSnone | SDG | RtL | New | CZ14 | 4.35 | 0.000689 | 0 | 4.75 | 0.000927 | -0.0282 | 4.35 | 0.000689 | 0 | 4.75 | 0.000927 | -0.0282 |  | CFL | None | 4350 | 0.689 | 4350 | 0.689 | 1.09 | 1.35 | -0.0064828 | 4350 | 0.689 | 4350 | 0.689 | 1.09 | 1.35 | -0.00648
CFLNoneSDGRtLNewCZ15 | Com-Iltg-dWatt-CFL_OSnone | SDG | RtL | New | CZ15 | 4.35 | 0.000689 | 0 | 5.14 | 0.000944 | -0.00424 | 4.35 | 0.000689 | 0 | 5.14 | 0.000944 | -0.00424 |  | CFL | None | 4350 | 0.689 | 4350 | 0.689 | 1.18 | 1.37 | -0.00097471 | 4350 | 0.689 | 4350 | 0.689 | 1.18 | 1.37 | -0.000975
CFLNoneSDGRtLNewIOU | Com-Iltg-dWatt-CFL_OSnone | SDG | RtL | New | IOU | 4.35 | 0.000689 | 0 | 4.7751 | 0.00086994 | -0.011903 | 4.35 | 0.000689 | 0 | 4.7751 | 0.00086994 | -0.011903 |  | CFL | None | 4350 | 0.689 | 4350 | 0.689 | 1.1 | 1.26 | -0.0027364 | 4350 | 0.689 | 4350 | 0.689 | 1.1 | 1.26 | -0.00274
CFLNoneSDGRtSExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SDG | RtS | Ex | CZ06 | 4.01 | 0.0007 | 0 | 4.44 | 0.000876 | -0.00794 | 4.01 | 0.0007 | 0 | 4.44 | 0.000876 | -0.00794 |  | CFL | None | 4010 | 0.7 | 4010 | 0.7 | 1.11 | 1.25 | -0.00198 | 4010 | 0.7 | 4010 | 0.7 | 1.11 | 1.25 | -0.00198
CFLNoneSDGRtSExCZ07 | Com-Iltg-dWatt-CFL_OSnone | SDG | RtS | Ex | CZ07 | 4.01 | 0.0007 | 0 | 4.45 | 0.000856 | -0.00489 | 4.01 | 0.0007 | 0 | 4.45 | 0.000856 | -0.00489 |  | CFL | None | 4010 | 0.7 | 4010 | 0.7 | 1.11 | 1.22 | -0.0012195 | 4010 | 0.7 | 4010 | 0.7 | 1.11 | 1.22 | -0.00122
CFLNoneSDGRtSExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SDG | RtS | Ex | CZ08 | 4.01 | 0.0007 | 0 | 4.47 | 0.000877 | -0.00674 | 4.01 | 0.0007 | 0 | 4.47 | 0.000877 | -0.00674 |  | CFL | None | 4010 | 0.7 | 4010 | 0.7 | 1.11 | 1.25 | -0.0016808 | 4010 | 0.7 | 4010 | 0.7 | 1.11 | 1.25 | -0.00168
CFLNoneSDGRtSExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SDG | RtS | Ex | CZ10 | 4.01 | 0.0007 | 0 | 4.45 | 0.000885 | -0.0093892 | 4.01 | 0.0007 | 0 | 4.45 | 0.000885 | -0.0093892 |  | CFL | None | 4010 | 0.7 | 4010 | 0.7 | 1.11 | 1.26 | -0.0023414 | 4010 | 0.7 | 4010 | 0.7 | 1.11 | 1.26 | -0.00234
CFLNoneSDGRtSExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SDG | RtS | Ex | CZ14 | 4.01 | 0.0007 | 0 | 4.32 | 0.000883 | -0.0206 | 4.01 | 0.0007 | 0 | 4.32 | 0.000883 | -0.0206 |  | CFL | None | 4010 | 0.7 | 4010 | 0.7 | 1.08 | 1.26 | -0.0051372 | 4010 | 0.7 | 4010 | 0.7 | 1.08 | 1.26 | -0.00514
CFLNoneSDGRtSExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SDG | RtS | Ex | CZ15 | 4.01 | 0.0007 | 0 | 4.76 | 0.000871 | -0.00244 | 4.01 | 0.0007 | 0 | 4.76 | 0.000871 | -0.00244 |  | CFL | None | 4010 | 0.7 | 4010 | 0.7 | 1.19 | 1.24 | -0.00060848 | 4010 | 0.7 | 4010 | 0.7 | 1.19 | 1.24 | -0.000608
CFLNoneSDGRtSExIOU | Com-Iltg-dWatt-CFL_OSnone | SDG | RtS | Ex | IOU | 4.01 | 0.0007 | 0 | 4.4509 | 0.0008651 | -0.0062228 | 4.01 | 0.0007 | 0 | 4.4509 | 0.0008651 | -0.0062228 |  | CFL | None | 4010 | 0.7 | 4010 | 0.7 | 1.11 | 1.24 | -0.0015518 | 4010 | 0.7 | 4010 | 0.7 | 1.11 | 1.24 | -0.00155
CFLNoneSDGRtSNewCZ06 | Com-Iltg-dWatt-CFL_OSnone | SDG | RtS | New | CZ06 | 4.01 | 0.0007 | 0 | 4.33 | 0.000862 | -0.00999 | 4.01 | 0.0007 | 0 | 4.33 | 0.000862 | -0.00999 |  | CFL | None | 4010 | 0.7 | 4010 | 0.7 | 1.08 | 1.23 | -0.0024913 | 4010 | 0.7 | 4010 | 0.7 | 1.08 | 1.23 | -0.00249
CFLNoneSDGRtSNewCZ07 | Com-Iltg-dWatt-CFL_OSnone | SDG | RtS | New | CZ07 | 4.01 | 0.0007 | 0 | 4.32 | 0.000851 | -0.0061 | 4.01 | 0.0007 | 0 | 4.32 | 0.000851 | -0.0061 |  | CFL | None | 4010 | 0.7 | 4010 | 0.7 | 1.08 | 1.22 | -0.0015212 | 4010 | 0.7 | 4010 | 0.7 | 1.08 | 1.22 | -0.00152
CFLNoneSDGRtSNewCZ08 | Com-Iltg-dWatt-CFL_OSnone | SDG | RtS | New | CZ08 | 4.01 | 0.0007 | 0 | 4.37 | 0.000871 | -0.00834 | 4.01 | 0.0007 | 0 | 4.37 | 0.000871 | -0.00834 |  | CFL | None | 4010 | 0.7 | 4010 | 0.7 | 1.09 | 1.24 | -0.0020798 | 4010 | 0.7 | 4010 | 0.7 | 1.09 | 1.24 | -0.00208
CFLNoneSDGRtSNewCZ10 | Com-Iltg-dWatt-CFL_OSnone | SDG | RtS | New | CZ10 | 4.01 | 0.0007 | 0 | 4.41 | 0.000908 | -0.00999 | 4.01 | 0.0007 | 0 | 4.41 | 0.000908 | -0.00999 |  | CFL | None | 4010 | 0.7 | 4010 | 0.7 | 1.1 | 1.3 | -0.0024913 | 4010 | 0.7 | 4010 | 0.7 | 1.1 | 1.3 | -0.00249
CFLNoneSDGRtSNewCZ14 | Com-Iltg-dWatt-CFL_OSnone | SDG | RtS | New | CZ14 | 4.01 | 0.0007 | 0 | 4.31 | 0.000895 | -0.022 | 4.01 | 0.0007 | 0 | 4.31 | 0.000895 | -0.022 |  | CFL | None | 4010 | 0.7 | 4010 | 0.7 | 1.07 | 1.28 | -0.0054863 | 4010 | 0.7 | 4010 | 0.7 | 1.07 | 1.28 | -0.00549
CFLNoneSDGRtSNewCZ15 | Com-Iltg-dWatt-CFL_OSnone | SDG | RtS | New | CZ15 | 4.01 | 0.0007 | 0 | 4.61 | 0.00092 | -0.00193 | 4.01 | 0.0007 | 0 | 4.61 | 0.00092 | -0.00193 |  | CFL | None | 4010 | 0.7 | 4010 | 0.7 | 1.15 | 1.31 | -0.0004813 | 4010 | 0.7 | 4010 | 0.7 | 1.15 | 1.31 | -0.000481
CFLNoneSDGRtSNewIOU | Com-Iltg-dWatt-CFL_OSnone | SDG | RtS | New | IOU | 4.01 | 0.0007 | 0 | 4.3455 | 0.00086663 | -0.0073348 | 4.01 | 0.0007 | 0 | 4.3455 | 0.00086663 | -0.0073348 |  | CFL | None | 4010 | 0.7 | 4010 | 0.7 | 1.08 | 1.24 | -0.0018291 | 4010 | 0.7 | 4010 | 0.7 | 1.08 | 1.24 | -0.00183
CFLNoneSDGSCnExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SDG | SCn | Ex | CZ06 | 2.76 | 0.000575 | 0 | 2.8382 | 0.000739 | -0.0144 | 2.76 | 0.000575 | 0 | 2.8382 | 0.000739 | -0.0144 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 1.03 | 1.29 | -0.0052174 | 2760 | 0.575 | 2760 | 0.575 | 1.03 | 1.29 | -0.00522
CFLNoneSDGSCnExCZ07 | Com-Iltg-dWatt-CFL_OSnone | SDG | SCn | Ex | CZ07 | 2.76 | 0.000575 | 0 | 2.79 | 0.000743 | -0.0116 | 2.76 | 0.000575 | 0 | 2.79 | 0.000743 | -0.0116 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 1.01 | 1.29 | -0.0042029 | 2760 | 0.575 | 2760 | 0.575 | 1.01 | 1.29 | -0.0042
CFLNoneSDGSCnExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SDG | SCn | Ex | CZ08 | 2.76 | 0.000575 | 0 | 2.88 | 0.000738 | -0.0123 | 2.76 | 0.000575 | 0 | 2.88 | 0.000738 | -0.0123 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 1.04 | 1.28 | -0.0044565 | 2760 | 0.575 | 2760 | 0.575 | 1.04 | 1.28 | -0.00446
CFLNoneSDGSCnExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SDG | SCn | Ex | CZ10 | 2.76 | 0.000575 | 0 | 2.89 | 0.000748 | -0.0157 | 2.76 | 0.000575 | 0 | 2.89 | 0.000748 | -0.0157 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 1.05 | 1.3 | -0.0056884 | 2760 | 0.575 | 2760 | 0.575 | 1.05 | 1.3 | -0.00569
CFLNoneSDGSCnExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SDG | SCn | Ex | CZ14 | 2.76 | 0.000575 | 0 | 2.8 | 0.000734 | -0.0232 | 2.76 | 0.000575 | 0 | 2.8 | 0.000734 | -0.0232 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 1.01 | 1.28 | -0.0084058 | 2760 | 0.575 | 2760 | 0.575 | 1.01 | 1.28 | -0.00841
CFLNoneSDGSCnExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SDG | SCn | Ex | CZ15 | 2.76 | 0.000575 | 0 | 3.09 | 0.000735 | -0.00652 | 2.76 | 0.000575 | 0 | 3.09 | 0.000735 | -0.00652 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 1.12 | 1.28 | -0.0023623 | 2760 | 0.575 | 2760 | 0.575 | 1.12 | 1.28 | -0.00236
CFLNoneSDGSCnExIOU | Com-Iltg-dWatt-CFL_OSnone | SDG | SCn | Ex | IOU | 2.76 | 0.000575 | 0 | 2.823 | 0.00074428 | -0.012935 | 2.76 | 0.000575 | 0 | 2.823 | 0.00074428 | -0.012935 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 1.02 | 1.29 | -0.0046868 | 2760 | 0.575 | 2760 | 0.575 | 1.02 | 1.29 | -0.00469
CFLNoneSDGSCnNewCZ06 | Com-Iltg-dWatt-CFL_OSnone | SDG | SCn | New | CZ06 | 2.76 | 0.000575 | 0 | 2.76 | 0.000688 | -0.0163 | 2.76 | 0.000575 | 0 | 2.76 | 0.000688 | -0.0163 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 1 | 1.2 | -0.0059058 | 2760 | 0.575 | 2760 | 0.575 | 1 | 1.2 | -0.00591
CFLNoneSDGSCnNewCZ07 | Com-Iltg-dWatt-CFL_OSnone | SDG | SCn | New | CZ07 | 2.76 | 0.000575 | 0 | 2.76 | 0.000703 | -0.0135 | 2.76 | 0.000575 | 0 | 2.76 | 0.000703 | -0.0135 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 1 | 1.22 | -0.0048913 | 2760 | 0.575 | 2760 | 0.575 | 1 | 1.22 | -0.00489
CFLNoneSDGSCnNewCZ08 | Com-Iltg-dWatt-CFL_OSnone | SDG | SCn | New | CZ08 | 2.76 | 0.000575 | 0 | 2.82 | 0.000699 | -0.0142 | 2.76 | 0.000575 | 0 | 2.82 | 0.000699 | -0.0142 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 1.02 | 1.22 | -0.0051449 | 2760 | 0.575 | 2760 | 0.575 | 1.02 | 1.22 | -0.00514
CFLNoneSDGSCnNewCZ10 | Com-Iltg-dWatt-CFL_OSnone | SDG | SCn | New | CZ10 | 2.76 | 0.000575 | 0 | 2.83 | 0.000715 | -0.0166 | 2.76 | 0.000575 | 0 | 2.83 | 0.000715 | -0.0166 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 1.03 | 1.24 | -0.0060145 | 2760 | 0.575 | 2760 | 0.575 | 1.03 | 1.24 | -0.00601
CFLNoneSDGSCnNewCZ14 | Com-Iltg-dWatt-CFL_OSnone | SDG | SCn | New | CZ14 | 2.76 | 0.000575 | 0 | 2.78 | 0.000712 | -0.0244 | 2.76 | 0.000575 | 0 | 2.78 | 0.000712 | -0.0244 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 1.01 | 1.24 | -0.0088406 | 2760 | 0.575 | 2760 | 0.575 | 1.01 | 1.24 | -0.00884
CFLNoneSDGSCnNewCZ15 | Com-Iltg-dWatt-CFL_OSnone | SDG | SCn | New | CZ15 | 2.76 | 0.000575 | 0 | 3.01 | 0.000718 | -0.00517 | 2.76 | 0.000575 | 0 | 3.01 | 0.000718 | -0.00517 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 1.09 | 1.25 | -0.0018732 | 2760 | 0.575 | 2760 | 0.575 | 1.09 | 1.25 | -0.00187
CFLNoneSDGSCnNewIOU | Com-Iltg-dWatt-CFL_OSnone | SDG | SCn | New | IOU | 2.76 | 0.000575 | 0 | 2.7823 | 0.0007062 | -0.01453 | 2.76 | 0.000575 | 0 | 2.7823 | 0.0007062 | -0.01453 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 1.01 | 1.23 | -0.0052644 | 2760 | 0.575 | 2760 | 0.575 | 1.01 | 1.23 | -0.00526
CFLNoneSDGSUnExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SDG | SUn | Ex | CZ06 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0 | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0
CFLNoneSDGSUnExCZ07 | Com-Iltg-dWatt-CFL_OSnone | SDG | SUn | Ex | CZ07 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0 | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0
CFLNoneSDGSUnExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SDG | SUn | Ex | CZ08 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0 | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0
CFLNoneSDGSUnExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SDG | SUn | Ex | CZ10 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0 | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0
CFLNoneSDGSUnExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SDG | SUn | Ex | CZ14 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0 | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0
CFLNoneSDGSUnExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SDG | SUn | Ex | CZ15 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0 | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0
CFLNoneSDGSUnExIOU | Com-Iltg-dWatt-CFL_OSnone | SDG | SUn | Ex | IOU | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0 | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0
CFLNoneSDGSUnNewCZ06 | Com-Iltg-dWatt-CFL_OSnone | SDG | SUn | New | CZ06 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0 | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0
CFLNoneSDGSUnNewCZ07 | Com-Iltg-dWatt-CFL_OSnone | SDG | SUn | New | CZ07 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0 | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0
CFLNoneSDGSUnNewCZ08 | Com-Iltg-dWatt-CFL_OSnone | SDG | SUn | New | CZ08 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0 | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0
CFLNoneSDGSUnNewCZ10 | Com-Iltg-dWatt-CFL_OSnone | SDG | SUn | New | CZ10 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0 | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0
CFLNoneSDGSUnNewCZ14 | Com-Iltg-dWatt-CFL_OSnone | SDG | SUn | New | CZ14 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0 | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0
CFLNoneSDGSUnNewCZ15 | Com-Iltg-dWatt-CFL_OSnone | SDG | SUn | New | CZ15 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0 | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0
CFLNoneSDGSUnNewIOU | Com-Iltg-dWatt-CFL_OSnone | SDG | SUn | New | IOU | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 | 2.76 | 0.000575 | 0 |  | CFL | None | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0 | 2760 | 0.575 | 2760 | 0.575 | 1 | 1 | 0
CFLNoneSDGWRfExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SDG | WRf | Ex | CZ06 | 4.73 | 0.000548 | 0 | 7.45 | 0.000687 | 0 | 4.73 | 0.000548 | 0 | 7.45 | 0.000687 | 0 |  | CFL | None | 4730 | 0.548 | 4730 | 0.548 | 1.58 | 1.25 | 0 | 4730 | 0.548 | 4730 | 0.548 | 1.58 | 1.25 | 0
CFLNoneSDGWRfExCZ07 | Com-Iltg-dWatt-CFL_OSnone | SDG | WRf | Ex | CZ07 | 4.73 | 0.000548 | 0 | 7.4 | 0.000688 | 0 | 4.73 | 0.000548 | 0 | 7.4 | 0.000688 | 0 |  | CFL | None | 4730 | 0.548 | 4730 | 0.548 | 1.56 | 1.26 | 0 | 4730 | 0.548 | 4730 | 0.548 | 1.56 | 1.26 | 0
CFLNoneSDGWRfExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SDG | WRf | Ex | CZ10 | 4.73 | 0.000548 | 0 | 7.63 | 0.000693 | 0 | 4.73 | 0.000548 | 0 | 7.63 | 0.000693 | 0 |  | CFL | None | 4730 | 0.548 | 4730 | 0.548 | 1.61 | 1.26 | 0 | 4730 | 0.548 | 4730 | 0.548 | 1.61 | 1.26 | 0
CFLNoneSDGWRfExIOU | Com-Iltg-dWatt-CFL_OSnone | SDG | WRf | Ex | IOU | 4.73 | 0.000548 | 0 | 7.451 | 0.00068909 | 0 | 4.73 | 0.000548 | 0 | 7.451 | 0.00068909 | 0 |  | CFL | None | 4730 | 0.548 | 4730 | 0.548 | 1.58 | 1.26 | 0 | 4730 | 0.548 | 4730 | 0.548 | 1.58 | 1.26 | 0
CFLNoneSDGWRfNewCZ06 | Com-Iltg-dWatt-CFL_OSnone | SDG | WRf | New | CZ06 | 4.73 | 0.000548 | 0 | 7.17 | 0.000676 | 0 | 4.73 | 0.000548 | 0 | 7.17 | 0.000676 | 0 |  | CFL | None | 4730 | 0.548 | 4730 | 0.548 | 1.52 | 1.23 | 0 | 4730 | 0.548 | 4730 | 0.548 | 1.52 | 1.23 | 0
CFLNoneSDGWRfNewCZ07 | Com-Iltg-dWatt-CFL_OSnone | SDG | WRf | New | CZ07 | 4.73 | 0.000548 | 0 | 7.23 | 0.000676 | 0 | 4.73 | 0.000548 | 0 | 7.23 | 0.000676 | 0 |  | CFL | None | 4730 | 0.548 | 4730 | 0.548 | 1.53 | 1.23 | 0 | 4730 | 0.548 | 4730 | 0.548 | 1.53 | 1.23 | 0
CFLNoneSDGWRfNewCZ08 | Com-Iltg-dWatt-CFL_OSnone | SDG | WRf | New | CZ08 | 4.73 | 0.000548 | 0 | 7.13 | 0.000677 | 0 | 4.73 | 0.000548 | 0 | 7.13 | 0.000677 | 0 |  | CFL | None | 4730 | 0.548 | 4730 | 0.548 | 1.51 | 1.24 | 0 | 4730 | 0.548 | 4730 | 0.548 | 1.51 | 1.24 | 0
CFLNoneSDGWRfNewCZ10 | Com-Iltg-dWatt-CFL_OSnone | SDG | WRf | New | CZ10 | 4.73 | 0.000548 | 0 | 6.96 | 0.000685 | 0 | 4.73 | 0.000548 | 0 | 6.96 | 0.000685 | 0 |  | CFL | None | 4730 | 0.548 | 4730 | 0.548 | 1.47 | 1.25 | 0 | 4730 | 0.548 | 4730 | 0.548 | 1.47 | 1.25 | 0
CFLNoneSDGWRfNewCZ14 | Com-Iltg-dWatt-CFL_OSnone | SDG | WRf | New | CZ14 | 4.73 | 0.000548 | 0 | 6.7 | 0.000679 | 0 | 4.73 | 0.000548 | 0 | 6.7 | 0.000679 | 0 |  | CFL | None | 4730 | 0.548 | 4730 | 0.548 | 1.42 | 1.24 | 0 | 4730 | 0.548 | 4730 | 0.548 | 1.42 | 1.24 | 0
CFLNoneSDGWRfNewCZ15 | Com-Iltg-dWatt-CFL_OSnone | SDG | WRf | New | CZ15 | 4.73 | 0.000548 | 0 | 7.19 | 0.000683 | 0 | 4.73 | 0.000548 | 0 | 7.19 | 0.000683 | 0 |  | CFL | None | 4730 | 0.548 | 4730 | 0.548 | 1.52 | 1.25 | 0 | 4730 | 0.548 | 4730 | 0.548 | 1.52 | 1.25 | 0
CFLNoneSDGWRfNewIOU | Com-Iltg-dWatt-CFL_OSnone | SDG | WRf | New | IOU | 4.73 | 0.000548 | 0 | 7.1702 | 0.00067797 | 0 | 4.73 | 0.000548 | 0 | 7.1702 | 0.00067797 | 0 |  | CFL | None | 4730 | 0.548 | 4730 | 0.548 | 1.52 | 1.24 | 0 | 4730 | 0.548 | 4730 | 0.548 | 1.52 | 1.24 | 0
CFLAllSpcPGEAsmExCZ01 | Com-Iltg-dWatt-CFL_OSspc | PGE | Asm | Ex | CZ01 | 2.03 | 0.00033195 | 0 | 1.9305 | 0.000384 | -0.036105 | 2.03 | 0.00033195 | 0 | 1.9305 | 0.000384 | -0.036105 |  | CFL | AllSpc | 2030 | 0.332 | 2030 | 0.332 | 0.951 | 1.16 | -0.017786 | 2030 | 0.332 | 2030 | 0.332 | 0.951 | 1.16 | -0.0178
CFLAllSpcPGEAsmExCZ02 | Com-Iltg-dWatt-CFL_OSspc | PGE | Asm | Ex | CZ02 | 2.03 | 0.00033196 | 0 | 2.0904 | 0.00038796 | -0.020904 | 2.03 | 0.00033196 | 0 | 2.0904 | 0.00038796 | -0.020904 |  | CFL | AllSpc | 2030 | 0.332 | 2030 | 0.332 | 1.03 | 1.17 | -0.010298 | 2030 | 0.332 | 2030 | 0.332 | 1.03 | 1.17 | -0.0103
CFLAllSpcPGEAsmExCZ03 | Com-Iltg-dWatt-CFL_OSspc | PGE | Asm | Ex | CZ03 | 2.03 | 0.00033197 | 0 | 2.0703 | 0.00038797 | -0.022903 | 2.03 | 0.00033197 | 0 | 2.0703 | 0.00038797 | -0.022903 |  | CFL | AllSpc | 2030 | 0.332 | 2030 | 0.332 | 1.02 | 1.17 | -0.011282 | 2030 | 0.332 | 2030 | 0.332 | 1.02 | 1.17 | -0.0113
CFLAllSpcPGEAsmExCZ04 | Com-Iltg-dWatt-CFL_OSspc | PGE | Asm | Ex | CZ04 | 2.03 | 0.00033196 | 0 | 2.13 | 0.00038796 | -0.017 | 2.03 | 0.00033196 | 0 | 2.13 | 0.00038796 | -0.017 |  | CFL | AllSpc | 2030 | 0.332 | 2030 | 0.332 | 1.05 | 1.17 | -0.0083744 | 2030 | 0.332 | 2030 | 0.332 | 1.05 | 1.17 | -0.00837
CFLAllSpcPGEAsmExCZ05 | Com-Iltg-dWatt-CFL_OSspc | PGE | Asm | Ex | CZ05 | 2.03 | 0.00033196 | 0 | 2.0804 | 0.000381 | -0.0203 | 2.03 | 0.00033196 | 0 | 2.0804 | 0.000381 | -0.0203 |  | CFL | AllSpc | 2030 | 0.332 | 2030 | 0.332 | 1.02 | 1.15 | -0.01 | 2030 | 0.332 | 2030 | 0.332 | 1.02 | 1.15 | -0.01
CFLAllSpcPGEAsmExCZ11 | Com-Iltg-dWatt-CFL_OSspc | PGE | Asm | Ex | CZ11 | 2.03 | 0.00033193 | 0 | 2.14 | 0.00038693 | -0.018 | 2.03 | 0.00033193 | 0 | 2.14 | 0.00038693 | -0.018 |  | CFL | AllSpc | 2030 | 0.332 | 2030 | 0.332 | 1.05 | 1.17 | -0.008867 | 2030 | 0.332 | 2030 | 0.332 | 1.05 | 1.17 | -0.00887
CFLAllSpcPGEAsmExCZ12 | Com-Iltg-dWatt-CFL_OSspc | PGE | Asm | Ex | CZ12 | 2.03 | 0.00033195 | 0 | 2.12 | 0.00039095 | -0.019 | 2.03 | 0.00033195 | 0 | 2.12 | 0.00039095 | -0.019 |  | CFL | AllSpc | 2030 | 0.332 | 2030 | 0.332 | 1.04 | 1.18 | -0.0093596 | 2030 | 0.332 | 2030 | 0.332 | 1.04 | 1.18 | -0.00936
CFLAllSpcPGEAsmExCZ13 | Com-Iltg-dWatt-CFL_OSspc | PGE | Asm | Ex | CZ13 | 2.03 | 0.00033194 | 0 | 2.15 | 0.00038594 | -0.017506 | 2.03 | 0.00033194 | 0 | 2.15 | 0.00038594 | -0.017506 |  | CFL | AllSpc | 2030 | 0.332 | 2030 | 0.332 | 1.06 | 1.16 | -0.0086238 | 2030 | 0.332 | 2030 | 0.332 | 1.06 | 1.16 | -0.00862
CFLAllSpcPGEAsmExCZ16 | Com-Iltg-dWatt-CFL_OSspc | PGE | Asm | Ex | CZ16 | 2.03 | 0.00033194 | 0 | 1.98 | 0.00038194 | -0.027406 | 2.03 | 0.00033194 | 0 | 1.98 | 0.00038194 | -0.027406 |  | CFL | AllSpc | 2030 | 0.332 | 2030 | 0.332 | 0.975 | 1.15 | -0.0135 | 2030 | 0.332 | 2030 | 0.332 | 0.975 | 1.15 | -0.0135
CFLAllSpcPGEAsmExIOU | Com-Iltg-dWatt-CFL_OSspc | PGE | Asm | Ex | IOU | 2.03 | 0.00033196 | 0 | 2.1036 | 0.000388 | -0.020117 | 2.03 | 0.00033196 | 0 | 2.1036 | 0.000388 | -0.020117 |  | CFL | AllSpc | 2030 | 0.332 | 2030 | 0.332 | 1.04 | 1.17 | -0.0099099 | 2030 | 0.332 | 2030 | 0.332 | 1.04 | 1.17 | -0.00991
CFLAllSpcPGEAsmNewCZ01 | Com-Iltg-dWatt-CFL_OSspc | PGE | Asm | New | CZ01 | 2.03 | 0.000331 | 0 | 1.95 | 0.000383 | -0.036 | 2.03 | 0.000331 | 0 | 1.95 | 0.000383 | -0.036 |  | CFL | AllSpc | 2030 | 0.331 | 2030 | 0.331 | 0.961 | 1.16 | -0.017734 | 2030 | 0.331 | 2030 | 0.331 | 0.961 | 1.16 | -0.0177
CFLAllSpcPGEAsmNewCZ02 | Com-Iltg-dWatt-CFL_OSspc | PGE | Asm | New | CZ02 | 2.03 | 0.000331 | 0 | 2.07 | 0.000387 | -0.0228 | 2.03 | 0.000331 | 0 | 2.07 | 0.000387 | -0.0228 |  | CFL | AllSpc | 2030 | 0.331 | 2030 | 0.331 | 1.02 | 1.17 | -0.011232 | 2030 | 0.331 | 2030 | 0.331 | 1.02 | 1.17 | -0.0112
CFLAllSpcPGEAsmNewCZ03 | Com-Iltg-dWatt-CFL_OSspc | PGE | Asm | New | CZ03 | 2.03 | 0.000331 | 0 | 2.05 | 0.000382 | -0.0236 | 2.03 | 0.000331 | 0 | 2.05 | 0.000382 | -0.0236 |  | CFL | AllSpc | 2030 | 0.331 | 2030 | 0.331 | 1.01 | 1.15 | -0.011626 | 2030 | 0.331 | 2030 | 0.331 | 1.01 | 1.15 | -0.0116
CFLAllSpcPGEAsmNewCZ04 | Com-Iltg-dWatt-CFL_OSspc | PGE | Asm | New | CZ04 | 2.03 | 0.000331 | 0 | 2.1 | 0.000387 | -0.0186 | 2.03 | 0.000331 | 0 | 2.1 | 0.000387 | -0.0186 |  | CFL | AllSpc | 2030 | 0.331 | 2030 | 0.331 | 1.03 | 1.17 | -0.0091626 | 2030 | 0.331 | 2030 | 0.331 | 1.03 | 1.17 | -0.00916
CFLAllSpcPGEAsmNewCZ05 | Com-Iltg-dWatt-CFL_OSspc | PGE | Asm | New | CZ05 | 2.03 | 0.000331 | 0 | 2.07 | 0.000377 | -0.0206 | 2.03 | 0.000331 | 0 | 2.07 | 0.000377 | -0.0206 |  | CFL | AllSpc | 2030 | 0.331 | 2030 | 0.331 | 1.02 | 1.14 | -0.010148 | 2030 | 0.331 | 2030 | 0.331 | 1.02 | 1.14 | -0.0101
CFLAllSpcPGEAsmNewCZ11 | Com-Iltg-dWatt-CFL_OSspc | PGE | Asm | New | CZ11 | 2.03 | 0.000331 | 0 | 2.12 | 0.000394 | -0.0196 | 2.03 | 0.000331 | 0 | 2.12 | 0.000394 | -0.0196 |  | CFL | AllSpc | 2030 | 0.331 | 2030 | 0.331 | 1.04 | 1.19 | -0.0096552 | 2030 | 0.331 | 2030 | 0.331 | 1.04 | 1.19 | -0.00966
CFLAllSpcPGEAsmNewCZ12 | Com-Iltg-dWatt-CFL_OSspc | PGE | Asm | New | CZ12 | 2.03 | 0.000331 | 0 | 2.1 | 0.000393 | -0.0208 | 2.03 | 0.000331 | 0 | 2.1 | 0.000393 | -0.0208 |  | CFL | AllSpc | 2030 | 0.331 | 2030 | 0.331 | 1.03 | 1.19 | -0.010246 | 2030 | 0.331 | 2030 | 0.331 | 1.03 | 1.19 | -0.0102
CFLAllSpcPGEAsmNewCZ13 | Com-Iltg-dWatt-CFL_OSspc | PGE | Asm | New | CZ13 | 2.03 | 0.000331 | 0 | 2.13 | 0.000395 | -0.0189 | 2.03 | 0.000331 | 0 | 2.13 | 0.000395 | -0.0189 |  | CFL | AllSpc | 2030 | 0.331 | 2030 | 0.331 | 1.05 | 1.19 | -0.0093103 | 2030 | 0.331 | 2030 | 0.331 | 1.05 | 1.19 | -0.00931
CFLAllSpcPGEAsmNewCZ16 | Com-Iltg-dWatt-CFL_OSspc | PGE | Asm | New | CZ16 | 2.03 | 0.000331 | 0 | 1.99 | 0.000381 | -0.0273 | 2.03 | 0.000331 | 0 | 1.99 | 0.000381 | -0.0273 |  | CFL | AllSpc | 2030 | 0.331 | 2030 | 0.331 | 0.98 | 1.15 | -0.013448 | 2030 | 0.331 | 2030 | 0.331 | 0.98 | 1.15 | -0.0134
CFLAllSpcPGEAsmNewIOU | Com-Iltg-dWatt-CFL_OSspc | PGE | Asm | New | IOU | 2.03 | 0.000331 | 0 | 2.0897 | 0.00038879 | -0.020977 | 2.03 | 0.000331 | 0 | 2.0897 | 0.00038879 | -0.020977 |  | CFL | AllSpc | 2030 | 0.331 | 2030 | 0.331 | 1.03 | 1.17 | -0.010334 | 2030 | 0.331 | 2030 | 0.331 | 1.03 | 1.17 | -0.0103
CFLAllSpcPGEComExCZ01 | Com-Iltg-dWatt-CFL_OSspc | PGE | Com | Ex | CZ01 | 2.7665 | 0.00052884 | 0 | 2.7248 | 0.00061704 | -0.033315 | 2.7665 | 0.00052884 | 0 | 2.7248 | 0.00061704 | -0.033315 |  | CFL | AllSpc | 2770 | 0.529 | 2770 | 0.529 | 0.985 | 1.17 | -0.012042 | 2770 | 0.529 | 2770 | 0.529 | 0.985 | 1.17 | -0.012
CFLAllSpcPGEComExCZ02 | Com-Iltg-dWatt-CFL_OSspc | PGE | Com | Ex | CZ02 | 2.8298 | 0.00046978 | 0 | 2.956 | 0.00057175 | -0.021159 | 2.8298 | 0.00046978 | 0 | 2.956 | 0.00057175 | -0.021159 |  | CFL | AllSpc | 2830 | 0.47 | 2830 | 0.47 | 1.04 | 1.22 | -0.0074771 | 2830 | 0.47 | 2830 | 0.47 | 1.04 | 1.22 | -0.00748
CFLAllSpcPGEComExCZ03 | Com-Iltg-dWatt-CFL_OSspc | PGE | Com | Ex | CZ03 | 2.7482 | 0.00047462 | 0 | 2.896 | 0.00057997 | -0.019024 | 2.7482 | 0.00047462 | 0 | 2.896 | 0.00057997 | -0.019024 |  | CFL | AllSpc | 2750 | 0.475 | 2750 | 0.475 | 1.05 | 1.22 | -0.0069225 | 2750 | 0.475 | 2750 | 0.475 | 1.05 | 1.22 | -0.00692
CFLAllSpcPGEComExCZ04 | Com-Iltg-dWatt-CFL_OSspc | PGE | Com | Ex | CZ04 | 2.7495 | 0.00053207 | 0 | 2.9385 | 0.00065016 | -0.015451 | 2.7495 | 0.00053207 | 0 | 2.9385 | 0.00065016 | -0.015451 |  | CFL | AllSpc | 2750 | 0.532 | 2750 | 0.532 | 1.07 | 1.22 | -0.0056195 | 2750 | 0.532 | 2750 | 0.532 | 1.07 | 1.22 | -0.00562
CFLAllSpcPGEComExCZ05 | Com-Iltg-dWatt-CFL_OSspc | PGE | Com | Ex | CZ05 | 2.6983 | 0.00050904 | 0 | 2.8453 | 0.00061096 | -0.01942 | 2.6983 | 0.00050904 | 0 | 2.8453 | 0.00061096 | -0.01942 |  | CFL | AllSpc | 2700 | 0.509 | 2700 | 0.509 | 1.05 | 1.2 | -0.0071969 | 2700 | 0.509 | 2700 | 0.509 | 1.05 | 1.2 | -0.0072
CFLAllSpcPGEComExCZ11 | Com-Iltg-dWatt-CFL_OSspc | PGE | Com | Ex | CZ11 | 2.8476 | 0.00046557 | 0 | 3.0269 | 0.00056492 | -0.019257 | 2.8476 | 0.00046557 | 0 | 3.0269 | 0.00056492 | -0.019257 |  | CFL | AllSpc | 2850 | 0.466 | 2850 | 0.466 | 1.06 | 1.21 | -0.0067623 | 2850 | 0.466 | 2850 | 0.466 | 1.06 | 1.21 | -0.00676
CFLAllSpcPGEComExCZ12 | Com-Iltg-dWatt-CFL_OSspc | PGE | Com | Ex | CZ12 | 2.8764 | 0.0004819 | 0 | 3.0499 | 0.0005856 | -0.018883 | 2.8764 | 0.0004819 | 0 | 3.0499 | 0.0005856 | -0.018883 |  | CFL | AllSpc | 2880 | 0.482 | 2880 | 0.482 | 1.06 | 1.22 | -0.0065648 | 2880 | 0.482 | 2880 | 0.482 | 1.06 | 1.22 | -0.00656
CFLAllSpcPGEComExCZ13 | Com-Iltg-dWatt-CFL_OSspc | PGE | Com | Ex | CZ13 | 2.8791 | 0.00046991 | 0 | 3.1211 | 0.0005688 | -0.017171 | 2.8791 | 0.00046991 | 0 | 3.1211 | 0.0005688 | -0.017171 |  | CFL | AllSpc | 2880 | 0.47 | 2880 | 0.47 | 1.08 | 1.21 | -0.0059638 | 2880 | 0.47 | 2880 | 0.47 | 1.08 | 1.21 | -0.00596
CFLAllSpcPGEComExCZ16 | Com-Iltg-dWatt-CFL_OSspc | PGE | Com | Ex | CZ16 | 2.6012 | 0.00043186 | 0 | 2.5388 | 0.00050465 | -0.027591 | 2.6012 | 0.00043186 | 0 | 2.5388 | 0.00050465 | -0.027591 |  | CFL | AllSpc | 2600 | 0.432 | 2600 | 0.432 | 0.976 | 1.17 | -0.010607 | 2600 | 0.432 | 2600 | 0.432 | 0.976 | 1.17 | -0.0106
CFLAllSpcPGEComExIOU | Com-Iltg-dWatt-CFL_OSspc | PGE | Com | Ex | IOU | 2.7996 | 0.00048468 | 0 | 2.9682 | 0.00058984 | -0.018556 | 2.7996 | 0.00048468 | 0 | 2.9682 | 0.00058984 | -0.018556 |  | CFL | AllSpc | 2800 | 0.485 | 2800 | 0.485 | 1.06 | 1.22 | -0.0066283 | 2800 | 0.485 | 2800 | 0.485 | 1.06 | 1.22 | -0.00663
CFLAllSpcPGEComNewCZ05 | Com-Iltg-dWatt-CFL_OSspc | PGE | Com | New | CZ05 | 2.6614 | 0.00049318 | 0 | 2.7586 | 0.00059616 | -0.019337 | 2.6614 | 0.00049318 | 0 | 2.7586 | 0.00059616 | -0.019337 |  | CFL | AllSpc | 2660 | 0.493 | 2660 | 0.493 | 1.04 | 1.21 | -0.0072658 | 2660 | 0.493 | 2660 | 0.493 | 1.04 | 1.21 | -0.00727
CFLAllSpcPGEComNewCZ11 | Com-Iltg-dWatt-CFL_OSspc | PGE | Com | New | CZ11 | 2.8408 | 0.00047081 | 0 | 3.0099 | 0.00057633 | -0.018669 | 2.8408 | 0.00047081 | 0 | 3.0099 | 0.00057633 | -0.018669 |  | CFL | AllSpc | 2840 | 0.471 | 2840 | 0.471 | 1.06 | 1.22 | -0.0065719 | 2840 | 0.471 | 2840 | 0.471 | 1.06 | 1.22 | -0.00657
CFLAllSpcPGEComNewCZ12 | Com-Iltg-dWatt-CFL_OSspc | PGE | Com | New | CZ12 | 2.8617 | 0.00048395 | 0 | 3.0313 | 0.00058893 | -0.018082 | 2.8617 | 0.00048395 | 0 | 3.0313 | 0.00058893 | -0.018082 |  | CFL | AllSpc | 2860 | 0.484 | 2860 | 0.484 | 1.06 | 1.22 | -0.0063186 | 2860 | 0.484 | 2860 | 0.484 | 1.06 | 1.22 | -0.00632
CFLAllSpcPGEComNewCZ13 | Com-Iltg-dWatt-CFL_OSspc | PGE | Com | New | CZ13 | 2.8985 | 0.00047949 | 0 | 3.1237 | 0.00058191 | -0.016937 | 2.8985 | 0.00047949 | 0 | 3.1237 | 0.00058191 | -0.016937 |  | CFL | AllSpc | 2900 | 0.479 | 2900 | 0.479 | 1.08 | 1.21 | -0.0058433 | 2900 | 0.479 | 2900 | 0.479 | 1.08 | 1.21 | -0.00584
CFLAllSpcPGEComNewCZ16 | Com-Iltg-dWatt-CFL_OSspc | PGE | Com | New | CZ16 | 2.5776 | 0.00043125 | 0 | 2.5119 | 0.00050166 | -0.025987 | 2.5776 | 0.00043125 | 0 | 2.5119 | 0.00050166 | -0.025987 |  | CFL | AllSpc | 2580 | 0.431 | 2580 | 0.431 | 0.975 | 1.16 | -0.010082 | 2580 | 0.431 | 2580 | 0.431 | 0.975 | 1.16 | -0.0101
CFLAllSpcPGEComNewIOU | Com-Iltg-dWatt-CFL_OSspc | PGE | Com | New | IOU | 2.8292 | 0.0004908 | 0 | 2.9808 | 0.00059654 | -0.018107 | 2.8292 | 0.0004908 | 0 | 2.9808 | 0.00059654 | -0.018107 |  | CFL | AllSpc | 2830 | 0.491 | 2830 | 0.491 | 1.05 | 1.22 | -0.0063999 | 2830 | 0.491 | 2830 | 0.491 | 1.05 | 1.22 | -0.0064
CFLAllSpcPGEECCExCZ01 | Com-Iltg-dWatt-CFL_OSspc | PGE | ECC | Ex | CZ01 | 2.22 | 0.000532 | 0 | 2.28 | 0.00064997 | -0.044 | 2.22 | 0.000532 | 0 | 2.28 | 0.00064997 | -0.044 |  | CFL | AllSpc | 2220 | 0.532 | 2220 | 0.532 | 1.03 | 1.22 | -0.01982 | 2220 | 0.532 | 2220 | 0.532 | 1.03 | 1.22 | -0.0198
CFLAllSpcPGEECCExCZ02 | Com-Iltg-dWatt-CFL_OSspc | PGE | ECC | Ex | CZ02 | 2.22 | 0.00034595 | 0 | 2.42 | 0.000455 | -0.0269 | 2.22 | 0.00034595 | 0 | 2.42 | 0.000455 | -0.0269 |  | CFL | AllSpc | 2220 | 0.346 | 2220 | 0.346 | 1.09 | 1.32 | -0.012117 | 2220 | 0.346 | 2220 | 0.346 | 1.09 | 1.32 | -0.0121
CFLAllSpcPGEECCExCZ03 | Com-Iltg-dWatt-CFL_OSspc | PGE | ECC | Ex | CZ03 | 2.22 | 0.00034596 | 0 | 2.4 | 0.00043 | -0.028 | 2.22 | 0.00034596 | 0 | 2.4 | 0.00043 | -0.028 |  | CFL | AllSpc | 2220 | 0.346 | 2220 | 0.346 | 1.08 | 1.24 | -0.012613 | 2220 | 0.346 | 2220 | 0.346 | 1.08 | 1.24 | -0.0126
CFLAllSpcPGEECCExCZ04 | Com-Iltg-dWatt-CFL_OSspc | PGE | ECC | Ex | CZ04 | 2.22 | 0.000532 | 0 | 2.45 | 0.00069195 | -0.021405 | 2.22 | 0.000532 | 0 | 2.45 | 0.00069195 | -0.021405 |  | CFL | AllSpc | 2220 | 0.532 | 2220 | 0.532 | 1.1 | 1.3 | -0.009642 | 2220 | 0.532 | 2220 | 0.532 | 1.1 | 1.3 | -0.00964
CFLAllSpcPGEECCExCZ05 | Com-Iltg-dWatt-CFL_OSspc | PGE | ECC | Ex | CZ05 | 2.22 | 0.000532 | 0 | 2.39 | 0.00065695 | -0.0273 | 2.22 | 0.000532 | 0 | 2.39 | 0.00065695 | -0.0273 |  | CFL | AllSpc | 2220 | 0.532 | 2220 | 0.532 | 1.08 | 1.23 | -0.012297 | 2220 | 0.532 | 2220 | 0.532 | 1.08 | 1.23 | -0.0123
CFLAllSpcPGEECCExCZ11 | Com-Iltg-dWatt-CFL_OSspc | PGE | ECC | Ex | CZ11 | 2.22 | 0.00034594 | 0 | 2.48 | 0.00043 | -0.024606 | 2.22 | 0.00034594 | 0 | 2.48 | 0.00043 | -0.024606 |  | CFL | AllSpc | 2220 | 0.346 | 2220 | 0.346 | 1.12 | 1.24 | -0.011084 | 2220 | 0.346 | 2220 | 0.346 | 1.12 | 1.24 | -0.0111
CFLAllSpcPGEECCExCZ12 | Com-Iltg-dWatt-CFL_OSspc | PGE | ECC | Ex | CZ12 | 2.22 | 0.00034594 | 0 | 2.46 | 0.000434 | -0.0242 | 2.22 | 0.00034594 | 0 | 2.46 | 0.000434 | -0.0242 |  | CFL | AllSpc | 2220 | 0.346 | 2220 | 0.346 | 1.11 | 1.25 | -0.010901 | 2220 | 0.346 | 2220 | 0.346 | 1.11 | 1.25 | -0.0109
CFLAllSpcPGEECCExCZ13 | Com-Iltg-dWatt-CFL_OSspc | PGE | ECC | Ex | CZ13 | 2.22 | 0.00034594 | 0 | 2.5 | 0.00045494 | -0.0214 | 2.22 | 0.00034594 | 0 | 2.5 | 0.00045494 | -0.0214 |  | CFL | AllSpc | 2220 | 0.346 | 2220 | 0.346 | 1.13 | 1.32 | -0.0096396 | 2220 | 0.346 | 2220 | 0.346 | 1.13 | 1.32 | -0.00964
CFLAllSpcPGEECCExCZ16 | Com-Iltg-dWatt-CFL_OSspc | PGE | ECC | Ex | CZ16 | 2.22 | 0.00034595 | 0 | 2.34 | 0.000409 | -0.0384 | 2.22 | 0.00034595 | 0 | 2.34 | 0.000409 | -0.0384 |  | CFL | AllSpc | 2220 | 0.346 | 2220 | 0.346 | 1.05 | 1.18 | -0.017297 | 2220 | 0.346 | 2220 | 0.346 | 1.05 | 1.18 | -0.0173
CFLAllSpcPGEECCExIOU | Com-Iltg-dWatt-CFL_OSspc | PGE | ECC | Ex | IOU | 2.22 | 0.00038143 | 0 | 2.4304 | 0.00048204 | -0.02605 | 2.22 | 0.00038143 | 0 | 2.4304 | 0.00048204 | -0.02605 |  | CFL | AllSpc | 2220 | 0.381 | 2220 | 0.381 | 1.09 | 1.26 | -0.011734 | 2220 | 0.381 | 2220 | 0.381 | 1.09 | 1.26 | -0.0117
CFLAllSpcPGEECCNewCZ01 | Com-Iltg-dWatt-CFL_OSspc | PGE | ECC | New | CZ01 | 2.22 | 0.000532 | 0 | 2.27 | 0.000621 | -0.0453 | 2.22 | 0.000532 | 0 | 2.27 | 0.000621 | -0.0453 |  | CFL | AllSpc | 2220 | 0.532 | 2220 | 0.532 | 1.02 | 1.17 | -0.020405 | 2220 | 0.532 | 2220 | 0.532 | 1.02 | 1.17 | -0.0204
CFLAllSpcPGEECCNewCZ02 | Com-Iltg-dWatt-CFL_OSspc | PGE | ECC | New | CZ02 | 2.22 | 0.000345 | 0 | 2.4 | 0.00047 | -0.0275 | 2.22 | 0.000345 | 0 | 2.4 | 0.00047 | -0.0275 |  | CFL | AllSpc | 2220 | 0.345 | 2220 | 0.345 | 1.08 | 1.36 | -0.012387 | 2220 | 0.345 | 2220 | 0.345 | 1.08 | 1.36 | -0.0124
CFLAllSpcPGEECCNewCZ03 | Com-Iltg-dWatt-CFL_OSspc | PGE | ECC | New | CZ03 | 2.22 | 0.000345 | 0 | 2.36 | 0.000452 | -0.0302 | 2.22 | 0.000345 | 0 | 2.36 | 0.000452 | -0.0302 |  | CFL | AllSpc | 2220 | 0.345 | 2220 | 0.345 | 1.06 | 1.31 | -0.013604 | 2220 | 0.345 | 2220 | 0.345 | 1.06 | 1.31 | -0.0136
CFLAllSpcPGEECCNewCZ04 | Com-Iltg-dWatt-CFL_OSspc | PGE | ECC | New | CZ04 | 2.22 | 0.000532 | 0 | 2.43 | 0.000676 | -0.0222 | 2.22 | 0.000532 | 0 | 2.43 | 0.000676 | -0.0222 |  | CFL | AllSpc | 2220 | 0.532 | 2220 | 0.532 | 1.09 | 1.27 | -0.01 | 2220 | 0.532 | 2220 | 0.532 | 1.09 | 1.27 | -0.01
CFLAllSpcPGEECCNewCZ05 | Com-Iltg-dWatt-CFL_OSspc | PGE | ECC | New | CZ05 | 2.22 | 0.000532 | 0 | 2.36 | 0.000652 | -0.0293 | 2.22 | 0.000532 | 0 | 2.36 | 0.000652 | -0.0293 |  | CFL | AllSpc | 2220 | 0.532 | 2220 | 0.532 | 1.06 | 1.23 | -0.013198 | 2220 | 0.532 | 2220 | 0.532 | 1.06 | 1.23 | -0.0132
CFLAllSpcPGEECCNewCZ11 | Com-Iltg-dWatt-CFL_OSspc | PGE | ECC | New | CZ11 | 2.22 | 0.000345 | 0 | 2.47 | 0.000461 | -0.0231 | 2.22 | 0.000345 | 0 | 2.47 | 0.000461 | -0.0231 |  | CFL | AllSpc | 2220 | 0.345 | 2220 | 0.345 | 1.11 | 1.34 | -0.010405 | 2220 | 0.345 | 2220 | 0.345 | 1.11 | 1.34 | -0.0104
CFLAllSpcPGEECCNewCZ12 | Com-Iltg-dWatt-CFL_OSspc | PGE | ECC | New | CZ12 | 2.22 | 0.000345 | 0 | 2.45 | 0.000471 | -0.0235 | 2.22 | 0.000345 | 0 | 2.45 | 0.000471 | -0.0235 |  | CFL | AllSpc | 2220 | 0.345 | 2220 | 0.345 | 1.1 | 1.37 | -0.010586 | 2220 | 0.345 | 2220 | 0.345 | 1.1 | 1.37 | -0.0106
CFLAllSpcPGEECCNewCZ13 | Com-Iltg-dWatt-CFL_OSspc | PGE | ECC | New | CZ13 | 2.22 | 0.000345 | 0 | 2.49 | 0.000466 | -0.0201 | 2.22 | 0.000345 | 0 | 2.49 | 0.000466 | -0.0201 |  | CFL | AllSpc | 2220 | 0.345 | 2220 | 0.345 | 1.12 | 1.35 | -0.0090541 | 2220 | 0.345 | 2220 | 0.345 | 1.12 | 1.35 | -0.00905
CFLAllSpcPGEECCNewCZ16 | Com-Iltg-dWatt-CFL_OSspc | PGE | ECC | New | CZ16 | 2.22 | 0.000345 | 0 | 2.33 | 0.000447 | -0.0369 | 2.22 | 0.000345 | 0 | 2.33 | 0.000447 | -0.0369 |  | CFL | AllSpc | 2220 | 0.345 | 2220 | 0.345 | 1.05 | 1.3 | -0.016622 | 2220 | 0.345 | 2220 | 0.345 | 1.05 | 1.3 | -0.0166
CFLAllSpcPGEECCNewIOU | Com-Iltg-dWatt-CFL_OSspc | PGE | ECC | New | IOU | 2.22 | 0.00038088 | 0 | 2.418 | 0.00050009 | -0.025752 | 2.22 | 0.00038088 | 0 | 2.418 | 0.00050009 | -0.025752 |  | CFL | AllSpc | 2220 | 0.381 | 2220 | 0.381 | 1.09 | 1.31 | -0.0116 | 2220 | 0.381 | 2220 | 0.381 | 1.09 | 1.31 | -0.0116
CFLAllSpcPGEEPrExCZ01 | Com-Iltg-dWatt-CFL_OSspc | PGE | EPr | Ex | CZ01 | 2.05 | 0.00054427 | 0 | 2.02 | 0.00064734 | -0.0368 | 2.05 | 0.00054427 | 0 | 2.02 | 0.00064734 | -0.0368 |  | CFL | AllSpc | 2050 | 0.544 | 2050 | 0.544 | 0.985 | 1.19 | -0.017951 | 2050 | 0.544 | 2050 | 0.544 | 0.985 | 1.19 | -0.018
CFLAllSpcPGEEPrExCZ02 | Com-Iltg-dWatt-CFL_OSspc | PGE | EPr | Ex | CZ02 | 2.05 | 1.7306e-05 | 0 | 2.15 | 1.7306e-05 | -0.0221 | 2.05 | 1.7306e-05 | 0 | 2.15 | 1.7306e-05 | -0.0221 |  | CFL | AllSpc | 2050 | 0.0173 | 2050 | 0.0173 | 1.05 | 1 | -0.01078 | 2050 | 0.0173 | 2050 | 0.0173 | 1.05 | 1 | -0.0108
CFLAllSpcPGEEPrExCZ03 | Com-Iltg-dWatt-CFL_OSspc | PGE | EPr | Ex | CZ03 | 2.05 | 1.7305e-05 | 0 | 2.17 | 1.7305e-05 | -0.0215 | 2.05 | 1.7305e-05 | 0 | 2.17 | 1.7305e-05 | -0.0215 |  | CFL | AllSpc | 2050 | 0.0173 | 2050 | 0.0173 | 1.06 | 1 | -0.010488 | 2050 | 0.0173 | 2050 | 0.0173 | 1.06 | 1 | -0.0105
CFLAllSpcPGEEPrExCZ04 | Com-Iltg-dWatt-CFL_OSspc | PGE | EPr | Ex | CZ04 | 2.05 | 0.00054422 | 0 | 2.2 | 0.00066725 | -0.017 | 2.05 | 0.00054422 | 0 | 2.2 | 0.00066725 | -0.017 |  | CFL | AllSpc | 2050 | 0.544 | 2050 | 0.544 | 1.07 | 1.23 | -0.0082927 | 2050 | 0.544 | 2050 | 0.544 | 1.07 | 1.23 | -0.00829
CFLAllSpcPGEEPrExCZ05 | Com-Iltg-dWatt-CFL_OSspc | PGE | EPr | Ex | CZ05 | 2.05 | 0.00054422 | 0 | 2.17 | 0.00065325 | -0.0203 | 2.05 | 0.00054422 | 0 | 2.17 | 0.00065325 | -0.0203 |  | CFL | AllSpc | 2050 | 0.544 | 2050 | 0.544 | 1.06 | 1.2 | -0.0099024 | 2050 | 0.544 | 2050 | 0.544 | 1.06 | 1.2 | -0.0099
CFLAllSpcPGEEPrExCZ11 | Com-Iltg-dWatt-CFL_OSspc | PGE | EPr | Ex | CZ11 | 2.05 | 1.7312e-05 | 0 | 2.17 | 1.7312e-05 | -0.0202 | 2.05 | 1.7312e-05 | 0 | 2.17 | 1.7312e-05 | -0.0202 |  | CFL | AllSpc | 2050 | 0.0173 | 2050 | 0.0173 | 1.06 | 1 | -0.0098537 | 2050 | 0.0173 | 2050 | 0.0173 | 1.06 | 1 | -0.00985
CFLAllSpcPGEEPrExCZ12 | Com-Iltg-dWatt-CFL_OSspc | PGE | EPr | Ex | CZ12 | 2.05 | 1.731e-05 | 0 | 2.17 | 1.731e-05 | -0.0211 | 2.05 | 1.731e-05 | 0 | 2.17 | 1.731e-05 | -0.0211 |  | CFL | AllSpc | 2050 | 0.0173 | 2050 | 0.0173 | 1.06 | 1 | -0.010293 | 2050 | 0.0173 | 2050 | 0.0173 | 1.06 | 1 | -0.0103
CFLAllSpcPGEEPrExCZ13 | Com-Iltg-dWatt-CFL_OSspc | PGE | EPr | Ex | CZ13 | 2.05 | 1.7311e-05 | 0 | 2.19 | 1.7311e-05 | -0.0183 | 2.05 | 1.7311e-05 | 0 | 2.19 | 1.7311e-05 | -0.0183 |  | CFL | AllSpc | 2050 | 0.0173 | 2050 | 0.0173 | 1.07 | 1 | -0.0089268 | 2050 | 0.0173 | 2050 | 0.0173 | 1.07 | 1 | -0.00893
CFLAllSpcPGEEPrExCZ16 | Com-Iltg-dWatt-CFL_OSspc | PGE | EPr | Ex | CZ16 | 2.05 | 1.7311e-05 | 0 | 1.99 | 1.7311e-05 | -0.0364 | 2.05 | 1.7311e-05 | 0 | 1.99 | 1.7311e-05 | -0.0364 |  | CFL | AllSpc | 2050 | 0.0173 | 2050 | 0.0173 | 0.971 | 1 | -0.017756 | 2050 | 0.0173 | 2050 | 0.0173 | 0.971 | 1 | -0.0178
CFLAllSpcPGEEPrExIOU | Com-Iltg-dWatt-CFL_OSspc | PGE | EPr | Ex | IOU | 2.05 | 0.00011003 | 0 | 2.173 | 0.00013119 | -0.020452 | 2.05 | 0.00011003 | 0 | 2.173 | 0.00013119 | -0.020452 |  | CFL | AllSpc | 2050 | 0.11 | 2050 | 0.11 | 1.06 | 1.19 | -0.0099764 | 2050 | 0.11 | 2050 | 0.11 | 1.06 | 1.19 | -0.00998
CFLAllSpcPGEEPrNewCZ01 | Com-Iltg-dWatt-CFL_OSspc | PGE | EPr | New | CZ01 | 2.05 | 0.000551 | 0 | 2.01 | 0.000634 | -0.0436 | 2.05 | 0.000551 | 0 | 2.01 | 0.000634 | -0.0436 |  | CFL | AllSpc | 2050 | 0.551 | 2050 | 0.551 | 0.98 | 1.15 | -0.021268 | 2050 | 0.551 | 2050 | 0.551 | 0.98 | 1.15 | -0.0213
CFLAllSpcPGEEPrNewCZ02 | Com-Iltg-dWatt-CFL_OSspc | PGE | EPr | New | CZ02 | 2.05 | 1.75e-05 | 0 | 2.13 | 1.75e-05 | -0.028 | 2.05 | 1.75e-05 | 0 | 2.13 | 1.75e-05 | -0.028 |  | CFL | AllSpc | 2050 | 0.0175 | 2050 | 0.0175 | 1.04 | 1 | -0.013659 | 2050 | 0.0175 | 2050 | 0.0175 | 1.04 | 1 | -0.0137
CFLAllSpcPGEEPrNewCZ03 | Com-Iltg-dWatt-CFL_OSspc | PGE | EPr | New | CZ03 | 2.05 | 1.75e-05 | 0 | 2.11 | 1.75e-05 | -0.0266 | 2.05 | 1.75e-05 | 0 | 2.11 | 1.75e-05 | -0.0266 |  | CFL | AllSpc | 2050 | 0.0175 | 2050 | 0.0175 | 1.03 | 1 | -0.012976 | 2050 | 0.0175 | 2050 | 0.0175 | 1.03 | 1 | -0.013
CFLAllSpcPGEEPrNewCZ04 | Com-Iltg-dWatt-CFL_OSspc | PGE | EPr | New | CZ04 | 2.05 | 0.000551 | 0 | 2.17 | 0.000716 | -0.0217 | 2.05 | 0.000551 | 0 | 2.17 | 0.000716 | -0.0217 |  | CFL | AllSpc | 2050 | 0.551 | 2050 | 0.551 | 1.06 | 1.3 | -0.010585 | 2050 | 0.551 | 2050 | 0.551 | 1.06 | 1.3 | -0.0106
CFLAllSpcPGEEPrNewCZ05 | Com-Iltg-dWatt-CFL_OSspc | PGE | EPr | New | CZ05 | 2.05 | 0.000551 | 0 | 2.12 | 0.00068 | -0.0221 | 2.05 | 0.000551 | 0 | 2.12 | 0.00068 | -0.0221 |  | CFL | AllSpc | 2050 | 0.551 | 2050 | 0.551 | 1.03 | 1.23 | -0.01078 | 2050 | 0.551 | 2050 | 0.551 | 1.03 | 1.23 | -0.0108
CFLAllSpcPGEEPrNewCZ11 | Com-Iltg-dWatt-CFL_OSspc | PGE | EPr | New | CZ11 | 2.05 | 1.75e-05 | 0 | 2.2 | 1.75e-05 | -0.0246 | 2.05 | 1.75e-05 | 0 | 2.2 | 1.75e-05 | -0.0246 |  | CFL | AllSpc | 2050 | 0.0175 | 2050 | 0.0175 | 1.07 | 1 | -0.012 | 2050 | 0.0175 | 2050 | 0.0175 | 1.07 | 1 | -0.012
CFLAllSpcPGEEPrNewCZ12 | Com-Iltg-dWatt-CFL_OSspc | PGE | EPr | New | CZ12 | 2.05 | 1.75e-05 | 0 | 2.17 | 1.75e-05 | -0.0252 | 2.05 | 1.75e-05 | 0 | 2.17 | 1.75e-05 | -0.0252 |  | CFL | AllSpc | 2050 | 0.0175 | 2050 | 0.0175 | 1.06 | 1 | -0.012293 | 2050 | 0.0175 | 2050 | 0.0175 | 1.06 | 1 | -0.0123
CFLAllSpcPGEEPrNewCZ13 | Com-Iltg-dWatt-CFL_OSspc | PGE | EPr | New | CZ13 | 2.05 | 1.75e-05 | 0 | 2.21 | 1.75e-05 | -0.0225 | 2.05 | 1.75e-05 | 0 | 2.21 | 1.75e-05 | -0.0225 |  | CFL | AllSpc | 2050 | 0.0175 | 2050 | 0.0175 | 1.08 | 1 | -0.010976 | 2050 | 0.0175 | 2050 | 0.0175 | 1.08 | 1 | -0.011
CFLAllSpcPGEEPrNewCZ16 | Com-Iltg-dWatt-CFL_OSspc | PGE | EPr | New | CZ16 | 2.05 | 1.75e-05 | 0 | 2.04 | 1.75e-05 | -0.0321 | 2.05 | 1.75e-05 | 0 | 2.04 | 1.75e-05 | -0.0321 |  | CFL | AllSpc | 2050 | 0.0175 | 2050 | 0.0175 | 0.995 | 1 | -0.015659 | 2050 | 0.0175 | 2050 | 0.0175 | 0.995 | 1 | -0.0157
CFLAllSpcPGEEPrNewIOU | Com-Iltg-dWatt-CFL_OSspc | PGE | EPr | New | IOU | 2.05 | 9.2749e-05 | 0 | 2.1654 | 0.00011466 | -0.024736 | 2.05 | 9.2749e-05 | 0 | 2.1654 | 0.00011466 | -0.024736 |  | CFL | AllSpc | 2050 | 0.0927 | 2050 | 0.0927 | 1.06 | 1.24 | -0.012066 | 2050 | 0.0927 | 2050 | 0.0927 | 1.06 | 1.24 | -0.0121
CFLAllSpcPGEERCExCZ01 | Com-Iltg-dWatt-CFL_OSspc | PGE | ERC | Ex | CZ01 | 2.39 | 0.0006233 | 0 | 2.32 | 0.00073938 | -0.0398 | 2.39 | 0.0006233 | 0 | 2.32 | 0.00073938 | -0.0398 |  | CFL | AllSpc | 2390 | 0.623 | 2390 | 0.623 | 0.971 | 1.19 | -0.016653 | 2390 | 0.623 | 2390 | 0.623 | 0.971 | 1.19 | -0.0167
CFLAllSpcPGEERCExCZ02 | Com-Iltg-dWatt-CFL_OSspc | PGE | ERC | Ex | CZ02 | 2.39 | 1.8006e-05 | 0 | 2.41 | 1.8006e-05 | -0.0286 | 2.39 | 1.8006e-05 | 0 | 2.41 | 1.8006e-05 | -0.0286 |  | CFL | AllSpc | 2390 | 0.018 | 2390 | 0.018 | 1.01 | 1 | -0.011967 | 2390 | 0.018 | 2390 | 0.018 | 1.01 | 1 | -0.012
CFLAllSpcPGEERCExCZ03 | Com-Iltg-dWatt-CFL_OSspc | PGE | ERC | Ex | CZ03 | 2.39 | 1.8005e-05 | 0 | 2.41 | 1.8005e-05 | -0.0267 | 2.39 | 1.8005e-05 | 0 | 2.41 | 1.8005e-05 | -0.0267 |  | CFL | AllSpc | 2390 | 0.018 | 2390 | 0.018 | 1.01 | 1 | -0.011172 | 2390 | 0.018 | 2390 | 0.018 | 1.01 | 1 | -0.0112
CFLAllSpcPGEERCExCZ04 | Com-Iltg-dWatt-CFL_OSspc | PGE | ERC | Ex | CZ04 | 2.39 | 0.00062325 | 0 | 2.48 | 0.00074832 | -0.0224 | 2.39 | 0.00062325 | 0 | 2.48 | 0.00074832 | -0.0224 |  | CFL | AllSpc | 2390 | 0.623 | 2390 | 0.623 | 1.04 | 1.2 | -0.0093724 | 2390 | 0.623 | 2390 | 0.623 | 1.04 | 1.2 | -0.00937
CFLAllSpcPGEERCExCZ05 | Com-Iltg-dWatt-CFL_OSspc | PGE | ERC | Ex | CZ05 | 2.39 | 0.00062325 | 0 | 2.42 | 0.00074435 | -0.0265 | 2.39 | 0.00062325 | 0 | 2.42 | 0.00074435 | -0.0265 |  | CFL | AllSpc | 2390 | 0.623 | 2390 | 0.623 | 1.01 | 1.19 | -0.011088 | 2390 | 0.623 | 2390 | 0.623 | 1.01 | 1.19 | -0.0111
CFLAllSpcPGEERCExCZ11 | Com-Iltg-dWatt-CFL_OSspc | PGE | ERC | Ex | CZ11 | 2.39 | 1.8012e-05 | 0 | 2.47 | 1.8012e-05 | -0.0241 | 2.39 | 1.8012e-05 | 0 | 2.47 | 1.8012e-05 | -0.0241 |  | CFL | AllSpc | 2390 | 0.018 | 2390 | 0.018 | 1.03 | 1 | -0.010084 | 2390 | 0.018 | 2390 | 0.018 | 1.03 | 1 | -0.0101
CFLAllSpcPGEERCExCZ12 | Com-Iltg-dWatt-CFL_OSspc | PGE | ERC | Ex | CZ12 | 2.39 | 1.801e-05 | 0 | 2.46 | 1.801e-05 | -0.0255 | 2.39 | 1.801e-05 | 0 | 2.46 | 1.801e-05 | -0.0255 |  | CFL | AllSpc | 2390 | 0.018 | 2390 | 0.018 | 1.03 | 1 | -0.010669 | 2390 | 0.018 | 2390 | 0.018 | 1.03 | 1 | -0.0107
CFLAllSpcPGEERCExCZ13 | Com-Iltg-dWatt-CFL_OSspc | PGE | ERC | Ex | CZ13 | 2.39 | 1.8011e-05 | 0 | 2.5 | 1.8011e-05 | -0.0228 | 2.39 | 1.8011e-05 | 0 | 2.5 | 1.8011e-05 | -0.0228 |  | CFL | AllSpc | 2390 | 0.018 | 2390 | 0.018 | 1.05 | 1 | -0.0095397 | 2390 | 0.018 | 2390 | 0.018 | 1.05 | 1 | -0.00954
CFLAllSpcPGEERCExCZ16 | Com-Iltg-dWatt-CFL_OSspc | PGE | ERC | Ex | CZ16 | 2.39 | 1.8011e-05 | 0 | 2.35 | 1.8011e-05 | -0.0384 | 2.39 | 1.8011e-05 | 0 | 2.35 | 1.8011e-05 | -0.0384 |  | CFL | AllSpc | 2390 | 0.018 | 2390 | 0.018 | 0.983 | 1 | -0.016067 | 2390 | 0.018 | 2390 | 0.018 | 0.983 | 1 | -0.0161
CFLAllSpcPGEERCExIOU | Com-Iltg-dWatt-CFL_OSspc | PGE | ERC | Ex | IOU | 2.39 | 0.00012451 | 0 | 2.4489 | 0.00014635 | -0.025369 | 2.39 | 0.00012451 | 0 | 2.4489 | 0.00014635 | -0.025369 |  | CFL | AllSpc | 2390 | 0.125 | 2390 | 0.125 | 1.02 | 1.18 | -0.010615 | 2390 | 0.125 | 2390 | 0.125 | 1.02 | 1.18 | -0.0106
CFLAllSpcPGEERCNewCZ01 | Com-Iltg-dWatt-CFL_OSspc | PGE | ERC | New | CZ01 | 2.39 | 0.000631 | 0 | 2.45 | 0.000747 | -0.047 | 2.39 | 0.000631 | 0 | 2.45 | 0.000747 | -0.047 |  | CFL | AllSpc | 2390 | 0.631 | 2390 | 0.631 | 1.03 | 1.18 | -0.019665 | 2390 | 0.631 | 2390 | 0.631 | 1.03 | 1.18 | -0.0197
CFLAllSpcPGEERCNewCZ02 | Com-Iltg-dWatt-CFL_OSspc | PGE | ERC | New | CZ02 | 2.39 | 1.82e-05 | 0 | 2.56 | 1.82e-05 | -0.031 | 2.39 | 1.82e-05 | 0 | 2.56 | 1.82e-05 | -0.031 |  | CFL | AllSpc | 2390 | 0.0182 | 2390 | 0.0182 | 1.07 | 1 | -0.012971 | 2390 | 0.0182 | 2390 | 0.0182 | 1.07 | 1 | -0.013
CFLAllSpcPGEERCNewCZ03 | Com-Iltg-dWatt-CFL_OSspc | PGE | ERC | New | CZ03 | 2.39 | 1.82e-05 | 0 | 2.56 | 1.82e-05 | -0.0284 | 2.39 | 1.82e-05 | 0 | 2.56 | 1.82e-05 | -0.0284 |  | CFL | AllSpc | 2390 | 0.0182 | 2390 | 0.0182 | 1.07 | 1 | -0.011883 | 2390 | 0.0182 | 2390 | 0.0182 | 1.07 | 1 | -0.0119
CFLAllSpcPGEERCNewCZ04 | Com-Iltg-dWatt-CFL_OSspc | PGE | ERC | New | CZ04 | 2.39 | 0.000631 | 0 | 2.63 | 0.000797 | -0.0246 | 2.39 | 0.000631 | 0 | 2.63 | 0.000797 | -0.0246 |  | CFL | AllSpc | 2390 | 0.631 | 2390 | 0.631 | 1.1 | 1.26 | -0.010293 | 2390 | 0.631 | 2390 | 0.631 | 1.1 | 1.26 | -0.0103
CFLAllSpcPGEERCNewCZ05 | Com-Iltg-dWatt-CFL_OSspc | PGE | ERC | New | CZ05 | 2.39 | 0.000631 | 0 | 2.55 | 0.000809 | -0.0272 | 2.39 | 0.000631 | 0 | 2.55 | 0.000809 | -0.0272 |  | CFL | AllSpc | 2390 | 0.631 | 2390 | 0.631 | 1.07 | 1.28 | -0.011381 | 2390 | 0.631 | 2390 | 0.631 | 1.07 | 1.28 | -0.0114
CFLAllSpcPGEERCNewCZ11 | Com-Iltg-dWatt-CFL_OSspc | PGE | ERC | New | CZ11 | 2.39 | 1.82e-05 | 0 | 2.68 | 1.82e-05 | -0.0284 | 2.39 | 1.82e-05 | 0 | 2.68 | 1.82e-05 | -0.0284 |  | CFL | AllSpc | 2390 | 0.0182 | 2390 | 0.0182 | 1.12 | 1 | -0.011883 | 2390 | 0.0182 | 2390 | 0.0182 | 1.12 | 1 | -0.0119
CFLAllSpcPGEERCNewCZ12 | Com-Iltg-dWatt-CFL_OSspc | PGE | ERC | New | CZ12 | 2.39 | 1.82e-05 | 0 | 2.63 | 1.82e-05 | -0.0289 | 2.39 | 1.82e-05 | 0 | 2.63 | 1.82e-05 | -0.0289 |  | CFL | AllSpc | 2390 | 0.0182 | 2390 | 0.0182 | 1.1 | 1 | -0.012092 | 2390 | 0.0182 | 2390 | 0.0182 | 1.1 | 1 | -0.0121
CFLAllSpcPGEERCNewCZ13 | Com-Iltg-dWatt-CFL_OSspc | PGE | ERC | New | CZ13 | 2.39 | 1.82e-05 | 0 | 2.67 | 1.82e-05 | -0.0253 | 2.39 | 1.82e-05 | 0 | 2.67 | 1.82e-05 | -0.0253 |  | CFL | AllSpc | 2390 | 0.0182 | 2390 | 0.0182 | 1.12 | 1 | -0.010586 | 2390 | 0.0182 | 2390 | 0.0182 | 1.12 | 1 | -0.0106
CFLAllSpcPGEERCNewCZ16 | Com-Iltg-dWatt-CFL_OSspc | PGE | ERC | New | CZ16 | 2.39 | 1.82e-05 | 0 | 2.45 | 1.82e-05 | -0.0439 | 2.39 | 1.82e-05 | 0 | 2.45 | 1.82e-05 | -0.0439 |  | CFL | AllSpc | 2390 | 0.0182 | 2390 | 0.0182 | 1.03 | 1 | -0.018368 | 2390 | 0.0182 | 2390 | 0.0182 | 1.03 | 1 | -0.0184
CFLAllSpcPGEERCNewIOU | Com-Iltg-dWatt-CFL_OSspc | PGE | ERC | New | IOU | 2.39 | 0.00010463 | 0 | 2.6226 | 0.00012776 | -0.027908 | 2.39 | 0.00010463 | 0 | 2.6226 | 0.00012776 | -0.027908 |  | CFL | AllSpc | 2390 | 0.105 | 2390 | 0.105 | 1.1 | 1.22 | -0.011677 | 2390 | 0.105 | 2390 | 0.105 | 1.1 | 1.22 | -0.0117
CFLAllSpcPGEESeExCZ01 | Com-Iltg-dWatt-CFL_OSspc | PGE | ESe | Ex | CZ01 | 2.12 | 0.00062031 | 0 | 2.06 | 0.00073434 | -0.0433 | 2.12 | 0.00062031 | 0 | 2.06 | 0.00073434 | -0.0433 |  | CFL | AllSpc | 2120 | 0.62 | 2120 | 0.62 | 0.972 | 1.18 | -0.020425 | 2120 | 0.62 | 2120 | 0.62 | 0.972 | 1.18 | -0.0204
CFLAllSpcPGEESeExCZ02 | Com-Iltg-dWatt-CFL_OSspc | PGE | ESe | Ex | CZ02 | 2.12 | 1.7309e-05 | 0 | 2.21 | 1.7309e-05 | -0.0272 | 2.12 | 1.7309e-05 | 0 | 2.21 | 1.7309e-05 | -0.0272 |  | CFL | AllSpc | 2120 | 0.0173 | 2120 | 0.0173 | 1.04 | 1 | -0.01283 | 2120 | 0.0173 | 2120 | 0.0173 | 1.04 | 1 | -0.0128
CFLAllSpcPGEESeExCZ03 | Com-Iltg-dWatt-CFL_OSspc | PGE | ESe | Ex | CZ03 | 2.12 | 1.7307e-05 | 0 | 2.21 | 1.7307e-05 | -0.028 | 2.12 | 1.7307e-05 | 0 | 2.21 | 1.7307e-05 | -0.028 |  | CFL | AllSpc | 2120 | 0.0173 | 2120 | 0.0173 | 1.04 | 1 | -0.013208 | 2120 | 0.0173 | 2120 | 0.0173 | 1.04 | 1 | -0.0132
CFLAllSpcPGEESeExCZ04 | Com-Iltg-dWatt-CFL_OSspc | PGE | ESe | Ex | CZ04 | 2.12 | 0.00062025 | 0 | 2.26 | 0.00075229 | -0.0217 | 2.12 | 0.00062025 | 0 | 2.26 | 0.00075229 | -0.0217 |  | CFL | AllSpc | 2120 | 0.62 | 2120 | 0.62 | 1.07 | 1.21 | -0.010236 | 2120 | 0.62 | 2120 | 0.62 | 1.07 | 1.21 | -0.0102
CFLAllSpcPGEESeExCZ05 | Com-Iltg-dWatt-CFL_OSspc | PGE | ESe | Ex | CZ05 | 2.12 | 0.00062026 | 0 | 2.21 | 0.00073429 | -0.0257 | 2.12 | 0.00062026 | 0 | 2.21 | 0.00073429 | -0.0257 |  | CFL | AllSpc | 2120 | 0.62 | 2120 | 0.62 | 1.04 | 1.18 | -0.012123 | 2120 | 0.62 | 2120 | 0.62 | 1.04 | 1.18 | -0.0121
CFLAllSpcPGEESeExCZ11 | Com-Iltg-dWatt-CFL_OSspc | PGE | ESe | Ex | CZ11 | 2.12 | 1.7318e-05 | 0 | 2.26 | 1.7318e-05 | -0.024 | 2.12 | 1.7318e-05 | 0 | 2.26 | 1.7318e-05 | -0.024 |  | CFL | AllSpc | 2120 | 0.0173 | 2120 | 0.0173 | 1.07 | 1 | -0.011321 | 2120 | 0.0173 | 2120 | 0.0173 | 1.07 | 1 | -0.0113
CFLAllSpcPGEESeExCZ12 | Com-Iltg-dWatt-CFL_OSspc | PGE | ESe | Ex | CZ12 | 2.12 | 1.7316e-05 | 0 | 2.24 | 1.7316e-05 | -0.0251 | 2.12 | 1.7316e-05 | 0 | 2.24 | 1.7316e-05 | -0.0251 |  | CFL | AllSpc | 2120 | 0.0173 | 2120 | 0.0173 | 1.06 | 1 | -0.01184 | 2120 | 0.0173 | 2120 | 0.0173 | 1.06 | 1 | -0.0118
CFLAllSpcPGEESeExCZ13 | Com-Iltg-dWatt-CFL_OSspc | PGE | ESe | Ex | CZ13 | 2.12 | 1.7316e-05 | 0 | 2.28 | 1.7316e-05 | -0.0219 | 2.12 | 1.7316e-05 | 0 | 2.28 | 1.7316e-05 | -0.0219 |  | CFL | AllSpc | 2120 | 0.0173 | 2120 | 0.0173 | 1.08 | 1 | -0.01033 | 2120 | 0.0173 | 2120 | 0.0173 | 1.08 | 1 | -0.0103
CFLAllSpcPGEESeExCZ16 | Com-Iltg-dWatt-CFL_OSspc | PGE | ESe | Ex | CZ16 | 2.12 | 1.7316e-05 | 0 | 2.08 | 1.7316e-05 | -0.0376 | 2.12 | 1.7316e-05 | 0 | 2.08 | 1.7316e-05 | -0.0376 |  | CFL | AllSpc | 2120 | 0.0173 | 2120 | 0.0173 | 0.981 | 1 | -0.017736 | 2120 | 0.0173 | 2120 | 0.0173 | 0.981 | 1 | -0.0177
CFLAllSpcPGEESeExIOU | Com-Iltg-dWatt-CFL_OSspc | PGE | ESe | Ex | IOU | 2.12 | 0.00012341 | 0 | 2.2361 | 0.0001461 | -0.0253 | 2.12 | 0.00012341 | 0 | 2.2361 | 0.0001461 | -0.0253 |  | CFL | AllSpc | 2120 | 0.123 | 2120 | 0.123 | 1.05 | 1.18 | -0.011934 | 2120 | 0.123 | 2120 | 0.123 | 1.05 | 1.18 | -0.0119
CFLAllSpcPGEESeNewCZ01 | Com-Iltg-dWatt-CFL_OSspc | PGE | ESe | New | CZ01 | 2.12 | 0.000628 | 0 | 2.1 | 0.000722 | -0.0342 | 2.12 | 0.000628 | 0 | 2.1 | 0.000722 | -0.0342 |  | CFL | AllSpc | 2120 | 0.628 | 2120 | 0.628 | 0.991 | 1.15 | -0.016132 | 2120 | 0.628 | 2120 | 0.628 | 0.991 | 1.15 | -0.0161
CFLAllSpcPGEESeNewCZ02 | Com-Iltg-dWatt-CFL_OSspc | PGE | ESe | New | CZ02 | 2.12 | 1.76e-05 | 0 | 2.24 | 1.76e-05 | -0.0314 | 2.12 | 1.76e-05 | 0 | 2.24 | 1.76e-05 | -0.0314 |  | CFL | AllSpc | 2120 | 0.0176 | 2120 | 0.0176 | 1.06 | 1 | -0.014811 | 2120 | 0.0176 | 2120 | 0.0176 | 1.06 | 1 | -0.0148
CFLAllSpcPGEESeNewCZ03 | Com-Iltg-dWatt-CFL_OSspc | PGE | ESe | New | CZ03 | 2.12 | 1.76e-05 | 0 | 2.21 | 1.76e-05 | -0.0276 | 2.12 | 1.76e-05 | 0 | 2.21 | 1.76e-05 | -0.0276 |  | CFL | AllSpc | 2120 | 0.0176 | 2120 | 0.0176 | 1.04 | 1 | -0.013019 | 2120 | 0.0176 | 2120 | 0.0176 | 1.04 | 1 | -0.013
CFLAllSpcPGEESeNewCZ04 | Com-Iltg-dWatt-CFL_OSspc | PGE | ESe | New | CZ04 | 2.12 | 0.000628 | 0 | 2.27 | 0.000817 | -0.0251 | 2.12 | 0.000628 | 0 | 2.27 | 0.000817 | -0.0251 |  | CFL | AllSpc | 2120 | 0.628 | 2120 | 0.628 | 1.07 | 1.3 | -0.01184 | 2120 | 0.628 | 2120 | 0.628 | 1.07 | 1.3 | -0.0118
CFLAllSpcPGEESeNewCZ05 | Com-Iltg-dWatt-CFL_OSspc | PGE | ESe | New | CZ05 | 2.12 | 0.000628 | 0 | 2.2 | 0.00076 | -0.024 | 2.12 | 0.000628 | 0 | 2.2 | 0.00076 | -0.024 |  | CFL | AllSpc | 2120 | 0.628 | 2120 | 0.628 | 1.04 | 1.21 | -0.011321 | 2120 | 0.628 | 2120 | 0.628 | 1.04 | 1.21 | -0.0113
CFLAllSpcPGEESeNewCZ11 | Com-Iltg-dWatt-CFL_OSspc | PGE | ESe | New | CZ11 | 2.12 | 1.76e-05 | 0 | 2.31 | 1.76e-05 | -0.0272 | 2.12 | 1.76e-05 | 0 | 2.31 | 1.76e-05 | -0.0272 |  | CFL | AllSpc | 2120 | 0.0176 | 2120 | 0.0176 | 1.09 | 1 | -0.01283 | 2120 | 0.0176 | 2120 | 0.0176 | 1.09 | 1 | -0.0128
CFLAllSpcPGEESeNewCZ12 | Com-Iltg-dWatt-CFL_OSspc | PGE | ESe | New | CZ12 | 2.12 | 1.76e-05 | 0 | 2.29 | 1.76e-05 | -0.028 | 2.12 | 1.76e-05 | 0 | 2.29 | 1.76e-05 | -0.028 |  | CFL | AllSpc | 2120 | 0.0176 | 2120 | 0.0176 | 1.08 | 1 | -0.013208 | 2120 | 0.0176 | 2120 | 0.0176 | 1.08 | 1 | -0.0132
CFLAllSpcPGEESeNewCZ13 | Com-Iltg-dWatt-CFL_OSspc | PGE | ESe | New | CZ13 | 2.12 | 1.76e-05 | 0 | 2.34 | 1.76e-05 | -0.0253 | 2.12 | 1.76e-05 | 0 | 2.34 | 1.76e-05 | -0.0253 |  | CFL | AllSpc | 2120 | 0.0176 | 2120 | 0.0176 | 1.1 | 1 | -0.011934 | 2120 | 0.0176 | 2120 | 0.0176 | 1.1 | 1 | -0.0119
CFLAllSpcPGEESeNewCZ16 | Com-Iltg-dWatt-CFL_OSspc | PGE | ESe | New | CZ16 | 2.12 | 1.76e-05 | 0 | 2.12 | 1.76e-05 | -0.0314 | 2.12 | 1.76e-05 | 0 | 2.12 | 1.76e-05 | -0.0314 |  | CFL | AllSpc | 2120 | 0.0176 | 2120 | 0.0176 | 1 | 1 | -0.014811 | 2120 | 0.0176 | 2120 | 0.0176 | 1 | 1 | -0.0148
CFLAllSpcPGEESeNewIOU | Com-Iltg-dWatt-CFL_OSspc | PGE | ESe | New | IOU | 2.12 | 0.00010369 | 0 | 2.279 | 0.00012853 | -0.027134 | 2.12 | 0.00010369 | 0 | 2.279 | 0.00012853 | -0.027134 |  | CFL | AllSpc | 2120 | 0.104 | 2120 | 0.104 | 1.08 | 1.24 | -0.012799 | 2120 | 0.104 | 2120 | 0.104 | 1.08 | 1.24 | -0.0128
CFLAllSpcPGEEUnExCZ01 | Com-Iltg-dWatt-CFL_OSspc | PGE | EUn | Ex | CZ01 | 2.17 | 0.00054997 | 0 | 2.2903 | 0.000674 | -0.023 | 2.17 | 0.00054997 | 0 | 2.2903 | 0.000674 | -0.023 |  | CFL | AllSpc | 2170 | 0.55 | 2170 | 0.55 | 1.06 | 1.23 | -0.010599 | 2170 | 0.55 | 2170 | 0.55 | 1.06 | 1.23 | -0.0106
CFLAllSpcPGEEUnExCZ02 | Com-Iltg-dWatt-CFL_OSspc | PGE | EUn | Ex | CZ02 | 2.17 | 0.00036095 | 0 | 2.39 | 0.000447 | -0.0169 | 2.17 | 0.00036095 | 0 | 2.39 | 0.000447 | -0.0169 |  | CFL | AllSpc | 2170 | 0.361 | 2170 | 0.361 | 1.1 | 1.24 | -0.007788 | 2170 | 0.361 | 2170 | 0.361 | 1.1 | 1.24 | -0.00779
CFLAllSpcPGEEUnExCZ03 | Com-Iltg-dWatt-CFL_OSspc | PGE | EUn | Ex | CZ03 | 2.17 | 0.00036096 | 0 | 2.38 | 0.000436 | -0.0161 | 2.17 | 0.00036096 | 0 | 2.38 | 0.000436 | -0.0161 |  | CFL | AllSpc | 2170 | 0.361 | 2170 | 0.361 | 1.1 | 1.21 | -0.0074194 | 2170 | 0.361 | 2170 | 0.361 | 1.1 | 1.21 | -0.00742
CFLAllSpcPGEEUnExCZ04 | Com-Iltg-dWatt-CFL_OSspc | PGE | EUn | Ex | CZ04 | 2.17 | 0.00054995 | 0 | 2.4205 | 0.000702 | -0.0131 | 2.17 | 0.00054995 | 0 | 2.4205 | 0.000702 | -0.0131 |  | CFL | AllSpc | 2170 | 0.55 | 2170 | 0.55 | 1.12 | 1.28 | -0.0060369 | 2170 | 0.55 | 2170 | 0.55 | 1.12 | 1.28 | -0.00604
CFLAllSpcPGEEUnExCZ05 | Com-Iltg-dWatt-CFL_OSspc | PGE | EUn | Ex | CZ05 | 2.17 | 0.00054995 | 0 | 2.37 | 0.00066895 | -0.0154 | 2.17 | 0.00054995 | 0 | 2.37 | 0.00066895 | -0.0154 |  | CFL | AllSpc | 2170 | 0.55 | 2170 | 0.55 | 1.09 | 1.22 | -0.0070968 | 2170 | 0.55 | 2170 | 0.55 | 1.09 | 1.22 | -0.0071
CFLAllSpcPGEEUnExCZ11 | Com-Iltg-dWatt-CFL_OSspc | PGE | EUn | Ex | CZ11 | 2.17 | 0.00036094 | 0 | 2.43 | 0.000454 | -0.0152 | 2.17 | 0.00036094 | 0 | 2.43 | 0.000454 | -0.0152 |  | CFL | AllSpc | 2170 | 0.361 | 2170 | 0.361 | 1.12 | 1.26 | -0.0070046 | 2170 | 0.361 | 2170 | 0.361 | 1.12 | 1.26 | -0.007
CFLAllSpcPGEEUnExCZ12 | Com-Iltg-dWatt-CFL_OSspc | PGE | EUn | Ex | CZ12 | 2.17 | 0.00036094 | 0 | 2.4206 | 0.000451 | -0.0151 | 2.17 | 0.00036094 | 0 | 2.4206 | 0.000451 | -0.0151 |  | CFL | AllSpc | 2170 | 0.361 | 2170 | 0.361 | 1.12 | 1.25 | -0.0069585 | 2170 | 0.361 | 2170 | 0.361 | 1.12 | 1.25 | -0.00696
CFLAllSpcPGEEUnExCZ13 | Com-Iltg-dWatt-CFL_OSspc | PGE | EUn | Ex | CZ13 | 2.17 | 0.00036094 | 0 | 2.45 | 0.000458 | -0.0132 | 2.17 | 0.00036094 | 0 | 2.45 | 0.000458 | -0.0132 |  | CFL | AllSpc | 2170 | 0.361 | 2170 | 0.361 | 1.13 | 1.27 | -0.0060829 | 2170 | 0.361 | 2170 | 0.361 | 1.13 | 1.27 | -0.00608
CFLAllSpcPGEEUnExCZ16 | Com-Iltg-dWatt-CFL_OSspc | PGE | EUn | Ex | CZ16 | 2.17 | 0.00036095 | 0 | 2.31 | 0.00043596 | -0.023604 | 2.17 | 0.00036095 | 0 | 2.31 | 0.00043596 | -0.023604 |  | CFL | AllSpc | 2170 | 0.361 | 2170 | 0.361 | 1.06 | 1.21 | -0.010878 | 2170 | 0.361 | 2170 | 0.361 | 1.06 | 1.21 | -0.0109
CFLAllSpcPGEEUnExIOU | Com-Iltg-dWatt-CFL_OSspc | PGE | EUn | Ex | IOU | 2.17 | 0.00039699 | 0 | 2.4004 | 0.00049101 | -0.015446 | 2.17 | 0.00039699 | 0 | 2.4004 | 0.00049101 | -0.015446 |  | CFL | AllSpc | 2170 | 0.397 | 2170 | 0.397 | 1.11 | 1.24 | -0.0071181 | 2170 | 0.397 | 2170 | 0.397 | 1.11 | 1.24 | -0.00712
CFLAllSpcPGEEUnNewCZ01 | Com-Iltg-dWatt-CFL_OSspc | PGE | EUn | New | CZ01 | 2.17 | 0.000549 | 0 | 2.27 | 0.000645 | -0.0209 | 2.17 | 0.000549 | 0 | 2.27 | 0.000645 | -0.0209 |  | CFL | AllSpc | 2170 | 0.549 | 2170 | 0.549 | 1.05 | 1.17 | -0.0096313 | 2170 | 0.549 | 2170 | 0.549 | 1.05 | 1.17 | -0.00963
CFLAllSpcPGEEUnNewCZ02 | Com-Iltg-dWatt-CFL_OSspc | PGE | EUn | New | CZ02 | 2.17 | 0.00036 | 0 | 2.4 | 0.000469 | -0.0169 | 2.17 | 0.00036 | 0 | 2.4 | 0.000469 | -0.0169 |  | CFL | AllSpc | 2170 | 0.36 | 2170 | 0.36 | 1.11 | 1.3 | -0.007788 | 2170 | 0.36 | 2170 | 0.36 | 1.11 | 1.3 | -0.00779
CFLAllSpcPGEEUnNewCZ03 | Com-Iltg-dWatt-CFL_OSspc | PGE | EUn | New | CZ03 | 2.17 | 0.00036 | 0 | 2.36 | 0.000454 | -0.0125 | 2.17 | 0.00036 | 0 | 2.36 | 0.000454 | -0.0125 |  | CFL | AllSpc | 2170 | 0.36 | 2170 | 0.36 | 1.09 | 1.26 | -0.0057604 | 2170 | 0.36 | 2170 | 0.36 | 1.09 | 1.26 | -0.00576
CFLAllSpcPGEEUnNewCZ04 | Com-Iltg-dWatt-CFL_OSspc | PGE | EUn | New | CZ04 | 2.17 | 0.000549 | 0 | 2.42 | 0.000689 | -0.0112 | 2.17 | 0.000549 | 0 | 2.42 | 0.000689 | -0.0112 |  | CFL | AllSpc | 2170 | 0.549 | 2170 | 0.549 | 1.12 | 1.26 | -0.0051613 | 2170 | 0.549 | 2170 | 0.549 | 1.12 | 1.26 | -0.00516
CFLAllSpcPGEEUnNewCZ05 | Com-Iltg-dWatt-CFL_OSspc | PGE | EUn | New | CZ05 | 2.17 | 0.000549 | 0 | 2.36 | 0.000661 | -0.0136 | 2.17 | 0.000549 | 0 | 2.36 | 0.000661 | -0.0136 |  | CFL | AllSpc | 2170 | 0.549 | 2170 | 0.549 | 1.09 | 1.2 | -0.0062673 | 2170 | 0.549 | 2170 | 0.549 | 1.09 | 1.2 | -0.00627
CFLAllSpcPGEEUnNewCZ11 | Com-Iltg-dWatt-CFL_OSspc | PGE | EUn | New | CZ11 | 2.17 | 0.00036 | 0 | 2.46 | 0.000467 | -0.0126 | 2.17 | 0.00036 | 0 | 2.46 | 0.000467 | -0.0126 |  | CFL | AllSpc | 2170 | 0.36 | 2170 | 0.36 | 1.13 | 1.3 | -0.0058065 | 2170 | 0.36 | 2170 | 0.36 | 1.13 | 1.3 | -0.00581
CFLAllSpcPGEEUnNewCZ12 | Com-Iltg-dWatt-CFL_OSspc | PGE | EUn | New | CZ12 | 2.17 | 0.00036 | 0 | 2.45 | 0.000468 | -0.0136 | 2.17 | 0.00036 | 0 | 2.45 | 0.000468 | -0.0136 |  | CFL | AllSpc | 2170 | 0.36 | 2170 | 0.36 | 1.13 | 1.3 | -0.0062673 | 2170 | 0.36 | 2170 | 0.36 | 1.13 | 1.3 | -0.00627
CFLAllSpcPGEEUnNewCZ13 | Com-Iltg-dWatt-CFL_OSspc | PGE | EUn | New | CZ13 | 2.17 | 0.00036 | 0 | 2.51 | 0.000488 | -0.0141 | 2.17 | 0.00036 | 0 | 2.51 | 0.000488 | -0.0141 |  | CFL | AllSpc | 2170 | 0.36 | 2170 | 0.36 | 1.16 | 1.36 | -0.0064977 | 2170 | 0.36 | 2170 | 0.36 | 1.16 | 1.36 | -0.0065
CFLAllSpcPGEEUnNewCZ16 | Com-Iltg-dWatt-CFL_OSspc | PGE | EUn | New | CZ16 | 2.17 | 0.00036 | 0 | 2.31 | 0.00045 | -0.0226 | 2.17 | 0.00036 | 0 | 2.31 | 0.00045 | -0.0226 |  | CFL | AllSpc | 2170 | 0.36 | 2170 | 0.36 | 1.06 | 1.25 | -0.010415 | 2170 | 0.36 | 2170 | 0.36 | 1.06 | 1.25 | -0.0104
CFLAllSpcPGEEUnNewIOU | Com-Iltg-dWatt-CFL_OSspc | PGE | EUn | New | IOU | 2.17 | 0.00039627 | 0 | 2.4193 | 0.00050701 | -0.013404 | 2.17 | 0.00039627 | 0 | 2.4193 | 0.00050701 | -0.013404 |  | CFL | AllSpc | 2170 | 0.396 | 2170 | 0.396 | 1.11 | 1.28 | -0.0061768 | 2170 | 0.396 | 2170 | 0.396 | 1.11 | 1.28 | -0.00618
CFLAllSpcPGEGroExCZ01 | Com-Iltg-dWatt-CFL_OSspc | PGE | Gro | Ex | CZ01 | 3.8 | 0.00047891 | 0 | 3.0595 | 0.00044695 | -0.0669 | 3.8 | 0.00047891 | 0 | 3.0595 | 0.00044695 | -0.0669 |  | CFL | AllSpc | 3800 | 0.479 | 3800 | 0.479 | 0.805 | 0.933 | -0.017605 | 3800 | 0.479 | 3800 | 0.479 | 0.805 | 0.933 | -0.0176
CFLAllSpcPGEGroExCZ02 | Com-Iltg-dWatt-CFL_OSspc | PGE | Gro | Ex | CZ02 | 3.8 | 0.0004789 | 0 | 3.4395 | 0.0006419 | -0.0521 | 3.8 | 0.0004789 | 0 | 3.4395 | 0.0006419 | -0.0521 |  | CFL | AllSpc | 3800 | 0.479 | 3800 | 0.479 | 0.905 | 1.34 | -0.013711 | 3800 | 0.479 | 3800 | 0.479 | 0.905 | 1.34 | -0.0137
CFLAllSpcPGEGroExCZ03 | Com-Iltg-dWatt-CFL_OSspc | PGE | Gro | Ex | CZ03 | 3.8 | 0.00047891 | 0 | 3.28 | 0.00060396 | -0.0593 | 3.8 | 0.00047891 | 0 | 3.28 | 0.00060396 | -0.0593 |  | CFL | AllSpc | 3800 | 0.479 | 3800 | 0.479 | 0.863 | 1.26 | -0.015605 | 3800 | 0.479 | 3800 | 0.479 | 0.863 | 1.26 | -0.0156
CFLAllSpcPGEGroExCZ04 | Com-Iltg-dWatt-CFL_OSspc | PGE | Gro | Ex | CZ04 | 3.8 | 0.0004789 | 0 | 3.5095 | 0.0006079 | -0.0502 | 3.8 | 0.0004789 | 0 | 3.5095 | 0.0006079 | -0.0502 |  | CFL | AllSpc | 3800 | 0.479 | 3800 | 0.479 | 0.924 | 1.27 | -0.013211 | 3800 | 0.479 | 3800 | 0.479 | 0.924 | 1.27 | -0.0132
CFLAllSpcPGEGroExCZ05 | Com-Iltg-dWatt-CFL_OSspc | PGE | Gro | Ex | CZ05 | 3.8 | 0.0004789 | 0 | 3.26 | 0.0005879 | -0.0593 | 3.8 | 0.0004789 | 0 | 3.26 | 0.0005879 | -0.0593 |  | CFL | AllSpc | 3800 | 0.479 | 3800 | 0.479 | 0.858 | 1.23 | -0.015605 | 3800 | 0.479 | 3800 | 0.479 | 0.858 | 1.23 | -0.0156
CFLAllSpcPGEGroExCZ11 | Com-Iltg-dWatt-CFL_OSspc | PGE | Gro | Ex | CZ11 | 3.8 | 0.00047885 | 0 | 3.72 | 0.00063885 | -0.0426 | 3.8 | 0.00047885 | 0 | 3.72 | 0.00063885 | -0.0426 |  | CFL | AllSpc | 3800 | 0.479 | 3800 | 0.479 | 0.979 | 1.33 | -0.011211 | 3800 | 0.479 | 3800 | 0.479 | 0.979 | 1.33 | -0.0112
CFLAllSpcPGEGroExCZ12 | Com-Iltg-dWatt-CFL_OSspc | PGE | Gro | Ex | CZ12 | 3.8 | 0.00047887 | 0 | 3.62 | 0.00063387 | -0.0464 | 3.8 | 0.00047887 | 0 | 3.62 | 0.00063387 | -0.0464 |  | CFL | AllSpc | 3800 | 0.479 | 3800 | 0.479 | 0.953 | 1.32 | -0.012211 | 3800 | 0.479 | 3800 | 0.479 | 0.953 | 1.32 | -0.0122
CFLAllSpcPGEGroExCZ13 | Com-Iltg-dWatt-CFL_OSspc | PGE | Gro | Ex | CZ13 | 3.8 | 0.00047885 | 0 | 3.75 | 0.00063385 | -0.0403 | 3.8 | 0.00047885 | 0 | 3.75 | 0.00063385 | -0.0403 |  | CFL | AllSpc | 3800 | 0.479 | 3800 | 0.479 | 0.987 | 1.32 | -0.010605 | 3800 | 0.479 | 3800 | 0.479 | 0.987 | 1.32 | -0.0106
CFLAllSpcPGEGroExCZ16 | Com-Iltg-dWatt-CFL_OSspc | PGE | Gro | Ex | CZ16 | 3.8 | 0.00047887 | 0 | 3.27 | 0.00059987 | -0.055193 | 3.8 | 0.00047887 | 0 | 3.27 | 0.00059987 | -0.055193 |  | CFL | AllSpc | 3800 | 0.479 | 3800 | 0.479 | 0.861 | 1.25 | -0.014525 | 3800 | 0.479 | 3800 | 0.479 | 0.861 | 1.25 | -0.0145
CFLAllSpcPGEGroExIOU | Com-Iltg-dWatt-CFL_OSspc | PGE | Gro | Ex | IOU | 3.8 | 0.00047888 | 0 | 3.5055 | 0.00061961 | -0.050332 | 3.8 | 0.00047888 | 0 | 3.5055 | 0.00061961 | -0.050332 |  | CFL | AllSpc | 3800 | 0.479 | 3800 | 0.479 | 0.922 | 1.29 | -0.013245 | 3800 | 0.479 | 3800 | 0.479 | 0.922 | 1.29 | -0.0132
CFLAllSpcPGEGroNewCZ01 | Com-Iltg-dWatt-CFL_OSspc | PGE | Gro | New | CZ01 | 3.8 | 0.000477 | 0 | 3.15 | 0.000562 | -0.071 | 3.8 | 0.000477 | 0 | 3.15 | 0.000562 | -0.071 |  | CFL | AllSpc | 3800 | 0.477 | 3800 | 0.477 | 0.829 | 1.18 | -0.018684 | 3800 | 0.477 | 3800 | 0.477 | 0.829 | 1.18 | -0.0187
CFLAllSpcPGEGroNewCZ02 | Com-Iltg-dWatt-CFL_OSspc | PGE | Gro | New | CZ02 | 3.8 | 0.000477 | 0 | 3.58 | 0.000663 | -0.0521 | 3.8 | 0.000477 | 0 | 3.58 | 0.000663 | -0.0521 |  | CFL | AllSpc | 3800 | 0.477 | 3800 | 0.477 | 0.942 | 1.39 | -0.013711 | 3800 | 0.477 | 3800 | 0.477 | 0.942 | 1.39 | -0.0137
CFLAllSpcPGEGroNewCZ03 | Com-Iltg-dWatt-CFL_OSspc | PGE | Gro | New | CZ03 | 3.8 | 0.000477 | 0 | 3.39 | 0.000624 | -0.0585 | 3.8 | 0.000477 | 0 | 3.39 | 0.000624 | -0.0585 |  | CFL | AllSpc | 3800 | 0.477 | 3800 | 0.477 | 0.892 | 1.31 | -0.015395 | 3800 | 0.477 | 3800 | 0.477 | 0.892 | 1.31 | -0.0154
CFLAllSpcPGEGroNewCZ04 | Com-Iltg-dWatt-CFL_OSspc | PGE | Gro | New | CZ04 | 3.8 | 0.000477 | 0 | 3.67 | 0.000624 | -0.0479 | 3.8 | 0.000477 | 0 | 3.67 | 0.000624 | -0.0479 |  | CFL | AllSpc | 3800 | 0.477 | 3800 | 0.477 | 0.966 | 1.31 | -0.012605 | 3800 | 0.477 | 3800 | 0.477 | 0.966 | 1.31 | -0.0126
CFLAllSpcPGEGroNewCZ05 | Com-Iltg-dWatt-CFL_OSspc | PGE | Gro | New | CZ05 | 3.8 | 0.000477 | 0 | 3.39 | 0.000604 | -0.0581 | 3.8 | 0.000477 | 0 | 3.39 | 0.000604 | -0.0581 |  | CFL | AllSpc | 3800 | 0.477 | 3800 | 0.477 | 0.892 | 1.27 | -0.015289 | 3800 | 0.477 | 3800 | 0.477 | 0.892 | 1.27 | -0.0153
CFLAllSpcPGEGroNewCZ11 | Com-Iltg-dWatt-CFL_OSspc | PGE | Gro | New | CZ11 | 3.8 | 0.000477 | 0 | 3.84 | 0.000668 | -0.0414 | 3.8 | 0.000477 | 0 | 3.84 | 0.000668 | -0.0414 |  | CFL | AllSpc | 3800 | 0.477 | 3800 | 0.477 | 1.01 | 1.4 | -0.010895 | 3800 | 0.477 | 3800 | 0.477 | 1.01 | 1.4 | -0.0109
CFLAllSpcPGEGroNewCZ12 | Com-Iltg-dWatt-CFL_OSspc | PGE | Gro | New | CZ12 | 3.8 | 0.000477 | 0 | 3.77 | 0.00067 | -0.046 | 3.8 | 0.000477 | 0 | 3.77 | 0.00067 | -0.046 |  | CFL | AllSpc | 3800 | 0.477 | 3800 | 0.477 | 0.992 | 1.4 | -0.012105 | 3800 | 0.477 | 3800 | 0.477 | 0.992 | 1.4 | -0.0121
CFLAllSpcPGEGroNewCZ13 | Com-Iltg-dWatt-CFL_OSspc | PGE | Gro | New | CZ13 | 3.8 | 0.000477 | 0 | 3.88 | 0.000648 | -0.0391 | 3.8 | 0.000477 | 0 | 3.88 | 0.000648 | -0.0391 |  | CFL | AllSpc | 3800 | 0.477 | 3800 | 0.477 | 1.02 | 1.36 | -0.010289 | 3800 | 0.477 | 3800 | 0.477 | 1.02 | 1.36 | -0.0103
CFLAllSpcPGEGroNewCZ16 | Com-Iltg-dWatt-CFL_OSspc | PGE | Gro | New | CZ16 | 3.8 | 0.000477 | 0 | 3.43 | 0.000607 | -0.054 | 3.8 | 0.000477 | 0 | 3.43 | 0.000607 | -0.054 |  | CFL | AllSpc | 3800 | 0.477 | 3800 | 0.477 | 0.903 | 1.27 | -0.014211 | 3800 | 0.477 | 3800 | 0.477 | 0.903 | 1.27 | -0.0142
CFLAllSpcPGEGroNewIOU | Com-Iltg-dWatt-CFL_OSspc | PGE | Gro | New | IOU | 3.8 | 0.000477 | 0 | 3.6769 | 0.00064663 | -0.04798 | 3.8 | 0.000477 | 0 | 3.6769 | 0.00064663 | -0.04798 |  | CFL | AllSpc | 3800 | 0.477 | 3800 | 0.477 | 0.968 | 1.36 | -0.012626 | 3800 | 0.477 | 3800 | 0.477 | 0.968 | 1.36 | -0.0126
CFLAllSpcPGEHspExCZ01 | Com-Iltg-dWatt-CFL_OSspc | PGE | Hsp | Ex | CZ01 | 3.92 | 0.000656 | 0 | 4.2 | 0.00075196 | -0.0344 | 3.92 | 0.000656 | 0 | 4.2 | 0.00075196 | -0.0344 |  | CFL | AllSpc | 3920 | 0.656 | 3920 | 0.656 | 1.07 | 1.15 | -0.0087755 | 3920 | 0.656 | 3920 | 0.656 | 1.07 | 1.15 | -0.00878
CFLAllSpcPGEHspExCZ02 | Com-Iltg-dWatt-CFL_OSspc | PGE | Hsp | Ex | CZ02 | 3.92 | 0.000656 | 0 | 4.3195 | 0.00080695 | -0.0269 | 3.92 | 0.000656 | 0 | 4.3195 | 0.00080695 | -0.0269 |  | CFL | AllSpc | 3920 | 0.656 | 3920 | 0.656 | 1.1 | 1.23 | -0.0068622 | 3920 | 0.656 | 3920 | 0.656 | 1.1 | 1.23 | -0.00686
CFLAllSpcPGEHspExCZ03 | Com-Iltg-dWatt-CFL_OSspc | PGE | Hsp | Ex | CZ03 | 3.92 | 0.000656 | 0 | 4.3395 | 0.00078795 | -0.0255 | 3.92 | 0.000656 | 0 | 4.3395 | 0.00078795 | -0.0255 |  | CFL | AllSpc | 3920 | 0.656 | 3920 | 0.656 | 1.11 | 1.2 | -0.0065051 | 3920 | 0.656 | 3920 | 0.656 | 1.11 | 1.2 | -0.00651
CFLAllSpcPGEHspExCZ04 | Com-Iltg-dWatt-CFL_OSspc | PGE | Hsp | Ex | CZ04 | 3.92 | 0.000656 | 0 | 4.34 | 0.00079995 | -0.0242 | 3.92 | 0.000656 | 0 | 4.34 | 0.00079995 | -0.0242 |  | CFL | AllSpc | 3920 | 0.656 | 3920 | 0.656 | 1.11 | 1.22 | -0.0061735 | 3920 | 0.656 | 3920 | 0.656 | 1.11 | 1.22 | -0.00617
CFLAllSpcPGEHspExCZ05 | Com-Iltg-dWatt-CFL_OSspc | PGE | Hsp | Ex | CZ05 | 3.92 | 0.000656 | 0 | 4.27 | 0.00077295 | -0.0271 | 3.92 | 0.000656 | 0 | 4.27 | 0.00077295 | -0.0271 |  | CFL | AllSpc | 3920 | 0.656 | 3920 | 0.656 | 1.09 | 1.18 | -0.0069133 | 3920 | 0.656 | 3920 | 0.656 | 1.09 | 1.18 | -0.00691
CFLAllSpcPGEHspExCZ11 | Com-Iltg-dWatt-CFL_OSspc | PGE | Hsp | Ex | CZ11 | 3.92 | 0.000656 | 0 | 4.36 | 0.00081194 | -0.0253 | 3.92 | 0.000656 | 0 | 4.36 | 0.00081194 | -0.0253 |  | CFL | AllSpc | 3920 | 0.656 | 3920 | 0.656 | 1.11 | 1.24 | -0.0064541 | 3920 | 0.656 | 3920 | 0.656 | 1.11 | 1.24 | -0.00645
CFLAllSpcPGEHspExCZ12 | Com-Iltg-dWatt-CFL_OSspc | PGE | Hsp | Ex | CZ12 | 3.92 | 0.000656 | 0 | 4.35 | 0.00080994 | -0.0246 | 3.92 | 0.000656 | 0 | 4.35 | 0.00080994 | -0.0246 |  | CFL | AllSpc | 3920 | 0.656 | 3920 | 0.656 | 1.11 | 1.23 | -0.0062755 | 3920 | 0.656 | 3920 | 0.656 | 1.11 | 1.23 | -0.00628
CFLAllSpcPGEHspExCZ13 | Com-Iltg-dWatt-CFL_OSspc | PGE | Hsp | Ex | CZ13 | 3.92 | 0.000656 | 0 | 4.38 | 0.00080894 | -0.023794 | 3.92 | 0.000656 | 0 | 4.38 | 0.00080894 | -0.023794 |  | CFL | AllSpc | 3920 | 0.656 | 3920 | 0.656 | 1.12 | 1.23 | -0.0060698 | 3920 | 0.656 | 3920 | 0.656 | 1.12 | 1.23 | -0.00607
CFLAllSpcPGEHspExCZ16 | Com-Iltg-dWatt-CFL_OSspc | PGE | Hsp | Ex | CZ16 | 3.92 | 0.000656 | 0 | 4.1295 | 0.00078489 | -0.039 | 3.92 | 0.000656 | 0 | 4.1295 | 0.00078489 | -0.039 |  | CFL | AllSpc | 3920 | 0.656 | 3920 | 0.656 | 1.05 | 1.2 | -0.009949 | 3920 | 0.656 | 3920 | 0.656 | 1.05 | 1.2 | -0.00995
CFLAllSpcPGEHspExIOU | Com-Iltg-dWatt-CFL_OSspc | PGE | Hsp | Ex | IOU | 3.92 | 0.000656 | 0 | 4.3443 | 0.00080048 | -0.025157 | 3.92 | 0.000656 | 0 | 4.3443 | 0.00080048 | -0.025157 |  | CFL | AllSpc | 3920 | 0.656 | 3920 | 0.656 | 1.11 | 1.22 | -0.0064177 | 3920 | 0.656 | 3920 | 0.656 | 1.11 | 1.22 | -0.00642
CFLAllSpcPGEHspNewCZ01 | Com-Iltg-dWatt-CFL_OSspc | PGE | Hsp | New | CZ01 | 3.92 | 0.000656 | 0 | 4.01 | 0.000716 | -0.0365 | 3.92 | 0.000656 | 0 | 4.01 | 0.000716 | -0.0365 |  | CFL | AllSpc | 3920 | 0.656 | 3920 | 0.656 | 1.02 | 1.09 | -0.0093112 | 3920 | 0.656 | 3920 | 0.656 | 1.02 | 1.09 | -0.00931
CFLAllSpcPGEHspNewCZ02 | Com-Iltg-dWatt-CFL_OSspc | PGE | Hsp | New | CZ02 | 3.92 | 0.000656 | 0 | 4.15 | 0.000784 | -0.0292 | 3.92 | 0.000656 | 0 | 4.15 | 0.000784 | -0.0292 |  | CFL | AllSpc | 3920 | 0.656 | 3920 | 0.656 | 1.06 | 1.2 | -0.007449 | 3920 | 0.656 | 3920 | 0.656 | 1.06 | 1.2 | -0.00745
CFLAllSpcPGEHspNewCZ03 | Com-Iltg-dWatt-CFL_OSspc | PGE | Hsp | New | CZ03 | 3.92 | 0.000656 | 0 | 4.13 | 0.000764 | -0.0262 | 3.92 | 0.000656 | 0 | 4.13 | 0.000764 | -0.0262 |  | CFL | AllSpc | 3920 | 0.656 | 3920 | 0.656 | 1.05 | 1.16 | -0.0066837 | 3920 | 0.656 | 3920 | 0.656 | 1.05 | 1.16 | -0.00668
CFLAllSpcPGEHspNewCZ04 | Com-Iltg-dWatt-CFL_OSspc | PGE | Hsp | New | CZ04 | 3.92 | 0.000656 | 0 | 4.19 | 0.000778 | -0.0255 | 3.92 | 0.000656 | 0 | 4.19 | 0.000778 | -0.0255 |  | CFL | AllSpc | 3920 | 0.656 | 3920 | 0.656 | 1.07 | 1.19 | -0.0065051 | 3920 | 0.656 | 3920 | 0.656 | 1.07 | 1.19 | -0.00651
CFLAllSpcPGEHspNewCZ05 | Com-Iltg-dWatt-CFL_OSspc | PGE | Hsp | New | CZ05 | 3.92 | 0.000656 | 0 | 4.11 | 0.000754 | -0.0294 | 3.92 | 0.000656 | 0 | 4.11 | 0.000754 | -0.0294 |  | CFL | AllSpc | 3920 | 0.656 | 3920 | 0.656 | 1.05 | 1.15 | -0.0075 | 3920 | 0.656 | 3920 | 0.656 | 1.05 | 1.15 | -0.0075
CFLAllSpcPGEHspNewCZ11 | Com-Iltg-dWatt-CFL_OSspc | PGE | Hsp | New | CZ11 | 3.92 | 0.000656 | 0 | 4.24 | 0.000789 | -0.0272 | 3.92 | 0.000656 | 0 | 4.24 | 0.000789 | -0.0272 |  | CFL | AllSpc | 3920 | 0.656 | 3920 | 0.656 | 1.08 | 1.2 | -0.0069388 | 3920 | 0.656 | 3920 | 0.656 | 1.08 | 1.2 | -0.00694
CFLAllSpcPGEHspNewCZ12 | Com-Iltg-dWatt-CFL_OSspc | PGE | Hsp | New | CZ12 | 3.92 | 0.000656 | 0 | 4.22 | 0.000789 | -0.0264 | 3.92 | 0.000656 | 0 | 4.22 | 0.000789 | -0.0264 |  | CFL | AllSpc | 3920 | 0.656 | 3920 | 0.656 | 1.08 | 1.2 | -0.0067347 | 3920 | 0.656 | 3920 | 0.656 | 1.08 | 1.2 | -0.00673
CFLAllSpcPGEHspNewCZ13 | Com-Iltg-dWatt-CFL_OSspc | PGE | Hsp | New | CZ13 | 3.92 | 0.000656 | 0 | 4.26 | 0.000787 | -0.0258 | 3.92 | 0.000656 | 0 | 4.26 | 0.000787 | -0.0258 |  | CFL | AllSpc | 3920 | 0.656 | 3920 | 0.656 | 1.09 | 1.2 | -0.0065816 | 3920 | 0.656 | 3920 | 0.656 | 1.09 | 1.2 | -0.00658
CFLAllSpcPGEHspNewCZ16 | Com-Iltg-dWatt-CFL_OSspc | PGE | Hsp | New | CZ16 | 3.92 | 0.000656 | 0 | 3.96 | 0.000762 | -0.0435 | 3.92 | 0.000656 | 0 | 3.96 | 0.000762 | -0.0435 |  | CFL | AllSpc | 3920 | 0.656 | 3920 | 0.656 | 1.01 | 1.16 | -0.011097 | 3920 | 0.656 | 3920 | 0.656 | 1.01 | 1.16 | -0.0111
CFLAllSpcPGEHspNewIOU | Com-Iltg-dWatt-CFL_OSspc | PGE | Hsp | New | IOU | 3.92 | 0.000656 | 0 | 4.1927 | 0.00077935 | -0.026642 | 3.92 | 0.000656 | 0 | 4.1927 | 0.00077935 | -0.026642 |  | CFL | AllSpc | 3920 | 0.656 | 3920 | 0.656 | 1.07 | 1.19 | -0.0067965 | 3920 | 0.656 | 3920 | 0.656 | 1.07 | 1.19 | -0.0068
CFLAllSpcPGEHtlExCZ01 | Com-Iltg-dWatt-CFL_OSspc | PGE | Htl | Ex | CZ01 | 1.4706 | 0.000171 | 0 | 1.3306 | 0.00020406 | -0.0077319 | 1.4706 | 0.000171 | 0 | 1.3306 | 0.00020406 | -0.0077319 |  | CFL | AllSpc | 1470 | 0.171 | 1470 | 0.171 | 0.905 | 1.19 | -0.0052576 | 1470 | 0.171 | 1470 | 0.171 | 0.905 | 1.19 | -0.00526
CFLAllSpcPGEHtlExCZ02 | Com-Iltg-dWatt-CFL_OSspc | PGE | Htl | Ex | CZ02 | 1.4706 | 0.000171 | 0 | 1.4506 | 0.00021206 | -0.0056218 | 1.4706 | 0.000171 | 0 | 1.4506 | 0.00021206 | -0.0056218 |  | CFL | AllSpc | 1470 | 0.171 | 1470 | 0.171 | 0.986 | 1.24 | -0.0038228 | 1470 | 0.171 | 1470 | 0.171 | 0.986 | 1.24 | -0.00382
CFLAllSpcPGEHtlExCZ03 | Com-Iltg-dWatt-CFL_OSspc | PGE | Htl | Ex | CZ03 | 1.4703 | 0.000171 | 0 | 1.4703 | 0.00020903 | -0.0054206 | 1.4703 | 0.000171 | 0 | 1.4703 | 0.00020903 | -0.0054206 |  | CFL | AllSpc | 1470 | 0.171 | 1470 | 0.171 | 1 | 1.22 | -0.0036867 | 1470 | 0.171 | 1470 | 0.171 | 1 | 1.22 | -0.00369
CFLAllSpcPGEHtlExCZ04 | Com-Iltg-dWatt-CFL_OSspc | PGE | Htl | Ex | CZ04 | 1.4706 | 0.000171 | 0 | 1.51 | 0.00021106 | -0.0045512 | 1.4706 | 0.000171 | 0 | 1.51 | 0.00021106 | -0.0045512 |  | CFL | AllSpc | 1470 | 0.171 | 1470 | 0.171 | 1.03 | 1.23 | -0.0030948 | 1470 | 0.171 | 1470 | 0.171 | 1.03 | 1.23 | -0.00309
CFLAllSpcPGEHtlExCZ05 | Com-Iltg-dWatt-CFL_OSspc | PGE | Htl | Ex | CZ05 | 1.4706 | 0.000171 | 0 | 1.4506 | 0.00020706 | -0.0056113 | 1.4706 | 0.000171 | 0 | 1.4506 | 0.00020706 | -0.0056113 |  | CFL | AllSpc | 1470 | 0.171 | 1470 | 0.171 | 0.986 | 1.21 | -0.0038156 | 1470 | 0.171 | 1470 | 0.171 | 0.986 | 1.21 | -0.00382
CFLAllSpcPGEHtlExCZ11 | Com-Iltg-dWatt-CFL_OSspc | PGE | Htl | Ex | CZ11 | 1.4707 | 0.000171 | 0 | 1.5207 | 0.00021507 | -0.0049214 | 1.4707 | 0.000171 | 0 | 1.5207 | 0.00021507 | -0.0049214 |  | CFL | AllSpc | 1470 | 0.171 | 1470 | 0.171 | 1.03 | 1.26 | -0.0033463 | 1470 | 0.171 | 1470 | 0.171 | 1.03 | 1.26 | -0.00335
CFLAllSpcPGEHtlExCZ12 | Com-Iltg-dWatt-CFL_OSspc | PGE | Htl | Ex | CZ12 | 1.4708 | 0.000171 | 0 | 1.5 | 0.000215 | -0.0050015 | 1.4708 | 0.000171 | 0 | 1.5 | 0.000215 | -0.0050015 |  | CFL | AllSpc | 1470 | 0.171 | 1470 | 0.171 | 1.02 | 1.26 | -0.0034006 | 1470 | 0.171 | 1470 | 0.171 | 1.02 | 1.26 | -0.0034
CFLAllSpcPGEHtlExCZ13 | Com-Iltg-dWatt-CFL_OSspc | PGE | Htl | Ex | CZ13 | 1.4707 | 0.000171 | 0 | 1.5407 | 0.00021307 | -0.0045813 | 1.4707 | 0.000171 | 0 | 1.5407 | 0.00021307 | -0.0045813 |  | CFL | AllSpc | 1470 | 0.171 | 1470 | 0.171 | 1.05 | 1.25 | -0.0031151 | 1470 | 0.171 | 1470 | 0.171 | 1.05 | 1.25 | -0.00312
CFLAllSpcPGEHtlExCZ16 | Com-Iltg-dWatt-CFL_OSspc | PGE | Htl | Ex | CZ16 | 1.4706 | 0.000171 | 0 | 1.35 | 0.00020807 | -0.0078019 | 1.4706 | 0.000171 | 0 | 1.35 | 0.00020807 | -0.0078019 |  | CFL | AllSpc | 1470 | 0.171 | 1470 | 0.171 | 0.918 | 1.22 | -0.0053051 | 1470 | 0.171 | 1470 | 0.171 | 0.918 | 1.22 | -0.00531
CFLAllSpcPGEHtlExIOU | Com-Iltg-dWatt-CFL_OSspc | PGE | Htl | Ex | IOU | 1.4705 | 0.000171 | 0 | 1.4813 | 0.00021068 | -0.0052478 | 1.4705 | 0.000171 | 0 | 1.4813 | 0.00021068 | -0.0052478 |  | CFL | AllSpc | 1470 | 0.171 | 1470 | 0.171 | 1.01 | 1.23 | -0.0035687 | 1470 | 0.171 | 1470 | 0.171 | 1.01 | 1.23 | -0.00357
CFLAllSpcPGEHtlNewCZ01 | Com-Iltg-dWatt-CFL_OSspc | PGE | Htl | New | CZ01 | 1.48 | 0.000171 | 0 | 1.3 | 0.000204 | -0.00859 | 1.48 | 0.000171 | 0 | 1.3 | 0.000204 | -0.00859 |  | CFL | AllSpc | 1480 | 0.171 | 1480 | 0.171 | 0.878 | 1.19 | -0.0058041 | 1480 | 0.171 | 1480 | 0.171 | 0.878 | 1.19 | -0.0058
CFLAllSpcPGEHtlNewCZ02 | Com-Iltg-dWatt-CFL_OSspc | PGE | Htl | New | CZ02 | 1.48 | 0.000171 | 0 | 1.44 | 0.000217 | -0.00671 | 1.48 | 0.000171 | 0 | 1.44 | 0.000217 | -0.00671 |  | CFL | AllSpc | 1480 | 0.171 | 1480 | 0.171 | 0.973 | 1.27 | -0.0045338 | 1480 | 0.171 | 1480 | 0.171 | 0.973 | 1.27 | -0.00453
CFLAllSpcPGEHtlNewCZ03 | Com-Iltg-dWatt-CFL_OSspc | PGE | Htl | New | CZ03 | 1.48 | 0.000171 | 0 | 1.44 | 0.000211 | -0.00613 | 1.48 | 0.000171 | 0 | 1.44 | 0.000211 | -0.00613 |  | CFL | AllSpc | 1480 | 0.171 | 1480 | 0.171 | 0.973 | 1.23 | -0.0041419 | 1480 | 0.171 | 1480 | 0.171 | 0.973 | 1.23 | -0.00414
CFLAllSpcPGEHtlNewCZ04 | Com-Iltg-dWatt-CFL_OSspc | PGE | Htl | New | CZ04 | 1.48 | 0.000171 | 0 | 1.5 | 0.000217 | -0.00529 | 1.48 | 0.000171 | 0 | 1.5 | 0.000217 | -0.00529 |  | CFL | AllSpc | 1480 | 0.171 | 1480 | 0.171 | 1.01 | 1.27 | -0.0035743 | 1480 | 0.171 | 1480 | 0.171 | 1.01 | 1.27 | -0.00357
CFLAllSpcPGEHtlNewCZ05 | Com-Iltg-dWatt-CFL_OSspc | PGE | Htl | New | CZ05 | 1.48 | 0.000171 | 0 | 1.43 | 0.000209 | -0.00652 | 1.48 | 0.000171 | 0 | 1.43 | 0.000209 | -0.00652 |  | CFL | AllSpc | 1480 | 0.171 | 1480 | 0.171 | 0.966 | 1.22 | -0.0044054 | 1480 | 0.171 | 1480 | 0.171 | 0.966 | 1.22 | -0.00441
CFLAllSpcPGEHtlNewCZ11 | Com-Iltg-dWatt-CFL_OSspc | PGE | Htl | New | CZ11 | 1.48 | 0.000171 | 0 | 1.51 | 0.000219 | -0.00582 | 1.48 | 0.000171 | 0 | 1.51 | 0.000219 | -0.00582 |  | CFL | AllSpc | 1480 | 0.171 | 1480 | 0.171 | 1.02 | 1.28 | -0.0039324 | 1480 | 0.171 | 1480 | 0.171 | 1.02 | 1.28 | -0.00393
CFLAllSpcPGEHtlNewCZ12 | Com-Iltg-dWatt-CFL_OSspc | PGE | Htl | New | CZ12 | 1.48 | 0.000171 | 0 | 1.49 | 0.000218 | -0.00588 | 1.48 | 0.000171 | 0 | 1.49 | 0.000218 | -0.00588 |  | CFL | AllSpc | 1480 | 0.171 | 1480 | 0.171 | 1.01 | 1.27 | -0.003973 | 1480 | 0.171 | 1480 | 0.171 | 1.01 | 1.27 | -0.00397
CFLAllSpcPGEHtlNewCZ13 | Com-Iltg-dWatt-CFL_OSspc | PGE | Htl | New | CZ13 | 1.48 | 0.000171 | 0 | 1.53 | 0.000216 | -0.00534 | 1.48 | 0.000171 | 0 | 1.53 | 0.000216 | -0.00534 |  | CFL | AllSpc | 1480 | 0.171 | 1480 | 0.171 | 1.03 | 1.26 | -0.0036081 | 1480 | 0.171 | 1480 | 0.171 | 1.03 | 1.26 | -0.00361
CFLAllSpcPGEHtlNewCZ16 | Com-Iltg-dWatt-CFL_OSspc | PGE | Htl | New | CZ16 | 1.48 | 0.000171 | 0 | 1.33 | 0.000211 | -0.00967 | 1.48 | 0.000171 | 0 | 1.33 | 0.000211 | -0.00967 |  | CFL | AllSpc | 1480 | 0.171 | 1480 | 0.171 | 0.899 | 1.23 | -0.0065338 | 1480 | 0.171 | 1480 | 0.171 | 0.899 | 1.23 | -0.00653
CFLAllSpcPGEHtlNewIOU | Com-Iltg-dWatt-CFL_OSspc | PGE | Htl | New | IOU | 1.48 | 0.000171 | 0 | 1.4695 | 0.00021474 | -0.0060177 | 1.48 | 0.000171 | 0 | 1.4695 | 0.00021474 | -0.0060177 |  | CFL | AllSpc | 1480 | 0.171 | 1480 | 0.171 | 0.993 | 1.26 | -0.004066 | 1480 | 0.171 | 1480 | 0.171 | 0.993 | 1.26 | -0.00407
CFLAllSpcPGEMBTExCZ01 | Com-Iltg-dWatt-CFL_OSspc | PGE | MBT | Ex | CZ01 | 2.78 | 0.000667 | 0 | 3 | 0.00078605 | -0.0031905 | 2.78 | 0.000667 | 0 | 3 | 0.00078605 | -0.0031905 |  | CFL | AllSpc | 2780 | 0.667 | 2780 | 0.667 | 1.08 | 1.18 | -0.0011477 | 2780 | 0.667 | 2780 | 0.667 | 1.08 | 1.18 | -0.00115
CFLAllSpcPGEMBTExCZ02 | Com-Iltg-dWatt-CFL_OSspc | PGE | MBT | Ex | CZ02 | 2.78 | 0.000667 | 0 | 3.0804 | 0.000787 | -0.00161 | 2.78 | 0.000667 | 0 | 3.0804 | 0.000787 | -0.00161 |  | CFL | AllSpc | 2780 | 0.667 | 2780 | 0.667 | 1.11 | 1.18 | -0.00057914 | 2780 | 0.667 | 2780 | 0.667 | 1.11 | 1.18 | -0.000579
CFLAllSpcPGEMBTExCZ03 | Com-Iltg-dWatt-CFL_OSspc | PGE | MBT | Ex | CZ03 | 2.78 | 0.000667 | 0 | 3.11 | 0.000789 | -0.0014 | 2.78 | 0.000667 | 0 | 3.11 | 0.000789 | -0.0014 |  | CFL | AllSpc | 2780 | 0.667 | 2780 | 0.667 | 1.12 | 1.18 | -0.0005036 | 2780 | 0.667 | 2780 | 0.667 | 1.12 | 1.18 | -0.000504
CFLAllSpcPGEMBTExCZ04 | Com-Iltg-dWatt-CFL_OSspc | PGE | MBT | Ex | CZ04 | 2.78 | 0.000667 | 0 | 3.1004 | 0.000799 | -0.00108 | 2.78 | 0.000667 | 0 | 3.1004 | 0.000799 | -0.00108 |  | CFL | AllSpc | 2780 | 0.667 | 2780 | 0.667 | 1.12 | 1.2 | -0.00038849 | 2780 | 0.667 | 2780 | 0.667 | 1.12 | 1.2 | -0.000388
CFLAllSpcPGEMBTExCZ05 | Com-Iltg-dWatt-CFL_OSspc | PGE | MBT | Ex | CZ05 | 2.78 | 0.000667 | 0 | 3.08 | 0.00079004 | -0.00088104 | 2.78 | 0.000667 | 0 | 3.08 | 0.00079004 | -0.00088104 |  | CFL | AllSpc | 2780 | 0.667 | 2780 | 0.667 | 1.11 | 1.18 | -0.00031692 | 2780 | 0.667 | 2780 | 0.667 | 1.11 | 1.18 | -0.000317
CFLAllSpcPGEMBTExCZ11 | Com-Iltg-dWatt-CFL_OSspc | PGE | MBT | Ex | CZ11 | 2.78 | 0.000667 | 0 | 3.1007 | 0.000803 | -0.0017207 | 2.78 | 0.000667 | 0 | 3.1007 | 0.000803 | -0.0017207 |  | CFL | AllSpc | 2780 | 0.667 | 2780 | 0.667 | 1.12 | 1.2 | -0.00061894 | 2780 | 0.667 | 2780 | 0.667 | 1.12 | 1.2 | -0.000619
CFLAllSpcPGEMBTExCZ12 | Com-Iltg-dWatt-CFL_OSspc | PGE | MBT | Ex | CZ12 | 2.78 | 0.000667 | 0 | 3.09 | 0.00078105 | -0.0016905 | 2.78 | 0.000667 | 0 | 3.09 | 0.00078105 | -0.0016905 |  | CFL | AllSpc | 2780 | 0.667 | 2780 | 0.667 | 1.11 | 1.17 | -0.00060811 | 2780 | 0.667 | 2780 | 0.667 | 1.11 | 1.17 | -0.000608
CFLAllSpcPGEMBTExCZ13 | Com-Iltg-dWatt-CFL_OSspc | PGE | MBT | Ex | CZ13 | 2.78 | 0.000667 | 0 | 3.1106 | 0.000783 | -0.0014206 | 2.78 | 0.000667 | 0 | 3.1106 | 0.000783 | -0.0014206 |  | CFL | AllSpc | 2780 | 0.667 | 2780 | 0.667 | 1.12 | 1.17 | -0.00051102 | 2780 | 0.667 | 2780 | 0.667 | 1.12 | 1.17 | -0.000511
CFLAllSpcPGEMBTExCZ16 | Com-Iltg-dWatt-CFL_OSspc | PGE | MBT | Ex | CZ16 | 2.78 | 0.000667 | 0 | 2.9706 | 0.000769 | -0.0073906 | 2.78 | 0.000667 | 0 | 2.9706 | 0.000769 | -0.0073906 |  | CFL | AllSpc | 2780 | 0.667 | 2780 | 0.667 | 1.07 | 1.15 | -0.0026585 | 2780 | 0.667 | 2780 | 0.667 | 1.07 | 1.15 | -0.00266
CFLAllSpcPGEMBTExIOU | Com-Iltg-dWatt-CFL_OSspc | PGE | MBT | Ex | IOU | 2.78 | 0.000667 | 0 | 3.0991 | 0.00078891 | -0.0014961 | 2.78 | 0.000667 | 0 | 3.0991 | 0.00078891 | -0.0014961 |  | CFL | AllSpc | 2780 | 0.667 | 2780 | 0.667 | 1.11 | 1.18 | -0.00053817 | 2780 | 0.667 | 2780 | 0.667 | 1.11 | 1.18 | -0.000538
CFLAllSpcPGEMBTNewCZ01 | Com-Iltg-dWatt-CFL_OSspc | PGE | MBT | New | CZ01 | 2.78 | 0.000667 | 0 | 2.85 | 0.000755 | -0.00309 | 2.78 | 0.000667 | 0 | 2.85 | 0.000755 | -0.00309 |  | CFL | AllSpc | 2780 | 0.667 | 2780 | 0.667 | 1.03 | 1.13 | -0.0011115 | 2780 | 0.667 | 2780 | 0.667 | 1.03 | 1.13 | -0.00111
CFLAllSpcPGEMBTNewCZ02 | Com-Iltg-dWatt-CFL_OSspc | PGE | MBT | New | CZ02 | 2.78 | 0.000667 | 0 | 2.97 | 0.000819 | -0.00146 | 2.78 | 0.000667 | 0 | 2.97 | 0.000819 | -0.00146 |  | CFL | AllSpc | 2780 | 0.667 | 2780 | 0.667 | 1.07 | 1.23 | -0.00052518 | 2780 | 0.667 | 2780 | 0.667 | 1.07 | 1.23 | -0.000525
CFLAllSpcPGEMBTNewCZ03 | Com-Iltg-dWatt-CFL_OSspc | PGE | MBT | New | CZ03 | 2.78 | 0.000667 | 0 | 2.94 | 0.000795 | -0.00138 | 2.78 | 0.000667 | 0 | 2.94 | 0.000795 | -0.00138 |  | CFL | AllSpc | 2780 | 0.667 | 2780 | 0.667 | 1.06 | 1.19 | -0.0004964 | 2780 | 0.667 | 2780 | 0.667 | 1.06 | 1.19 | -0.000496
CFLAllSpcPGEMBTNewCZ04 | Com-Iltg-dWatt-CFL_OSspc | PGE | MBT | New | CZ04 | 2.78 | 0.000667 | 0 | 3 | 0.000812 | -0.0011 | 2.78 | 0.000667 | 0 | 3 | 0.000812 | -0.0011 |  | CFL | AllSpc | 2780 | 0.667 | 2780 | 0.667 | 1.08 | 1.22 | -0.00039568 | 2780 | 0.667 | 2780 | 0.667 | 1.08 | 1.22 | -0.000396
CFLAllSpcPGEMBTNewCZ05 | Com-Iltg-dWatt-CFL_OSspc | PGE | MBT | New | CZ05 | 2.78 | 0.000667 | 0 | 2.95 | 0.000791 | -0.000737 | 2.78 | 0.000667 | 0 | 2.95 | 0.000791 | -0.000737 |  | CFL | AllSpc | 2780 | 0.667 | 2780 | 0.667 | 1.06 | 1.19 | -0.00026511 | 2780 | 0.667 | 2780 | 0.667 | 1.06 | 1.19 | -0.000265
CFLAllSpcPGEMBTNewCZ11 | Com-Iltg-dWatt-CFL_OSspc | PGE | MBT | New | CZ11 | 2.78 | 0.000667 | 0 | 3.03 | 0.000827 | -0.00153 | 2.78 | 0.000667 | 0 | 3.03 | 0.000827 | -0.00153 |  | CFL | AllSpc | 2780 | 0.667 | 2780 | 0.667 | 1.09 | 1.24 | -0.00055036 | 2780 | 0.667 | 2780 | 0.667 | 1.09 | 1.24 | -0.00055
CFLAllSpcPGEMBTNewCZ12 | Com-Iltg-dWatt-CFL_OSspc | PGE | MBT | New | CZ12 | 2.78 | 0.000667 | 0 | 3.01 | 0.000821 | -0.00132 | 2.78 | 0.000667 | 0 | 3.01 | 0.000821 | -0.00132 |  | CFL | AllSpc | 2780 | 0.667 | 2780 | 0.667 | 1.08 | 1.23 | -0.00047482 | 2780 | 0.667 | 2780 | 0.667 | 1.08 | 1.23 | -0.000475
CFLAllSpcPGEMBTNewCZ13 | Com-Iltg-dWatt-CFL_OSspc | PGE | MBT | New | CZ13 | 2.78 | 0.000667 | 0 | 3.03 | 0.000818 | -0.00123 | 2.78 | 0.000667 | 0 | 3.03 | 0.000818 | -0.00123 |  | CFL | AllSpc | 2780 | 0.667 | 2780 | 0.667 | 1.09 | 1.23 | -0.00044245 | 2780 | 0.667 | 2780 | 0.667 | 1.09 | 1.23 | -0.000442
CFLAllSpcPGEMBTNewCZ16 | Com-Iltg-dWatt-CFL_OSspc | PGE | MBT | New | CZ16 | 2.78 | 0.000667 | 0 | 2.91 | 0.000791 | -0.00573 | 2.78 | 0.000667 | 0 | 2.91 | 0.000791 | -0.00573 |  | CFL | AllSpc | 2780 | 0.667 | 2780 | 0.667 | 1.05 | 1.19 | -0.0020612 | 2780 | 0.667 | 2780 | 0.667 | 1.05 | 1.19 | -0.00206
CFLAllSpcPGEMBTNewIOU | Com-Iltg-dWatt-CFL_OSspc | PGE | MBT | New | IOU | 2.78 | 0.000667 | 0 | 2.9903 | 0.00081147 | -0.0013659 | 2.78 | 0.000667 | 0 | 2.9903 | 0.00081147 | -0.0013659 |  | CFL | AllSpc | 2780 | 0.667 | 2780 | 0.667 | 1.08 | 1.22 | -0.00049133 | 2780 | 0.667 | 2780 | 0.667 | 1.08 | 1.22 | -0.000491
CFLAllSpcPGEMLIExCZ01 | Com-Iltg-dWatt-CFL_OSspc | PGE | MLI | Ex | CZ01 | 2.29 | 0.00066 | 0 | 2.2305 | 0.000751 | -0.026305 | 2.29 | 0.00066 | 0 | 2.2305 | 0.000751 | -0.026305 |  | CFL | AllSpc | 2290 | 0.66 | 2290 | 0.66 | 0.974 | 1.14 | -0.011487 | 2290 | 0.66 | 2290 | 0.66 | 0.974 | 1.14 | -0.0115
CFLAllSpcPGEMLIExCZ02 | Com-Iltg-dWatt-CFL_OSspc | PGE | MLI | Ex | CZ02 | 2.29 | 0.00066 | 0 | 2.39 | 0.00076496 | -0.013 | 2.29 | 0.00066 | 0 | 2.39 | 0.00076496 | -0.013 |  | CFL | AllSpc | 2290 | 0.66 | 2290 | 0.66 | 1.04 | 1.16 | -0.0056769 | 2290 | 0.66 | 2290 | 0.66 | 1.04 | 1.16 | -0.00568
CFLAllSpcPGEMLIExCZ03 | Com-Iltg-dWatt-CFL_OSspc | PGE | MLI | Ex | CZ03 | 2.29 | 0.00066 | 0 | 2.3803 | 0.000765 | -0.012003 | 2.29 | 0.00066 | 0 | 2.3803 | 0.000765 | -0.012003 |  | CFL | AllSpc | 2290 | 0.66 | 2290 | 0.66 | 1.04 | 1.16 | -0.0052415 | 2290 | 0.66 | 2290 | 0.66 | 1.04 | 1.16 | -0.00524
CFLAllSpcPGEMLIExCZ04 | Com-Iltg-dWatt-CFL_OSspc | PGE | MLI | Ex | CZ04 | 2.29 | 0.00066 | 0 | 2.41 | 0.000762 | -0.0097604 | 2.29 | 0.00066 | 0 | 2.41 | 0.000762 | -0.0097604 |  | CFL | AllSpc | 2290 | 0.66 | 2290 | 0.66 | 1.05 | 1.15 | -0.0042622 | 2290 | 0.66 | 2290 | 0.66 | 1.05 | 1.15 | -0.00426
CFLAllSpcPGEMLIExCZ05 | Com-Iltg-dWatt-CFL_OSspc | PGE | MLI | Ex | CZ05 | 2.29 | 0.00066 | 0 | 2.38 | 0.000764 | -0.0112 | 2.29 | 0.00066 | 0 | 2.38 | 0.000764 | -0.0112 |  | CFL | AllSpc | 2290 | 0.66 | 2290 | 0.66 | 1.04 | 1.16 | -0.0048908 | 2290 | 0.66 | 2290 | 0.66 | 1.04 | 1.16 | -0.00489
CFLAllSpcPGEMLIExCZ11 | Com-Iltg-dWatt-CFL_OSspc | PGE | MLI | Ex | CZ11 | 2.29 | 0.00066 | 0 | 2.4 | 0.000764 | -0.013607 | 2.29 | 0.00066 | 0 | 2.4 | 0.000764 | -0.013607 |  | CFL | AllSpc | 2290 | 0.66 | 2290 | 0.66 | 1.05 | 1.16 | -0.0059417 | 2290 | 0.66 | 2290 | 0.66 | 1.05 | 1.16 | -0.00594
CFLAllSpcPGEMLIExCZ12 | Com-Iltg-dWatt-CFL_OSspc | PGE | MLI | Ex | CZ12 | 2.29 | 0.00066 | 0 | 2.3905 | 0.00076895 | -0.0132 | 2.29 | 0.00066 | 0 | 2.3905 | 0.00076895 | -0.0132 |  | CFL | AllSpc | 2290 | 0.66 | 2290 | 0.66 | 1.04 | 1.17 | -0.0057642 | 2290 | 0.66 | 2290 | 0.66 | 1.04 | 1.17 | -0.00576
CFLAllSpcPGEMLIExCZ13 | Com-Iltg-dWatt-CFL_OSspc | PGE | MLI | Ex | CZ13 | 2.29 | 0.00066 | 0 | 2.42 | 0.000756 | -0.0119 | 2.29 | 0.00066 | 0 | 2.42 | 0.000756 | -0.0119 |  | CFL | AllSpc | 2290 | 0.66 | 2290 | 0.66 | 1.06 | 1.15 | -0.0051965 | 2290 | 0.66 | 2290 | 0.66 | 1.06 | 1.15 | -0.0052
CFLAllSpcPGEMLIExCZ16 | Com-Iltg-dWatt-CFL_OSspc | PGE | MLI | Ex | CZ16 | 2.29 | 0.00066 | 0 | 2.2506 | 0.00075 | -0.0275 | 2.29 | 0.00066 | 0 | 2.2506 | 0.00075 | -0.0275 |  | CFL | AllSpc | 2290 | 0.66 | 2290 | 0.66 | 0.983 | 1.14 | -0.012009 | 2290 | 0.66 | 2290 | 0.66 | 0.983 | 1.14 | -0.012
CFLAllSpcPGEMLIExIOU | Com-Iltg-dWatt-CFL_OSspc | PGE | MLI | Ex | IOU | 2.29 | 0.00066 | 0 | 2.3917 | 0.00076378 | -0.012208 | 2.29 | 0.00066 | 0 | 2.3917 | 0.00076378 | -0.012208 |  | CFL | AllSpc | 2290 | 0.66 | 2290 | 0.66 | 1.04 | 1.16 | -0.0053309 | 2290 | 0.66 | 2290 | 0.66 | 1.04 | 1.16 | -0.00533
CFLAllSpcPGEMLINewCZ01 | Com-Iltg-dWatt-CFL_OSspc | PGE | MLI | New | CZ01 | 2.29 | 0.00066 | 0 | 2.17 | 0.000717 | -0.0351 | 2.29 | 0.00066 | 0 | 2.17 | 0.000717 | -0.0351 |  | CFL | AllSpc | 2290 | 0.66 | 2290 | 0.66 | 0.948 | 1.09 | -0.015328 | 2290 | 0.66 | 2290 | 0.66 | 0.948 | 1.09 | -0.0153
CFLAllSpcPGEMLINewCZ02 | Com-Iltg-dWatt-CFL_OSspc | PGE | MLI | New | CZ02 | 2.29 | 0.00066 | 0 | 2.31 | 0.00076 | -0.0194 | 2.29 | 0.00066 | 0 | 2.31 | 0.00076 | -0.0194 |  | CFL | AllSpc | 2290 | 0.66 | 2290 | 0.66 | 1.01 | 1.15 | -0.0084716 | 2290 | 0.66 | 2290 | 0.66 | 1.01 | 1.15 | -0.00847
CFLAllSpcPGEMLINewCZ03 | Com-Iltg-dWatt-CFL_OSspc | PGE | MLI | New | CZ03 | 2.29 | 0.00066 | 0 | 2.27 | 0.000768 | -0.019 | 2.29 | 0.00066 | 0 | 2.27 | 0.000768 | -0.019 |  | CFL | AllSpc | 2290 | 0.66 | 2290 | 0.66 | 0.991 | 1.16 | -0.0082969 | 2290 | 0.66 | 2290 | 0.66 | 0.991 | 1.16 | -0.0083
CFLAllSpcPGEMLINewCZ04 | Com-Iltg-dWatt-CFL_OSspc | PGE | MLI | New | CZ04 | 2.29 | 0.00066 | 0 | 2.34 | 0.000759 | -0.0153 | 2.29 | 0.00066 | 0 | 2.34 | 0.000759 | -0.0153 |  | CFL | AllSpc | 2290 | 0.66 | 2290 | 0.66 | 1.02 | 1.15 | -0.0066812 | 2290 | 0.66 | 2290 | 0.66 | 1.02 | 1.15 | -0.00668
CFLAllSpcPGEMLINewCZ05 | Com-Iltg-dWatt-CFL_OSspc | PGE | MLI | New | CZ05 | 2.29 | 0.00066 | 0 | 2.27 | 0.000756 | -0.0185 | 2.29 | 0.00066 | 0 | 2.27 | 0.000756 | -0.0185 |  | CFL | AllSpc | 2290 | 0.66 | 2290 | 0.66 | 0.991 | 1.15 | -0.0080786 | 2290 | 0.66 | 2290 | 0.66 | 0.991 | 1.15 | -0.00808
CFLAllSpcPGEMLINewCZ11 | Com-Iltg-dWatt-CFL_OSspc | PGE | MLI | New | CZ11 | 2.29 | 0.00066 | 0 | 2.4 | 0.000788 | -0.0163 | 2.29 | 0.00066 | 0 | 2.4 | 0.000788 | -0.0163 |  | CFL | AllSpc | 2290 | 0.66 | 2290 | 0.66 | 1.05 | 1.19 | -0.0071179 | 2290 | 0.66 | 2290 | 0.66 | 1.05 | 1.19 | -0.00712
CFLAllSpcPGEMLINewCZ12 | Com-Iltg-dWatt-CFL_OSspc | PGE | MLI | New | CZ12 | 2.29 | 0.00066 | 0 | 2.36 | 0.000778 | -0.0177 | 2.29 | 0.00066 | 0 | 2.36 | 0.000778 | -0.0177 |  | CFL | AllSpc | 2290 | 0.66 | 2290 | 0.66 | 1.03 | 1.18 | -0.0077293 | 2290 | 0.66 | 2290 | 0.66 | 1.03 | 1.18 | -0.00773
CFLAllSpcPGEMLINewCZ13 | Com-Iltg-dWatt-CFL_OSspc | PGE | MLI | New | CZ13 | 2.29 | 0.00066 | 0 | 2.43 | 0.000793 | -0.0153 | 2.29 | 0.00066 | 0 | 2.43 | 0.000793 | -0.0153 |  | CFL | AllSpc | 2290 | 0.66 | 2290 | 0.66 | 1.06 | 1.2 | -0.0066812 | 2290 | 0.66 | 2290 | 0.66 | 1.06 | 1.2 | -0.00668
CFLAllSpcPGEMLINewCZ16 | Com-Iltg-dWatt-CFL_OSspc | PGE | MLI | New | CZ16 | 2.29 | 0.00066 | 0 | 2.25 | 0.000749 | -0.0298 | 2.29 | 0.00066 | 0 | 2.25 | 0.000749 | -0.0298 |  | CFL | AllSpc | 2290 | 0.66 | 2290 | 0.66 | 0.983 | 1.13 | -0.013013 | 2290 | 0.66 | 2290 | 0.66 | 0.983 | 1.13 | -0.013
CFLAllSpcPGEMLINewIOU | Com-Iltg-dWatt-CFL_OSspc | PGE | MLI | New | IOU | 2.29 | 0.00066 | 0 | 2.3422 | 0.00077311 | -0.017485 | 2.29 | 0.00066 | 0 | 2.3422 | 0.00077311 | -0.017485 |  | CFL | AllSpc | 2290 | 0.66 | 2290 | 0.66 | 1.02 | 1.17 | -0.0076355 | 2290 | 0.66 | 2290 | 0.66 | 1.02 | 1.17 | -0.00764
CFLAllSpcPGEMtlExCZ01 | Com-Iltg-dWatt-CFL_OSspc | PGE | Mtl | Ex | CZ01 | 1.22 | 0.000131 | 0 | 1.2 | 0.000155 | -0.0105 | 1.22 | 0.000131 | 0 | 1.2 | 0.000155 | -0.0105 |  | CFL | AllSpc | 1220 | 0.131 | 1220 | 0.131 | 0.984 | 1.18 | -0.0086066 | 1220 | 0.131 | 1220 | 0.131 | 0.984 | 1.18 | -0.00861
CFLAllSpcPGEMtlExCZ02 | Com-Iltg-dWatt-CFL_OSspc | PGE | Mtl | Ex | CZ02 | 1.22 | 0.000131 | 0 | 1.27 | 0.000161 | -0.00697 | 1.22 | 0.000131 | 0 | 1.27 | 0.000161 | -0.00697 |  | CFL | AllSpc | 1220 | 0.131 | 1220 | 0.131 | 1.04 | 1.23 | -0.0057131 | 1220 | 0.131 | 1220 | 0.131 | 1.04 | 1.23 | -0.00571
CFLAllSpcPGEMtlExCZ03 | Com-Iltg-dWatt-CFL_OSspc | PGE | Mtl | Ex | CZ03 | 1.22 | 0.000131 | 0 | 1.2803 | 0.000158 | -0.00676 | 1.22 | 0.000131 | 0 | 1.2803 | 0.000158 | -0.00676 |  | CFL | AllSpc | 1220 | 0.131 | 1220 | 0.131 | 1.05 | 1.21 | -0.005541 | 1220 | 0.131 | 1220 | 0.131 | 1.05 | 1.21 | -0.00554
CFLAllSpcPGEMtlExCZ04 | Com-Iltg-dWatt-CFL_OSspc | PGE | Mtl | Ex | CZ04 | 1.22 | 0.000131 | 0 | 1.3 | 0.00016 | -0.00559 | 1.22 | 0.000131 | 0 | 1.3 | 0.00016 | -0.00559 |  | CFL | AllSpc | 1220 | 0.131 | 1220 | 0.131 | 1.07 | 1.22 | -0.004582 | 1220 | 0.131 | 1220 | 0.131 | 1.07 | 1.22 | -0.00458
CFLAllSpcPGEMtlExCZ05 | Com-Iltg-dWatt-CFL_OSspc | PGE | Mtl | Ex | CZ05 | 1.22 | 0.000131 | 0 | 1.27 | 0.00015635 | -0.00711 | 1.22 | 0.000131 | 0 | 1.27 | 0.00015635 | -0.00711 |  | CFL | AllSpc | 1220 | 0.131 | 1220 | 0.131 | 1.04 | 1.19 | -0.0058279 | 1220 | 0.131 | 1220 | 0.131 | 1.04 | 1.19 | -0.00583
CFLAllSpcPGEMtlExCZ11 | Com-Iltg-dWatt-CFL_OSspc | PGE | Mtl | Ex | CZ11 | 1.22 | 0.000131 | 0 | 1.31 | 0.000163 | -0.00587 | 1.22 | 0.000131 | 0 | 1.31 | 0.000163 | -0.00587 |  | CFL | AllSpc | 1220 | 0.131 | 1220 | 0.131 | 1.07 | 1.24 | -0.0048115 | 1220 | 0.131 | 1220 | 0.131 | 1.07 | 1.24 | -0.00481
CFLAllSpcPGEMtlExCZ12 | Com-Iltg-dWatt-CFL_OSspc | PGE | Mtl | Ex | CZ12 | 1.22 | 0.000131 | 0 | 1.3 | 0.000163 | -0.0062 | 1.22 | 0.000131 | 0 | 1.3 | 0.000163 | -0.0062 |  | CFL | AllSpc | 1220 | 0.131 | 1220 | 0.131 | 1.07 | 1.24 | -0.005082 | 1220 | 0.131 | 1220 | 0.131 | 1.07 | 1.24 | -0.00508
CFLAllSpcPGEMtlExCZ13 | Com-Iltg-dWatt-CFL_OSspc | PGE | Mtl | Ex | CZ13 | 1.22 | 0.000131 | 0 | 1.33 | 0.000162 | -0.00549 | 1.22 | 0.000131 | 0 | 1.33 | 0.000162 | -0.00549 |  | CFL | AllSpc | 1220 | 0.131 | 1220 | 0.131 | 1.09 | 1.24 | -0.0045 | 1220 | 0.131 | 1220 | 0.131 | 1.09 | 1.24 | -0.0045
CFLAllSpcPGEMtlExCZ16 | Com-Iltg-dWatt-CFL_OSspc | PGE | Mtl | Ex | CZ16 | 1.22 | 0.000131 | 0 | 1.2 | 0.000157 | -0.00936 | 1.22 | 0.000131 | 0 | 1.2 | 0.000157 | -0.00936 |  | CFL | AllSpc | 1220 | 0.131 | 1220 | 0.131 | 0.984 | 1.2 | -0.0076721 | 1220 | 0.131 | 1220 | 0.131 | 0.984 | 1.2 | -0.00767
CFLAllSpcPGEMtlExIOU | Com-Iltg-dWatt-CFL_OSspc | PGE | Mtl | Ex | IOU | 1.22 | 0.000131 | 0 | 1.2872 | 0.00015952 | -0.0065087 | 1.22 | 0.000131 | 0 | 1.2872 | 0.00015952 | -0.0065087 |  | CFL | AllSpc | 1220 | 0.131 | 1220 | 0.131 | 1.06 | 1.22 | -0.005335 | 1220 | 0.131 | 1220 | 0.131 | 1.06 | 1.22 | -0.00534
CFLAllSpcPGEMtlNewCZ01 | Com-Iltg-dWatt-CFL_OSspc | PGE | Mtl | New | CZ01 | 1.22 | 0.000131 | 0 | 1.15 | 0.000155 | -0.0135 | 1.22 | 0.000131 | 0 | 1.15 | 0.000155 | -0.0135 |  | CFL | AllSpc | 1220 | 0.131 | 1220 | 0.131 | 0.943 | 1.18 | -0.011066 | 1220 | 0.131 | 1220 | 0.131 | 0.943 | 1.18 | -0.0111
CFLAllSpcPGEMtlNewCZ02 | Com-Iltg-dWatt-CFL_OSspc | PGE | Mtl | New | CZ02 | 1.22 | 0.000131 | 0 | 1.25 | 0.000165 | -0.00914 | 1.22 | 0.000131 | 0 | 1.25 | 0.000165 | -0.00914 |  | CFL | AllSpc | 1220 | 0.131 | 1220 | 0.131 | 1.02 | 1.26 | -0.0074918 | 1220 | 0.131 | 1220 | 0.131 | 1.02 | 1.26 | -0.00749
CFLAllSpcPGEMtlNewCZ03 | Com-Iltg-dWatt-CFL_OSspc | PGE | Mtl | New | CZ03 | 1.22 | 0.000131 | 0 | 1.26 | 0.00016 | -0.00859 | 1.22 | 0.000131 | 0 | 1.26 | 0.00016 | -0.00859 |  | CFL | AllSpc | 1220 | 0.131 | 1220 | 0.131 | 1.03 | 1.22 | -0.007041 | 1220 | 0.131 | 1220 | 0.131 | 1.03 | 1.22 | -0.00704
CFLAllSpcPGEMtlNewCZ04 | Com-Iltg-dWatt-CFL_OSspc | PGE | Mtl | New | CZ04 | 1.22 | 0.000131 | 0 | 1.29 | 0.000164 | -0.00724 | 1.22 | 0.000131 | 0 | 1.29 | 0.000164 | -0.00724 |  | CFL | AllSpc | 1220 | 0.131 | 1220 | 0.131 | 1.06 | 1.25 | -0.0059344 | 1220 | 0.131 | 1220 | 0.131 | 1.06 | 1.25 | -0.00593
CFLAllSpcPGEMtlNewCZ05 | Com-Iltg-dWatt-CFL_OSspc | PGE | Mtl | New | CZ05 | 1.22 | 0.000131 | 0 | 1.24 | 0.000158 | -0.00964 | 1.22 | 0.000131 | 0 | 1.24 | 0.000158 | -0.00964 |  | CFL | AllSpc | 1220 | 0.131 | 1220 | 0.131 | 1.02 | 1.21 | -0.0079016 | 1220 | 0.131 | 1220 | 0.131 | 1.02 | 1.21 | -0.0079
CFLAllSpcPGEMtlNewCZ11 | Com-Iltg-dWatt-CFL_OSspc | PGE | Mtl | New | CZ11 | 1.22 | 0.000131 | 0 | 1.3 | 0.000167 | -0.00732 | 1.22 | 0.000131 | 0 | 1.3 | 0.000167 | -0.00732 |  | CFL | AllSpc | 1220 | 0.131 | 1220 | 0.131 | 1.07 | 1.27 | -0.006 | 1220 | 0.131 | 1220 | 0.131 | 1.07 | 1.27 | -0.006
CFLAllSpcPGEMtlNewCZ12 | Com-Iltg-dWatt-CFL_OSspc | PGE | Mtl | New | CZ12 | 1.22 | 0.000131 | 0 | 1.29 | 0.000166 | -0.00765 | 1.22 | 0.000131 | 0 | 1.29 | 0.000166 | -0.00765 |  | CFL | AllSpc | 1220 | 0.131 | 1220 | 0.131 | 1.06 | 1.27 | -0.0062705 | 1220 | 0.131 | 1220 | 0.131 | 1.06 | 1.27 | -0.00627
CFLAllSpcPGEMtlNewCZ13 | Com-Iltg-dWatt-CFL_OSspc | PGE | Mtl | New | CZ13 | 1.22 | 0.000131 | 0 | 1.31 | 0.000166 | -0.00688 | 1.22 | 0.000131 | 0 | 1.31 | 0.000166 | -0.00688 |  | CFL | AllSpc | 1220 | 0.131 | 1220 | 0.131 | 1.07 | 1.27 | -0.0056393 | 1220 | 0.131 | 1220 | 0.131 | 1.07 | 1.27 | -0.00564
CFLAllSpcPGEMtlNewCZ16 | Com-Iltg-dWatt-CFL_OSspc | PGE | Mtl | New | CZ16 | 1.22 | 0.000131 | 0 | 1.18 | 0.000159 | -0.0108 | 1.22 | 0.000131 | 0 | 1.18 | 0.000159 | -0.0108 |  | CFL | AllSpc | 1220 | 0.131 | 1220 | 0.131 | 0.967 | 1.21 | -0.0088525 | 1220 | 0.131 | 1220 | 0.131 | 0.967 | 1.21 | -0.00885
CFLAllSpcPGEMtlNewIOU | Com-Iltg-dWatt-CFL_OSspc | PGE | Mtl | New | IOU | 1.22 | 0.000131 | 0 | 1.2734 | 0.00016317 | -0.008152 | 1.22 | 0.000131 | 0 | 1.2734 | 0.00016317 | -0.008152 |  | CFL | AllSpc | 1220 | 0.131 | 1220 | 0.131 | 1.04 | 1.25 | -0.006682 | 1220 | 0.131 | 1220 | 0.131 | 1.04 | 1.25 | -0.00668
CFLAllSpcPGENrsExCZ01 | Com-Iltg-dWatt-CFL_OSspc | PGE | Nrs | Ex | CZ01 | 3.18 | 0.00048404 | 0 | 3.12 | 0.00055304 | -0.0642 | 3.18 | 0.00048404 | 0 | 3.12 | 0.00055304 | -0.0642 |  | CFL | AllSpc | 3180 | 0.484 | 3180 | 0.484 | 0.981 | 1.14 | -0.020189 | 3180 | 0.484 | 3180 | 0.484 | 0.981 | 1.14 | -0.0202
CFLAllSpcPGENrsExCZ02 | Com-Iltg-dWatt-CFL_OSspc | PGE | Nrs | Ex | CZ02 | 3.18 | 0.00048405 | 0 | 3.29 | 0.0006081 | -0.0464 | 3.18 | 0.00048405 | 0 | 3.29 | 0.0006081 | -0.0464 |  | CFL | AllSpc | 3180 | 0.484 | 3180 | 0.484 | 1.03 | 1.26 | -0.014591 | 3180 | 0.484 | 3180 | 0.484 | 1.03 | 1.26 | -0.0146
CFLAllSpcPGENrsExCZ03 | Com-Iltg-dWatt-CFL_OSspc | PGE | Nrs | Ex | CZ03 | 3.18 | 0.00048405 | 0 | 3.26 | 0.00059005 | -0.047005 | 3.18 | 0.00048405 | 0 | 3.26 | 0.00059005 | -0.047005 |  | CFL | AllSpc | 3180 | 0.484 | 3180 | 0.484 | 1.03 | 1.22 | -0.014781 | 3180 | 0.484 | 3180 | 0.484 | 1.03 | 1.22 | -0.0148
CFLAllSpcPGENrsExCZ04 | Com-Iltg-dWatt-CFL_OSspc | PGE | Nrs | Ex | CZ04 | 3.18 | 0.00048405 | 0 | 3.34 | 0.00060405 | -0.039705 | 3.18 | 0.00048405 | 0 | 3.34 | 0.00060405 | -0.039705 |  | CFL | AllSpc | 3180 | 0.484 | 3180 | 0.484 | 1.05 | 1.25 | -0.012486 | 3180 | 0.484 | 3180 | 0.484 | 1.05 | 1.25 | -0.0125
CFLAllSpcPGENrsExCZ05 | Com-Iltg-dWatt-CFL_OSspc | PGE | Nrs | Ex | CZ05 | 3.18 | 0.00048405 | 0 | 3.23 | 0.00057505 | -0.0483 | 3.18 | 0.00048405 | 0 | 3.23 | 0.00057505 | -0.0483 |  | CFL | AllSpc | 3180 | 0.484 | 3180 | 0.484 | 1.02 | 1.19 | -0.015189 | 3180 | 0.484 | 3180 | 0.484 | 1.02 | 1.19 | -0.0152
CFLAllSpcPGENrsExCZ11 | Com-Iltg-dWatt-CFL_OSspc | PGE | Nrs | Ex | CZ11 | 3.18 | 0.00048406 | 0 | 3.3806 | 0.00061312 | -0.038406 | 3.18 | 0.00048406 | 0 | 3.3806 | 0.00061312 | -0.038406 |  | CFL | AllSpc | 3180 | 0.484 | 3180 | 0.484 | 1.06 | 1.27 | -0.012077 | 3180 | 0.484 | 3180 | 0.484 | 1.06 | 1.27 | -0.0121
CFLAllSpcPGENrsExCZ12 | Com-Iltg-dWatt-CFL_OSspc | PGE | Nrs | Ex | CZ12 | 3.18 | 0.00048406 | 0 | 3.3506 | 0.00061013 | -0.040306 | 3.18 | 0.00048406 | 0 | 3.3506 | 0.00061013 | -0.040306 |  | CFL | AllSpc | 3180 | 0.484 | 3180 | 0.484 | 1.05 | 1.26 | -0.012675 | 3180 | 0.484 | 3180 | 0.484 | 1.05 | 1.26 | -0.0127
CFLAllSpcPGENrsExCZ13 | Com-Iltg-dWatt-CFL_OSspc | PGE | Nrs | Ex | CZ13 | 3.18 | 0.00048406 | 0 | 3.4 | 0.00061106 | -0.036806 | 3.18 | 0.00048406 | 0 | 3.4 | 0.00061106 | -0.036806 |  | CFL | AllSpc | 3180 | 0.484 | 3180 | 0.484 | 1.07 | 1.26 | -0.011574 | 3180 | 0.484 | 3180 | 0.484 | 1.07 | 1.26 | -0.0116
CFLAllSpcPGENrsExCZ16 | Com-Iltg-dWatt-CFL_OSspc | PGE | Nrs | Ex | CZ16 | 3.18 | 0.00048405 | 0 | 3.2 | 0.00058605 | -0.055905 | 3.18 | 0.00048405 | 0 | 3.2 | 0.00058605 | -0.055905 |  | CFL | AllSpc | 3180 | 0.484 | 3180 | 0.484 | 1.01 | 1.21 | -0.01758 | 3180 | 0.484 | 3180 | 0.484 | 1.01 | 1.21 | -0.0176
CFLAllSpcPGENrsExIOU | Com-Iltg-dWatt-CFL_OSspc | PGE | Nrs | Ex | IOU | 3.18 | 0.00048405 | 0 | 3.322 | 0.00060227 | -0.042524 | 3.18 | 0.00048405 | 0 | 3.322 | 0.00060227 | -0.042524 |  | CFL | AllSpc | 3180 | 0.484 | 3180 | 0.484 | 1.04 | 1.24 | -0.013372 | 3180 | 0.484 | 3180 | 0.484 | 1.04 | 1.24 | -0.0134
CFLAllSpcPGENrsNewCZ01 | Com-Iltg-dWatt-CFL_OSspc | PGE | Nrs | New | CZ01 | 3.18 | 0.000485 | 0 | 3.02 | 0.00053 | -0.07 | 3.18 | 0.000485 | 0 | 3.02 | 0.00053 | -0.07 |  | CFL | AllSpc | 3180 | 0.485 | 3180 | 0.485 | 0.95 | 1.09 | -0.022013 | 3180 | 0.485 | 3180 | 0.485 | 0.95 | 1.09 | -0.022
CFLAllSpcPGENrsNewCZ02 | Com-Iltg-dWatt-CFL_OSspc | PGE | Nrs | New | CZ02 | 3.18 | 0.000485 | 0 | 3.18 | 0.000607 | -0.0493 | 3.18 | 0.000485 | 0 | 3.18 | 0.000607 | -0.0493 |  | CFL | AllSpc | 3180 | 0.485 | 3180 | 0.485 | 1 | 1.25 | -0.015503 | 3180 | 0.485 | 3180 | 0.485 | 1 | 1.25 | -0.0155
CFLAllSpcPGENrsNewCZ03 | Com-Iltg-dWatt-CFL_OSspc | PGE | Nrs | New | CZ03 | 3.18 | 0.000485 | 0 | 3.13 | 0.000597 | -0.0515 | 3.18 | 0.000485 | 0 | 3.13 | 0.000597 | -0.0515 |  | CFL | AllSpc | 3180 | 0.485 | 3180 | 0.485 | 0.984 | 1.23 | -0.016195 | 3180 | 0.485 | 3180 | 0.485 | 0.984 | 1.23 | -0.0162
CFLAllSpcPGENrsNewCZ04 | Com-Iltg-dWatt-CFL_OSspc | PGE | Nrs | New | CZ04 | 3.18 | 0.000485 | 0 | 3.26 | 0.000607 | -0.0417 | 3.18 | 0.000485 | 0 | 3.26 | 0.000607 | -0.0417 |  | CFL | AllSpc | 3180 | 0.485 | 3180 | 0.485 | 1.03 | 1.25 | -0.013113 | 3180 | 0.485 | 3180 | 0.485 | 1.03 | 1.25 | -0.0131
CFLAllSpcPGENrsNewCZ05 | Com-Iltg-dWatt-CFL_OSspc | PGE | Nrs | New | CZ05 | 3.18 | 0.000485 | 0 | 3.13 | 0.000575 | -0.0534 | 3.18 | 0.000485 | 0 | 3.13 | 0.000575 | -0.0534 |  | CFL | AllSpc | 3180 | 0.485 | 3180 | 0.485 | 0.984 | 1.19 | -0.016792 | 3180 | 0.485 | 3180 | 0.485 | 0.984 | 1.19 | -0.0168
CFLAllSpcPGENrsNewCZ11 | Com-Iltg-dWatt-CFL_OSspc | PGE | Nrs | New | CZ11 | 3.18 | 0.000485 | 0 | 3.34 | 0.000615 | -0.0398 | 3.18 | 0.000485 | 0 | 3.34 | 0.000615 | -0.0398 |  | CFL | AllSpc | 3180 | 0.485 | 3180 | 0.485 | 1.05 | 1.27 | -0.012516 | 3180 | 0.485 | 3180 | 0.485 | 1.05 | 1.27 | -0.0125
CFLAllSpcPGENrsNewCZ12 | Com-Iltg-dWatt-CFL_OSspc | PGE | Nrs | New | CZ12 | 3.18 | 0.000485 | 0 | 3.29 | 0.000617 | -0.0417 | 3.18 | 0.000485 | 0 | 3.29 | 0.000617 | -0.0417 |  | CFL | AllSpc | 3180 | 0.485 | 3180 | 0.485 | 1.03 | 1.27 | -0.013113 | 3180 | 0.485 | 3180 | 0.485 | 1.03 | 1.27 | -0.0131
CFLAllSpcPGENrsNewCZ13 | Com-Iltg-dWatt-CFL_OSspc | PGE | Nrs | New | CZ13 | 3.18 | 0.000485 | 0 | 3.35 | 0.000616 | -0.0378 | 3.18 | 0.000485 | 0 | 3.35 | 0.000616 | -0.0378 |  | CFL | AllSpc | 3180 | 0.485 | 3180 | 0.485 | 1.05 | 1.27 | -0.011887 | 3180 | 0.485 | 3180 | 0.485 | 1.05 | 1.27 | -0.0119
CFLAllSpcPGENrsNewCZ16 | Com-Iltg-dWatt-CFL_OSspc | PGE | Nrs | New | CZ16 | 3.18 | 0.000485 | 0 | 3.14 | 0.000588 | -0.0588 | 3.18 | 0.000485 | 0 | 3.14 | 0.000588 | -0.0588 |  | CFL | AllSpc | 3180 | 0.485 | 3180 | 0.485 | 0.987 | 1.21 | -0.018491 | 3180 | 0.485 | 3180 | 0.485 | 0.987 | 1.21 | -0.0185
CFLAllSpcPGENrsNewIOU | Com-Iltg-dWatt-CFL_OSspc | PGE | Nrs | New | IOU | 3.18 | 0.000485 | 0 | 3.2472 | 0.00060801 | -0.044384 | 3.18 | 0.000485 | 0 | 3.2472 | 0.00060801 | -0.044384 |  | CFL | AllSpc | 3180 | 0.485 | 3180 | 0.485 | 1.02 | 1.25 | -0.013957 | 3180 | 0.485 | 3180 | 0.485 | 1.02 | 1.25 | -0.014
CFLAllSpcPGEOfLExCZ01 | Com-Iltg-dWatt-CFL_OSspc | PGE | OfL | Ex | CZ01 | 2.5896 | 0.00050696 | 0 | 2.76 | 0.000643 | -0.024 | 2.5896 | 0.00050696 | 0 | 2.76 | 0.000643 | -0.024 |  | CFL | AllSpc | 2590 | 0.507 | 2590 | 0.507 | 1.07 | 1.27 | -0.0092679 | 2590 | 0.507 | 2590 | 0.507 | 1.07 | 1.27 | -0.00927
CFLAllSpcPGEOfLExCZ02 | Com-Iltg-dWatt-CFL_OSspc | PGE | OfL | Ex | CZ02 | 2.5894 | 0.00050695 | 0 | 2.84 | 0.000677 | -0.0179 | 2.5894 | 0.00050695 | 0 | 2.84 | 0.000677 | -0.0179 |  | CFL | AllSpc | 2590 | 0.507 | 2590 | 0.507 | 1.1 | 1.34 | -0.0069127 | 2590 | 0.507 | 2590 | 0.507 | 1.1 | 1.34 | -0.00691
CFLAllSpcPGEOfLExCZ03 | Com-Iltg-dWatt-CFL_OSspc | PGE | OfL | Ex | CZ03 | 2.5895 | 0.00050695 | 0 | 2.83 | 0.00065995 | -0.0165 | 2.5895 | 0.00050695 | 0 | 2.83 | 0.00065995 | -0.0165 |  | CFL | AllSpc | 2590 | 0.507 | 2590 | 0.507 | 1.09 | 1.3 | -0.0063718 | 2590 | 0.507 | 2590 | 0.507 | 1.09 | 1.3 | -0.00637
CFLAllSpcPGEOfLExCZ04 | Com-Iltg-dWatt-CFL_OSspc | PGE | OfL | Ex | CZ04 | 2.5894 | 0.00050694 | 0 | 2.87 | 0.00066294 | -0.015 | 2.5894 | 0.00050694 | 0 | 2.87 | 0.00066294 | -0.015 |  | CFL | AllSpc | 2590 | 0.507 | 2590 | 0.507 | 1.11 | 1.31 | -0.0057929 | 2590 | 0.507 | 2590 | 0.507 | 1.11 | 1.31 | -0.00579
CFLAllSpcPGEOfLExCZ05 | Com-Iltg-dWatt-CFL_OSspc | PGE | OfL | Ex | CZ05 | 2.5894 | 0.00050694 | 0 | 2.83 | 0.00064494 | -0.0164 | 2.5894 | 0.00050694 | 0 | 2.83 | 0.00064494 | -0.0164 |  | CFL | AllSpc | 2590 | 0.507 | 2590 | 0.507 | 1.09 | 1.27 | -0.0063336 | 2590 | 0.507 | 2590 | 0.507 | 1.09 | 1.27 | -0.00633
CFLAllSpcPGEOfLExCZ11 | Com-Iltg-dWatt-CFL_OSspc | PGE | OfL | Ex | CZ11 | 2.5892 | 0.00050692 | 0 | 2.9 | 0.000676 | -0.0172 | 2.5892 | 0.00050692 | 0 | 2.9 | 0.000676 | -0.0172 |  | CFL | AllSpc | 2590 | 0.507 | 2590 | 0.507 | 1.12 | 1.33 | -0.006643 | 2590 | 0.507 | 2590 | 0.507 | 1.12 | 1.33 | -0.00664
CFLAllSpcPGEOfLExCZ12 | Com-Iltg-dWatt-CFL_OSspc | PGE | OfL | Ex | CZ12 | 2.5892 | 0.00050692 | 0 | 2.87 | 0.00067 | -0.0165 | 2.5892 | 0.00050692 | 0 | 2.87 | 0.00067 | -0.0165 |  | CFL | AllSpc | 2590 | 0.507 | 2590 | 0.507 | 1.11 | 1.32 | -0.0063726 | 2590 | 0.507 | 2590 | 0.507 | 1.11 | 1.32 | -0.00637
CFLAllSpcPGEOfLExCZ13 | Com-Iltg-dWatt-CFL_OSspc | PGE | OfL | Ex | CZ13 | 2.5892 | 0.00050692 | 0 | 2.93 | 0.00067892 | -0.0155 | 2.5892 | 0.00050692 | 0 | 2.93 | 0.00067892 | -0.0155 |  | CFL | AllSpc | 2590 | 0.507 | 2590 | 0.507 | 1.13 | 1.34 | -0.0059864 | 2590 | 0.507 | 2590 | 0.507 | 1.13 | 1.34 | -0.00599
CFLAllSpcPGEOfLExCZ16 | Com-Iltg-dWatt-CFL_OSspc | PGE | OfL | Ex | CZ16 | 2.5894 | 0.00050694 | 0 | 2.69 | 0.00065194 | -0.0305 | 2.5894 | 0.00050694 | 0 | 2.69 | 0.00065194 | -0.0305 |  | CFL | AllSpc | 2590 | 0.507 | 2590 | 0.507 | 1.04 | 1.29 | -0.011779 | 2590 | 0.507 | 2590 | 0.507 | 1.04 | 1.29 | -0.0118
CFLAllSpcPGEOfLExIOU | Com-Iltg-dWatt-CFL_OSspc | PGE | OfL | Ex | IOU | 2.5894 | 0.00050694 | 0 | 2.8516 | 0.00066401 | -0.016263 | 2.5894 | 0.00050694 | 0 | 2.8516 | 0.00066401 | -0.016263 |  | CFL | AllSpc | 2590 | 0.507 | 2590 | 0.507 | 1.1 | 1.31 | -0.0062804 | 2590 | 0.507 | 2590 | 0.507 | 1.1 | 1.31 | -0.00628
CFLAllSpcPGEOfLNewCZ01 | Com-Iltg-dWatt-CFL_OSspc | PGE | OfL | New | CZ01 | 2.58 | 0.000506 | 0 | 2.74 | 0.000616 | -0.0156 | 2.58 | 0.000506 | 0 | 2.74 | 0.000616 | -0.0156 |  | CFL | AllSpc | 2580 | 0.506 | 2580 | 0.506 | 1.06 | 1.22 | -0.0060465 | 2580 | 0.506 | 2580 | 0.506 | 1.06 | 1.22 | -0.00605
CFLAllSpcPGEOfLNewCZ02 | Com-Iltg-dWatt-CFL_OSspc | PGE | OfL | New | CZ02 | 2.58 | 0.000506 | 0 | 2.86 | 0.000628 | -0.0104 | 2.58 | 0.000506 | 0 | 2.86 | 0.000628 | -0.0104 |  | CFL | AllSpc | 2580 | 0.506 | 2580 | 0.506 | 1.11 | 1.24 | -0.004031 | 2580 | 0.506 | 2580 | 0.506 | 1.11 | 1.24 | -0.00403
CFLAllSpcPGEOfLNewCZ03 | Com-Iltg-dWatt-CFL_OSspc | PGE | OfL | New | CZ03 | 2.58 | 0.000506 | 0 | 2.84 | 0.000626 | -0.0103 | 2.58 | 0.000506 | 0 | 2.84 | 0.000626 | -0.0103 |  | CFL | AllSpc | 2580 | 0.506 | 2580 | 0.506 | 1.1 | 1.24 | -0.0039922 | 2580 | 0.506 | 2580 | 0.506 | 1.1 | 1.24 | -0.00399
CFLAllSpcPGEOfLNewCZ04 | Com-Iltg-dWatt-CFL_OSspc | PGE | OfL | New | CZ04 | 2.58 | 0.000506 | 0 | 2.87 | 0.000629 | -0.00946 | 2.58 | 0.000506 | 0 | 2.87 | 0.000629 | -0.00946 |  | CFL | AllSpc | 2580 | 0.506 | 2580 | 0.506 | 1.11 | 1.24 | -0.0036667 | 2580 | 0.506 | 2580 | 0.506 | 1.11 | 1.24 | -0.00367
CFLAllSpcPGEOfLNewCZ05 | Com-Iltg-dWatt-CFL_OSspc | PGE | OfL | New | CZ05 | 2.58 | 0.000506 | 0 | 2.83 | 0.000612 | -0.00817 | 2.58 | 0.000506 | 0 | 2.83 | 0.000612 | -0.00817 |  | CFL | AllSpc | 2580 | 0.506 | 2580 | 0.506 | 1.1 | 1.21 | -0.0031667 | 2580 | 0.506 | 2580 | 0.506 | 1.1 | 1.21 | -0.00317
CFLAllSpcPGEOfLNewCZ11 | Com-Iltg-dWatt-CFL_OSspc | PGE | OfL | New | CZ11 | 2.58 | 0.000506 | 0 | 2.89 | 0.000634 | -0.00894 | 2.58 | 0.000506 | 0 | 2.89 | 0.000634 | -0.00894 |  | CFL | AllSpc | 2580 | 0.506 | 2580 | 0.506 | 1.12 | 1.25 | -0.0034651 | 2580 | 0.506 | 2580 | 0.506 | 1.12 | 1.25 | -0.00347
CFLAllSpcPGEOfLNewCZ12 | Com-Iltg-dWatt-CFL_OSspc | PGE | OfL | New | CZ12 | 2.58 | 0.000506 | 0 | 2.87 | 0.000631 | -0.0101 | 2.58 | 0.000506 | 0 | 2.87 | 0.000631 | -0.0101 |  | CFL | AllSpc | 2580 | 0.506 | 2580 | 0.506 | 1.11 | 1.25 | -0.0039147 | 2580 | 0.506 | 2580 | 0.506 | 1.11 | 1.25 | -0.00391
CFLAllSpcPGEOfLNewCZ13 | Com-Iltg-dWatt-CFL_OSspc | PGE | OfL | New | CZ13 | 2.58 | 0.000506 | 0 | 2.9 | 0.000633 | -0.00876 | 2.58 | 0.000506 | 0 | 2.9 | 0.000633 | -0.00876 |  | CFL | AllSpc | 2580 | 0.506 | 2580 | 0.506 | 1.12 | 1.25 | -0.0033953 | 2580 | 0.506 | 2580 | 0.506 | 1.12 | 1.25 | -0.0034
CFLAllSpcPGEOfLNewCZ16 | Com-Iltg-dWatt-CFL_OSspc | PGE | OfL | New | CZ16 | 2.58 | 0.000506 | 0 | 2.76 | 0.000621 | -0.0219 | 2.58 | 0.000506 | 0 | 2.76 | 0.000621 | -0.0219 |  | CFL | AllSpc | 2580 | 0.506 | 2580 | 0.506 | 1.07 | 1.23 | -0.0084884 | 2580 | 0.506 | 2580 | 0.506 | 1.07 | 1.23 | -0.00849
CFLAllSpcPGEOfLNewIOU | Com-Iltg-dWatt-CFL_OSspc | PGE | OfL | New | IOU | 2.58 | 0.000506 | 0 | 2.8595 | 0.00062833 | -0.0099187 | 2.58 | 0.000506 | 0 | 2.8595 | 0.00062833 | -0.0099187 |  | CFL | AllSpc | 2580 | 0.506 | 2580 | 0.506 | 1.11 | 1.24 | -0.0038444 | 2580 | 0.506 | 2580 | 0.506 | 1.11 | 1.24 | -0.00384
CFLAllSpcPGEOfSExCZ01 | Com-Iltg-dWatt-CFL_OSspc | PGE | OfS | Ex | CZ01 | 2.4405 | 0.0005021 | 0 | 2.4505 | 0.00059605 | -0.0153 | 2.4405 | 0.0005021 | 0 | 2.4505 | 0.00059605 | -0.0153 |  | CFL | AllSpc | 2440 | 0.502 | 2440 | 0.502 | 1 | 1.19 | -0.0062693 | 2440 | 0.502 | 2440 | 0.502 | 1 | 1.19 | -0.00627
CFLAllSpcPGEOfSExCZ02 | Com-Iltg-dWatt-CFL_OSspc | PGE | OfS | Ex | CZ02 | 2.4406 | 0.00050211 | 0 | 2.5606 | 0.00061311 | -0.0099011 | 2.4406 | 0.00050211 | 0 | 2.5606 | 0.00061311 | -0.0099011 |  | CFL | AllSpc | 2440 | 0.502 | 2440 | 0.502 | 1.05 | 1.22 | -0.0040569 | 2440 | 0.502 | 2440 | 0.502 | 1.05 | 1.22 | -0.00406
CFLAllSpcPGEOfSExCZ03 | Com-Iltg-dWatt-CFL_OSspc | PGE | OfS | Ex | CZ03 | 2.4406 | 0.00050211 | 0 | 2.56 | 0.00061306 | -0.0084311 | 2.4406 | 0.00050211 | 0 | 2.56 | 0.00061306 | -0.0084311 |  | CFL | AllSpc | 2440 | 0.502 | 2440 | 0.502 | 1.05 | 1.22 | -0.0034546 | 2440 | 0.502 | 2440 | 0.502 | 1.05 | 1.22 | -0.00345
CFLAllSpcPGEOfSExCZ04 | Com-Iltg-dWatt-CFL_OSspc | PGE | OfS | Ex | CZ04 | 2.4406 | 0.00050212 | 0 | 2.61 | 0.00061512 | -0.0067706 | 2.4406 | 0.00050212 | 0 | 2.61 | 0.00061512 | -0.0067706 |  | CFL | AllSpc | 2440 | 0.502 | 2440 | 0.502 | 1.07 | 1.23 | -0.0027742 | 2440 | 0.502 | 2440 | 0.502 | 1.07 | 1.23 | -0.00277
CFLAllSpcPGEOfSExCZ05 | Com-Iltg-dWatt-CFL_OSspc | PGE | OfS | Ex | CZ05 | 2.4406 | 0.00050212 | 0 | 2.57 | 0.00060106 | -0.0070406 | 2.4406 | 0.00050212 | 0 | 2.57 | 0.00060106 | -0.0070406 |  | CFL | AllSpc | 2440 | 0.502 | 2440 | 0.502 | 1.05 | 1.2 | -0.0028848 | 2440 | 0.502 | 2440 | 0.502 | 1.05 | 1.2 | -0.00288
CFLAllSpcPGEOfSExCZ11 | Com-Iltg-dWatt-CFL_OSspc | PGE | OfS | Ex | CZ11 | 2.4406 | 0.00050211 | 0 | 2.61 | 0.00061411 | -0.0104 | 2.4406 | 0.00050211 | 0 | 2.61 | 0.00061411 | -0.0104 |  | CFL | AllSpc | 2440 | 0.502 | 2440 | 0.502 | 1.07 | 1.22 | -0.0042613 | 2440 | 0.502 | 2440 | 0.502 | 1.07 | 1.22 | -0.00426
CFLAllSpcPGEOfSExCZ12 | Com-Iltg-dWatt-CFL_OSspc | PGE | OfS | Ex | CZ12 | 2.4406 | 0.00050212 | 0 | 2.5906 | 0.00061512 | -0.0101 | 2.4406 | 0.00050212 | 0 | 2.5906 | 0.00061512 | -0.0101 |  | CFL | AllSpc | 2440 | 0.502 | 2440 | 0.502 | 1.06 | 1.23 | -0.0041383 | 2440 | 0.502 | 2440 | 0.502 | 1.06 | 1.23 | -0.00414
CFLAllSpcPGEOfSExCZ13 | Com-Iltg-dWatt-CFL_OSspc | PGE | OfS | Ex | CZ13 | 2.4406 | 0.00050212 | 0 | 2.62 | 0.00060906 | -0.0094812 | 2.4406 | 0.00050212 | 0 | 2.62 | 0.00060906 | -0.0094812 |  | CFL | AllSpc | 2440 | 0.502 | 2440 | 0.502 | 1.07 | 1.21 | -0.0038848 | 2440 | 0.502 | 2440 | 0.502 | 1.07 | 1.21 | -0.00388
CFLAllSpcPGEOfSExCZ16 | Com-Iltg-dWatt-CFL_OSspc | PGE | OfS | Ex | CZ16 | 2.4405 | 0.0005021 | 0 | 2.4205 | 0.0006031 | -0.0189 | 2.4405 | 0.0005021 | 0 | 2.4205 | 0.0006031 | -0.0189 |  | CFL | AllSpc | 2440 | 0.502 | 2440 | 0.502 | 0.992 | 1.2 | -0.0077443 | 2440 | 0.502 | 2440 | 0.502 | 0.992 | 1.2 | -0.00774
CFLAllSpcPGEOfSExIOU | Com-Iltg-dWatt-CFL_OSspc | PGE | OfS | Ex | IOU | 2.4406 | 0.00050211 | 0 | 2.5889 | 0.00061264 | -0.0090819 | 2.4406 | 0.00050211 | 0 | 2.5889 | 0.00061264 | -0.0090819 |  | CFL | AllSpc | 2440 | 0.502 | 2440 | 0.502 | 1.06 | 1.22 | -0.0037212 | 2440 | 0.502 | 2440 | 0.502 | 1.06 | 1.22 | -0.00372
CFLAllSpcPGEOfSNewCZ01 | Com-Iltg-dWatt-CFL_OSspc | PGE | OfS | New | CZ01 | 2.45 | 0.000504 | 0 | 2.4 | 0.000592 | -0.0142 | 2.45 | 0.000504 | 0 | 2.4 | 0.000592 | -0.0142 |  | CFL | AllSpc | 2450 | 0.504 | 2450 | 0.504 | 0.98 | 1.17 | -0.0057959 | 2450 | 0.504 | 2450 | 0.504 | 0.98 | 1.17 | -0.0058
CFLAllSpcPGEOfSNewCZ02 | Com-Iltg-dWatt-CFL_OSspc | PGE | OfS | New | CZ02 | 2.45 | 0.000504 | 0 | 2.56 | 0.000626 | -0.00761 | 2.45 | 0.000504 | 0 | 2.56 | 0.000626 | -0.00761 |  | CFL | AllSpc | 2450 | 0.504 | 2450 | 0.504 | 1.04 | 1.24 | -0.0031061 | 2450 | 0.504 | 2450 | 0.504 | 1.04 | 1.24 | -0.00311
CFLAllSpcPGEOfSNewCZ03 | Com-Iltg-dWatt-CFL_OSspc | PGE | OfS | New | CZ03 | 2.45 | 0.000504 | 0 | 2.52 | 0.000611 | -0.0083 | 2.45 | 0.000504 | 0 | 2.52 | 0.000611 | -0.0083 |  | CFL | AllSpc | 2450 | 0.504 | 2450 | 0.504 | 1.03 | 1.21 | -0.0033878 | 2450 | 0.504 | 2450 | 0.504 | 1.03 | 1.21 | -0.00339
CFLAllSpcPGEOfSNewCZ04 | Com-Iltg-dWatt-CFL_OSspc | PGE | OfS | New | CZ04 | 2.45 | 0.000504 | 0 | 2.58 | 0.000623 | -0.00607 | 2.45 | 0.000504 | 0 | 2.58 | 0.000623 | -0.00607 |  | CFL | AllSpc | 2450 | 0.504 | 2450 | 0.504 | 1.05 | 1.24 | -0.0024776 | 2450 | 0.504 | 2450 | 0.504 | 1.05 | 1.24 | -0.00248
CFLAllSpcPGEOfSNewCZ05 | Com-Iltg-dWatt-CFL_OSspc | PGE | OfS | New | CZ05 | 2.45 | 0.000504 | 0 | 2.53 | 0.000601 | -0.00659 | 2.45 | 0.000504 | 0 | 2.53 | 0.000601 | -0.00659 |  | CFL | AllSpc | 2450 | 0.504 | 2450 | 0.504 | 1.03 | 1.19 | -0.0026898 | 2450 | 0.504 | 2450 | 0.504 | 1.03 | 1.19 | -0.00269
CFLAllSpcPGEOfSNewCZ11 | Com-Iltg-dWatt-CFL_OSspc | PGE | OfS | New | CZ11 | 2.45 | 0.000504 | 0 | 2.6 | 0.000632 | -0.00842 | 2.45 | 0.000504 | 0 | 2.6 | 0.000632 | -0.00842 |  | CFL | AllSpc | 2450 | 0.504 | 2450 | 0.504 | 1.06 | 1.25 | -0.0034367 | 2450 | 0.504 | 2450 | 0.504 | 1.06 | 1.25 | -0.00344
CFLAllSpcPGEOfSNewCZ12 | Com-Iltg-dWatt-CFL_OSspc | PGE | OfS | New | CZ12 | 2.45 | 0.000504 | 0 | 2.59 | 0.000629 | -0.00815 | 2.45 | 0.000504 | 0 | 2.59 | 0.000629 | -0.00815 |  | CFL | AllSpc | 2450 | 0.504 | 2450 | 0.504 | 1.06 | 1.25 | -0.0033265 | 2450 | 0.504 | 2450 | 0.504 | 1.06 | 1.25 | -0.00333
CFLAllSpcPGEOfSNewCZ13 | Com-Iltg-dWatt-CFL_OSspc | PGE | OfS | New | CZ13 | 2.45 | 0.000504 | 0 | 2.61 | 0.000625 | -0.00776 | 2.45 | 0.000504 | 0 | 2.61 | 0.000625 | -0.00776 |  | CFL | AllSpc | 2450 | 0.504 | 2450 | 0.504 | 1.07 | 1.24 | -0.0031673 | 2450 | 0.504 | 2450 | 0.504 | 1.07 | 1.24 | -0.00317
CFLAllSpcPGEOfSNewCZ16 | Com-Iltg-dWatt-CFL_OSspc | PGE | OfS | New | CZ16 | 2.45 | 0.000504 | 0 | 2.43 | 0.000609 | -0.0176 | 2.45 | 0.000504 | 0 | 2.43 | 0.000609 | -0.0176 |  | CFL | AllSpc | 2450 | 0.504 | 2450 | 0.504 | 0.992 | 1.21 | -0.0071837 | 2450 | 0.504 | 2450 | 0.504 | 0.992 | 1.21 | -0.00718
CFLAllSpcPGEOfSNewIOU | Com-Iltg-dWatt-CFL_OSspc | PGE | OfS | New | IOU | 2.45 | 0.000504 | 0 | 2.5708 | 0.00062189 | -0.0078388 | 2.45 | 0.000504 | 0 | 2.5708 | 0.00062189 | -0.0078388 |  | CFL | AllSpc | 2450 | 0.504 | 2450 | 0.504 | 1.05 | 1.23 | -0.0031995 | 2450 | 0.504 | 2450 | 0.504 | 1.05 | 1.23 | -0.0032
CFLAllSpcPGERFFExCZ01 | Com-Iltg-dWatt-CFL_OSspc | PGE | RFF | Ex | CZ01 | 4.31 | 0.000687 | 0 | 4.2 | 0.00078 | -0.0509 | 4.31 | 0.000687 | 0 | 4.2 | 0.00078 | -0.0509 |  | CFL | AllSpc | 4310 | 0.687 | 4310 | 0.687 | 0.974 | 1.14 | -0.01181 | 4310 | 0.687 | 4310 | 0.687 | 0.974 | 1.14 | -0.0118
CFLAllSpcPGERFFExCZ02 | Com-Iltg-dWatt-CFL_OSspc | PGE | RFF | Ex | CZ02 | 4.31 | 0.000687 | 0 | 4.45 | 0.000797 | -0.033 | 4.31 | 0.000687 | 0 | 4.45 | 0.000797 | -0.033 |  | CFL | AllSpc | 4310 | 0.687 | 4310 | 0.687 | 1.03 | 1.16 | -0.0076566 | 4310 | 0.687 | 4310 | 0.687 | 1.03 | 1.16 | -0.00766
CFLAllSpcPGERFFExCZ03 | Com-Iltg-dWatt-CFL_OSspc | PGE | RFF | Ex | CZ03 | 4.31 | 0.000687 | 0 | 4.41 | 0.000793 | -0.035 | 4.31 | 0.000687 | 0 | 4.41 | 0.000793 | -0.035 |  | CFL | AllSpc | 4310 | 0.687 | 4310 | 0.687 | 1.02 | 1.15 | -0.0081206 | 4310 | 0.687 | 4310 | 0.687 | 1.02 | 1.15 | -0.00812
CFLAllSpcPGERFFExCZ04 | Com-Iltg-dWatt-CFL_OSspc | PGE | RFF | Ex | CZ04 | 4.31 | 0.000687 | 0 | 4.52 | 0.000797 | -0.0278 | 4.31 | 0.000687 | 0 | 4.52 | 0.000797 | -0.0278 |  | CFL | AllSpc | 4310 | 0.687 | 4310 | 0.687 | 1.05 | 1.16 | -0.0064501 | 4310 | 0.687 | 4310 | 0.687 | 1.05 | 1.16 | -0.00645
CFLAllSpcPGERFFExCZ05 | Com-Iltg-dWatt-CFL_OSspc | PGE | RFF | Ex | CZ05 | 4.31 | 0.000687 | 0 | 4.38 | 0.000784 | -0.0353 | 4.31 | 0.000687 | 0 | 4.38 | 0.000784 | -0.0353 |  | CFL | AllSpc | 4310 | 0.687 | 4310 | 0.687 | 1.02 | 1.14 | -0.0081903 | 4310 | 0.687 | 4310 | 0.687 | 1.02 | 1.14 | -0.00819
CFLAllSpcPGERFFExCZ11 | Com-Iltg-dWatt-CFL_OSspc | PGE | RFF | Ex | CZ11 | 4.31 | 0.000687 | 0 | 4.54 | 0.000812 | -0.0272 | 4.31 | 0.000687 | 0 | 4.54 | 0.000812 | -0.0272 |  | CFL | AllSpc | 4310 | 0.687 | 4310 | 0.687 | 1.05 | 1.18 | -0.0063109 | 4310 | 0.687 | 4310 | 0.687 | 1.05 | 1.18 | -0.00631
CFLAllSpcPGERFFExCZ12 | Com-Iltg-dWatt-CFL_OSspc | PGE | RFF | Ex | CZ12 | 4.31 | 0.000687 | 0 | 4.52 | 0.000804 | -0.0284 | 4.31 | 0.000687 | 0 | 4.52 | 0.000804 | -0.0284 |  | CFL | AllSpc | 4310 | 0.687 | 4310 | 0.687 | 1.05 | 1.17 | -0.0065893 | 4310 | 0.687 | 4310 | 0.687 | 1.05 | 1.17 | -0.00659
CFLAllSpcPGERFFExCZ13 | Com-Iltg-dWatt-CFL_OSspc | PGE | RFF | Ex | CZ13 | 4.31 | 0.000687 | 0 | 4.56 | 0.000801 | -0.026 | 4.31 | 0.000687 | 0 | 4.56 | 0.000801 | -0.026 |  | CFL | AllSpc | 4310 | 0.687 | 4310 | 0.687 | 1.06 | 1.17 | -0.0060325 | 4310 | 0.687 | 4310 | 0.687 | 1.06 | 1.17 | -0.00603
CFLAllSpcPGERFFExCZ16 | Com-Iltg-dWatt-CFL_OSspc | PGE | RFF | Ex | CZ16 | 4.31 | 0.000687 | 0 | 4.23 | 0.00079 | -0.0496 | 4.31 | 0.000687 | 0 | 4.23 | 0.00079 | -0.0496 |  | CFL | AllSpc | 4310 | 0.687 | 4310 | 0.687 | 0.981 | 1.15 | -0.011508 | 4310 | 0.687 | 4310 | 0.687 | 0.981 | 1.15 | -0.0115
CFLAllSpcPGERFFExIOU | Com-Iltg-dWatt-CFL_OSspc | PGE | RFF | Ex | IOU | 4.31 | 0.000687 | 0 | 4.4753 | 0.00079804 | -0.03108 | 4.31 | 0.000687 | 0 | 4.4753 | 0.00079804 | -0.03108 |  | CFL | AllSpc | 4310 | 0.687 | 4310 | 0.687 | 1.04 | 1.16 | -0.0072112 | 4310 | 0.687 | 4310 | 0.687 | 1.04 | 1.16 | -0.00721
CFLAllSpcPGERFFNewCZ01 | Com-Iltg-dWatt-CFL_OSspc | PGE | RFF | New | CZ01 | 4.31 | 0.000687 | 0 | 4.05 | 0.000747 | -0.0534 | 4.31 | 0.000687 | 0 | 4.05 | 0.000747 | -0.0534 |  | CFL | AllSpc | 4310 | 0.687 | 4310 | 0.687 | 0.94 | 1.09 | -0.01239 | 4310 | 0.687 | 4310 | 0.687 | 0.94 | 1.09 | -0.0124
CFLAllSpcPGERFFNewCZ02 | Com-Iltg-dWatt-CFL_OSspc | PGE | RFF | New | CZ02 | 4.31 | 0.000687 | 0 | 4.35 | 0.000828 | -0.0392 | 4.31 | 0.000687 | 0 | 4.35 | 0.000828 | -0.0392 |  | CFL | AllSpc | 4310 | 0.687 | 4310 | 0.687 | 1.01 | 1.21 | -0.0090951 | 4310 | 0.687 | 4310 | 0.687 | 1.01 | 1.21 | -0.0091
CFLAllSpcPGERFFNewCZ03 | Com-Iltg-dWatt-CFL_OSspc | PGE | RFF | New | CZ03 | 4.31 | 0.000687 | 0 | 4.27 | 0.000804 | -0.0399 | 4.31 | 0.000687 | 0 | 4.27 | 0.000804 | -0.0399 |  | CFL | AllSpc | 4310 | 0.687 | 4310 | 0.687 | 0.991 | 1.17 | -0.0092575 | 4310 | 0.687 | 4310 | 0.687 | 0.991 | 1.17 | -0.00926
CFLAllSpcPGERFFNewCZ04 | Com-Iltg-dWatt-CFL_OSspc | PGE | RFF | New | CZ04 | 4.31 | 0.000687 | 0 | 4.43 | 0.000819 | -0.033 | 4.31 | 0.000687 | 0 | 4.43 | 0.000819 | -0.033 |  | CFL | AllSpc | 4310 | 0.687 | 4310 | 0.687 | 1.03 | 1.19 | -0.0076566 | 4310 | 0.687 | 4310 | 0.687 | 1.03 | 1.19 | -0.00766
CFLAllSpcPGERFFNewCZ05 | Com-Iltg-dWatt-CFL_OSspc | PGE | RFF | New | CZ05 | 4.31 | 0.000687 | 0 | 4.26 | 0.000792 | -0.0353 | 4.31 | 0.000687 | 0 | 4.26 | 0.000792 | -0.0353 |  | CFL | AllSpc | 4310 | 0.687 | 4310 | 0.687 | 0.988 | 1.15 | -0.0081903 | 4310 | 0.687 | 4310 | 0.687 | 0.988 | 1.15 | -0.00819
CFLAllSpcPGERFFNewCZ11 | Com-Iltg-dWatt-CFL_OSspc | PGE | RFF | New | CZ11 | 4.31 | 0.000687 | 0 | 4.53 | 0.000847 | -0.0297 | 4.31 | 0.000687 | 0 | 4.53 | 0.000847 | -0.0297 |  | CFL | AllSpc | 4310 | 0.687 | 4310 | 0.687 | 1.05 | 1.23 | -0.006891 | 4310 | 0.687 | 4310 | 0.687 | 1.05 | 1.23 | -0.00689
CFLAllSpcPGERFFNewCZ12 | Com-Iltg-dWatt-CFL_OSspc | PGE | RFF | New | CZ12 | 4.31 | 0.000687 | 0 | 4.48 | 0.000838 | -0.035 | 4.31 | 0.000687 | 0 | 4.48 | 0.000838 | -0.035 |  | CFL | AllSpc | 4310 | 0.687 | 4310 | 0.687 | 1.04 | 1.22 | -0.0081206 | 4310 | 0.687 | 4310 | 0.687 | 1.04 | 1.22 | -0.00812
CFLAllSpcPGERFFNewCZ13 | Com-Iltg-dWatt-CFL_OSspc | PGE | RFF | New | CZ13 | 4.31 | 0.000687 | 0 | 4.54 | 0.000837 | -0.031 | 4.31 | 0.000687 | 0 | 4.54 | 0.000837 | -0.031 |  | CFL | AllSpc | 4310 | 0.687 | 4310 | 0.687 | 1.05 | 1.22 | -0.0071926 | 4310 | 0.687 | 4310 | 0.687 | 1.05 | 1.22 | -0.00719
CFLAllSpcPGERFFNewCZ16 | Com-Iltg-dWatt-CFL_OSspc | PGE | RFF | New | CZ16 | 4.31 | 0.000687 | 0 | 4.2 | 0.000809 | -0.0552 | 4.31 | 0.000687 | 0 | 4.2 | 0.000809 | -0.0552 |  | CFL | AllSpc | 4310 | 0.687 | 4310 | 0.687 | 0.974 | 1.18 | -0.012807 | 4310 | 0.687 | 4310 | 0.687 | 0.974 | 1.18 | -0.0128
CFLAllSpcPGERFFNewIOU | Com-Iltg-dWatt-CFL_OSspc | PGE | RFF | New | IOU | 4.31 | 0.000687 | 0 | 4.3987 | 0.00082223 | -0.03603 | 4.31 | 0.000687 | 0 | 4.3987 | 0.00082223 | -0.03603 |  | CFL | AllSpc | 4310 | 0.687 | 4310 | 0.687 | 1.02 | 1.2 | -0.0083597 | 4310 | 0.687 | 4310 | 0.687 | 1.02 | 1.2 | -0.00836
CFLAllSpcPGERSDExCZ01 | Com-Iltg-dWatt-CFL_OSspc | PGE | RSD | Ex | CZ01 | 4.33 | 0.000677 | 0 | 4.16 | 0.000794 | -0.0541 | 4.33 | 0.000677 | 0 | 4.16 | 0.000794 | -0.0541 |  | CFL | AllSpc | 4330 | 0.677 | 4330 | 0.677 | 0.961 | 1.17 | -0.012494 | 4330 | 0.677 | 4330 | 0.677 | 0.961 | 1.17 | -0.0125
CFLAllSpcPGERSDExCZ02 | Com-Iltg-dWatt-CFL_OSspc | PGE | RSD | Ex | CZ02 | 4.33 | 0.000677 | 0 | 4.49 | 0.000794 | -0.0317 | 4.33 | 0.000677 | 0 | 4.49 | 0.000794 | -0.0317 |  | CFL | AllSpc | 4330 | 0.677 | 4330 | 0.677 | 1.04 | 1.17 | -0.007321 | 4330 | 0.677 | 4330 | 0.677 | 1.04 | 1.17 | -0.00732
CFLAllSpcPGERSDExCZ03 | Com-Iltg-dWatt-CFL_OSspc | PGE | RSD | Ex | CZ03 | 4.33 | 0.000677 | 0 | 4.43 | 0.000795 | -0.0355 | 4.33 | 0.000677 | 0 | 4.43 | 0.000795 | -0.0355 |  | CFL | AllSpc | 4330 | 0.677 | 4330 | 0.677 | 1.02 | 1.17 | -0.0081986 | 4330 | 0.677 | 4330 | 0.677 | 1.02 | 1.17 | -0.0082
CFLAllSpcPGERSDExCZ04 | Com-Iltg-dWatt-CFL_OSspc | PGE | RSD | Ex | CZ04 | 4.33 | 0.000677 | 0 | 4.57 | 0.000797 | -0.0264 | 4.33 | 0.000677 | 0 | 4.57 | 0.000797 | -0.0264 |  | CFL | AllSpc | 4330 | 0.677 | 4330 | 0.677 | 1.06 | 1.18 | -0.006097 | 4330 | 0.677 | 4330 | 0.677 | 1.06 | 1.18 | -0.0061
CFLAllSpcPGERSDExCZ05 | Com-Iltg-dWatt-CFL_OSspc | PGE | RSD | Ex | CZ05 | 4.33 | 0.000677 | 0 | 4.44 | 0.000789 | -0.0343 | 4.33 | 0.000677 | 0 | 4.44 | 0.000789 | -0.0343 |  | CFL | AllSpc | 4330 | 0.677 | 4330 | 0.677 | 1.03 | 1.17 | -0.0079215 | 4330 | 0.677 | 4330 | 0.677 | 1.03 | 1.17 | -0.00792
CFLAllSpcPGERSDExCZ11 | Com-Iltg-dWatt-CFL_OSspc | PGE | RSD | Ex | CZ11 | 4.33 | 0.000677 | 0 | 4.59 | 0.000802 | -0.0275 | 4.33 | 0.000677 | 0 | 4.59 | 0.000802 | -0.0275 |  | CFL | AllSpc | 4330 | 0.677 | 4330 | 0.677 | 1.06 | 1.18 | -0.006351 | 4330 | 0.677 | 4330 | 0.677 | 1.06 | 1.18 | -0.00635
CFLAllSpcPGERSDExCZ12 | Com-Iltg-dWatt-CFL_OSspc | PGE | RSD | Ex | CZ12 | 4.33 | 0.000677 | 0 | 4.54 | 0.000776 | -0.0284 | 4.33 | 0.000677 | 0 | 4.54 | 0.000776 | -0.0284 |  | CFL | AllSpc | 4330 | 0.677 | 4330 | 0.677 | 1.05 | 1.15 | -0.0065589 | 4330 | 0.677 | 4330 | 0.677 | 1.05 | 1.15 | -0.00656
CFLAllSpcPGERSDExCZ13 | Com-Iltg-dWatt-CFL_OSspc | PGE | RSD | Ex | CZ13 | 4.33 | 0.000677 | 0 | 4.61 | 0.000799 | -0.026 | 4.33 | 0.000677 | 0 | 4.61 | 0.000799 | -0.026 |  | CFL | AllSpc | 4330 | 0.677 | 4330 | 0.677 | 1.06 | 1.18 | -0.0060046 | 4330 | 0.677 | 4330 | 0.677 | 1.06 | 1.18 | -0.006
CFLAllSpcPGERSDExCZ16 | Com-Iltg-dWatt-CFL_OSspc | PGE | RSD | Ex | CZ16 | 4.33 | 0.000677 | 0 | 4.22 | 0.000776 | -0.0485 | 4.33 | 0.000677 | 0 | 4.22 | 0.000776 | -0.0485 |  | CFL | AllSpc | 4330 | 0.677 | 4330 | 0.677 | 0.975 | 1.15 | -0.011201 | 4330 | 0.677 | 4330 | 0.677 | 0.975 | 1.15 | -0.0112
CFLAllSpcPGERSDExIOU | Com-Iltg-dWatt-CFL_OSspc | PGE | RSD | Ex | IOU | 4.33 | 0.000677 | 0 | 4.507 | 0.00079178 | -0.03098 | 4.33 | 0.000677 | 0 | 4.507 | 0.00079178 | -0.03098 |  | CFL | AllSpc | 4330 | 0.677 | 4330 | 0.677 | 1.04 | 1.17 | -0.0071548 | 4330 | 0.677 | 4330 | 0.677 | 1.04 | 1.17 | -0.00715
CFLAllSpcPGERSDNewCZ01 | Com-Iltg-dWatt-CFL_OSspc | PGE | RSD | New | CZ01 | 4.33 | 0.000677 | 0 | 4.14 | 0.00077 | -0.0131 | 4.33 | 0.000677 | 0 | 4.14 | 0.00077 | -0.0131 |  | CFL | AllSpc | 4330 | 0.677 | 4330 | 0.677 | 0.956 | 1.14 | -0.0030254 | 4330 | 0.677 | 4330 | 0.677 | 0.956 | 1.14 | -0.00303
CFLAllSpcPGERSDNewCZ02 | Com-Iltg-dWatt-CFL_OSspc | PGE | RSD | New | CZ02 | 4.33 | 0.000677 | 0 | 4.43 | 0.000824 | -0.0352 | 4.33 | 0.000677 | 0 | 4.43 | 0.000824 | -0.0352 |  | CFL | AllSpc | 4330 | 0.677 | 4330 | 0.677 | 1.02 | 1.22 | -0.0081293 | 4330 | 0.677 | 4330 | 0.677 | 1.02 | 1.22 | -0.00813
CFLAllSpcPGERSDNewCZ03 | Com-Iltg-dWatt-CFL_OSspc | PGE | RSD | New | CZ03 | 4.33 | 0.000677 | 0 | 4.31 | 0.000786 | -0.0442 | 4.33 | 0.000677 | 0 | 4.31 | 0.000786 | -0.0442 |  | CFL | AllSpc | 4330 | 0.677 | 4330 | 0.677 | 0.995 | 1.16 | -0.010208 | 4330 | 0.677 | 4330 | 0.677 | 0.995 | 1.16 | -0.0102
CFLAllSpcPGERSDNewCZ04 | Com-Iltg-dWatt-CFL_OSspc | PGE | RSD | New | CZ04 | 4.33 | 0.000677 | 0 | 4.52 | 0.000825 | -0.0295 | 4.33 | 0.000677 | 0 | 4.52 | 0.000825 | -0.0295 |  | CFL | AllSpc | 4330 | 0.677 | 4330 | 0.677 | 1.04 | 1.22 | -0.0068129 | 4330 | 0.677 | 4330 | 0.677 | 1.04 | 1.22 | -0.00681
CFLAllSpcPGERSDNewCZ05 | Com-Iltg-dWatt-CFL_OSspc | PGE | RSD | New | CZ05 | 4.33 | 0.000677 | 0 | 4.34 | 0.000794 | -0.0378 | 4.33 | 0.000677 | 0 | 4.34 | 0.000794 | -0.0378 |  | CFL | AllSpc | 4330 | 0.677 | 4330 | 0.677 | 1 | 1.17 | -0.0087298 | 4330 | 0.677 | 4330 | 0.677 | 1 | 1.17 | -0.00873
CFLAllSpcPGERSDNewCZ11 | Com-Iltg-dWatt-CFL_OSspc | PGE | RSD | New | CZ11 | 4.33 | 0.000677 | 0 | 4.57 | 0.000842 | -0.0304 | 4.33 | 0.000677 | 0 | 4.57 | 0.000842 | -0.0304 |  | CFL | AllSpc | 4330 | 0.677 | 4330 | 0.677 | 1.06 | 1.24 | -0.0070208 | 4330 | 0.677 | 4330 | 0.677 | 1.06 | 1.24 | -0.00702
CFLAllSpcPGERSDNewCZ12 | Com-Iltg-dWatt-CFL_OSspc | PGE | RSD | New | CZ12 | 4.33 | 0.000677 | 0 | 4.51 | 0.000812 | -0.0306 | 4.33 | 0.000677 | 0 | 4.51 | 0.000812 | -0.0306 |  | CFL | AllSpc | 4330 | 0.677 | 4330 | 0.677 | 1.04 | 1.2 | -0.007067 | 4330 | 0.677 | 4330 | 0.677 | 1.04 | 1.2 | -0.00707
CFLAllSpcPGERSDNewCZ13 | Com-Iltg-dWatt-CFL_OSspc | PGE | RSD | New | CZ13 | 4.33 | 0.000677 | 0 | 4.59 | 0.00084 | -0.0291 | 4.33 | 0.000677 | 0 | 4.59 | 0.00084 | -0.0291 |  | CFL | AllSpc | 4330 | 0.677 | 4330 | 0.677 | 1.06 | 1.24 | -0.0067206 | 4330 | 0.677 | 4330 | 0.677 | 1.06 | 1.24 | -0.00672
CFLAllSpcPGERSDNewCZ16 | Com-Iltg-dWatt-CFL_OSspc | PGE | RSD | New | CZ16 | 4.33 | 0.000677 | 0 | 4.2 | 0.000799 | -0.0406 | 4.33 | 0.000677 | 0 | 4.2 | 0.000799 | -0.0406 |  | CFL | AllSpc | 4330 | 0.677 | 4330 | 0.677 | 0.97 | 1.18 | -0.0093764 | 4330 | 0.677 | 4330 | 0.677 | 0.97 | 1.18 | -0.00938
CFLAllSpcPGERSDNewIOU | Com-Iltg-dWatt-CFL_OSspc | PGE | RSD | New | IOU | 4.33 | 0.000677 | 0 | 4.4479 | 0.00081149 | -0.034884 | 4.33 | 0.000677 | 0 | 4.4479 | 0.00081149 | -0.034884 |  | CFL | AllSpc | 4330 | 0.677 | 4330 | 0.677 | 1.03 | 1.2 | -0.0080563 | 4330 | 0.677 | 4330 | 0.677 | 1.03 | 1.2 | -0.00806
CFLAllSpcPGERt3ExCZ01 | Com-Iltg-dWatt-CFL_OSspc | PGE | Rt3 | Ex | CZ01 | 3.69 | 0.00062095 | 0 | 3.54 | 0.00076991 | -0.0542 | 3.69 | 0.00062095 | 0 | 3.54 | 0.00076991 | -0.0542 |  | CFL | AllSpc | 3690 | 0.621 | 3690 | 0.621 | 0.959 | 1.24 | -0.014688 | 3690 | 0.621 | 3690 | 0.621 | 0.959 | 1.24 | -0.0147
CFLAllSpcPGERt3ExCZ02 | Com-Iltg-dWatt-CFL_OSspc | PGE | Rt3 | Ex | CZ02 | 3.69 | 0.00062095 | 0 | 3.88 | 0.0007559 | -0.0275 | 3.69 | 0.00062095 | 0 | 3.88 | 0.0007559 | -0.0275 |  | CFL | AllSpc | 3690 | 0.621 | 3690 | 0.621 | 1.05 | 1.22 | -0.0074526 | 3690 | 0.621 | 3690 | 0.621 | 1.05 | 1.22 | -0.00745
CFLAllSpcPGERt3ExCZ03 | Com-Iltg-dWatt-CFL_OSspc | PGE | Rt3 | Ex | CZ03 | 3.69 | 0.00062096 | 0 | 3.9 | 0.00075991 | -0.0264 | 3.69 | 0.00062096 | 0 | 3.9 | 0.00075991 | -0.0264 |  | CFL | AllSpc | 3690 | 0.621 | 3690 | 0.621 | 1.06 | 1.22 | -0.0071545 | 3690 | 0.621 | 3690 | 0.621 | 1.06 | 1.22 | -0.00715
CFLAllSpcPGERt3ExCZ04 | Com-Iltg-dWatt-CFL_OSspc | PGE | Rt3 | Ex | CZ04 | 3.69 | 0.00062095 | 0 | 3.97 | 0.00075895 | -0.0182 | 3.69 | 0.00062095 | 0 | 3.97 | 0.00075895 | -0.0182 |  | CFL | AllSpc | 3690 | 0.621 | 3690 | 0.621 | 1.08 | 1.22 | -0.0049322 | 3690 | 0.621 | 3690 | 0.621 | 1.08 | 1.22 | -0.00493
CFLAllSpcPGERt3ExCZ05 | Com-Iltg-dWatt-CFL_OSspc | PGE | Rt3 | Ex | CZ05 | 3.69 | 0.00062095 | 0 | 3.9 | 0.0007519 | -0.0218 | 3.69 | 0.00062095 | 0 | 3.9 | 0.0007519 | -0.0218 |  | CFL | AllSpc | 3690 | 0.621 | 3690 | 0.621 | 1.06 | 1.21 | -0.0059079 | 3690 | 0.621 | 3690 | 0.621 | 1.06 | 1.21 | -0.00591
CFLAllSpcPGERt3ExCZ11 | Com-Iltg-dWatt-CFL_OSspc | PGE | Rt3 | Ex | CZ11 | 3.69 | 0.00062093 | 0 | 3.8993 | 0.00076186 | -0.026193 | 3.69 | 0.00062093 | 0 | 3.8993 | 0.00076186 | -0.026193 |  | CFL | AllSpc | 3690 | 0.621 | 3690 | 0.621 | 1.06 | 1.23 | -0.0070984 | 3690 | 0.621 | 3690 | 0.621 | 1.06 | 1.23 | -0.0071
CFLAllSpcPGERt3ExCZ12 | Com-Iltg-dWatt-CFL_OSspc | PGE | Rt3 | Ex | CZ12 | 3.69 | 0.00062094 | 0 | 3.9 | 0.00076588 | -0.025494 | 3.69 | 0.00062094 | 0 | 3.9 | 0.00076588 | -0.025494 |  | CFL | AllSpc | 3690 | 0.621 | 3690 | 0.621 | 1.06 | 1.23 | -0.0069089 | 3690 | 0.621 | 3690 | 0.621 | 1.06 | 1.23 | -0.00691
CFLAllSpcPGERt3ExCZ13 | Com-Iltg-dWatt-CFL_OSspc | PGE | Rt3 | Ex | CZ13 | 3.69 | 0.00062093 | 0 | 3.92 | 0.00075986 | -0.024093 | 3.69 | 0.00062093 | 0 | 3.92 | 0.00075986 | -0.024093 |  | CFL | AllSpc | 3690 | 0.621 | 3690 | 0.621 | 1.06 | 1.22 | -0.0065293 | 3690 | 0.621 | 3690 | 0.621 | 1.06 | 1.22 | -0.00653
CFLAllSpcPGERt3ExCZ16 | Com-Iltg-dWatt-CFL_OSspc | PGE | Rt3 | Ex | CZ16 | 3.69 | 0.00062094 | 0 | 3.59 | 0.00074294 | -0.0505 | 3.69 | 0.00062094 | 0 | 3.59 | 0.00074294 | -0.0505 |  | CFL | AllSpc | 3690 | 0.621 | 3690 | 0.621 | 0.973 | 1.2 | -0.013686 | 3690 | 0.621 | 3690 | 0.621 | 0.973 | 1.2 | -0.0137
CFLAllSpcPGERt3ExIOU | Com-Iltg-dWatt-CFL_OSspc | PGE | Rt3 | Ex | IOU | 3.69 | 0.00062095 | 0 | 3.9066 | 0.00076084 | -0.025026 | 3.69 | 0.00062095 | 0 | 3.9066 | 0.00076084 | -0.025026 |  | CFL | AllSpc | 3690 | 0.621 | 3690 | 0.621 | 1.06 | 1.23 | -0.006782 | 3690 | 0.621 | 3690 | 0.621 | 1.06 | 1.23 | -0.00678
CFLAllSpcPGERt3NewCZ01 | Com-Iltg-dWatt-CFL_OSspc | PGE | Rt3 | New | CZ01 | 3.69 | 0.00062 | 0 | 3.47 | 0.000756 | -0.0597 | 3.69 | 0.00062 | 0 | 3.47 | 0.000756 | -0.0597 |  | CFL | AllSpc | 3690 | 0.62 | 3690 | 0.62 | 0.94 | 1.22 | -0.016179 | 3690 | 0.62 | 3690 | 0.62 | 0.94 | 1.22 | -0.0162
CFLAllSpcPGERt3NewCZ02 | Com-Iltg-dWatt-CFL_OSspc | PGE | Rt3 | New | CZ02 | 3.69 | 0.00062 | 0 | 3.77 | 0.000737 | -0.0322 | 3.69 | 0.00062 | 0 | 3.77 | 0.000737 | -0.0322 |  | CFL | AllSpc | 3690 | 0.62 | 3690 | 0.62 | 1.02 | 1.19 | -0.0087263 | 3690 | 0.62 | 3690 | 0.62 | 1.02 | 1.19 | -0.00873
CFLAllSpcPGERt3NewCZ03 | Com-Iltg-dWatt-CFL_OSspc | PGE | Rt3 | New | CZ03 | 3.69 | 0.00062 | 0 | 3.74 | 0.000742 | -0.0327 | 3.69 | 0.00062 | 0 | 3.74 | 0.000742 | -0.0327 |  | CFL | AllSpc | 3690 | 0.62 | 3690 | 0.62 | 1.01 | 1.2 | -0.0088618 | 3690 | 0.62 | 3690 | 0.62 | 1.01 | 1.2 | -0.00886
CFLAllSpcPGERt3NewCZ04 | Com-Iltg-dWatt-CFL_OSspc | PGE | Rt3 | New | CZ04 | 3.69 | 0.00062 | 0 | 3.85 | 0.000746 | -0.0234 | 3.69 | 0.00062 | 0 | 3.85 | 0.000746 | -0.0234 |  | CFL | AllSpc | 3690 | 0.62 | 3690 | 0.62 | 1.04 | 1.2 | -0.0063415 | 3690 | 0.62 | 3690 | 0.62 | 1.04 | 1.2 | -0.00634
CFLAllSpcPGERt3NewCZ05 | Com-Iltg-dWatt-CFL_OSspc | PGE | Rt3 | New | CZ05 | 3.69 | 0.00062 | 0 | 3.77 | 0.000738 | -0.0272 | 3.69 | 0.00062 | 0 | 3.77 | 0.000738 | -0.0272 |  | CFL | AllSpc | 3690 | 0.62 | 3690 | 0.62 | 1.02 | 1.19 | -0.0073713 | 3690 | 0.62 | 3690 | 0.62 | 1.02 | 1.19 | -0.00737
CFLAllSpcPGERt3NewCZ11 | Com-Iltg-dWatt-CFL_OSspc | PGE | Rt3 | New | CZ11 | 3.69 | 0.00062 | 0 | 3.87 | 0.000764 | -0.0277 | 3.69 | 0.00062 | 0 | 3.87 | 0.000764 | -0.0277 |  | CFL | AllSpc | 3690 | 0.62 | 3690 | 0.62 | 1.05 | 1.23 | -0.0075068 | 3690 | 0.62 | 3690 | 0.62 | 1.05 | 1.23 | -0.00751
CFLAllSpcPGERt3NewCZ12 | Com-Iltg-dWatt-CFL_OSspc | PGE | Rt3 | New | CZ12 | 3.69 | 0.00062 | 0 | 3.85 | 0.000761 | -0.0296 | 3.69 | 0.00062 | 0 | 3.85 | 0.000761 | -0.0296 |  | CFL | AllSpc | 3690 | 0.62 | 3690 | 0.62 | 1.04 | 1.23 | -0.0080217 | 3690 | 0.62 | 3690 | 0.62 | 1.04 | 1.23 | -0.00802
CFLAllSpcPGERt3NewCZ13 | Com-Iltg-dWatt-CFL_OSspc | PGE | Rt3 | New | CZ13 | 3.69 | 0.00062 | 0 | 3.88 | 0.000756 | -0.0267 | 3.69 | 0.00062 | 0 | 3.88 | 0.000756 | -0.0267 |  | CFL | AllSpc | 3690 | 0.62 | 3690 | 0.62 | 1.05 | 1.22 | -0.0072358 | 3690 | 0.62 | 3690 | 0.62 | 1.05 | 1.22 | -0.00724
CFLAllSpcPGERt3NewCZ16 | Com-Iltg-dWatt-CFL_OSspc | PGE | Rt3 | New | CZ16 | 3.69 | 0.00062 | 0 | 3.52 | 0.000682 | -0.0483 | 3.69 | 0.00062 | 0 | 3.52 | 0.000682 | -0.0483 |  | CFL | AllSpc | 3690 | 0.62 | 3690 | 0.62 | 0.954 | 1.1 | -0.013089 | 3690 | 0.62 | 3690 | 0.62 | 0.954 | 1.1 | -0.0131
CFLAllSpcPGERt3NewIOU | Com-Iltg-dWatt-CFL_OSspc | PGE | Rt3 | New | IOU | 3.69 | 0.00062 | 0 | 3.8172 | 0.00075114 | -0.029373 | 3.69 | 0.00062 | 0 | 3.8172 | 0.00075114 | -0.029373 |  | CFL | AllSpc | 3690 | 0.62 | 3690 | 0.62 | 1.03 | 1.21 | -0.0079602 | 3690 | 0.62 | 3690 | 0.62 | 1.03 | 1.21 | -0.00796
CFLAllSpcPGERtLExCZ01 | Com-Iltg-dWatt-CFL_OSspc | PGE | RtL | Ex | CZ01 | 4.32 | 0.00068095 | 0 | 4.1995 | 0.00082895 | -0.0583 | 4.32 | 0.00068095 | 0 | 4.1995 | 0.00082895 | -0.0583 |  | CFL | AllSpc | 4320 | 0.681 | 4320 | 0.681 | 0.972 | 1.22 | -0.013495 | 4320 | 0.681 | 4320 | 0.681 | 0.972 | 1.22 | -0.0135
CFLAllSpcPGERtLExCZ02 | Com-Iltg-dWatt-CFL_OSspc | PGE | RtL | Ex | CZ02 | 4.32 | 0.00068095 | 0 | 4.5395 | 0.00082695 | -0.0303 | 4.32 | 0.00068095 | 0 | 4.5395 | 0.00082695 | -0.0303 |  | CFL | AllSpc | 4320 | 0.681 | 4320 | 0.681 | 1.05 | 1.21 | -0.0070139 | 4320 | 0.681 | 4320 | 0.681 | 1.05 | 1.21 | -0.00701
CFLAllSpcPGERtLExCZ03 | Com-Iltg-dWatt-CFL_OSspc | PGE | RtL | Ex | CZ03 | 4.32 | 0.00068096 | 0 | 4.5696 | 0.00082295 | -0.0285 | 4.32 | 0.00068096 | 0 | 4.5696 | 0.00082295 | -0.0285 |  | CFL | AllSpc | 4320 | 0.681 | 4320 | 0.681 | 1.06 | 1.21 | -0.0065972 | 4320 | 0.681 | 4320 | 0.681 | 1.06 | 1.21 | -0.0066
CFLAllSpcPGERtLExCZ04 | Com-Iltg-dWatt-CFL_OSspc | PGE | RtL | Ex | CZ04 | 4.32 | 0.00068095 | 0 | 4.6395 | 0.00082795 | -0.0213 | 4.32 | 0.00068095 | 0 | 4.6395 | 0.00082795 | -0.0213 |  | CFL | AllSpc | 4320 | 0.681 | 4320 | 0.681 | 1.07 | 1.22 | -0.0049306 | 4320 | 0.681 | 4320 | 0.681 | 1.07 | 1.22 | -0.00493
CFLAllSpcPGERtLExCZ05 | Com-Iltg-dWatt-CFL_OSspc | PGE | RtL | Ex | CZ05 | 4.32 | 0.00068095 | 0 | 4.5495 | 0.00081295 | -0.028295 | 4.32 | 0.00068095 | 0 | 4.5495 | 0.00081295 | -0.028295 |  | CFL | AllSpc | 4320 | 0.681 | 4320 | 0.681 | 1.05 | 1.19 | -0.0065497 | 4320 | 0.681 | 4320 | 0.681 | 1.05 | 1.19 | -0.00655
CFLAllSpcPGERtLExCZ11 | Com-Iltg-dWatt-CFL_OSspc | PGE | RtL | Ex | CZ11 | 4.32 | 0.00068093 | 0 | 4.57 | 0.00083586 | -0.028893 | 4.32 | 0.00068093 | 0 | 4.57 | 0.00083586 | -0.028893 |  | CFL | AllSpc | 4320 | 0.681 | 4320 | 0.681 | 1.06 | 1.23 | -0.0066882 | 4320 | 0.681 | 4320 | 0.681 | 1.06 | 1.23 | -0.00669
CFLAllSpcPGERtLExCZ12 | Com-Iltg-dWatt-CFL_OSspc | PGE | RtL | Ex | CZ12 | 4.32 | 0.00068094 | 0 | 4.5794 | 0.00084294 | -0.026494 | 4.32 | 0.00068094 | 0 | 4.5794 | 0.00084294 | -0.026494 |  | CFL | AllSpc | 4320 | 0.681 | 4320 | 0.681 | 1.06 | 1.24 | -0.0061328 | 4320 | 0.681 | 4320 | 0.681 | 1.06 | 1.24 | -0.00613
CFLAllSpcPGERtLExCZ13 | Com-Iltg-dWatt-CFL_OSspc | PGE | RtL | Ex | CZ13 | 4.32 | 0.00068093 | 0 | 4.61 | 0.00083593 | -0.0255 | 4.32 | 0.00068093 | 0 | 4.61 | 0.00083593 | -0.0255 |  | CFL | AllSpc | 4320 | 0.681 | 4320 | 0.681 | 1.07 | 1.23 | -0.0059028 | 4320 | 0.681 | 4320 | 0.681 | 1.07 | 1.23 | -0.0059
CFLAllSpcPGERtLExCZ16 | Com-Iltg-dWatt-CFL_OSspc | PGE | RtL | Ex | CZ16 | 4.32 | 0.00068094 | 0 | 4.2094 | 0.00080194 | -0.057494 | 4.32 | 0.00068094 | 0 | 4.2094 | 0.00080194 | -0.057494 |  | CFL | AllSpc | 4320 | 0.681 | 4320 | 0.681 | 0.974 | 1.18 | -0.013309 | 4320 | 0.681 | 4320 | 0.681 | 0.974 | 1.18 | -0.0133
CFLAllSpcPGERtLExIOU | Com-Iltg-dWatt-CFL_OSspc | PGE | RtL | Ex | IOU | 4.32 | 0.00068094 | 0 | 4.5799 | 0.00083089 | -0.027136 | 4.32 | 0.00068094 | 0 | 4.5799 | 0.00083089 | -0.027136 |  | CFL | AllSpc | 4320 | 0.681 | 4320 | 0.681 | 1.06 | 1.22 | -0.0062816 | 4320 | 0.681 | 4320 | 0.681 | 1.06 | 1.22 | -0.00628
CFLAllSpcPGERtLNewCZ01 | Com-Iltg-dWatt-CFL_OSspc | PGE | RtL | New | CZ01 | 4.32 | 0.00068 | 0 | 4.16 | 0.000811 | -0.0648 | 4.32 | 0.00068 | 0 | 4.16 | 0.000811 | -0.0648 |  | CFL | AllSpc | 4320 | 0.68 | 4320 | 0.68 | 0.963 | 1.19 | -0.015 | 4320 | 0.68 | 4320 | 0.68 | 0.963 | 1.19 | -0.015
CFLAllSpcPGERtLNewCZ02 | Com-Iltg-dWatt-CFL_OSspc | PGE | RtL | New | CZ02 | 4.32 | 0.00068 | 0 | 4.49 | 0.000866 | -0.0344 | 4.32 | 0.00068 | 0 | 4.49 | 0.000866 | -0.0344 |  | CFL | AllSpc | 4320 | 0.68 | 4320 | 0.68 | 1.04 | 1.27 | -0.007963 | 4320 | 0.68 | 4320 | 0.68 | 1.04 | 1.27 | -0.00796
CFLAllSpcPGERtLNewCZ03 | Com-Iltg-dWatt-CFL_OSspc | PGE | RtL | New | CZ03 | 4.32 | 0.00068 | 0 | 4.43 | 0.000841 | -0.0322 | 4.32 | 0.00068 | 0 | 4.43 | 0.000841 | -0.0322 |  | CFL | AllSpc | 4320 | 0.68 | 4320 | 0.68 | 1.03 | 1.24 | -0.0074537 | 4320 | 0.68 | 4320 | 0.68 | 1.03 | 1.24 | -0.00745
CFLAllSpcPGERtLNewCZ04 | Com-Iltg-dWatt-CFL_OSspc | PGE | RtL | New | CZ04 | 4.32 | 0.00068 | 0 | 4.58 | 0.000856 | -0.0244 | 4.32 | 0.00068 | 0 | 4.58 | 0.000856 | -0.0244 |  | CFL | AllSpc | 4320 | 0.68 | 4320 | 0.68 | 1.06 | 1.26 | -0.0056481 | 4320 | 0.68 | 4320 | 0.68 | 1.06 | 1.26 | -0.00565
CFLAllSpcPGERtLNewCZ05 | Com-Iltg-dWatt-CFL_OSspc | PGE | RtL | New | CZ05 | 4.32 | 0.00068 | 0 | 4.44 | 0.000821 | -0.0335 | 4.32 | 0.00068 | 0 | 4.44 | 0.000821 | -0.0335 |  | CFL | AllSpc | 4320 | 0.68 | 4320 | 0.68 | 1.03 | 1.21 | -0.0077546 | 4320 | 0.68 | 4320 | 0.68 | 1.03 | 1.21 | -0.00775
CFLAllSpcPGERtLNewCZ11 | Com-Iltg-dWatt-CFL_OSspc | PGE | RtL | New | CZ11 | 4.32 | 0.00068 | 0 | 4.61 | 0.000869 | -0.0308 | 4.32 | 0.00068 | 0 | 4.61 | 0.000869 | -0.0308 |  | CFL | AllSpc | 4320 | 0.68 | 4320 | 0.68 | 1.07 | 1.28 | -0.0071296 | 4320 | 0.68 | 4320 | 0.68 | 1.07 | 1.28 | -0.00713
CFLAllSpcPGERtLNewCZ12 | Com-Iltg-dWatt-CFL_OSspc | PGE | RtL | New | CZ12 | 4.32 | 0.00068 | 0 | 4.59 | 0.000879 | -0.0303 | 4.32 | 0.00068 | 0 | 4.59 | 0.000879 | -0.0303 |  | CFL | AllSpc | 4320 | 0.68 | 4320 | 0.68 | 1.06 | 1.29 | -0.0070139 | 4320 | 0.68 | 4320 | 0.68 | 1.06 | 1.29 | -0.00701
CFLAllSpcPGERtLNewCZ13 | Com-Iltg-dWatt-CFL_OSspc | PGE | RtL | New | CZ13 | 4.32 | 0.00068 | 0 | 4.64 | 0.000871 | -0.0288 | 4.32 | 0.00068 | 0 | 4.64 | 0.000871 | -0.0288 |  | CFL | AllSpc | 4320 | 0.68 | 4320 | 0.68 | 1.07 | 1.28 | -0.0066667 | 4320 | 0.68 | 4320 | 0.68 | 1.07 | 1.28 | -0.00667
CFLAllSpcPGERtLNewCZ16 | Com-Iltg-dWatt-CFL_OSspc | PGE | RtL | New | CZ16 | 4.32 | 0.00068 | 0 | 4.23 | 0.000831 | -0.0605 | 4.32 | 0.00068 | 0 | 4.23 | 0.000831 | -0.0605 |  | CFL | AllSpc | 4320 | 0.68 | 4320 | 0.68 | 0.979 | 1.22 | -0.014005 | 4320 | 0.68 | 4320 | 0.68 | 0.979 | 1.22 | -0.014
CFLAllSpcPGERtLNewIOU | Com-Iltg-dWatt-CFL_OSspc | PGE | RtL | New | IOU | 4.32 | 0.00068 | 0 | 4.5432 | 0.00086117 | -0.030511 | 4.32 | 0.00068 | 0 | 4.5432 | 0.00086117 | -0.030511 |  | CFL | AllSpc | 4320 | 0.68 | 4320 | 0.68 | 1.05 | 1.27 | -0.0070628 | 4320 | 0.68 | 4320 | 0.68 | 1.05 | 1.27 | -0.00706
CFLAllSpcPGERtSExCZ01 | Com-Iltg-dWatt-CFL_OSspc | PGE | RtS | Ex | CZ01 | 3.9695 | 0.00068991 | 0 | 3.8395 | 0.00081591 | -0.047595 | 3.9695 | 0.00068991 | 0 | 3.8395 | 0.00081591 | -0.047595 |  | CFL | AllSpc | 3970 | 0.69 | 3970 | 0.69 | 0.967 | 1.18 | -0.01199 | 3970 | 0.69 | 3970 | 0.69 | 0.967 | 1.18 | -0.012
CFLAllSpcPGERtSExCZ02 | Com-Iltg-dWatt-CFL_OSspc | PGE | RtS | Ex | CZ02 | 3.9695 | 0.0006899 | 0 | 4.1295 | 0.00082385 | -0.025995 | 3.9695 | 0.0006899 | 0 | 4.1295 | 0.00082385 | -0.025995 |  | CFL | AllSpc | 3970 | 0.69 | 3970 | 0.69 | 1.04 | 1.19 | -0.0065487 | 3970 | 0.69 | 3970 | 0.69 | 1.04 | 1.19 | -0.00655
CFLAllSpcPGERtSExCZ03 | Com-Iltg-dWatt-CFL_OSspc | PGE | RtS | Ex | CZ03 | 3.9695 | 0.00068991 | 0 | 4.1396 | 0.00083591 | -0.0245 | 3.9695 | 0.00068991 | 0 | 4.1396 | 0.00083591 | -0.0245 |  | CFL | AllSpc | 3970 | 0.69 | 3970 | 0.69 | 1.04 | 1.21 | -0.006172 | 3970 | 0.69 | 3970 | 0.69 | 1.04 | 1.21 | -0.00617
CFLAllSpcPGERtSExCZ04 | Com-Iltg-dWatt-CFL_OSspc | PGE | RtS | Ex | CZ04 | 3.9695 | 0.0006899 | 0 | 4.2195 | 0.0008359 | -0.0184 | 3.9695 | 0.0006899 | 0 | 4.2195 | 0.0008359 | -0.0184 |  | CFL | AllSpc | 3970 | 0.69 | 3970 | 0.69 | 1.06 | 1.21 | -0.0046354 | 3970 | 0.69 | 3970 | 0.69 | 1.06 | 1.21 | -0.00464
CFLAllSpcPGERtSExCZ05 | Com-Iltg-dWatt-CFL_OSspc | PGE | RtS | Ex | CZ05 | 3.9695 | 0.0006899 | 0 | 4.1395 | 0.0008219 | -0.021595 | 3.9695 | 0.0006899 | 0 | 4.1395 | 0.0008219 | -0.021595 |  | CFL | AllSpc | 3970 | 0.69 | 3970 | 0.69 | 1.04 | 1.19 | -0.0054402 | 3970 | 0.69 | 3970 | 0.69 | 1.04 | 1.19 | -0.00544
CFLAllSpcPGERtSExCZ11 | Com-Iltg-dWatt-CFL_OSspc | PGE | RtS | Ex | CZ11 | 3.9693 | 0.00068986 | 0 | 4.1693 | 0.00084486 | -0.0245 | 3.9693 | 0.00068986 | 0 | 4.1693 | 0.00084486 | -0.0245 |  | CFL | AllSpc | 3970 | 0.69 | 3970 | 0.69 | 1.05 | 1.22 | -0.0061723 | 3970 | 0.69 | 3970 | 0.69 | 1.05 | 1.22 | -0.00617
CFLAllSpcPGERtSExCZ12 | Com-Iltg-dWatt-CFL_OSspc | PGE | RtS | Ex | CZ12 | 3.9694 | 0.00068988 | 0 | 4.1594 | 0.00083281 | -0.025294 | 3.9694 | 0.00068988 | 0 | 4.1594 | 0.00083281 | -0.025294 |  | CFL | AllSpc | 3970 | 0.69 | 3970 | 0.69 | 1.05 | 1.21 | -0.0063722 | 3970 | 0.69 | 3970 | 0.69 | 1.05 | 1.21 | -0.00637
CFLAllSpcPGERtSExCZ13 | Com-Iltg-dWatt-CFL_OSspc | PGE | RtS | Ex | CZ13 | 3.9693 | 0.00068986 | 0 | 4.1893 | 0.00083779 | -0.022993 | 3.9693 | 0.00068986 | 0 | 4.1893 | 0.00083779 | -0.022993 |  | CFL | AllSpc | 3970 | 0.69 | 3970 | 0.69 | 1.06 | 1.21 | -0.0057927 | 3970 | 0.69 | 3970 | 0.69 | 1.06 | 1.21 | -0.00579
CFLAllSpcPGERtSExCZ16 | Com-Iltg-dWatt-CFL_OSspc | PGE | RtS | Ex | CZ16 | 3.9694 | 0.00068989 | 0 | 3.8894 | 0.00081989 | -0.044394 | 3.9694 | 0.00068989 | 0 | 3.8894 | 0.00081989 | -0.044394 |  | CFL | AllSpc | 3970 | 0.69 | 3970 | 0.69 | 0.98 | 1.19 | -0.011184 | 3970 | 0.69 | 3970 | 0.69 | 0.98 | 1.19 | -0.0112
CFLAllSpcPGERtSExIOU | Com-Iltg-dWatt-CFL_OSspc | PGE | RtS | Ex | IOU | 3.9694 | 0.00068989 | 0 | 4.1595 | 0.00083452 | -0.023948 | 3.9694 | 0.00068989 | 0 | 4.1595 | 0.00083452 | -0.023948 |  | CFL | AllSpc | 3970 | 0.69 | 3970 | 0.69 | 1.05 | 1.21 | -0.0060331 | 3970 | 0.69 | 3970 | 0.69 | 1.05 | 1.21 | -0.00603
CFLAllSpcPGERtSNewCZ01 | Com-Iltg-dWatt-CFL_OSspc | PGE | RtS | New | CZ01 | 3.96 | 0.000688 | 0 | 3.81 | 0.000801 | -0.053 | 3.96 | 0.000688 | 0 | 3.81 | 0.000801 | -0.053 |  | CFL | AllSpc | 3960 | 0.688 | 3960 | 0.688 | 0.962 | 1.16 | -0.013384 | 3960 | 0.688 | 3960 | 0.688 | 0.962 | 1.16 | -0.0134
CFLAllSpcPGERtSNewCZ02 | Com-Iltg-dWatt-CFL_OSspc | PGE | RtS | New | CZ02 | 3.96 | 0.000688 | 0 | 4.08 | 0.00084 | -0.0286 | 3.96 | 0.000688 | 0 | 4.08 | 0.00084 | -0.0286 |  | CFL | AllSpc | 3960 | 0.688 | 3960 | 0.688 | 1.03 | 1.22 | -0.0072222 | 3960 | 0.688 | 3960 | 0.688 | 1.03 | 1.22 | -0.00722
CFLAllSpcPGERtSNewCZ03 | Com-Iltg-dWatt-CFL_OSspc | PGE | RtS | New | CZ03 | 3.96 | 0.000688 | 0 | 4.01 | 0.000825 | -0.0273 | 3.96 | 0.000688 | 0 | 4.01 | 0.000825 | -0.0273 |  | CFL | AllSpc | 3960 | 0.688 | 3960 | 0.688 | 1.01 | 1.2 | -0.0068939 | 3960 | 0.688 | 3960 | 0.688 | 1.01 | 1.2 | -0.00689
CFLAllSpcPGERtSNewCZ04 | Com-Iltg-dWatt-CFL_OSspc | PGE | RtS | New | CZ04 | 3.96 | 0.000688 | 0 | 4.13 | 0.000833 | -0.0205 | 3.96 | 0.000688 | 0 | 4.13 | 0.000833 | -0.0205 |  | CFL | AllSpc | 3960 | 0.688 | 3960 | 0.688 | 1.04 | 1.21 | -0.0051768 | 3960 | 0.688 | 3960 | 0.688 | 1.04 | 1.21 | -0.00518
CFLAllSpcPGERtSNewCZ05 | Com-Iltg-dWatt-CFL_OSspc | PGE | RtS | New | CZ05 | 3.96 | 0.000688 | 0 | 4.04 | 0.000811 | -0.0243 | 3.96 | 0.000688 | 0 | 4.04 | 0.000811 | -0.0243 |  | CFL | AllSpc | 3960 | 0.688 | 3960 | 0.688 | 1.02 | 1.18 | -0.0061364 | 3960 | 0.688 | 3960 | 0.688 | 1.02 | 1.18 | -0.00614
CFLAllSpcPGERtSNewCZ11 | Com-Iltg-dWatt-CFL_OSspc | PGE | RtS | New | CZ11 | 3.96 | 0.000688 | 0 | 4.18 | 0.000856 | -0.0248 | 3.96 | 0.000688 | 0 | 4.18 | 0.000856 | -0.0248 |  | CFL | AllSpc | 3960 | 0.688 | 3960 | 0.688 | 1.06 | 1.24 | -0.0062626 | 3960 | 0.688 | 3960 | 0.688 | 1.06 | 1.24 | -0.00626
CFLAllSpcPGERtSNewCZ12 | Com-Iltg-dWatt-CFL_OSspc | PGE | RtS | New | CZ12 | 3.96 | 0.000688 | 0 | 4.15 | 0.000848 | -0.0264 | 3.96 | 0.000688 | 0 | 4.15 | 0.000848 | -0.0264 |  | CFL | AllSpc | 3960 | 0.688 | 3960 | 0.688 | 1.05 | 1.23 | -0.0066667 | 3960 | 0.688 | 3960 | 0.688 | 1.05 | 1.23 | -0.00667
CFLAllSpcPGERtSNewCZ13 | Com-Iltg-dWatt-CFL_OSspc | PGE | RtS | New | CZ13 | 3.96 | 0.000688 | 0 | 4.18 | 0.000847 | -0.0239 | 3.96 | 0.000688 | 0 | 4.18 | 0.000847 | -0.0239 |  | CFL | AllSpc | 3960 | 0.688 | 3960 | 0.688 | 1.06 | 1.23 | -0.0060354 | 3960 | 0.688 | 3960 | 0.688 | 1.06 | 1.23 | -0.00604
CFLAllSpcPGERtSNewCZ16 | Com-Iltg-dWatt-CFL_OSspc | PGE | RtS | New | CZ16 | 3.96 | 0.000688 | 0 | 3.86 | 0.000818 | -0.0475 | 3.96 | 0.000688 | 0 | 3.86 | 0.000818 | -0.0475 |  | CFL | AllSpc | 3960 | 0.688 | 3960 | 0.688 | 0.975 | 1.19 | -0.011995 | 3960 | 0.688 | 3960 | 0.688 | 0.975 | 1.19 | -0.012
CFLAllSpcPGERtSNewIOU | Com-Iltg-dWatt-CFL_OSspc | PGE | RtS | New | IOU | 3.96 | 0.000688 | 0 | 4.1079 | 0.00083864 | -0.025692 | 3.96 | 0.000688 | 0 | 4.1079 | 0.00083864 | -0.025692 |  | CFL | AllSpc | 3960 | 0.688 | 3960 | 0.688 | 1.04 | 1.22 | -0.006488 | 3960 | 0.688 | 3960 | 0.688 | 1.04 | 1.22 | -0.00649
CFLAllSpcPGESCnExCZ01 | Com-Iltg-dWatt-CFL_OSspc | PGE | SCn | Ex | CZ01 | 2.6 | 0.000483 | 0 | 2.21 | 0.000483 | -0.0438 | 2.6 | 0.000483 | 0 | 2.21 | 0.000483 | -0.0438 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 0.85 | 1 | -0.016846 | 2600 | 0.483 | 2600 | 0.483 | 0.85 | 1 | -0.0168
CFLAllSpcPGESCnExCZ02 | Com-Iltg-dWatt-CFL_OSspc | PGE | SCn | Ex | CZ02 | 2.6 | 0.000483 | 0 | 2.49 | 0.000602 | -0.0232 | 2.6 | 0.000483 | 0 | 2.49 | 0.000602 | -0.0232 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 0.958 | 1.25 | -0.0089231 | 2600 | 0.483 | 2600 | 0.483 | 0.958 | 1.25 | -0.00892
CFLAllSpcPGESCnExCZ03 | Com-Iltg-dWatt-CFL_OSspc | PGE | SCn | Ex | CZ03 | 2.6 | 0.000483 | 0 | 2.41 | 0.000638 | -0.0254 | 2.6 | 0.000483 | 0 | 2.41 | 0.000638 | -0.0254 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 0.927 | 1.32 | -0.0097692 | 2600 | 0.483 | 2600 | 0.483 | 0.927 | 1.32 | -0.00977
CFLAllSpcPGESCnExCZ04 | Com-Iltg-dWatt-CFL_OSspc | PGE | SCn | Ex | CZ04 | 2.6 | 0.000483 | 0 | 2.56 | 0.000603 | -0.0203 | 2.6 | 0.000483 | 0 | 2.56 | 0.000603 | -0.0203 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 0.985 | 1.25 | -0.0078077 | 2600 | 0.483 | 2600 | 0.483 | 0.985 | 1.25 | -0.00781
CFLAllSpcPGESCnExCZ05 | Com-Iltg-dWatt-CFL_OSspc | PGE | SCn | Ex | CZ05 | 2.6 | 0.000483 | 0 | 2.39 | 0.000575 | -0.0252 | 2.6 | 0.000483 | 0 | 2.39 | 0.000575 | -0.0252 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 0.919 | 1.19 | -0.0096923 | 2600 | 0.483 | 2600 | 0.483 | 0.919 | 1.19 | -0.00969
CFLAllSpcPGESCnExCZ11 | Com-Iltg-dWatt-CFL_OSspc | PGE | SCn | Ex | CZ11 | 2.6 | 0.000483 | 0 | 2.55 | 0.000587 | -0.0215 | 2.6 | 0.000483 | 0 | 2.55 | 0.000587 | -0.0215 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 0.981 | 1.22 | -0.0082692 | 2600 | 0.483 | 2600 | 0.483 | 0.981 | 1.22 | -0.00827
CFLAllSpcPGESCnExCZ12 | Com-Iltg-dWatt-CFL_OSspc | PGE | SCn | Ex | CZ12 | 2.6 | 0.000483 | 0 | 2.56 | 0.000595 | -0.0216 | 2.6 | 0.000483 | 0 | 2.56 | 0.000595 | -0.0216 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 0.985 | 1.23 | -0.0083077 | 2600 | 0.483 | 2600 | 0.483 | 0.985 | 1.23 | -0.00831
CFLAllSpcPGESCnExCZ13 | Com-Iltg-dWatt-CFL_OSspc | PGE | SCn | Ex | CZ13 | 2.6 | 0.000483 | 0 | 2.58 | 0.000585 | -0.0192 | 2.6 | 0.000483 | 0 | 2.58 | 0.000585 | -0.0192 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 0.992 | 1.21 | -0.0073846 | 2600 | 0.483 | 2600 | 0.483 | 0.992 | 1.21 | -0.00738
CFLAllSpcPGESCnExCZ16 | Com-Iltg-dWatt-CFL_OSspc | PGE | SCn | Ex | CZ16 | 2.6 | 0.000483 | 0 | 2.32 | 0.000574 | -0.0305 | 2.6 | 0.000483 | 0 | 2.32 | 0.000574 | -0.0305 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 0.892 | 1.19 | -0.011731 | 2600 | 0.483 | 2600 | 0.483 | 0.892 | 1.19 | -0.0117
CFLAllSpcPGESCnExIOU | Com-Iltg-dWatt-CFL_OSspc | PGE | SCn | Ex | IOU | 2.6 | 0.000483 | 0 | 2.5001 | 0.00060799 | -0.02277 | 2.6 | 0.000483 | 0 | 2.5001 | 0.00060799 | -0.02277 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 0.962 | 1.26 | -0.0087575 | 2600 | 0.483 | 2600 | 0.483 | 0.962 | 1.26 | -0.00876
CFLAllSpcPGESCnNewCZ01 | Com-Iltg-dWatt-CFL_OSspc | PGE | SCn | New | CZ01 | 2.6 | 0.000483 | 0 | 2.23 | 0.000483 | -0.0471 | 2.6 | 0.000483 | 0 | 2.23 | 0.000483 | -0.0471 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 0.858 | 1 | -0.018115 | 2600 | 0.483 | 2600 | 0.483 | 0.858 | 1 | -0.0181
CFLAllSpcPGESCnNewCZ02 | Com-Iltg-dWatt-CFL_OSspc | PGE | SCn | New | CZ02 | 2.6 | 0.000483 | 0 | 2.48 | 0.000585 | -0.0246 | 2.6 | 0.000483 | 0 | 2.48 | 0.000585 | -0.0246 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 0.954 | 1.21 | -0.0094615 | 2600 | 0.483 | 2600 | 0.483 | 0.954 | 1.21 | -0.00946
CFLAllSpcPGESCnNewCZ03 | Com-Iltg-dWatt-CFL_OSspc | PGE | SCn | New | CZ03 | 2.6 | 0.000483 | 0 | 2.41 | 0.000604 | -0.0276 | 2.6 | 0.000483 | 0 | 2.41 | 0.000604 | -0.0276 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 0.927 | 1.25 | -0.010615 | 2600 | 0.483 | 2600 | 0.483 | 0.927 | 1.25 | -0.0106
CFLAllSpcPGESCnNewCZ04 | Com-Iltg-dWatt-CFL_OSspc | PGE | SCn | New | CZ04 | 2.6 | 0.000483 | 0 | 2.54 | 0.00058 | -0.0219 | 2.6 | 0.000483 | 0 | 2.54 | 0.00058 | -0.0219 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 0.977 | 1.2 | -0.0084231 | 2600 | 0.483 | 2600 | 0.483 | 0.977 | 1.2 | -0.00842
CFLAllSpcPGESCnNewCZ05 | Com-Iltg-dWatt-CFL_OSspc | PGE | SCn | New | CZ05 | 2.6 | 0.000483 | 0 | 2.39 | 0.000577 | -0.0279 | 2.6 | 0.000483 | 0 | 2.39 | 0.000577 | -0.0279 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 0.919 | 1.19 | -0.010731 | 2600 | 0.483 | 2600 | 0.483 | 0.919 | 1.19 | -0.0107
CFLAllSpcPGESCnNewCZ11 | Com-Iltg-dWatt-CFL_OSspc | PGE | SCn | New | CZ11 | 2.6 | 0.000483 | 0 | 2.54 | 0.000574 | -0.0225 | 2.6 | 0.000483 | 0 | 2.54 | 0.000574 | -0.0225 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 0.977 | 1.19 | -0.0086538 | 2600 | 0.483 | 2600 | 0.483 | 0.977 | 1.19 | -0.00865
CFLAllSpcPGESCnNewCZ12 | Com-Iltg-dWatt-CFL_OSspc | PGE | SCn | New | CZ12 | 2.6 | 0.000483 | 0 | 2.54 | 0.000577 | -0.0228 | 2.6 | 0.000483 | 0 | 2.54 | 0.000577 | -0.0228 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 0.977 | 1.19 | -0.0087692 | 2600 | 0.483 | 2600 | 0.483 | 0.977 | 1.19 | -0.00877
CFLAllSpcPGESCnNewCZ13 | Com-Iltg-dWatt-CFL_OSspc | PGE | SCn | New | CZ13 | 2.6 | 0.000483 | 0 | 2.53 | 0.000562 | -0.0198 | 2.6 | 0.000483 | 0 | 2.53 | 0.000562 | -0.0198 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 0.973 | 1.16 | -0.0076154 | 2600 | 0.483 | 2600 | 0.483 | 0.973 | 1.16 | -0.00762
CFLAllSpcPGESCnNewCZ16 | Com-Iltg-dWatt-CFL_OSspc | PGE | SCn | New | CZ16 | 2.6 | 0.000483 | 0 | 2.31 | 0.000558 | -0.032 | 2.6 | 0.000483 | 0 | 2.31 | 0.000558 | -0.032 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 0.888 | 1.16 | -0.012308 | 2600 | 0.483 | 2600 | 0.483 | 0.888 | 1.16 | -0.0123
CFLAllSpcPGESCnNewIOU | Com-Iltg-dWatt-CFL_OSspc | PGE | SCn | New | IOU | 2.6 | 0.000483 | 0 | 2.4992 | 0.00057981 | -0.023615 | 2.6 | 0.000483 | 0 | 2.4992 | 0.00057981 | -0.023615 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 0.961 | 1.2 | -0.0090828 | 2600 | 0.483 | 2600 | 0.483 | 0.961 | 1.2 | -0.00908
CFLAllSpcPGESUnExCZ01 | Com-Iltg-dWatt-CFL_OSspc | PGE | SUn | Ex | CZ01 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0 | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0
CFLAllSpcPGESUnExCZ02 | Com-Iltg-dWatt-CFL_OSspc | PGE | SUn | Ex | CZ02 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0 | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0
CFLAllSpcPGESUnExCZ03 | Com-Iltg-dWatt-CFL_OSspc | PGE | SUn | Ex | CZ03 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0 | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0
CFLAllSpcPGESUnExCZ04 | Com-Iltg-dWatt-CFL_OSspc | PGE | SUn | Ex | CZ04 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0 | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0
CFLAllSpcPGESUnExCZ05 | Com-Iltg-dWatt-CFL_OSspc | PGE | SUn | Ex | CZ05 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0 | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0
CFLAllSpcPGESUnExCZ11 | Com-Iltg-dWatt-CFL_OSspc | PGE | SUn | Ex | CZ11 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0 | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0
CFLAllSpcPGESUnExCZ12 | Com-Iltg-dWatt-CFL_OSspc | PGE | SUn | Ex | CZ12 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0 | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0
CFLAllSpcPGESUnExCZ13 | Com-Iltg-dWatt-CFL_OSspc | PGE | SUn | Ex | CZ13 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0 | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0
CFLAllSpcPGESUnExCZ16 | Com-Iltg-dWatt-CFL_OSspc | PGE | SUn | Ex | CZ16 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0 | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0
CFLAllSpcPGESUnExIOU | Com-Iltg-dWatt-CFL_OSspc | PGE | SUn | Ex | IOU | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0 | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0
CFLAllSpcPGESUnNewCZ01 | Com-Iltg-dWatt-CFL_OSspc | PGE | SUn | New | CZ01 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0 | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0
CFLAllSpcPGESUnNewCZ02 | Com-Iltg-dWatt-CFL_OSspc | PGE | SUn | New | CZ02 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0 | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0
CFLAllSpcPGESUnNewCZ03 | Com-Iltg-dWatt-CFL_OSspc | PGE | SUn | New | CZ03 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0 | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0
CFLAllSpcPGESUnNewCZ04 | Com-Iltg-dWatt-CFL_OSspc | PGE | SUn | New | CZ04 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0 | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0
CFLAllSpcPGESUnNewCZ05 | Com-Iltg-dWatt-CFL_OSspc | PGE | SUn | New | CZ05 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0 | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0
CFLAllSpcPGESUnNewCZ11 | Com-Iltg-dWatt-CFL_OSspc | PGE | SUn | New | CZ11 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0 | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0
CFLAllSpcPGESUnNewCZ12 | Com-Iltg-dWatt-CFL_OSspc | PGE | SUn | New | CZ12 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0 | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0
CFLAllSpcPGESUnNewCZ13 | Com-Iltg-dWatt-CFL_OSspc | PGE | SUn | New | CZ13 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0 | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0
CFLAllSpcPGESUnNewCZ16 | Com-Iltg-dWatt-CFL_OSspc | PGE | SUn | New | CZ16 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0 | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0
CFLAllSpcPGESUnNewIOU | Com-Iltg-dWatt-CFL_OSspc | PGE | SUn | New | IOU | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0 | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0
CFLAllSpcPGEWRfExCZ01 | Com-Iltg-dWatt-CFL_OSspc | PGE | WRf | Ex | CZ01 | 4.24 | 0.000466 | 0 | 6.7774 | 0.000657 | 0 | 4.24 | 0.000466 | 0 | 6.7774 | 0.000657 | 0 |  | CFL | AllSpc | 4240 | 0.466 | 4240 | 0.466 | 1.6 | 1.41 | 0 | 4240 | 0.466 | 4240 | 0.466 | 1.6 | 1.41 | 0
CFLAllSpcPGEWRfExCZ02 | Com-Iltg-dWatt-CFL_OSspc | PGE | WRf | Ex | CZ02 | 4.24 | 0.000466 | 0 | 6.8773 | 0.000592 | 0 | 4.24 | 0.000466 | 0 | 6.8773 | 0.000592 | 0 |  | CFL | AllSpc | 4240 | 0.466 | 4240 | 0.466 | 1.62 | 1.27 | 0 | 4240 | 0.466 | 4240 | 0.466 | 1.62 | 1.27 | 0
CFLAllSpcPGEWRfExCZ03 | Com-Iltg-dWatt-CFL_OSspc | PGE | WRf | Ex | CZ03 | 4.24 | 0.000466 | 0 | 6.86 | 0.00061637 | 0 | 4.24 | 0.000466 | 0 | 6.86 | 0.00061637 | 0 |  | CFL | AllSpc | 4240 | 0.466 | 4240 | 0.466 | 1.62 | 1.32 | 0 | 4240 | 0.466 | 4240 | 0.466 | 1.62 | 1.32 | 0
CFLAllSpcPGEWRfExCZ04 | Com-Iltg-dWatt-CFL_OSspc | PGE | WRf | Ex | CZ04 | 4.24 | 0.000466 | 0 | 6.8705 | 0.000595 | 0 | 4.24 | 0.000466 | 0 | 6.8705 | 0.000595 | 0 |  | CFL | AllSpc | 4240 | 0.466 | 4240 | 0.466 | 1.62 | 1.28 | 0 | 4240 | 0.466 | 4240 | 0.466 | 1.62 | 1.28 | 0
CFLAllSpcPGEWRfExCZ05 | Com-Iltg-dWatt-CFL_OSspc | PGE | WRf | Ex | CZ05 | 4.24 | 0.000466 | 0 | 6.74 | 0.000613 | 0 | 4.24 | 0.000466 | 0 | 6.74 | 0.000613 | 0 |  | CFL | AllSpc | 4240 | 0.466 | 4240 | 0.466 | 1.59 | 1.32 | 0 | 4240 | 0.466 | 4240 | 0.466 | 1.59 | 1.32 | 0
CFLAllSpcPGEWRfExCZ11 | Com-Iltg-dWatt-CFL_OSspc | PGE | WRf | Ex | CZ11 | 4.24 | 0.000466 | 0 | 6.841 | 0.000609 | 0 | 4.24 | 0.000466 | 0 | 6.841 | 0.000609 | 0 |  | CFL | AllSpc | 4240 | 0.466 | 4240 | 0.466 | 1.61 | 1.31 | 0 | 4240 | 0.466 | 4240 | 0.466 | 1.61 | 1.31 | 0
CFLAllSpcPGEWRfExCZ12 | Com-Iltg-dWatt-CFL_OSspc | PGE | WRf | Ex | CZ12 | 4.24 | 0.000466 | 0 | 6.8 | 0.000597 | 0 | 4.24 | 0.000466 | 0 | 6.8 | 0.000597 | 0 |  | CFL | AllSpc | 4240 | 0.466 | 4240 | 0.466 | 1.6 | 1.28 | 0 | 4240 | 0.466 | 4240 | 0.466 | 1.6 | 1.28 | 0
CFLAllSpcPGEWRfExCZ13 | Com-Iltg-dWatt-CFL_OSspc | PGE | WRf | Ex | CZ13 | 4.24 | 0.000466 | 0 | 6.9 | 0.000588 | 0 | 4.24 | 0.000466 | 0 | 6.9 | 0.000588 | 0 |  | CFL | AllSpc | 4240 | 0.466 | 4240 | 0.466 | 1.63 | 1.26 | 0 | 4240 | 0.466 | 4240 | 0.466 | 1.63 | 1.26 | 0
CFLAllSpcPGEWRfExCZ16 | Com-Iltg-dWatt-CFL_OSspc | PGE | WRf | Ex | CZ16 | 4.24 | 0.000466 | 0 | 6.2 | 0.00064 | 0 | 4.24 | 0.000466 | 0 | 6.2 | 0.00064 | 0 |  | CFL | AllSpc | 4240 | 0.466 | 4240 | 0.466 | 1.46 | 1.37 | 0 | 4240 | 0.466 | 4240 | 0.466 | 1.46 | 1.37 | 0
CFLAllSpcPGEWRfExIOU | Com-Iltg-dWatt-CFL_OSspc | PGE | WRf | Ex | IOU | 4.24 | 0.000466 | 0 | 6.8551 | 0.00060208 | 0 | 4.24 | 0.000466 | 0 | 6.8551 | 0.00060208 | 0 |  | CFL | AllSpc | 4240 | 0.466 | 4240 | 0.466 | 1.62 | 1.29 | 0 | 4240 | 0.466 | 4240 | 0.466 | 1.62 | 1.29 | 0
CFLAllSpcPGEWRfNewCZ01 | Com-Iltg-dWatt-CFL_OSspc | PGE | WRf | New | CZ01 | 4.24 | 0.000466 | 0 | 5.63 | 0.000932 | 0 | 4.24 | 0.000466 | 0 | 5.63 | 0.000932 | 0 |  | CFL | AllSpc | 4240 | 0.466 | 4240 | 0.466 | 1.33 | 2 | 0 | 4240 | 0.466 | 4240 | 0.466 | 1.33 | 2 | 0
CFLAllSpcPGEWRfNewCZ02 | Com-Iltg-dWatt-CFL_OSspc | PGE | WRf | New | CZ02 | 4.24 | 0.000466 | 0 | 5.96 | 0.00063 | 0 | 4.24 | 0.000466 | 0 | 5.96 | 0.00063 | 0 |  | CFL | AllSpc | 4240 | 0.466 | 4240 | 0.466 | 1.41 | 1.35 | 0 | 4240 | 0.466 | 4240 | 0.466 | 1.41 | 1.35 | 0
CFLAllSpcPGEWRfNewCZ03 | Com-Iltg-dWatt-CFL_OSspc | PGE | WRf | New | CZ03 | 4.24 | 0.000466 | 0 | 6.02 | 0.000932 | 0 | 4.24 | 0.000466 | 0 | 6.02 | 0.000932 | 0 |  | CFL | AllSpc | 4240 | 0.466 | 4240 | 0.466 | 1.42 | 2 | 0 | 4240 | 0.466 | 4240 | 0.466 | 1.42 | 2 | 0
CFLAllSpcPGEWRfNewCZ04 | Com-Iltg-dWatt-CFL_OSspc | PGE | WRf | New | CZ04 | 4.24 | 0.000466 | 0 | 6.13 | 0.000683 | 0 | 4.24 | 0.000466 | 0 | 6.13 | 0.000683 | 0 |  | CFL | AllSpc | 4240 | 0.466 | 4240 | 0.466 | 1.45 | 1.47 | 0 | 4240 | 0.466 | 4240 | 0.466 | 1.45 | 1.47 | 0
CFLAllSpcPGEWRfNewCZ05 | Com-Iltg-dWatt-CFL_OSspc | PGE | WRf | New | CZ05 | 4.24 | 0.000466 | 0 | 5.97 | 0.000932 | 0 | 4.24 | 0.000466 | 0 | 5.97 | 0.000932 | 0 |  | CFL | AllSpc | 4240 | 0.466 | 4240 | 0.466 | 1.41 | 2 | 0 | 4240 | 0.466 | 4240 | 0.466 | 1.41 | 2 | 0
CFLAllSpcPGEWRfNewCZ11 | Com-Iltg-dWatt-CFL_OSspc | PGE | WRf | New | CZ11 | 4.24 | 0.000466 | 0 | 6.11 | 0.000735 | 0 | 4.24 | 0.000466 | 0 | 6.11 | 0.000735 | 0 |  | CFL | AllSpc | 4240 | 0.466 | 4240 | 0.466 | 1.44 | 1.58 | 0 | 4240 | 0.466 | 4240 | 0.466 | 1.44 | 1.58 | 0
CFLAllSpcPGEWRfNewCZ12 | Com-Iltg-dWatt-CFL_OSspc | PGE | WRf | New | CZ12 | 4.24 | 0.000466 | 0 | 6.09 | 0.000637 | 0 | 4.24 | 0.000466 | 0 | 6.09 | 0.000637 | 0 |  | CFL | AllSpc | 4240 | 0.466 | 4240 | 0.466 | 1.44 | 1.37 | 0 | 4240 | 0.466 | 4240 | 0.466 | 1.44 | 1.37 | 0
CFLAllSpcPGEWRfNewCZ13 | Com-Iltg-dWatt-CFL_OSspc | PGE | WRf | New | CZ13 | 4.24 | 0.000466 | 0 | 6.23 | 0.000582 | 0 | 4.24 | 0.000466 | 0 | 6.23 | 0.000582 | 0 |  | CFL | AllSpc | 4240 | 0.466 | 4240 | 0.466 | 1.47 | 1.25 | 0 | 4240 | 0.466 | 4240 | 0.466 | 1.47 | 1.25 | 0
CFLAllSpcPGEWRfNewCZ16 | Com-Iltg-dWatt-CFL_OSspc | PGE | WRf | New | CZ16 | 4.24 | 0.000466 | 0 | 5.59 | 0.000932 | 0 | 4.24 | 0.000466 | 0 | 5.59 | 0.000932 | 0 |  | CFL | AllSpc | 4240 | 0.466 | 4240 | 0.466 | 1.32 | 2 | 0 | 4240 | 0.466 | 4240 | 0.466 | 1.32 | 2 | 0
CFLAllSpcPGEWRfNewIOU | Com-Iltg-dWatt-CFL_OSspc | PGE | WRf | New | IOU | 4.24 | 0.000466 | 0 | 6.1159 | 0.00069835 | 0 | 4.24 | 0.000466 | 0 | 6.1159 | 0.00069835 | 0 |  | CFL | AllSpc | 4240 | 0.466 | 4240 | 0.466 | 1.44 | 1.5 | 0 | 4240 | 0.466 | 4240 | 0.466 | 1.44 | 1.5 | 0
CFLAllSpcSCEAsmExCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCE | Asm | Ex | CZ05 | 2.03 | 0.00033194 | 0 | 2.13 | 0.00039794 | -0.0198 | 2.03 | 0.00033194 | 0 | 2.13 | 0.00039794 | -0.0198 |  | CFL | AllSpc | 2030 | 0.332 | 2030 | 0.332 | 1.05 | 1.2 | -0.0097537 | 2030 | 0.332 | 2030 | 0.332 | 1.05 | 1.2 | -0.00975
CFLAllSpcSCEAsmExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCE | Asm | Ex | CZ06 | 2.03 | 0.00033194 | 0 | 2.27 | 0.000413 | -0.0094011 | 2.03 | 0.00033194 | 0 | 2.27 | 0.000413 | -0.0094011 |  | CFL | AllSpc | 2030 | 0.332 | 2030 | 0.332 | 1.12 | 1.24 | -0.0046311 | 2030 | 0.332 | 2030 | 0.332 | 1.12 | 1.24 | -0.00463
CFLAllSpcSCEAsmExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCE | Asm | Ex | CZ08 | 2.03 | 0.00033194 | 0 | 2.28 | 0.00040194 | -0.0084911 | 2.03 | 0.00033194 | 0 | 2.28 | 0.00040194 | -0.0084911 |  | CFL | AllSpc | 2030 | 0.332 | 2030 | 0.332 | 1.12 | 1.21 | -0.0041828 | 2030 | 0.332 | 2030 | 0.332 | 1.12 | 1.21 | -0.00418
CFLAllSpcSCEAsmExCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCE | Asm | Ex | CZ09 | 2.03 | 0.00033194 | 0 | 2.2606 | 0.00041194 | -0.010105 | 2.03 | 0.00033194 | 0 | 2.2606 | 0.00041194 | -0.010105 |  | CFL | AllSpc | 2030 | 0.332 | 2030 | 0.332 | 1.11 | 1.24 | -0.0049781 | 2030 | 0.332 | 2030 | 0.332 | 1.11 | 1.24 | -0.00498
CFLAllSpcSCEAsmExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCE | Asm | Ex | CZ10 | 2.03 | 0.00033186 | 0 | 2.2014 | 0.00039786 | -0.0112 | 2.03 | 0.00033186 | 0 | 2.2014 | 0.00039786 | -0.0112 |  | CFL | AllSpc | 2030 | 0.332 | 2030 | 0.332 | 1.08 | 1.2 | -0.0055172 | 2030 | 0.332 | 2030 | 0.332 | 1.08 | 1.2 | -0.00552
CFLAllSpcSCEAsmExCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCE | Asm | Ex | CZ13 | 2.03 | 0.00033191 | 0 | 2.1809 | 0.00040191 | -0.0175 | 2.03 | 0.00033191 | 0 | 2.1809 | 0.00040191 | -0.0175 |  | CFL | AllSpc | 2030 | 0.332 | 2030 | 0.332 | 1.07 | 1.21 | -0.0086207 | 2030 | 0.332 | 2030 | 0.332 | 1.07 | 1.21 | -0.00862
CFLAllSpcSCEAsmExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCE | Asm | Ex | CZ14 | 2.03 | 0.0003319 | 0 | 2.171 | 0.0003759 | -0.0173 | 2.03 | 0.0003319 | 0 | 2.171 | 0.0003759 | -0.0173 |  | CFL | AllSpc | 2030 | 0.332 | 2030 | 0.332 | 1.07 | 1.13 | -0.0085222 | 2030 | 0.332 | 2030 | 0.332 | 1.07 | 1.13 | -0.00852
CFLAllSpcSCEAsmExCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCE | Asm | Ex | CZ15 | 2.03 | 0.00033186 | 0 | 2.4914 | 0.00038886 | -0.0049514 | 2.03 | 0.00033186 | 0 | 2.4914 | 0.00038886 | -0.0049514 |  | CFL | AllSpc | 2030 | 0.332 | 2030 | 0.332 | 1.23 | 1.17 | -0.0024391 | 2030 | 0.332 | 2030 | 0.332 | 1.23 | 1.17 | -0.00244
CFLAllSpcSCEAsmExCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCE | Asm | Ex | CZ16 | 2.03 | 0.00033189 | 0 | 2.0011 | 0.00039489 | -0.027211 | 2.03 | 0.00033189 | 0 | 2.0011 | 0.00039489 | -0.027211 |  | CFL | AllSpc | 2030 | 0.332 | 2030 | 0.332 | 0.986 | 1.19 | -0.013404 | 2030 | 0.332 | 2030 | 0.332 | 0.986 | 1.19 | -0.0134
CFLAllSpcSCEAsmExIOU | Com-Iltg-dWatt-CFL_OSspc | SCE | Asm | Ex | IOU | 2.03 | 0.00033192 | 0 | 2.2617 | 0.00040326 | -0.010143 | 2.03 | 0.00033192 | 0 | 2.2617 | 0.00040326 | -0.010143 |  | CFL | AllSpc | 2030 | 0.332 | 2030 | 0.332 | 1.11 | 1.21 | -0.0049966 | 2030 | 0.332 | 2030 | 0.332 | 1.11 | 1.21 | -0.005
CFLAllSpcSCEAsmNewCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCE | Asm | New | CZ05 | 2.03 | 0.000331 | 0 | 2.1 | 0.00039 | -0.0201 | 2.03 | 0.000331 | 0 | 2.1 | 0.00039 | -0.0201 |  | CFL | AllSpc | 2030 | 0.331 | 2030 | 0.331 | 1.03 | 1.18 | -0.0099015 | 2030 | 0.331 | 2030 | 0.331 | 1.03 | 1.18 | -0.0099
CFLAllSpcSCEAsmNewCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCE | Asm | New | CZ06 | 2.03 | 0.000331 | 0 | 2.19 | 0.000405 | -0.0128 | 2.03 | 0.000331 | 0 | 2.19 | 0.000405 | -0.0128 |  | CFL | AllSpc | 2030 | 0.331 | 2030 | 0.331 | 1.08 | 1.22 | -0.0063054 | 2030 | 0.331 | 2030 | 0.331 | 1.08 | 1.22 | -0.00631
CFLAllSpcSCEAsmNewCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCE | Asm | New | CZ08 | 2.03 | 0.000331 | 0 | 2.22 | 0.0004 | -0.00991 | 2.03 | 0.000331 | 0 | 2.22 | 0.0004 | -0.00991 |  | CFL | AllSpc | 2030 | 0.331 | 2030 | 0.331 | 1.09 | 1.21 | -0.0048818 | 2030 | 0.331 | 2030 | 0.331 | 1.09 | 1.21 | -0.00488
CFLAllSpcSCEAsmNewCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCE | Asm | New | CZ09 | 2.03 | 0.000331 | 0 | 2.22 | 0.000423 | -0.0119 | 2.03 | 0.000331 | 0 | 2.22 | 0.000423 | -0.0119 |  | CFL | AllSpc | 2030 | 0.331 | 2030 | 0.331 | 1.09 | 1.28 | -0.0058621 | 2030 | 0.331 | 2030 | 0.331 | 1.09 | 1.28 | -0.00586
CFLAllSpcSCEAsmNewCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCE | Asm | New | CZ10 | 2.03 | 0.000331 | 0 | 2.21 | 0.000409 | -0.0118 | 2.03 | 0.000331 | 0 | 2.21 | 0.000409 | -0.0118 |  | CFL | AllSpc | 2030 | 0.331 | 2030 | 0.331 | 1.09 | 1.24 | -0.0058128 | 2030 | 0.331 | 2030 | 0.331 | 1.09 | 1.24 | -0.00581
CFLAllSpcSCEAsmNewCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCE | Asm | New | CZ13 | 2.03 | 0.000331 | 0 | 2.17 | 0.000413 | -0.0186 | 2.03 | 0.000331 | 0 | 2.17 | 0.000413 | -0.0186 |  | CFL | AllSpc | 2030 | 0.331 | 2030 | 0.331 | 1.07 | 1.25 | -0.0091626 | 2030 | 0.331 | 2030 | 0.331 | 1.07 | 1.25 | -0.00916
CFLAllSpcSCEAsmNewCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCE | Asm | New | CZ14 | 2.03 | 0.000331 | 0 | 2.16 | 0.000393 | -0.0183 | 2.03 | 0.000331 | 0 | 2.16 | 0.000393 | -0.0183 |  | CFL | AllSpc | 2030 | 0.331 | 2030 | 0.331 | 1.06 | 1.19 | -0.0090148 | 2030 | 0.331 | 2030 | 0.331 | 1.06 | 1.19 | -0.00901
CFLAllSpcSCEAsmNewCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCE | Asm | New | CZ15 | 2.03 | 0.000331 | 0 | 2.43 | 0.000412 | -0.00566 | 2.03 | 0.000331 | 0 | 2.43 | 0.000412 | -0.00566 |  | CFL | AllSpc | 2030 | 0.331 | 2030 | 0.331 | 1.2 | 1.24 | -0.0027882 | 2030 | 0.331 | 2030 | 0.331 | 1.2 | 1.24 | -0.00279
CFLAllSpcSCEAsmNewCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCE | Asm | New | CZ16 | 2.03 | 0.000331 | 0 | 2.01 | 0.000394 | -0.0271 | 2.03 | 0.000331 | 0 | 2.01 | 0.000394 | -0.0271 |  | CFL | AllSpc | 2030 | 0.331 | 2030 | 0.331 | 0.99 | 1.19 | -0.01335 | 2030 | 0.331 | 2030 | 0.331 | 0.99 | 1.19 | -0.0134
CFLAllSpcSCEAsmNewIOU | Com-Iltg-dWatt-CFL_OSspc | SCE | Asm | New | IOU | 2.03 | 0.000331 | 0 | 2.2245 | 0.0004069 | -0.011852 | 2.03 | 0.000331 | 0 | 2.2245 | 0.0004069 | -0.011852 |  | CFL | AllSpc | 2030 | 0.331 | 2030 | 0.331 | 1.1 | 1.23 | -0.0058385 | 2030 | 0.331 | 2030 | 0.331 | 1.1 | 1.23 | -0.00584
CFLAllSpcSCEComExCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCE | Com | Ex | CZ05 | 3.1744 | 0.0005591 | 0 | 3.3937 | 0.00069511 | -0.025016 | 3.1744 | 0.0005591 | 0 | 3.3937 | 0.00069511 | -0.025016 |  | CFL | AllSpc | 3170 | 0.559 | 3170 | 0.559 | 1.07 | 1.24 | -0.0078807 | 3170 | 0.559 | 3170 | 0.559 | 1.07 | 1.24 | -0.00788
CFLAllSpcSCEComExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCE | Com | Ex | CZ06 | 2.8391 | 0.00053388 | 0 | 3.1948 | 0.00067016 | -0.010772 | 2.8391 | 0.00053388 | 0 | 3.1948 | 0.00067016 | -0.010772 |  | CFL | AllSpc | 2840 | 0.534 | 2840 | 0.534 | 1.13 | 1.26 | -0.0037941 | 2840 | 0.534 | 2840 | 0.534 | 1.13 | 1.26 | -0.00379
CFLAllSpcSCEComExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCE | Com | Ex | CZ08 | 2.7992 | 0.00053691 | 0 | 3.1395 | 0.0006714 | -0.0095063 | 2.7992 | 0.00053691 | 0 | 3.1395 | 0.0006714 | -0.0095063 |  | CFL | AllSpc | 2800 | 0.537 | 2800 | 0.537 | 1.12 | 1.25 | -0.0033961 | 2800 | 0.537 | 2800 | 0.537 | 1.12 | 1.25 | -0.0034
CFLAllSpcSCEComExCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCE | Com | Ex | CZ09 | 2.8245 | 0.00053858 | 0 | 3.1747 | 0.00068769 | -0.011183 | 2.8245 | 0.00053858 | 0 | 3.1747 | 0.00068769 | -0.011183 |  | CFL | AllSpc | 2820 | 0.539 | 2820 | 0.539 | 1.12 | 1.28 | -0.0039592 | 2820 | 0.539 | 2820 | 0.539 | 1.12 | 1.28 | -0.00396
CFLAllSpcSCEComExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCE | Com | Ex | CZ10 | 2.9251 | 0.00054871 | 0 | 3.1891 | 0.00067862 | -0.011158 | 2.9251 | 0.00054871 | 0 | 3.1891 | 0.00067862 | -0.011158 |  | CFL | AllSpc | 2930 | 0.549 | 2930 | 0.549 | 1.09 | 1.24 | -0.0038144 | 2930 | 0.549 | 2930 | 0.549 | 1.09 | 1.24 | -0.00381
CFLAllSpcSCEComExCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCE | Com | Ex | CZ13 | 2.9604 | 0.00046925 | 0 | 3.3156 | 0.00058628 | -0.01732 | 2.9604 | 0.00046925 | 0 | 3.3156 | 0.00058628 | -0.01732 |  | CFL | AllSpc | 2960 | 0.469 | 2960 | 0.469 | 1.12 | 1.25 | -0.0058505 | 2960 | 0.469 | 2960 | 0.469 | 1.12 | 1.25 | -0.00585
CFLAllSpcSCEComExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCE | Com | Ex | CZ14 | 2.9226 | 0.00056027 | 0 | 3.1705 | 0.00070669 | -0.019211 | 2.9226 | 0.00056027 | 0 | 3.1705 | 0.00070669 | -0.019211 |  | CFL | AllSpc | 2920 | 0.56 | 2920 | 0.56 | 1.08 | 1.26 | -0.0065733 | 2920 | 0.56 | 2920 | 0.56 | 1.08 | 1.26 | -0.00657
CFLAllSpcSCEComExCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCE | Com | Ex | CZ15 | 2.6307 | 0.00050031 | 0 | 3.104 | 0.00063091 | -0.0044814 | 2.6307 | 0.00050031 | 0 | 3.104 | 0.00063091 | -0.0044814 |  | CFL | AllSpc | 2630 | 0.5 | 2630 | 0.5 | 1.18 | 1.26 | -0.0017035 | 2630 | 0.5 | 2630 | 0.5 | 1.18 | 1.26 | -0.0017
CFLAllSpcSCEComExCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCE | Com | Ex | CZ16 | 2.5913 | 0.00042761 | 0 | 2.6075 | 0.00051867 | -0.029493 | 2.5913 | 0.00042761 | 0 | 2.6075 | 0.00051867 | -0.029493 |  | CFL | AllSpc | 2590 | 0.428 | 2590 | 0.428 | 1.01 | 1.21 | -0.011381 | 2590 | 0.428 | 2590 | 0.428 | 1.01 | 1.21 | -0.0114
CFLAllSpcSCEComExIOU | Com-Iltg-dWatt-CFL_OSspc | SCE | Com | Ex | IOU | 2.8349 | 0.00053469 | 0 | 3.162 | 0.00066999 | -0.011057 | 2.8349 | 0.00053469 | 0 | 3.162 | 0.00066999 | -0.011057 |  | CFL | AllSpc | 2830 | 0.535 | 2830 | 0.535 | 1.12 | 1.25 | -0.0039004 | 2830 | 0.535 | 2830 | 0.535 | 1.12 | 1.25 | -0.0039
CFLAllSpcSCEComNewCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCE | Com | New | CZ05 | 3.3072 | 0.00057612 | 0 | 3.4126 | 0.00070495 | -0.027003 | 3.3072 | 0.00057612 | 0 | 3.4126 | 0.00070495 | -0.027003 |  | CFL | AllSpc | 3310 | 0.576 | 3310 | 0.576 | 1.03 | 1.22 | -0.0081647 | 3310 | 0.576 | 3310 | 0.576 | 1.03 | 1.22 | -0.00816
CFLAllSpcSCEComNewCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCE | Com | New | CZ06 | 2.9804 | 0.00054774 | 0 | 3.2574 | 0.00067347 | -0.011293 | 2.9804 | 0.00054774 | 0 | 3.2574 | 0.00067347 | -0.011293 |  | CFL | AllSpc | 2980 | 0.548 | 2980 | 0.548 | 1.09 | 1.23 | -0.0037893 | 2980 | 0.548 | 2980 | 0.548 | 1.09 | 1.23 | -0.00379
CFLAllSpcSCEComNewCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCE | Com | New | CZ08 | 2.9095 | 0.00054455 | 0 | 3.1768 | 0.00066482 | -0.009428 | 2.9095 | 0.00054455 | 0 | 3.1768 | 0.00066482 | -0.009428 |  | CFL | AllSpc | 2910 | 0.545 | 2910 | 0.545 | 1.09 | 1.22 | -0.0032404 | 2910 | 0.545 | 2910 | 0.545 | 1.09 | 1.22 | -0.00324
CFLAllSpcSCEComNewCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCE | Com | New | CZ09 | 2.9259 | 0.00054258 | 0 | 3.2226 | 0.0006964 | -0.010625 | 2.9259 | 0.00054258 | 0 | 3.2226 | 0.0006964 | -0.010625 |  | CFL | AllSpc | 2930 | 0.543 | 2930 | 0.543 | 1.1 | 1.28 | -0.0036315 | 2930 | 0.543 | 2930 | 0.543 | 1.1 | 1.28 | -0.00363
CFLAllSpcSCEComNewCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCE | Com | New | CZ10 | 2.8677 | 0.00053502 | 0 | 3.08 | 0.00066412 | -0.010309 | 2.8677 | 0.00053502 | 0 | 3.08 | 0.00066412 | -0.010309 |  | CFL | AllSpc | 2870 | 0.535 | 2870 | 0.535 | 1.07 | 1.24 | -0.0035948 | 2870 | 0.535 | 2870 | 0.535 | 1.07 | 1.24 | -0.00359
CFLAllSpcSCEComNewCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCE | Com | New | CZ13 | 3.0358 | 0.00048795 | 0 | 3.3883 | 0.00061607 | -0.017217 | 3.0358 | 0.00048795 | 0 | 3.3883 | 0.00061607 | -0.017217 |  | CFL | AllSpc | 3040 | 0.488 | 3040 | 0.488 | 1.12 | 1.26 | -0.0056714 | 3040 | 0.488 | 3040 | 0.488 | 1.12 | 1.26 | -0.00567
CFLAllSpcSCEComNewCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCE | Com | New | CZ14 | 2.9665 | 0.00055701 | 0 | 3.2139 | 0.00071614 | -0.019544 | 2.9665 | 0.00055701 | 0 | 3.2139 | 0.00071614 | -0.019544 |  | CFL | AllSpc | 2970 | 0.557 | 2970 | 0.557 | 1.08 | 1.29 | -0.0065882 | 2970 | 0.557 | 2970 | 0.557 | 1.08 | 1.29 | -0.00659
CFLAllSpcSCEComNewCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCE | Com | New | CZ15 | 2.6295 | 0.00050627 | 0 | 3.0926 | 0.00066706 | -0.0037228 | 2.6295 | 0.00050627 | 0 | 3.0926 | 0.00066706 | -0.0037228 |  | CFL | AllSpc | 2630 | 0.506 | 2630 | 0.506 | 1.18 | 1.32 | -0.0014158 | 2630 | 0.506 | 2630 | 0.506 | 1.18 | 1.32 | -0.00142
CFLAllSpcSCEComNewCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCE | Com | New | CZ16 | 2.6148 | 0.00045373 | 0 | 2.6256 | 0.00055371 | -0.028262 | 2.6148 | 0.00045373 | 0 | 2.6256 | 0.00055371 | -0.028262 |  | CFL | AllSpc | 2610 | 0.454 | 2610 | 0.454 | 1 | 1.22 | -0.010808 | 2610 | 0.454 | 2610 | 0.454 | 1 | 1.22 | -0.0108
CFLAllSpcSCEComNewIOU | Com-Iltg-dWatt-CFL_OSspc | SCE | Com | New | IOU | 2.8897 | 0.00053566 | 0 | 3.1481 | 0.00066733 | -0.010957 | 2.8897 | 0.00053566 | 0 | 3.1481 | 0.00066733 | -0.010957 |  | CFL | AllSpc | 2890 | 0.536 | 2890 | 0.536 | 1.09 | 1.25 | -0.0037917 | 2890 | 0.536 | 2890 | 0.536 | 1.09 | 1.25 | -0.00379
CFLAllSpcSCEECCExCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCE | ECC | Ex | CZ05 | 2.22 | 0.000532 | 0 | 2.4 | 0.00065795 | -0.0262 | 2.22 | 0.000532 | 0 | 2.4 | 0.00065795 | -0.0262 |  | CFL | AllSpc | 2220 | 0.532 | 2220 | 0.532 | 1.08 | 1.24 | -0.011802 | 2220 | 0.532 | 2220 | 0.532 | 1.08 | 1.24 | -0.0118
CFLAllSpcSCEECCExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCE | ECC | Ex | CZ06 | 2.22 | 0.000532 | 0 | 2.55 | 0.00068395 | -0.0124 | 2.22 | 0.000532 | 0 | 2.55 | 0.00068395 | -0.0124 |  | CFL | AllSpc | 2220 | 0.532 | 2220 | 0.532 | 1.15 | 1.29 | -0.0055856 | 2220 | 0.532 | 2220 | 0.532 | 1.15 | 1.29 | -0.00559
CFLAllSpcSCEECCExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCE | ECC | Ex | CZ08 | 2.22 | 0.000532 | 0 | 2.57 | 0.00067995 | -0.0113 | 2.22 | 0.000532 | 0 | 2.57 | 0.00067995 | -0.0113 |  | CFL | AllSpc | 2220 | 0.532 | 2220 | 0.532 | 1.16 | 1.28 | -0.0050901 | 2220 | 0.532 | 2220 | 0.532 | 1.16 | 1.28 | -0.00509
CFLAllSpcSCEECCExCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCE | ECC | Ex | CZ09 | 2.22 | 0.000532 | 0 | 2.56 | 0.00069494 | -0.0129 | 2.22 | 0.000532 | 0 | 2.56 | 0.00069494 | -0.0129 |  | CFL | AllSpc | 2220 | 0.532 | 2220 | 0.532 | 1.15 | 1.31 | -0.0058108 | 2220 | 0.532 | 2220 | 0.532 | 1.15 | 1.31 | -0.00581
CFLAllSpcSCEECCExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCE | ECC | Ex | CZ10 | 2.22 | 0.000532 | 0 | 2.53 | 0.0006869 | -0.0127 | 2.22 | 0.000532 | 0 | 2.53 | 0.0006869 | -0.0127 |  | CFL | AllSpc | 2220 | 0.532 | 2220 | 0.532 | 1.14 | 1.29 | -0.0057207 | 2220 | 0.532 | 2220 | 0.532 | 1.14 | 1.29 | -0.00572
CFLAllSpcSCEECCExCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCE | ECC | Ex | CZ13 | 2.22 | 0.00034588 | 0 | 2.49 | 0.00044788 | -0.0194 | 2.22 | 0.00034588 | 0 | 2.49 | 0.00044788 | -0.0194 |  | CFL | AllSpc | 2220 | 0.346 | 2220 | 0.346 | 1.12 | 1.29 | -0.0087387 | 2220 | 0.346 | 2220 | 0.346 | 1.12 | 1.29 | -0.00874
CFLAllSpcSCEECCExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCE | ECC | Ex | CZ14 | 2.22 | 0.000532 | 0 | 2.48 | 0.000676 | -0.0202 | 2.22 | 0.000532 | 0 | 2.48 | 0.000676 | -0.0202 |  | CFL | AllSpc | 2220 | 0.532 | 2220 | 0.532 | 1.12 | 1.27 | -0.0090991 | 2220 | 0.532 | 2220 | 0.532 | 1.12 | 1.27 | -0.0091
CFLAllSpcSCEECCExCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCE | ECC | Ex | CZ15 | 2.22 | 0.000532 | 0 | 2.73 | 0.0006779 | -0.005591 | 2.22 | 0.000532 | 0 | 2.73 | 0.0006779 | -0.005591 |  | CFL | AllSpc | 2220 | 0.532 | 2220 | 0.532 | 1.23 | 1.27 | -0.0025185 | 2220 | 0.532 | 2220 | 0.532 | 1.23 | 1.27 | -0.00252
CFLAllSpcSCEECCExCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCE | ECC | Ex | CZ16 | 2.22 | 0.0003459 | 0 | 2.31 | 0.0004259 | -0.0366 | 2.22 | 0.0003459 | 0 | 2.31 | 0.0004259 | -0.0366 |  | CFL | AllSpc | 2220 | 0.346 | 2220 | 0.346 | 1.04 | 1.23 | -0.016486 | 2220 | 0.346 | 2220 | 0.346 | 1.04 | 1.23 | -0.0165
CFLAllSpcSCEECCExIOU | Com-Iltg-dWatt-CFL_OSspc | SCE | ECC | Ex | IOU | 2.22 | 0.00051421 | 0 | 2.5406 | 0.00065897 | -0.014061 | 2.22 | 0.00051421 | 0 | 2.5406 | 0.00065897 | -0.014061 |  | CFL | AllSpc | 2220 | 0.514 | 2220 | 0.514 | 1.14 | 1.28 | -0.0063339 | 2220 | 0.514 | 2220 | 0.514 | 1.14 | 1.28 | -0.00633
CFLAllSpcSCEECCNewCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCE | ECC | New | CZ05 | 2.22 | 0.000532 | 0 | 2.36 | 0.000672 | -0.0304 | 2.22 | 0.000532 | 0 | 2.36 | 0.000672 | -0.0304 |  | CFL | AllSpc | 2220 | 0.532 | 2220 | 0.532 | 1.06 | 1.26 | -0.013694 | 2220 | 0.532 | 2220 | 0.532 | 1.06 | 1.26 | -0.0137
CFLAllSpcSCEECCNewCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCE | ECC | New | CZ06 | 2.22 | 0.000532 | 0 | 2.5 | 0.000688 | -0.0158 | 2.22 | 0.000532 | 0 | 2.5 | 0.000688 | -0.0158 |  | CFL | AllSpc | 2220 | 0.532 | 2220 | 0.532 | 1.13 | 1.29 | -0.0071171 | 2220 | 0.532 | 2220 | 0.532 | 1.13 | 1.29 | -0.00712
CFLAllSpcSCEECCNewCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCE | ECC | New | CZ08 | 2.22 | 0.000532 | 0 | 2.52 | 0.000688 | -0.0112 | 2.22 | 0.000532 | 0 | 2.52 | 0.000688 | -0.0112 |  | CFL | AllSpc | 2220 | 0.532 | 2220 | 0.532 | 1.14 | 1.29 | -0.005045 | 2220 | 0.532 | 2220 | 0.532 | 1.14 | 1.29 | -0.00505
CFLAllSpcSCEECCNewCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCE | ECC | New | CZ09 | 2.22 | 0.000532 | 0 | 2.51 | 0.000706 | -0.013 | 2.22 | 0.000532 | 0 | 2.51 | 0.000706 | -0.013 |  | CFL | AllSpc | 2220 | 0.532 | 2220 | 0.532 | 1.13 | 1.33 | -0.0058559 | 2220 | 0.532 | 2220 | 0.532 | 1.13 | 1.33 | -0.00586
CFLAllSpcSCEECCNewCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCE | ECC | New | CZ10 | 2.22 | 0.000532 | 0 | 2.54 | 0.000714 | -0.0129 | 2.22 | 0.000532 | 0 | 2.54 | 0.000714 | -0.0129 |  | CFL | AllSpc | 2220 | 0.532 | 2220 | 0.532 | 1.14 | 1.34 | -0.0058108 | 2220 | 0.532 | 2220 | 0.532 | 1.14 | 1.34 | -0.00581
CFLAllSpcSCEECCNewCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCE | ECC | New | CZ13 | 2.22 | 0.000345 | 0 | 2.51 | 0.000485 | -0.0202 | 2.22 | 0.000345 | 0 | 2.51 | 0.000485 | -0.0202 |  | CFL | AllSpc | 2220 | 0.345 | 2220 | 0.345 | 1.13 | 1.41 | -0.0090991 | 2220 | 0.345 | 2220 | 0.345 | 1.13 | 1.41 | -0.0091
CFLAllSpcSCEECCNewCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCE | ECC | New | CZ14 | 2.22 | 0.000532 | 0 | 2.5 | 0.000692 | -0.021 | 2.22 | 0.000532 | 0 | 2.5 | 0.000692 | -0.021 |  | CFL | AllSpc | 2220 | 0.532 | 2220 | 0.532 | 1.13 | 1.3 | -0.0094595 | 2220 | 0.532 | 2220 | 0.532 | 1.13 | 1.3 | -0.00946
CFLAllSpcSCEECCNewCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCE | ECC | New | CZ15 | 2.22 | 0.000532 | 0 | 2.7 | 0.000711 | -0.00495 | 2.22 | 0.000532 | 0 | 2.7 | 0.000711 | -0.00495 |  | CFL | AllSpc | 2220 | 0.532 | 2220 | 0.532 | 1.22 | 1.34 | -0.0022297 | 2220 | 0.532 | 2220 | 0.532 | 1.22 | 1.34 | -0.00223
CFLAllSpcSCEECCNewCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCE | ECC | New | CZ16 | 2.22 | 0.000345 | 0 | 2.33 | 0.000464 | -0.0378 | 2.22 | 0.000345 | 0 | 2.33 | 0.000464 | -0.0378 |  | CFL | AllSpc | 2220 | 0.345 | 2220 | 0.345 | 1.05 | 1.34 | -0.017027 | 2220 | 0.345 | 2220 | 0.345 | 1.05 | 1.34 | -0.017
CFLAllSpcSCEECCNewIOU | Com-Iltg-dWatt-CFL_OSspc | SCE | ECC | New | IOU | 2.22 | 0.0005014 | 0 | 2.5046 | 0.00065971 | -0.016265 | 2.22 | 0.0005014 | 0 | 2.5046 | 0.00065971 | -0.016265 |  | CFL | AllSpc | 2220 | 0.501 | 2220 | 0.501 | 1.13 | 1.32 | -0.0073265 | 2220 | 0.501 | 2220 | 0.501 | 1.13 | 1.32 | -0.00733
CFLAllSpcSCEEPrExCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCE | EPr | Ex | CZ05 | 2.05 | 0.00054417 | 0 | 2.22 | 0.0006892 | -0.0186 | 2.05 | 0.00054417 | 0 | 2.22 | 0.0006892 | -0.0186 |  | CFL | AllSpc | 2050 | 0.544 | 2050 | 0.544 | 1.08 | 1.27 | -0.0090732 | 2050 | 0.544 | 2050 | 0.544 | 1.08 | 1.27 | -0.00907
CFLAllSpcSCEEPrExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCE | EPr | Ex | CZ06 | 2.05 | 0.00054418 | 0 | 2.36 | 0.00070223 | -0.00915 | 2.05 | 0.00054418 | 0 | 2.36 | 0.00070223 | -0.00915 |  | CFL | AllSpc | 2050 | 0.544 | 2050 | 0.544 | 1.15 | 1.29 | -0.0044634 | 2050 | 0.544 | 2050 | 0.544 | 1.15 | 1.29 | -0.00446
CFLAllSpcSCEEPrExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCE | EPr | Ex | CZ08 | 2.05 | 0.00054418 | 0 | 2.39 | 0.00071223 | -0.00765 | 2.05 | 0.00054418 | 0 | 2.39 | 0.00071223 | -0.00765 |  | CFL | AllSpc | 2050 | 0.544 | 2050 | 0.544 | 1.17 | 1.31 | -0.0037317 | 2050 | 0.544 | 2050 | 0.544 | 1.17 | 1.31 | -0.00373
CFLAllSpcSCEEPrExCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCE | EPr | Ex | CZ09 | 2.05 | 0.00054419 | 0 | 2.36 | 0.00070925 | -0.0094703 | 2.05 | 0.00054419 | 0 | 2.36 | 0.00070925 | -0.0094703 |  | CFL | AllSpc | 2050 | 0.544 | 2050 | 0.544 | 1.15 | 1.3 | -0.0046196 | 2050 | 0.544 | 2050 | 0.544 | 1.15 | 1.3 | -0.00462
CFLAllSpcSCEEPrExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCE | EPr | Ex | CZ10 | 2.05 | 0.00054442 | 0 | 2.29 | 0.00069349 | -0.0104 | 2.05 | 0.00054442 | 0 | 2.29 | 0.00069349 | -0.0104 |  | CFL | AllSpc | 2050 | 0.544 | 2050 | 0.544 | 1.12 | 1.27 | -0.0050732 | 2050 | 0.544 | 2050 | 0.544 | 1.12 | 1.27 | -0.00507
CFLAllSpcSCEEPrExCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCE | EPr | Ex | CZ13 | 2.05 | 1.7313e-05 | 0 | 2.24 | 1.7313e-05 | -0.017 | 2.05 | 1.7313e-05 | 0 | 2.24 | 1.7313e-05 | -0.017 |  | CFL | AllSpc | 2050 | 0.0173 | 2050 | 0.0173 | 1.09 | 1 | -0.0082927 | 2050 | 0.0173 | 2050 | 0.0173 | 1.09 | 1 | -0.00829
CFLAllSpcSCEEPrExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCE | EPr | Ex | CZ14 | 2.05 | 0.00054437 | 0 | 2.22 | 0.00069647 | -0.0169 | 2.05 | 0.00054437 | 0 | 2.22 | 0.00069647 | -0.0169 |  | CFL | AllSpc | 2050 | 0.544 | 2050 | 0.544 | 1.08 | 1.28 | -0.0082439 | 2050 | 0.544 | 2050 | 0.544 | 1.08 | 1.28 | -0.00824
CFLAllSpcSCEEPrExCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCE | EPr | Ex | CZ15 | 2.05 | 0.00054442 | 0 | 2.46 | 0.00069755 | -0.00442 | 2.05 | 0.00054442 | 0 | 2.46 | 0.00069755 | -0.00442 |  | CFL | AllSpc | 2050 | 0.544 | 2050 | 0.544 | 1.2 | 1.28 | -0.0021561 | 2050 | 0.544 | 2050 | 0.544 | 1.2 | 1.28 | -0.00216
CFLAllSpcSCEEPrExCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCE | EPr | Ex | CZ16 | 2.05 | 1.7312e-05 | 0 | 1.98 | 1.7312e-05 | -0.0336 | 2.05 | 1.7312e-05 | 0 | 1.98 | 1.7312e-05 | -0.0336 |  | CFL | AllSpc | 2050 | 0.0173 | 2050 | 0.0173 | 0.966 | 1 | -0.01639 | 2050 | 0.0173 | 2050 | 0.0173 | 0.966 | 1 | -0.0164
CFLAllSpcSCEEPrExIOU | Com-Iltg-dWatt-CFL_OSspc | SCE | EPr | Ex | IOU | 2.05 | 0.00050954 | 0 | 2.3351 | 0.00065924 | -0.01025 | 2.05 | 0.00050954 | 0 | 2.3351 | 0.00065924 | -0.01025 |  | CFL | AllSpc | 2050 | 0.51 | 2050 | 0.51 | 1.14 | 1.29 | -0.0050001 | 2050 | 0.51 | 2050 | 0.51 | 1.14 | 1.29 | -0.005
CFLAllSpcSCEEPrNewCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCE | EPr | New | CZ05 | 2.05 | 0.000551 | 0 | 2.14 | 0.00071 | -0.0202 | 2.05 | 0.000551 | 0 | 2.14 | 0.00071 | -0.0202 |  | CFL | AllSpc | 2050 | 0.551 | 2050 | 0.551 | 1.04 | 1.29 | -0.0098537 | 2050 | 0.551 | 2050 | 0.551 | 1.04 | 1.29 | -0.00985
CFLAllSpcSCEEPrNewCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCE | EPr | New | CZ06 | 2.05 | 0.000551 | 0 | 2.25 | 0.000742 | -0.0129 | 2.05 | 0.000551 | 0 | 2.25 | 0.000742 | -0.0129 |  | CFL | AllSpc | 2050 | 0.551 | 2050 | 0.551 | 1.1 | 1.35 | -0.0062927 | 2050 | 0.551 | 2050 | 0.551 | 1.1 | 1.35 | -0.00629
CFLAllSpcSCEEPrNewCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCE | EPr | New | CZ08 | 2.05 | 0.000551 | 0 | 2.29 | 0.000762 | -0.011 | 2.05 | 0.000551 | 0 | 2.29 | 0.000762 | -0.011 |  | CFL | AllSpc | 2050 | 0.551 | 2050 | 0.551 | 1.12 | 1.38 | -0.0053659 | 2050 | 0.551 | 2050 | 0.551 | 1.12 | 1.38 | -0.00537
CFLAllSpcSCEEPrNewCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCE | EPr | New | CZ09 | 2.05 | 0.000551 | 0 | 2.28 | 0.000778 | -0.0125 | 2.05 | 0.000551 | 0 | 2.28 | 0.000778 | -0.0125 |  | CFL | AllSpc | 2050 | 0.551 | 2050 | 0.551 | 1.11 | 1.41 | -0.0060976 | 2050 | 0.551 | 2050 | 0.551 | 1.11 | 1.41 | -0.0061
CFLAllSpcSCEEPrNewCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCE | EPr | New | CZ10 | 2.05 | 0.000551 | 0 | 2.29 | 0.000791 | -0.0133 | 2.05 | 0.000551 | 0 | 2.29 | 0.000791 | -0.0133 |  | CFL | AllSpc | 2050 | 0.551 | 2050 | 0.551 | 1.12 | 1.44 | -0.0064878 | 2050 | 0.551 | 2050 | 0.551 | 1.12 | 1.44 | -0.00649
CFLAllSpcSCEEPrNewCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCE | EPr | New | CZ13 | 2.05 | 1.75e-05 | 0 | 2.24 | 1.75e-05 | -0.0209 | 2.05 | 1.75e-05 | 0 | 2.24 | 1.75e-05 | -0.0209 |  | CFL | AllSpc | 2050 | 0.0175 | 2050 | 0.0175 | 1.09 | 1 | -0.010195 | 2050 | 0.0175 | 2050 | 0.0175 | 1.09 | 1 | -0.0102
CFLAllSpcSCEEPrNewCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCE | EPr | New | CZ14 | 2.05 | 0.000551 | 0 | 2.24 | 0.000773 | -0.0209 | 2.05 | 0.000551 | 0 | 2.24 | 0.000773 | -0.0209 |  | CFL | AllSpc | 2050 | 0.551 | 2050 | 0.551 | 1.09 | 1.4 | -0.010195 | 2050 | 0.551 | 2050 | 0.551 | 1.09 | 1.4 | -0.0102
CFLAllSpcSCEEPrNewCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCE | EPr | New | CZ15 | 2.05 | 0.000551 | 0 | 2.49 | 0.0008 | -0.00581 | 2.05 | 0.000551 | 0 | 2.49 | 0.0008 | -0.00581 |  | CFL | AllSpc | 2050 | 0.551 | 2050 | 0.551 | 1.21 | 1.45 | -0.0028341 | 2050 | 0.551 | 2050 | 0.551 | 1.21 | 1.45 | -0.00283
CFLAllSpcSCEEPrNewCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCE | EPr | New | CZ16 | 2.05 | 1.75e-05 | 0 | 2.01 | 1.75e-05 | -0.0299 | 2.05 | 1.75e-05 | 0 | 2.01 | 1.75e-05 | -0.0299 |  | CFL | AllSpc | 2050 | 0.0175 | 2050 | 0.0175 | 0.98 | 1 | -0.014585 | 2050 | 0.0175 | 2050 | 0.0175 | 0.98 | 1 | -0.0146
CFLAllSpcSCEEPrNewIOU | Com-Iltg-dWatt-CFL_OSspc | SCE | EPr | New | IOU | 2.05 | 0.00049122 | 0 | 2.2715 | 0.00068965 | -0.014228 | 2.05 | 0.00049122 | 0 | 2.2715 | 0.00068965 | -0.014228 |  | CFL | AllSpc | 2050 | 0.491 | 2050 | 0.491 | 1.11 | 1.4 | -0.0069407 | 2050 | 0.491 | 2050 | 0.491 | 1.11 | 1.4 | -0.00694
CFLAllSpcSCEERCExCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCE | ERC | Ex | CZ05 | 2.39 | 0.0006232 | 0 | 2.48 | 0.00077925 | -0.0243 | 2.39 | 0.0006232 | 0 | 2.48 | 0.00077925 | -0.0243 |  | CFL | AllSpc | 2390 | 0.623 | 2390 | 0.623 | 1.04 | 1.25 | -0.010167 | 2390 | 0.623 | 2390 | 0.623 | 1.04 | 1.25 | -0.0102
CFLAllSpcSCEERCExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCE | ERC | Ex | CZ06 | 2.39 | 0.0006232 | 0 | 2.62 | 0.00078228 | -0.0147 | 2.39 | 0.0006232 | 0 | 2.62 | 0.00078228 | -0.0147 |  | CFL | AllSpc | 2390 | 0.623 | 2390 | 0.623 | 1.1 | 1.26 | -0.0061506 | 2390 | 0.623 | 2390 | 0.623 | 1.1 | 1.26 | -0.00615
CFLAllSpcSCEERCExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCE | ERC | Ex | CZ08 | 2.39 | 0.00062321 | 0 | 2.66 | 0.00079128 | -0.0129 | 2.39 | 0.00062321 | 0 | 2.66 | 0.00079128 | -0.0129 |  | CFL | AllSpc | 2390 | 0.623 | 2390 | 0.623 | 1.11 | 1.27 | -0.0053975 | 2390 | 0.623 | 2390 | 0.623 | 1.11 | 1.27 | -0.0054
CFLAllSpcSCEERCExCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCE | ERC | Ex | CZ09 | 2.39 | 0.00062322 | 0 | 2.66 | 0.0007853 | -0.0145 | 2.39 | 0.00062322 | 0 | 2.66 | 0.0007853 | -0.0145 |  | CFL | AllSpc | 2390 | 0.623 | 2390 | 0.623 | 1.11 | 1.26 | -0.0060669 | 2390 | 0.623 | 2390 | 0.623 | 1.11 | 1.26 | -0.00607
CFLAllSpcSCEERCExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCE | ERC | Ex | CZ10 | 2.39 | 0.00062349 | 0 | 2.63 | 0.00078261 | -0.0149 | 2.39 | 0.00062349 | 0 | 2.63 | 0.00078261 | -0.0149 |  | CFL | AllSpc | 2390 | 0.623 | 2390 | 0.623 | 1.1 | 1.26 | -0.0062343 | 2390 | 0.623 | 2390 | 0.623 | 1.1 | 1.26 | -0.00623
CFLAllSpcSCEERCExCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCE | ERC | Ex | CZ13 | 2.39 | 1.8013e-05 | 0 | 2.58 | 1.8013e-05 | -0.0209 | 2.39 | 1.8013e-05 | 0 | 2.58 | 1.8013e-05 | -0.0209 |  | CFL | AllSpc | 2390 | 0.018 | 2390 | 0.018 | 1.08 | 1 | -0.0087448 | 2390 | 0.018 | 2390 | 0.018 | 1.08 | 1 | -0.00874
CFLAllSpcSCEERCExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCE | ERC | Ex | CZ14 | 2.39 | 0.00062342 | 0 | 2.61 | 0.00079453 | -0.0198 | 2.39 | 0.00062342 | 0 | 2.61 | 0.00079453 | -0.0198 |  | CFL | AllSpc | 2390 | 0.623 | 2390 | 0.623 | 1.09 | 1.27 | -0.0082845 | 2390 | 0.623 | 2390 | 0.623 | 1.09 | 1.27 | -0.00828
CFLAllSpcSCEERCExCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCE | ERC | Ex | CZ15 | 2.39 | 0.00062349 | 0 | 2.82 | 0.00080467 | -0.0072 | 2.39 | 0.00062349 | 0 | 2.82 | 0.00080467 | -0.0072 |  | CFL | AllSpc | 2390 | 0.623 | 2390 | 0.623 | 1.18 | 1.29 | -0.0030126 | 2390 | 0.623 | 2390 | 0.623 | 1.18 | 1.29 | -0.00301
CFLAllSpcSCEERCExCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCE | ERC | Ex | CZ16 | 2.39 | 1.8012e-05 | 0 | 2.37 | 1.8012e-05 | -0.0353 | 2.39 | 1.8012e-05 | 0 | 2.37 | 1.8012e-05 | -0.0353 |  | CFL | AllSpc | 2390 | 0.018 | 2390 | 0.018 | 0.992 | 1 | -0.01477 | 2390 | 0.018 | 2390 | 0.018 | 0.992 | 1 | -0.0148
CFLAllSpcSCEERCExIOU | Com-Iltg-dWatt-CFL_OSspc | SCE | ERC | Ex | IOU | 2.39 | 0.00058342 | 0 | 2.6363 | 0.00073638 | -0.015053 | 2.39 | 0.00058342 | 0 | 2.6363 | 0.00073638 | -0.015053 |  | CFL | AllSpc | 2390 | 0.583 | 2390 | 0.583 | 1.1 | 1.26 | -0.0062985 | 2390 | 0.583 | 2390 | 0.583 | 1.1 | 1.26 | -0.0063
CFLAllSpcSCEERCNewCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCE | ERC | New | CZ05 | 2.39 | 0.000631 | 0 | 2.59 | 0.00085 | -0.025 | 2.39 | 0.000631 | 0 | 2.59 | 0.00085 | -0.025 |  | CFL | AllSpc | 2390 | 0.631 | 2390 | 0.631 | 1.08 | 1.35 | -0.01046 | 2390 | 0.631 | 2390 | 0.631 | 1.08 | 1.35 | -0.0105
CFLAllSpcSCEERCNewCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCE | ERC | New | CZ06 | 2.39 | 0.000631 | 0 | 2.72 | 0.000813 | -0.0161 | 2.39 | 0.000631 | 0 | 2.72 | 0.000813 | -0.0161 |  | CFL | AllSpc | 2390 | 0.631 | 2390 | 0.631 | 1.14 | 1.29 | -0.0067364 | 2390 | 0.631 | 2390 | 0.631 | 1.14 | 1.29 | -0.00674
CFLAllSpcSCEERCNewCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCE | ERC | New | CZ08 | 2.39 | 0.000631 | 0 | 2.76 | 0.000833 | -0.014 | 2.39 | 0.000631 | 0 | 2.76 | 0.000833 | -0.014 |  | CFL | AllSpc | 2390 | 0.631 | 2390 | 0.631 | 1.15 | 1.32 | -0.0058577 | 2390 | 0.631 | 2390 | 0.631 | 1.15 | 1.32 | -0.00586
CFLAllSpcSCEERCNewCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCE | ERC | New | CZ09 | 2.39 | 0.000631 | 0 | 2.77 | 0.000855 | -0.0151 | 2.39 | 0.000631 | 0 | 2.77 | 0.000855 | -0.0151 |  | CFL | AllSpc | 2390 | 0.631 | 2390 | 0.631 | 1.16 | 1.35 | -0.006318 | 2390 | 0.631 | 2390 | 0.631 | 1.16 | 1.35 | -0.00632
CFLAllSpcSCEERCNewCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCE | ERC | New | CZ10 | 2.39 | 0.000631 | 0 | 2.78 | 0.000871 | -0.0159 | 2.39 | 0.000631 | 0 | 2.78 | 0.000871 | -0.0159 |  | CFL | AllSpc | 2390 | 0.631 | 2390 | 0.631 | 1.16 | 1.38 | -0.0066527 | 2390 | 0.631 | 2390 | 0.631 | 1.16 | 1.38 | -0.00665
CFLAllSpcSCEERCNewCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCE | ERC | New | CZ13 | 2.39 | 1.82e-05 | 0 | 2.74 | 1.82e-05 | -0.0233 | 2.39 | 1.82e-05 | 0 | 2.74 | 1.82e-05 | -0.0233 |  | CFL | AllSpc | 2390 | 0.0182 | 2390 | 0.0182 | 1.15 | 1 | -0.009749 | 2390 | 0.0182 | 2390 | 0.0182 | 1.15 | 1 | -0.00975
CFLAllSpcSCEERCNewCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCE | ERC | New | CZ14 | 2.39 | 0.000631 | 0 | 2.74 | 0.000858 | -0.0231 | 2.39 | 0.000631 | 0 | 2.74 | 0.000858 | -0.0231 |  | CFL | AllSpc | 2390 | 0.631 | 2390 | 0.631 | 1.15 | 1.36 | -0.0096653 | 2390 | 0.631 | 2390 | 0.631 | 1.15 | 1.36 | -0.00967
CFLAllSpcSCEERCNewCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCE | ERC | New | CZ15 | 2.39 | 0.000631 | 0 | 3.03 | 0.000873 | -0.00797 | 2.39 | 0.000631 | 0 | 3.03 | 0.000873 | -0.00797 |  | CFL | AllSpc | 2390 | 0.631 | 2390 | 0.631 | 1.27 | 1.38 | -0.0033347 | 2390 | 0.631 | 2390 | 0.631 | 1.27 | 1.38 | -0.00333
CFLAllSpcSCEERCNewCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCE | ERC | New | CZ16 | 2.39 | 1.82e-05 | 0 | 2.45 | 1.82e-05 | -0.0408 | 2.39 | 1.82e-05 | 0 | 2.45 | 1.82e-05 | -0.0408 |  | CFL | AllSpc | 2390 | 0.0182 | 2390 | 0.0182 | 1.03 | 1 | -0.017071 | 2390 | 0.0182 | 2390 | 0.0182 | 1.03 | 1 | -0.0171
CFLAllSpcSCEERCNewIOU | Com-Iltg-dWatt-CFL_OSspc | SCE | ERC | New | IOU | 2.39 | 0.00056233 | 0 | 2.7558 | 0.00075764 | -0.017254 | 2.39 | 0.00056233 | 0 | 2.7558 | 0.00075764 | -0.017254 |  | CFL | AllSpc | 2390 | 0.562 | 2390 | 0.562 | 1.15 | 1.35 | -0.0072192 | 2390 | 0.562 | 2390 | 0.562 | 1.15 | 1.35 | -0.00722
CFLAllSpcSCEESeExCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCE | ESe | Ex | CZ05 | 2.12 | 0.0006202 | 0 | 2.25 | 0.00076825 | -0.0238 | 2.12 | 0.0006202 | 0 | 2.25 | 0.00076825 | -0.0238 |  | CFL | AllSpc | 2120 | 0.62 | 2120 | 0.62 | 1.06 | 1.24 | -0.011226 | 2120 | 0.62 | 2120 | 0.62 | 1.06 | 1.24 | -0.0112
CFLAllSpcSCEESeExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCE | ESe | Ex | CZ06 | 2.12 | 0.0006202 | 0 | 2.42 | 0.00080025 | -0.0126 | 2.12 | 0.0006202 | 0 | 2.42 | 0.00080025 | -0.0126 |  | CFL | AllSpc | 2120 | 0.62 | 2120 | 0.62 | 1.14 | 1.29 | -0.0059434 | 2120 | 0.62 | 2120 | 0.62 | 1.14 | 1.29 | -0.00594
CFLAllSpcSCEESeExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCE | ESe | Ex | CZ08 | 2.12 | 0.00062021 | 0 | 2.44 | 0.00079623 | -0.0109 | 2.12 | 0.00062021 | 0 | 2.44 | 0.00079623 | -0.0109 |  | CFL | AllSpc | 2120 | 0.62 | 2120 | 0.62 | 1.15 | 1.28 | -0.0051415 | 2120 | 0.62 | 2120 | 0.62 | 1.15 | 1.28 | -0.00514
CFLAllSpcSCEESeExCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCE | ESe | Ex | CZ09 | 2.12 | 0.00062022 | 0 | 2.42 | 0.00079628 | -0.0126 | 2.12 | 0.00062022 | 0 | 2.42 | 0.00079628 | -0.0126 |  | CFL | AllSpc | 2120 | 0.62 | 2120 | 0.62 | 1.14 | 1.28 | -0.0059434 | 2120 | 0.62 | 2120 | 0.62 | 1.14 | 1.28 | -0.00594
CFLAllSpcSCEESeExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCE | ESe | Ex | CZ10 | 2.12 | 0.00062048 | 0 | 2.36 | 0.00078461 | -0.0137 | 2.12 | 0.00062048 | 0 | 2.36 | 0.00078461 | -0.0137 |  | CFL | AllSpc | 2120 | 0.62 | 2120 | 0.62 | 1.11 | 1.26 | -0.0064623 | 2120 | 0.62 | 2120 | 0.62 | 1.11 | 1.26 | -0.00646
CFLAllSpcSCEESeExCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCE | ESe | Ex | CZ13 | 2.12 | 1.732e-05 | 0 | 2.33 | 1.732e-05 | -0.0206 | 2.12 | 1.732e-05 | 0 | 2.33 | 1.732e-05 | -0.0206 |  | CFL | AllSpc | 2120 | 0.0173 | 2120 | 0.0173 | 1.1 | 1 | -0.009717 | 2120 | 0.0173 | 2120 | 0.0173 | 1.1 | 1 | -0.00972
CFLAllSpcSCEESeExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCE | ESe | Ex | CZ14 | 2.12 | 0.00062042 | 0 | 2.31 | 0.00075947 | -0.0209 | 2.12 | 0.00062042 | 0 | 2.31 | 0.00075947 | -0.0209 |  | CFL | AllSpc | 2120 | 0.62 | 2120 | 0.62 | 1.09 | 1.22 | -0.0098585 | 2120 | 0.62 | 2120 | 0.62 | 1.09 | 1.22 | -0.00986
CFLAllSpcSCEESeExCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCE | ESe | Ex | CZ15 | 2.12 | 0.00062048 | 0 | 2.57 | 0.00078161 | -0.0062 | 2.12 | 0.00062048 | 0 | 2.57 | 0.00078161 | -0.0062 |  | CFL | AllSpc | 2120 | 0.62 | 2120 | 0.62 | 1.21 | 1.26 | -0.0029245 | 2120 | 0.62 | 2120 | 0.62 | 1.21 | 1.26 | -0.00292
CFLAllSpcSCEESeExCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCE | ESe | Ex | CZ16 | 2.12 | 1.7318e-05 | 0 | 2.07 | 1.7318e-05 | -0.0355 | 2.12 | 1.7318e-05 | 0 | 2.07 | 1.7318e-05 | -0.0355 |  | CFL | AllSpc | 2120 | 0.0173 | 2120 | 0.0173 | 0.976 | 1 | -0.016745 | 2120 | 0.0173 | 2120 | 0.0173 | 0.976 | 1 | -0.0167
CFLAllSpcSCEESeExIOU | Com-Iltg-dWatt-CFL_OSspc | SCE | ESe | Ex | IOU | 2.12 | 0.00058057 | 0 | 2.3984 | 0.00074105 | -0.013523 | 2.12 | 0.00058057 | 0 | 2.3984 | 0.00074105 | -0.013523 |  | CFL | AllSpc | 2120 | 0.581 | 2120 | 0.581 | 1.13 | 1.28 | -0.0063787 | 2120 | 0.581 | 2120 | 0.581 | 1.13 | 1.28 | -0.00638
CFLAllSpcSCEESeNewCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCE | ESe | New | CZ05 | 2.12 | 0.000628 | 0 | 2.21 | 0.000788 | -0.0221 | 2.12 | 0.000628 | 0 | 2.21 | 0.000788 | -0.0221 |  | CFL | AllSpc | 2120 | 0.628 | 2120 | 0.628 | 1.04 | 1.25 | -0.010425 | 2120 | 0.628 | 2120 | 0.628 | 1.04 | 1.25 | -0.0104
CFLAllSpcSCEESeNewCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCE | ESe | New | CZ06 | 2.12 | 0.000628 | 0 | 2.34 | 0.000836 | -0.0158 | 2.12 | 0.000628 | 0 | 2.34 | 0.000836 | -0.0158 |  | CFL | AllSpc | 2120 | 0.628 | 2120 | 0.628 | 1.1 | 1.33 | -0.0074528 | 2120 | 0.628 | 2120 | 0.628 | 1.1 | 1.33 | -0.00745
CFLAllSpcSCEESeNewCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCE | ESe | New | CZ08 | 2.12 | 0.000628 | 0 | 2.37 | 0.000845 | -0.0129 | 2.12 | 0.000628 | 0 | 2.37 | 0.000845 | -0.0129 |  | CFL | AllSpc | 2120 | 0.628 | 2120 | 0.628 | 1.12 | 1.35 | -0.0060849 | 2120 | 0.628 | 2120 | 0.628 | 1.12 | 1.35 | -0.00608
CFLAllSpcSCEESeNewCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCE | ESe | New | CZ09 | 2.12 | 0.000628 | 0 | 2.37 | 0.000874 | -0.0151 | 2.12 | 0.000628 | 0 | 2.37 | 0.000874 | -0.0151 |  | CFL | AllSpc | 2120 | 0.628 | 2120 | 0.628 | 1.12 | 1.39 | -0.0071226 | 2120 | 0.628 | 2120 | 0.628 | 1.12 | 1.39 | -0.00712
CFLAllSpcSCEESeNewCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCE | ESe | New | CZ10 | 2.12 | 0.000628 | 0 | 2.39 | 0.000886 | -0.0162 | 2.12 | 0.000628 | 0 | 2.39 | 0.000886 | -0.0162 |  | CFL | AllSpc | 2120 | 0.628 | 2120 | 0.628 | 1.13 | 1.41 | -0.0076415 | 2120 | 0.628 | 2120 | 0.628 | 1.13 | 1.41 | -0.00764
CFLAllSpcSCEESeNewCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCE | ESe | New | CZ13 | 2.12 | 1.76e-05 | 0 | 2.37 | 1.76e-05 | -0.0238 | 2.12 | 1.76e-05 | 0 | 2.37 | 1.76e-05 | -0.0238 |  | CFL | AllSpc | 2120 | 0.0176 | 2120 | 0.0176 | 1.12 | 1 | -0.011226 | 2120 | 0.0176 | 2120 | 0.0176 | 1.12 | 1 | -0.0112
CFLAllSpcSCEESeNewCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCE | ESe | New | CZ14 | 2.12 | 0.000628 | 0 | 2.35 | 0.000868 | -0.0236 | 2.12 | 0.000628 | 0 | 2.35 | 0.000868 | -0.0236 |  | CFL | AllSpc | 2120 | 0.628 | 2120 | 0.628 | 1.11 | 1.38 | -0.011132 | 2120 | 0.628 | 2120 | 0.628 | 1.11 | 1.38 | -0.0111
CFLAllSpcSCEESeNewCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCE | ESe | New | CZ15 | 2.12 | 0.000628 | 0 | 2.64 | 0.000878 | -0.00707 | 2.12 | 0.000628 | 0 | 2.64 | 0.000878 | -0.00707 |  | CFL | AllSpc | 2120 | 0.628 | 2120 | 0.628 | 1.25 | 1.4 | -0.0033349 | 2120 | 0.628 | 2120 | 0.628 | 1.25 | 1.4 | -0.00333
CFLAllSpcSCEESeNewCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCE | ESe | New | CZ16 | 2.12 | 1.76e-05 | 0 | 2.11 | 1.76e-05 | -0.0295 | 2.12 | 1.76e-05 | 0 | 2.11 | 1.76e-05 | -0.0295 |  | CFL | AllSpc | 2120 | 0.0176 | 2120 | 0.0176 | 0.995 | 1 | -0.013915 | 2120 | 0.0176 | 2120 | 0.0176 | 0.995 | 1 | -0.0139
CFLAllSpcSCEESeNewIOU | Com-Iltg-dWatt-CFL_OSspc | SCE | ESe | New | IOU | 2.12 | 0.0005596 | 0 | 2.3693 | 0.00077096 | -0.016687 | 2.12 | 0.0005596 | 0 | 2.3693 | 0.00077096 | -0.016687 |  | CFL | AllSpc | 2120 | 0.56 | 2120 | 0.56 | 1.12 | 1.38 | -0.0078714 | 2120 | 0.56 | 2120 | 0.56 | 1.12 | 1.38 | -0.00787
CFLAllSpcSCEEUnExCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCE | EUn | Ex | CZ05 | 2.17 | 0.00054995 | 0 | 2.4005 | 0.00066895 | -0.0154 | 2.17 | 0.00054995 | 0 | 2.4005 | 0.00066895 | -0.0154 |  | CFL | AllSpc | 2170 | 0.55 | 2170 | 0.55 | 1.11 | 1.22 | -0.0070968 | 2170 | 0.55 | 2170 | 0.55 | 1.11 | 1.22 | -0.0071
CFLAllSpcSCEEUnExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCE | EUn | Ex | CZ06 | 2.17 | 0.00054995 | 0 | 2.51 | 0.000696 | -0.0088505 | 2.17 | 0.00054995 | 0 | 2.51 | 0.000696 | -0.0088505 |  | CFL | AllSpc | 2170 | 0.55 | 2170 | 0.55 | 1.16 | 1.27 | -0.0040786 | 2170 | 0.55 | 2170 | 0.55 | 1.16 | 1.27 | -0.00408
CFLAllSpcSCEEUnExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCE | EUn | Ex | CZ08 | 2.17 | 0.00054995 | 0 | 2.5205 | 0.00069795 | -0.0085505 | 2.17 | 0.00054995 | 0 | 2.5205 | 0.00069795 | -0.0085505 |  | CFL | AllSpc | 2170 | 0.55 | 2170 | 0.55 | 1.16 | 1.27 | -0.0039403 | 2170 | 0.55 | 2170 | 0.55 | 1.16 | 1.27 | -0.00394
CFLAllSpcSCEEUnExCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCE | EUn | Ex | CZ09 | 2.17 | 0.00054994 | 0 | 2.51 | 0.000707 | -0.0096305 | 2.17 | 0.00054994 | 0 | 2.51 | 0.000707 | -0.0096305 |  | CFL | AllSpc | 2170 | 0.55 | 2170 | 0.55 | 1.16 | 1.29 | -0.004438 | 2170 | 0.55 | 2170 | 0.55 | 1.16 | 1.29 | -0.00444
CFLAllSpcSCEEUnExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCE | EUn | Ex | CZ10 | 2.17 | 0.0005499 | 0 | 2.49 | 0.0007029 | -0.008871 | 2.17 | 0.0005499 | 0 | 2.49 | 0.0007029 | -0.008871 |  | CFL | AllSpc | 2170 | 0.55 | 2170 | 0.55 | 1.15 | 1.28 | -0.004088 | 2170 | 0.55 | 2170 | 0.55 | 1.15 | 1.28 | -0.00409
CFLAllSpcSCEEUnExCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCE | EUn | Ex | CZ13 | 2.17 | 0.00036088 | 0 | 2.45 | 0.000454 | -0.0119 | 2.17 | 0.00036088 | 0 | 2.45 | 0.000454 | -0.0119 |  | CFL | AllSpc | 2170 | 0.361 | 2170 | 0.361 | 1.13 | 1.26 | -0.0054839 | 2170 | 0.361 | 2170 | 0.361 | 1.13 | 1.26 | -0.00548
CFLAllSpcSCEEUnExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCE | EUn | Ex | CZ14 | 2.17 | 0.00054991 | 0 | 2.45 | 0.00069791 | -0.0131 | 2.17 | 0.00054991 | 0 | 2.45 | 0.00069791 | -0.0131 |  | CFL | AllSpc | 2170 | 0.55 | 2170 | 0.55 | 1.13 | 1.27 | -0.0060369 | 2170 | 0.55 | 2170 | 0.55 | 1.13 | 1.27 | -0.00604
CFLAllSpcSCEEUnExCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCE | EUn | Ex | CZ15 | 2.17 | 0.0005499 | 0 | 2.6 | 0.0007049 | -0.004681 | 2.17 | 0.0005499 | 0 | 2.6 | 0.0007049 | -0.004681 |  | CFL | AllSpc | 2170 | 0.55 | 2170 | 0.55 | 1.2 | 1.28 | -0.0021571 | 2170 | 0.55 | 2170 | 0.55 | 1.2 | 1.28 | -0.00216
CFLAllSpcSCEEUnExCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCE | EUn | Ex | CZ16 | 2.17 | 0.0003609 | 0 | 2.281 | 0.0004399 | -0.0252 | 2.17 | 0.0003609 | 0 | 2.281 | 0.0004399 | -0.0252 |  | CFL | AllSpc | 2170 | 0.361 | 2170 | 0.361 | 1.05 | 1.22 | -0.011613 | 2170 | 0.361 | 2170 | 0.361 | 1.05 | 1.22 | -0.0116
CFLAllSpcSCEEUnExIOU | Com-Iltg-dWatt-CFL_OSspc | SCE | EUn | Ex | IOU | 2.17 | 0.00053187 | 0 | 2.4943 | 0.00067468 | -0.010099 | 2.17 | 0.00053187 | 0 | 2.4943 | 0.00067468 | -0.010099 |  | CFL | AllSpc | 2170 | 0.532 | 2170 | 0.532 | 1.15 | 1.27 | -0.0046538 | 2170 | 0.532 | 2170 | 0.532 | 1.15 | 1.27 | -0.00465
CFLAllSpcSCEEUnNewCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCE | EUn | New | CZ05 | 2.17 | 0.000549 | 0 | 2.36 | 0.000679 | -0.0142 | 2.17 | 0.000549 | 0 | 2.36 | 0.000679 | -0.0142 |  | CFL | AllSpc | 2170 | 0.549 | 2170 | 0.549 | 1.09 | 1.24 | -0.0065438 | 2170 | 0.549 | 2170 | 0.549 | 1.09 | 1.24 | -0.00654
CFLAllSpcSCEEUnNewCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCE | EUn | New | CZ06 | 2.17 | 0.000549 | 0 | 2.49 | 0.000697 | -0.00643 | 2.17 | 0.000549 | 0 | 2.49 | 0.000697 | -0.00643 |  | CFL | AllSpc | 2170 | 0.549 | 2170 | 0.549 | 1.15 | 1.27 | -0.0029631 | 2170 | 0.549 | 2170 | 0.549 | 1.15 | 1.27 | -0.00296
CFLAllSpcSCEEUnNewCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCE | EUn | New | CZ08 | 2.17 | 0.000549 | 0 | 2.51 | 0.000707 | -0.00569 | 2.17 | 0.000549 | 0 | 2.51 | 0.000707 | -0.00569 |  | CFL | AllSpc | 2170 | 0.549 | 2170 | 0.549 | 1.16 | 1.29 | -0.0026221 | 2170 | 0.549 | 2170 | 0.549 | 1.16 | 1.29 | -0.00262
CFLAllSpcSCEEUnNewCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCE | EUn | New | CZ09 | 2.17 | 0.000549 | 0 | 2.52 | 0.00073 | -0.00656 | 2.17 | 0.000549 | 0 | 2.52 | 0.00073 | -0.00656 |  | CFL | AllSpc | 2170 | 0.549 | 2170 | 0.549 | 1.16 | 1.33 | -0.003023 | 2170 | 0.549 | 2170 | 0.549 | 1.16 | 1.33 | -0.00302
CFLAllSpcSCEEUnNewCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCE | EUn | New | CZ10 | 2.17 | 0.000549 | 0 | 2.53 | 0.000732 | -0.00695 | 2.17 | 0.000549 | 0 | 2.53 | 0.000732 | -0.00695 |  | CFL | AllSpc | 2170 | 0.549 | 2170 | 0.549 | 1.17 | 1.33 | -0.0032028 | 2170 | 0.549 | 2170 | 0.549 | 1.17 | 1.33 | -0.0032
CFLAllSpcSCEEUnNewCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCE | EUn | New | CZ13 | 2.17 | 0.00036 | 0 | 2.55 | 0.000518 | -0.0142 | 2.17 | 0.00036 | 0 | 2.55 | 0.000518 | -0.0142 |  | CFL | AllSpc | 2170 | 0.36 | 2170 | 0.36 | 1.18 | 1.44 | -0.0065438 | 2170 | 0.36 | 2170 | 0.36 | 1.18 | 1.44 | -0.00654
CFLAllSpcSCEEUnNewCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCE | EUn | New | CZ14 | 2.17 | 0.000549 | 0 | 2.4 | 0.000669 | -0.0116 | 2.17 | 0.000549 | 0 | 2.4 | 0.000669 | -0.0116 |  | CFL | AllSpc | 2170 | 0.549 | 2170 | 0.549 | 1.11 | 1.22 | -0.0053456 | 2170 | 0.549 | 2170 | 0.549 | 1.11 | 1.22 | -0.00535
CFLAllSpcSCEEUnNewCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCE | EUn | New | CZ15 | 2.17 | 0.000549 | 0 | 2.67 | 0.000743 | -0.00298 | 2.17 | 0.000549 | 0 | 2.67 | 0.000743 | -0.00298 |  | CFL | AllSpc | 2170 | 0.549 | 2170 | 0.549 | 1.23 | 1.35 | -0.0013733 | 2170 | 0.549 | 2170 | 0.549 | 1.23 | 1.35 | -0.00137
CFLAllSpcSCEEUnNewCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCE | EUn | New | CZ16 | 2.17 | 0.00036 | 0 | 2.29 | 0.000465 | -0.0254 | 2.17 | 0.00036 | 0 | 2.29 | 0.000465 | -0.0254 |  | CFL | AllSpc | 2170 | 0.36 | 2170 | 0.36 | 1.06 | 1.29 | -0.011705 | 2170 | 0.36 | 2170 | 0.36 | 1.06 | 1.29 | -0.0117
CFLAllSpcSCEEUnNewIOU | Com-Iltg-dWatt-CFL_OSspc | SCE | EUn | New | IOU | 2.17 | 0.00051807 | 0 | 2.4886 | 0.00067381 | -0.0090246 | 2.17 | 0.00051807 | 0 | 2.4886 | 0.00067381 | -0.0090246 |  | CFL | AllSpc | 2170 | 0.518 | 2170 | 0.518 | 1.15 | 1.3 | -0.0041588 | 2170 | 0.518 | 2170 | 0.518 | 1.15 | 1.3 | -0.00416
CFLAllSpcSCEGroExCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCE | Gro | Ex | CZ05 | 3.8 | 0.00047888 | 0 | 3.64 | 0.00059888 | -0.066194 | 3.8 | 0.00047888 | 0 | 3.64 | 0.00059888 | -0.066194 |  | CFL | AllSpc | 3800 | 0.479 | 3800 | 0.479 | 0.958 | 1.25 | -0.017419 | 3800 | 0.479 | 3800 | 0.479 | 0.958 | 1.25 | -0.0174
CFLAllSpcSCEGroExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCE | Gro | Ex | CZ06 | 3.8 | 0.00047888 | 0 | 3.8594 | 0.00060288 | -0.053294 | 3.8 | 0.00047888 | 0 | 3.8594 | 0.00060288 | -0.053294 |  | CFL | AllSpc | 3800 | 0.479 | 3800 | 0.479 | 1.02 | 1.26 | -0.014025 | 3800 | 0.479 | 3800 | 0.479 | 1.02 | 1.26 | -0.014
CFLAllSpcSCEGroExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCE | Gro | Ex | CZ08 | 3.8 | 0.00047888 | 0 | 3.95 | 0.00061987 | -0.0483 | 3.8 | 0.00047888 | 0 | 3.95 | 0.00061987 | -0.0483 |  | CFL | AllSpc | 3800 | 0.479 | 3800 | 0.479 | 1.04 | 1.29 | -0.012711 | 3800 | 0.479 | 3800 | 0.479 | 1.04 | 1.29 | -0.0127
CFLAllSpcSCEGroExCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCE | Gro | Ex | CZ09 | 3.8 | 0.00047887 | 0 | 3.99 | 0.00062594 | -0.047194 | 3.8 | 0.00047887 | 0 | 3.99 | 0.00062594 | -0.047194 |  | CFL | AllSpc | 3800 | 0.479 | 3800 | 0.479 | 1.05 | 1.31 | -0.012419 | 3800 | 0.479 | 3800 | 0.479 | 1.05 | 1.31 | -0.0124
CFLAllSpcSCEGroExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCE | Gro | Ex | CZ10 | 3.8 | 0.00047878 | 0 | 3.9789 | 0.00064078 | -0.046 | 3.8 | 0.00047878 | 0 | 3.9789 | 0.00064078 | -0.046 |  | CFL | AllSpc | 3800 | 0.479 | 3800 | 0.479 | 1.05 | 1.34 | -0.012105 | 3800 | 0.479 | 3800 | 0.479 | 1.05 | 1.34 | -0.0121
CFLAllSpcSCEGroExCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCE | Gro | Ex | CZ13 | 3.8 | 0.00047881 | 0 | 3.99 | 0.0006328 | -0.04529 | 3.8 | 0.00047881 | 0 | 3.99 | 0.0006328 | -0.04529 |  | CFL | AllSpc | 3800 | 0.479 | 3800 | 0.479 | 1.05 | 1.32 | -0.011918 | 3800 | 0.479 | 3800 | 0.479 | 1.05 | 1.32 | -0.0119
CFLAllSpcSCEGroExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCE | Gro | Ex | CZ14 | 3.8 | 0.00047879 | 0 | 3.97 | 0.00065279 | -0.0464 | 3.8 | 0.00047879 | 0 | 3.97 | 0.00065279 | -0.0464 |  | CFL | AllSpc | 3800 | 0.479 | 3800 | 0.479 | 1.04 | 1.36 | -0.012211 | 3800 | 0.479 | 3800 | 0.479 | 1.04 | 1.36 | -0.0122
CFLAllSpcSCEGroExCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCE | Gro | Ex | CZ15 | 3.8 | 0.00047878 | 0 | 4.28 | 0.00063789 | -0.0266 | 3.8 | 0.00047878 | 0 | 4.28 | 0.00063789 | -0.0266 |  | CFL | AllSpc | 3800 | 0.479 | 3800 | 0.479 | 1.13 | 1.33 | -0.007 | 3800 | 0.479 | 3800 | 0.479 | 1.13 | 1.33 | -0.007
CFLAllSpcSCEGroExCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCE | Gro | Ex | CZ16 | 3.8 | 0.00047879 | 0 | 3.61 | 0.0006029 | -0.06199 | 3.8 | 0.00047879 | 0 | 3.61 | 0.0006029 | -0.06199 |  | CFL | AllSpc | 3800 | 0.479 | 3800 | 0.479 | 0.95 | 1.26 | -0.016313 | 3800 | 0.479 | 3800 | 0.479 | 0.95 | 1.26 | -0.0163
CFLAllSpcSCEGroExIOU | Com-Iltg-dWatt-CFL_OSspc | SCE | Gro | Ex | IOU | 3.8 | 0.00047884 | 0 | 3.9471 | 0.00062392 | -0.048189 | 3.8 | 0.00047884 | 0 | 3.9471 | 0.00062392 | -0.048189 |  | CFL | AllSpc | 3800 | 0.479 | 3800 | 0.479 | 1.04 | 1.3 | -0.012681 | 3800 | 0.479 | 3800 | 0.479 | 1.04 | 1.3 | -0.0127
CFLAllSpcSCEGroNewCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCE | Gro | New | CZ05 | 3.8 | 0.000477 | 0 | 3.73 | 0.000603 | -0.0634 | 3.8 | 0.000477 | 0 | 3.73 | 0.000603 | -0.0634 |  | CFL | AllSpc | 3800 | 0.477 | 3800 | 0.477 | 0.982 | 1.26 | -0.016684 | 3800 | 0.477 | 3800 | 0.477 | 0.982 | 1.26 | -0.0167
CFLAllSpcSCEGroNewCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCE | Gro | New | CZ06 | 3.8 | 0.000477 | 0 | 4 | 0.000606 | -0.0452 | 3.8 | 0.000477 | 0 | 4 | 0.000606 | -0.0452 |  | CFL | AllSpc | 3800 | 0.477 | 3800 | 0.477 | 1.05 | 1.27 | -0.011895 | 3800 | 0.477 | 3800 | 0.477 | 1.05 | 1.27 | -0.0119
CFLAllSpcSCEGroNewCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCE | Gro | New | CZ08 | 3.8 | 0.000477 | 0 | 4.05 | 0.000617 | -0.0395 | 3.8 | 0.000477 | 0 | 4.05 | 0.000617 | -0.0395 |  | CFL | AllSpc | 3800 | 0.477 | 3800 | 0.477 | 1.07 | 1.29 | -0.010395 | 3800 | 0.477 | 3800 | 0.477 | 1.07 | 1.29 | -0.0104
CFLAllSpcSCEGroNewCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCE | Gro | New | CZ09 | 3.8 | 0.000477 | 0 | 4.07 | 0.000652 | -0.0418 | 3.8 | 0.000477 | 0 | 4.07 | 0.000652 | -0.0418 |  | CFL | AllSpc | 3800 | 0.477 | 3800 | 0.477 | 1.07 | 1.37 | -0.011 | 3800 | 0.477 | 3800 | 0.477 | 1.07 | 1.37 | -0.011
CFLAllSpcSCEGroNewCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCE | Gro | New | CZ10 | 3.8 | 0.000477 | 0 | 4.1 | 0.000679 | -0.041 | 3.8 | 0.000477 | 0 | 4.1 | 0.000679 | -0.041 |  | CFL | AllSpc | 3800 | 0.477 | 3800 | 0.477 | 1.08 | 1.42 | -0.010789 | 3800 | 0.477 | 3800 | 0.477 | 1.08 | 1.42 | -0.0108
CFLAllSpcSCEGroNewCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCE | Gro | New | CZ13 | 3.8 | 0.000477 | 0 | 4.1 | 0.000655 | -0.0429 | 3.8 | 0.000477 | 0 | 4.1 | 0.000655 | -0.0429 |  | CFL | AllSpc | 3800 | 0.477 | 3800 | 0.477 | 1.08 | 1.37 | -0.011289 | 3800 | 0.477 | 3800 | 0.477 | 1.08 | 1.37 | -0.0113
CFLAllSpcSCEGroNewCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCE | Gro | New | CZ14 | 3.8 | 0.000477 | 0 | 4.11 | 0.000663 | -0.0452 | 3.8 | 0.000477 | 0 | 4.11 | 0.000663 | -0.0452 |  | CFL | AllSpc | 3800 | 0.477 | 3800 | 0.477 | 1.08 | 1.39 | -0.011895 | 3800 | 0.477 | 3800 | 0.477 | 1.08 | 1.39 | -0.0119
CFLAllSpcSCEGroNewCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCE | Gro | New | CZ15 | 3.8 | 0.000477 | 0 | 4.43 | 0.000674 | -0.0233 | 3.8 | 0.000477 | 0 | 4.43 | 0.000674 | -0.0233 |  | CFL | AllSpc | 3800 | 0.477 | 3800 | 0.477 | 1.17 | 1.41 | -0.0061316 | 3800 | 0.477 | 3800 | 0.477 | 1.17 | 1.41 | -0.00613
CFLAllSpcSCEGroNewCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCE | Gro | New | CZ16 | 3.8 | 0.000477 | 0 | 3.73 | 0.000615 | -0.0589 | 3.8 | 0.000477 | 0 | 3.73 | 0.000615 | -0.0589 |  | CFL | AllSpc | 3800 | 0.477 | 3800 | 0.477 | 0.982 | 1.29 | -0.0155 | 3800 | 0.477 | 3800 | 0.477 | 0.982 | 1.29 | -0.0155
CFLAllSpcSCEGroNewIOU | Com-Iltg-dWatt-CFL_OSspc | SCE | Gro | New | IOU | 3.8 | 0.000477 | 0 | 4.0732 | 0.00064576 | -0.041549 | 3.8 | 0.000477 | 0 | 4.0732 | 0.00064576 | -0.041549 |  | CFL | AllSpc | 3800 | 0.477 | 3800 | 0.477 | 1.07 | 1.35 | -0.010934 | 3800 | 0.477 | 3800 | 0.477 | 1.07 | 1.35 | -0.0109
CFLAllSpcSCEHspExCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCE | Hsp | Ex | CZ05 | 3.92 | 0.000656 | 0 | 4.3996 | 0.00079896 | -0.0276 | 3.92 | 0.000656 | 0 | 4.3996 | 0.00079896 | -0.0276 |  | CFL | AllSpc | 3920 | 0.656 | 3920 | 0.656 | 1.12 | 1.22 | -0.0070408 | 3920 | 0.656 | 3920 | 0.656 | 1.12 | 1.22 | -0.00704
CFLAllSpcSCEHspExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCE | Hsp | Ex | CZ06 | 3.92 | 0.000656 | 0 | 4.53 | 0.00081996 | -0.0207 | 3.92 | 0.000656 | 0 | 4.53 | 0.00081996 | -0.0207 |  | CFL | AllSpc | 3920 | 0.656 | 3920 | 0.656 | 1.16 | 1.25 | -0.0052806 | 3920 | 0.656 | 3920 | 0.656 | 1.16 | 1.25 | -0.00528
CFLAllSpcSCEHspExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCE | Hsp | Ex | CZ08 | 3.92 | 0.000656 | 0 | 4.5696 | 0.00081896 | -0.0203 | 3.92 | 0.000656 | 0 | 4.5696 | 0.00081896 | -0.0203 |  | CFL | AllSpc | 3920 | 0.656 | 3920 | 0.656 | 1.17 | 1.25 | -0.0051786 | 3920 | 0.656 | 3920 | 0.656 | 1.17 | 1.25 | -0.00518
CFLAllSpcSCEHspExCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCE | Hsp | Ex | CZ09 | 3.92 | 0.000656 | 0 | 4.58 | 0.00084195 | -0.020595 | 3.92 | 0.000656 | 0 | 4.58 | 0.00084195 | -0.020595 |  | CFL | AllSpc | 3920 | 0.656 | 3920 | 0.656 | 1.17 | 1.28 | -0.0052538 | 3920 | 0.656 | 3920 | 0.656 | 1.17 | 1.28 | -0.00525
CFLAllSpcSCEHspExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCE | Hsp | Ex | CZ10 | 3.92 | 0.000656 | 0 | 4.46 | 0.00082992 | -0.0221 | 3.92 | 0.000656 | 0 | 4.46 | 0.00082992 | -0.0221 |  | CFL | AllSpc | 3920 | 0.656 | 3920 | 0.656 | 1.14 | 1.27 | -0.0056378 | 3920 | 0.656 | 3920 | 0.656 | 1.14 | 1.27 | -0.00564
CFLAllSpcSCEHspExCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCE | Hsp | Ex | CZ13 | 3.92 | 0.000656 | 0 | 4.44 | 0.00082794 | -0.0252 | 3.92 | 0.000656 | 0 | 4.44 | 0.00082794 | -0.0252 |  | CFL | AllSpc | 3920 | 0.656 | 3920 | 0.656 | 1.13 | 1.26 | -0.0064286 | 3920 | 0.656 | 3920 | 0.656 | 1.13 | 1.26 | -0.00643
CFLAllSpcSCEHspExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCE | Hsp | Ex | CZ14 | 3.92 | 0.000656 | 0 | 4.43 | 0.00082885 | -0.027 | 3.92 | 0.000656 | 0 | 4.43 | 0.00082885 | -0.027 |  | CFL | AllSpc | 3920 | 0.656 | 3920 | 0.656 | 1.13 | 1.26 | -0.0068878 | 3920 | 0.656 | 3920 | 0.656 | 1.13 | 1.26 | -0.00689
CFLAllSpcSCEHspExCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCE | Hsp | Ex | CZ15 | 3.92 | 0.000656 | 0 | 4.64 | 0.00083892 | -0.0176 | 3.92 | 0.000656 | 0 | 4.64 | 0.00083892 | -0.0176 |  | CFL | AllSpc | 3920 | 0.656 | 3920 | 0.656 | 1.18 | 1.28 | -0.0044898 | 3920 | 0.656 | 3920 | 0.656 | 1.18 | 1.28 | -0.00449
CFLAllSpcSCEHspExCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCE | Hsp | Ex | CZ16 | 3.92 | 0.000656 | 0 | 4.1492 | 0.00080385 | -0.037 | 3.92 | 0.000656 | 0 | 4.1492 | 0.00080385 | -0.037 |  | CFL | AllSpc | 3920 | 0.656 | 3920 | 0.656 | 1.06 | 1.23 | -0.0094388 | 3920 | 0.656 | 3920 | 0.656 | 1.06 | 1.23 | -0.00944
CFLAllSpcSCEHspExIOU | Com-Iltg-dWatt-CFL_OSspc | SCE | Hsp | Ex | IOU | 3.92 | 0.000656 | 0 | 4.5262 | 0.0008248 | -0.02145 | 3.92 | 0.000656 | 0 | 4.5262 | 0.0008248 | -0.02145 |  | CFL | AllSpc | 3920 | 0.656 | 3920 | 0.656 | 1.15 | 1.26 | -0.0054719 | 3920 | 0.656 | 3920 | 0.656 | 1.15 | 1.26 | -0.00547
CFLAllSpcSCEHspNewCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCE | Hsp | New | CZ05 | 3.92 | 0.000656 | 0 | 4.13 | 0.000774 | -0.0293 | 3.92 | 0.000656 | 0 | 4.13 | 0.000774 | -0.0293 |  | CFL | AllSpc | 3920 | 0.656 | 3920 | 0.656 | 1.05 | 1.18 | -0.0074745 | 3920 | 0.656 | 3920 | 0.656 | 1.05 | 1.18 | -0.00747
CFLAllSpcSCEHspNewCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCE | Hsp | New | CZ06 | 3.92 | 0.000656 | 0 | 4.29 | 0.000789 | -0.0225 | 3.92 | 0.000656 | 0 | 4.29 | 0.000789 | -0.0225 |  | CFL | AllSpc | 3920 | 0.656 | 3920 | 0.656 | 1.09 | 1.2 | -0.0057398 | 3920 | 0.656 | 3920 | 0.656 | 1.09 | 1.2 | -0.00574
CFLAllSpcSCEHspNewCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCE | Hsp | New | CZ08 | 3.92 | 0.000656 | 0 | 4.33 | 0.000793 | -0.0207 | 3.92 | 0.000656 | 0 | 4.33 | 0.000793 | -0.0207 |  | CFL | AllSpc | 3920 | 0.656 | 3920 | 0.656 | 1.1 | 1.21 | -0.0052806 | 3920 | 0.656 | 3920 | 0.656 | 1.1 | 1.21 | -0.00528
CFLAllSpcSCEHspNewCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCE | Hsp | New | CZ09 | 3.92 | 0.000656 | 0 | 4.35 | 0.000815 | -0.0211 | 3.92 | 0.000656 | 0 | 4.35 | 0.000815 | -0.0211 |  | CFL | AllSpc | 3920 | 0.656 | 3920 | 0.656 | 1.11 | 1.24 | -0.0053827 | 3920 | 0.656 | 3920 | 0.656 | 1.11 | 1.24 | -0.00538
CFLAllSpcSCEHspNewCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCE | Hsp | New | CZ10 | 3.92 | 0.000656 | 0 | 4.33 | 0.00082 | -0.0232 | 3.92 | 0.000656 | 0 | 4.33 | 0.00082 | -0.0232 |  | CFL | AllSpc | 3920 | 0.656 | 3920 | 0.656 | 1.1 | 1.25 | -0.0059184 | 3920 | 0.656 | 3920 | 0.656 | 1.1 | 1.25 | -0.00592
CFLAllSpcSCEHspNewCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCE | Hsp | New | CZ13 | 3.92 | 0.000656 | 0 | 4.32 | 0.000815 | -0.0261 | 3.92 | 0.000656 | 0 | 4.32 | 0.000815 | -0.0261 |  | CFL | AllSpc | 3920 | 0.656 | 3920 | 0.656 | 1.1 | 1.24 | -0.0066582 | 3920 | 0.656 | 3920 | 0.656 | 1.1 | 1.24 | -0.00666
CFLAllSpcSCEHspNewCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCE | Hsp | New | CZ14 | 3.92 | 0.000656 | 0 | 4.27 | 0.000813 | -0.0288 | 3.92 | 0.000656 | 0 | 4.27 | 0.000813 | -0.0288 |  | CFL | AllSpc | 3920 | 0.656 | 3920 | 0.656 | 1.09 | 1.24 | -0.0073469 | 3920 | 0.656 | 3920 | 0.656 | 1.09 | 1.24 | -0.00735
CFLAllSpcSCEHspNewCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCE | Hsp | New | CZ15 | 3.92 | 0.000656 | 0 | 4.55 | 0.000825 | -0.0187 | 3.92 | 0.000656 | 0 | 4.55 | 0.000825 | -0.0187 |  | CFL | AllSpc | 3920 | 0.656 | 3920 | 0.656 | 1.16 | 1.26 | -0.0047704 | 3920 | 0.656 | 3920 | 0.656 | 1.16 | 1.26 | -0.00477
CFLAllSpcSCEHspNewCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCE | Hsp | New | CZ16 | 3.92 | 0.000656 | 0 | 3.95 | 0.000784 | -0.0415 | 3.92 | 0.000656 | 0 | 3.95 | 0.000784 | -0.0415 |  | CFL | AllSpc | 3920 | 0.656 | 3920 | 0.656 | 1.01 | 1.2 | -0.010587 | 3920 | 0.656 | 3920 | 0.656 | 1.01 | 1.2 | -0.0106
CFLAllSpcSCEHspNewIOU | Com-Iltg-dWatt-CFL_OSspc | SCE | Hsp | New | IOU | 3.92 | 0.000656 | 0 | 4.3187 | 0.00080474 | -0.022924 | 3.92 | 0.000656 | 0 | 4.3187 | 0.00080474 | -0.022924 |  | CFL | AllSpc | 3920 | 0.656 | 3920 | 0.656 | 1.1 | 1.23 | -0.005848 | 3920 | 0.656 | 3920 | 0.656 | 1.1 | 1.23 | -0.00585
CFLAllSpcSCEHtlExCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCE | Htl | Ex | CZ05 | 1.4703 | 0.000171 | 0 | 1.48 | 0.00021403 | -0.0044203 | 1.4703 | 0.000171 | 0 | 1.48 | 0.00021403 | -0.0044203 |  | CFL | AllSpc | 1470 | 0.171 | 1470 | 0.171 | 1.01 | 1.25 | -0.0030063 | 1470 | 0.171 | 1470 | 0.171 | 1.01 | 1.25 | -0.00301
CFLAllSpcSCEHtlExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCE | Htl | Ex | CZ06 | 1.4704 | 0.000171 | 0 | 1.63 | 0.00021604 | -0.0028104 | 1.4704 | 0.000171 | 0 | 1.63 | 0.00021604 | -0.0028104 |  | CFL | AllSpc | 1470 | 0.171 | 1470 | 0.171 | 1.11 | 1.26 | -0.0019113 | 1470 | 0.171 | 1470 | 0.171 | 1.11 | 1.26 | -0.00191
CFLAllSpcSCEHtlExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCE | Htl | Ex | CZ08 | 1.4704 | 0.000171 | 0 | 1.6504 | 0.00021704 | -0.0025504 | 1.4704 | 0.000171 | 0 | 1.6504 | 0.00021704 | -0.0025504 |  | CFL | AllSpc | 1470 | 0.171 | 1470 | 0.171 | 1.12 | 1.27 | -0.0017345 | 1470 | 0.171 | 1470 | 0.171 | 1.12 | 1.27 | -0.00173
CFLAllSpcSCEHtlExCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCE | Htl | Ex | CZ09 | 1.4705 | 0.000171 | 0 | 1.64 | 0.000221 | -0.0027105 | 1.4705 | 0.000171 | 0 | 1.64 | 0.000221 | -0.0027105 |  | CFL | AllSpc | 1470 | 0.171 | 1470 | 0.171 | 1.12 | 1.29 | -0.0018432 | 1470 | 0.171 | 1470 | 0.171 | 1.12 | 1.29 | -0.00184
CFLAllSpcSCEHtlExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCE | Htl | Ex | CZ10 | 1.471 | 0.000171 | 0 | 1.6 | 0.00022 | -0.002811 | 1.471 | 0.000171 | 0 | 1.6 | 0.00022 | -0.002811 |  | CFL | AllSpc | 1470 | 0.171 | 1470 | 0.171 | 1.09 | 1.29 | -0.0019109 | 1470 | 0.171 | 1470 | 0.171 | 1.09 | 1.29 | -0.00191
CFLAllSpcSCEHtlExCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCE | Htl | Ex | CZ13 | 1.4708 | 0.000171 | 0 | 1.5508 | 0.00021908 | -0.0038415 | 1.4708 | 0.000171 | 0 | 1.5508 | 0.00021908 | -0.0038415 |  | CFL | AllSpc | 1470 | 0.171 | 1470 | 0.171 | 1.05 | 1.28 | -0.0026119 | 1470 | 0.171 | 1470 | 0.171 | 1.05 | 1.28 | -0.00261
CFLAllSpcSCEHtlExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCE | Htl | Ex | CZ14 | 1.471 | 0.000171 | 0 | 1.531 | 0.0002201 | -0.003891 | 1.471 | 0.000171 | 0 | 1.531 | 0.0002201 | -0.003891 |  | CFL | AllSpc | 1470 | 0.171 | 1470 | 0.171 | 1.04 | 1.29 | -0.0026452 | 1470 | 0.171 | 1470 | 0.171 | 1.04 | 1.29 | -0.00265
CFLAllSpcSCEHtlExCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCE | Htl | Ex | CZ15 | 1.471 | 0.000171 | 0 | 1.72 | 0.0002211 | -0.00155 | 1.471 | 0.000171 | 0 | 1.72 | 0.0002211 | -0.00155 |  | CFL | AllSpc | 1470 | 0.171 | 1470 | 0.171 | 1.17 | 1.29 | -0.0010537 | 1470 | 0.171 | 1470 | 0.171 | 1.17 | 1.29 | -0.00105
CFLAllSpcSCEHtlExCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCE | Htl | Ex | CZ16 | 1.4708 | 0.000171 | 0 | 1.3508 | 0.000215 | -0.0063126 | 1.4708 | 0.000171 | 0 | 1.3508 | 0.000215 | -0.0063126 |  | CFL | AllSpc | 1470 | 0.171 | 1470 | 0.171 | 0.918 | 1.26 | -0.0042918 | 1470 | 0.171 | 1470 | 0.171 | 0.918 | 1.26 | -0.00429
CFLAllSpcSCEHtlExIOU | Com-Iltg-dWatt-CFL_OSspc | SCE | Htl | Ex | IOU | 1.4706 | 0.000171 | 0 | 1.6329 | 0.00021808 | -0.0027336 | 1.4706 | 0.000171 | 0 | 1.6329 | 0.00021808 | -0.0027336 |  | CFL | AllSpc | 1470 | 0.171 | 1470 | 0.171 | 1.11 | 1.28 | -0.0018588 | 1470 | 0.171 | 1470 | 0.171 | 1.11 | 1.28 | -0.00186
CFLAllSpcSCEHtlNewCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCE | Htl | New | CZ05 | 1.48 | 0.000171 | 0 | 1.42 | 0.000217 | -0.00466 | 1.48 | 0.000171 | 0 | 1.42 | 0.000217 | -0.00466 |  | CFL | AllSpc | 1480 | 0.171 | 1480 | 0.171 | 0.959 | 1.27 | -0.0031486 | 1480 | 0.171 | 1480 | 0.171 | 0.959 | 1.27 | -0.00315
CFLAllSpcSCEHtlNewCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCE | Htl | New | CZ06 | 1.48 | 0.000171 | 0 | 1.6 | 0.00022 | -0.00256 | 1.48 | 0.000171 | 0 | 1.6 | 0.00022 | -0.00256 |  | CFL | AllSpc | 1480 | 0.171 | 1480 | 0.171 | 1.08 | 1.29 | -0.0017297 | 1480 | 0.171 | 1480 | 0.171 | 1.08 | 1.29 | -0.00173
CFLAllSpcSCEHtlNewCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCE | Htl | New | CZ08 | 1.48 | 0.000171 | 0 | 1.62 | 0.000222 | -0.00225 | 1.48 | 0.000171 | 0 | 1.62 | 0.000222 | -0.00225 |  | CFL | AllSpc | 1480 | 0.171 | 1480 | 0.171 | 1.09 | 1.3 | -0.0015203 | 1480 | 0.171 | 1480 | 0.171 | 1.09 | 1.3 | -0.00152
CFLAllSpcSCEHtlNewCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCE | Htl | New | CZ09 | 1.48 | 0.000171 | 0 | 1.61 | 0.000226 | -0.00256 | 1.48 | 0.000171 | 0 | 1.61 | 0.000226 | -0.00256 |  | CFL | AllSpc | 1480 | 0.171 | 1480 | 0.171 | 1.09 | 1.32 | -0.0017297 | 1480 | 0.171 | 1480 | 0.171 | 1.09 | 1.32 | -0.00173
CFLAllSpcSCEHtlNewCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCE | Htl | New | CZ10 | 1.48 | 0.000171 | 0 | 1.6 | 0.000233 | -0.00284 | 1.48 | 0.000171 | 0 | 1.6 | 0.000233 | -0.00284 |  | CFL | AllSpc | 1480 | 0.171 | 1480 | 0.171 | 1.08 | 1.36 | -0.0019189 | 1480 | 0.171 | 1480 | 0.171 | 1.08 | 1.36 | -0.00192
CFLAllSpcSCEHtlNewCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCE | Htl | New | CZ13 | 1.48 | 0.000171 | 0 | 1.54 | 0.000227 | -0.00389 | 1.48 | 0.000171 | 0 | 1.54 | 0.000227 | -0.00389 |  | CFL | AllSpc | 1480 | 0.171 | 1480 | 0.171 | 1.04 | 1.33 | -0.0026284 | 1480 | 0.171 | 1480 | 0.171 | 1.04 | 1.33 | -0.00263
CFLAllSpcSCEHtlNewCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCE | Htl | New | CZ14 | 1.48 | 0.000171 | 0 | 1.51 | 0.000228 | -0.00427 | 1.48 | 0.000171 | 0 | 1.51 | 0.000228 | -0.00427 |  | CFL | AllSpc | 1480 | 0.171 | 1480 | 0.171 | 1.02 | 1.33 | -0.0028851 | 1480 | 0.171 | 1480 | 0.171 | 1.02 | 1.33 | -0.00289
CFLAllSpcSCEHtlNewCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCE | Htl | New | CZ15 | 1.48 | 0.000171 | 0 | 1.74 | 0.000232 | -0.00142 | 1.48 | 0.000171 | 0 | 1.74 | 0.000232 | -0.00142 |  | CFL | AllSpc | 1480 | 0.171 | 1480 | 0.171 | 1.18 | 1.36 | -0.00095946 | 1480 | 0.171 | 1480 | 0.171 | 1.18 | 1.36 | -0.000959
CFLAllSpcSCEHtlNewCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCE | Htl | New | CZ16 | 1.48 | 0.000171 | 0 | 1.3 | 0.000219 | -0.00724 | 1.48 | 0.000171 | 0 | 1.3 | 0.000219 | -0.00724 |  | CFL | AllSpc | 1480 | 0.171 | 1480 | 0.171 | 0.878 | 1.28 | -0.0048919 | 1480 | 0.171 | 1480 | 0.171 | 0.878 | 1.28 | -0.00489
CFLAllSpcSCEHtlNewIOU | Com-Iltg-dWatt-CFL_OSspc | SCE | Htl | New | IOU | 1.48 | 0.000171 | 0 | 1.6192 | 0.00022604 | -0.0026053 | 1.48 | 0.000171 | 0 | 1.6192 | 0.00022604 | -0.0026053 |  | CFL | AllSpc | 1480 | 0.171 | 1480 | 0.171 | 1.09 | 1.32 | -0.0017603 | 1480 | 0.171 | 1480 | 0.171 | 1.09 | 1.32 | -0.00176
CFLAllSpcSCEMBTExCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCE | MBT | Ex | CZ05 | 2.78 | 0.000667 | 0 | 3.1831 | 0.00082931 | -0.0011731 | 2.78 | 0.000667 | 0 | 3.1831 | 0.00082931 | -0.0011731 |  | CFL | AllSpc | 2780 | 0.667 | 2780 | 0.667 | 1.14 | 1.24 | -0.00042197 | 2780 | 0.667 | 2780 | 0.667 | 1.14 | 1.24 | -0.000422
CFLAllSpcSCEMBTExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCE | MBT | Ex | CZ06 | 2.78 | 0.000667 | 0 | 3.26 | 0.00080731 | -0.00050831 | 2.78 | 0.000667 | 0 | 3.26 | 0.00080731 | -0.00050831 |  | CFL | AllSpc | 2780 | 0.667 | 2780 | 0.667 | 1.17 | 1.21 | -0.00018284 | 2780 | 0.667 | 2780 | 0.667 | 1.17 | 1.21 | -0.000183
CFLAllSpcSCEMBTExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCE | MBT | Ex | CZ08 | 2.78 | 0.000667 | 0 | 3.2731 | 0.000839 | -0.00019 | 2.78 | 0.000667 | 0 | 3.2731 | 0.000839 | -0.00019 |  | CFL | AllSpc | 2780 | 0.667 | 2780 | 0.667 | 1.18 | 1.26 | -6.8345e-05 | 2780 | 0.667 | 2780 | 0.667 | 1.18 | 1.26 | -6.83e-05
CFLAllSpcSCEMBTExCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCE | MBT | Ex | CZ09 | 2.78 | 0.000667 | 0 | 3.263 | 0.0008413 | -0.00078106 | 2.78 | 0.000667 | 0 | 3.263 | 0.0008413 | -0.00078106 |  | CFL | AllSpc | 2780 | 0.667 | 2780 | 0.667 | 1.17 | 1.26 | -0.00028096 | 2780 | 0.667 | 2780 | 0.667 | 1.17 | 1.26 | -0.000281
CFLAllSpcSCEMBTExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCE | MBT | Ex | CZ10 | 2.78 | 0.000667 | 0 | 3.1623 | 0.00084214 | -0.00087223 | 2.78 | 0.000667 | 0 | 3.1623 | 0.00084214 | -0.00087223 |  | CFL | AllSpc | 2780 | 0.667 | 2780 | 0.667 | 1.14 | 1.26 | -0.00031375 | 2780 | 0.667 | 2780 | 0.667 | 1.14 | 1.26 | -0.000314
CFLAllSpcSCEMBTExCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCE | MBT | Ex | CZ13 | 2.78 | 0.000667 | 0 | 3.1615 | 0.00081409 | -0.00182 | 2.78 | 0.000667 | 0 | 3.1615 | 0.00081409 | -0.00182 |  | CFL | AllSpc | 2780 | 0.667 | 2780 | 0.667 | 1.14 | 1.22 | -0.00065468 | 2780 | 0.667 | 2780 | 0.667 | 1.14 | 1.22 | -0.000655
CFLAllSpcSCEMBTExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCE | MBT | Ex | CZ14 | 2.78 | 0.000667 | 0 | 3.17 | 0.000841 | -0.0020917 | 2.78 | 0.000667 | 0 | 3.17 | 0.000841 | -0.0020917 |  | CFL | AllSpc | 2780 | 0.667 | 2780 | 0.667 | 1.14 | 1.26 | -0.00075242 | 2780 | 0.667 | 2780 | 0.667 | 1.14 | 1.26 | -0.000752
CFLAllSpcSCEMBTExCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCE | MBT | Ex | CZ15 | 2.78 | 0.000667 | 0 | 3.2914 | 0.000845 | 0 | 2.78 | 0.000667 | 0 | 3.2914 | 0.000845 | 0 |  | CFL | AllSpc | 2780 | 0.667 | 2780 | 0.667 | 1.18 | 1.27 | 0 | 2780 | 0.667 | 2780 | 0.667 | 1.18 | 1.27 | 0
CFLAllSpcSCEMBTExCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCE | MBT | Ex | CZ16 | 2.78 | 0.000667 | 0 | 2.9711 | 0.00079411 | -0.0073611 | 2.78 | 0.000667 | 0 | 2.9711 | 0.00079411 | -0.0073611 |  | CFL | AllSpc | 2780 | 0.667 | 2780 | 0.667 | 1.07 | 1.19 | -0.0026479 | 2780 | 0.667 | 2780 | 0.667 | 1.07 | 1.19 | -0.00265
CFLAllSpcSCEMBTExIOU | Com-Iltg-dWatt-CFL_OSspc | SCE | MBT | Ex | IOU | 2.78 | 0.000667 | 0 | 3.2383 | 0.00083177 | -0.00071975 | 2.78 | 0.000667 | 0 | 3.2383 | 0.00083177 | -0.00071975 |  | CFL | AllSpc | 2780 | 0.667 | 2780 | 0.667 | 1.16 | 1.25 | -0.0002589 | 2780 | 0.667 | 2780 | 0.667 | 1.16 | 1.25 | -0.000259
CFLAllSpcSCEMBTNewCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCE | MBT | New | CZ05 | 2.78 | 0.000667 | 0 | 3 | 0.000824 | -0.000954 | 2.78 | 0.000667 | 0 | 3 | 0.000824 | -0.000954 |  | CFL | AllSpc | 2780 | 0.667 | 2780 | 0.667 | 1.08 | 1.24 | -0.00034317 | 2780 | 0.667 | 2780 | 0.667 | 1.08 | 1.24 | -0.000343
CFLAllSpcSCEMBTNewCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCE | MBT | New | CZ06 | 2.78 | 0.000667 | 0 | 3.11 | 0.000829 | -0.000912 | 2.78 | 0.000667 | 0 | 3.11 | 0.000829 | -0.000912 |  | CFL | AllSpc | 2780 | 0.667 | 2780 | 0.667 | 1.12 | 1.24 | -0.00032806 | 2780 | 0.667 | 2780 | 0.667 | 1.12 | 1.24 | -0.000328
CFLAllSpcSCEMBTNewCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCE | MBT | New | CZ08 | 2.78 | 0.000667 | 0 | 3.12 | 0.00085 | -0.000732 | 2.78 | 0.000667 | 0 | 3.12 | 0.00085 | -0.000732 |  | CFL | AllSpc | 2780 | 0.667 | 2780 | 0.667 | 1.12 | 1.27 | -0.00026331 | 2780 | 0.667 | 2780 | 0.667 | 1.12 | 1.27 | -0.000263
CFLAllSpcSCEMBTNewCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCE | MBT | New | CZ09 | 2.78 | 0.000667 | 0 | 3.12 | 0.000869 | -0.00086 | 2.78 | 0.000667 | 0 | 3.12 | 0.000869 | -0.00086 |  | CFL | AllSpc | 2780 | 0.667 | 2780 | 0.667 | 1.12 | 1.3 | -0.00030935 | 2780 | 0.667 | 2780 | 0.667 | 1.12 | 1.3 | -0.000309
CFLAllSpcSCEMBTNewCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCE | MBT | New | CZ10 | 2.78 | 0.000667 | 0 | 3.13 | 0.000883 | -0.000907 | 2.78 | 0.000667 | 0 | 3.13 | 0.000883 | -0.000907 |  | CFL | AllSpc | 2780 | 0.667 | 2780 | 0.667 | 1.13 | 1.32 | -0.00032626 | 2780 | 0.667 | 2780 | 0.667 | 1.13 | 1.32 | -0.000326
CFLAllSpcSCEMBTNewCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCE | MBT | New | CZ13 | 2.78 | 0.000667 | 0 | 3.1 | 0.000859 | -0.0016 | 2.78 | 0.000667 | 0 | 3.1 | 0.000859 | -0.0016 |  | CFL | AllSpc | 2780 | 0.667 | 2780 | 0.667 | 1.12 | 1.29 | -0.00057554 | 2780 | 0.667 | 2780 | 0.667 | 1.12 | 1.29 | -0.000576
CFLAllSpcSCEMBTNewCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCE | MBT | New | CZ14 | 2.78 | 0.000667 | 0 | 3.1 | 0.000871 | -0.00176 | 2.78 | 0.000667 | 0 | 3.1 | 0.000871 | -0.00176 |  | CFL | AllSpc | 2780 | 0.667 | 2780 | 0.667 | 1.12 | 1.31 | -0.00063309 | 2780 | 0.667 | 2780 | 0.667 | 1.12 | 1.31 | -0.000633
CFLAllSpcSCEMBTNewCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCE | MBT | New | CZ15 | 2.78 | 0.000667 | 0 | 3.29 | 0.000883 | 0 | 2.78 | 0.000667 | 0 | 3.29 | 0.000883 | 0 |  | CFL | AllSpc | 2780 | 0.667 | 2780 | 0.667 | 1.18 | 1.32 | 0 | 2780 | 0.667 | 2780 | 0.667 | 1.18 | 1.32 | 0
CFLAllSpcSCEMBTNewCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCE | MBT | New | CZ16 | 2.78 | 0.000667 | 0 | 2.94 | 0.000824 | -0.00598 | 2.78 | 0.000667 | 0 | 2.94 | 0.000824 | -0.00598 |  | CFL | AllSpc | 2780 | 0.667 | 2780 | 0.667 | 1.06 | 1.24 | -0.0021511 | 2780 | 0.667 | 2780 | 0.667 | 1.06 | 1.24 | -0.00215
CFLAllSpcSCEMBTNewIOU | Com-Iltg-dWatt-CFL_OSspc | SCE | MBT | New | IOU | 2.78 | 0.000667 | 0 | 3.1329 | 0.00086285 | -0.00098468 | 2.78 | 0.000667 | 0 | 3.1329 | 0.00086285 | -0.00098468 |  | CFL | AllSpc | 2780 | 0.667 | 2780 | 0.667 | 1.13 | 1.29 | -0.0003542 | 2780 | 0.667 | 2780 | 0.667 | 1.13 | 1.29 | -0.000354
CFLAllSpcSCEMLIExCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCE | MLI | Ex | CZ05 | 2.29 | 0.00066 | 0 | 2.42 | 0.00079847 | -0.0111 | 2.29 | 0.00066 | 0 | 2.42 | 0.00079847 | -0.0111 |  | CFL | AllSpc | 2290 | 0.66 | 2290 | 0.66 | 1.06 | 1.21 | -0.0048472 | 2290 | 0.66 | 2290 | 0.66 | 1.06 | 1.21 | -0.00485
CFLAllSpcSCEMLIExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCE | MLI | Ex | CZ06 | 2.29 | 0.00066 | 0 | 2.5406 | 0.00078447 | -0.00385 | 2.29 | 0.00066 | 0 | 2.5406 | 0.00078447 | -0.00385 |  | CFL | AllSpc | 2290 | 0.66 | 2290 | 0.66 | 1.11 | 1.19 | -0.0016812 | 2290 | 0.66 | 2290 | 0.66 | 1.11 | 1.19 | -0.00168
CFLAllSpcSCEMLIExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCE | MLI | Ex | CZ08 | 2.29 | 0.00066 | 0 | 2.56 | 0.00078247 | -0.00316 | 2.29 | 0.00066 | 0 | 2.56 | 0.00078247 | -0.00316 |  | CFL | AllSpc | 2290 | 0.66 | 2290 | 0.66 | 1.12 | 1.19 | -0.0013799 | 2290 | 0.66 | 2290 | 0.66 | 1.12 | 1.19 | -0.00138
CFLAllSpcSCEMLIExCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCE | MLI | Ex | CZ09 | 2.29 | 0.00066 | 0 | 2.5405 | 0.00080048 | -0.00433 | 2.29 | 0.00066 | 0 | 2.5405 | 0.00080048 | -0.00433 |  | CFL | AllSpc | 2290 | 0.66 | 2290 | 0.66 | 1.11 | 1.21 | -0.0018908 | 2290 | 0.66 | 2290 | 0.66 | 1.11 | 1.21 | -0.00189
CFLAllSpcSCEMLIExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCE | MLI | Ex | CZ10 | 2.29 | 0.00066 | 0 | 2.47 | 0.00079417 | -0.0055614 | 2.29 | 0.00066 | 0 | 2.47 | 0.00079417 | -0.0055614 |  | CFL | AllSpc | 2290 | 0.66 | 2290 | 0.66 | 1.08 | 1.2 | -0.0024286 | 2290 | 0.66 | 2290 | 0.66 | 1.08 | 1.2 | -0.00243
CFLAllSpcSCEMLIExCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCE | MLI | Ex | CZ13 | 2.29 | 0.00066 | 0 | 2.45 | 0.00078409 | -0.0123 | 2.29 | 0.00066 | 0 | 2.45 | 0.00078409 | -0.0123 |  | CFL | AllSpc | 2290 | 0.66 | 2290 | 0.66 | 1.07 | 1.19 | -0.0053712 | 2290 | 0.66 | 2290 | 0.66 | 1.07 | 1.19 | -0.00537
CFLAllSpcSCEMLIExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCE | MLI | Ex | CZ14 | 2.29 | 0.00066 | 0 | 2.43 | 0.00078812 | -0.0142 | 2.29 | 0.00066 | 0 | 2.43 | 0.00078812 | -0.0142 |  | CFL | AllSpc | 2290 | 0.66 | 2290 | 0.66 | 1.06 | 1.19 | -0.0062009 | 2290 | 0.66 | 2290 | 0.66 | 1.06 | 1.19 | -0.0062
CFLAllSpcSCEMLIExCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCE | MLI | Ex | CZ15 | 2.29 | 0.00066 | 0 | 2.64 | 0.000786 | -0.00143 | 2.29 | 0.00066 | 0 | 2.64 | 0.000786 | -0.00143 |  | CFL | AllSpc | 2290 | 0.66 | 2290 | 0.66 | 1.15 | 1.19 | -0.00062445 | 2290 | 0.66 | 2290 | 0.66 | 1.15 | 1.19 | -0.000624
CFLAllSpcSCEMLIExCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCE | MLI | Ex | CZ16 | 2.29 | 0.00066 | 0 | 2.26 | 0.000776 | -0.0277 | 2.29 | 0.00066 | 0 | 2.26 | 0.000776 | -0.0277 |  | CFL | AllSpc | 2290 | 0.66 | 2290 | 0.66 | 0.987 | 1.18 | -0.012096 | 2290 | 0.66 | 2290 | 0.66 | 0.987 | 1.18 | -0.0121
CFLAllSpcSCEMLIExIOU | Com-Iltg-dWatt-CFL_OSspc | SCE | MLI | Ex | IOU | 2.29 | 0.00066 | 0 | 2.5284 | 0.0007879 | -0.0049634 | 2.29 | 0.00066 | 0 | 2.5284 | 0.0007879 | -0.0049634 |  | CFL | AllSpc | 2290 | 0.66 | 2290 | 0.66 | 1.1 | 1.19 | -0.0021674 | 2290 | 0.66 | 2290 | 0.66 | 1.1 | 1.19 | -0.00217
CFLAllSpcSCEMLINewCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCE | MLI | New | CZ05 | 2.29 | 0.00066 | 0 | 2.28 | 0.000785 | -0.0183 | 2.29 | 0.00066 | 0 | 2.28 | 0.000785 | -0.0183 |  | CFL | AllSpc | 2290 | 0.66 | 2290 | 0.66 | 0.996 | 1.19 | -0.0079913 | 2290 | 0.66 | 2290 | 0.66 | 0.996 | 1.19 | -0.00799
CFLAllSpcSCEMLINewCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCE | MLI | New | CZ06 | 2.29 | 0.00066 | 0 | 2.4 | 0.000771 | -0.00827 | 2.29 | 0.00066 | 0 | 2.4 | 0.000771 | -0.00827 |  | CFL | AllSpc | 2290 | 0.66 | 2290 | 0.66 | 1.05 | 1.17 | -0.0036114 | 2290 | 0.66 | 2290 | 0.66 | 1.05 | 1.17 | -0.00361
CFLAllSpcSCEMLINewCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCE | MLI | New | CZ08 | 2.29 | 0.00066 | 0 | 2.44 | 0.000776 | -0.00666 | 2.29 | 0.00066 | 0 | 2.44 | 0.000776 | -0.00666 |  | CFL | AllSpc | 2290 | 0.66 | 2290 | 0.66 | 1.07 | 1.18 | -0.0029083 | 2290 | 0.66 | 2290 | 0.66 | 1.07 | 1.18 | -0.00291
CFLAllSpcSCEMLINewCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCE | MLI | New | CZ09 | 2.29 | 0.00066 | 0 | 2.5 | 0.000848 | -0.00767 | 2.29 | 0.00066 | 0 | 2.5 | 0.000848 | -0.00767 |  | CFL | AllSpc | 2290 | 0.66 | 2290 | 0.66 | 1.09 | 1.28 | -0.0033493 | 2290 | 0.66 | 2290 | 0.66 | 1.09 | 1.28 | -0.00335
CFLAllSpcSCEMLINewCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCE | MLI | New | CZ10 | 2.29 | 0.00066 | 0 | 2.52 | 0.000862 | -0.00839 | 2.29 | 0.00066 | 0 | 2.52 | 0.000862 | -0.00839 |  | CFL | AllSpc | 2290 | 0.66 | 2290 | 0.66 | 1.1 | 1.31 | -0.0036638 | 2290 | 0.66 | 2290 | 0.66 | 1.1 | 1.31 | -0.00366
CFLAllSpcSCEMLINewCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCE | MLI | New | CZ13 | 2.29 | 0.00066 | 0 | 2.47 | 0.000829 | -0.0152 | 2.29 | 0.00066 | 0 | 2.47 | 0.000829 | -0.0152 |  | CFL | AllSpc | 2290 | 0.66 | 2290 | 0.66 | 1.08 | 1.26 | -0.0066376 | 2290 | 0.66 | 2290 | 0.66 | 1.08 | 1.26 | -0.00664
CFLAllSpcSCEMLINewCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCE | MLI | New | CZ14 | 2.29 | 0.00066 | 0 | 2.43 | 0.000805 | -0.0165 | 2.29 | 0.00066 | 0 | 2.43 | 0.000805 | -0.0165 |  | CFL | AllSpc | 2290 | 0.66 | 2290 | 0.66 | 1.06 | 1.22 | -0.0072052 | 2290 | 0.66 | 2290 | 0.66 | 1.06 | 1.22 | -0.00721
CFLAllSpcSCEMLINewCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCE | MLI | New | CZ15 | 2.29 | 0.00066 | 0 | 2.69 | 0.000876 | -0.00141 | 2.29 | 0.00066 | 0 | 2.69 | 0.000876 | -0.00141 |  | CFL | AllSpc | 2290 | 0.66 | 2290 | 0.66 | 1.17 | 1.33 | -0.00061572 | 2290 | 0.66 | 2290 | 0.66 | 1.17 | 1.33 | -0.000616
CFLAllSpcSCEMLINewCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCE | MLI | New | CZ16 | 2.29 | 0.00066 | 0 | 2.26 | 0.000776 | -0.0293 | 2.29 | 0.00066 | 0 | 2.26 | 0.000776 | -0.0293 |  | CFL | AllSpc | 2290 | 0.66 | 2290 | 0.66 | 0.987 | 1.18 | -0.012795 | 2290 | 0.66 | 2290 | 0.66 | 0.987 | 1.18 | -0.0128
CFLAllSpcSCEMLINewIOU | Com-Iltg-dWatt-CFL_OSspc | SCE | MLI | New | IOU | 2.29 | 0.00066 | 0 | 2.4862 | 0.00082259 | -0.0083946 | 2.29 | 0.00066 | 0 | 2.4862 | 0.00082259 | -0.0083946 |  | CFL | AllSpc | 2290 | 0.66 | 2290 | 0.66 | 1.09 | 1.25 | -0.0036658 | 2290 | 0.66 | 2290 | 0.66 | 1.09 | 1.25 | -0.00367
CFLAllSpcSCEMtlExCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCE | Mtl | Ex | CZ05 | 1.22 | 0.000131 | 0 | 1.3 | 0.00016401 | -0.00583 | 1.22 | 0.000131 | 0 | 1.3 | 0.00016401 | -0.00583 |  | CFL | AllSpc | 1220 | 0.131 | 1220 | 0.131 | 1.07 | 1.25 | -0.0047787 | 1220 | 0.131 | 1220 | 0.131 | 1.07 | 1.25 | -0.00478
CFLAllSpcSCEMtlExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCE | Mtl | Ex | CZ06 | 1.22 | 0.000131 | 0 | 1.4 | 0.00016504 | -0.00303 | 1.22 | 0.000131 | 0 | 1.4 | 0.00016504 | -0.00303 |  | CFL | AllSpc | 1220 | 0.131 | 1220 | 0.131 | 1.15 | 1.26 | -0.0024836 | 1220 | 0.131 | 1220 | 0.131 | 1.15 | 1.26 | -0.00248
CFLAllSpcSCEMtlExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCE | Mtl | Ex | CZ08 | 1.22 | 0.000131 | 0 | 1.42 | 0.00016701 | -0.00253 | 1.22 | 0.000131 | 0 | 1.42 | 0.00016701 | -0.00253 |  | CFL | AllSpc | 1220 | 0.131 | 1220 | 0.131 | 1.16 | 1.27 | -0.0020738 | 1220 | 0.131 | 1220 | 0.131 | 1.16 | 1.27 | -0.00207
CFLAllSpcSCEMtlExCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCE | Mtl | Ex | CZ09 | 1.22 | 0.000131 | 0 | 1.41 | 0.00017105 | -0.00284 | 1.22 | 0.000131 | 0 | 1.41 | 0.00017105 | -0.00284 |  | CFL | AllSpc | 1220 | 0.131 | 1220 | 0.131 | 1.16 | 1.31 | -0.0023279 | 1220 | 0.131 | 1220 | 0.131 | 1.16 | 1.31 | -0.00233
CFLAllSpcSCEMtlExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCE | Mtl | Ex | CZ10 | 1.22 | 0.000131 | 0 | 1.3892 | 0.00017108 | -0.003181 | 1.22 | 0.000131 | 0 | 1.3892 | 0.00017108 | -0.003181 |  | CFL | AllSpc | 1220 | 0.131 | 1220 | 0.131 | 1.14 | 1.31 | -0.0026074 | 1220 | 0.131 | 1220 | 0.131 | 1.14 | 1.31 | -0.00261
CFLAllSpcSCEMtlExCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCE | Mtl | Ex | CZ13 | 1.22 | 0.000131 | 0 | 1.36 | 0.000171 | -0.0045 | 1.22 | 0.000131 | 0 | 1.36 | 0.000171 | -0.0045 |  | CFL | AllSpc | 1220 | 0.131 | 1220 | 0.131 | 1.11 | 1.31 | -0.0036885 | 1220 | 0.131 | 1220 | 0.131 | 1.11 | 1.31 | -0.00369
CFLAllSpcSCEMtlExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCE | Mtl | Ex | CZ14 | 1.22 | 0.000131 | 0 | 1.35 | 0.0001711 | -0.00437 | 1.22 | 0.000131 | 0 | 1.35 | 0.0001711 | -0.00437 |  | CFL | AllSpc | 1220 | 0.131 | 1220 | 0.131 | 1.11 | 1.31 | -0.003582 | 1220 | 0.131 | 1220 | 0.131 | 1.11 | 1.31 | -0.00358
CFLAllSpcSCEMtlExCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCE | Mtl | Ex | CZ15 | 1.22 | 0.000131 | 0 | 1.47 | 0.000174 | -0.00129 | 1.22 | 0.000131 | 0 | 1.47 | 0.000174 | -0.00129 |  | CFL | AllSpc | 1220 | 0.131 | 1220 | 0.131 | 1.2 | 1.33 | -0.0010574 | 1220 | 0.131 | 1220 | 0.131 | 1.2 | 1.33 | -0.00106
CFLAllSpcSCEMtlExCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCE | Mtl | Ex | CZ16 | 1.22 | 0.000131 | 0 | 1.21 | 0.000164 | -0.00775 | 1.22 | 0.000131 | 0 | 1.21 | 0.000164 | -0.00775 |  | CFL | AllSpc | 1220 | 0.131 | 1220 | 0.131 | 0.992 | 1.25 | -0.0063525 | 1220 | 0.131 | 1220 | 0.131 | 0.992 | 1.25 | -0.00635
CFLAllSpcSCEMtlExIOU | Com-Iltg-dWatt-CFL_OSspc | SCE | Mtl | Ex | IOU | 1.22 | 0.000131 | 0 | 1.4062 | 0.00016821 | -0.0028862 | 1.22 | 0.000131 | 0 | 1.4062 | 0.00016821 | -0.0028862 |  | CFL | AllSpc | 1220 | 0.131 | 1220 | 0.131 | 1.15 | 1.28 | -0.0023658 | 1220 | 0.131 | 1220 | 0.131 | 1.15 | 1.28 | -0.00237
CFLAllSpcSCEMtlNewCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCE | Mtl | New | CZ05 | 1.22 | 0.000131 | 0 | 1.26 | 0.000166 | -0.00783 | 1.22 | 0.000131 | 0 | 1.26 | 0.000166 | -0.00783 |  | CFL | AllSpc | 1220 | 0.131 | 1220 | 0.131 | 1.03 | 1.27 | -0.006418 | 1220 | 0.131 | 1220 | 0.131 | 1.03 | 1.27 | -0.00642
CFLAllSpcSCEMtlNewCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCE | Mtl | New | CZ06 | 1.22 | 0.000131 | 0 | 1.38 | 0.000169 | -0.00415 | 1.22 | 0.000131 | 0 | 1.38 | 0.000169 | -0.00415 |  | CFL | AllSpc | 1220 | 0.131 | 1220 | 0.131 | 1.13 | 1.29 | -0.0034016 | 1220 | 0.131 | 1220 | 0.131 | 1.13 | 1.29 | -0.0034
CFLAllSpcSCEMtlNewCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCE | Mtl | New | CZ08 | 1.22 | 0.000131 | 0 | 1.4 | 0.000171 | -0.00345 | 1.22 | 0.000131 | 0 | 1.4 | 0.000171 | -0.00345 |  | CFL | AllSpc | 1220 | 0.131 | 1220 | 0.131 | 1.15 | 1.31 | -0.0028279 | 1220 | 0.131 | 1220 | 0.131 | 1.15 | 1.31 | -0.00283
CFLAllSpcSCEMtlNewCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCE | Mtl | New | CZ09 | 1.22 | 0.000131 | 0 | 1.4 | 0.000176 | -0.00348 | 1.22 | 0.000131 | 0 | 1.4 | 0.000176 | -0.00348 |  | CFL | AllSpc | 1220 | 0.131 | 1220 | 0.131 | 1.15 | 1.34 | -0.0028525 | 1220 | 0.131 | 1220 | 0.131 | 1.15 | 1.34 | -0.00285
CFLAllSpcSCEMtlNewCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCE | Mtl | New | CZ10 | 1.22 | 0.000131 | 0 | 1.38 | 0.000177 | -0.00431 | 1.22 | 0.000131 | 0 | 1.38 | 0.000177 | -0.00431 |  | CFL | AllSpc | 1220 | 0.131 | 1220 | 0.131 | 1.13 | 1.35 | -0.0035328 | 1220 | 0.131 | 1220 | 0.131 | 1.13 | 1.35 | -0.00353
CFLAllSpcSCEMtlNewCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCE | Mtl | New | CZ13 | 1.22 | 0.000131 | 0 | 1.34 | 0.000174 | -0.00557 | 1.22 | 0.000131 | 0 | 1.34 | 0.000174 | -0.00557 |  | CFL | AllSpc | 1220 | 0.131 | 1220 | 0.131 | 1.1 | 1.33 | -0.0045656 | 1220 | 0.131 | 1220 | 0.131 | 1.1 | 1.33 | -0.00457
CFLAllSpcSCEMtlNewCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCE | Mtl | New | CZ14 | 1.22 | 0.000131 | 0 | 1.33 | 0.000176 | -0.00578 | 1.22 | 0.000131 | 0 | 1.33 | 0.000176 | -0.00578 |  | CFL | AllSpc | 1220 | 0.131 | 1220 | 0.131 | 1.09 | 1.34 | -0.0047377 | 1220 | 0.131 | 1220 | 0.131 | 1.09 | 1.34 | -0.00474
CFLAllSpcSCEMtlNewCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCE | Mtl | New | CZ15 | 1.22 | 0.000131 | 0 | 1.48 | 0.000181 | -0.002 | 1.22 | 0.000131 | 0 | 1.48 | 0.000181 | -0.002 |  | CFL | AllSpc | 1220 | 0.131 | 1220 | 0.131 | 1.21 | 1.38 | -0.0016393 | 1220 | 0.131 | 1220 | 0.131 | 1.21 | 1.38 | -0.00164
CFLAllSpcSCEMtlNewCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCE | Mtl | New | CZ16 | 1.22 | 0.000131 | 0 | 1.18 | 0.000167 | -0.00901 | 1.22 | 0.000131 | 0 | 1.18 | 0.000167 | -0.00901 |  | CFL | AllSpc | 1220 | 0.131 | 1220 | 0.131 | 0.967 | 1.27 | -0.0073852 | 1220 | 0.131 | 1220 | 0.131 | 0.967 | 1.27 | -0.00739
CFLAllSpcSCEMtlNewIOU | Com-Iltg-dWatt-CFL_OSspc | SCE | Mtl | New | IOU | 1.22 | 0.000131 | 0 | 1.3979 | 0.00017455 | -0.0037754 | 1.22 | 0.000131 | 0 | 1.3979 | 0.00017455 | -0.0037754 |  | CFL | AllSpc | 1220 | 0.131 | 1220 | 0.131 | 1.15 | 1.33 | -0.0030946 | 1220 | 0.131 | 1220 | 0.131 | 1.15 | 1.33 | -0.00309
CFLAllSpcSCENrsExCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCE | Nrs | Ex | CZ05 | 3.18 | 0.00048404 | 0 | 3.25 | 0.00059708 | -0.0464 | 3.18 | 0.00048404 | 0 | 3.25 | 0.00059708 | -0.0464 |  | CFL | AllSpc | 3180 | 0.484 | 3180 | 0.484 | 1.02 | 1.23 | -0.014591 | 3180 | 0.484 | 3180 | 0.484 | 1.02 | 1.23 | -0.0146
CFLAllSpcSCENrsExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCE | Nrs | Ex | CZ06 | 3.18 | 0.00048404 | 0 | 3.46 | 0.00062604 | -0.0307 | 3.18 | 0.00048404 | 0 | 3.46 | 0.00062604 | -0.0307 |  | CFL | AllSpc | 3180 | 0.484 | 3180 | 0.484 | 1.09 | 1.29 | -0.0096541 | 3180 | 0.484 | 3180 | 0.484 | 1.09 | 1.29 | -0.00965
CFLAllSpcSCENrsExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCE | Nrs | Ex | CZ08 | 3.18 | 0.00048404 | 0 | 3.49 | 0.00062808 | -0.029604 | 3.18 | 0.00048404 | 0 | 3.49 | 0.00062808 | -0.029604 |  | CFL | AllSpc | 3180 | 0.484 | 3180 | 0.484 | 1.1 | 1.3 | -0.0093094 | 3180 | 0.484 | 3180 | 0.484 | 1.1 | 1.3 | -0.00931
CFLAllSpcSCENrsExCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCE | Nrs | Ex | CZ09 | 3.18 | 0.00048405 | 0 | 3.5005 | 0.0006471 | -0.0303 | 3.18 | 0.00048405 | 0 | 3.5005 | 0.0006471 | -0.0303 |  | CFL | AllSpc | 3180 | 0.484 | 3180 | 0.484 | 1.1 | 1.34 | -0.0095283 | 3180 | 0.484 | 3180 | 0.484 | 1.1 | 1.34 | -0.00953
CFLAllSpcSCENrsExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCE | Nrs | Ex | CZ10 | 3.18 | 0.00048408 | 0 | 3.46 | 0.00064675 | -0.0302 | 3.18 | 0.00048408 | 0 | 3.46 | 0.00064675 | -0.0302 |  | CFL | AllSpc | 3180 | 0.484 | 3180 | 0.484 | 1.09 | 1.34 | -0.0094969 | 3180 | 0.484 | 3180 | 0.484 | 1.09 | 1.34 | -0.0095
CFLAllSpcSCENrsExCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCE | Nrs | Ex | CZ13 | 3.18 | 0.00048407 | 0 | 3.4238 | 0.00063913 | -0.034938 | 3.18 | 0.00048407 | 0 | 3.4238 | 0.00063913 | -0.034938 |  | CFL | AllSpc | 3180 | 0.484 | 3180 | 0.484 | 1.08 | 1.32 | -0.010987 | 3180 | 0.484 | 3180 | 0.484 | 1.08 | 1.32 | -0.011
CFLAllSpcSCENrsExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCE | Nrs | Ex | CZ14 | 3.18 | 0.00048407 | 0 | 3.4337 | 0.00063977 | -0.036238 | 3.18 | 0.00048407 | 0 | 3.4337 | 0.00063977 | -0.036238 |  | CFL | AllSpc | 3180 | 0.484 | 3180 | 0.484 | 1.08 | 1.32 | -0.011395 | 3180 | 0.484 | 3180 | 0.484 | 1.08 | 1.32 | -0.0114
CFLAllSpcSCENrsExCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCE | Nrs | Ex | CZ15 | 3.18 | 0.00048408 | 0 | 3.6908 | 0.00065208 | -0.0182 | 3.18 | 0.00048408 | 0 | 3.6908 | 0.00065208 | -0.0182 |  | CFL | AllSpc | 3180 | 0.484 | 3180 | 0.484 | 1.16 | 1.35 | -0.0057233 | 3180 | 0.484 | 3180 | 0.484 | 1.16 | 1.35 | -0.00572
CFLAllSpcSCENrsExCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCE | Nrs | Ex | CZ16 | 3.18 | 0.00048408 | 0 | 3.17 | 0.00061115 | -0.052708 | 3.18 | 0.00048408 | 0 | 3.17 | 0.00061115 | -0.052708 |  | CFL | AllSpc | 3180 | 0.484 | 3180 | 0.484 | 0.997 | 1.26 | -0.016575 | 3180 | 0.484 | 3180 | 0.484 | 0.997 | 1.26 | -0.0166
CFLAllSpcSCENrsExIOU | Com-Iltg-dWatt-CFL_OSspc | SCE | Nrs | Ex | IOU | 3.18 | 0.00048405 | 0 | 3.4706 | 0.00063368 | -0.030861 | 3.18 | 0.00048405 | 0 | 3.4706 | 0.00063368 | -0.030861 |  | CFL | AllSpc | 3180 | 0.484 | 3180 | 0.484 | 1.09 | 1.31 | -0.0097046 | 3180 | 0.484 | 3180 | 0.484 | 1.09 | 1.31 | -0.0097
CFLAllSpcSCENrsNewCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCE | Nrs | New | CZ05 | 3.18 | 0.000485 | 0 | 3.12 | 0.000591 | -0.0518 | 3.18 | 0.000485 | 0 | 3.12 | 0.000591 | -0.0518 |  | CFL | AllSpc | 3180 | 0.485 | 3180 | 0.485 | 0.981 | 1.22 | -0.016289 | 3180 | 0.485 | 3180 | 0.485 | 0.981 | 1.22 | -0.0163
CFLAllSpcSCENrsNewCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCE | Nrs | New | CZ06 | 3.18 | 0.000485 | 0 | 3.31 | 0.000618 | -0.0318 | 3.18 | 0.000485 | 0 | 3.31 | 0.000618 | -0.0318 |  | CFL | AllSpc | 3180 | 0.485 | 3180 | 0.485 | 1.04 | 1.27 | -0.01 | 3180 | 0.485 | 3180 | 0.485 | 1.04 | 1.27 | -0.01
CFLAllSpcSCENrsNewCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCE | Nrs | New | CZ08 | 3.18 | 0.000485 | 0 | 3.37 | 0.00062 | -0.0303 | 3.18 | 0.000485 | 0 | 3.37 | 0.00062 | -0.0303 |  | CFL | AllSpc | 3180 | 0.485 | 3180 | 0.485 | 1.06 | 1.28 | -0.0095283 | 3180 | 0.485 | 3180 | 0.485 | 1.06 | 1.28 | -0.00953
CFLAllSpcSCENrsNewCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCE | Nrs | New | CZ09 | 3.18 | 0.000485 | 0 | 3.39 | 0.000643 | -0.0306 | 3.18 | 0.000485 | 0 | 3.39 | 0.000643 | -0.0306 |  | CFL | AllSpc | 3180 | 0.485 | 3180 | 0.485 | 1.07 | 1.33 | -0.0096226 | 3180 | 0.485 | 3180 | 0.485 | 1.07 | 1.33 | -0.00962
CFLAllSpcSCENrsNewCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCE | Nrs | New | CZ10 | 3.18 | 0.000485 | 0 | 3.4 | 0.000645 | -0.0312 | 3.18 | 0.000485 | 0 | 3.4 | 0.000645 | -0.0312 |  | CFL | AllSpc | 3180 | 0.485 | 3180 | 0.485 | 1.07 | 1.33 | -0.0098113 | 3180 | 0.485 | 3180 | 0.485 | 1.07 | 1.33 | -0.00981
CFLAllSpcSCENrsNewCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCE | Nrs | New | CZ13 | 3.18 | 0.000485 | 0 | 3.38 | 0.000638 | -0.0369 | 3.18 | 0.000485 | 0 | 3.38 | 0.000638 | -0.0369 |  | CFL | AllSpc | 3180 | 0.485 | 3180 | 0.485 | 1.06 | 1.32 | -0.011604 | 3180 | 0.485 | 3180 | 0.485 | 1.06 | 1.32 | -0.0116
CFLAllSpcSCENrsNewCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCE | Nrs | New | CZ14 | 3.18 | 0.000485 | 0 | 3.37 | 0.000628 | -0.0385 | 3.18 | 0.000485 | 0 | 3.37 | 0.000628 | -0.0385 |  | CFL | AllSpc | 3180 | 0.485 | 3180 | 0.485 | 1.06 | 1.29 | -0.012107 | 3180 | 0.485 | 3180 | 0.485 | 1.06 | 1.29 | -0.0121
CFLAllSpcSCENrsNewCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCE | Nrs | New | CZ15 | 3.18 | 0.000485 | 0 | 3.66 | 0.000645 | -0.0149 | 3.18 | 0.000485 | 0 | 3.66 | 0.000645 | -0.0149 |  | CFL | AllSpc | 3180 | 0.485 | 3180 | 0.485 | 1.15 | 1.33 | -0.0046855 | 3180 | 0.485 | 3180 | 0.485 | 1.15 | 1.33 | -0.00469
CFLAllSpcSCENrsNewCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCE | Nrs | New | CZ16 | 3.18 | 0.000485 | 0 | 3.12 | 0.000607 | -0.0572 | 3.18 | 0.000485 | 0 | 3.12 | 0.000607 | -0.0572 |  | CFL | AllSpc | 3180 | 0.485 | 3180 | 0.485 | 0.981 | 1.25 | -0.017987 | 3180 | 0.485 | 3180 | 0.485 | 0.981 | 1.25 | -0.018
CFLAllSpcSCENrsNewIOU | Com-Iltg-dWatt-CFL_OSspc | SCE | Nrs | New | IOU | 3.18 | 0.000485 | 0 | 3.372 | 0.00063057 | -0.031773 | 3.18 | 0.000485 | 0 | 3.372 | 0.00063057 | -0.031773 |  | CFL | AllSpc | 3180 | 0.485 | 3180 | 0.485 | 1.06 | 1.3 | -0.0099916 | 3180 | 0.485 | 3180 | 0.485 | 1.06 | 1.3 | -0.00999
CFLAllSpcSCEOfLExCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCE | OfL | Ex | CZ05 | 2.5898 | 0.00050698 | 0 | 2.87 | 0.00065598 | -0.0179 | 2.5898 | 0.00050698 | 0 | 2.87 | 0.00065598 | -0.0179 |  | CFL | AllSpc | 2590 | 0.507 | 2590 | 0.507 | 1.11 | 1.29 | -0.0069118 | 2590 | 0.507 | 2590 | 0.507 | 1.11 | 1.29 | -0.00691
CFLAllSpcSCEOfLExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCE | OfL | Ex | CZ06 | 2.5897 | 0.00050697 | 0 | 2.99 | 0.00067397 | -0.0116 | 2.5897 | 0.00050697 | 0 | 2.99 | 0.00067397 | -0.0116 |  | CFL | AllSpc | 2590 | 0.507 | 2590 | 0.507 | 1.15 | 1.33 | -0.0044792 | 2590 | 0.507 | 2590 | 0.507 | 1.15 | 1.33 | -0.00448
CFLAllSpcSCEOfLExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCE | OfL | Ex | CZ08 | 2.5897 | 0.00050697 | 0 | 3.01 | 0.00068897 | -0.0111 | 2.5897 | 0.00050697 | 0 | 3.01 | 0.00068897 | -0.0111 |  | CFL | AllSpc | 2590 | 0.507 | 2590 | 0.507 | 1.16 | 1.36 | -0.0042862 | 2590 | 0.507 | 2590 | 0.507 | 1.16 | 1.36 | -0.00429
CFLAllSpcSCEOfLExCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCE | OfL | Ex | CZ09 | 2.5896 | 0.00050696 | 0 | 2.99 | 0.00068896 | -0.0131 | 2.5896 | 0.00050696 | 0 | 2.99 | 0.00068896 | -0.0131 |  | CFL | AllSpc | 2590 | 0.507 | 2590 | 0.507 | 1.15 | 1.36 | -0.0050587 | 2590 | 0.507 | 2590 | 0.507 | 1.15 | 1.36 | -0.00506
CFLAllSpcSCEOfLExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCE | OfL | Ex | CZ10 | 2.5891 | 0.00050691 | 0 | 2.99 | 0.00068491 | -0.0106 | 2.5891 | 0.00050691 | 0 | 2.99 | 0.00068491 | -0.0106 |  | CFL | AllSpc | 2590 | 0.507 | 2590 | 0.507 | 1.15 | 1.35 | -0.0040941 | 2590 | 0.507 | 2590 | 0.507 | 1.15 | 1.35 | -0.00409
CFLAllSpcSCEOfLExCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCE | OfL | Ex | CZ13 | 2.5893 | 0.00050693 | 0 | 2.97 | 0.00067 | -0.0156 | 2.5893 | 0.00050693 | 0 | 2.97 | 0.00067 | -0.0156 |  | CFL | AllSpc | 2590 | 0.507 | 2590 | 0.507 | 1.15 | 1.32 | -0.0060249 | 2590 | 0.507 | 2590 | 0.507 | 1.15 | 1.32 | -0.00602
CFLAllSpcSCEOfLExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCE | OfL | Ex | CZ14 | 2.5893 | 0.00050693 | 0 | 2.94 | 0.00068193 | -0.015 | 2.5893 | 0.00050693 | 0 | 2.94 | 0.00068193 | -0.015 |  | CFL | AllSpc | 2590 | 0.507 | 2590 | 0.507 | 1.14 | 1.35 | -0.0057931 | 2590 | 0.507 | 2590 | 0.507 | 1.14 | 1.35 | -0.00579
CFLAllSpcSCEOfLExCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCE | OfL | Ex | CZ15 | 2.5891 | 0.00050691 | 0 | 3.16 | 0.00068091 | -0.00662 | 2.5891 | 0.00050691 | 0 | 3.16 | 0.00068091 | -0.00662 |  | CFL | AllSpc | 2590 | 0.507 | 2590 | 0.507 | 1.22 | 1.34 | -0.0025569 | 2590 | 0.507 | 2590 | 0.507 | 1.22 | 1.34 | -0.00256
CFLAllSpcSCEOfLExCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCE | OfL | Ex | CZ16 | 2.5893 | 0.00050693 | 0 | 2.74 | 0.000643 | -0.0274 | 2.5893 | 0.00050693 | 0 | 2.74 | 0.000643 | -0.0274 |  | CFL | AllSpc | 2590 | 0.507 | 2590 | 0.507 | 1.06 | 1.27 | -0.010582 | 2590 | 0.507 | 2590 | 0.507 | 1.06 | 1.27 | -0.0106
CFLAllSpcSCEOfLExIOU | Com-Iltg-dWatt-CFL_OSspc | SCE | OfL | Ex | IOU | 2.5896 | 0.00050696 | 0 | 2.9971 | 0.00068329 | -0.011809 | 2.5896 | 0.00050696 | 0 | 2.9971 | 0.00068329 | -0.011809 |  | CFL | AllSpc | 2590 | 0.507 | 2590 | 0.507 | 1.16 | 1.35 | -0.0045602 | 2590 | 0.507 | 2590 | 0.507 | 1.16 | 1.35 | -0.00456
CFLAllSpcSCEOfLNewCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCE | OfL | New | CZ05 | 2.58 | 0.000506 | 0 | 2.86 | 0.000628 | -0.0084 | 2.58 | 0.000506 | 0 | 2.86 | 0.000628 | -0.0084 |  | CFL | AllSpc | 2580 | 0.506 | 2580 | 0.506 | 1.11 | 1.24 | -0.0032558 | 2580 | 0.506 | 2580 | 0.506 | 1.11 | 1.24 | -0.00326
CFLAllSpcSCEOfLNewCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCE | OfL | New | CZ06 | 2.58 | 0.000506 | 0 | 2.97 | 0.000639 | -0.00561 | 2.58 | 0.000506 | 0 | 2.97 | 0.000639 | -0.00561 |  | CFL | AllSpc | 2580 | 0.506 | 2580 | 0.506 | 1.15 | 1.26 | -0.0021744 | 2580 | 0.506 | 2580 | 0.506 | 1.15 | 1.26 | -0.00217
CFLAllSpcSCEOfLNewCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCE | OfL | New | CZ08 | 2.58 | 0.000506 | 0 | 2.98 | 0.000647 | -0.00489 | 2.58 | 0.000506 | 0 | 2.98 | 0.000647 | -0.00489 |  | CFL | AllSpc | 2580 | 0.506 | 2580 | 0.506 | 1.16 | 1.28 | -0.0018953 | 2580 | 0.506 | 2580 | 0.506 | 1.16 | 1.28 | -0.0019
CFLAllSpcSCEOfLNewCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCE | OfL | New | CZ09 | 2.58 | 0.000506 | 0 | 2.97 | 0.000666 | -0.00682 | 2.58 | 0.000506 | 0 | 2.97 | 0.000666 | -0.00682 |  | CFL | AllSpc | 2580 | 0.506 | 2580 | 0.506 | 1.15 | 1.32 | -0.0026434 | 2580 | 0.506 | 2580 | 0.506 | 1.15 | 1.32 | -0.00264
CFLAllSpcSCEOfLNewCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCE | OfL | New | CZ10 | 2.58 | 0.000506 | 0 | 2.99 | 0.000668 | -0.00591 | 2.58 | 0.000506 | 0 | 2.99 | 0.000668 | -0.00591 |  | CFL | AllSpc | 2580 | 0.506 | 2580 | 0.506 | 1.16 | 1.32 | -0.0022907 | 2580 | 0.506 | 2580 | 0.506 | 1.16 | 1.32 | -0.00229
CFLAllSpcSCEOfLNewCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCE | OfL | New | CZ13 | 2.58 | 0.000506 | 0 | 2.93 | 0.00065 | -0.0088 | 2.58 | 0.000506 | 0 | 2.93 | 0.00065 | -0.0088 |  | CFL | AllSpc | 2580 | 0.506 | 2580 | 0.506 | 1.14 | 1.28 | -0.0034109 | 2580 | 0.506 | 2580 | 0.506 | 1.14 | 1.28 | -0.00341
CFLAllSpcSCEOfLNewCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCE | OfL | New | CZ14 | 2.58 | 0.000506 | 0 | 2.94 | 0.000675 | -0.00777 | 2.58 | 0.000506 | 0 | 2.94 | 0.000675 | -0.00777 |  | CFL | AllSpc | 2580 | 0.506 | 2580 | 0.506 | 1.14 | 1.33 | -0.0030116 | 2580 | 0.506 | 2580 | 0.506 | 1.14 | 1.33 | -0.00301
CFLAllSpcSCEOfLNewCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCE | OfL | New | CZ15 | 2.58 | 0.000506 | 0 | 3.11 | 0.000662 | -0.00287 | 2.58 | 0.000506 | 0 | 3.11 | 0.000662 | -0.00287 |  | CFL | AllSpc | 2580 | 0.506 | 2580 | 0.506 | 1.21 | 1.31 | -0.0011124 | 2580 | 0.506 | 2580 | 0.506 | 1.21 | 1.31 | -0.00111
CFLAllSpcSCEOfLNewCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCE | OfL | New | CZ16 | 2.58 | 0.000506 | 0 | 2.78 | 0.000635 | -0.0215 | 2.58 | 0.000506 | 0 | 2.78 | 0.000635 | -0.0215 |  | CFL | AllSpc | 2580 | 0.506 | 2580 | 0.506 | 1.08 | 1.25 | -0.0083333 | 2580 | 0.506 | 2580 | 0.506 | 1.08 | 1.25 | -0.00833
CFLAllSpcSCEOfLNewIOU | Com-Iltg-dWatt-CFL_OSspc | SCE | OfL | New | IOU | 2.58 | 0.000506 | 0 | 2.979 | 0.00065543 | -0.0060046 | 2.58 | 0.000506 | 0 | 2.979 | 0.00065543 | -0.0060046 |  | CFL | AllSpc | 2580 | 0.506 | 2580 | 0.506 | 1.15 | 1.3 | -0.0023273 | 2580 | 0.506 | 2580 | 0.506 | 1.15 | 1.3 | -0.00233
CFLAllSpcSCEOfSExCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCE | OfS | Ex | CZ05 | 2.4406 | 0.00050211 | 0 | 2.6596 | 0.00063111 | -0.0076501 | 2.4406 | 0.00050211 | 0 | 2.6596 | 0.00063111 | -0.0076501 |  | CFL | AllSpc | 2440 | 0.502 | 2440 | 0.502 | 1.09 | 1.26 | -0.0031346 | 2440 | 0.502 | 2440 | 0.502 | 1.09 | 1.26 | -0.00313
CFLAllSpcSCEOfSExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCE | OfS | Ex | CZ06 | 2.4406 | 0.00050211 | 0 | 2.7806 | 0.00064011 | -0.0036901 | 2.4406 | 0.00050211 | 0 | 2.7806 | 0.00064011 | -0.0036901 |  | CFL | AllSpc | 2440 | 0.502 | 2440 | 0.502 | 1.14 | 1.27 | -0.001512 | 2440 | 0.502 | 2440 | 0.502 | 1.14 | 1.27 | -0.00151
CFLAllSpcSCEOfSExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCE | OfS | Ex | CZ08 | 2.4406 | 0.00050211 | 0 | 2.8005 | 0.00064411 | -0.0033496 | 2.4406 | 0.00050211 | 0 | 2.8005 | 0.00064411 | -0.0033496 |  | CFL | AllSpc | 2440 | 0.502 | 2440 | 0.502 | 1.15 | 1.28 | -0.0013725 | 2440 | 0.502 | 2440 | 0.502 | 1.15 | 1.28 | -0.00137
CFLAllSpcSCEOfSExCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCE | OfS | Ex | CZ09 | 2.4405 | 0.00050211 | 0 | 2.7895 | 0.00065011 | -0.0041505 | 2.4405 | 0.00050211 | 0 | 2.7895 | 0.00065011 | -0.0041505 |  | CFL | AllSpc | 2440 | 0.502 | 2440 | 0.502 | 1.14 | 1.29 | -0.0017007 | 2440 | 0.502 | 2440 | 0.502 | 1.14 | 1.29 | -0.0017
CFLAllSpcSCEOfSExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCE | OfS | Ex | CZ10 | 2.4406 | 0.00050212 | 0 | 2.75 | 0.00064412 | -0.0038897 | 2.4406 | 0.00050212 | 0 | 2.75 | 0.00064412 | -0.0038897 |  | CFL | AllSpc | 2440 | 0.502 | 2440 | 0.502 | 1.13 | 1.28 | -0.0015938 | 2440 | 0.502 | 2440 | 0.502 | 1.13 | 1.28 | -0.00159
CFLAllSpcSCEOfSExCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCE | OfS | Ex | CZ13 | 2.4404 | 0.00050208 | 0 | 2.6998 | 0.00064008 | -0.00917 | 2.4404 | 0.00050208 | 0 | 2.6998 | 0.00064008 | -0.00917 |  | CFL | AllSpc | 2440 | 0.502 | 2440 | 0.502 | 1.11 | 1.27 | -0.0037576 | 2440 | 0.502 | 2440 | 0.502 | 1.11 | 1.27 | -0.00376
CFLAllSpcSCEOfSExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCE | OfS | Ex | CZ14 | 2.4405 | 0.00050211 | 0 | 2.7005 | 0.00065311 | -0.0072808 | 2.4405 | 0.00050211 | 0 | 2.7005 | 0.00065311 | -0.0072808 |  | CFL | AllSpc | 2440 | 0.502 | 2440 | 0.502 | 1.11 | 1.3 | -0.0029833 | 2440 | 0.502 | 2440 | 0.502 | 1.11 | 1.3 | -0.00298
CFLAllSpcSCEOfSExCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCE | OfS | Ex | CZ15 | 2.4409 | 0.00050217 | 0 | 2.9409 | 0.00063817 | -0.0011509 | 2.4409 | 0.00050217 | 0 | 2.9409 | 0.00063817 | -0.0011509 |  | CFL | AllSpc | 2440 | 0.502 | 2440 | 0.502 | 1.2 | 1.27 | -0.0004715 | 2440 | 0.502 | 2440 | 0.502 | 1.2 | 1.27 | -0.000472
CFLAllSpcSCEOfSExCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCE | OfS | Ex | CZ16 | 2.4407 | 0.00050214 | 0 | 2.4507 | 0.00062814 | -0.017307 | 2.4407 | 0.00050214 | 0 | 2.4507 | 0.00062814 | -0.017307 |  | CFL | AllSpc | 2440 | 0.502 | 2440 | 0.502 | 1 | 1.25 | -0.007091 | 2440 | 0.502 | 2440 | 0.502 | 1 | 1.25 | -0.00709
CFLAllSpcSCEOfSExIOU | Com-Iltg-dWatt-CFL_OSspc | SCE | OfS | Ex | IOU | 2.4406 | 0.00050211 | 0 | 2.7779 | 0.00064351 | -0.0041684 | 2.4406 | 0.00050211 | 0 | 2.7779 | 0.00064351 | -0.0041684 |  | CFL | AllSpc | 2440 | 0.502 | 2440 | 0.502 | 1.14 | 1.28 | -0.001708 | 2440 | 0.502 | 2440 | 0.502 | 1.14 | 1.28 | -0.00171
CFLAllSpcSCEOfSNewCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCE | OfS | New | CZ05 | 2.45 | 0.000504 | 0 | 2.56 | 0.000623 | -0.00693 | 2.45 | 0.000504 | 0 | 2.56 | 0.000623 | -0.00693 |  | CFL | AllSpc | 2450 | 0.504 | 2450 | 0.504 | 1.04 | 1.24 | -0.0028286 | 2450 | 0.504 | 2450 | 0.504 | 1.04 | 1.24 | -0.00283
CFLAllSpcSCEOfSNewCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCE | OfS | New | CZ06 | 2.45 | 0.000504 | 0 | 2.7 | 0.000632 | -0.00279 | 2.45 | 0.000504 | 0 | 2.7 | 0.000632 | -0.00279 |  | CFL | AllSpc | 2450 | 0.504 | 2450 | 0.504 | 1.1 | 1.25 | -0.0011388 | 2450 | 0.504 | 2450 | 0.504 | 1.1 | 1.25 | -0.00114
CFLAllSpcSCEOfSNewCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCE | OfS | New | CZ08 | 2.45 | 0.000504 | 0 | 2.72 | 0.00064 | -0.00247 | 2.45 | 0.000504 | 0 | 2.72 | 0.00064 | -0.00247 |  | CFL | AllSpc | 2450 | 0.504 | 2450 | 0.504 | 1.11 | 1.27 | -0.0010082 | 2450 | 0.504 | 2450 | 0.504 | 1.11 | 1.27 | -0.00101
CFLAllSpcSCEOfSNewCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCE | OfS | New | CZ09 | 2.45 | 0.000504 | 0 | 2.71 | 0.000656 | -0.00279 | 2.45 | 0.000504 | 0 | 2.71 | 0.000656 | -0.00279 |  | CFL | AllSpc | 2450 | 0.504 | 2450 | 0.504 | 1.11 | 1.3 | -0.0011388 | 2450 | 0.504 | 2450 | 0.504 | 1.11 | 1.3 | -0.00114
CFLAllSpcSCEOfSNewCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCE | OfS | New | CZ10 | 2.45 | 0.000504 | 0 | 2.74 | 0.000664 | -0.00196 | 2.45 | 0.000504 | 0 | 2.74 | 0.000664 | -0.00196 |  | CFL | AllSpc | 2450 | 0.504 | 2450 | 0.504 | 1.12 | 1.32 | -0.0008 | 2450 | 0.504 | 2450 | 0.504 | 1.12 | 1.32 | -0.0008
CFLAllSpcSCEOfSNewCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCE | OfS | New | CZ13 | 2.45 | 0.000504 | 0 | 2.66 | 0.000652 | -0.00734 | 2.45 | 0.000504 | 0 | 2.66 | 0.000652 | -0.00734 |  | CFL | AllSpc | 2450 | 0.504 | 2450 | 0.504 | 1.09 | 1.29 | -0.0029959 | 2450 | 0.504 | 2450 | 0.504 | 1.09 | 1.29 | -0.003
CFLAllSpcSCEOfSNewCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCE | OfS | New | CZ14 | 2.45 | 0.000504 | 0 | 2.68 | 0.000663 | -0.00612 | 2.45 | 0.000504 | 0 | 2.68 | 0.000663 | -0.00612 |  | CFL | AllSpc | 2450 | 0.504 | 2450 | 0.504 | 1.09 | 1.32 | -0.002498 | 2450 | 0.504 | 2450 | 0.504 | 1.09 | 1.32 | -0.0025
CFLAllSpcSCEOfSNewCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCE | OfS | New | CZ15 | 2.45 | 0.000504 | 0 | 2.87 | 0.000671 | -0.000183 | 2.45 | 0.000504 | 0 | 2.87 | 0.000671 | -0.000183 |  | CFL | AllSpc | 2450 | 0.504 | 2450 | 0.504 | 1.17 | 1.33 | -7.4694e-05 | 2450 | 0.504 | 2450 | 0.504 | 1.17 | 1.33 | -7.47e-05
CFLAllSpcSCEOfSNewCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCE | OfS | New | CZ16 | 2.45 | 0.000504 | 0 | 2.45 | 0.000632 | -0.0164 | 2.45 | 0.000504 | 0 | 2.45 | 0.000632 | -0.0164 |  | CFL | AllSpc | 2450 | 0.504 | 2450 | 0.504 | 1 | 1.25 | -0.0066939 | 2450 | 0.504 | 2450 | 0.504 | 1 | 1.25 | -0.00669
CFLAllSpcSCEOfSNewIOU | Com-Iltg-dWatt-CFL_OSspc | SCE | OfS | New | IOU | 2.45 | 0.000504 | 0 | 2.7231 | 0.00065088 | -0.0028552 | 2.45 | 0.000504 | 0 | 2.7231 | 0.00065088 | -0.0028552 |  | CFL | AllSpc | 2450 | 0.504 | 2450 | 0.504 | 1.11 | 1.29 | -0.0011654 | 2450 | 0.504 | 2450 | 0.504 | 1.11 | 1.29 | -0.00117
CFLAllSpcSCERFFExCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCE | RFF | Ex | CZ05 | 4.31 | 0.000687 | 0 | 4.48 | 0.000813 | -0.0403 | 4.31 | 0.000687 | 0 | 4.48 | 0.000813 | -0.0403 |  | CFL | AllSpc | 4310 | 0.687 | 4310 | 0.687 | 1.04 | 1.18 | -0.0093503 | 4310 | 0.687 | 4310 | 0.687 | 1.04 | 1.18 | -0.00935
CFLAllSpcSCERFFExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCE | RFF | Ex | CZ06 | 4.31 | 0.000687 | 0 | 4.7 | 0.000831 | -0.0225 | 4.31 | 0.000687 | 0 | 4.7 | 0.000831 | -0.0225 |  | CFL | AllSpc | 4310 | 0.687 | 4310 | 0.687 | 1.09 | 1.21 | -0.0052204 | 4310 | 0.687 | 4310 | 0.687 | 1.09 | 1.21 | -0.00522
CFLAllSpcSCERFFExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCE | RFF | Ex | CZ08 | 4.31 | 0.000687 | 0 | 4.75 | 0.000824 | -0.0198 | 4.31 | 0.000687 | 0 | 4.75 | 0.000824 | -0.0198 |  | CFL | AllSpc | 4310 | 0.687 | 4310 | 0.687 | 1.1 | 1.2 | -0.004594 | 4310 | 0.687 | 4310 | 0.687 | 1.1 | 1.2 | -0.00459
CFLAllSpcSCERFFExCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCE | RFF | Ex | CZ09 | 4.31 | 0.000687 | 0 | 4.75 | 0.00084113 | -0.0207 | 4.31 | 0.000687 | 0 | 4.75 | 0.00084113 | -0.0207 |  | CFL | AllSpc | 4310 | 0.687 | 4310 | 0.687 | 1.1 | 1.22 | -0.0048028 | 4310 | 0.687 | 4310 | 0.687 | 1.1 | 1.22 | -0.0048
CFLAllSpcSCERFFExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCE | RFF | Ex | CZ10 | 4.31 | 0.000687 | 0 | 4.66 | 0.00082806 | -0.0229 | 4.31 | 0.000687 | 0 | 4.66 | 0.00082806 | -0.0229 |  | CFL | AllSpc | 4310 | 0.687 | 4310 | 0.687 | 1.08 | 1.21 | -0.0053132 | 4310 | 0.687 | 4310 | 0.687 | 1.08 | 1.21 | -0.00531
CFLAllSpcSCERFFExCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCE | RFF | Ex | CZ13 | 4.31 | 0.000687 | 0 | 4.66 | 0.000833 | -0.0303 | 4.31 | 0.000687 | 0 | 4.66 | 0.000833 | -0.0303 |  | CFL | AllSpc | 4310 | 0.687 | 4310 | 0.687 | 1.08 | 1.21 | -0.0070302 | 4310 | 0.687 | 4310 | 0.687 | 1.08 | 1.21 | -0.00703
CFLAllSpcSCERFFExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCE | RFF | Ex | CZ14 | 4.31 | 0.000687 | 0 | 4.6294 | 0.000843 | -0.032 | 4.31 | 0.000687 | 0 | 4.6294 | 0.000843 | -0.032 |  | CFL | AllSpc | 4310 | 0.687 | 4310 | 0.687 | 1.07 | 1.23 | -0.0074246 | 4310 | 0.687 | 4310 | 0.687 | 1.07 | 1.23 | -0.00742
CFLAllSpcSCERFFExCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCE | RFF | Ex | CZ15 | 4.31 | 0.000687 | 0 | 4.95 | 0.000839 | -0.0107 | 4.31 | 0.000687 | 0 | 4.95 | 0.000839 | -0.0107 |  | CFL | AllSpc | 4310 | 0.687 | 4310 | 0.687 | 1.15 | 1.22 | -0.0024826 | 4310 | 0.687 | 4310 | 0.687 | 1.15 | 1.22 | -0.00248
CFLAllSpcSCERFFExCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCE | RFF | Ex | CZ16 | 4.31 | 0.000687 | 0 | 4.31 | 0.000815 | -0.0582 | 4.31 | 0.000687 | 0 | 4.31 | 0.000815 | -0.0582 |  | CFL | AllSpc | 4310 | 0.687 | 4310 | 0.687 | 1 | 1.19 | -0.013503 | 4310 | 0.687 | 4310 | 0.687 | 1 | 1.19 | -0.0135
CFLAllSpcSCERFFExIOU | Com-Iltg-dWatt-CFL_OSspc | SCE | RFF | Ex | IOU | 4.31 | 0.000687 | 0 | 4.7106 | 0.00083059 | -0.022401 | 4.31 | 0.000687 | 0 | 4.7106 | 0.00083059 | -0.022401 |  | CFL | AllSpc | 4310 | 0.687 | 4310 | 0.687 | 1.09 | 1.21 | -0.0051975 | 4310 | 0.687 | 4310 | 0.687 | 1.09 | 1.21 | -0.0052
CFLAllSpcSCERFFNewCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCE | RFF | New | CZ05 | 4.31 | 0.000687 | 0 | 4.42 | 0.000826 | -0.0391 | 4.31 | 0.000687 | 0 | 4.42 | 0.000826 | -0.0391 |  | CFL | AllSpc | 4310 | 0.687 | 4310 | 0.687 | 1.03 | 1.2 | -0.0090719 | 4310 | 0.687 | 4310 | 0.687 | 1.03 | 1.2 | -0.00907
CFLAllSpcSCERFFNewCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCE | RFF | New | CZ06 | 4.31 | 0.000687 | 0 | 4.63 | 0.00085 | -0.0232 | 4.31 | 0.000687 | 0 | 4.63 | 0.00085 | -0.0232 |  | CFL | AllSpc | 4310 | 0.687 | 4310 | 0.687 | 1.07 | 1.24 | -0.0053828 | 4310 | 0.687 | 4310 | 0.687 | 1.07 | 1.24 | -0.00538
CFLAllSpcSCERFFNewCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCE | RFF | New | CZ08 | 4.31 | 0.000687 | 0 | 4.64 | 0.000824 | -0.0228 | 4.31 | 0.000687 | 0 | 4.64 | 0.000824 | -0.0228 |  | CFL | AllSpc | 4310 | 0.687 | 4310 | 0.687 | 1.08 | 1.2 | -0.00529 | 4310 | 0.687 | 4310 | 0.687 | 1.08 | 1.2 | -0.00529
CFLAllSpcSCERFFNewCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCE | RFF | New | CZ09 | 4.31 | 0.000687 | 0 | 4.72 | 0.000881 | -0.0255 | 4.31 | 0.000687 | 0 | 4.72 | 0.000881 | -0.0255 |  | CFL | AllSpc | 4310 | 0.687 | 4310 | 0.687 | 1.1 | 1.28 | -0.0059165 | 4310 | 0.687 | 4310 | 0.687 | 1.1 | 1.28 | -0.00592
CFLAllSpcSCERFFNewCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCE | RFF | New | CZ10 | 4.31 | 0.000687 | 0 | 4.75 | 0.000888 | -0.0266 | 4.31 | 0.000687 | 0 | 4.75 | 0.000888 | -0.0266 |  | CFL | AllSpc | 4310 | 0.687 | 4310 | 0.687 | 1.1 | 1.29 | -0.0061717 | 4310 | 0.687 | 4310 | 0.687 | 1.1 | 1.29 | -0.00617
CFLAllSpcSCERFFNewCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCE | RFF | New | CZ13 | 4.31 | 0.000687 | 0 | 4.73 | 0.000885 | -0.0348 | 4.31 | 0.000687 | 0 | 4.73 | 0.000885 | -0.0348 |  | CFL | AllSpc | 4310 | 0.687 | 4310 | 0.687 | 1.1 | 1.29 | -0.0080742 | 4310 | 0.687 | 4310 | 0.687 | 1.1 | 1.29 | -0.00807
CFLAllSpcSCERFFNewCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCE | RFF | New | CZ14 | 4.31 | 0.000687 | 0 | 4.73 | 0.000893 | -0.037 | 4.31 | 0.000687 | 0 | 4.73 | 0.000893 | -0.037 |  | CFL | AllSpc | 4310 | 0.687 | 4310 | 0.687 | 1.1 | 1.3 | -0.0085847 | 4310 | 0.687 | 4310 | 0.687 | 1.1 | 1.3 | -0.00858
CFLAllSpcSCERFFNewCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCE | RFF | New | CZ15 | 4.31 | 0.000687 | 0 | 5.07 | 0.000904 | -0.0132 | 4.31 | 0.000687 | 0 | 5.07 | 0.000904 | -0.0132 |  | CFL | AllSpc | 4310 | 0.687 | 4310 | 0.687 | 1.18 | 1.32 | -0.0030626 | 4310 | 0.687 | 4310 | 0.687 | 1.18 | 1.32 | -0.00306
CFLAllSpcSCERFFNewCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCE | RFF | New | CZ16 | 4.31 | 0.000687 | 0 | 4.37 | 0.000848 | -0.0625 | 4.31 | 0.000687 | 0 | 4.37 | 0.000848 | -0.0625 |  | CFL | AllSpc | 4310 | 0.687 | 4310 | 0.687 | 1.01 | 1.23 | -0.014501 | 4310 | 0.687 | 4310 | 0.687 | 1.01 | 1.23 | -0.0145
CFLAllSpcSCERFFNewIOU | Com-Iltg-dWatt-CFL_OSspc | SCE | RFF | New | IOU | 4.31 | 0.000687 | 0 | 4.7018 | 0.00086386 | -0.025591 | 4.31 | 0.000687 | 0 | 4.7018 | 0.00086386 | -0.025591 |  | CFL | AllSpc | 4310 | 0.687 | 4310 | 0.687 | 1.09 | 1.26 | -0.0059377 | 4310 | 0.687 | 4310 | 0.687 | 1.09 | 1.26 | -0.00594
CFLAllSpcSCERSDExCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCE | RSD | Ex | CZ05 | 4.33 | 0.000677 | 0 | 4.55 | 0.00082367 | -0.0389 | 4.33 | 0.000677 | 0 | 4.55 | 0.00082367 | -0.0389 |  | CFL | AllSpc | 4330 | 0.677 | 4330 | 0.677 | 1.05 | 1.22 | -0.0089838 | 4330 | 0.677 | 4330 | 0.677 | 1.05 | 1.22 | -0.00898
CFLAllSpcSCERSDExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCE | RSD | Ex | CZ06 | 4.33 | 0.000677 | 0 | 4.82 | 0.00083367 | -0.02 | 4.33 | 0.000677 | 0 | 4.82 | 0.00083367 | -0.02 |  | CFL | AllSpc | 4330 | 0.677 | 4330 | 0.677 | 1.11 | 1.23 | -0.0046189 | 4330 | 0.677 | 4330 | 0.677 | 1.11 | 1.23 | -0.00462
CFLAllSpcSCERSDExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCE | RSD | Ex | CZ08 | 4.33 | 0.000677 | 0 | 4.85 | 0.00081267 | -0.017 | 4.33 | 0.000677 | 0 | 4.85 | 0.00081267 | -0.017 |  | CFL | AllSpc | 4330 | 0.677 | 4330 | 0.677 | 1.12 | 1.2 | -0.0039261 | 4330 | 0.677 | 4330 | 0.677 | 1.12 | 1.2 | -0.00393
CFLAllSpcSCERSDExCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCE | RSD | Ex | CZ09 | 4.33 | 0.000677 | 0 | 4.85 | 0.000826 | -0.0194 | 4.33 | 0.000677 | 0 | 4.85 | 0.000826 | -0.0194 |  | CFL | AllSpc | 4330 | 0.677 | 4330 | 0.677 | 1.12 | 1.22 | -0.0044804 | 4330 | 0.677 | 4330 | 0.677 | 1.12 | 1.22 | -0.00448
CFLAllSpcSCERSDExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCE | RSD | Ex | CZ10 | 4.33 | 0.000677 | 0 | 4.77 | 0.000801 | -0.0205 | 4.33 | 0.000677 | 0 | 4.77 | 0.000801 | -0.0205 |  | CFL | AllSpc | 4330 | 0.677 | 4330 | 0.677 | 1.1 | 1.18 | -0.0047344 | 4330 | 0.677 | 4330 | 0.677 | 1.1 | 1.18 | -0.00473
CFLAllSpcSCERSDExCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCE | RSD | Ex | CZ13 | 4.33 | 0.000677 | 0 | 4.74 | 0.00083394 | -0.0301 | 4.33 | 0.000677 | 0 | 4.74 | 0.00083394 | -0.0301 |  | CFL | AllSpc | 4330 | 0.677 | 4330 | 0.677 | 1.09 | 1.23 | -0.0069515 | 4330 | 0.677 | 4330 | 0.677 | 1.09 | 1.23 | -0.00695
CFLAllSpcSCERSDExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCE | RSD | Ex | CZ14 | 4.33 | 0.000677 | 0 | 4.69 | 0.00080294 | -0.0312 | 4.33 | 0.000677 | 0 | 4.69 | 0.00080294 | -0.0312 |  | CFL | AllSpc | 4330 | 0.677 | 4330 | 0.677 | 1.08 | 1.19 | -0.0072055 | 4330 | 0.677 | 4330 | 0.677 | 1.08 | 1.19 | -0.00721
CFLAllSpcSCERSDExCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCE | RSD | Ex | CZ15 | 4.33 | 0.000677 | 0 | 5.1 | 0.000847 | -0.00771 | 4.33 | 0.000677 | 0 | 5.1 | 0.000847 | -0.00771 |  | CFL | AllSpc | 4330 | 0.677 | 4330 | 0.677 | 1.18 | 1.25 | -0.0017806 | 4330 | 0.677 | 4330 | 0.677 | 1.18 | 1.25 | -0.00178
CFLAllSpcSCERSDExCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCE | RSD | Ex | CZ16 | 4.33 | 0.000677 | 0 | 4.36 | 0.000803 | -0.0554 | 4.33 | 0.000677 | 0 | 4.36 | 0.000803 | -0.0554 |  | CFL | AllSpc | 4330 | 0.677 | 4330 | 0.677 | 1.01 | 1.19 | -0.012794 | 4330 | 0.677 | 4330 | 0.677 | 1.01 | 1.19 | -0.0128
CFLAllSpcSCERSDExIOU | Com-Iltg-dWatt-CFL_OSspc | SCE | RSD | Ex | IOU | 4.33 | 0.000677 | 0 | 4.8164 | 0.0008181 | -0.020121 | 4.33 | 0.000677 | 0 | 4.8164 | 0.0008181 | -0.020121 |  | CFL | AllSpc | 4330 | 0.677 | 4330 | 0.677 | 1.11 | 1.21 | -0.0046469 | 4330 | 0.677 | 4330 | 0.677 | 1.11 | 1.21 | -0.00465
CFLAllSpcSCERSDNewCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCE | RSD | New | CZ05 | 4.33 | 0.000677 | 0 | 4.49 | 0.000832 | -0.0424 | 4.33 | 0.000677 | 0 | 4.49 | 0.000832 | -0.0424 |  | CFL | AllSpc | 4330 | 0.677 | 4330 | 0.677 | 1.04 | 1.23 | -0.0097921 | 4330 | 0.677 | 4330 | 0.677 | 1.04 | 1.23 | -0.00979
CFLAllSpcSCERSDNewCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCE | RSD | New | CZ06 | 4.33 | 0.000677 | 0 | 4.74 | 0.000845 | -0.0239 | 4.33 | 0.000677 | 0 | 4.74 | 0.000845 | -0.0239 |  | CFL | AllSpc | 4330 | 0.677 | 4330 | 0.677 | 1.09 | 1.25 | -0.0055196 | 4330 | 0.677 | 4330 | 0.677 | 1.09 | 1.25 | -0.00552
CFLAllSpcSCERSDNewCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCE | RSD | New | CZ08 | 4.33 | 0.000677 | 0 | 4.65 | 0.000737 | -0.0199 | 4.33 | 0.000677 | 0 | 4.65 | 0.000737 | -0.0199 |  | CFL | AllSpc | 4330 | 0.677 | 4330 | 0.677 | 1.07 | 1.09 | -0.0045958 | 4330 | 0.677 | 4330 | 0.677 | 1.07 | 1.09 | -0.0046
CFLAllSpcSCERSDNewCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCE | RSD | New | CZ09 | 4.33 | 0.000677 | 0 | 4.82 | 0.000887 | -0.0221 | 4.33 | 0.000677 | 0 | 4.82 | 0.000887 | -0.0221 |  | CFL | AllSpc | 4330 | 0.677 | 4330 | 0.677 | 1.11 | 1.31 | -0.0051039 | 4330 | 0.677 | 4330 | 0.677 | 1.11 | 1.31 | -0.0051
CFLAllSpcSCERSDNewCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCE | RSD | New | CZ10 | 4.33 | 0.000677 | 0 | 4.83 | 0.000887 | -0.0226 | 4.33 | 0.000677 | 0 | 4.83 | 0.000887 | -0.0226 |  | CFL | AllSpc | 4330 | 0.677 | 4330 | 0.677 | 1.12 | 1.31 | -0.0052194 | 4330 | 0.677 | 4330 | 0.677 | 1.12 | 1.31 | -0.00522
CFLAllSpcSCERSDNewCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCE | RSD | New | CZ13 | 4.33 | 0.000677 | 0 | 4.79 | 0.000892 | -0.0327 | 4.33 | 0.000677 | 0 | 4.79 | 0.000892 | -0.0327 |  | CFL | AllSpc | 4330 | 0.677 | 4330 | 0.677 | 1.11 | 1.32 | -0.007552 | 4330 | 0.677 | 4330 | 0.677 | 1.11 | 1.32 | -0.00755
CFLAllSpcSCERSDNewCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCE | RSD | New | CZ14 | 4.33 | 0.000677 | 0 | 4.77 | 0.000885 | -0.0336 | 4.33 | 0.000677 | 0 | 4.77 | 0.000885 | -0.0336 |  | CFL | AllSpc | 4330 | 0.677 | 4330 | 0.677 | 1.1 | 1.31 | -0.0077598 | 4330 | 0.677 | 4330 | 0.677 | 1.1 | 1.31 | -0.00776
CFLAllSpcSCERSDNewCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCE | RSD | New | CZ15 | 4.33 | 0.000677 | 0 | 5.19 | 0.000915 | -0.00979 | 4.33 | 0.000677 | 0 | 5.19 | 0.000915 | -0.00979 |  | CFL | AllSpc | 4330 | 0.677 | 4330 | 0.677 | 1.2 | 1.35 | -0.002261 | 4330 | 0.677 | 4330 | 0.677 | 1.2 | 1.35 | -0.00226
CFLAllSpcSCERSDNewCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCE | RSD | New | CZ16 | 4.33 | 0.000677 | 0 | 4.39 | 0.000838 | -0.0459 | 4.33 | 0.000677 | 0 | 4.39 | 0.000838 | -0.0459 |  | CFL | AllSpc | 4330 | 0.677 | 4330 | 0.677 | 1.01 | 1.24 | -0.0106 | 4330 | 0.677 | 4330 | 0.677 | 1.01 | 1.24 | -0.0106
CFLAllSpcSCERSDNewIOU | Com-Iltg-dWatt-CFL_OSspc | SCE | RSD | New | IOU | 4.33 | 0.000677 | 0 | 4.7722 | 0.00084254 | -0.022788 | 4.33 | 0.000677 | 0 | 4.7722 | 0.00084254 | -0.022788 |  | CFL | AllSpc | 4330 | 0.677 | 4330 | 0.677 | 1.1 | 1.24 | -0.0052628 | 4330 | 0.677 | 4330 | 0.677 | 1.1 | 1.24 | -0.00526
CFLAllSpcSCERt3ExCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCE | Rt3 | Ex | CZ05 | 3.69 | 0.00062094 | 0 | 3.97 | 0.00078449 | -0.020694 | 3.69 | 0.00062094 | 0 | 3.97 | 0.00078449 | -0.020694 |  | CFL | AllSpc | 3690 | 0.621 | 3690 | 0.621 | 1.08 | 1.26 | -0.005608 | 3690 | 0.621 | 3690 | 0.621 | 1.08 | 1.26 | -0.00561
CFLAllSpcSCERt3ExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCE | Rt3 | Ex | CZ06 | 3.69 | 0.00062094 | 0 | 4.25 | 0.00078494 | -0.00535 | 3.69 | 0.00062094 | 0 | 4.25 | 0.00078494 | -0.00535 |  | CFL | AllSpc | 3690 | 0.621 | 3690 | 0.621 | 1.15 | 1.26 | -0.0014499 | 3690 | 0.621 | 3690 | 0.621 | 1.15 | 1.26 | -0.00145
CFLAllSpcSCERt3ExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCE | Rt3 | Ex | CZ08 | 3.69 | 0.00062093 | 0 | 4.26 | 0.00077349 | -0.0046838 | 3.69 | 0.00062093 | 0 | 4.26 | 0.00077349 | -0.0046838 |  | CFL | AllSpc | 3690 | 0.621 | 3690 | 0.621 | 1.15 | 1.25 | -0.0012693 | 3690 | 0.621 | 3690 | 0.621 | 1.15 | 1.25 | -0.00127
CFLAllSpcSCERt3ExCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCE | Rt3 | Ex | CZ09 | 3.69 | 0.00062093 | 0 | 4.2093 | 0.00078387 | -0.0071937 | 3.69 | 0.00062093 | 0 | 4.2093 | 0.00078387 | -0.0071937 |  | CFL | AllSpc | 3690 | 0.621 | 3690 | 0.621 | 1.14 | 1.26 | -0.0019495 | 3690 | 0.621 | 3690 | 0.621 | 1.14 | 1.26 | -0.00195
CFLAllSpcSCERt3ExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCE | Rt3 | Ex | CZ10 | 3.69 | 0.00062088 | 0 | 4.11 | 0.00077276 | -0.00841 | 3.69 | 0.00062088 | 0 | 4.11 | 0.00077276 | -0.00841 |  | CFL | AllSpc | 3690 | 0.621 | 3690 | 0.621 | 1.11 | 1.24 | -0.0022791 | 3690 | 0.621 | 3690 | 0.621 | 1.11 | 1.24 | -0.00228
CFLAllSpcSCERt3ExCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCE | Rt3 | Ex | CZ13 | 3.69 | 0.0006209 | 0 | 4 | 0.00079079 | -0.022911 | 3.69 | 0.0006209 | 0 | 4 | 0.00079079 | -0.022911 |  | CFL | AllSpc | 3690 | 0.621 | 3690 | 0.621 | 1.08 | 1.27 | -0.0062088 | 3690 | 0.621 | 3690 | 0.621 | 1.08 | 1.27 | -0.00621
CFLAllSpcSCERt3ExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCE | Rt3 | Ex | CZ14 | 3.69 | 0.0006209 | 0 | 3.95 | 0.00078268 | -0.0246 | 3.69 | 0.0006209 | 0 | 3.95 | 0.00078268 | -0.0246 |  | CFL | AllSpc | 3690 | 0.621 | 3690 | 0.621 | 1.07 | 1.26 | -0.0066667 | 3690 | 0.621 | 3690 | 0.621 | 1.07 | 1.26 | -0.00667
CFLAllSpcSCERt3ExCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCE | Rt3 | Ex | CZ15 | 3.69 | 0.00062088 | 0 | 4.2588 | 0.00079488 | -0.00213 | 3.69 | 0.00062088 | 0 | 4.2588 | 0.00079488 | -0.00213 |  | CFL | AllSpc | 3690 | 0.621 | 3690 | 0.621 | 1.15 | 1.28 | -0.00057724 | 3690 | 0.621 | 3690 | 0.621 | 1.15 | 1.28 | -0.000577
CFLAllSpcSCERt3ExCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCE | Rt3 | Ex | CZ16 | 3.69 | 0.0006209 | 0 | 3.61 | 0.00076879 | -0.0476 | 3.69 | 0.0006209 | 0 | 3.61 | 0.00076879 | -0.0476 |  | CFL | AllSpc | 3690 | 0.621 | 3690 | 0.621 | 0.978 | 1.24 | -0.0129 | 3690 | 0.621 | 3690 | 0.621 | 0.978 | 1.24 | -0.0129
CFLAllSpcSCERt3ExIOU | Com-Iltg-dWatt-CFL_OSspc | SCE | Rt3 | Ex | IOU | 3.69 | 0.00062092 | 0 | 4.1911 | 0.0007792 | -0.0076933 | 3.69 | 0.00062092 | 0 | 4.1911 | 0.0007792 | -0.0076933 |  | CFL | AllSpc | 3690 | 0.621 | 3690 | 0.621 | 1.14 | 1.25 | -0.0020849 | 3690 | 0.621 | 3690 | 0.621 | 1.14 | 1.25 | -0.00208
CFLAllSpcSCERt3NewCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCE | Rt3 | New | CZ05 | 3.69 | 0.00062 | 0 | 3.82 | 0.000766 | -0.0256 | 3.69 | 0.00062 | 0 | 3.82 | 0.000766 | -0.0256 |  | CFL | AllSpc | 3690 | 0.62 | 3690 | 0.62 | 1.04 | 1.24 | -0.0069377 | 3690 | 0.62 | 3690 | 0.62 | 1.04 | 1.24 | -0.00694
CFLAllSpcSCERt3NewCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCE | Rt3 | New | CZ06 | 3.69 | 0.00062 | 0 | 4.09 | 0.000759 | -0.00771 | 3.69 | 0.00062 | 0 | 4.09 | 0.000759 | -0.00771 |  | CFL | AllSpc | 3690 | 0.62 | 3690 | 0.62 | 1.11 | 1.22 | -0.0020894 | 3690 | 0.62 | 3690 | 0.62 | 1.11 | 1.22 | -0.00209
CFLAllSpcSCERt3NewCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCE | Rt3 | New | CZ08 | 3.69 | 0.00062 | 0 | 4.13 | 0.000749 | -0.00631 | 3.69 | 0.00062 | 0 | 4.13 | 0.000749 | -0.00631 |  | CFL | AllSpc | 3690 | 0.62 | 3690 | 0.62 | 1.12 | 1.21 | -0.00171 | 3690 | 0.62 | 3690 | 0.62 | 1.12 | 1.21 | -0.00171
CFLAllSpcSCERt3NewCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCE | Rt3 | New | CZ09 | 3.69 | 0.00062 | 0 | 4.07 | 0.000766 | -0.00948 | 3.69 | 0.00062 | 0 | 4.07 | 0.000766 | -0.00948 |  | CFL | AllSpc | 3690 | 0.62 | 3690 | 0.62 | 1.1 | 1.24 | -0.0025691 | 3690 | 0.62 | 3690 | 0.62 | 1.1 | 1.24 | -0.00257
CFLAllSpcSCERt3NewCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCE | Rt3 | New | CZ10 | 3.69 | 0.00062 | 0 | 4.08 | 0.000774 | -0.0109 | 3.69 | 0.00062 | 0 | 4.08 | 0.000774 | -0.0109 |  | CFL | AllSpc | 3690 | 0.62 | 3690 | 0.62 | 1.11 | 1.25 | -0.0029539 | 3690 | 0.62 | 3690 | 0.62 | 1.11 | 1.25 | -0.00295
CFLAllSpcSCERt3NewCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCE | Rt3 | New | CZ13 | 3.69 | 0.00062 | 0 | 3.96 | 0.000787 | -0.0251 | 3.69 | 0.00062 | 0 | 3.96 | 0.000787 | -0.0251 |  | CFL | AllSpc | 3690 | 0.62 | 3690 | 0.62 | 1.07 | 1.27 | -0.0068022 | 3690 | 0.62 | 3690 | 0.62 | 1.07 | 1.27 | -0.0068
CFLAllSpcSCERt3NewCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCE | Rt3 | New | CZ14 | 3.69 | 0.00062 | 0 | 3.94 | 0.000779 | -0.0261 | 3.69 | 0.00062 | 0 | 3.94 | 0.000779 | -0.0261 |  | CFL | AllSpc | 3690 | 0.62 | 3690 | 0.62 | 1.07 | 1.26 | -0.0070732 | 3690 | 0.62 | 3690 | 0.62 | 1.07 | 1.26 | -0.00707
CFLAllSpcSCERt3NewCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCE | Rt3 | New | CZ15 | 3.69 | 0.00062 | 0 | 4.3 | 0.000828 | -0.00167 | 3.69 | 0.00062 | 0 | 4.3 | 0.000828 | -0.00167 |  | CFL | AllSpc | 3690 | 0.62 | 3690 | 0.62 | 1.17 | 1.34 | -0.00045257 | 3690 | 0.62 | 3690 | 0.62 | 1.17 | 1.34 | -0.000453
CFLAllSpcSCERt3NewCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCE | Rt3 | New | CZ16 | 3.69 | 0.00062 | 0 | 3.56 | 0.000699 | -0.0453 | 3.69 | 0.00062 | 0 | 3.56 | 0.000699 | -0.0453 |  | CFL | AllSpc | 3690 | 0.62 | 3690 | 0.62 | 0.965 | 1.13 | -0.012276 | 3690 | 0.62 | 3690 | 0.62 | 0.965 | 1.13 | -0.0123
CFLAllSpcSCERt3NewIOU | Com-Iltg-dWatt-CFL_OSspc | SCE | Rt3 | New | IOU | 3.69 | 0.00062 | 0 | 4.0836 | 0.00076711 | -0.010415 | 3.69 | 0.00062 | 0 | 4.0836 | 0.00076711 | -0.010415 |  | CFL | AllSpc | 3690 | 0.62 | 3690 | 0.62 | 1.11 | 1.24 | -0.0028225 | 3690 | 0.62 | 3690 | 0.62 | 1.11 | 1.24 | -0.00282
CFLAllSpcSCERtLExCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCE | RtL | Ex | CZ05 | 4.32 | 0.00068096 | 0 | 4.63 | 0.00084891 | -0.0259 | 4.32 | 0.00068096 | 0 | 4.63 | 0.00084891 | -0.0259 |  | CFL | AllSpc | 4320 | 0.681 | 4320 | 0.681 | 1.07 | 1.25 | -0.0059954 | 4320 | 0.681 | 4320 | 0.681 | 1.07 | 1.25 | -0.006
CFLAllSpcSCERtLExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCE | RtL | Ex | CZ06 | 4.32 | 0.00068096 | 0 | 4.9196 | 0.00086096 | -0.0104 | 4.32 | 0.00068096 | 0 | 4.9196 | 0.00086096 | -0.0104 |  | CFL | AllSpc | 4320 | 0.681 | 4320 | 0.681 | 1.14 | 1.26 | -0.0024074 | 4320 | 0.681 | 4320 | 0.681 | 1.14 | 1.26 | -0.00241
CFLAllSpcSCERtLExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCE | RtL | Ex | CZ08 | 4.32 | 0.00068096 | 0 | 4.93 | 0.00086296 | -0.0089896 | 4.32 | 0.00068096 | 0 | 4.93 | 0.00086296 | -0.0089896 |  | CFL | AllSpc | 4320 | 0.681 | 4320 | 0.681 | 1.14 | 1.27 | -0.0020809 | 4320 | 0.681 | 4320 | 0.681 | 1.14 | 1.27 | -0.00208
CFLAllSpcSCERtLExCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCE | RtL | Ex | CZ09 | 4.32 | 0.00068096 | 0 | 4.88 | 0.00088296 | -0.0108 | 4.32 | 0.00068096 | 0 | 4.88 | 0.00088296 | -0.0108 |  | CFL | AllSpc | 4320 | 0.681 | 4320 | 0.681 | 1.13 | 1.3 | -0.0025 | 4320 | 0.681 | 4320 | 0.681 | 1.13 | 1.3 | -0.0025
CFLAllSpcSCERtLExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCE | RtL | Ex | CZ10 | 4.32 | 0.00068088 | 0 | 4.7988 | 0.00087188 | -0.012 | 4.32 | 0.00068088 | 0 | 4.7988 | 0.00087188 | -0.012 |  | CFL | AllSpc | 4320 | 0.681 | 4320 | 0.681 | 1.11 | 1.28 | -0.0027778 | 4320 | 0.681 | 4320 | 0.681 | 1.11 | 1.28 | -0.00278
CFLAllSpcSCERtLExCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCE | RtL | Ex | CZ13 | 4.32 | 0.0006809 | 0 | 4.7171 | 0.0008779 | -0.0236 | 4.32 | 0.0006809 | 0 | 4.7171 | 0.0008779 | -0.0236 |  | CFL | AllSpc | 4320 | 0.681 | 4320 | 0.681 | 1.09 | 1.29 | -0.005463 | 4320 | 0.681 | 4320 | 0.681 | 1.09 | 1.29 | -0.00546
CFLAllSpcSCERtLExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCE | RtL | Ex | CZ14 | 4.32 | 0.0006809 | 0 | 4.67 | 0.0008859 | -0.02449 | 4.32 | 0.0006809 | 0 | 4.67 | 0.0008859 | -0.02449 |  | CFL | AllSpc | 4320 | 0.681 | 4320 | 0.681 | 1.08 | 1.3 | -0.005669 | 4320 | 0.681 | 4320 | 0.681 | 1.08 | 1.3 | -0.00567
CFLAllSpcSCERtLExCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCE | RtL | Ex | CZ15 | 4.32 | 0.00068088 | 0 | 5.02 | 0.00088876 | -0.00421 | 4.32 | 0.00068088 | 0 | 5.02 | 0.00088876 | -0.00421 |  | CFL | AllSpc | 4320 | 0.681 | 4320 | 0.681 | 1.16 | 1.31 | -0.00097454 | 4320 | 0.681 | 4320 | 0.681 | 1.16 | 1.31 | -0.000975
CFLAllSpcSCERtLExCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCE | RtL | Ex | CZ16 | 4.32 | 0.0006809 | 0 | 4.24 | 0.0008369 | -0.054 | 4.32 | 0.0006809 | 0 | 4.24 | 0.0008369 | -0.054 |  | CFL | AllSpc | 4320 | 0.681 | 4320 | 0.681 | 0.981 | 1.23 | -0.0125 | 4320 | 0.681 | 4320 | 0.681 | 0.981 | 1.23 | -0.0125
CFLAllSpcSCERtLExIOU | Com-Iltg-dWatt-CFL_OSspc | SCE | RtL | Ex | IOU | 4.32 | 0.00068093 | 0 | 4.8708 | 0.00086923 | -0.011597 | 4.32 | 0.00068093 | 0 | 4.8708 | 0.00086923 | -0.011597 |  | CFL | AllSpc | 4320 | 0.681 | 4320 | 0.681 | 1.13 | 1.28 | -0.0026845 | 4320 | 0.681 | 4320 | 0.681 | 1.13 | 1.28 | -0.00268
CFLAllSpcSCERtLNewCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCE | RtL | New | CZ05 | 4.32 | 0.00068 | 0 | 4.49 | 0.000852 | -0.0309 | 4.32 | 0.00068 | 0 | 4.49 | 0.000852 | -0.0309 |  | CFL | AllSpc | 4320 | 0.68 | 4320 | 0.68 | 1.04 | 1.25 | -0.0071528 | 4320 | 0.68 | 4320 | 0.68 | 1.04 | 1.25 | -0.00715
CFLAllSpcSCERtLNewCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCE | RtL | New | CZ06 | 4.32 | 0.00068 | 0 | 4.73 | 0.000866 | -0.0143 | 4.32 | 0.00068 | 0 | 4.73 | 0.000866 | -0.0143 |  | CFL | AllSpc | 4320 | 0.68 | 4320 | 0.68 | 1.09 | 1.27 | -0.0033102 | 4320 | 0.68 | 4320 | 0.68 | 1.09 | 1.27 | -0.00331
CFLAllSpcSCERtLNewCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCE | RtL | New | CZ08 | 4.32 | 0.00068 | 0 | 4.79 | 0.000879 | -0.0121 | 4.32 | 0.00068 | 0 | 4.79 | 0.000879 | -0.0121 |  | CFL | AllSpc | 4320 | 0.68 | 4320 | 0.68 | 1.11 | 1.29 | -0.0028009 | 4320 | 0.68 | 4320 | 0.68 | 1.11 | 1.29 | -0.0028
CFLAllSpcSCERtLNewCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCE | RtL | New | CZ09 | 4.32 | 0.00068 | 0 | 4.81 | 0.000921 | -0.012 | 4.32 | 0.00068 | 0 | 4.81 | 0.000921 | -0.012 |  | CFL | AllSpc | 4320 | 0.68 | 4320 | 0.68 | 1.11 | 1.35 | -0.0027778 | 4320 | 0.68 | 4320 | 0.68 | 1.11 | 1.35 | -0.00278
CFLAllSpcSCERtLNewCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCE | RtL | New | CZ10 | 4.32 | 0.00068 | 0 | 4.83 | 0.000924 | -0.014 | 4.32 | 0.00068 | 0 | 4.83 | 0.000924 | -0.014 |  | CFL | AllSpc | 4320 | 0.68 | 4320 | 0.68 | 1.12 | 1.36 | -0.0032407 | 4320 | 0.68 | 4320 | 0.68 | 1.12 | 1.36 | -0.00324
CFLAllSpcSCERtLNewCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCE | RtL | New | CZ13 | 4.32 | 0.00068 | 0 | 4.73 | 0.000915 | -0.0265 | 4.32 | 0.00068 | 0 | 4.73 | 0.000915 | -0.0265 |  | CFL | AllSpc | 4320 | 0.68 | 4320 | 0.68 | 1.09 | 1.35 | -0.0061343 | 4320 | 0.68 | 4320 | 0.68 | 1.09 | 1.35 | -0.00613
CFLAllSpcSCERtLNewCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCE | RtL | New | CZ14 | 4.32 | 0.00068 | 0 | 4.72 | 0.000917 | -0.0271 | 4.32 | 0.00068 | 0 | 4.72 | 0.000917 | -0.0271 |  | CFL | AllSpc | 4320 | 0.68 | 4320 | 0.68 | 1.09 | 1.35 | -0.0062731 | 4320 | 0.68 | 4320 | 0.68 | 1.09 | 1.35 | -0.00627
CFLAllSpcSCERtLNewCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCE | RtL | New | CZ15 | 4.32 | 0.00068 | 0 | 5.11 | 0.000934 | -0.00412 | 4.32 | 0.00068 | 0 | 5.11 | 0.000934 | -0.00412 |  | CFL | AllSpc | 4320 | 0.68 | 4320 | 0.68 | 1.18 | 1.37 | -0.0009537 | 4320 | 0.68 | 4320 | 0.68 | 1.18 | 1.37 | -0.000954
CFLAllSpcSCERtLNewCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCE | RtL | New | CZ16 | 4.32 | 0.00068 | 0 | 4.27 | 0.000864 | -0.0561 | 4.32 | 0.00068 | 0 | 4.27 | 0.000864 | -0.0561 |  | CFL | AllSpc | 4320 | 0.68 | 4320 | 0.68 | 0.988 | 1.27 | -0.012986 | 4320 | 0.68 | 4320 | 0.68 | 0.988 | 1.27 | -0.013
CFLAllSpcSCERtLNewIOU | Com-Iltg-dWatt-CFL_OSspc | SCE | RtL | New | IOU | 4.32 | 0.00068 | 0 | 4.7963 | 0.00090176 | -0.014585 | 4.32 | 0.00068 | 0 | 4.7963 | 0.00090176 | -0.014585 |  | CFL | AllSpc | 4320 | 0.68 | 4320 | 0.68 | 1.11 | 1.33 | -0.0033761 | 4320 | 0.68 | 4320 | 0.68 | 1.11 | 1.33 | -0.00338
CFLAllSpcSCERtSExCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCE | RtS | Ex | CZ05 | 3.9698 | 0.00068996 | 0 | 4.1902 | 0.00085796 | -0.020798 | 3.9698 | 0.00068996 | 0 | 4.1902 | 0.00085796 | -0.020798 |  | CFL | AllSpc | 3970 | 0.69 | 3970 | 0.69 | 1.06 | 1.24 | -0.005239 | 3970 | 0.69 | 3970 | 0.69 | 1.06 | 1.24 | -0.00524
CFLAllSpcSCERtSExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCE | RtS | Ex | CZ06 | 3.9698 | 0.00068996 | 0 | 4.4396 | 0.00086696 | -0.0076196 | 3.9698 | 0.00068996 | 0 | 4.4396 | 0.00086696 | -0.0076196 |  | CFL | AllSpc | 3970 | 0.69 | 3970 | 0.69 | 1.12 | 1.26 | -0.0019194 | 3970 | 0.69 | 3970 | 0.69 | 1.12 | 1.26 | -0.00192
CFLAllSpcSCERtSExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCE | RtS | Ex | CZ08 | 3.9698 | 0.00068996 | 0 | 4.4602 | 0.00086889 | -0.0065096 | 3.9698 | 0.00068996 | 0 | 4.4602 | 0.00086889 | -0.0065096 |  | CFL | AllSpc | 3970 | 0.69 | 3970 | 0.69 | 1.12 | 1.26 | -0.0016398 | 3970 | 0.69 | 3970 | 0.69 | 1.12 | 1.26 | -0.00164
CFLAllSpcSCERtSExCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCE | RtS | Ex | CZ09 | 3.9698 | 0.00068996 | 0 | 4.4298 | 0.00088189 | -0.00825 | 3.9698 | 0.00068996 | 0 | 4.4298 | 0.00088189 | -0.00825 |  | CFL | AllSpc | 3970 | 0.69 | 3970 | 0.69 | 1.12 | 1.28 | -0.0020782 | 3970 | 0.69 | 3970 | 0.69 | 1.12 | 1.28 | -0.00208
CFLAllSpcSCERtSExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCE | RtS | Ex | CZ10 | 3.9688 | 0.00068976 | 0 | 4.3522 | 0.00086731 | -0.009241 | 3.9688 | 0.00068976 | 0 | 4.3522 | 0.00086731 | -0.009241 |  | CFL | AllSpc | 3970 | 0.69 | 3970 | 0.69 | 1.1 | 1.26 | -0.0023284 | 3970 | 0.69 | 3970 | 0.69 | 1.1 | 1.26 | -0.00233
CFLAllSpcSCERtSExCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCE | RtS | Ex | CZ13 | 3.969 | 0.00068979 | 0 | 4.2712 | 0.00087479 | -0.02189 | 3.969 | 0.00068979 | 0 | 4.2712 | 0.00087479 | -0.02189 |  | CFL | AllSpc | 3970 | 0.69 | 3970 | 0.69 | 1.08 | 1.27 | -0.0055152 | 3970 | 0.69 | 3970 | 0.69 | 1.08 | 1.27 | -0.00552
CFLAllSpcSCERtSExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCE | RtS | Ex | CZ14 | 3.969 | 0.0006898 | 0 | 4.259 | 0.00087038 | -0.02009 | 3.969 | 0.0006898 | 0 | 4.259 | 0.00087038 | -0.02009 |  | CFL | AllSpc | 3970 | 0.69 | 3970 | 0.69 | 1.07 | 1.26 | -0.0050617 | 3970 | 0.69 | 3970 | 0.69 | 1.07 | 1.26 | -0.00506
CFLAllSpcSCERtSExCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCE | RtS | Ex | CZ15 | 3.9688 | 0.00068976 | 0 | 4.6488 | 0.00086064 | -0.00237 | 3.9688 | 0.00068976 | 0 | 4.6488 | 0.00086064 | -0.00237 |  | CFL | AllSpc | 3970 | 0.69 | 3970 | 0.69 | 1.17 | 1.25 | -0.00059716 | 3970 | 0.69 | 3970 | 0.69 | 1.17 | 1.25 | -0.000597
CFLAllSpcSCERtSExCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCE | RtS | Ex | CZ16 | 3.969 | 0.00068979 | 0 | 3.919 | 0.00085169 | -0.042079 | 3.969 | 0.00068979 | 0 | 3.919 | 0.00085169 | -0.042079 |  | CFL | AllSpc | 3970 | 0.69 | 3970 | 0.69 | 0.987 | 1.23 | -0.010602 | 3970 | 0.69 | 3970 | 0.69 | 0.987 | 1.23 | -0.0106
CFLAllSpcSCERtSExIOU | Com-Iltg-dWatt-CFL_OSspc | SCE | RtS | Ex | IOU | 3.9695 | 0.0006899 | 0 | 4.4138 | 0.00086981 | -0.0088455 | 3.9695 | 0.0006899 | 0 | 4.4138 | 0.00086981 | -0.0088455 |  | CFL | AllSpc | 3970 | 0.69 | 3970 | 0.69 | 1.11 | 1.26 | -0.0022284 | 3970 | 0.69 | 3970 | 0.69 | 1.11 | 1.26 | -0.00223
CFLAllSpcSCERtSNewCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCE | RtS | New | CZ05 | 3.96 | 0.000688 | 0 | 4.07 | 0.000837 | -0.0231 | 3.96 | 0.000688 | 0 | 4.07 | 0.000837 | -0.0231 |  | CFL | AllSpc | 3960 | 0.688 | 3960 | 0.688 | 1.03 | 1.22 | -0.0058333 | 3960 | 0.688 | 3960 | 0.688 | 1.03 | 1.22 | -0.00583
CFLAllSpcSCERtSNewCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCE | RtS | New | CZ06 | 3.96 | 0.000688 | 0 | 4.28 | 0.000848 | -0.00966 | 3.96 | 0.000688 | 0 | 4.28 | 0.000848 | -0.00966 |  | CFL | AllSpc | 3960 | 0.688 | 3960 | 0.688 | 1.08 | 1.23 | -0.0024394 | 3960 | 0.688 | 3960 | 0.688 | 1.08 | 1.23 | -0.00244
CFLAllSpcSCERtSNewCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCE | RtS | New | CZ08 | 3.96 | 0.000688 | 0 | 4.32 | 0.000858 | -0.00807 | 3.96 | 0.000688 | 0 | 4.32 | 0.000858 | -0.00807 |  | CFL | AllSpc | 3960 | 0.688 | 3960 | 0.688 | 1.09 | 1.25 | -0.0020379 | 3960 | 0.688 | 3960 | 0.688 | 1.09 | 1.25 | -0.00204
CFLAllSpcSCERtSNewCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCE | RtS | New | CZ09 | 3.96 | 0.000688 | 0 | 4.31 | 0.00088 | -0.0093 | 3.96 | 0.000688 | 0 | 4.31 | 0.00088 | -0.0093 |  | CFL | AllSpc | 3960 | 0.688 | 3960 | 0.688 | 1.09 | 1.28 | -0.0023485 | 3960 | 0.688 | 3960 | 0.688 | 1.09 | 1.28 | -0.00235
CFLAllSpcSCERtSNewCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCE | RtS | New | CZ10 | 3.96 | 0.000688 | 0 | 4.35 | 0.000894 | -0.00966 | 3.96 | 0.000688 | 0 | 4.35 | 0.000894 | -0.00966 |  | CFL | AllSpc | 3960 | 0.688 | 3960 | 0.688 | 1.1 | 1.3 | -0.0024394 | 3960 | 0.688 | 3960 | 0.688 | 1.1 | 1.3 | -0.00244
CFLAllSpcSCERtSNewCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCE | RtS | New | CZ13 | 3.96 | 0.000688 | 0 | 4.25 | 0.000881 | -0.0225 | 3.96 | 0.000688 | 0 | 4.25 | 0.000881 | -0.0225 |  | CFL | AllSpc | 3960 | 0.688 | 3960 | 0.688 | 1.07 | 1.28 | -0.0056818 | 3960 | 0.688 | 3960 | 0.688 | 1.07 | 1.28 | -0.00568
CFLAllSpcSCERtSNewCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCE | RtS | New | CZ14 | 3.96 | 0.000688 | 0 | 4.25 | 0.000882 | -0.0211 | 3.96 | 0.000688 | 0 | 4.25 | 0.000882 | -0.0211 |  | CFL | AllSpc | 3960 | 0.688 | 3960 | 0.688 | 1.07 | 1.28 | -0.0053283 | 3960 | 0.688 | 3960 | 0.688 | 1.07 | 1.28 | -0.00533
CFLAllSpcSCERtSNewCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCE | RtS | New | CZ15 | 3.96 | 0.000688 | 0 | 4.55 | 0.000907 | -0.00192 | 3.96 | 0.000688 | 0 | 4.55 | 0.000907 | -0.00192 |  | CFL | AllSpc | 3960 | 0.688 | 3960 | 0.688 | 1.15 | 1.32 | -0.00048485 | 3960 | 0.688 | 3960 | 0.688 | 1.15 | 1.32 | -0.000485
CFLAllSpcSCERtSNewCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCE | RtS | New | CZ16 | 3.96 | 0.000688 | 0 | 3.89 | 0.000845 | -0.0447 | 3.96 | 0.000688 | 0 | 3.89 | 0.000845 | -0.0447 |  | CFL | AllSpc | 3960 | 0.688 | 3960 | 0.688 | 0.982 | 1.23 | -0.011288 | 3960 | 0.688 | 3960 | 0.688 | 0.982 | 1.23 | -0.0113
CFLAllSpcSCERtSNewIOU | Com-Iltg-dWatt-CFL_OSspc | SCE | RtS | New | IOU | 3.96 | 0.000688 | 0 | 4.3199 | 0.00087458 | -0.010389 | 3.96 | 0.000688 | 0 | 4.3199 | 0.00087458 | -0.010389 |  | CFL | AllSpc | 3960 | 0.688 | 3960 | 0.688 | 1.09 | 1.27 | -0.0026234 | 3960 | 0.688 | 3960 | 0.688 | 1.09 | 1.27 | -0.00262
CFLAllSpcSCEs_AgrExCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCE | s_Agr | Ex | CZ05 | 2.32 | 0.0006284 | 0 | 2.466 | 0.0007654 | -0.010408 | 2.32 | 0.0006284 | 0 | 2.466 | 0.0007654 | -0.010408 |  | CFL | AllSpc | 2320 | 0.628 | 2320 | 0.628 | 1.06 | 1.22 | -0.0044862 | 2320 | 0.628 | 2320 | 0.628 | 1.06 | 1.22 | -0.00449
CFLAllSpcSCEs_AgrExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCE | s_Agr | Ex | CZ06 | 2.32 | 0.0006284 | 0 | 2.588 | 0.000756 | -0.003816 | 2.32 | 0.0006284 | 0 | 2.588 | 0.000756 | -0.003816 |  | CFL | AllSpc | 2320 | 0.628 | 2320 | 0.628 | 1.12 | 1.2 | -0.0016448 | 2320 | 0.628 | 2320 | 0.628 | 1.12 | 1.2 | -0.00164
CFLAllSpcSCEs_AgrExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCE | s_Agr | Ex | CZ08 | 2.32 | 0.0006284 | 0 | 2.608 | 0.0007552 | -0.003196 | 2.32 | 0.0006284 | 0 | 2.608 | 0.0007552 | -0.003196 |  | CFL | AllSpc | 2320 | 0.628 | 2320 | 0.628 | 1.12 | 1.2 | -0.0013776 | 2320 | 0.628 | 2320 | 0.628 | 1.12 | 1.2 | -0.00138
CFLAllSpcSCEs_AgrExCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCE | s_Agr | Ex | CZ09 | 2.32 | 0.0006284 | 0 | 2.588 | 0.0007708 | -0.004294 | 2.32 | 0.0006284 | 0 | 2.588 | 0.0007708 | -0.004294 |  | CFL | AllSpc | 2320 | 0.628 | 2320 | 0.628 | 1.12 | 1.23 | -0.0018509 | 2320 | 0.628 | 2320 | 0.628 | 1.12 | 1.23 | -0.00185
CFLAllSpcSCEs_AgrExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCE | s_Agr | Ex | CZ10 | 2.32 | 0.0006284 | 0 | 2.526 | 0.0007648 | -0.005224 | 2.32 | 0.0006284 | 0 | 2.526 | 0.0007648 | -0.005224 |  | CFL | AllSpc | 2320 | 0.628 | 2320 | 0.628 | 1.09 | 1.22 | -0.0022517 | 2320 | 0.628 | 2320 | 0.628 | 1.09 | 1.22 | -0.00225
CFLAllSpcSCEs_AgrExCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCE | s_Agr | Ex | CZ13 | 2.32 | 0.0006284 | 0 | 2.498 | 0.000756 | -0.01167 | 2.32 | 0.0006284 | 0 | 2.498 | 0.000756 | -0.01167 |  | CFL | AllSpc | 2320 | 0.628 | 2320 | 0.628 | 1.08 | 1.2 | -0.0050302 | 2320 | 0.628 | 2320 | 0.628 | 1.08 | 1.2 | -0.00503
CFLAllSpcSCEs_AgrExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCE | s_Agr | Ex | CZ14 | 2.32 | 0.0006284 | 0 | 2.484 | 0.0007618 | -0.012814 | 2.32 | 0.0006284 | 0 | 2.484 | 0.0007618 | -0.012814 |  | CFL | AllSpc | 2320 | 0.628 | 2320 | 0.628 | 1.07 | 1.21 | -0.0055233 | 2320 | 0.628 | 2320 | 0.628 | 1.07 | 1.21 | -0.00552
CFLAllSpcSCEs_AgrExCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCE | s_Agr | Ex | CZ15 | 2.32 | 0.0006284 | 0 | 2.7 | 0.0007564 | -0.001374 | 2.32 | 0.0006284 | 0 | 2.7 | 0.0007564 | -0.001374 |  | CFL | AllSpc | 2320 | 0.628 | 2320 | 0.628 | 1.16 | 1.2 | -0.00059224 | 2320 | 0.628 | 2320 | 0.628 | 1.16 | 1.2 | -0.000592
CFLAllSpcSCEs_AgrExCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCE | s_Agr | Ex | CZ16 | 2.32 | 0.0006284 | 0 | 2.298 | 0.0007472 | -0.02562 | 2.32 | 0.0006284 | 0 | 2.298 | 0.0007472 | -0.02562 |  | CFL | AllSpc | 2320 | 0.628 | 2320 | 0.628 | 0.991 | 1.19 | -0.011043 | 2320 | 0.628 | 2320 | 0.628 | 0.991 | 1.19 | -0.011
CFLAllSpcSCEs_AgrExIOU | Com-Iltg-dWatt-CFL_OSspc | SCE | s_Agr | Ex | IOU | 2.32 | 0.0006284 | 0 | 2.5777 | 0.00075946 | -0.0048025 | 2.32 | 0.0006284 | 0 | 2.5777 | 0.00075946 | -0.0048025 |  | CFL | AllSpc | 2320 | 0.628 | 2320 | 0.628 | 1.11 | 1.21 | -0.0020701 | 2320 | 0.628 | 2320 | 0.628 | 1.11 | 1.21 | -0.00207
CFLAllSpcSCEs_CliExCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCE | s_Cli | Ex | CZ05 | 2.81 | 0.000493 | 0 | 2.95 | 0.000614 | -0.02702 | 2.81 | 0.000493 | 0 | 2.95 | 0.000614 | -0.02702 |  | CFL | AllSpc | 2810 | 0.493 | 2810 | 0.493 | 1.05 | 1.25 | -0.0096157 | 2810 | 0.493 | 2810 | 0.493 | 1.05 | 1.25 | -0.00962
CFLAllSpcSCEs_CliExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCE | s_Cli | Ex | CZ06 | 2.81 | 0.000493 | 0 | 3.12 | 0.0006325 | -0.01719 | 2.81 | 0.000493 | 0 | 3.12 | 0.0006325 | -0.01719 |  | CFL | AllSpc | 2810 | 0.493 | 2810 | 0.493 | 1.11 | 1.28 | -0.0061174 | 2810 | 0.493 | 2810 | 0.493 | 1.11 | 1.28 | -0.00612
CFLAllSpcSCEs_CliExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCE | s_Cli | Ex | CZ08 | 2.81 | 0.000493 | 0 | 3.145 | 0.000636 | -0.01652 | 2.81 | 0.000493 | 0 | 3.145 | 0.000636 | -0.01652 |  | CFL | AllSpc | 2810 | 0.493 | 2810 | 0.493 | 1.12 | 1.29 | -0.005879 | 2810 | 0.493 | 2810 | 0.493 | 1.12 | 1.29 | -0.00588
CFLAllSpcSCEs_CliExCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCE | s_Cli | Ex | CZ09 | 2.81 | 0.000493 | 0 | 3.145 | 0.0006485 | -0.017225 | 2.81 | 0.000493 | 0 | 3.145 | 0.0006485 | -0.017225 |  | CFL | AllSpc | 2810 | 0.493 | 2810 | 0.493 | 1.12 | 1.32 | -0.0061299 | 2810 | 0.493 | 2810 | 0.493 | 1.12 | 1.32 | -0.00613
CFLAllSpcSCEs_CliExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCE | s_Cli | Ex | CZ10 | 2.81 | 0.000493 | 0 | 3.105 | 0.000645 | -0.01704 | 2.81 | 0.000493 | 0 | 3.105 | 0.000645 | -0.01704 |  | CFL | AllSpc | 2810 | 0.493 | 2810 | 0.493 | 1.1 | 1.31 | -0.0060641 | 2810 | 0.493 | 2810 | 0.493 | 1.1 | 1.31 | -0.00606
CFLAllSpcSCEs_CliExCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCE | s_Cli | Ex | CZ13 | 2.81 | 0.000493 | 0 | 3.06 | 0.0006395 | -0.022075 | 2.81 | 0.000493 | 0 | 3.06 | 0.0006395 | -0.022075 |  | CFL | AllSpc | 2810 | 0.493 | 2810 | 0.493 | 1.09 | 1.3 | -0.0078559 | 2810 | 0.493 | 2810 | 0.493 | 1.09 | 1.3 | -0.00786
CFLAllSpcSCEs_CliExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCE | s_Cli | Ex | CZ14 | 2.81 | 0.000493 | 0 | 3.07 | 0.000646 | -0.021785 | 2.81 | 0.000493 | 0 | 3.07 | 0.000646 | -0.021785 |  | CFL | AllSpc | 2810 | 0.493 | 2810 | 0.493 | 1.09 | 1.31 | -0.0077527 | 2810 | 0.493 | 2810 | 0.493 | 1.09 | 1.31 | -0.00775
CFLAllSpcSCEs_CliExCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCE | s_Cli | Ex | CZ15 | 2.81 | 0.000493 | 0 | 3.32 | 0.0006445 | -0.009675 | 2.81 | 0.000493 | 0 | 3.32 | 0.0006445 | -0.009675 |  | CFL | AllSpc | 2810 | 0.493 | 2810 | 0.493 | 1.18 | 1.31 | -0.0034431 | 2810 | 0.493 | 2810 | 0.493 | 1.18 | 1.31 | -0.00344
CFLAllSpcSCEs_CliExCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCE | s_Cli | Ex | CZ16 | 2.81 | 0.000493 | 0 | 2.81 | 0.0006195 | -0.03505 | 2.81 | 0.000493 | 0 | 2.81 | 0.0006195 | -0.03505 |  | CFL | AllSpc | 2810 | 0.493 | 2810 | 0.493 | 1 | 1.26 | -0.012473 | 2810 | 0.493 | 2810 | 0.493 | 1 | 1.26 | -0.0125
CFLAllSpcSCEs_CliExIOU | Com-Iltg-dWatt-CFL_OSspc | SCE | s_Cli | Ex | IOU | 2.81 | 0.000493 | 0 | 3.1242 | 0.00063829 | -0.017527 | 2.81 | 0.000493 | 0 | 3.1242 | 0.00063829 | -0.017527 |  | CFL | AllSpc | 2810 | 0.493 | 2810 | 0.493 | 1.11 | 1.29 | -0.0062374 | 2810 | 0.493 | 2810 | 0.493 | 1.11 | 1.29 | -0.00624
CFLAllSpcSCEs_FStExCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCE | s_FSt | Ex | CZ05 | 3.885 | 0.0005845 | 0 | 3.92 | 0.0007285 | -0.04345 | 3.885 | 0.0005845 | 0 | 3.92 | 0.0007285 | -0.04345 |  | CFL | AllSpc | 3880 | 0.585 | 3880 | 0.585 | 1.01 | 1.25 | -0.011184 | 3880 | 0.585 | 3880 | 0.585 | 1.01 | 1.25 | -0.0112
CFLAllSpcSCEs_FStExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCE | s_FSt | Ex | CZ06 | 3.885 | 0.0005845 | 0 | 4.145 | 0.000735 | -0.03041 | 3.885 | 0.0005845 | 0 | 4.145 | 0.000735 | -0.03041 |  | CFL | AllSpc | 3880 | 0.585 | 3880 | 0.585 | 1.07 | 1.26 | -0.0078275 | 3880 | 0.585 | 3880 | 0.585 | 1.07 | 1.26 | -0.00783
CFLAllSpcSCEs_FStExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCE | s_FSt | Ex | CZ08 | 3.885 | 0.0005845 | 0 | 4.21 | 0.000744 | -0.027405 | 3.885 | 0.0005845 | 0 | 4.21 | 0.000744 | -0.027405 |  | CFL | AllSpc | 3880 | 0.585 | 3880 | 0.585 | 1.08 | 1.27 | -0.0070541 | 3880 | 0.585 | 3880 | 0.585 | 1.08 | 1.27 | -0.00705
CFLAllSpcSCEs_FStExCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCE | s_FSt | Ex | CZ09 | 3.885 | 0.0005845 | 0 | 4.21 | 0.000754 | -0.02768 | 3.885 | 0.0005845 | 0 | 4.21 | 0.000754 | -0.02768 |  | CFL | AllSpc | 3880 | 0.585 | 3880 | 0.585 | 1.08 | 1.29 | -0.0071248 | 3880 | 0.585 | 3880 | 0.585 | 1.08 | 1.29 | -0.00712
CFLAllSpcSCEs_FStExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCE | s_FSt | Ex | CZ10 | 3.885 | 0.0005845 | 0 | 4.165 | 0.000754 | -0.027625 | 3.885 | 0.0005845 | 0 | 4.165 | 0.000754 | -0.027625 |  | CFL | AllSpc | 3880 | 0.585 | 3880 | 0.585 | 1.07 | 1.29 | -0.0071107 | 3880 | 0.585 | 3880 | 0.585 | 1.07 | 1.29 | -0.00711
CFLAllSpcSCEs_FStExCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCE | s_FSt | Ex | CZ13 | 3.885 | 0.0005845 | 0 | 4.135 | 0.000754 | -0.03355 | 3.885 | 0.0005845 | 0 | 4.135 | 0.000754 | -0.03355 |  | CFL | AllSpc | 3880 | 0.585 | 3880 | 0.585 | 1.06 | 1.29 | -0.0086358 | 3880 | 0.585 | 3880 | 0.585 | 1.06 | 1.29 | -0.00864
CFLAllSpcSCEs_FStExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCE | s_FSt | Ex | CZ14 | 3.885 | 0.0005845 | 0 | 4.115 | 0.0007615 | -0.03325 | 3.885 | 0.0005845 | 0 | 4.115 | 0.0007615 | -0.03325 |  | CFL | AllSpc | 3880 | 0.585 | 3880 | 0.585 | 1.06 | 1.3 | -0.0085586 | 3880 | 0.585 | 3880 | 0.585 | 1.06 | 1.3 | -0.00856
CFLAllSpcSCEs_FStExCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCE | s_FSt | Ex | CZ15 | 3.885 | 0.0005845 | 0 | 4.465 | 0.0007495 | -0.014485 | 3.885 | 0.0005845 | 0 | 4.465 | 0.0007495 | -0.014485 |  | CFL | AllSpc | 3880 | 0.585 | 3880 | 0.585 | 1.15 | 1.28 | -0.0037284 | 3880 | 0.585 | 3880 | 0.585 | 1.15 | 1.28 | -0.00373
CFLAllSpcSCEs_FStExCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCE | s_FSt | Ex | CZ16 | 3.885 | 0.0005845 | 0 | 3.765 | 0.0007275 | -0.052 | 3.885 | 0.0005845 | 0 | 3.765 | 0.0007275 | -0.052 |  | CFL | AllSpc | 3880 | 0.585 | 3880 | 0.585 | 0.969 | 1.24 | -0.013385 | 3880 | 0.585 | 3880 | 0.585 | 0.969 | 1.24 | -0.0134
CFLAllSpcSCEs_FStExIOU | Com-Iltg-dWatt-CFL_OSspc | SCE | s_FSt | Ex | IOU | 3.885 | 0.0005845 | 0 | 4.181 | 0.00074679 | -0.028501 | 3.885 | 0.0005845 | 0 | 4.181 | 0.00074679 | -0.028501 |  | CFL | AllSpc | 3880 | 0.585 | 3880 | 0.585 | 1.08 | 1.28 | -0.0073362 | 3880 | 0.585 | 3880 | 0.585 | 1.08 | 1.28 | -0.00734
CFLAllSpcSCEs_IndExCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCE | s_Ind | Ex | CZ05 | 2.535 | 0.0006635 | 0 | 2.805 | 0.0008145 | -0.00614 | 2.535 | 0.0006635 | 0 | 2.805 | 0.0008145 | -0.00614 |  | CFL | AllSpc | 2540 | 0.663 | 2540 | 0.663 | 1.11 | 1.23 | -0.0024221 | 2540 | 0.663 | 2540 | 0.663 | 1.11 | 1.23 | -0.00242
CFLAllSpcSCEs_IndExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCE | s_Ind | Ex | CZ06 | 2.535 | 0.0006635 | 0 | 2.9 | 0.0007965 | -0.0021795 | 2.535 | 0.0006635 | 0 | 2.9 | 0.0007965 | -0.0021795 |  | CFL | AllSpc | 2540 | 0.663 | 2540 | 0.663 | 1.14 | 1.2 | -0.00085976 | 2540 | 0.663 | 2540 | 0.663 | 1.14 | 1.2 | -0.00086
CFLAllSpcSCEs_IndExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCE | s_Ind | Ex | CZ08 | 2.535 | 0.0006635 | 0 | 2.92 | 0.000811 | -0.001675 | 2.535 | 0.0006635 | 0 | 2.92 | 0.000811 | -0.001675 |  | CFL | AllSpc | 2540 | 0.663 | 2540 | 0.663 | 1.15 | 1.22 | -0.00066075 | 2540 | 0.663 | 2540 | 0.663 | 1.15 | 1.22 | -0.000661
CFLAllSpcSCEs_IndExCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCE | s_Ind | Ex | CZ09 | 2.535 | 0.0006635 | 0 | 2.905 | 0.0008215 | -0.0025555 | 2.535 | 0.0006635 | 0 | 2.905 | 0.0008215 | -0.0025555 |  | CFL | AllSpc | 2540 | 0.663 | 2540 | 0.663 | 1.15 | 1.24 | -0.0010081 | 2540 | 0.663 | 2540 | 0.663 | 1.15 | 1.24 | -0.00101
CFLAllSpcSCEs_IndExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCE | s_Ind | Ex | CZ10 | 2.535 | 0.0006635 | 0 | 2.82 | 0.0008185 | -0.0032165 | 2.535 | 0.0006635 | 0 | 2.82 | 0.0008185 | -0.0032165 |  | CFL | AllSpc | 2540 | 0.663 | 2540 | 0.663 | 1.11 | 1.23 | -0.0012688 | 2540 | 0.663 | 2540 | 0.663 | 1.11 | 1.23 | -0.00127
CFLAllSpcSCEs_IndExCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCE | s_Ind | Ex | CZ13 | 2.535 | 0.0006635 | 0 | 2.81 | 0.0007995 | -0.00706 | 2.535 | 0.0006635 | 0 | 2.81 | 0.0007995 | -0.00706 |  | CFL | AllSpc | 2540 | 0.663 | 2540 | 0.663 | 1.11 | 1.2 | -0.002785 | 2540 | 0.663 | 2540 | 0.663 | 1.11 | 1.2 | -0.00279
CFLAllSpcSCEs_IndExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCE | s_Ind | Ex | CZ14 | 2.535 | 0.0006635 | 0 | 2.8 | 0.000815 | -0.00815 | 2.535 | 0.0006635 | 0 | 2.8 | 0.000815 | -0.00815 |  | CFL | AllSpc | 2540 | 0.663 | 2540 | 0.663 | 1.1 | 1.23 | -0.003215 | 2540 | 0.663 | 2540 | 0.663 | 1.1 | 1.23 | -0.00322
CFLAllSpcSCEs_IndExCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCE | s_Ind | Ex | CZ15 | 2.535 | 0.0006635 | 0 | 2.965 | 0.0008155 | -0.000715 | 2.535 | 0.0006635 | 0 | 2.965 | 0.0008155 | -0.000715 |  | CFL | AllSpc | 2540 | 0.663 | 2540 | 0.663 | 1.17 | 1.23 | -0.00028205 | 2540 | 0.663 | 2540 | 0.663 | 1.17 | 1.23 | -0.000282
CFLAllSpcSCEs_IndExCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCE | s_Ind | Ex | CZ16 | 2.535 | 0.0006635 | 0 | 2.62 | 0.0007855 | -0.017535 | 2.535 | 0.0006635 | 0 | 2.62 | 0.0007855 | -0.017535 |  | CFL | AllSpc | 2540 | 0.663 | 2540 | 0.663 | 1.03 | 1.18 | -0.0069172 | 2540 | 0.663 | 2540 | 0.663 | 1.03 | 1.18 | -0.00692
CFLAllSpcSCEs_IndExIOU | Com-Iltg-dWatt-CFL_OSspc | SCE | s_Ind | Ex | IOU | 2.535 | 0.0006635 | 0 | 2.8856 | 0.00081024 | -0.0028419 | 2.535 | 0.0006635 | 0 | 2.8856 | 0.00081024 | -0.0028419 |  | CFL | AllSpc | 2540 | 0.663 | 2540 | 0.663 | 1.14 | 1.22 | -0.001121 | 2540 | 0.663 | 2540 | 0.663 | 1.14 | 1.22 | -0.00112
CFLAllSpcSCEs_MiCExCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCE | s_MiC | Ex | CZ05 | 3.58 | 0.000623 | 0 | 3.8 | 0.00077067 | -0.022447 | 3.58 | 0.000623 | 0 | 3.8 | 0.00077067 | -0.022447 |  | CFL | AllSpc | 3580 | 0.623 | 3580 | 0.623 | 1.06 | 1.24 | -0.00627 | 3580 | 0.623 | 3580 | 0.623 | 1.06 | 1.24 | -0.00627
CFLAllSpcSCEs_MiCExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCE | s_MiC | Ex | CZ06 | 3.58 | 0.000623 | 0 | 4.0133 | 0.00078 | -0.010433 | 3.58 | 0.000623 | 0 | 4.0133 | 0.00078 | -0.010433 |  | CFL | AllSpc | 3580 | 0.623 | 3580 | 0.623 | 1.12 | 1.25 | -0.0029143 | 3580 | 0.623 | 3580 | 0.623 | 1.12 | 1.25 | -0.00291
CFLAllSpcSCEs_MiCExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCE | s_MiC | Ex | CZ08 | 3.58 | 0.000623 | 0 | 4.04 | 0.00077467 | -0.00895 | 3.58 | 0.000623 | 0 | 4.04 | 0.00077467 | -0.00895 |  | CFL | AllSpc | 3580 | 0.623 | 3580 | 0.623 | 1.13 | 1.24 | -0.0025 | 3580 | 0.623 | 3580 | 0.623 | 1.13 | 1.24 | -0.0025
CFLAllSpcSCEs_MiCExCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCE | s_MiC | Ex | CZ09 | 3.58 | 0.000623 | 0 | 4.02 | 0.00078567 | -0.010603 | 3.58 | 0.000623 | 0 | 4.02 | 0.00078567 | -0.010603 |  | CFL | AllSpc | 3580 | 0.623 | 3580 | 0.623 | 1.12 | 1.26 | -0.0029618 | 3580 | 0.623 | 3580 | 0.623 | 1.12 | 1.26 | -0.00296
CFLAllSpcSCEs_MiCExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCE | s_MiC | Ex | CZ10 | 3.58 | 0.000623 | 0 | 3.96 | 0.00077067 | -0.01121 | 3.58 | 0.000623 | 0 | 3.96 | 0.00077067 | -0.01121 |  | CFL | AllSpc | 3580 | 0.623 | 3580 | 0.623 | 1.11 | 1.24 | -0.0031313 | 3580 | 0.623 | 3580 | 0.623 | 1.11 | 1.24 | -0.00313
CFLAllSpcSCEs_MiCExCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCE | s_MiC | Ex | CZ13 | 3.58 | 0.000623 | 0 | 3.9033 | 0.00078267 | -0.020383 | 3.58 | 0.000623 | 0 | 3.9033 | 0.00078267 | -0.020383 |  | CFL | AllSpc | 3580 | 0.623 | 3580 | 0.623 | 1.09 | 1.26 | -0.0056937 | 3580 | 0.623 | 3580 | 0.623 | 1.09 | 1.26 | -0.00569
CFLAllSpcSCEs_MiCExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCE | s_MiC | Ex | CZ14 | 3.58 | 0.000623 | 0 | 3.8833 | 0.000775 | -0.019523 | 3.58 | 0.000623 | 0 | 3.8833 | 0.000775 | -0.019523 |  | CFL | AllSpc | 3580 | 0.623 | 3580 | 0.623 | 1.08 | 1.24 | -0.0054534 | 3580 | 0.623 | 3580 | 0.623 | 1.08 | 1.24 | -0.00545
CFLAllSpcSCEs_MiCExCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCE | s_MiC | Ex | CZ15 | 3.58 | 0.000623 | 0 | 4.23 | 0.00078167 | -0.0037433 | 3.58 | 0.000623 | 0 | 4.23 | 0.00078167 | -0.0037433 |  | CFL | AllSpc | 3580 | 0.623 | 3580 | 0.623 | 1.18 | 1.25 | -0.0010456 | 3580 | 0.623 | 3580 | 0.623 | 1.18 | 1.25 | -0.00105
CFLAllSpcSCEs_MiCExCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCE | s_MiC | Ex | CZ16 | 3.58 | 0.000623 | 0 | 3.5767 | 0.00076033 | -0.038267 | 3.58 | 0.000623 | 0 | 3.5767 | 0.00076033 | -0.038267 |  | CFL | AllSpc | 3580 | 0.623 | 3580 | 0.623 | 0.999 | 1.22 | -0.010689 | 3580 | 0.623 | 3580 | 0.623 | 0.999 | 1.22 | -0.0107
CFLAllSpcSCEs_MiCExIOU | Com-Iltg-dWatt-CFL_OSspc | SCE | s_MiC | Ex | IOU | 3.58 | 0.000623 | 0 | 4.0036 | 0.00077681 | -0.011044 | 3.58 | 0.000623 | 0 | 4.0036 | 0.00077681 | -0.011044 |  | CFL | AllSpc | 3580 | 0.623 | 3580 | 0.623 | 1.12 | 1.25 | -0.0030848 | 3580 | 0.623 | 3580 | 0.623 | 1.12 | 1.25 | -0.00308
CFLAllSpcSCEs_TCUExCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCE | s_TCU | Ex | CZ05 | 2.504 | 0.000527 | 0 | 2.592 | 0.0006346 | -0.012528 | 2.504 | 0.000527 | 0 | 2.592 | 0.0006346 | -0.012528 |  | CFL | AllSpc | 2500 | 0.527 | 2500 | 0.527 | 1.04 | 1.2 | -0.0050032 | 2500 | 0.527 | 2500 | 0.527 | 1.04 | 1.2 | -0.005
CFLAllSpcSCEs_TCUExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCE | s_TCU | Ex | CZ06 | 2.504 | 0.000527 | 0 | 2.72 | 0.0006416 | -0.006506 | 2.504 | 0.000527 | 0 | 2.72 | 0.0006416 | -0.006506 |  | CFL | AllSpc | 2500 | 0.527 | 2500 | 0.527 | 1.09 | 1.22 | -0.0025982 | 2500 | 0.527 | 2500 | 0.527 | 1.09 | 1.22 | -0.0026
CFLAllSpcSCEs_TCUExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCE | s_TCU | Ex | CZ08 | 2.504 | 0.000527 | 0 | 2.742 | 0.0006448 | -0.00584 | 2.504 | 0.000527 | 0 | 2.742 | 0.0006448 | -0.00584 |  | CFL | AllSpc | 2500 | 0.527 | 2500 | 0.527 | 1.1 | 1.22 | -0.0023323 | 2500 | 0.527 | 2500 | 0.527 | 1.1 | 1.22 | -0.00233
CFLAllSpcSCEs_TCUExCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCE | s_TCU | Ex | CZ09 | 2.504 | 0.000527 | 0 | 2.728 | 0.0006518 | -0.007136 | 2.504 | 0.000527 | 0 | 2.728 | 0.0006518 | -0.007136 |  | CFL | AllSpc | 2500 | 0.527 | 2500 | 0.527 | 1.09 | 1.24 | -0.0028498 | 2500 | 0.527 | 2500 | 0.527 | 1.09 | 1.24 | -0.00285
CFLAllSpcSCEs_TCUExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCE | s_TCU | Ex | CZ10 | 2.504 | 0.000527 | 0 | 2.704 | 0.0006468 | -0.007008 | 2.504 | 0.000527 | 0 | 2.704 | 0.0006468 | -0.007008 |  | CFL | AllSpc | 2500 | 0.527 | 2500 | 0.527 | 1.08 | 1.23 | -0.0027987 | 2500 | 0.527 | 2500 | 0.527 | 1.08 | 1.23 | -0.0028
CFLAllSpcSCEs_TCUExCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCE | s_TCU | Ex | CZ13 | 2.504 | 0.000527 | 0 | 2.676 | 0.0006396 | -0.01141 | 2.504 | 0.000527 | 0 | 2.676 | 0.0006396 | -0.01141 |  | CFL | AllSpc | 2500 | 0.527 | 2500 | 0.527 | 1.07 | 1.21 | -0.0045567 | 2500 | 0.527 | 2500 | 0.527 | 1.07 | 1.21 | -0.00456
CFLAllSpcSCEs_TCUExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCE | s_TCU | Ex | CZ14 | 2.504 | 0.000527 | 0 | 2.664 | 0.0006452 | -0.011694 | 2.504 | 0.000527 | 0 | 2.664 | 0.0006452 | -0.011694 |  | CFL | AllSpc | 2500 | 0.527 | 2500 | 0.527 | 1.06 | 1.22 | -0.0046701 | 2500 | 0.527 | 2500 | 0.527 | 1.06 | 1.22 | -0.00467
CFLAllSpcSCEs_TCUExCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCE | s_TCU | Ex | CZ15 | 2.504 | 0.000527 | 0 | 2.848 | 0.000642 | -0.003018 | 2.504 | 0.000527 | 0 | 2.848 | 0.000642 | -0.003018 |  | CFL | AllSpc | 2500 | 0.527 | 2500 | 0.527 | 1.14 | 1.22 | -0.0012053 | 2500 | 0.527 | 2500 | 0.527 | 1.14 | 1.22 | -0.00121
CFLAllSpcSCEs_TCUExCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCE | s_TCU | Ex | CZ16 | 2.504 | 0.000527 | 0 | 2.486 | 0.0006266 | -0.02084 | 2.504 | 0.000527 | 0 | 2.486 | 0.0006266 | -0.02084 |  | CFL | AllSpc | 2500 | 0.527 | 2500 | 0.527 | 0.993 | 1.19 | -0.0083227 | 2500 | 0.527 | 2500 | 0.527 | 0.993 | 1.19 | -0.00832
CFLAllSpcSCEs_TCUExIOU | Com-Iltg-dWatt-CFL_OSspc | SCE | s_TCU | Ex | IOU | 2.504 | 0.000527 | 0 | 2.7239 | 0.00064502 | -0.0068901 | 2.504 | 0.000527 | 0 | 2.7239 | 0.00064502 | -0.0068901 |  | CFL | AllSpc | 2500 | 0.527 | 2500 | 0.527 | 1.09 | 1.22 | -0.0027517 | 2500 | 0.527 | 2500 | 0.527 | 1.09 | 1.22 | -0.00275
CFLAllSpcSCESCnExCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCE | SCn | Ex | CZ05 | 2.6 | 0.000483 | 0 | 2.42 | 0.000604 | -0.026 | 2.6 | 0.000483 | 0 | 2.42 | 0.000604 | -0.026 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 0.931 | 1.25 | -0.01 | 2600 | 0.483 | 2600 | 0.483 | 0.931 | 1.25 | -0.01
CFLAllSpcSCESCnExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCE | SCn | Ex | CZ06 | 2.6 | 0.000483 | 0 | 2.69 | 0.000626 | -0.013496 | 2.6 | 0.000483 | 0 | 2.69 | 0.000626 | -0.013496 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 1.03 | 1.3 | -0.0051908 | 2600 | 0.483 | 2600 | 0.483 | 1.03 | 1.3 | -0.00519
CFLAllSpcSCESCnExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCE | SCn | Ex | CZ08 | 2.6 | 0.000483 | 0 | 2.74 | 0.000625 | -0.0116 | 2.6 | 0.000483 | 0 | 2.74 | 0.000625 | -0.0116 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 1.05 | 1.29 | -0.0044615 | 2600 | 0.483 | 2600 | 0.483 | 1.05 | 1.29 | -0.00446
CFLAllSpcSCESCnExCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCE | SCn | Ex | CZ09 | 2.6 | 0.000483 | 0 | 2.72 | 0.000636 | -0.014 | 2.6 | 0.000483 | 0 | 2.72 | 0.000636 | -0.014 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 1.05 | 1.32 | -0.0053846 | 2600 | 0.483 | 2600 | 0.483 | 1.05 | 1.32 | -0.00538
CFLAllSpcSCESCnExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCE | SCn | Ex | CZ10 | 2.6 | 0.000483 | 0 | 2.7094 | 0.000628 | -0.015 | 2.6 | 0.000483 | 0 | 2.7094 | 0.000628 | -0.015 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 1.04 | 1.3 | -0.0057692 | 2600 | 0.483 | 2600 | 0.483 | 1.04 | 1.3 | -0.00577
CFLAllSpcSCESCnExCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCE | SCn | Ex | CZ13 | 2.6 | 0.000483 | 0 | 2.66 | 0.00062 | -0.020087 | 2.6 | 0.000483 | 0 | 2.66 | 0.00062 | -0.020087 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 1.02 | 1.28 | -0.0077257 | 2600 | 0.483 | 2600 | 0.483 | 1.02 | 1.28 | -0.00773
CFLAllSpcSCESCnExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCE | SCn | Ex | CZ14 | 2.6 | 0.000483 | 0 | 2.64 | 0.000619 | -0.022088 | 2.6 | 0.000483 | 0 | 2.64 | 0.000619 | -0.022088 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 1.02 | 1.28 | -0.0084953 | 2600 | 0.483 | 2600 | 0.483 | 1.02 | 1.28 | -0.0085
CFLAllSpcSCESCnExCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCE | SCn | Ex | CZ15 | 2.6 | 0.000483 | 0 | 2.89 | 0.000622 | -0.00589 | 2.6 | 0.000483 | 0 | 2.89 | 0.000622 | -0.00589 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 1.11 | 1.29 | -0.0022654 | 2600 | 0.483 | 2600 | 0.483 | 1.11 | 1.29 | -0.00227
CFLAllSpcSCESCnExCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCE | SCn | Ex | CZ16 | 2.6 | 0.000483 | 0 | 2.38 | 0.000602 | -0.0318 | 2.6 | 0.000483 | 0 | 2.38 | 0.000602 | -0.0318 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 0.915 | 1.25 | -0.012231 | 2600 | 0.483 | 2600 | 0.483 | 0.915 | 1.25 | -0.0122
CFLAllSpcSCESCnExIOU | Com-Iltg-dWatt-CFL_OSspc | SCE | SCn | Ex | IOU | 2.6 | 0.000483 | 0 | 2.7179 | 0.00062697 | -0.013511 | 2.6 | 0.000483 | 0 | 2.7179 | 0.00062697 | -0.013511 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 1.05 | 1.3 | -0.0051967 | 2600 | 0.483 | 2600 | 0.483 | 1.05 | 1.3 | -0.0052
CFLAllSpcSCESCnNewCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCE | SCn | New | CZ05 | 2.6 | 0.000483 | 0 | 2.42 | 0.000606 | -0.0286 | 2.6 | 0.000483 | 0 | 2.42 | 0.000606 | -0.0286 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 0.931 | 1.25 | -0.011 | 2600 | 0.483 | 2600 | 0.483 | 0.931 | 1.25 | -0.011
CFLAllSpcSCESCnNewCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCE | SCn | New | CZ06 | 2.6 | 0.000483 | 0 | 2.61 | 0.000581 | -0.0153 | 2.6 | 0.000483 | 0 | 2.61 | 0.000581 | -0.0153 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 1 | 1.2 | -0.0058846 | 2600 | 0.483 | 2600 | 0.483 | 1 | 1.2 | -0.00588
CFLAllSpcSCESCnNewCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCE | SCn | New | CZ08 | 2.6 | 0.000483 | 0 | 2.67 | 0.000589 | -0.0133 | 2.6 | 0.000483 | 0 | 2.67 | 0.000589 | -0.0133 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 1.03 | 1.22 | -0.0051154 | 2600 | 0.483 | 2600 | 0.483 | 1.03 | 1.22 | -0.00512
CFLAllSpcSCESCnNewCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCE | SCn | New | CZ09 | 2.6 | 0.000483 | 0 | 2.67 | 0.000609 | -0.0143 | 2.6 | 0.000483 | 0 | 2.67 | 0.000609 | -0.0143 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 1.03 | 1.26 | -0.0055 | 2600 | 0.483 | 2600 | 0.483 | 1.03 | 1.26 | -0.0055
CFLAllSpcSCESCnNewCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCE | SCn | New | CZ10 | 2.6 | 0.000483 | 0 | 2.67 | 0.000604 | -0.0155 | 2.6 | 0.000483 | 0 | 2.67 | 0.000604 | -0.0155 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 1.03 | 1.25 | -0.0059615 | 2600 | 0.483 | 2600 | 0.483 | 1.03 | 1.25 | -0.00596
CFLAllSpcSCESCnNewCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCE | SCn | New | CZ13 | 2.6 | 0.000483 | 0 | 2.59 | 0.000588 | -0.0204 | 2.6 | 0.000483 | 0 | 2.59 | 0.000588 | -0.0204 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 0.996 | 1.22 | -0.0078462 | 2600 | 0.483 | 2600 | 0.483 | 0.996 | 1.22 | -0.00785
CFLAllSpcSCESCnNewCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCE | SCn | New | CZ14 | 2.6 | 0.000483 | 0 | 2.62 | 0.000601 | -0.0229 | 2.6 | 0.000483 | 0 | 2.62 | 0.000601 | -0.0229 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 1.01 | 1.24 | -0.0088077 | 2600 | 0.483 | 2600 | 0.483 | 1.01 | 1.24 | -0.00881
CFLAllSpcSCESCnNewCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCE | SCn | New | CZ15 | 2.6 | 0.000483 | 0 | 2.84 | 0.000607 | -0.00484 | 2.6 | 0.000483 | 0 | 2.84 | 0.000607 | -0.00484 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 1.09 | 1.26 | -0.0018615 | 2600 | 0.483 | 2600 | 0.483 | 1.09 | 1.26 | -0.00186
CFLAllSpcSCESCnNewCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCE | SCn | New | CZ16 | 2.6 | 0.000483 | 0 | 2.36 | 0.000581 | -0.0331 | 2.6 | 0.000483 | 0 | 2.36 | 0.000581 | -0.0331 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 0.908 | 1.2 | -0.012731 | 2600 | 0.483 | 2600 | 0.483 | 0.908 | 1.2 | -0.0127
CFLAllSpcSCESCnNewIOU | Com-Iltg-dWatt-CFL_OSspc | SCE | SCn | New | IOU | 2.6 | 0.000483 | 0 | 2.6622 | 0.00059929 | -0.015263 | 2.6 | 0.000483 | 0 | 2.6622 | 0.00059929 | -0.015263 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 1.02 | 1.24 | -0.0058703 | 2600 | 0.483 | 2600 | 0.483 | 1.02 | 1.24 | -0.00587
CFLAllSpcSCESUnExCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCE | SUn | Ex | CZ05 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0 | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0
CFLAllSpcSCESUnExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCE | SUn | Ex | CZ06 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0 | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0
CFLAllSpcSCESUnExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCE | SUn | Ex | CZ08 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0 | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0
CFLAllSpcSCESUnExCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCE | SUn | Ex | CZ09 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0 | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0
CFLAllSpcSCESUnExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCE | SUn | Ex | CZ10 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0 | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0
CFLAllSpcSCESUnExCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCE | SUn | Ex | CZ13 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0 | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0
CFLAllSpcSCESUnExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCE | SUn | Ex | CZ14 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0 | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0
CFLAllSpcSCESUnExCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCE | SUn | Ex | CZ15 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0 | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0
CFLAllSpcSCESUnExCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCE | SUn | Ex | CZ16 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0 | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0
CFLAllSpcSCESUnExIOU | Com-Iltg-dWatt-CFL_OSspc | SCE | SUn | Ex | IOU | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0 | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0
CFLAllSpcSCESUnNewCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCE | SUn | New | CZ05 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0 | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0
CFLAllSpcSCESUnNewCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCE | SUn | New | CZ06 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0 | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0
CFLAllSpcSCESUnNewCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCE | SUn | New | CZ08 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0 | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0
CFLAllSpcSCESUnNewCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCE | SUn | New | CZ09 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0 | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0
CFLAllSpcSCESUnNewCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCE | SUn | New | CZ10 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0 | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0
CFLAllSpcSCESUnNewCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCE | SUn | New | CZ13 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0 | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0
CFLAllSpcSCESUnNewCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCE | SUn | New | CZ14 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0 | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0
CFLAllSpcSCESUnNewCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCE | SUn | New | CZ15 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0 | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0
CFLAllSpcSCESUnNewCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCE | SUn | New | CZ16 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0 | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0
CFLAllSpcSCESUnNewIOU | Com-Iltg-dWatt-CFL_OSspc | SCE | SUn | New | IOU | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0 | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0
CFLAllSpcSCEWRfExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCE | WRf | Ex | CZ06 | 4.24 | 0.000466 | 0 | 6.61 | 0.000585 | 0 | 4.24 | 0.000466 | 0 | 6.61 | 0.000585 | 0 |  | CFL | AllSpc | 4240 | 0.466 | 4240 | 0.466 | 1.56 | 1.26 | 0 | 4240 | 0.466 | 4240 | 0.466 | 1.56 | 1.26 | 0
CFLAllSpcSCEWRfExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCE | WRf | Ex | CZ08 | 4.24 | 0.000466 | 0 | 6.69 | 0.000586 | 0 | 4.24 | 0.000466 | 0 | 6.69 | 0.000586 | 0 |  | CFL | AllSpc | 4240 | 0.466 | 4240 | 0.466 | 1.58 | 1.26 | 0 | 4240 | 0.466 | 4240 | 0.466 | 1.58 | 1.26 | 0
CFLAllSpcSCEWRfExCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCE | WRf | Ex | CZ09 | 4.24 | 0.000466 | 0 | 6.79 | 0.0006 | 0 | 4.24 | 0.000466 | 0 | 6.79 | 0.0006 | 0 |  | CFL | AllSpc | 4240 | 0.466 | 4240 | 0.466 | 1.6 | 1.29 | 0 | 4240 | 0.466 | 4240 | 0.466 | 1.6 | 1.29 | 0
CFLAllSpcSCEWRfExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCE | WRf | Ex | CZ10 | 4.24 | 0.000466 | 0 | 6.83 | 0.000589 | 0 | 4.24 | 0.000466 | 0 | 6.83 | 0.000589 | 0 |  | CFL | AllSpc | 4240 | 0.466 | 4240 | 0.466 | 1.61 | 1.26 | 0 | 4240 | 0.466 | 4240 | 0.466 | 1.61 | 1.26 | 0
CFLAllSpcSCEWRfExCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCE | WRf | Ex | CZ13 | 4.24 | 0.000466 | 0 | 6.8414 | 0.000587 | 0 | 4.24 | 0.000466 | 0 | 6.8414 | 0.000587 | 0 |  | CFL | AllSpc | 4240 | 0.466 | 4240 | 0.466 | 1.61 | 1.26 | 0 | 4240 | 0.466 | 4240 | 0.466 | 1.61 | 1.26 | 0
CFLAllSpcSCEWRfExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCE | WRf | Ex | CZ14 | 4.24 | 0.000466 | 0 | 6.6809 | 0.000586 | 0 | 4.24 | 0.000466 | 0 | 6.6809 | 0.000586 | 0 |  | CFL | AllSpc | 4240 | 0.466 | 4240 | 0.466 | 1.58 | 1.26 | 0 | 4240 | 0.466 | 4240 | 0.466 | 1.58 | 1.26 | 0
CFLAllSpcSCEWRfExCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCE | WRf | Ex | CZ15 | 4.24 | 0.000466 | 0 | 7.04 | 0.000589 | 0 | 4.24 | 0.000466 | 0 | 7.04 | 0.000589 | 0 |  | CFL | AllSpc | 4240 | 0.466 | 4240 | 0.466 | 1.66 | 1.26 | 0 | 4240 | 0.466 | 4240 | 0.466 | 1.66 | 1.26 | 0
CFLAllSpcSCEWRfExCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCE | WRf | Ex | CZ16 | 4.24 | 0.000466 | 0 | 6.18 | 0.000661 | 0 | 4.24 | 0.000466 | 0 | 6.18 | 0.000661 | 0 |  | CFL | AllSpc | 4240 | 0.466 | 4240 | 0.466 | 1.46 | 1.42 | 0 | 4240 | 0.466 | 4240 | 0.466 | 1.46 | 1.42 | 0
CFLAllSpcSCEWRfExIOU | Com-Iltg-dWatt-CFL_OSspc | SCE | WRf | Ex | IOU | 4.24 | 0.000466 | 0 | 6.731 | 0.00058803 | 0 | 4.24 | 0.000466 | 0 | 6.731 | 0.00058803 | 0 |  | CFL | AllSpc | 4240 | 0.466 | 4240 | 0.466 | 1.59 | 1.26 | 0 | 4240 | 0.466 | 4240 | 0.466 | 1.59 | 1.26 | 0
CFLAllSpcSCEWRfNewCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCE | WRf | New | CZ05 | 4.24 | 0.000466 | 0 | 5.97 | 0.000932 | 0 | 4.24 | 0.000466 | 0 | 5.97 | 0.000932 | 0 |  | CFL | AllSpc | 4240 | 0.466 | 4240 | 0.466 | 1.41 | 2 | 0 | 4240 | 0.466 | 4240 | 0.466 | 1.41 | 2 | 0
CFLAllSpcSCEWRfNewCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCE | WRf | New | CZ06 | 4.24 | 0.000466 | 0 | 6.44 | 0.000574 | 0 | 4.24 | 0.000466 | 0 | 6.44 | 0.000574 | 0 |  | CFL | AllSpc | 4240 | 0.466 | 4240 | 0.466 | 1.52 | 1.23 | 0 | 4240 | 0.466 | 4240 | 0.466 | 1.52 | 1.23 | 0
CFLAllSpcSCEWRfNewCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCE | WRf | New | CZ08 | 4.24 | 0.000466 | 0 | 6.4 | 0.000575 | 0 | 4.24 | 0.000466 | 0 | 6.4 | 0.000575 | 0 |  | CFL | AllSpc | 4240 | 0.466 | 4240 | 0.466 | 1.51 | 1.23 | 0 | 4240 | 0.466 | 4240 | 0.466 | 1.51 | 1.23 | 0
CFLAllSpcSCEWRfNewCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCE | WRf | New | CZ09 | 4.24 | 0.000466 | 0 | 6.27 | 0.000598 | 0 | 4.24 | 0.000466 | 0 | 6.27 | 0.000598 | 0 |  | CFL | AllSpc | 4240 | 0.466 | 4240 | 0.466 | 1.48 | 1.28 | 0 | 4240 | 0.466 | 4240 | 0.466 | 1.48 | 1.28 | 0
CFLAllSpcSCEWRfNewCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCE | WRf | New | CZ10 | 4.24 | 0.000466 | 0 | 6.24 | 0.000582 | 0 | 4.24 | 0.000466 | 0 | 6.24 | 0.000582 | 0 |  | CFL | AllSpc | 4240 | 0.466 | 4240 | 0.466 | 1.47 | 1.25 | 0 | 4240 | 0.466 | 4240 | 0.466 | 1.47 | 1.25 | 0
CFLAllSpcSCEWRfNewCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCE | WRf | New | CZ13 | 4.24 | 0.000466 | 0 | 6.23 | 0.000582 | 0 | 4.24 | 0.000466 | 0 | 6.23 | 0.000582 | 0 |  | CFL | AllSpc | 4240 | 0.466 | 4240 | 0.466 | 1.47 | 1.25 | 0 | 4240 | 0.466 | 4240 | 0.466 | 1.47 | 1.25 | 0
CFLAllSpcSCEWRfNewCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCE | WRf | New | CZ14 | 4.24 | 0.000466 | 0 | 6.01 | 0.000577 | 0 | 4.24 | 0.000466 | 0 | 6.01 | 0.000577 | 0 |  | CFL | AllSpc | 4240 | 0.466 | 4240 | 0.466 | 1.42 | 1.24 | 0 | 4240 | 0.466 | 4240 | 0.466 | 1.42 | 1.24 | 0
CFLAllSpcSCEWRfNewCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCE | WRf | New | CZ15 | 4.24 | 0.000466 | 0 | 6.45 | 0.000581 | 0 | 4.24 | 0.000466 | 0 | 6.45 | 0.000581 | 0 |  | CFL | AllSpc | 4240 | 0.466 | 4240 | 0.466 | 1.52 | 1.25 | 0 | 4240 | 0.466 | 4240 | 0.466 | 1.52 | 1.25 | 0
CFLAllSpcSCEWRfNewCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCE | WRf | New | CZ16 | 4.24 | 0.000466 | 0 | 5.59 | 0.000932 | 0 | 4.24 | 0.000466 | 0 | 5.59 | 0.000932 | 0 |  | CFL | AllSpc | 4240 | 0.466 | 4240 | 0.466 | 1.32 | 2 | 0 | 4240 | 0.466 | 4240 | 0.466 | 1.32 | 2 | 0
CFLAllSpcSCEWRfNewIOU | Com-Iltg-dWatt-CFL_OSspc | SCE | WRf | New | IOU | 4.24 | 0.000466 | 0 | 6.3163 | 0.00058189 | 0 | 4.24 | 0.000466 | 0 | 6.3163 | 0.00058189 | 0 |  | CFL | AllSpc | 4240 | 0.466 | 4240 | 0.466 | 1.49 | 1.25 | 0 | 4240 | 0.466 | 4240 | 0.466 | 1.49 | 1.25 | 0
CFLAllSpcSDGAsmExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SDG | Asm | Ex | CZ06 | 2.03 | 0.00033191 | 0 | 2.2209 | 0.00041191 | -0.0106 | 2.03 | 0.00033191 | 0 | 2.2209 | 0.00041191 | -0.0106 |  | CFL | AllSpc | 2030 | 0.332 | 2030 | 0.332 | 1.09 | 1.24 | -0.0052217 | 2030 | 0.332 | 2030 | 0.332 | 1.09 | 1.24 | -0.00522
CFLAllSpcSDGAsmExCZ07 | Com-Iltg-dWatt-CFL_OSspc | SDG | Asm | Ex | CZ07 | 2.03 | 0.00033191 | 0 | 2.23 | 0.00041091 | -0.0097228 | 2.03 | 0.00033191 | 0 | 2.23 | 0.00041091 | -0.0097228 |  | CFL | AllSpc | 2030 | 0.332 | 2030 | 0.332 | 1.1 | 1.24 | -0.0047895 | 2030 | 0.332 | 2030 | 0.332 | 1.1 | 1.24 | -0.00479
CFLAllSpcSDGAsmExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SDG | Asm | Ex | CZ08 | 2.03 | 0.00033191 | 0 | 2.24 | 0.00039991 | -0.0092619 | 2.03 | 0.00033191 | 0 | 2.24 | 0.00039991 | -0.0092619 |  | CFL | AllSpc | 2030 | 0.332 | 2030 | 0.332 | 1.1 | 1.2 | -0.0045625 | 2030 | 0.332 | 2030 | 0.332 | 1.1 | 1.2 | -0.00456
CFLAllSpcSDGAsmExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SDG | Asm | Ex | CZ10 | 2.03 | 0.00033191 | 0 | 2.2209 | 0.00040291 | -0.0118 | 2.03 | 0.00033191 | 0 | 2.2209 | 0.00040291 | -0.0118 |  | CFL | AllSpc | 2030 | 0.332 | 2030 | 0.332 | 1.09 | 1.21 | -0.0058128 | 2030 | 0.332 | 2030 | 0.332 | 1.09 | 1.21 | -0.00581
CFLAllSpcSDGAsmExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SDG | Asm | Ex | CZ14 | 2.03 | 0.00033191 | 0 | 2.1709 | 0.00037691 | -0.0185 | 2.03 | 0.00033191 | 0 | 2.1709 | 0.00037691 | -0.0185 |  | CFL | AllSpc | 2030 | 0.332 | 2030 | 0.332 | 1.07 | 1.14 | -0.0091133 | 2030 | 0.332 | 2030 | 0.332 | 1.07 | 1.14 | -0.00911
CFLAllSpcSDGAsmExCZ15 | Com-Iltg-dWatt-CFL_OSspc | SDG | Asm | Ex | CZ15 | 2.03 | 0.00033191 | 0 | 2.5409 | 0.00039191 | -0.0051809 | 2.03 | 0.00033191 | 0 | 2.5409 | 0.00039191 | -0.0051809 |  | CFL | AllSpc | 2030 | 0.332 | 2030 | 0.332 | 1.25 | 1.18 | -0.0025522 | 2030 | 0.332 | 2030 | 0.332 | 1.25 | 1.18 | -0.00255
CFLAllSpcSDGAsmExIOU | Com-Iltg-dWatt-CFL_OSspc | SDG | Asm | Ex | IOU | 2.03 | 0.00033191 | 0 | 2.2276 | 0.00040791 | -0.010442 | 2.03 | 0.00033191 | 0 | 2.2276 | 0.00040791 | -0.010442 |  | CFL | AllSpc | 2030 | 0.332 | 2030 | 0.332 | 1.1 | 1.23 | -0.0051437 | 2030 | 0.332 | 2030 | 0.332 | 1.1 | 1.23 | -0.00514
CFLAllSpcSDGAsmNewCZ06 | Com-Iltg-dWatt-CFL_OSspc | SDG | Asm | New | CZ06 | 2.03 | 0.000331 | 0 | 2.2 | 0.000408 | -0.0137 | 2.03 | 0.000331 | 0 | 2.2 | 0.000408 | -0.0137 |  | CFL | AllSpc | 2030 | 0.331 | 2030 | 0.331 | 1.08 | 1.23 | -0.0067488 | 2030 | 0.331 | 2030 | 0.331 | 1.08 | 1.23 | -0.00675
CFLAllSpcSDGAsmNewCZ07 | Com-Iltg-dWatt-CFL_OSspc | SDG | Asm | New | CZ07 | 2.03 | 0.000331 | 0 | 2.21 | 0.000406 | -0.012 | 2.03 | 0.000331 | 0 | 2.21 | 0.000406 | -0.012 |  | CFL | AllSpc | 2030 | 0.331 | 2030 | 0.331 | 1.09 | 1.23 | -0.0059113 | 2030 | 0.331 | 2030 | 0.331 | 1.09 | 1.23 | -0.00591
CFLAllSpcSDGAsmNewCZ08 | Com-Iltg-dWatt-CFL_OSspc | SDG | Asm | New | CZ08 | 2.03 | 0.000331 | 0 | 2.23 | 0.000403 | -0.0106 | 2.03 | 0.000331 | 0 | 2.23 | 0.000403 | -0.0106 |  | CFL | AllSpc | 2030 | 0.331 | 2030 | 0.331 | 1.1 | 1.22 | -0.0052217 | 2030 | 0.331 | 2030 | 0.331 | 1.1 | 1.22 | -0.00522
CFLAllSpcSDGAsmNewCZ10 | Com-Iltg-dWatt-CFL_OSspc | SDG | Asm | New | CZ10 | 2.03 | 0.000331 | 0 | 2.21 | 0.000412 | -0.0127 | 2.03 | 0.000331 | 0 | 2.21 | 0.000412 | -0.0127 |  | CFL | AllSpc | 2030 | 0.331 | 2030 | 0.331 | 1.09 | 1.24 | -0.0062562 | 2030 | 0.331 | 2030 | 0.331 | 1.09 | 1.24 | -0.00626
CFLAllSpcSDGAsmNewCZ14 | Com-Iltg-dWatt-CFL_OSspc | SDG | Asm | New | CZ14 | 2.03 | 0.000331 | 0 | 2.16 | 0.000396 | -0.0196 | 2.03 | 0.000331 | 0 | 2.16 | 0.000396 | -0.0196 |  | CFL | AllSpc | 2030 | 0.331 | 2030 | 0.331 | 1.06 | 1.2 | -0.0096552 | 2030 | 0.331 | 2030 | 0.331 | 1.06 | 1.2 | -0.00966
CFLAllSpcSDGAsmNewCZ15 | Com-Iltg-dWatt-CFL_OSspc | SDG | Asm | New | CZ15 | 2.03 | 0.000331 | 0 | 2.45 | 0.000415 | -0.00608 | 2.03 | 0.000331 | 0 | 2.45 | 0.000415 | -0.00608 |  | CFL | AllSpc | 2030 | 0.331 | 2030 | 0.331 | 1.21 | 1.25 | -0.0029951 | 2030 | 0.331 | 2030 | 0.331 | 1.21 | 1.25 | -0.003
CFLAllSpcSDGAsmNewIOU | Com-Iltg-dWatt-CFL_OSspc | SDG | Asm | New | IOU | 2.03 | 0.000331 | 0 | 2.2103 | 0.00040776 | -0.012294 | 2.03 | 0.000331 | 0 | 2.2103 | 0.00040776 | -0.012294 |  | CFL | AllSpc | 2030 | 0.331 | 2030 | 0.331 | 1.09 | 1.23 | -0.0060561 | 2030 | 0.331 | 2030 | 0.331 | 1.09 | 1.23 | -0.00606
CFLAllSpcSDGComExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SDG | Com | Ex | CZ06 | 2.8441 | 0.0005185 | 0 | 3.1253 | 0.00064232 | -0.012338 | 2.8441 | 0.0005185 | 0 | 3.1253 | 0.00064232 | -0.012338 |  | CFL | AllSpc | 2840 | 0.519 | 2840 | 0.519 | 1.1 | 1.24 | -0.0043382 | 2840 | 0.519 | 2840 | 0.519 | 1.1 | 1.24 | -0.00434
CFLAllSpcSDGComExCZ07 | Com-Iltg-dWatt-CFL_OSspc | SDG | Com | Ex | CZ07 | 2.7824 | 0.00051892 | 0 | 3.088 | 0.00063836 | -0.0086344 | 2.7824 | 0.00051892 | 0 | 3.088 | 0.00063836 | -0.0086344 |  | CFL | AllSpc | 2780 | 0.519 | 2780 | 0.519 | 1.11 | 1.23 | -0.0031032 | 2780 | 0.519 | 2780 | 0.519 | 1.11 | 1.23 | -0.0031
CFLAllSpcSDGComExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SDG | Com | Ex | CZ08 | 3.1591 | 0.00058362 | 0 | 3.5375 | 0.00073061 | -0.010149 | 3.1591 | 0.00058362 | 0 | 3.5375 | 0.00073061 | -0.010149 |  | CFL | AllSpc | 3160 | 0.584 | 3160 | 0.584 | 1.12 | 1.25 | -0.0032126 | 3160 | 0.584 | 3160 | 0.584 | 1.12 | 1.25 | -0.00321
CFLAllSpcSDGComExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SDG | Com | Ex | CZ10 | 2.8419 | 0.00054476 | 0 | 3.1434 | 0.00068437 | -0.01102 | 2.8419 | 0.00054476 | 0 | 3.1434 | 0.00068437 | -0.01102 |  | CFL | AllSpc | 2840 | 0.545 | 2840 | 0.545 | 1.11 | 1.26 | -0.0038778 | 2840 | 0.545 | 2840 | 0.545 | 1.11 | 1.26 | -0.00388
CFLAllSpcSDGComExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SDG | Com | Ex | CZ14 | 2.3886 | 0.00048881 | 0 | 2.6023 | 0.00061081 | -0.01336 | 2.3886 | 0.00048881 | 0 | 2.6023 | 0.00061081 | -0.01336 |  | CFL | AllSpc | 2390 | 0.489 | 2390 | 0.489 | 1.09 | 1.25 | -0.0055932 | 2390 | 0.489 | 2390 | 0.489 | 1.09 | 1.25 | -0.00559
CFLAllSpcSDGComExCZ15 | Com-Iltg-dWatt-CFL_OSspc | SDG | Com | Ex | CZ15 | 2.104 | 0.00038845 | 0 | 2.4879 | 0.00048888 | -0.0031907 | 2.104 | 0.00038845 | 0 | 2.4879 | 0.00048888 | -0.0031907 |  | CFL | AllSpc | 2100 | 0.388 | 2100 | 0.388 | 1.18 | 1.26 | -0.0015165 | 2100 | 0.388 | 2100 | 0.388 | 1.18 | 1.26 | -0.00152
CFLAllSpcSDGComExIOU | Com-Iltg-dWatt-CFL_OSspc | SDG | Com | Ex | IOU | 2.8058 | 0.00052634 | 0 | 3.1115 | 0.00065135 | -0.009356 | 2.8058 | 0.00052634 | 0 | 3.1115 | 0.00065135 | -0.009356 |  | CFL | AllSpc | 2810 | 0.526 | 2810 | 0.526 | 1.11 | 1.24 | -0.0033346 | 2810 | 0.526 | 2810 | 0.526 | 1.11 | 1.24 | -0.00333
CFLAllSpcSDGComNewCZ06 | Com-Iltg-dWatt-CFL_OSspc | SDG | Com | New | CZ06 | 2.7925 | 0.00049329 | 0 | 3.0223 | 0.00060841 | -0.012635 | 2.7925 | 0.00049329 | 0 | 3.0223 | 0.00060841 | -0.012635 |  | CFL | AllSpc | 2790 | 0.493 | 2790 | 0.493 | 1.08 | 1.23 | -0.0045246 | 2790 | 0.493 | 2790 | 0.493 | 1.08 | 1.23 | -0.00452
CFLAllSpcSDGComNewCZ07 | Com-Iltg-dWatt-CFL_OSspc | SDG | Com | New | CZ07 | 2.7293 | 0.00050023 | 0 | 2.9715 | 0.00060739 | -0.0085585 | 2.7293 | 0.00050023 | 0 | 2.9715 | 0.00060739 | -0.0085585 |  | CFL | AllSpc | 2730 | 0.5 | 2730 | 0.5 | 1.09 | 1.21 | -0.0031358 | 2730 | 0.5 | 2730 | 0.5 | 1.09 | 1.21 | -0.00314
CFLAllSpcSDGComNewCZ08 | Com-Iltg-dWatt-CFL_OSspc | SDG | Com | New | CZ08 | 3.2317 | 0.00058428 | 0 | 3.551 | 0.00072738 | -0.010599 | 3.2317 | 0.00058428 | 0 | 3.551 | 0.00072738 | -0.010599 |  | CFL | AllSpc | 3230 | 0.584 | 3230 | 0.584 | 1.1 | 1.24 | -0.0032798 | 3230 | 0.584 | 3230 | 0.584 | 1.1 | 1.24 | -0.00328
CFLAllSpcSDGComNewCZ10 | Com-Iltg-dWatt-CFL_OSspc | SDG | Com | New | CZ10 | 2.8475 | 0.00053771 | 0 | 3.1306 | 0.00069528 | -0.011255 | 2.8475 | 0.00053771 | 0 | 3.1306 | 0.00069528 | -0.011255 |  | CFL | AllSpc | 2850 | 0.538 | 2850 | 0.538 | 1.1 | 1.29 | -0.0039527 | 2850 | 0.538 | 2850 | 0.538 | 1.1 | 1.29 | -0.00395
CFLAllSpcSDGComNewCZ14 | Com-Iltg-dWatt-CFL_OSspc | SDG | Com | New | CZ14 | 2.3226 | 0.00046171 | 0 | 2.5164 | 0.00059119 | -0.013178 | 2.3226 | 0.00046171 | 0 | 2.5164 | 0.00059119 | -0.013178 |  | CFL | AllSpc | 2320 | 0.462 | 2320 | 0.462 | 1.08 | 1.28 | -0.0056739 | 2320 | 0.462 | 2320 | 0.462 | 1.08 | 1.28 | -0.00567
CFLAllSpcSDGComNewCZ15 | Com-Iltg-dWatt-CFL_OSspc | SDG | Com | New | CZ15 | 1.9722 | 0.000344 | 0 | 2.3189 | 0.00045263 | -0.0028414 | 1.9722 | 0.000344 | 0 | 2.3189 | 0.00045263 | -0.0028414 |  | CFL | AllSpc | 1970 | 0.344 | 1970 | 0.344 | 1.18 | 1.32 | -0.0014407 | 1970 | 0.344 | 1970 | 0.344 | 1.18 | 1.32 | -0.00144
CFLAllSpcSDGComNewIOU | Com-Iltg-dWatt-CFL_OSspc | SDG | Com | New | IOU | 2.7685 | 0.0005104 | 0 | 3.0219 | 0.00063062 | -0.0093826 | 2.7685 | 0.0005104 | 0 | 3.0219 | 0.00063062 | -0.0093826 |  | CFL | AllSpc | 2770 | 0.51 | 2770 | 0.51 | 1.09 | 1.24 | -0.0033891 | 2770 | 0.51 | 2770 | 0.51 | 1.09 | 1.24 | -0.00339
CFLAllSpcSDGECCExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SDG | ECC | Ex | CZ06 | 2.22 | 0.000532 | 0 | 2.49 | 0.00067894 | -0.0129 | 2.22 | 0.000532 | 0 | 2.49 | 0.00067894 | -0.0129 |  | CFL | AllSpc | 2220 | 0.532 | 2220 | 0.532 | 1.12 | 1.28 | -0.0058108 | 2220 | 0.532 | 2220 | 0.532 | 1.12 | 1.28 | -0.00581
CFLAllSpcSDGECCExCZ07 | Com-Iltg-dWatt-CFL_OSspc | SDG | ECC | Ex | CZ07 | 2.22 | 0.000532 | 0 | 2.51 | 0.00067794 | -0.0107 | 2.22 | 0.000532 | 0 | 2.51 | 0.00067794 | -0.0107 |  | CFL | AllSpc | 2220 | 0.532 | 2220 | 0.532 | 1.13 | 1.27 | -0.0048198 | 2220 | 0.532 | 2220 | 0.532 | 1.13 | 1.27 | -0.00482
CFLAllSpcSDGECCExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SDG | ECC | Ex | CZ08 | 2.22 | 0.000532 | 0 | 2.52 | 0.00067594 | -0.0116 | 2.22 | 0.000532 | 0 | 2.52 | 0.00067594 | -0.0116 |  | CFL | AllSpc | 2220 | 0.532 | 2220 | 0.532 | 1.14 | 1.27 | -0.0052252 | 2220 | 0.532 | 2220 | 0.532 | 1.14 | 1.27 | -0.00523
CFLAllSpcSDGECCExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SDG | ECC | Ex | CZ10 | 2.22 | 0.000532 | 0 | 2.51 | 0.00068894 | -0.0137 | 2.22 | 0.000532 | 0 | 2.51 | 0.00068894 | -0.0137 |  | CFL | AllSpc | 2220 | 0.532 | 2220 | 0.532 | 1.13 | 1.29 | -0.0061712 | 2220 | 0.532 | 2220 | 0.532 | 1.13 | 1.29 | -0.00617
CFLAllSpcSDGECCExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SDG | ECC | Ex | CZ14 | 2.22 | 0.000532 | 0 | 2.46 | 0.00067894 | -0.0207 | 2.22 | 0.000532 | 0 | 2.46 | 0.00067894 | -0.0207 |  | CFL | AllSpc | 2220 | 0.532 | 2220 | 0.532 | 1.11 | 1.28 | -0.0093243 | 2220 | 0.532 | 2220 | 0.532 | 1.11 | 1.28 | -0.00932
CFLAllSpcSDGECCExIOU | Com-Iltg-dWatt-CFL_OSspc | SDG | ECC | Ex | IOU | 2.22 | 0.000532 | 0 | 2.5097 | 0.00068052 | -0.011476 | 2.22 | 0.000532 | 0 | 2.5097 | 0.00068052 | -0.011476 |  | CFL | AllSpc | 2220 | 0.532 | 2220 | 0.532 | 1.13 | 1.28 | -0.0051695 | 2220 | 0.532 | 2220 | 0.532 | 1.13 | 1.28 | -0.00517
CFLAllSpcSDGECCNewCZ06 | Com-Iltg-dWatt-CFL_OSspc | SDG | ECC | New | CZ06 | 2.22 | 0.000532 | 0 | 2.5 | 0.000682 | -0.0157 | 2.22 | 0.000532 | 0 | 2.5 | 0.000682 | -0.0157 |  | CFL | AllSpc | 2220 | 0.532 | 2220 | 0.532 | 1.13 | 1.28 | -0.0070721 | 2220 | 0.532 | 2220 | 0.532 | 1.13 | 1.28 | -0.00707
CFLAllSpcSDGECCNewCZ07 | Com-Iltg-dWatt-CFL_OSspc | SDG | ECC | New | CZ07 | 2.22 | 0.000532 | 0 | 2.49 | 0.000687 | -0.0118 | 2.22 | 0.000532 | 0 | 2.49 | 0.000687 | -0.0118 |  | CFL | AllSpc | 2220 | 0.532 | 2220 | 0.532 | 1.12 | 1.29 | -0.0053153 | 2220 | 0.532 | 2220 | 0.532 | 1.12 | 1.29 | -0.00532
CFLAllSpcSDGECCNewCZ08 | Com-Iltg-dWatt-CFL_OSspc | SDG | ECC | New | CZ08 | 2.22 | 0.000532 | 0 | 2.52 | 0.000681 | -0.0115 | 2.22 | 0.000532 | 0 | 2.52 | 0.000681 | -0.0115 |  | CFL | AllSpc | 2220 | 0.532 | 2220 | 0.532 | 1.14 | 1.28 | -0.0051802 | 2220 | 0.532 | 2220 | 0.532 | 1.14 | 1.28 | -0.00518
CFLAllSpcSDGECCNewCZ10 | Com-Iltg-dWatt-CFL_OSspc | SDG | ECC | New | CZ10 | 2.22 | 0.000532 | 0 | 2.54 | 0.000702 | -0.0131 | 2.22 | 0.000532 | 0 | 2.54 | 0.000702 | -0.0131 |  | CFL | AllSpc | 2220 | 0.532 | 2220 | 0.532 | 1.14 | 1.32 | -0.0059009 | 2220 | 0.532 | 2220 | 0.532 | 1.14 | 1.32 | -0.0059
CFLAllSpcSDGECCNewCZ14 | Com-Iltg-dWatt-CFL_OSspc | SDG | ECC | New | CZ14 | 2.22 | 0.000532 | 0 | 2.51 | 0.00068 | -0.0206 | 2.22 | 0.000532 | 0 | 2.51 | 0.00068 | -0.0206 |  | CFL | AllSpc | 2220 | 0.532 | 2220 | 0.532 | 1.13 | 1.28 | -0.0092793 | 2220 | 0.532 | 2220 | 0.532 | 1.13 | 1.28 | -0.00928
CFLAllSpcSDGECCNewCZ15 | Com-Iltg-dWatt-CFL_OSspc | SDG | ECC | New | CZ15 | 2.22 | 0.000532 | 0 | 2.68 | 0.000697 | -0.00513 | 2.22 | 0.000532 | 0 | 2.68 | 0.000697 | -0.00513 |  | CFL | AllSpc | 2220 | 0.532 | 2220 | 0.532 | 1.21 | 1.31 | -0.0023108 | 2220 | 0.532 | 2220 | 0.532 | 1.21 | 1.31 | -0.00231
CFLAllSpcSDGECCNewIOU | Com-Iltg-dWatt-CFL_OSspc | SDG | ECC | New | IOU | 2.22 | 0.000532 | 0 | 2.5022 | 0.00069041 | -0.012169 | 2.22 | 0.000532 | 0 | 2.5022 | 0.00069041 | -0.012169 |  | CFL | AllSpc | 2220 | 0.532 | 2220 | 0.532 | 1.13 | 1.3 | -0.0054815 | 2220 | 0.532 | 2220 | 0.532 | 1.13 | 1.3 | -0.00548
CFLAllSpcSDGEPrExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SDG | EPr | Ex | CZ06 | 2.05 | 0.00054425 | 0 | 2.31 | 0.00069432 | -0.00954 | 2.05 | 0.00054425 | 0 | 2.31 | 0.00069432 | -0.00954 |  | CFL | AllSpc | 2050 | 0.544 | 2050 | 0.544 | 1.13 | 1.28 | -0.0046537 | 2050 | 0.544 | 2050 | 0.544 | 1.13 | 1.28 | -0.00465
CFLAllSpcSDGEPrExCZ07 | Com-Iltg-dWatt-CFL_OSspc | SDG | EPr | Ex | CZ07 | 2.05 | 0.00054425 | 0 | 2.31 | 0.00070032 | -0.00878 | 2.05 | 0.00054425 | 0 | 2.31 | 0.00070032 | -0.00878 |  | CFL | AllSpc | 2050 | 0.544 | 2050 | 0.544 | 1.13 | 1.29 | -0.0042829 | 2050 | 0.544 | 2050 | 0.544 | 1.13 | 1.29 | -0.00428
CFLAllSpcSDGEPrExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SDG | EPr | Ex | CZ08 | 2.05 | 0.00054425 | 0 | 2.34 | 0.00070132 | -0.00802 | 2.05 | 0.00054425 | 0 | 2.34 | 0.00070132 | -0.00802 |  | CFL | AllSpc | 2050 | 0.544 | 2050 | 0.544 | 1.14 | 1.29 | -0.0039122 | 2050 | 0.544 | 2050 | 0.544 | 1.14 | 1.29 | -0.00391
CFLAllSpcSDGEPrExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SDG | EPr | Ex | CZ10 | 2.05 | 0.00054425 | 0 | 2.32 | 0.00069432 | -0.0101 | 2.05 | 0.00054425 | 0 | 2.32 | 0.00069432 | -0.0101 |  | CFL | AllSpc | 2050 | 0.544 | 2050 | 0.544 | 1.13 | 1.28 | -0.0049268 | 2050 | 0.544 | 2050 | 0.544 | 1.13 | 1.28 | -0.00493
CFLAllSpcSDGEPrExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SDG | EPr | Ex | CZ14 | 2.05 | 0.00054425 | 0 | 2.22 | 0.00069532 | -0.0168 | 2.05 | 0.00054425 | 0 | 2.22 | 0.00069532 | -0.0168 |  | CFL | AllSpc | 2050 | 0.544 | 2050 | 0.544 | 1.08 | 1.28 | -0.0081951 | 2050 | 0.544 | 2050 | 0.544 | 1.08 | 1.28 | -0.0082
CFLAllSpcSDGEPrExCZ15 | Com-Iltg-dWatt-CFL_OSspc | SDG | EPr | Ex | CZ15 | 2.05 | 0.00054424 | 0 | 2.48 | 0.00069831 | -0.00428 | 2.05 | 0.00054424 | 0 | 2.48 | 0.00069831 | -0.00428 |  | CFL | AllSpc | 2050 | 0.544 | 2050 | 0.544 | 1.21 | 1.28 | -0.0020878 | 2050 | 0.544 | 2050 | 0.544 | 1.21 | 1.28 | -0.00209
CFLAllSpcSDGEPrExIOU | Com-Iltg-dWatt-CFL_OSspc | SDG | EPr | Ex | IOU | 2.05 | 0.00054425 | 0 | 2.3145 | 0.00069808 | -0.0092657 | 2.05 | 0.00054425 | 0 | 2.3145 | 0.00069808 | -0.0092657 |  | CFL | AllSpc | 2050 | 0.544 | 2050 | 0.544 | 1.13 | 1.28 | -0.0045199 | 2050 | 0.544 | 2050 | 0.544 | 1.13 | 1.28 | -0.00452
CFLAllSpcSDGEPrNewCZ06 | Com-Iltg-dWatt-CFL_OSspc | SDG | EPr | New | CZ06 | 2.05 | 0.000551 | 0 | 2.25 | 0.000737 | -0.013 | 2.05 | 0.000551 | 0 | 2.25 | 0.000737 | -0.013 |  | CFL | AllSpc | 2050 | 0.551 | 2050 | 0.551 | 1.1 | 1.34 | -0.0063415 | 2050 | 0.551 | 2050 | 0.551 | 1.1 | 1.34 | -0.00634
CFLAllSpcSDGEPrNewCZ07 | Com-Iltg-dWatt-CFL_OSspc | SDG | EPr | New | CZ07 | 2.05 | 0.000551 | 0 | 2.22 | 0.000729 | -0.0121 | 2.05 | 0.000551 | 0 | 2.22 | 0.000729 | -0.0121 |  | CFL | AllSpc | 2050 | 0.551 | 2050 | 0.551 | 1.08 | 1.32 | -0.0059024 | 2050 | 0.551 | 2050 | 0.551 | 1.08 | 1.32 | -0.0059
CFLAllSpcSDGEPrNewCZ08 | Com-Iltg-dWatt-CFL_OSspc | SDG | EPr | New | CZ08 | 2.05 | 0.000551 | 0 | 2.28 | 0.000757 | -0.0112 | 2.05 | 0.000551 | 0 | 2.28 | 0.000757 | -0.0112 |  | CFL | AllSpc | 2050 | 0.551 | 2050 | 0.551 | 1.11 | 1.37 | -0.0054634 | 2050 | 0.551 | 2050 | 0.551 | 1.11 | 1.37 | -0.00546
CFLAllSpcSDGEPrNewCZ10 | Com-Iltg-dWatt-CFL_OSspc | SDG | EPr | New | CZ10 | 2.05 | 0.000551 | 0 | 2.28 | 0.000784 | -0.0134 | 2.05 | 0.000551 | 0 | 2.28 | 0.000784 | -0.0134 |  | CFL | AllSpc | 2050 | 0.551 | 2050 | 0.551 | 1.11 | 1.42 | -0.0065366 | 2050 | 0.551 | 2050 | 0.551 | 1.11 | 1.42 | -0.00654
CFLAllSpcSDGEPrNewCZ14 | Com-Iltg-dWatt-CFL_OSspc | SDG | EPr | New | CZ14 | 2.05 | 0.000551 | 0 | 2.24 | 0.000767 | -0.0211 | 2.05 | 0.000551 | 0 | 2.24 | 0.000767 | -0.0211 |  | CFL | AllSpc | 2050 | 0.551 | 2050 | 0.551 | 1.09 | 1.39 | -0.010293 | 2050 | 0.551 | 2050 | 0.551 | 1.09 | 1.39 | -0.0103
CFLAllSpcSDGEPrNewCZ15 | Com-Iltg-dWatt-CFL_OSspc | SDG | EPr | New | CZ15 | 2.05 | 0.000551 | 0 | 2.48 | 0.000794 | -0.00587 | 2.05 | 0.000551 | 0 | 2.48 | 0.000794 | -0.00587 |  | CFL | AllSpc | 2050 | 0.551 | 2050 | 0.551 | 1.21 | 1.44 | -0.0028634 | 2050 | 0.551 | 2050 | 0.551 | 1.21 | 1.44 | -0.00286
CFLAllSpcSDGEPrNewIOU | Com-Iltg-dWatt-CFL_OSspc | SDG | EPr | New | IOU | 2.05 | 0.000551 | 0 | 2.2451 | 0.00074933 | -0.012584 | 2.05 | 0.000551 | 0 | 2.2451 | 0.00074933 | -0.012584 |  | CFL | AllSpc | 2050 | 0.551 | 2050 | 0.551 | 1.1 | 1.36 | -0.0061386 | 2050 | 0.551 | 2050 | 0.551 | 1.1 | 1.36 | -0.00614
CFLAllSpcSDGERCExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SDG | ERC | Ex | CZ06 | 2.39 | 0.00062329 | 0 | 2.61 | 0.00077536 | -0.0147 | 2.39 | 0.00062329 | 0 | 2.61 | 0.00077536 | -0.0147 |  | CFL | AllSpc | 2390 | 0.623 | 2390 | 0.623 | 1.09 | 1.24 | -0.0061506 | 2390 | 0.623 | 2390 | 0.623 | 1.09 | 1.24 | -0.00615
CFLAllSpcSDGERCExCZ07 | Com-Iltg-dWatt-CFL_OSspc | SDG | ERC | Ex | CZ07 | 2.39 | 0.00062328 | 0 | 2.67 | 0.00077436 | -0.0118 | 2.39 | 0.00062328 | 0 | 2.67 | 0.00077436 | -0.0118 |  | CFL | AllSpc | 2390 | 0.623 | 2390 | 0.623 | 1.12 | 1.24 | -0.0049372 | 2390 | 0.623 | 2390 | 0.623 | 1.12 | 1.24 | -0.00494
CFLAllSpcSDGERCExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SDG | ERC | Ex | CZ08 | 2.39 | 0.00062328 | 0 | 2.64 | 0.00078435 | -0.0129 | 2.39 | 0.00062328 | 0 | 2.64 | 0.00078435 | -0.0129 |  | CFL | AllSpc | 2390 | 0.623 | 2390 | 0.623 | 1.1 | 1.26 | -0.0053975 | 2390 | 0.623 | 2390 | 0.623 | 1.1 | 1.26 | -0.0054
CFLAllSpcSDGERCExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SDG | ERC | Ex | CZ10 | 2.39 | 0.00062328 | 0 | 2.61 | 0.00077939 | -0.015 | 2.39 | 0.00062328 | 0 | 2.61 | 0.00077939 | -0.015 |  | CFL | AllSpc | 2390 | 0.623 | 2390 | 0.623 | 1.09 | 1.25 | -0.0062762 | 2390 | 0.623 | 2390 | 0.623 | 1.09 | 1.25 | -0.00628
CFLAllSpcSDGERCExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SDG | ERC | Ex | CZ14 | 2.39 | 0.00062329 | 0 | 2.6 | 0.0007914 | -0.0199 | 2.39 | 0.00062329 | 0 | 2.6 | 0.0007914 | -0.0199 |  | CFL | AllSpc | 2390 | 0.623 | 2390 | 0.623 | 1.09 | 1.27 | -0.0083264 | 2390 | 0.623 | 2390 | 0.623 | 1.09 | 1.27 | -0.00833
CFLAllSpcSDGERCExCZ15 | Com-Iltg-dWatt-CFL_OSspc | SDG | ERC | Ex | CZ15 | 2.39 | 0.00062327 | 0 | 2.81 | 0.00080238 | -0.0073 | 2.39 | 0.00062327 | 0 | 2.81 | 0.00080238 | -0.0073 |  | CFL | AllSpc | 2390 | 0.623 | 2390 | 0.623 | 1.18 | 1.29 | -0.0030544 | 2390 | 0.623 | 2390 | 0.623 | 1.18 | 1.29 | -0.00305
CFLAllSpcSDGERCExIOU | Com-Iltg-dWatt-CFL_OSspc | SDG | ERC | Ex | IOU | 2.39 | 0.00062328 | 0 | 2.6456 | 0.00077681 | -0.013105 | 2.39 | 0.00062328 | 0 | 2.6456 | 0.00077681 | -0.013105 |  | CFL | AllSpc | 2390 | 0.623 | 2390 | 0.623 | 1.11 | 1.25 | -0.0054835 | 2390 | 0.623 | 2390 | 0.623 | 1.11 | 1.25 | -0.00548
CFLAllSpcSDGERCNewCZ06 | Com-Iltg-dWatt-CFL_OSspc | SDG | ERC | New | CZ06 | 2.39 | 0.000631 | 0 | 2.72 | 0.000808 | -0.0162 | 2.39 | 0.000631 | 0 | 2.72 | 0.000808 | -0.0162 |  | CFL | AllSpc | 2390 | 0.631 | 2390 | 0.631 | 1.14 | 1.28 | -0.0067782 | 2390 | 0.631 | 2390 | 0.631 | 1.14 | 1.28 | -0.00678
CFLAllSpcSDGERCNewCZ07 | Com-Iltg-dWatt-CFL_OSspc | SDG | ERC | New | CZ07 | 2.39 | 0.000631 | 0 | 2.73 | 0.000796 | -0.0125 | 2.39 | 0.000631 | 0 | 2.73 | 0.000796 | -0.0125 |  | CFL | AllSpc | 2390 | 0.631 | 2390 | 0.631 | 1.14 | 1.26 | -0.0052301 | 2390 | 0.631 | 2390 | 0.631 | 1.14 | 1.26 | -0.00523
CFLAllSpcSDGERCNewCZ08 | Com-Iltg-dWatt-CFL_OSspc | SDG | ERC | New | CZ08 | 2.39 | 0.000631 | 0 | 2.75 | 0.000827 | -0.0141 | 2.39 | 0.000631 | 0 | 2.75 | 0.000827 | -0.0141 |  | CFL | AllSpc | 2390 | 0.631 | 2390 | 0.631 | 1.15 | 1.31 | -0.0058996 | 2390 | 0.631 | 2390 | 0.631 | 1.15 | 1.31 | -0.0059
CFLAllSpcSDGERCNewCZ10 | Com-Iltg-dWatt-CFL_OSspc | SDG | ERC | New | CZ10 | 2.39 | 0.000631 | 0 | 2.77 | 0.000864 | -0.0161 | 2.39 | 0.000631 | 0 | 2.77 | 0.000864 | -0.0161 |  | CFL | AllSpc | 2390 | 0.631 | 2390 | 0.631 | 1.16 | 1.37 | -0.0067364 | 2390 | 0.631 | 2390 | 0.631 | 1.16 | 1.37 | -0.00674
CFLAllSpcSDGERCNewCZ14 | Com-Iltg-dWatt-CFL_OSspc | SDG | ERC | New | CZ14 | 2.39 | 0.000631 | 0 | 2.73 | 0.000852 | -0.0234 | 2.39 | 0.000631 | 0 | 2.73 | 0.000852 | -0.0234 |  | CFL | AllSpc | 2390 | 0.631 | 2390 | 0.631 | 1.14 | 1.35 | -0.0097908 | 2390 | 0.631 | 2390 | 0.631 | 1.14 | 1.35 | -0.00979
CFLAllSpcSDGERCNewCZ15 | Com-Iltg-dWatt-CFL_OSspc | SDG | ERC | New | CZ15 | 2.39 | 0.000631 | 0 | 3.02 | 0.000866 | -0.00806 | 2.39 | 0.000631 | 0 | 3.02 | 0.000866 | -0.00806 |  | CFL | AllSpc | 2390 | 0.631 | 2390 | 0.631 | 1.26 | 1.37 | -0.0033724 | 2390 | 0.631 | 2390 | 0.631 | 1.26 | 1.37 | -0.00337
CFLAllSpcSDGERCNewIOU | Com-Iltg-dWatt-CFL_OSspc | SDG | ERC | New | IOU | 2.39 | 0.000631 | 0 | 2.7443 | 0.0008211 | -0.014029 | 2.39 | 0.000631 | 0 | 2.7443 | 0.0008211 | -0.014029 |  | CFL | AllSpc | 2390 | 0.631 | 2390 | 0.631 | 1.15 | 1.3 | -0.0058697 | 2390 | 0.631 | 2390 | 0.631 | 1.15 | 1.3 | -0.00587
CFLAllSpcSDGESeExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SDG | ESe | Ex | CZ06 | 2.12 | 0.00062028 | 0 | 2.37 | 0.00078736 | -0.0122 | 2.12 | 0.00062028 | 0 | 2.37 | 0.00078736 | -0.0122 |  | CFL | AllSpc | 2120 | 0.62 | 2120 | 0.62 | 1.12 | 1.27 | -0.0057547 | 2120 | 0.62 | 2120 | 0.62 | 1.12 | 1.27 | -0.00575
CFLAllSpcSDGESeExCZ07 | Com-Iltg-dWatt-CFL_OSspc | SDG | ESe | Ex | CZ07 | 2.12 | 0.00062028 | 0 | 2.36 | 0.00077236 | -0.0108 | 2.12 | 0.00062028 | 0 | 2.36 | 0.00077236 | -0.0108 |  | CFL | AllSpc | 2120 | 0.62 | 2120 | 0.62 | 1.11 | 1.25 | -0.0050943 | 2120 | 0.62 | 2120 | 0.62 | 1.11 | 1.25 | -0.00509
CFLAllSpcSDGESeExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SDG | ESe | Ex | CZ08 | 2.12 | 0.00062028 | 0 | 2.39 | 0.00078332 | -0.0104 | 2.12 | 0.00062028 | 0 | 2.39 | 0.00078332 | -0.0104 |  | CFL | AllSpc | 2120 | 0.62 | 2120 | 0.62 | 1.13 | 1.26 | -0.0049057 | 2120 | 0.62 | 2120 | 0.62 | 1.13 | 1.26 | -0.00491
CFLAllSpcSDGESeExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SDG | ESe | Ex | CZ10 | 2.12 | 0.00062028 | 0 | 2.38 | 0.00078032 | -0.013 | 2.12 | 0.00062028 | 0 | 2.38 | 0.00078032 | -0.013 |  | CFL | AllSpc | 2120 | 0.62 | 2120 | 0.62 | 1.12 | 1.26 | -0.0061321 | 2120 | 0.62 | 2120 | 0.62 | 1.12 | 1.26 | -0.00613
CFLAllSpcSDGESeExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SDG | ESe | Ex | CZ14 | 2.12 | 0.00062029 | 0 | 2.31 | 0.00075332 | -0.0203 | 2.12 | 0.00062029 | 0 | 2.31 | 0.00075332 | -0.0203 |  | CFL | AllSpc | 2120 | 0.62 | 2120 | 0.62 | 1.09 | 1.21 | -0.0095755 | 2120 | 0.62 | 2120 | 0.62 | 1.09 | 1.21 | -0.00958
CFLAllSpcSDGESeExCZ15 | Com-Iltg-dWatt-CFL_OSspc | SDG | ESe | Ex | CZ15 | 2.12 | 0.00062027 | 0 | 2.59 | 0.00077931 | -0.0058 | 2.12 | 0.00062027 | 0 | 2.59 | 0.00077931 | -0.0058 |  | CFL | AllSpc | 2120 | 0.62 | 2120 | 0.62 | 1.22 | 1.26 | -0.0027358 | 2120 | 0.62 | 2120 | 0.62 | 1.22 | 1.26 | -0.00274
CFLAllSpcSDGESeExIOU | Com-Iltg-dWatt-CFL_OSspc | SDG | ESe | Ex | IOU | 2.12 | 0.00062028 | 0 | 2.3688 | 0.00077613 | -0.011635 | 2.12 | 0.00062028 | 0 | 2.3688 | 0.00077613 | -0.011635 |  | CFL | AllSpc | 2120 | 0.62 | 2120 | 0.62 | 1.12 | 1.25 | -0.0054884 | 2120 | 0.62 | 2120 | 0.62 | 1.12 | 1.25 | -0.00549
CFLAllSpcSDGESeNewCZ06 | Com-Iltg-dWatt-CFL_OSspc | SDG | ESe | New | CZ06 | 2.12 | 0.000628 | 0 | 2.33 | 0.000826 | -0.0157 | 2.12 | 0.000628 | 0 | 2.33 | 0.000826 | -0.0157 |  | CFL | AllSpc | 2120 | 0.628 | 2120 | 0.628 | 1.1 | 1.32 | -0.0074057 | 2120 | 0.628 | 2120 | 0.628 | 1.1 | 1.32 | -0.00741
CFLAllSpcSDGESeNewCZ07 | Com-Iltg-dWatt-CFL_OSspc | SDG | ESe | New | CZ07 | 2.12 | 0.000628 | 0 | 2.3 | 0.000807 | -0.0137 | 2.12 | 0.000628 | 0 | 2.3 | 0.000807 | -0.0137 |  | CFL | AllSpc | 2120 | 0.628 | 2120 | 0.628 | 1.08 | 1.29 | -0.0064623 | 2120 | 0.628 | 2120 | 0.628 | 1.08 | 1.29 | -0.00646
CFLAllSpcSDGESeNewCZ08 | Com-Iltg-dWatt-CFL_OSspc | SDG | ESe | New | CZ08 | 2.12 | 0.000628 | 0 | 2.36 | 0.000836 | -0.0129 | 2.12 | 0.000628 | 0 | 2.36 | 0.000836 | -0.0129 |  | CFL | AllSpc | 2120 | 0.628 | 2120 | 0.628 | 1.11 | 1.33 | -0.0060849 | 2120 | 0.628 | 2120 | 0.628 | 1.11 | 1.33 | -0.00608
CFLAllSpcSDGESeNewCZ10 | Com-Iltg-dWatt-CFL_OSspc | SDG | ESe | New | CZ10 | 2.12 | 0.000628 | 0 | 2.38 | 0.000874 | -0.0163 | 2.12 | 0.000628 | 0 | 2.38 | 0.000874 | -0.0163 |  | CFL | AllSpc | 2120 | 0.628 | 2120 | 0.628 | 1.12 | 1.39 | -0.0076887 | 2120 | 0.628 | 2120 | 0.628 | 1.12 | 1.39 | -0.00769
CFLAllSpcSDGESeNewCZ14 | Com-Iltg-dWatt-CFL_OSspc | SDG | ESe | New | CZ14 | 2.12 | 0.000628 | 0 | 2.34 | 0.000859 | -0.0238 | 2.12 | 0.000628 | 0 | 2.34 | 0.000859 | -0.0238 |  | CFL | AllSpc | 2120 | 0.628 | 2120 | 0.628 | 1.1 | 1.37 | -0.011226 | 2120 | 0.628 | 2120 | 0.628 | 1.1 | 1.37 | -0.0112
CFLAllSpcSDGESeNewCZ15 | Com-Iltg-dWatt-CFL_OSspc | SDG | ESe | New | CZ15 | 2.12 | 0.000628 | 0 | 2.62 | 0.000869 | -0.00714 | 2.12 | 0.000628 | 0 | 2.62 | 0.000869 | -0.00714 |  | CFL | AllSpc | 2120 | 0.628 | 2120 | 0.628 | 1.24 | 1.38 | -0.0033679 | 2120 | 0.628 | 2120 | 0.628 | 1.24 | 1.38 | -0.00337
CFLAllSpcSDGESeNewIOU | Com-Iltg-dWatt-CFL_OSspc | SDG | ESe | New | IOU | 2.12 | 0.000628 | 0 | 2.3319 | 0.00083195 | -0.014676 | 2.12 | 0.000628 | 0 | 2.3319 | 0.00083195 | -0.014676 |  | CFL | AllSpc | 2120 | 0.628 | 2120 | 0.628 | 1.1 | 1.32 | -0.0069226 | 2120 | 0.628 | 2120 | 0.628 | 1.1 | 1.32 | -0.00692
CFLAllSpcSDGEUnExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SDG | EUn | Ex | CZ06 | 2.17 | 0.00054994 | 0 | 2.4706 | 0.00069494 | -0.0092006 | 2.17 | 0.00054994 | 0 | 2.4706 | 0.00069494 | -0.0092006 |  | CFL | AllSpc | 2170 | 0.55 | 2170 | 0.55 | 1.14 | 1.26 | -0.0042399 | 2170 | 0.55 | 2170 | 0.55 | 1.14 | 1.26 | -0.00424
CFLAllSpcSDGEUnExCZ07 | Com-Iltg-dWatt-CFL_OSspc | SDG | EUn | Ex | CZ07 | 2.17 | 0.00054994 | 0 | 2.4606 | 0.00068794 | -0.0082006 | 2.17 | 0.00054994 | 0 | 2.4606 | 0.00068794 | -0.0082006 |  | CFL | AllSpc | 2170 | 0.55 | 2170 | 0.55 | 1.13 | 1.25 | -0.0037791 | 2170 | 0.55 | 2170 | 0.55 | 1.13 | 1.25 | -0.00378
CFLAllSpcSDGEUnExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SDG | EUn | Ex | CZ08 | 2.17 | 0.00054994 | 0 | 2.49 | 0.000696 | -0.0088506 | 2.17 | 0.00054994 | 0 | 2.49 | 0.000696 | -0.0088506 |  | CFL | AllSpc | 2170 | 0.55 | 2170 | 0.55 | 1.15 | 1.27 | -0.0040786 | 2170 | 0.55 | 2170 | 0.55 | 1.15 | 1.27 | -0.00408
CFLAllSpcSDGEUnExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SDG | EUn | Ex | CZ10 | 2.17 | 0.00054994 | 0 | 2.49 | 0.00070794 | -0.0104 | 2.17 | 0.00054994 | 0 | 2.49 | 0.00070794 | -0.0104 |  | CFL | AllSpc | 2170 | 0.55 | 2170 | 0.55 | 1.15 | 1.29 | -0.0047926 | 2170 | 0.55 | 2170 | 0.55 | 1.15 | 1.29 | -0.00479
CFLAllSpcSDGEUnExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SDG | EUn | Ex | CZ14 | 2.17 | 0.00054994 | 0 | 2.46 | 0.00069894 | -0.0144 | 2.17 | 0.00054994 | 0 | 2.46 | 0.00069894 | -0.0144 |  | CFL | AllSpc | 2170 | 0.55 | 2170 | 0.55 | 1.13 | 1.27 | -0.0066359 | 2170 | 0.55 | 2170 | 0.55 | 1.13 | 1.27 | -0.00664
CFLAllSpcSDGEUnExIOU | Com-Iltg-dWatt-CFL_OSspc | SDG | EUn | Ex | IOU | 2.17 | 0.00054994 | 0 | 2.4678 | 0.0006928 | -0.0087607 | 2.17 | 0.00054994 | 0 | 2.4678 | 0.0006928 | -0.0087607 |  | CFL | AllSpc | 2170 | 0.55 | 2170 | 0.55 | 1.14 | 1.26 | -0.0040372 | 2170 | 0.55 | 2170 | 0.55 | 1.14 | 1.26 | -0.00404
CFLAllSpcSDGEUnNewCZ06 | Com-Iltg-dWatt-CFL_OSspc | SDG | EUn | New | CZ06 | 2.17 | 0.000549 | 0 | 2.5 | 0.000691 | -0.00705 | 2.17 | 0.000549 | 0 | 2.5 | 0.000691 | -0.00705 |  | CFL | AllSpc | 2170 | 0.549 | 2170 | 0.549 | 1.15 | 1.26 | -0.0032488 | 2170 | 0.549 | 2170 | 0.549 | 1.15 | 1.26 | -0.00325
CFLAllSpcSDGEUnNewCZ07 | Com-Iltg-dWatt-CFL_OSspc | SDG | EUn | New | CZ07 | 2.17 | 0.000549 | 0 | 2.48 | 0.000686 | -0.00629 | 2.17 | 0.000549 | 0 | 2.48 | 0.000686 | -0.00629 |  | CFL | AllSpc | 2170 | 0.549 | 2170 | 0.549 | 1.14 | 1.25 | -0.0028986 | 2170 | 0.549 | 2170 | 0.549 | 1.14 | 1.25 | -0.0029
CFLAllSpcSDGEUnNewCZ08 | Com-Iltg-dWatt-CFL_OSspc | SDG | EUn | New | CZ08 | 2.17 | 0.000549 | 0 | 2.52 | 0.000698 | -0.00623 | 2.17 | 0.000549 | 0 | 2.52 | 0.000698 | -0.00623 |  | CFL | AllSpc | 2170 | 0.549 | 2170 | 0.549 | 1.16 | 1.27 | -0.002871 | 2170 | 0.549 | 2170 | 0.549 | 1.16 | 1.27 | -0.00287
CFLAllSpcSDGEUnNewCZ10 | Com-Iltg-dWatt-CFL_OSspc | SDG | EUn | New | CZ10 | 2.17 | 0.000549 | 0 | 2.54 | 0.00072 | -0.00721 | 2.17 | 0.000549 | 0 | 2.54 | 0.00072 | -0.00721 |  | CFL | AllSpc | 2170 | 0.549 | 2170 | 0.549 | 1.17 | 1.31 | -0.0033226 | 2170 | 0.549 | 2170 | 0.549 | 1.17 | 1.31 | -0.00332
CFLAllSpcSDGEUnNewCZ14 | Com-Iltg-dWatt-CFL_OSspc | SDG | EUn | New | CZ14 | 2.17 | 0.000549 | 0 | 2.44 | 0.000666 | -0.0119 | 2.17 | 0.000549 | 0 | 2.44 | 0.000666 | -0.0119 |  | CFL | AllSpc | 2170 | 0.549 | 2170 | 0.549 | 1.12 | 1.21 | -0.0054839 | 2170 | 0.549 | 2170 | 0.549 | 1.12 | 1.21 | -0.00548
CFLAllSpcSDGEUnNewCZ15 | Com-Iltg-dWatt-CFL_OSspc | SDG | EUn | New | CZ15 | 2.17 | 0.000549 | 0 | 2.66 | 0.000727 | -0.00332 | 2.17 | 0.000549 | 0 | 2.66 | 0.000727 | -0.00332 |  | CFL | AllSpc | 2170 | 0.549 | 2170 | 0.549 | 1.23 | 1.32 | -0.00153 | 2170 | 0.549 | 2170 | 0.549 | 1.23 | 1.32 | -0.00153
CFLAllSpcSDGEUnNewIOU | Com-Iltg-dWatt-CFL_OSspc | SDG | EUn | New | IOU | 2.17 | 0.000549 | 0 | 2.4943 | 0.00069402 | -0.0065388 | 2.17 | 0.000549 | 0 | 2.4943 | 0.00069402 | -0.0065388 |  | CFL | AllSpc | 2170 | 0.549 | 2170 | 0.549 | 1.15 | 1.26 | -0.0030133 | 2170 | 0.549 | 2170 | 0.549 | 1.15 | 1.26 | -0.00301
CFLAllSpcSDGGroExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SDG | Gro | Ex | CZ06 | 3.8 | 0.00047883 | 0 | 3.7986 | 0.00059083 | -0.0521 | 3.8 | 0.00047883 | 0 | 3.7986 | 0.00059083 | -0.0521 |  | CFL | AllSpc | 3800 | 0.479 | 3800 | 0.479 | 1 | 1.23 | -0.013711 | 3800 | 0.479 | 3800 | 0.479 | 1 | 1.23 | -0.0137
CFLAllSpcSDGGroExCZ07 | Com-Iltg-dWatt-CFL_OSspc | SDG | Gro | Ex | CZ07 | 3.8 | 0.00047883 | 0 | 3.74 | 0.00058192 | -0.0559 | 3.8 | 0.00047883 | 0 | 3.74 | 0.00058192 | -0.0559 |  | CFL | AllSpc | 3800 | 0.479 | 3800 | 0.479 | 0.984 | 1.22 | -0.014711 | 3800 | 0.479 | 3800 | 0.479 | 0.984 | 1.22 | -0.0147
CFLAllSpcSDGGroExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SDG | Gro | Ex | CZ08 | 3.8 | 0.00047883 | 0 | 3.88 | 0.00060683 | -0.0475 | 3.8 | 0.00047883 | 0 | 3.88 | 0.00060683 | -0.0475 |  | CFL | AllSpc | 3800 | 0.479 | 3800 | 0.479 | 1.02 | 1.27 | -0.0125 | 3800 | 0.479 | 3800 | 0.479 | 1.02 | 1.27 | -0.0125
CFLAllSpcSDGGroExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SDG | Gro | Ex | CZ10 | 3.8 | 0.00047883 | 0 | 3.95 | 0.00063683 | -0.044886 | 3.8 | 0.00047883 | 0 | 3.95 | 0.00063683 | -0.044886 |  | CFL | AllSpc | 3800 | 0.479 | 3800 | 0.479 | 1.04 | 1.33 | -0.011812 | 3800 | 0.479 | 3800 | 0.479 | 1.04 | 1.33 | -0.0118
CFLAllSpcSDGGroExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SDG | Gro | Ex | CZ14 | 3.8 | 0.00047883 | 0 | 3.9386 | 0.00064683 | -0.045286 | 3.8 | 0.00047883 | 0 | 3.9386 | 0.00064683 | -0.045286 |  | CFL | AllSpc | 3800 | 0.479 | 3800 | 0.479 | 1.04 | 1.35 | -0.011917 | 3800 | 0.479 | 3800 | 0.479 | 1.04 | 1.35 | -0.0119
CFLAllSpcSDGGroExCZ15 | Com-Iltg-dWatt-CFL_OSspc | SDG | Gro | Ex | CZ15 | 3.8 | 0.00047883 | 0 | 4.26 | 0.00063483 | -0.026091 | 3.8 | 0.00047883 | 0 | 4.26 | 0.00063483 | -0.026091 |  | CFL | AllSpc | 3800 | 0.479 | 3800 | 0.479 | 1.12 | 1.33 | -0.0068662 | 3800 | 0.479 | 3800 | 0.479 | 1.12 | 1.33 | -0.00687
CFLAllSpcSDGGroExIOU | Com-Iltg-dWatt-CFL_OSspc | SDG | Gro | Ex | IOU | 3.8 | 0.00047883 | 0 | 3.8051 | 0.00059823 | -0.052412 | 3.8 | 0.00047883 | 0 | 3.8051 | 0.00059823 | -0.052412 |  | CFL | AllSpc | 3800 | 0.479 | 3800 | 0.479 | 1 | 1.25 | -0.013793 | 3800 | 0.479 | 3800 | 0.479 | 1 | 1.25 | -0.0138
CFLAllSpcSDGGroNewCZ06 | Com-Iltg-dWatt-CFL_OSspc | SDG | Gro | New | CZ06 | 3.8 | 0.000477 | 0 | 3.97 | 0.000602 | -0.0433 | 3.8 | 0.000477 | 0 | 3.97 | 0.000602 | -0.0433 |  | CFL | AllSpc | 3800 | 0.477 | 3800 | 0.477 | 1.04 | 1.26 | -0.011395 | 3800 | 0.477 | 3800 | 0.477 | 1.04 | 1.26 | -0.0114
CFLAllSpcSDGGroNewCZ07 | Com-Iltg-dWatt-CFL_OSspc | SDG | Gro | New | CZ07 | 3.8 | 0.000477 | 0 | 3.93 | 0.000587 | -0.0452 | 3.8 | 0.000477 | 0 | 3.93 | 0.000587 | -0.0452 |  | CFL | AllSpc | 3800 | 0.477 | 3800 | 0.477 | 1.03 | 1.23 | -0.011895 | 3800 | 0.477 | 3800 | 0.477 | 1.03 | 1.23 | -0.0119
CFLAllSpcSDGGroNewCZ08 | Com-Iltg-dWatt-CFL_OSspc | SDG | Gro | New | CZ08 | 3.8 | 0.000477 | 0 | 4.02 | 0.000613 | -0.0378 | 3.8 | 0.000477 | 0 | 4.02 | 0.000613 | -0.0378 |  | CFL | AllSpc | 3800 | 0.477 | 3800 | 0.477 | 1.06 | 1.29 | -0.0099474 | 3800 | 0.477 | 3800 | 0.477 | 1.06 | 1.29 | -0.00995
CFLAllSpcSDGGroNewCZ10 | Com-Iltg-dWatt-CFL_OSspc | SDG | Gro | New | CZ10 | 3.8 | 0.000477 | 0 | 4.07 | 0.000673 | -0.0395 | 3.8 | 0.000477 | 0 | 4.07 | 0.000673 | -0.0395 |  | CFL | AllSpc | 3800 | 0.477 | 3800 | 0.477 | 1.07 | 1.41 | -0.010395 | 3800 | 0.477 | 3800 | 0.477 | 1.07 | 1.41 | -0.0104
CFLAllSpcSDGGroNewCZ14 | Com-Iltg-dWatt-CFL_OSspc | SDG | Gro | New | CZ14 | 3.8 | 0.000477 | 0 | 4.07 | 0.000656 | -0.0433 | 3.8 | 0.000477 | 0 | 4.07 | 0.000656 | -0.0433 |  | CFL | AllSpc | 3800 | 0.477 | 3800 | 0.477 | 1.07 | 1.38 | -0.011395 | 3800 | 0.477 | 3800 | 0.477 | 1.07 | 1.38 | -0.0114
CFLAllSpcSDGGroNewCZ15 | Com-Iltg-dWatt-CFL_OSspc | SDG | Gro | New | CZ15 | 3.8 | 0.000477 | 0 | 4.39 | 0.000667 | -0.0224 | 3.8 | 0.000477 | 0 | 4.39 | 0.000667 | -0.0224 |  | CFL | AllSpc | 3800 | 0.477 | 3800 | 0.477 | 1.16 | 1.4 | -0.0058947 | 3800 | 0.477 | 3800 | 0.477 | 1.16 | 1.4 | -0.00589
CFLAllSpcSDGGroNewIOU | Com-Iltg-dWatt-CFL_OSspc | SDG | Gro | New | IOU | 3.8 | 0.000477 | 0 | 3.9735 | 0.00061217 | -0.043329 | 3.8 | 0.000477 | 0 | 3.9735 | 0.00061217 | -0.043329 |  | CFL | AllSpc | 3800 | 0.477 | 3800 | 0.477 | 1.05 | 1.28 | -0.011402 | 3800 | 0.477 | 3800 | 0.477 | 1.05 | 1.28 | -0.0114
CFLAllSpcSDGHspExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SDG | Hsp | Ex | CZ06 | 3.92 | 0.00065638 | 0 | 4.48 | 0.00081236 | -0.021097 | 3.92 | 0.00065638 | 0 | 4.48 | 0.00081236 | -0.021097 |  | CFL | AllSpc | 3920 | 0.656 | 3920 | 0.656 | 1.14 | 1.24 | -0.005382 | 3920 | 0.656 | 3920 | 0.656 | 1.14 | 1.24 | -0.00538
CFLAllSpcSDGHspExCZ07 | Com-Iltg-dWatt-CFL_OSspc | SDG | Hsp | Ex | CZ07 | 3.92 | 0.00065638 | 0 | 4.48 | 0.00080497 | -0.0194 | 3.92 | 0.00065638 | 0 | 4.48 | 0.00080497 | -0.0194 |  | CFL | AllSpc | 3920 | 0.656 | 3920 | 0.656 | 1.14 | 1.23 | -0.004949 | 3920 | 0.656 | 3920 | 0.656 | 1.14 | 1.23 | -0.00495
CFLAllSpcSDGHspExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SDG | Hsp | Ex | CZ08 | 3.92 | 0.00065638 | 0 | 4.51 | 0.00081097 | -0.0207 | 3.92 | 0.00065638 | 0 | 4.51 | 0.00081097 | -0.0207 |  | CFL | AllSpc | 3920 | 0.656 | 3920 | 0.656 | 1.15 | 1.24 | -0.0052806 | 3920 | 0.656 | 3920 | 0.656 | 1.15 | 1.24 | -0.00528
CFLAllSpcSDGHspExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SDG | Hsp | Ex | CZ10 | 3.92 | 0.00065638 | 0 | 4.5 | 0.00083035 | -0.022159 | 3.92 | 0.00065638 | 0 | 4.5 | 0.00083035 | -0.022159 |  | CFL | AllSpc | 3920 | 0.656 | 3920 | 0.656 | 1.15 | 1.27 | -0.0056529 | 3920 | 0.656 | 3920 | 0.656 | 1.15 | 1.27 | -0.00565
CFLAllSpcSDGHspExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SDG | Hsp | Ex | CZ14 | 3.92 | 0.00065638 | 0 | 4.44 | 0.00082535 | -0.0271 | 3.92 | 0.00065638 | 0 | 4.44 | 0.00082535 | -0.0271 |  | CFL | AllSpc | 3920 | 0.656 | 3920 | 0.656 | 1.13 | 1.26 | -0.0069133 | 3920 | 0.656 | 3920 | 0.656 | 1.13 | 1.26 | -0.00691
CFLAllSpcSDGHspExIOU | Com-Iltg-dWatt-CFL_OSspc | SDG | Hsp | Ex | IOU | 3.92 | 0.00065638 | 0 | 4.4841 | 0.000809 | -0.019891 | 3.92 | 0.00065638 | 0 | 4.4841 | 0.000809 | -0.019891 |  | CFL | AllSpc | 3920 | 0.656 | 3920 | 0.656 | 1.14 | 1.23 | -0.0050743 | 3920 | 0.656 | 3920 | 0.656 | 1.14 | 1.23 | -0.00507
CFLAllSpcSDGHspNewCZ06 | Com-Iltg-dWatt-CFL_OSspc | SDG | Hsp | New | CZ06 | 3.92 | 0.000656 | 0 | 4.29 | 0.000783 | -0.0224 | 3.92 | 0.000656 | 0 | 4.29 | 0.000783 | -0.0224 |  | CFL | AllSpc | 3920 | 0.656 | 3920 | 0.656 | 1.09 | 1.19 | -0.0057143 | 3920 | 0.656 | 3920 | 0.656 | 1.09 | 1.19 | -0.00571
CFLAllSpcSDGHspNewCZ07 | Com-Iltg-dWatt-CFL_OSspc | SDG | Hsp | New | CZ07 | 3.92 | 0.000656 | 0 | 4.3 | 0.000779 | -0.0192 | 3.92 | 0.000656 | 0 | 4.3 | 0.000779 | -0.0192 |  | CFL | AllSpc | 3920 | 0.656 | 3920 | 0.656 | 1.1 | 1.19 | -0.004898 | 3920 | 0.656 | 3920 | 0.656 | 1.1 | 1.19 | -0.0049
CFLAllSpcSDGHspNewCZ08 | Com-Iltg-dWatt-CFL_OSspc | SDG | Hsp | New | CZ08 | 3.92 | 0.000656 | 0 | 4.33 | 0.000787 | -0.0207 | 3.92 | 0.000656 | 0 | 4.33 | 0.000787 | -0.0207 |  | CFL | AllSpc | 3920 | 0.656 | 3920 | 0.656 | 1.1 | 1.2 | -0.0052806 | 3920 | 0.656 | 3920 | 0.656 | 1.1 | 1.2 | -0.00528
CFLAllSpcSDGHspNewCZ10 | Com-Iltg-dWatt-CFL_OSspc | SDG | Hsp | New | CZ10 | 3.92 | 0.000656 | 0 | 4.33 | 0.000812 | -0.0233 | 3.92 | 0.000656 | 0 | 4.33 | 0.000812 | -0.0233 |  | CFL | AllSpc | 3920 | 0.656 | 3920 | 0.656 | 1.1 | 1.24 | -0.0059439 | 3920 | 0.656 | 3920 | 0.656 | 1.1 | 1.24 | -0.00594
CFLAllSpcSDGHspNewCZ14 | Com-Iltg-dWatt-CFL_OSspc | SDG | Hsp | New | CZ14 | 3.92 | 0.000656 | 0 | 4.27 | 0.000806 | -0.029 | 3.92 | 0.000656 | 0 | 4.27 | 0.000806 | -0.029 |  | CFL | AllSpc | 3920 | 0.656 | 3920 | 0.656 | 1.09 | 1.23 | -0.007398 | 3920 | 0.656 | 3920 | 0.656 | 1.09 | 1.23 | -0.0074
CFLAllSpcSDGHspNewCZ15 | Com-Iltg-dWatt-CFL_OSspc | SDG | Hsp | New | CZ15 | 3.92 | 0.000656 | 0 | 4.53 | 0.000818 | -0.0188 | 3.92 | 0.000656 | 0 | 4.53 | 0.000818 | -0.0188 |  | CFL | AllSpc | 3920 | 0.656 | 3920 | 0.656 | 1.16 | 1.25 | -0.0047959 | 3920 | 0.656 | 3920 | 0.656 | 1.16 | 1.25 | -0.0048
CFLAllSpcSDGHspNewIOU | Com-Iltg-dWatt-CFL_OSspc | SDG | Hsp | New | IOU | 3.92 | 0.000656 | 0 | 4.3053 | 0.00078411 | -0.019927 | 3.92 | 0.000656 | 0 | 4.3053 | 0.00078411 | -0.019927 |  | CFL | AllSpc | 3920 | 0.656 | 3920 | 0.656 | 1.1 | 1.2 | -0.0050835 | 3920 | 0.656 | 3920 | 0.656 | 1.1 | 1.2 | -0.00508
CFLAllSpcSDGHtlExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SDG | Htl | Ex | CZ06 | 1.471 | 0.000171 | 0 | 1.601 | 0.000214 | -0.002991 | 1.471 | 0.000171 | 0 | 1.601 | 0.000214 | -0.002991 |  | CFL | AllSpc | 1470 | 0.171 | 1470 | 0.171 | 1.09 | 1.25 | -0.0020333 | 1470 | 0.171 | 1470 | 0.171 | 1.09 | 1.25 | -0.00203
CFLAllSpcSDGHtlExCZ07 | Com-Iltg-dWatt-CFL_OSspc | SDG | Htl | Ex | CZ07 | 1.471 | 0.000171 | 0 | 1.631 | 0.000212 | -0.002331 | 1.471 | 0.000171 | 0 | 1.631 | 0.000212 | -0.002331 |  | CFL | AllSpc | 1470 | 0.171 | 1470 | 0.171 | 1.11 | 1.24 | -0.0015846 | 1470 | 0.171 | 1470 | 0.171 | 1.11 | 1.24 | -0.00158
CFLAllSpcSDGHtlExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SDG | Htl | Ex | CZ08 | 1.471 | 0.000171 | 0 | 1.621 | 0.000215 | -0.002691 | 1.471 | 0.000171 | 0 | 1.621 | 0.000215 | -0.002691 |  | CFL | AllSpc | 1470 | 0.171 | 1470 | 0.171 | 1.1 | 1.26 | -0.0018294 | 1470 | 0.171 | 1470 | 0.171 | 1.1 | 1.26 | -0.00183
CFLAllSpcSDGHtlExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SDG | Htl | Ex | CZ10 | 1.471 | 0.000171 | 0 | 1.6 | 0.000219 | -0.003121 | 1.471 | 0.000171 | 0 | 1.6 | 0.000219 | -0.003121 |  | CFL | AllSpc | 1470 | 0.171 | 1470 | 0.171 | 1.09 | 1.28 | -0.0021217 | 1470 | 0.171 | 1470 | 0.171 | 1.09 | 1.28 | -0.00212
CFLAllSpcSDGHtlExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SDG | Htl | Ex | CZ14 | 1.471 | 0.000171 | 0 | 1.531 | 0.0002181 | -0.0042521 | 1.471 | 0.000171 | 0 | 1.531 | 0.0002181 | -0.0042521 |  | CFL | AllSpc | 1470 | 0.171 | 1470 | 0.171 | 1.04 | 1.28 | -0.0028905 | 1470 | 0.171 | 1470 | 0.171 | 1.04 | 1.28 | -0.00289
CFLAllSpcSDGHtlExCZ15 | Com-Iltg-dWatt-CFL_OSspc | SDG | Htl | Ex | CZ15 | 1.471 | 0.000171 | 0 | 1.711 | 0.0002201 | -0.0018 | 1.471 | 0.000171 | 0 | 1.711 | 0.0002201 | -0.0018 |  | CFL | AllSpc | 1470 | 0.171 | 1470 | 0.171 | 1.16 | 1.29 | -0.0012236 | 1470 | 0.171 | 1470 | 0.171 | 1.16 | 1.29 | -0.00122
CFLAllSpcSDGHtlExIOU | Com-Iltg-dWatt-CFL_OSspc | SDG | Htl | Ex | IOU | 1.471 | 0.000171 | 0 | 1.6266 | 0.00021292 | -0.0024506 | 1.471 | 0.000171 | 0 | 1.6266 | 0.00021292 | -0.0024506 |  | CFL | AllSpc | 1470 | 0.171 | 1470 | 0.171 | 1.11 | 1.25 | -0.0016659 | 1470 | 0.171 | 1470 | 0.171 | 1.11 | 1.25 | -0.00167
CFLAllSpcSDGHtlNewCZ06 | Com-Iltg-dWatt-CFL_OSspc | SDG | Htl | New | CZ06 | 1.48 | 0.000171 | 0 | 1.6 | 0.000218 | -0.00279 | 1.48 | 0.000171 | 0 | 1.6 | 0.000218 | -0.00279 |  | CFL | AllSpc | 1480 | 0.171 | 1480 | 0.171 | 1.08 | 1.27 | -0.0018851 | 1480 | 0.171 | 1480 | 0.171 | 1.08 | 1.27 | -0.00189
CFLAllSpcSDGHtlNewCZ07 | Com-Iltg-dWatt-CFL_OSspc | SDG | Htl | New | CZ07 | 1.48 | 0.000171 | 0 | 1.63 | 0.000215 | -0.00201 | 1.48 | 0.000171 | 0 | 1.63 | 0.000215 | -0.00201 |  | CFL | AllSpc | 1480 | 0.171 | 1480 | 0.171 | 1.1 | 1.26 | -0.0013581 | 1480 | 0.171 | 1480 | 0.171 | 1.1 | 1.26 | -0.00136
CFLAllSpcSDGHtlNewCZ08 | Com-Iltg-dWatt-CFL_OSspc | SDG | Htl | New | CZ08 | 1.48 | 0.000171 | 0 | 1.62 | 0.00022 | -0.00246 | 1.48 | 0.000171 | 0 | 1.62 | 0.00022 | -0.00246 |  | CFL | AllSpc | 1480 | 0.171 | 1480 | 0.171 | 1.09 | 1.29 | -0.0016622 | 1480 | 0.171 | 1480 | 0.171 | 1.09 | 1.29 | -0.00166
CFLAllSpcSDGHtlNewCZ10 | Com-Iltg-dWatt-CFL_OSspc | SDG | Htl | New | CZ10 | 1.48 | 0.000171 | 0 | 1.6 | 0.000231 | -0.00308 | 1.48 | 0.000171 | 0 | 1.6 | 0.000231 | -0.00308 |  | CFL | AllSpc | 1480 | 0.171 | 1480 | 0.171 | 1.08 | 1.35 | -0.0020811 | 1480 | 0.171 | 1480 | 0.171 | 1.08 | 1.35 | -0.00208
CFLAllSpcSDGHtlNewCZ14 | Com-Iltg-dWatt-CFL_OSspc | SDG | Htl | New | CZ14 | 1.48 | 0.000171 | 0 | 1.52 | 0.000226 | -0.00462 | 1.48 | 0.000171 | 0 | 1.52 | 0.000226 | -0.00462 |  | CFL | AllSpc | 1480 | 0.171 | 1480 | 0.171 | 1.03 | 1.32 | -0.0031216 | 1480 | 0.171 | 1480 | 0.171 | 1.03 | 1.32 | -0.00312
CFLAllSpcSDGHtlNewCZ15 | Com-Iltg-dWatt-CFL_OSspc | SDG | Htl | New | CZ15 | 1.48 | 0.000171 | 0 | 1.73 | 0.000229 | -0.00155 | 1.48 | 0.000171 | 0 | 1.73 | 0.000229 | -0.00155 |  | CFL | AllSpc | 1480 | 0.171 | 1480 | 0.171 | 1.17 | 1.34 | -0.0010473 | 1480 | 0.171 | 1480 | 0.171 | 1.17 | 1.34 | -0.00105
CFLAllSpcSDGHtlNewIOU | Com-Iltg-dWatt-CFL_OSspc | SDG | Htl | New | IOU | 1.48 | 0.000171 | 0 | 1.6258 | 0.00021694 | -0.0021694 | 1.48 | 0.000171 | 0 | 1.6258 | 0.00021694 | -0.0021694 |  | CFL | AllSpc | 1480 | 0.171 | 1480 | 0.171 | 1.1 | 1.27 | -0.0014658 | 1480 | 0.171 | 1480 | 0.171 | 1.1 | 1.27 | -0.00147
CFLAllSpcSDGMBTExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SDG | MBT | Ex | CZ06 | 2.78 | 0.000667 | 0 | 3.22 | 0.0008013 | -0.00051403 | 2.78 | 0.000667 | 0 | 3.22 | 0.0008013 | -0.00051403 |  | CFL | AllSpc | 2780 | 0.667 | 2780 | 0.667 | 1.16 | 1.2 | -0.0001849 | 2780 | 0.667 | 2780 | 0.667 | 1.16 | 1.2 | -0.000185
CFLAllSpcSDGMBTExCZ07 | Com-Iltg-dWatt-CFL_OSspc | SDG | MBT | Ex | CZ07 | 2.78 | 0.000667 | 0 | 3.23 | 0.00079209 | -0.00013909 | 2.78 | 0.000667 | 0 | 3.23 | 0.00079209 | -0.00013909 |  | CFL | AllSpc | 2780 | 0.667 | 2780 | 0.667 | 1.16 | 1.19 | -5.0033e-05 | 2780 | 0.667 | 2780 | 0.667 | 1.16 | 1.19 | -5e-05
CFLAllSpcSDGMBTExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SDG | MBT | Ex | CZ08 | 2.78 | 0.000667 | 0 | 3.2215 | 0.000837 | -0.00033315 | 2.78 | 0.000667 | 0 | 3.2215 | 0.000837 | -0.00033315 |  | CFL | AllSpc | 2780 | 0.667 | 2780 | 0.667 | 1.16 | 1.25 | -0.00011984 | 2780 | 0.667 | 2780 | 0.667 | 1.16 | 1.25 | -0.00012
CFLAllSpcSDGMBTExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SDG | MBT | Ex | CZ10 | 2.78 | 0.000667 | 0 | 3.2109 | 0.00085409 | -0.00090015 | 2.78 | 0.000667 | 0 | 3.2109 | 0.00085409 | -0.00090015 |  | CFL | AllSpc | 2780 | 0.667 | 2780 | 0.667 | 1.16 | 1.28 | -0.0003238 | 2780 | 0.667 | 2780 | 0.667 | 1.16 | 1.28 | -0.000324
CFLAllSpcSDGMBTExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SDG | MBT | Ex | CZ14 | 2.78 | 0.000667 | 0 | 3.1615 | 0.00084715 | -0.00215 | 2.78 | 0.000667 | 0 | 3.1615 | 0.00084715 | -0.00215 |  | CFL | AllSpc | 2780 | 0.667 | 2780 | 0.667 | 1.14 | 1.27 | -0.00077338 | 2780 | 0.667 | 2780 | 0.667 | 1.14 | 1.27 | -0.000773
CFLAllSpcSDGMBTExCZ15 | Com-Iltg-dWatt-CFL_OSspc | SDG | MBT | Ex | CZ15 | 2.78 | 0.000667 | 0 | 3.3409 | 0.00085609 | 0 | 2.78 | 0.000667 | 0 | 3.3409 | 0.00085609 | 0 |  | CFL | AllSpc | 2780 | 0.667 | 2780 | 0.667 | 1.2 | 1.28 | 0 | 2780 | 0.667 | 2780 | 0.667 | 1.2 | 1.28 | 0
CFLAllSpcSDGMBTExIOU | Com-Iltg-dWatt-CFL_OSspc | SDG | MBT | Ex | IOU | 2.78 | 0.000667 | 0 | 3.2234 | 0.00081282 | -0.00040478 | 2.78 | 0.000667 | 0 | 3.2234 | 0.00081282 | -0.00040478 |  | CFL | AllSpc | 2780 | 0.667 | 2780 | 0.667 | 1.16 | 1.22 | -0.0001456 | 2780 | 0.667 | 2780 | 0.667 | 1.16 | 1.22 | -0.000146
CFLAllSpcSDGMBTNewCZ06 | Com-Iltg-dWatt-CFL_OSspc | SDG | MBT | New | CZ06 | 2.78 | 0.000667 | 0 | 3.12 | 0.000835 | -0.000943 | 2.78 | 0.000667 | 0 | 3.12 | 0.000835 | -0.000943 |  | CFL | AllSpc | 2780 | 0.667 | 2780 | 0.667 | 1.12 | 1.25 | -0.00033921 | 2780 | 0.667 | 2780 | 0.667 | 1.12 | 1.25 | -0.000339
CFLAllSpcSDGMBTNewCZ07 | Com-Iltg-dWatt-CFL_OSspc | SDG | MBT | New | CZ07 | 2.78 | 0.000667 | 0 | 3.11 | 0.000827 | 0 | 2.78 | 0.000667 | 0 | 3.11 | 0.000827 | 0 |  | CFL | AllSpc | 2780 | 0.667 | 2780 | 0.667 | 1.12 | 1.24 | 0 | 2780 | 0.667 | 2780 | 0.667 | 1.12 | 1.24 | 0
CFLAllSpcSDGMBTNewCZ08 | Com-Iltg-dWatt-CFL_OSspc | SDG | MBT | New | CZ08 | 2.78 | 0.000667 | 0 | 3.13 | 0.000856 | -0.000754 | 2.78 | 0.000667 | 0 | 3.13 | 0.000856 | -0.000754 |  | CFL | AllSpc | 2780 | 0.667 | 2780 | 0.667 | 1.13 | 1.28 | -0.00027122 | 2780 | 0.667 | 2780 | 0.667 | 1.13 | 1.28 | -0.000271
CFLAllSpcSDGMBTNewCZ10 | Com-Iltg-dWatt-CFL_OSspc | SDG | MBT | New | CZ10 | 2.78 | 0.000667 | 0 | 3.15 | 0.000891 | -0.000935 | 2.78 | 0.000667 | 0 | 3.15 | 0.000891 | -0.000935 |  | CFL | AllSpc | 2780 | 0.667 | 2780 | 0.667 | 1.13 | 1.34 | -0.00033633 | 2780 | 0.667 | 2780 | 0.667 | 1.13 | 1.34 | -0.000336
CFLAllSpcSDGMBTNewCZ14 | Com-Iltg-dWatt-CFL_OSspc | SDG | MBT | New | CZ14 | 2.78 | 0.000667 | 0 | 3.11 | 0.000879 | -0.00182 | 2.78 | 0.000667 | 0 | 3.11 | 0.000879 | -0.00182 |  | CFL | AllSpc | 2780 | 0.667 | 2780 | 0.667 | 1.12 | 1.32 | -0.00065468 | 2780 | 0.667 | 2780 | 0.667 | 1.12 | 1.32 | -0.000655
CFLAllSpcSDGMBTNewCZ15 | Com-Iltg-dWatt-CFL_OSspc | SDG | MBT | New | CZ15 | 2.78 | 0.000667 | 0 | 3.31 | 0.000891 | 0 | 2.78 | 0.000667 | 0 | 3.31 | 0.000891 | 0 |  | CFL | AllSpc | 2780 | 0.667 | 2780 | 0.667 | 1.19 | 1.34 | 0 | 2780 | 0.667 | 2780 | 0.667 | 1.19 | 1.34 | 0
CFLAllSpcSDGMBTNewIOU | Com-Iltg-dWatt-CFL_OSspc | SDG | MBT | New | IOU | 2.78 | 0.000667 | 0 | 3.1235 | 0.00084795 | -0.00034685 | 2.78 | 0.000667 | 0 | 3.1235 | 0.00084795 | -0.00034685 |  | CFL | AllSpc | 2780 | 0.667 | 2780 | 0.667 | 1.12 | 1.27 | -0.00012476 | 2780 | 0.667 | 2780 | 0.667 | 1.12 | 1.27 | -0.000125
CFLAllSpcSDGMLIExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SDG | MLI | Ex | CZ06 | 2.29 | 0.00066 | 0 | 2.48 | 0.000783 | -0.0049209 | 2.29 | 0.00066 | 0 | 2.48 | 0.000783 | -0.0049209 |  | CFL | AllSpc | 2290 | 0.66 | 2290 | 0.66 | 1.08 | 1.19 | -0.0021489 | 2290 | 0.66 | 2290 | 0.66 | 1.08 | 1.19 | -0.00215
CFLAllSpcSDGMLIExCZ07 | Com-Iltg-dWatt-CFL_OSspc | SDG | MLI | Ex | CZ07 | 2.29 | 0.00066 | 0 | 2.48 | 0.000781 | -0.00254 | 2.29 | 0.00066 | 0 | 2.48 | 0.000781 | -0.00254 |  | CFL | AllSpc | 2290 | 0.66 | 2290 | 0.66 | 1.08 | 1.18 | -0.0011092 | 2290 | 0.66 | 2290 | 0.66 | 1.08 | 1.18 | -0.00111
CFLAllSpcSDGMLIExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SDG | MLI | Ex | CZ08 | 2.29 | 0.00066 | 0 | 2.5006 | 0.000782 | -0.0040506 | 2.29 | 0.00066 | 0 | 2.5006 | 0.000782 | -0.0040506 |  | CFL | AllSpc | 2290 | 0.66 | 2290 | 0.66 | 1.09 | 1.18 | -0.0017688 | 2290 | 0.66 | 2290 | 0.66 | 1.09 | 1.18 | -0.00177
CFLAllSpcSDGMLIExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SDG | MLI | Ex | CZ10 | 2.29 | 0.00066 | 0 | 2.5 | 0.00080194 | -0.0055206 | 2.29 | 0.00066 | 0 | 2.5 | 0.00080194 | -0.0055206 |  | CFL | AllSpc | 2290 | 0.66 | 2290 | 0.66 | 1.09 | 1.22 | -0.0024108 | 2290 | 0.66 | 2290 | 0.66 | 1.09 | 1.22 | -0.00241
CFLAllSpcSDGMLIExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SDG | MLI | Ex | CZ14 | 2.29 | 0.00066 | 0 | 2.43 | 0.00079235 | -0.0153 | 2.29 | 0.00066 | 0 | 2.43 | 0.00079235 | -0.0153 |  | CFL | AllSpc | 2290 | 0.66 | 2290 | 0.66 | 1.06 | 1.2 | -0.0066812 | 2290 | 0.66 | 2290 | 0.66 | 1.06 | 1.2 | -0.00668
CFLAllSpcSDGMLIExCZ15 | Com-Iltg-dWatt-CFL_OSspc | SDG | MLI | Ex | CZ15 | 2.29 | 0.00066 | 0 | 2.6806 | 0.000791 | -0.00144 | 2.29 | 0.00066 | 0 | 2.6806 | 0.000791 | -0.00144 |  | CFL | AllSpc | 2290 | 0.66 | 2290 | 0.66 | 1.17 | 1.2 | -0.00062882 | 2290 | 0.66 | 2290 | 0.66 | 1.17 | 1.2 | -0.000629
CFLAllSpcSDGMLIExIOU | Com-Iltg-dWatt-CFL_OSspc | SDG | MLI | Ex | IOU | 2.29 | 0.00066 | 0 | 2.4866 | 0.00078758 | -0.00367 | 2.29 | 0.00066 | 0 | 2.4866 | 0.00078758 | -0.00367 |  | CFL | AllSpc | 2290 | 0.66 | 2290 | 0.66 | 1.09 | 1.19 | -0.0016026 | 2290 | 0.66 | 2290 | 0.66 | 1.09 | 1.19 | -0.0016
CFLAllSpcSDGMLINewCZ06 | Com-Iltg-dWatt-CFL_OSspc | SDG | MLI | New | CZ06 | 2.29 | 0.00066 | 0 | 2.41 | 0.000775 | -0.00889 | 2.29 | 0.00066 | 0 | 2.41 | 0.000775 | -0.00889 |  | CFL | AllSpc | 2290 | 0.66 | 2290 | 0.66 | 1.05 | 1.17 | -0.0038821 | 2290 | 0.66 | 2290 | 0.66 | 1.05 | 1.17 | -0.00388
CFLAllSpcSDGMLINewCZ07 | Com-Iltg-dWatt-CFL_OSspc | SDG | MLI | New | CZ07 | 2.29 | 0.00066 | 0 | 2.4 | 0.000772 | -0.00518 | 2.29 | 0.00066 | 0 | 2.4 | 0.000772 | -0.00518 |  | CFL | AllSpc | 2290 | 0.66 | 2290 | 0.66 | 1.05 | 1.17 | -0.002262 | 2290 | 0.66 | 2290 | 0.66 | 1.05 | 1.17 | -0.00226
CFLAllSpcSDGMLINewCZ08 | Com-Iltg-dWatt-CFL_OSspc | SDG | MLI | New | CZ08 | 2.29 | 0.00066 | 0 | 2.45 | 0.000779 | -0.00715 | 2.29 | 0.00066 | 0 | 2.45 | 0.000779 | -0.00715 |  | CFL | AllSpc | 2290 | 0.66 | 2290 | 0.66 | 1.07 | 1.18 | -0.0031223 | 2290 | 0.66 | 2290 | 0.66 | 1.07 | 1.18 | -0.00312
CFLAllSpcSDGMLINewCZ10 | Com-Iltg-dWatt-CFL_OSspc | SDG | MLI | New | CZ10 | 2.29 | 0.00066 | 0 | 2.53 | 0.000869 | -0.00899 | 2.29 | 0.00066 | 0 | 2.53 | 0.000869 | -0.00899 |  | CFL | AllSpc | 2290 | 0.66 | 2290 | 0.66 | 1.1 | 1.32 | -0.0039258 | 2290 | 0.66 | 2290 | 0.66 | 1.1 | 1.32 | -0.00393
CFLAllSpcSDGMLINewCZ14 | Com-Iltg-dWatt-CFL_OSspc | SDG | MLI | New | CZ14 | 2.29 | 0.00066 | 0 | 2.43 | 0.000811 | -0.0177 | 2.29 | 0.00066 | 0 | 2.43 | 0.000811 | -0.0177 |  | CFL | AllSpc | 2290 | 0.66 | 2290 | 0.66 | 1.06 | 1.23 | -0.0077293 | 2290 | 0.66 | 2290 | 0.66 | 1.06 | 1.23 | -0.00773
CFLAllSpcSDGMLINewCZ15 | Com-Iltg-dWatt-CFL_OSspc | SDG | MLI | New | CZ15 | 2.29 | 0.00066 | 0 | 2.71 | 0.000884 | -0.0015 | 2.29 | 0.00066 | 0 | 2.71 | 0.000884 | -0.0015 |  | CFL | AllSpc | 2290 | 0.66 | 2290 | 0.66 | 1.18 | 1.34 | -0.00065502 | 2290 | 0.66 | 2290 | 0.66 | 1.18 | 1.34 | -0.000655
CFLAllSpcSDGMLINewIOU | Com-Iltg-dWatt-CFL_OSspc | SDG | MLI | New | IOU | 2.29 | 0.00066 | 0 | 2.442 | 0.00080239 | -0.0066041 | 2.29 | 0.00066 | 0 | 2.442 | 0.00080239 | -0.0066041 |  | CFL | AllSpc | 2290 | 0.66 | 2290 | 0.66 | 1.07 | 1.22 | -0.0028839 | 2290 | 0.66 | 2290 | 0.66 | 1.07 | 1.22 | -0.00288
CFLAllSpcSDGMtlExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SDG | Mtl | Ex | CZ06 | 1.22 | 0.000131 | 0 | 1.38 | 0.000164 | -0.00325 | 1.22 | 0.000131 | 0 | 1.38 | 0.000164 | -0.00325 |  | CFL | AllSpc | 1220 | 0.131 | 1220 | 0.131 | 1.13 | 1.25 | -0.0026639 | 1220 | 0.131 | 1220 | 0.131 | 1.13 | 1.25 | -0.00266
CFLAllSpcSDGMtlExCZ07 | Com-Iltg-dWatt-CFL_OSspc | SDG | Mtl | Ex | CZ07 | 1.22 | 0.000131 | 0 | 1.41 | 0.000163 | -0.00231 | 1.22 | 0.000131 | 0 | 1.41 | 0.000163 | -0.00231 |  | CFL | AllSpc | 1220 | 0.131 | 1220 | 0.131 | 1.16 | 1.24 | -0.0018934 | 1220 | 0.131 | 1220 | 0.131 | 1.16 | 1.24 | -0.00189
CFLAllSpcSDGMtlExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SDG | Mtl | Ex | CZ08 | 1.22 | 0.000131 | 0 | 1.4 | 0.000166 | -0.00271 | 1.22 | 0.000131 | 0 | 1.4 | 0.000166 | -0.00271 |  | CFL | AllSpc | 1220 | 0.131 | 1220 | 0.131 | 1.15 | 1.27 | -0.0022213 | 1220 | 0.131 | 1220 | 0.131 | 1.15 | 1.27 | -0.00222
CFLAllSpcSDGMtlExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SDG | Mtl | Ex | CZ10 | 1.22 | 0.000131 | 0 | 1.39 | 0.000171 | -0.00323 | 1.22 | 0.000131 | 0 | 1.39 | 0.000171 | -0.00323 |  | CFL | AllSpc | 1220 | 0.131 | 1220 | 0.131 | 1.14 | 1.31 | -0.0026475 | 1220 | 0.131 | 1220 | 0.131 | 1.14 | 1.31 | -0.00265
CFLAllSpcSDGMtlExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SDG | Mtl | Ex | CZ14 | 1.22 | 0.000131 | 0 | 1.34 | 0.00017013 | -0.00455 | 1.22 | 0.000131 | 0 | 1.34 | 0.00017013 | -0.00455 |  | CFL | AllSpc | 1220 | 0.131 | 1220 | 0.131 | 1.1 | 1.3 | -0.0037295 | 1220 | 0.131 | 1220 | 0.131 | 1.1 | 1.3 | -0.00373
CFLAllSpcSDGMtlExCZ15 | Com-Iltg-dWatt-CFL_OSspc | SDG | Mtl | Ex | CZ15 | 1.22 | 0.000131 | 0 | 1.47 | 0.00017312 | -0.00132 | 1.22 | 0.000131 | 0 | 1.47 | 0.00017312 | -0.00132 |  | CFL | AllSpc | 1220 | 0.131 | 1220 | 0.131 | 1.2 | 1.32 | -0.001082 | 1220 | 0.131 | 1220 | 0.131 | 1.2 | 1.32 | -0.00108
CFLAllSpcSDGMtlExIOU | Com-Iltg-dWatt-CFL_OSspc | SDG | Mtl | Ex | IOU | 1.22 | 0.000131 | 0 | 1.4067 | 0.000164 | -0.0024532 | 1.22 | 0.000131 | 0 | 1.4067 | 0.000164 | -0.0024532 |  | CFL | AllSpc | 1220 | 0.131 | 1220 | 0.131 | 1.15 | 1.25 | -0.0020108 | 1220 | 0.131 | 1220 | 0.131 | 1.15 | 1.25 | -0.00201
CFLAllSpcSDGMtlNewCZ06 | Com-Iltg-dWatt-CFL_OSspc | SDG | Mtl | New | CZ06 | 1.22 | 0.000131 | 0 | 1.37 | 0.000168 | -0.00427 | 1.22 | 0.000131 | 0 | 1.37 | 0.000168 | -0.00427 |  | CFL | AllSpc | 1220 | 0.131 | 1220 | 0.131 | 1.12 | 1.28 | -0.0035 | 1220 | 0.131 | 1220 | 0.131 | 1.12 | 1.28 | -0.0035
CFLAllSpcSDGMtlNewCZ07 | Com-Iltg-dWatt-CFL_OSspc | SDG | Mtl | New | CZ07 | 1.22 | 0.000131 | 0 | 1.4 | 0.000166 | -0.00294 | 1.22 | 0.000131 | 0 | 1.4 | 0.000166 | -0.00294 |  | CFL | AllSpc | 1220 | 0.131 | 1220 | 0.131 | 1.15 | 1.27 | -0.0024098 | 1220 | 0.131 | 1220 | 0.131 | 1.15 | 1.27 | -0.00241
CFLAllSpcSDGMtlNewCZ08 | Com-Iltg-dWatt-CFL_OSspc | SDG | Mtl | New | CZ08 | 1.22 | 0.000131 | 0 | 1.39 | 0.00017 | -0.00356 | 1.22 | 0.000131 | 0 | 1.39 | 0.00017 | -0.00356 |  | CFL | AllSpc | 1220 | 0.131 | 1220 | 0.131 | 1.14 | 1.3 | -0.002918 | 1220 | 0.131 | 1220 | 0.131 | 1.14 | 1.3 | -0.00292
CFLAllSpcSDGMtlNewCZ10 | Com-Iltg-dWatt-CFL_OSspc | SDG | Mtl | New | CZ10 | 1.22 | 0.000131 | 0 | 1.37 | 0.000175 | -0.00447 | 1.22 | 0.000131 | 0 | 1.37 | 0.000175 | -0.00447 |  | CFL | AllSpc | 1220 | 0.131 | 1220 | 0.131 | 1.12 | 1.34 | -0.0036639 | 1220 | 0.131 | 1220 | 0.131 | 1.12 | 1.34 | -0.00366
CFLAllSpcSDGMtlNewCZ14 | Com-Iltg-dWatt-CFL_OSspc | SDG | Mtl | New | CZ14 | 1.22 | 0.000131 | 0 | 1.32 | 0.000175 | -0.00598 | 1.22 | 0.000131 | 0 | 1.32 | 0.000175 | -0.00598 |  | CFL | AllSpc | 1220 | 0.131 | 1220 | 0.131 | 1.08 | 1.34 | -0.0049016 | 1220 | 0.131 | 1220 | 0.131 | 1.08 | 1.34 | -0.0049
CFLAllSpcSDGMtlNewCZ15 | Com-Iltg-dWatt-CFL_OSspc | SDG | Mtl | New | CZ15 | 1.22 | 0.000131 | 0 | 1.47 | 0.000179 | -0.00205 | 1.22 | 0.000131 | 0 | 1.47 | 0.000179 | -0.00205 |  | CFL | AllSpc | 1220 | 0.131 | 1220 | 0.131 | 1.2 | 1.37 | -0.0016803 | 1220 | 0.131 | 1220 | 0.131 | 1.2 | 1.37 | -0.00168
CFLAllSpcSDGMtlNewIOU | Com-Iltg-dWatt-CFL_OSspc | SDG | Mtl | New | IOU | 1.22 | 0.000131 | 0 | 1.3957 | 0.00016719 | -0.003169 | 1.22 | 0.000131 | 0 | 1.3957 | 0.00016719 | -0.003169 |  | CFL | AllSpc | 1220 | 0.131 | 1220 | 0.131 | 1.14 | 1.28 | -0.0025975 | 1220 | 0.131 | 1220 | 0.131 | 1.14 | 1.28 | -0.0026
CFLAllSpcSDGNrsExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SDG | Nrs | Ex | CZ06 | 3.18 | 0.00048403 | 0 | 3.43 | 0.00062464 | -0.0301 | 3.18 | 0.00048403 | 0 | 3.43 | 0.00062464 | -0.0301 |  | CFL | AllSpc | 3180 | 0.484 | 3180 | 0.484 | 1.08 | 1.29 | -0.0094654 | 3180 | 0.484 | 3180 | 0.484 | 1.08 | 1.29 | -0.00947
CFLAllSpcSDGNrsExCZ07 | Com-Iltg-dWatt-CFL_OSspc | SDG | Nrs | Ex | CZ07 | 3.18 | 0.00048404 | 0 | 3.42 | 0.00061408 | -0.0267 | 3.18 | 0.00048404 | 0 | 3.42 | 0.00061408 | -0.0267 |  | CFL | AllSpc | 3180 | 0.484 | 3180 | 0.484 | 1.08 | 1.27 | -0.0083962 | 3180 | 0.484 | 3180 | 0.484 | 1.08 | 1.27 | -0.0084
CFLAllSpcSDGNrsExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SDG | Nrs | Ex | CZ08 | 3.18 | 0.00048401 | 0 | 3.4641 | 0.00062703 | -0.029041 | 3.18 | 0.00048401 | 0 | 3.4641 | 0.00062703 | -0.029041 |  | CFL | AllSpc | 3180 | 0.484 | 3180 | 0.484 | 1.09 | 1.3 | -0.0091324 | 3180 | 0.484 | 3180 | 0.484 | 1.09 | 1.3 | -0.00913
CFLAllSpcSDGNrsExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SDG | Nrs | Ex | CZ10 | 3.18 | 0.00048401 | 0 | 3.4741 | 0.00064762 | -0.031 | 3.18 | 0.00048401 | 0 | 3.4741 | 0.00064762 | -0.031 |  | CFL | AllSpc | 3180 | 0.484 | 3180 | 0.484 | 1.09 | 1.34 | -0.0097484 | 3180 | 0.484 | 3180 | 0.484 | 1.09 | 1.34 | -0.00975
CFLAllSpcSDGNrsExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SDG | Nrs | Ex | CZ14 | 3.18 | 0.00048402 | 0 | 3.44 | 0.00064004 | -0.036242 | 3.18 | 0.00048402 | 0 | 3.44 | 0.00064004 | -0.036242 |  | CFL | AllSpc | 3180 | 0.484 | 3180 | 0.484 | 1.08 | 1.32 | -0.011397 | 3180 | 0.484 | 3180 | 0.484 | 1.08 | 1.32 | -0.0114
CFLAllSpcSDGNrsExIOU | Com-Iltg-dWatt-CFL_OSspc | SDG | Nrs | Ex | IOU | 3.18 | 0.00048404 | 0 | 3.4298 | 0.00061964 | -0.027497 | 3.18 | 0.00048404 | 0 | 3.4298 | 0.00061964 | -0.027497 |  | CFL | AllSpc | 3180 | 0.484 | 3180 | 0.484 | 1.08 | 1.28 | -0.0086468 | 3180 | 0.484 | 3180 | 0.484 | 1.08 | 1.28 | -0.00865
CFLAllSpcSDGNrsNewCZ06 | Com-Iltg-dWatt-CFL_OSspc | SDG | Nrs | New | CZ06 | 3.18 | 0.000485 | 0 | 3.31 | 0.000617 | -0.0321 | 3.18 | 0.000485 | 0 | 3.31 | 0.000617 | -0.0321 |  | CFL | AllSpc | 3180 | 0.485 | 3180 | 0.485 | 1.04 | 1.27 | -0.010094 | 3180 | 0.485 | 3180 | 0.485 | 1.04 | 1.27 | -0.0101
CFLAllSpcSDGNrsNewCZ07 | Com-Iltg-dWatt-CFL_OSspc | SDG | Nrs | New | CZ07 | 3.18 | 0.000485 | 0 | 3.29 | 0.000617 | -0.03 | 3.18 | 0.000485 | 0 | 3.29 | 0.000617 | -0.03 |  | CFL | AllSpc | 3180 | 0.485 | 3180 | 0.485 | 1.03 | 1.27 | -0.009434 | 3180 | 0.485 | 3180 | 0.485 | 1.03 | 1.27 | -0.00943
CFLAllSpcSDGNrsNewCZ08 | Com-Iltg-dWatt-CFL_OSspc | SDG | Nrs | New | CZ08 | 3.18 | 0.000485 | 0 | 3.37 | 0.000619 | -0.0307 | 3.18 | 0.000485 | 0 | 3.37 | 0.000619 | -0.0307 |  | CFL | AllSpc | 3180 | 0.485 | 3180 | 0.485 | 1.06 | 1.28 | -0.0096541 | 3180 | 0.485 | 3180 | 0.485 | 1.06 | 1.28 | -0.00965
CFLAllSpcSDGNrsNewCZ10 | Com-Iltg-dWatt-CFL_OSspc | SDG | Nrs | New | CZ10 | 3.18 | 0.000485 | 0 | 3.4 | 0.000644 | -0.0315 | 3.18 | 0.000485 | 0 | 3.4 | 0.000644 | -0.0315 |  | CFL | AllSpc | 3180 | 0.485 | 3180 | 0.485 | 1.07 | 1.33 | -0.0099057 | 3180 | 0.485 | 3180 | 0.485 | 1.07 | 1.33 | -0.00991
CFLAllSpcSDGNrsNewCZ14 | Com-Iltg-dWatt-CFL_OSspc | SDG | Nrs | New | CZ14 | 3.18 | 0.000485 | 0 | 3.37 | 0.000626 | -0.0388 | 3.18 | 0.000485 | 0 | 3.37 | 0.000626 | -0.0388 |  | CFL | AllSpc | 3180 | 0.485 | 3180 | 0.485 | 1.06 | 1.29 | -0.012201 | 3180 | 0.485 | 3180 | 0.485 | 1.06 | 1.29 | -0.0122
CFLAllSpcSDGNrsNewCZ15 | Com-Iltg-dWatt-CFL_OSspc | SDG | Nrs | New | CZ15 | 3.18 | 0.000485 | 0 | 3.65 | 0.000643 | -0.0151 | 3.18 | 0.000485 | 0 | 3.65 | 0.000643 | -0.0151 |  | CFL | AllSpc | 3180 | 0.485 | 3180 | 0.485 | 1.15 | 1.33 | -0.0047484 | 3180 | 0.485 | 3180 | 0.485 | 1.15 | 1.33 | -0.00475
CFLAllSpcSDGNrsNewIOU | Com-Iltg-dWatt-CFL_OSspc | SDG | Nrs | New | IOU | 3.18 | 0.000485 | 0 | 3.3096 | 0.00062089 | -0.030299 | 3.18 | 0.000485 | 0 | 3.3096 | 0.00062089 | -0.030299 |  | CFL | AllSpc | 3180 | 0.485 | 3180 | 0.485 | 1.04 | 1.28 | -0.0095281 | 3180 | 0.485 | 3180 | 0.485 | 1.04 | 1.28 | -0.00953
CFLAllSpcSDGOfLExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SDG | OfL | Ex | CZ06 | 2.5895 | 0.00050695 | 0 | 2.97 | 0.00064695 | -0.0062018 | 2.5895 | 0.00050695 | 0 | 2.97 | 0.00064695 | -0.0062018 |  | CFL | AllSpc | 2590 | 0.507 | 2590 | 0.507 | 1.15 | 1.28 | -0.002395 | 2590 | 0.507 | 2590 | 0.507 | 1.15 | 1.28 | -0.0024
CFLAllSpcSDGOfLExCZ07 | Com-Iltg-dWatt-CFL_OSspc | SDG | OfL | Ex | CZ07 | 2.5895 | 0.00050695 | 0 | 2.96 | 0.00063795 | -0.0053295 | 2.5895 | 0.00050695 | 0 | 2.96 | 0.00063795 | -0.0053295 |  | CFL | AllSpc | 2590 | 0.507 | 2590 | 0.507 | 1.14 | 1.26 | -0.0020581 | 2590 | 0.507 | 2590 | 0.507 | 1.14 | 1.26 | -0.00206
CFLAllSpcSDGOfLExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SDG | OfL | Ex | CZ08 | 2.5895 | 0.00050695 | 0 | 2.98 | 0.00065995 | -0.0060215 | 2.5895 | 0.00050695 | 0 | 2.98 | 0.00065995 | -0.0060215 |  | CFL | AllSpc | 2590 | 0.507 | 2590 | 0.507 | 1.15 | 1.3 | -0.0023254 | 2590 | 0.507 | 2590 | 0.507 | 1.15 | 1.3 | -0.00233
CFLAllSpcSDGOfLExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SDG | OfL | Ex | CZ10 | 2.5895 | 0.00050695 | 0 | 2.9715 | 0.000665 | -0.0068815 | 2.5895 | 0.00050695 | 0 | 2.9715 | 0.000665 | -0.0068815 |  | CFL | AllSpc | 2590 | 0.507 | 2590 | 0.507 | 1.15 | 1.31 | -0.0026575 | 2590 | 0.507 | 2590 | 0.507 | 1.15 | 1.31 | -0.00266
CFLAllSpcSDGOfLExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SDG | OfL | Ex | CZ14 | 2.5895 | 0.00050695 | 0 | 2.93 | 0.00065495 | -0.0094931 | 2.5895 | 0.00050695 | 0 | 2.93 | 0.00065495 | -0.0094931 |  | CFL | AllSpc | 2590 | 0.507 | 2590 | 0.507 | 1.13 | 1.29 | -0.003666 | 2590 | 0.507 | 2590 | 0.507 | 1.13 | 1.29 | -0.00367
CFLAllSpcSDGOfLExCZ15 | Com-Iltg-dWatt-CFL_OSspc | SDG | OfL | Ex | CZ15 | 2.5895 | 0.00050695 | 0 | 3.1515 | 0.00066795 | -0.0039815 | 2.5895 | 0.00050695 | 0 | 3.1515 | 0.00066795 | -0.0039815 |  | CFL | AllSpc | 2590 | 0.507 | 2590 | 0.507 | 1.22 | 1.32 | -0.0015376 | 2590 | 0.507 | 2590 | 0.507 | 1.22 | 1.32 | -0.00154
CFLAllSpcSDGOfLExIOU | Com-Iltg-dWatt-CFL_OSspc | SDG | OfL | Ex | IOU | 2.5895 | 0.00050695 | 0 | 2.9627 | 0.00064339 | -0.0056473 | 2.5895 | 0.00050695 | 0 | 2.9627 | 0.00064339 | -0.0056473 |  | CFL | AllSpc | 2590 | 0.507 | 2590 | 0.507 | 1.14 | 1.27 | -0.0021809 | 2590 | 0.507 | 2590 | 0.507 | 1.14 | 1.27 | -0.00218
CFLAllSpcSDGOfLNewCZ06 | Com-Iltg-dWatt-CFL_OSspc | SDG | OfL | New | CZ06 | 2.58 | 0.000506 | 0 | 2.96 | 0.000631 | -0.00421 | 2.58 | 0.000506 | 0 | 2.96 | 0.000631 | -0.00421 |  | CFL | AllSpc | 2580 | 0.506 | 2580 | 0.506 | 1.15 | 1.25 | -0.0016318 | 2580 | 0.506 | 2580 | 0.506 | 1.15 | 1.25 | -0.00163
CFLAllSpcSDGOfLNewCZ07 | Com-Iltg-dWatt-CFL_OSspc | SDG | OfL | New | CZ07 | 2.58 | 0.000506 | 0 | 2.96 | 0.000623 | -0.00341 | 2.58 | 0.000506 | 0 | 2.96 | 0.000623 | -0.00341 |  | CFL | AllSpc | 2580 | 0.506 | 2580 | 0.506 | 1.15 | 1.23 | -0.0013217 | 2580 | 0.506 | 2580 | 0.506 | 1.15 | 1.23 | -0.00132
CFLAllSpcSDGOfLNewCZ08 | Com-Iltg-dWatt-CFL_OSspc | SDG | OfL | New | CZ08 | 2.58 | 0.000506 | 0 | 2.97 | 0.000639 | -0.00348 | 2.58 | 0.000506 | 0 | 2.97 | 0.000639 | -0.00348 |  | CFL | AllSpc | 2580 | 0.506 | 2580 | 0.506 | 1.15 | 1.26 | -0.0013488 | 2580 | 0.506 | 2580 | 0.506 | 1.15 | 1.26 | -0.00135
CFLAllSpcSDGOfLNewCZ10 | Com-Iltg-dWatt-CFL_OSspc | SDG | OfL | New | CZ10 | 2.58 | 0.000506 | 0 | 2.98 | 0.000658 | -0.00428 | 2.58 | 0.000506 | 0 | 2.98 | 0.000658 | -0.00428 |  | CFL | AllSpc | 2580 | 0.506 | 2580 | 0.506 | 1.16 | 1.3 | -0.0016589 | 2580 | 0.506 | 2580 | 0.506 | 1.16 | 1.3 | -0.00166
CFLAllSpcSDGOfLNewCZ14 | Com-Iltg-dWatt-CFL_OSspc | SDG | OfL | New | CZ14 | 2.58 | 0.000506 | 0 | 2.93 | 0.00067 | -0.00673 | 2.58 | 0.000506 | 0 | 2.93 | 0.00067 | -0.00673 |  | CFL | AllSpc | 2580 | 0.506 | 2580 | 0.506 | 1.14 | 1.32 | -0.0026085 | 2580 | 0.506 | 2580 | 0.506 | 1.14 | 1.32 | -0.00261
CFLAllSpcSDGOfLNewCZ15 | Com-Iltg-dWatt-CFL_OSspc | SDG | OfL | New | CZ15 | 2.58 | 0.000506 | 0 | 3.09 | 0.000655 | -0.00202 | 2.58 | 0.000506 | 0 | 3.09 | 0.000655 | -0.00202 |  | CFL | AllSpc | 2580 | 0.506 | 2580 | 0.506 | 1.2 | 1.29 | -0.00078295 | 2580 | 0.506 | 2580 | 0.506 | 1.2 | 1.29 | -0.000783
CFLAllSpcSDGOfLNewIOU | Com-Iltg-dWatt-CFL_OSspc | SDG | OfL | New | IOU | 2.58 | 0.000506 | 0 | 2.9637 | 0.00062981 | -0.0035918 | 2.58 | 0.000506 | 0 | 2.9637 | 0.00062981 | -0.0035918 |  | CFL | AllSpc | 2580 | 0.506 | 2580 | 0.506 | 1.15 | 1.24 | -0.0013922 | 2580 | 0.506 | 2580 | 0.506 | 1.15 | 1.24 | -0.00139
CFLAllSpcSDGOfSExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SDG | OfS | Ex | CZ06 | 2.4402 | 0.00050203 | 0 | 2.7942 | 0.00063303 | -0.00197 | 2.4402 | 0.00050203 | 0 | 2.7942 | 0.00063303 | -0.00197 |  | CFL | AllSpc | 2440 | 0.502 | 2440 | 0.502 | 1.15 | 1.26 | -0.00080732 | 2440 | 0.502 | 2440 | 0.502 | 1.15 | 1.26 | -0.000807
CFLAllSpcSDGOfSExCZ07 | Com-Iltg-dWatt-CFL_OSspc | SDG | OfS | Ex | CZ07 | 2.4405 | 0.00050209 | 0 | 2.81 | 0.00062605 | -0.00053505 | 2.4405 | 0.00050209 | 0 | 2.81 | 0.00062605 | -0.00053505 |  | CFL | AllSpc | 2440 | 0.502 | 2440 | 0.502 | 1.15 | 1.25 | -0.00021924 | 2440 | 0.502 | 2440 | 0.502 | 1.15 | 1.25 | -0.000219
CFLAllSpcSDGOfSExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SDG | OfS | Ex | CZ08 | 2.4405 | 0.00050209 | 0 | 2.8197 | 0.00063609 | -0.0016697 | 2.4405 | 0.00050209 | 0 | 2.8197 | 0.00063609 | -0.0016697 |  | CFL | AllSpc | 2440 | 0.502 | 2440 | 0.502 | 1.16 | 1.27 | -0.00068417 | 2440 | 0.502 | 2440 | 0.502 | 1.16 | 1.27 | -0.000684
CFLAllSpcSDGOfSExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SDG | OfS | Ex | CZ10 | 2.4405 | 0.00050209 | 0 | 2.8097 | 0.00063909 | -0.0025405 | 2.4405 | 0.00050209 | 0 | 2.8097 | 0.00063909 | -0.0025405 |  | CFL | AllSpc | 2440 | 0.502 | 2440 | 0.502 | 1.15 | 1.27 | -0.001041 | 2440 | 0.502 | 2440 | 0.502 | 1.15 | 1.27 | -0.00104
CFLAllSpcSDGOfSExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SDG | OfS | Ex | CZ14 | 2.4405 | 0.00050209 | 0 | 2.7305 | 0.0006461 | -0.0061802 | 2.4405 | 0.00050209 | 0 | 2.7305 | 0.0006461 | -0.0061802 |  | CFL | AllSpc | 2440 | 0.502 | 2440 | 0.502 | 1.12 | 1.29 | -0.0025324 | 2440 | 0.502 | 2440 | 0.502 | 1.12 | 1.29 | -0.00253
CFLAllSpcSDGOfSExCZ15 | Com-Iltg-dWatt-CFL_OSspc | SDG | OfS | Ex | CZ15 | 2.4405 | 0.00050209 | 0 | 2.9997 | 0.00063309 | -0.00053502 | 2.4405 | 0.00050209 | 0 | 2.9997 | 0.00063309 | -0.00053502 |  | CFL | AllSpc | 2440 | 0.502 | 2440 | 0.502 | 1.23 | 1.26 | -0.00021923 | 2440 | 0.502 | 2440 | 0.502 | 1.23 | 1.26 | -0.000219
CFLAllSpcSDGOfSExIOU | Com-Iltg-dWatt-CFL_OSspc | SDG | OfS | Ex | IOU | 2.4405 | 0.00050209 | 0 | 2.8097 | 0.00062876 | -0.00096073 | 2.4405 | 0.00050209 | 0 | 2.8097 | 0.00062876 | -0.00096073 |  | CFL | AllSpc | 2440 | 0.502 | 2440 | 0.502 | 1.15 | 1.25 | -0.00039367 | 2440 | 0.502 | 2440 | 0.502 | 1.15 | 1.25 | -0.000394
CFLAllSpcSDGOfSNewCZ06 | Com-Iltg-dWatt-CFL_OSspc | SDG | OfS | New | CZ06 | 2.45 | 0.000504 | 0 | 2.68 | 0.000624 | -0.00217 | 2.45 | 0.000504 | 0 | 2.68 | 0.000624 | -0.00217 |  | CFL | AllSpc | 2450 | 0.504 | 2450 | 0.504 | 1.09 | 1.24 | -0.00088571 | 2450 | 0.504 | 2450 | 0.504 | 1.09 | 1.24 | -0.000886
CFLAllSpcSDGOfSNewCZ07 | Com-Iltg-dWatt-CFL_OSspc | SDG | OfS | New | CZ07 | 2.45 | 0.000504 | 0 | 2.68 | 0.000616 | -0.000507 | 2.45 | 0.000504 | 0 | 2.68 | 0.000616 | -0.000507 |  | CFL | AllSpc | 2450 | 0.504 | 2450 | 0.504 | 1.09 | 1.22 | -0.00020694 | 2450 | 0.504 | 2450 | 0.504 | 1.09 | 1.22 | -0.000207
CFLAllSpcSDGOfSNewCZ08 | Com-Iltg-dWatt-CFL_OSspc | SDG | OfS | New | CZ08 | 2.45 | 0.000504 | 0 | 2.7 | 0.000631 | -0.00183 | 2.45 | 0.000504 | 0 | 2.7 | 0.000631 | -0.00183 |  | CFL | AllSpc | 2450 | 0.504 | 2450 | 0.504 | 1.1 | 1.25 | -0.00074694 | 2450 | 0.504 | 2450 | 0.504 | 1.1 | 1.25 | -0.000747
CFLAllSpcSDGOfSNewCZ10 | Com-Iltg-dWatt-CFL_OSspc | SDG | OfS | New | CZ10 | 2.45 | 0.000504 | 0 | 2.73 | 0.000653 | -0.00145 | 2.45 | 0.000504 | 0 | 2.73 | 0.000653 | -0.00145 |  | CFL | AllSpc | 2450 | 0.504 | 2450 | 0.504 | 1.11 | 1.3 | -0.00059184 | 2450 | 0.504 | 2450 | 0.504 | 1.11 | 1.3 | -0.000592
CFLAllSpcSDGOfSNewCZ14 | Com-Iltg-dWatt-CFL_OSspc | SDG | OfS | New | CZ14 | 2.45 | 0.000504 | 0 | 2.66 | 0.000654 | -0.00553 | 2.45 | 0.000504 | 0 | 2.66 | 0.000654 | -0.00553 |  | CFL | AllSpc | 2450 | 0.504 | 2450 | 0.504 | 1.09 | 1.3 | -0.0022571 | 2450 | 0.504 | 2450 | 0.504 | 1.09 | 1.3 | -0.00226
CFLAllSpcSDGOfSNewCZ15 | Com-Iltg-dWatt-CFL_OSspc | SDG | OfS | New | CZ15 | 2.45 | 0.000504 | 0 | 2.85 | 0.000661 | 0 | 2.45 | 0.000504 | 0 | 2.85 | 0.000661 | 0 |  | CFL | AllSpc | 2450 | 0.504 | 2450 | 0.504 | 1.16 | 1.31 | 0 | 2450 | 0.504 | 2450 | 0.504 | 1.16 | 1.31 | 0
CFLAllSpcSDGOfSNewIOU | Com-Iltg-dWatt-CFL_OSspc | SDG | OfS | New | IOU | 2.45 | 0.000504 | 0 | 2.6892 | 0.00062311 | -0.00075409 | 2.45 | 0.000504 | 0 | 2.6892 | 0.00062311 | -0.00075409 |  | CFL | AllSpc | 2450 | 0.504 | 2450 | 0.504 | 1.1 | 1.24 | -0.00030779 | 2450 | 0.504 | 2450 | 0.504 | 1.1 | 1.24 | -0.000308
CFLAllSpcSDGRFFExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SDG | RFF | Ex | CZ06 | 4.31 | 0.000687 | 0 | 4.79 | 0.000839 | -0.0231 | 4.31 | 0.000687 | 0 | 4.79 | 0.000839 | -0.0231 |  | CFL | AllSpc | 4310 | 0.687 | 4310 | 0.687 | 1.11 | 1.22 | -0.0053596 | 4310 | 0.687 | 4310 | 0.687 | 1.11 | 1.22 | -0.00536
CFLAllSpcSDGRFFExCZ07 | Com-Iltg-dWatt-CFL_OSspc | SDG | RFF | Ex | CZ07 | 4.31 | 0.000687 | 0 | 4.79 | 0.000832 | -0.0207 | 4.31 | 0.000687 | 0 | 4.79 | 0.000832 | -0.0207 |  | CFL | AllSpc | 4310 | 0.687 | 4310 | 0.687 | 1.11 | 1.21 | -0.0048028 | 4310 | 0.687 | 4310 | 0.687 | 1.11 | 1.21 | -0.0048
CFLAllSpcSDGRFFExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SDG | RFF | Ex | CZ08 | 4.31 | 0.000687 | 0 | 4.82 | 0.000832 | -0.0203 | 4.31 | 0.000687 | 0 | 4.82 | 0.000832 | -0.0203 |  | CFL | AllSpc | 4310 | 0.687 | 4310 | 0.687 | 1.12 | 1.21 | -0.00471 | 4310 | 0.687 | 4310 | 0.687 | 1.12 | 1.21 | -0.00471
CFLAllSpcSDGRFFExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SDG | RFF | Ex | CZ10 | 4.31 | 0.000687 | 0 | 4.83 | 0.00084522 | -0.0225 | 4.31 | 0.000687 | 0 | 4.83 | 0.00084522 | -0.0225 |  | CFL | AllSpc | 4310 | 0.687 | 4310 | 0.687 | 1.12 | 1.23 | -0.0052204 | 4310 | 0.687 | 4310 | 0.687 | 1.12 | 1.23 | -0.00522
CFLAllSpcSDGRFFExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SDG | RFF | Ex | CZ14 | 4.31 | 0.000687 | 0 | 4.75 | 0.000861 | -0.0318 | 4.31 | 0.000687 | 0 | 4.75 | 0.000861 | -0.0318 |  | CFL | AllSpc | 4310 | 0.687 | 4310 | 0.687 | 1.1 | 1.25 | -0.0073782 | 4310 | 0.687 | 4310 | 0.687 | 1.1 | 1.25 | -0.00738
CFLAllSpcSDGRFFExCZ15 | Com-Iltg-dWatt-CFL_OSspc | SDG | RFF | Ex | CZ15 | 4.31 | 0.000687 | 0 | 5.12 | 0.00085423 | -0.0105 | 4.31 | 0.000687 | 0 | 5.12 | 0.00085423 | -0.0105 |  | CFL | AllSpc | 4310 | 0.687 | 4310 | 0.687 | 1.19 | 1.24 | -0.0024362 | 4310 | 0.687 | 4310 | 0.687 | 1.19 | 1.24 | -0.00244
CFLAllSpcSDGRFFExIOU | Com-Iltg-dWatt-CFL_OSspc | SDG | RFF | Ex | IOU | 4.31 | 0.000687 | 0 | 4.8 | 0.00083531 | -0.021206 | 4.31 | 0.000687 | 0 | 4.8 | 0.00083531 | -0.021206 |  | CFL | AllSpc | 4310 | 0.687 | 4310 | 0.687 | 1.11 | 1.22 | -0.0049201 | 4310 | 0.687 | 4310 | 0.687 | 1.11 | 1.22 | -0.00492
CFLAllSpcSDGRFFNewCZ06 | Com-Iltg-dWatt-CFL_OSspc | SDG | RFF | New | CZ06 | 4.31 | 0.000687 | 0 | 4.62 | 0.000853 | -0.0242 | 4.31 | 0.000687 | 0 | 4.62 | 0.000853 | -0.0242 |  | CFL | AllSpc | 4310 | 0.687 | 4310 | 0.687 | 1.07 | 1.24 | -0.0056148 | 4310 | 0.687 | 4310 | 0.687 | 1.07 | 1.24 | -0.00561
CFLAllSpcSDGRFFNewCZ07 | Com-Iltg-dWatt-CFL_OSspc | SDG | RFF | New | CZ07 | 4.31 | 0.000687 | 0 | 4.59 | 0.000844 | -0.0256 | 4.31 | 0.000687 | 0 | 4.59 | 0.000844 | -0.0256 |  | CFL | AllSpc | 4310 | 0.687 | 4310 | 0.687 | 1.06 | 1.23 | -0.0059397 | 4310 | 0.687 | 4310 | 0.687 | 1.06 | 1.23 | -0.00594
CFLAllSpcSDGRFFNewCZ08 | Com-Iltg-dWatt-CFL_OSspc | SDG | RFF | New | CZ08 | 4.31 | 0.000687 | 0 | 4.63 | 0.000826 | -0.0237 | 4.31 | 0.000687 | 0 | 4.63 | 0.000826 | -0.0237 |  | CFL | AllSpc | 4310 | 0.687 | 4310 | 0.687 | 1.07 | 1.2 | -0.0054988 | 4310 | 0.687 | 4310 | 0.687 | 1.07 | 1.2 | -0.0055
CFLAllSpcSDGRFFNewCZ10 | Com-Iltg-dWatt-CFL_OSspc | SDG | RFF | New | CZ10 | 4.31 | 0.000687 | 0 | 4.74 | 0.000891 | -0.0276 | 4.31 | 0.000687 | 0 | 4.74 | 0.000891 | -0.0276 |  | CFL | AllSpc | 4310 | 0.687 | 4310 | 0.687 | 1.1 | 1.3 | -0.0064037 | 4310 | 0.687 | 4310 | 0.687 | 1.1 | 1.3 | -0.0064
CFLAllSpcSDGRFFNewCZ14 | Com-Iltg-dWatt-CFL_OSspc | SDG | RFF | New | CZ14 | 4.31 | 0.000687 | 0 | 4.72 | 0.000896 | -0.0384 | 4.31 | 0.000687 | 0 | 4.72 | 0.000896 | -0.0384 |  | CFL | AllSpc | 4310 | 0.687 | 4310 | 0.687 | 1.1 | 1.3 | -0.0089095 | 4310 | 0.687 | 4310 | 0.687 | 1.1 | 1.3 | -0.00891
CFLAllSpcSDGRFFNewCZ15 | Com-Iltg-dWatt-CFL_OSspc | SDG | RFF | New | CZ15 | 4.31 | 0.000687 | 0 | 5.08 | 0.000907 | -0.0137 | 4.31 | 0.000687 | 0 | 5.08 | 0.000907 | -0.0137 |  | CFL | AllSpc | 4310 | 0.687 | 4310 | 0.687 | 1.18 | 1.32 | -0.0031787 | 4310 | 0.687 | 4310 | 0.687 | 1.18 | 1.32 | -0.00318
CFLAllSpcSDGRFFNewIOU | Com-Iltg-dWatt-CFL_OSspc | SDG | RFF | New | IOU | 4.31 | 0.000687 | 0 | 4.6263 | 0.00085434 | -0.025931 | 4.31 | 0.000687 | 0 | 4.6263 | 0.00085434 | -0.025931 |  | CFL | AllSpc | 4310 | 0.687 | 4310 | 0.687 | 1.07 | 1.24 | -0.0060164 | 4310 | 0.687 | 4310 | 0.687 | 1.07 | 1.24 | -0.00602
CFLAllSpcSDGRSDExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SDG | RSD | Ex | CZ06 | 4.33 | 0.000677 | 0 | 4.89 | 0.000841 | -0.0207 | 4.33 | 0.000677 | 0 | 4.89 | 0.000841 | -0.0207 |  | CFL | AllSpc | 4330 | 0.677 | 4330 | 0.677 | 1.13 | 1.24 | -0.0047806 | 4330 | 0.677 | 4330 | 0.677 | 1.13 | 1.24 | -0.00478
CFLAllSpcSDGRSDExCZ07 | Com-Iltg-dWatt-CFL_OSspc | SDG | RSD | Ex | CZ07 | 4.33 | 0.000677 | 0 | 4.9 | 0.000845 | -0.0181 | 4.33 | 0.000677 | 0 | 4.9 | 0.000845 | -0.0181 |  | CFL | AllSpc | 4330 | 0.677 | 4330 | 0.677 | 1.13 | 1.25 | -0.0041801 | 4330 | 0.677 | 4330 | 0.677 | 1.13 | 1.25 | -0.00418
CFLAllSpcSDGRSDExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SDG | RSD | Ex | CZ08 | 4.33 | 0.000677 | 0 | 4.93 | 0.000821 | -0.0176 | 4.33 | 0.000677 | 0 | 4.93 | 0.000821 | -0.0176 |  | CFL | AllSpc | 4330 | 0.677 | 4330 | 0.677 | 1.14 | 1.21 | -0.0040647 | 4330 | 0.677 | 4330 | 0.677 | 1.14 | 1.21 | -0.00406
CFLAllSpcSDGRSDExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SDG | RSD | Ex | CZ10 | 4.33 | 0.000677 | 0 | 4.91 | 0.00081195 | -0.0207 | 4.33 | 0.000677 | 0 | 4.91 | 0.00081195 | -0.0207 |  | CFL | AllSpc | 4330 | 0.677 | 4330 | 0.677 | 1.13 | 1.2 | -0.0047806 | 4330 | 0.677 | 4330 | 0.677 | 1.13 | 1.2 | -0.00478
CFLAllSpcSDGRSDExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SDG | RSD | Ex | CZ14 | 4.33 | 0.000677 | 0 | 4.79 | 0.00081295 | -0.0322 | 4.33 | 0.000677 | 0 | 4.79 | 0.00081295 | -0.0322 |  | CFL | AllSpc | 4330 | 0.677 | 4330 | 0.677 | 1.11 | 1.2 | -0.0074365 | 4330 | 0.677 | 4330 | 0.677 | 1.11 | 1.2 | -0.00744
CFLAllSpcSDGRSDExCZ15 | Com-Iltg-dWatt-CFL_OSspc | SDG | RSD | Ex | CZ15 | 4.33 | 0.000677 | 0 | 5.27 | 0.000864 | -0.00766 | 4.33 | 0.000677 | 0 | 5.27 | 0.000864 | -0.00766 |  | CFL | AllSpc | 4330 | 0.677 | 4330 | 0.677 | 1.22 | 1.28 | -0.0017691 | 4330 | 0.677 | 4330 | 0.677 | 1.22 | 1.28 | -0.00177
CFLAllSpcSDGRSDExIOU | Com-Iltg-dWatt-CFL_OSspc | SDG | RSD | Ex | IOU | 4.33 | 0.000677 | 0 | 4.9028 | 0.00083678 | -0.018793 | 4.33 | 0.000677 | 0 | 4.9028 | 0.00083678 | -0.018793 |  | CFL | AllSpc | 4330 | 0.677 | 4330 | 0.677 | 1.13 | 1.24 | -0.0043403 | 4330 | 0.677 | 4330 | 0.677 | 1.13 | 1.24 | -0.00434
CFLAllSpcSDGRSDNewCZ06 | Com-Iltg-dWatt-CFL_OSspc | SDG | RSD | New | CZ06 | 4.33 | 0.000677 | 0 | 4.74 | 0.000848 | -0.0248 | 4.33 | 0.000677 | 0 | 4.74 | 0.000848 | -0.0248 |  | CFL | AllSpc | 4330 | 0.677 | 4330 | 0.677 | 1.09 | 1.25 | -0.0057275 | 4330 | 0.677 | 4330 | 0.677 | 1.09 | 1.25 | -0.00573
CFLAllSpcSDGRSDNewCZ07 | Com-Iltg-dWatt-CFL_OSspc | SDG | RSD | New | CZ07 | 4.33 | 0.000677 | 0 | 4.71 | 0.000851 | -0.0229 | 4.33 | 0.000677 | 0 | 4.71 | 0.000851 | -0.0229 |  | CFL | AllSpc | 4330 | 0.677 | 4330 | 0.677 | 1.09 | 1.26 | -0.0052887 | 4330 | 0.677 | 4330 | 0.677 | 1.09 | 1.26 | -0.00529
CFLAllSpcSDGRSDNewCZ08 | Com-Iltg-dWatt-CFL_OSspc | SDG | RSD | New | CZ08 | 4.33 | 0.000677 | 0 | 4.65 | 0.000738 | -0.0206 | 4.33 | 0.000677 | 0 | 4.65 | 0.000738 | -0.0206 |  | CFL | AllSpc | 4330 | 0.677 | 4330 | 0.677 | 1.07 | 1.09 | -0.0047575 | 4330 | 0.677 | 4330 | 0.677 | 1.07 | 1.09 | -0.00476
CFLAllSpcSDGRSDNewCZ10 | Com-Iltg-dWatt-CFL_OSspc | SDG | RSD | New | CZ10 | 4.33 | 0.000677 | 0 | 4.84 | 0.000891 | -0.0235 | 4.33 | 0.000677 | 0 | 4.84 | 0.000891 | -0.0235 |  | CFL | AllSpc | 4330 | 0.677 | 4330 | 0.677 | 1.12 | 1.32 | -0.0054273 | 4330 | 0.677 | 4330 | 0.677 | 1.12 | 1.32 | -0.00543
CFLAllSpcSDGRSDNewCZ14 | Com-Iltg-dWatt-CFL_OSspc | SDG | RSD | New | CZ14 | 4.33 | 0.000677 | 0 | 4.76 | 0.000889 | -0.0349 | 4.33 | 0.000677 | 0 | 4.76 | 0.000889 | -0.0349 |  | CFL | AllSpc | 4330 | 0.677 | 4330 | 0.677 | 1.1 | 1.31 | -0.00806 | 4330 | 0.677 | 4330 | 0.677 | 1.1 | 1.31 | -0.00806
CFLAllSpcSDGRSDNewCZ15 | Com-Iltg-dWatt-CFL_OSspc | SDG | RSD | New | CZ15 | 4.33 | 0.000677 | 0 | 5.2 | 0.000919 | -0.0101 | 4.33 | 0.000677 | 0 | 5.2 | 0.000919 | -0.0101 |  | CFL | AllSpc | 4330 | 0.677 | 4330 | 0.677 | 1.2 | 1.36 | -0.0023326 | 4330 | 0.677 | 4330 | 0.677 | 1.2 | 1.36 | -0.00233
CFLAllSpcSDGRSDNewIOU | Com-Iltg-dWatt-CFL_OSspc | SDG | RSD | New | IOU | 4.33 | 0.000677 | 0 | 4.7387 | 0.00085631 | -0.02306 | 4.33 | 0.000677 | 0 | 4.7387 | 0.00085631 | -0.02306 |  | CFL | AllSpc | 4330 | 0.677 | 4330 | 0.677 | 1.09 | 1.26 | -0.0053255 | 4330 | 0.677 | 4330 | 0.677 | 1.09 | 1.26 | -0.00533
CFLAllSpcSDGRt3ExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SDG | Rt3 | Ex | CZ06 | 3.69 | 0.00062095 | 0 | 4.2 | 0.00077995 | -0.00531 | 3.69 | 0.00062095 | 0 | 4.2 | 0.00077995 | -0.00531 |  | CFL | AllSpc | 3690 | 0.621 | 3690 | 0.621 | 1.14 | 1.26 | -0.001439 | 3690 | 0.621 | 3690 | 0.621 | 1.14 | 1.26 | -0.00144
CFLAllSpcSDGRt3ExCZ07 | Com-Iltg-dWatt-CFL_OSspc | SDG | Rt3 | Ex | CZ07 | 3.69 | 0.00062093 | 0 | 4.22 | 0.00076586 | -0.00244 | 3.69 | 0.00062093 | 0 | 4.22 | 0.00076586 | -0.00244 |  | CFL | AllSpc | 3690 | 0.621 | 3690 | 0.621 | 1.14 | 1.23 | -0.00066125 | 3690 | 0.621 | 3690 | 0.621 | 1.14 | 1.23 | -0.000661
CFLAllSpcSDGRt3ExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SDG | Rt3 | Ex | CZ08 | 3.69 | 0.00062098 | 0 | 4.2198 | 0.00076863 | -0.00461 | 3.69 | 0.00062098 | 0 | 4.2198 | 0.00076863 | -0.00461 |  | CFL | AllSpc | 3690 | 0.621 | 3690 | 0.621 | 1.14 | 1.24 | -0.0012493 | 3690 | 0.621 | 3690 | 0.621 | 1.14 | 1.24 | -0.00125
CFLAllSpcSDGRt3ExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SDG | Rt3 | Ex | CZ10 | 3.69 | 0.00062098 | 0 | 4.16 | 0.00077863 | -0.0081198 | 3.69 | 0.00062098 | 0 | 4.16 | 0.00077863 | -0.0081198 |  | CFL | AllSpc | 3690 | 0.621 | 3690 | 0.621 | 1.13 | 1.25 | -0.0022005 | 3690 | 0.621 | 3690 | 0.621 | 1.13 | 1.25 | -0.0022
CFLAllSpcSDGRt3ExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SDG | Rt3 | Ex | CZ14 | 3.69 | 0.00062097 | 0 | 3.96 | 0.00078463 | -0.0249 | 3.69 | 0.00062097 | 0 | 3.96 | 0.00078463 | -0.0249 |  | CFL | AllSpc | 3690 | 0.621 | 3690 | 0.621 | 1.07 | 1.26 | -0.006748 | 3690 | 0.621 | 3690 | 0.621 | 1.07 | 1.26 | -0.00675
CFLAllSpcSDGRt3ExCZ15 | Com-Iltg-dWatt-CFL_OSspc | SDG | Rt3 | Ex | CZ15 | 3.69 | 0.00062097 | 0 | 4.3 | 0.00079963 | -0.00206 | 3.69 | 0.00062097 | 0 | 4.3 | 0.00079963 | -0.00206 |  | CFL | AllSpc | 3690 | 0.621 | 3690 | 0.621 | 1.17 | 1.29 | -0.00055827 | 3690 | 0.621 | 3690 | 0.621 | 1.17 | 1.29 | -0.000558
CFLAllSpcSDGRt3ExIOU | Com-Iltg-dWatt-CFL_OSspc | SDG | Rt3 | Ex | IOU | 3.69 | 0.00062094 | 0 | 4.2044 | 0.00076966 | -0.0040826 | 3.69 | 0.00062094 | 0 | 4.2044 | 0.00076966 | -0.0040826 |  | CFL | AllSpc | 3690 | 0.621 | 3690 | 0.621 | 1.14 | 1.24 | -0.0011064 | 3690 | 0.621 | 3690 | 0.621 | 1.14 | 1.24 | -0.00111
CFLAllSpcSDGRt3NewCZ06 | Com-Iltg-dWatt-CFL_OSspc | SDG | Rt3 | New | CZ06 | 3.69 | 0.00062 | 0 | 4.08 | 0.000758 | -0.00789 | 3.69 | 0.00062 | 0 | 4.08 | 0.000758 | -0.00789 |  | CFL | AllSpc | 3690 | 0.62 | 3690 | 0.62 | 1.11 | 1.22 | -0.0021382 | 3690 | 0.62 | 3690 | 0.62 | 1.11 | 1.22 | -0.00214
CFLAllSpcSDGRt3NewCZ07 | Com-Iltg-dWatt-CFL_OSspc | SDG | Rt3 | New | CZ07 | 3.69 | 0.00062 | 0 | 4.11 | 0.000733 | -0.00376 | 3.69 | 0.00062 | 0 | 4.11 | 0.000733 | -0.00376 |  | CFL | AllSpc | 3690 | 0.62 | 3690 | 0.62 | 1.11 | 1.18 | -0.001019 | 3690 | 0.62 | 3690 | 0.62 | 1.11 | 1.18 | -0.00102
CFLAllSpcSDGRt3NewCZ08 | Com-Iltg-dWatt-CFL_OSspc | SDG | Rt3 | New | CZ08 | 3.69 | 0.00062 | 0 | 4.11 | 0.000747 | -0.00641 | 3.69 | 0.00062 | 0 | 4.11 | 0.000747 | -0.00641 |  | CFL | AllSpc | 3690 | 0.62 | 3690 | 0.62 | 1.11 | 1.2 | -0.0017371 | 3690 | 0.62 | 3690 | 0.62 | 1.11 | 1.2 | -0.00174
CFLAllSpcSDGRt3NewCZ10 | Com-Iltg-dWatt-CFL_OSspc | SDG | Rt3 | New | CZ10 | 3.69 | 0.00062 | 0 | 4.07 | 0.000772 | -0.0111 | 3.69 | 0.00062 | 0 | 4.07 | 0.000772 | -0.0111 |  | CFL | AllSpc | 3690 | 0.62 | 3690 | 0.62 | 1.1 | 1.25 | -0.0030081 | 3690 | 0.62 | 3690 | 0.62 | 1.1 | 1.25 | -0.00301
CFLAllSpcSDGRt3NewCZ14 | Com-Iltg-dWatt-CFL_OSspc | SDG | Rt3 | New | CZ14 | 3.69 | 0.00062 | 0 | 3.93 | 0.000776 | -0.0268 | 3.69 | 0.00062 | 0 | 3.93 | 0.000776 | -0.0268 |  | CFL | AllSpc | 3690 | 0.62 | 3690 | 0.62 | 1.07 | 1.25 | -0.0072629 | 3690 | 0.62 | 3690 | 0.62 | 1.07 | 1.25 | -0.00726
CFLAllSpcSDGRt3NewCZ15 | Com-Iltg-dWatt-CFL_OSspc | SDG | Rt3 | New | CZ15 | 3.69 | 0.00062 | 0 | 4.3 | 0.000826 | -0.00167 | 3.69 | 0.00062 | 0 | 4.3 | 0.000826 | -0.00167 |  | CFL | AllSpc | 3690 | 0.62 | 3690 | 0.62 | 1.17 | 1.33 | -0.00045257 | 3690 | 0.62 | 3690 | 0.62 | 1.17 | 1.33 | -0.000453
CFLAllSpcSDGRt3NewIOU | Com-Iltg-dWatt-CFL_OSspc | SDG | Rt3 | New | IOU | 3.69 | 0.00062 | 0 | 4.0991 | 0.00074433 | -0.0058813 | 3.69 | 0.00062 | 0 | 4.0991 | 0.00074433 | -0.0058813 |  | CFL | AllSpc | 3690 | 0.62 | 3690 | 0.62 | 1.11 | 1.2 | -0.0015939 | 3690 | 0.62 | 3690 | 0.62 | 1.11 | 1.2 | -0.00159
CFLAllSpcSDGRtLExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SDG | RtL | Ex | CZ06 | 4.32 | 0.00068093 | 0 | 4.8684 | 0.00085893 | -0.0107 | 4.32 | 0.00068093 | 0 | 4.8684 | 0.00085893 | -0.0107 |  | CFL | AllSpc | 4320 | 0.681 | 4320 | 0.681 | 1.13 | 1.26 | -0.0024769 | 4320 | 0.681 | 4320 | 0.681 | 1.13 | 1.26 | -0.00248
CFLAllSpcSDGRtLExCZ07 | Com-Iltg-dWatt-CFL_OSspc | SDG | RtL | Ex | CZ07 | 4.32 | 0.00068093 | 0 | 4.8993 | 0.00085893 | -0.0076493 | 4.32 | 0.00068093 | 0 | 4.8993 | 0.00085893 | -0.0076493 |  | CFL | AllSpc | 4320 | 0.681 | 4320 | 0.681 | 1.13 | 1.26 | -0.0017707 | 4320 | 0.681 | 4320 | 0.681 | 1.13 | 1.26 | -0.00177
CFLAllSpcSDGRtLExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SDG | RtL | Ex | CZ08 | 4.32 | 0.00068093 | 0 | 4.88 | 0.00085993 | -0.00916 | 4.32 | 0.00068093 | 0 | 4.88 | 0.00085993 | -0.00916 |  | CFL | AllSpc | 4320 | 0.681 | 4320 | 0.681 | 1.13 | 1.26 | -0.0021204 | 4320 | 0.681 | 4320 | 0.681 | 1.13 | 1.26 | -0.00212
CFLAllSpcSDGRtLExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SDG | RtL | Ex | CZ10 | 4.32 | 0.00068093 | 0 | 4.8475 | 0.00087593 | -0.0122 | 4.32 | 0.00068093 | 0 | 4.8475 | 0.00087593 | -0.0122 |  | CFL | AllSpc | 4320 | 0.681 | 4320 | 0.681 | 1.12 | 1.29 | -0.0028241 | 4320 | 0.681 | 4320 | 0.681 | 1.12 | 1.29 | -0.00282
CFLAllSpcSDGRtLExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SDG | RtL | Ex | CZ14 | 4.32 | 0.00068093 | 0 | 4.6875 | 0.00088693 | -0.025 | 4.32 | 0.00068093 | 0 | 4.6875 | 0.00088693 | -0.025 |  | CFL | AllSpc | 4320 | 0.681 | 4320 | 0.681 | 1.09 | 1.3 | -0.005787 | 4320 | 0.681 | 4320 | 0.681 | 1.09 | 1.3 | -0.00579
CFLAllSpcSDGRtLExCZ15 | Com-Iltg-dWatt-CFL_OSspc | SDG | RtL | Ex | CZ15 | 4.32 | 0.00068092 | 0 | 5.06 | 0.00089193 | -0.0043675 | 4.32 | 0.00068092 | 0 | 5.06 | 0.00089193 | -0.0043675 |  | CFL | AllSpc | 4320 | 0.681 | 4320 | 0.681 | 1.17 | 1.31 | -0.001011 | 4320 | 0.681 | 4320 | 0.681 | 1.17 | 1.31 | -0.00101
CFLAllSpcSDGRtLExIOU | Com-Iltg-dWatt-CFL_OSspc | SDG | RtL | Ex | IOU | 4.32 | 0.00068093 | 0 | 4.8842 | 0.0008632 | -0.0089755 | 4.32 | 0.00068093 | 0 | 4.8842 | 0.0008632 | -0.0089755 |  | CFL | AllSpc | 4320 | 0.681 | 4320 | 0.681 | 1.13 | 1.27 | -0.0020777 | 4320 | 0.681 | 4320 | 0.681 | 1.13 | 1.27 | -0.00208
CFLAllSpcSDGRtLNewCZ06 | Com-Iltg-dWatt-CFL_OSspc | SDG | RtL | New | CZ06 | 4.32 | 0.00068 | 0 | 4.73 | 0.000865 | -0.0148 | 4.32 | 0.00068 | 0 | 4.73 | 0.000865 | -0.0148 |  | CFL | AllSpc | 4320 | 0.68 | 4320 | 0.68 | 1.09 | 1.27 | -0.0034259 | 4320 | 0.68 | 4320 | 0.68 | 1.09 | 1.27 | -0.00343
CFLAllSpcSDGRtLNewCZ07 | Com-Iltg-dWatt-CFL_OSspc | SDG | RtL | New | CZ07 | 4.32 | 0.00068 | 0 | 4.71 | 0.000833 | -0.0106 | 4.32 | 0.00068 | 0 | 4.71 | 0.000833 | -0.0106 |  | CFL | AllSpc | 4320 | 0.68 | 4320 | 0.68 | 1.09 | 1.23 | -0.0024537 | 4320 | 0.68 | 4320 | 0.68 | 1.09 | 1.23 | -0.00245
CFLAllSpcSDGRtLNewCZ08 | Com-Iltg-dWatt-CFL_OSspc | SDG | RtL | New | CZ08 | 4.32 | 0.00068 | 0 | 4.79 | 0.000877 | -0.0125 | 4.32 | 0.00068 | 0 | 4.79 | 0.000877 | -0.0125 |  | CFL | AllSpc | 4320 | 0.68 | 4320 | 0.68 | 1.11 | 1.29 | -0.0028935 | 4320 | 0.68 | 4320 | 0.68 | 1.11 | 1.29 | -0.00289
CFLAllSpcSDGRtLNewCZ10 | Com-Iltg-dWatt-CFL_OSspc | SDG | RtL | New | CZ10 | 4.32 | 0.00068 | 0 | 4.83 | 0.000921 | -0.0144 | 4.32 | 0.00068 | 0 | 4.83 | 0.000921 | -0.0144 |  | CFL | AllSpc | 4320 | 0.68 | 4320 | 0.68 | 1.12 | 1.35 | -0.0033333 | 4320 | 0.68 | 4320 | 0.68 | 1.12 | 1.35 | -0.00333
CFLAllSpcSDGRtLNewCZ14 | Com-Iltg-dWatt-CFL_OSspc | SDG | RtL | New | CZ14 | 4.32 | 0.00068 | 0 | 4.72 | 0.000915 | -0.028 | 4.32 | 0.00068 | 0 | 4.72 | 0.000915 | -0.028 |  | CFL | AllSpc | 4320 | 0.68 | 4320 | 0.68 | 1.09 | 1.35 | -0.0064815 | 4320 | 0.68 | 4320 | 0.68 | 1.09 | 1.35 | -0.00648
CFLAllSpcSDGRtLNewCZ15 | Com-Iltg-dWatt-CFL_OSspc | SDG | RtL | New | CZ15 | 4.32 | 0.00068 | 0 | 5.1 | 0.000932 | -0.00421 | 4.32 | 0.00068 | 0 | 5.1 | 0.000932 | -0.00421 |  | CFL | AllSpc | 4320 | 0.68 | 4320 | 0.68 | 1.18 | 1.37 | -0.00097454 | 4320 | 0.68 | 4320 | 0.68 | 1.18 | 1.37 | -0.000975
CFLAllSpcSDGRtLNewIOU | Com-Iltg-dWatt-CFL_OSspc | SDG | RtL | New | IOU | 4.32 | 0.00068 | 0 | 4.7451 | 0.00085845 | -0.011803 | 4.32 | 0.00068 | 0 | 4.7451 | 0.00085845 | -0.011803 |  | CFL | AllSpc | 4320 | 0.68 | 4320 | 0.68 | 1.1 | 1.26 | -0.0027322 | 4320 | 0.68 | 4320 | 0.68 | 1.1 | 1.26 | -0.00273
CFLAllSpcSDGRtSExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SDG | RtS | Ex | CZ06 | 3.9698 | 0.00068995 | 0 | 4.3898 | 0.0008636 | -0.0078595 | 3.9698 | 0.00068995 | 0 | 4.3898 | 0.0008636 | -0.0078595 |  | CFL | AllSpc | 3970 | 0.69 | 3970 | 0.69 | 1.11 | 1.25 | -0.0019798 | 3970 | 0.69 | 3970 | 0.69 | 1.11 | 1.25 | -0.00198
CFLAllSpcSDGRtSExCZ07 | Com-Iltg-dWatt-CFL_OSspc | SDG | RtS | Ex | CZ07 | 3.9693 | 0.00068986 | 0 | 4.3993 | 0.00084386 | -0.0048393 | 3.9693 | 0.00068986 | 0 | 4.3993 | 0.00084386 | -0.0048393 |  | CFL | AllSpc | 3970 | 0.69 | 3970 | 0.69 | 1.11 | 1.22 | -0.0012192 | 3970 | 0.69 | 3970 | 0.69 | 1.11 | 1.22 | -0.00122
CFLAllSpcSDGRtSExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SDG | RtS | Ex | CZ08 | 3.9693 | 0.00068986 | 0 | 4.4193 | 0.00086478 | -0.0066685 | 3.9693 | 0.00068986 | 0 | 4.4193 | 0.00086478 | -0.0066685 |  | CFL | AllSpc | 3970 | 0.69 | 3970 | 0.69 | 1.11 | 1.25 | -0.00168 | 3970 | 0.69 | 3970 | 0.69 | 1.11 | 1.25 | -0.00168
CFLAllSpcSDGRtSExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SDG | RtS | Ex | CZ10 | 3.9693 | 0.00068986 | 0 | 4.3993 | 0.00087273 | -0.009279 | 3.9693 | 0.00068986 | 0 | 4.3993 | 0.00087273 | -0.009279 |  | CFL | AllSpc | 3970 | 0.69 | 3970 | 0.69 | 1.11 | 1.27 | -0.0023377 | 3970 | 0.69 | 3970 | 0.69 | 1.11 | 1.27 | -0.00234
CFLAllSpcSDGRtSExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SDG | RtS | Ex | CZ14 | 3.9693 | 0.00068986 | 0 | 4.2793 | 0.00087086 | -0.020393 | 3.9693 | 0.00068986 | 0 | 4.2793 | 0.00087086 | -0.020393 |  | CFL | AllSpc | 3970 | 0.69 | 3970 | 0.69 | 1.08 | 1.26 | -0.0051377 | 3970 | 0.69 | 3970 | 0.69 | 1.08 | 1.26 | -0.00514
CFLAllSpcSDGRtSExCZ15 | Com-Iltg-dWatt-CFL_OSspc | SDG | RtS | Ex | CZ15 | 3.9692 | 0.00068985 | 0 | 4.7092 | 0.00085873 | -0.00241 | 3.9692 | 0.00068985 | 0 | 4.7092 | 0.00085873 | -0.00241 |  | CFL | AllSpc | 3970 | 0.69 | 3970 | 0.69 | 1.19 | 1.24 | -0.00060717 | 3970 | 0.69 | 3970 | 0.69 | 1.19 | 1.24 | -0.000607
CFLAllSpcSDGRtSExIOU | Com-Iltg-dWatt-CFL_OSspc | SDG | RtS | Ex | IOU | 3.9693 | 0.00068986 | 0 | 4.4001 | 0.00085291 | -0.0061551 | 3.9693 | 0.00068986 | 0 | 4.4001 | 0.00085291 | -0.0061551 |  | CFL | AllSpc | 3970 | 0.69 | 3970 | 0.69 | 1.11 | 1.24 | -0.0015507 | 3970 | 0.69 | 3970 | 0.69 | 1.11 | 1.24 | -0.00155
CFLAllSpcSDGRtSNewCZ06 | Com-Iltg-dWatt-CFL_OSspc | SDG | RtS | New | CZ06 | 3.96 | 0.000688 | 0 | 4.27 | 0.000847 | -0.00985 | 3.96 | 0.000688 | 0 | 4.27 | 0.000847 | -0.00985 |  | CFL | AllSpc | 3960 | 0.688 | 3960 | 0.688 | 1.08 | 1.23 | -0.0024874 | 3960 | 0.688 | 3960 | 0.688 | 1.08 | 1.23 | -0.00249
CFLAllSpcSDGRtSNewCZ07 | Com-Iltg-dWatt-CFL_OSspc | SDG | RtS | New | CZ07 | 3.96 | 0.000688 | 0 | 4.26 | 0.000837 | -0.00602 | 3.96 | 0.000688 | 0 | 4.26 | 0.000837 | -0.00602 |  | CFL | AllSpc | 3960 | 0.688 | 3960 | 0.688 | 1.08 | 1.22 | -0.0015202 | 3960 | 0.688 | 3960 | 0.688 | 1.08 | 1.22 | -0.00152
CFLAllSpcSDGRtSNewCZ08 | Com-Iltg-dWatt-CFL_OSspc | SDG | RtS | New | CZ08 | 3.96 | 0.000688 | 0 | 4.31 | 0.000856 | -0.00823 | 3.96 | 0.000688 | 0 | 4.31 | 0.000856 | -0.00823 |  | CFL | AllSpc | 3960 | 0.688 | 3960 | 0.688 | 1.09 | 1.24 | -0.0020783 | 3960 | 0.688 | 3960 | 0.688 | 1.09 | 1.24 | -0.00208
CFLAllSpcSDGRtSNewCZ10 | Com-Iltg-dWatt-CFL_OSspc | SDG | RtS | New | CZ10 | 3.96 | 0.000688 | 0 | 4.35 | 0.000893 | -0.00985 | 3.96 | 0.000688 | 0 | 4.35 | 0.000893 | -0.00985 |  | CFL | AllSpc | 3960 | 0.688 | 3960 | 0.688 | 1.1 | 1.3 | -0.0024874 | 3960 | 0.688 | 3960 | 0.688 | 1.1 | 1.3 | -0.00249
CFLAllSpcSDGRtSNewCZ14 | Com-Iltg-dWatt-CFL_OSspc | SDG | RtS | New | CZ14 | 3.96 | 0.000688 | 0 | 4.25 | 0.00088 | -0.0217 | 3.96 | 0.000688 | 0 | 4.25 | 0.00088 | -0.0217 |  | CFL | AllSpc | 3960 | 0.688 | 3960 | 0.688 | 1.07 | 1.28 | -0.0054798 | 3960 | 0.688 | 3960 | 0.688 | 1.07 | 1.28 | -0.00548
CFLAllSpcSDGRtSNewCZ15 | Com-Iltg-dWatt-CFL_OSspc | SDG | RtS | New | CZ15 | 3.96 | 0.000688 | 0 | 4.55 | 0.000905 | -0.0019 | 3.96 | 0.000688 | 0 | 4.55 | 0.000905 | -0.0019 |  | CFL | AllSpc | 3960 | 0.688 | 3960 | 0.688 | 1.15 | 1.32 | -0.0004798 | 3960 | 0.688 | 3960 | 0.688 | 1.15 | 1.32 | -0.00048
CFLAllSpcSDGRtSNewIOU | Com-Iltg-dWatt-CFL_OSspc | SDG | RtS | New | IOU | 3.96 | 0.000688 | 0 | 4.2855 | 0.00085229 | -0.007236 | 3.96 | 0.000688 | 0 | 4.2855 | 0.00085229 | -0.007236 |  | CFL | AllSpc | 3960 | 0.688 | 3960 | 0.688 | 1.08 | 1.24 | -0.0018273 | 3960 | 0.688 | 3960 | 0.688 | 1.08 | 1.24 | -0.00183
CFLAllSpcSDGSCnExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SDG | SCn | Ex | CZ06 | 2.6 | 0.000483 | 0 | 2.67 | 0.000621 | -0.013582 | 2.6 | 0.000483 | 0 | 2.67 | 0.000621 | -0.013582 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 1.03 | 1.29 | -0.0052237 | 2600 | 0.483 | 2600 | 0.483 | 1.03 | 1.29 | -0.00522
CFLAllSpcSDGSCnExCZ07 | Com-Iltg-dWatt-CFL_OSspc | SDG | SCn | Ex | CZ07 | 2.6 | 0.000483 | 0 | 2.63 | 0.000625 | -0.0109 | 2.6 | 0.000483 | 0 | 2.63 | 0.000625 | -0.0109 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 1.01 | 1.29 | -0.0041923 | 2600 | 0.483 | 2600 | 0.483 | 1.01 | 1.29 | -0.00419
CFLAllSpcSDGSCnExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SDG | SCn | Ex | CZ08 | 2.6 | 0.000483 | 0 | 2.71 | 0.00062 | -0.0116 | 2.6 | 0.000483 | 0 | 2.71 | 0.00062 | -0.0116 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 1.04 | 1.28 | -0.0044615 | 2600 | 0.483 | 2600 | 0.483 | 1.04 | 1.28 | -0.00446
CFLAllSpcSDGSCnExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SDG | SCn | Ex | CZ10 | 2.6 | 0.000483 | 0 | 2.7155 | 0.000628 | -0.0148 | 2.6 | 0.000483 | 0 | 2.7155 | 0.000628 | -0.0148 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 1.04 | 1.3 | -0.0056923 | 2600 | 0.483 | 2600 | 0.483 | 1.04 | 1.3 | -0.00569
CFLAllSpcSDGSCnExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SDG | SCn | Ex | CZ14 | 2.6 | 0.000483 | 0 | 2.6356 | 0.000617 | -0.021855 | 2.6 | 0.000483 | 0 | 2.6356 | 0.000617 | -0.021855 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 1.01 | 1.28 | -0.008406 | 2600 | 0.483 | 2600 | 0.483 | 1.01 | 1.28 | -0.00841
CFLAllSpcSDGSCnExCZ15 | Com-Iltg-dWatt-CFL_OSspc | SDG | SCn | Ex | CZ15 | 2.6 | 0.000483 | 0 | 2.91 | 0.000617 | -0.0061455 | 2.6 | 0.000483 | 0 | 2.91 | 0.000617 | -0.0061455 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 1.12 | 1.28 | -0.0023637 | 2600 | 0.483 | 2600 | 0.483 | 1.12 | 1.28 | -0.00236
CFLAllSpcSDGSCnExIOU | Com-Iltg-dWatt-CFL_OSspc | SDG | SCn | Ex | IOU | 2.6 | 0.000483 | 0 | 2.6583 | 0.00062569 | -0.012171 | 2.6 | 0.000483 | 0 | 2.6583 | 0.00062569 | -0.012171 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 1.02 | 1.3 | -0.0046812 | 2600 | 0.483 | 2600 | 0.483 | 1.02 | 1.3 | -0.00468
CFLAllSpcSDGSCnNewCZ06 | Com-Iltg-dWatt-CFL_OSspc | SDG | SCn | New | CZ06 | 2.6 | 0.000483 | 0 | 2.6 | 0.000578 | -0.0153 | 2.6 | 0.000483 | 0 | 2.6 | 0.000578 | -0.0153 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 1 | 1.2 | -0.0058846 | 2600 | 0.483 | 2600 | 0.483 | 1 | 1.2 | -0.00588
CFLAllSpcSDGSCnNewCZ07 | Com-Iltg-dWatt-CFL_OSspc | SDG | SCn | New | CZ07 | 2.6 | 0.000483 | 0 | 2.6 | 0.000591 | -0.0127 | 2.6 | 0.000483 | 0 | 2.6 | 0.000591 | -0.0127 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 1 | 1.22 | -0.0048846 | 2600 | 0.483 | 2600 | 0.483 | 1 | 1.22 | -0.00488
CFLAllSpcSDGSCnNewCZ08 | Com-Iltg-dWatt-CFL_OSspc | SDG | SCn | New | CZ08 | 2.6 | 0.000483 | 0 | 2.66 | 0.000587 | -0.0133 | 2.6 | 0.000483 | 0 | 2.66 | 0.000587 | -0.0133 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 1.02 | 1.22 | -0.0051154 | 2600 | 0.483 | 2600 | 0.483 | 1.02 | 1.22 | -0.00512
CFLAllSpcSDGSCnNewCZ10 | Com-Iltg-dWatt-CFL_OSspc | SDG | SCn | New | CZ10 | 2.6 | 0.000483 | 0 | 2.67 | 0.000601 | -0.0156 | 2.6 | 0.000483 | 0 | 2.67 | 0.000601 | -0.0156 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 1.03 | 1.24 | -0.006 | 2600 | 0.483 | 2600 | 0.483 | 1.03 | 1.24 | -0.006
CFLAllSpcSDGSCnNewCZ14 | Com-Iltg-dWatt-CFL_OSspc | SDG | SCn | New | CZ14 | 2.6 | 0.000483 | 0 | 2.61 | 0.000598 | -0.023 | 2.6 | 0.000483 | 0 | 2.61 | 0.000598 | -0.023 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 1 | 1.24 | -0.0088462 | 2600 | 0.483 | 2600 | 0.483 | 1 | 1.24 | -0.00885
CFLAllSpcSDGSCnNewCZ15 | Com-Iltg-dWatt-CFL_OSspc | SDG | SCn | New | CZ15 | 2.6 | 0.000483 | 0 | 2.84 | 0.000603 | -0.00487 | 2.6 | 0.000483 | 0 | 2.84 | 0.000603 | -0.00487 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 1.09 | 1.25 | -0.0018731 | 2600 | 0.483 | 2600 | 0.483 | 1.09 | 1.25 | -0.00187
CFLAllSpcSDGSCnNewIOU | Com-Iltg-dWatt-CFL_OSspc | SDG | SCn | New | IOU | 2.6 | 0.000483 | 0 | 2.6222 | 0.00059364 | -0.013662 | 2.6 | 0.000483 | 0 | 2.6222 | 0.00059364 | -0.013662 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 1.01 | 1.23 | -0.0052547 | 2600 | 0.483 | 2600 | 0.483 | 1.01 | 1.23 | -0.00525
CFLAllSpcSDGSUnExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SDG | SUn | Ex | CZ06 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0 | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0
CFLAllSpcSDGSUnExCZ07 | Com-Iltg-dWatt-CFL_OSspc | SDG | SUn | Ex | CZ07 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0 | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0
CFLAllSpcSDGSUnExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SDG | SUn | Ex | CZ08 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0 | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0
CFLAllSpcSDGSUnExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SDG | SUn | Ex | CZ10 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0 | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0
CFLAllSpcSDGSUnExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SDG | SUn | Ex | CZ14 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0 | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0
CFLAllSpcSDGSUnExCZ15 | Com-Iltg-dWatt-CFL_OSspc | SDG | SUn | Ex | CZ15 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0 | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0
CFLAllSpcSDGSUnExIOU | Com-Iltg-dWatt-CFL_OSspc | SDG | SUn | Ex | IOU | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0 | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0
CFLAllSpcSDGSUnNewCZ06 | Com-Iltg-dWatt-CFL_OSspc | SDG | SUn | New | CZ06 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0 | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0
CFLAllSpcSDGSUnNewCZ07 | Com-Iltg-dWatt-CFL_OSspc | SDG | SUn | New | CZ07 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0 | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0
CFLAllSpcSDGSUnNewCZ08 | Com-Iltg-dWatt-CFL_OSspc | SDG | SUn | New | CZ08 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0 | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0
CFLAllSpcSDGSUnNewCZ10 | Com-Iltg-dWatt-CFL_OSspc | SDG | SUn | New | CZ10 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0 | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0
CFLAllSpcSDGSUnNewCZ14 | Com-Iltg-dWatt-CFL_OSspc | SDG | SUn | New | CZ14 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0 | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0
CFLAllSpcSDGSUnNewCZ15 | Com-Iltg-dWatt-CFL_OSspc | SDG | SUn | New | CZ15 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0 | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0
CFLAllSpcSDGSUnNewIOU | Com-Iltg-dWatt-CFL_OSspc | SDG | SUn | New | IOU | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 | 2.6 | 0.000483 | 0 |  | CFL | AllSpc | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0 | 2600 | 0.483 | 2600 | 0.483 | 1 | 1 | 0
CFLAllSpcSDGWRfExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SDG | WRf | Ex | CZ06 | 4.24 | 0.000466 | 0 | 6.6789 | 0.000584 | 0 | 4.24 | 0.000466 | 0 | 6.6789 | 0.000584 | 0 |  | CFL | AllSpc | 4240 | 0.466 | 4240 | 0.466 | 1.58 | 1.25 | 0 | 4240 | 0.466 | 4240 | 0.466 | 1.58 | 1.25 | 0
CFLAllSpcSDGWRfExCZ07 | Com-Iltg-dWatt-CFL_OSspc | SDG | WRf | Ex | CZ07 | 4.24 | 0.000466 | 0 | 6.64 | 0.000585 | 0 | 4.24 | 0.000466 | 0 | 6.64 | 0.000585 | 0 |  | CFL | AllSpc | 4240 | 0.466 | 4240 | 0.466 | 1.57 | 1.26 | 0 | 4240 | 0.466 | 4240 | 0.466 | 1.57 | 1.26 | 0
CFLAllSpcSDGWRfExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SDG | WRf | Ex | CZ10 | 4.24 | 0.000466 | 0 | 6.8372 | 0.000589 | 0 | 4.24 | 0.000466 | 0 | 6.8372 | 0.000589 | 0 |  | CFL | AllSpc | 4240 | 0.466 | 4240 | 0.466 | 1.61 | 1.26 | 0 | 4240 | 0.466 | 4240 | 0.466 | 1.61 | 1.26 | 0
CFLAllSpcSDGWRfExIOU | Com-Iltg-dWatt-CFL_OSspc | SDG | WRf | Ex | IOU | 4.24 | 0.000466 | 0 | 6.6837 | 0.00058587 | 0 | 4.24 | 0.000466 | 0 | 6.6837 | 0.00058587 | 0 |  | CFL | AllSpc | 4240 | 0.466 | 4240 | 0.466 | 1.58 | 1.26 | 0 | 4240 | 0.466 | 4240 | 0.466 | 1.58 | 1.26 | 0
CFLAllSpcSDGWRfNewCZ06 | Com-Iltg-dWatt-CFL_OSspc | SDG | WRf | New | CZ06 | 4.24 | 0.000466 | 0 | 6.44 | 0.000574 | 0 | 4.24 | 0.000466 | 0 | 6.44 | 0.000574 | 0 |  | CFL | AllSpc | 4240 | 0.466 | 4240 | 0.466 | 1.52 | 1.23 | 0 | 4240 | 0.466 | 4240 | 0.466 | 1.52 | 1.23 | 0
CFLAllSpcSDGWRfNewCZ07 | Com-Iltg-dWatt-CFL_OSspc | SDG | WRf | New | CZ07 | 4.24 | 0.000466 | 0 | 6.49 | 0.000575 | 0 | 4.24 | 0.000466 | 0 | 6.49 | 0.000575 | 0 |  | CFL | AllSpc | 4240 | 0.466 | 4240 | 0.466 | 1.53 | 1.23 | 0 | 4240 | 0.466 | 4240 | 0.466 | 1.53 | 1.23 | 0
CFLAllSpcSDGWRfNewCZ08 | Com-Iltg-dWatt-CFL_OSspc | SDG | WRf | New | CZ08 | 4.24 | 0.000466 | 0 | 6.4 | 0.000575 | 0 | 4.24 | 0.000466 | 0 | 6.4 | 0.000575 | 0 |  | CFL | AllSpc | 4240 | 0.466 | 4240 | 0.466 | 1.51 | 1.23 | 0 | 4240 | 0.466 | 4240 | 0.466 | 1.51 | 1.23 | 0
CFLAllSpcSDGWRfNewCZ10 | Com-Iltg-dWatt-CFL_OSspc | SDG | WRf | New | CZ10 | 4.24 | 0.000466 | 0 | 6.24 | 0.000582 | 0 | 4.24 | 0.000466 | 0 | 6.24 | 0.000582 | 0 |  | CFL | AllSpc | 4240 | 0.466 | 4240 | 0.466 | 1.47 | 1.25 | 0 | 4240 | 0.466 | 4240 | 0.466 | 1.47 | 1.25 | 0
CFLAllSpcSDGWRfNewCZ14 | Com-Iltg-dWatt-CFL_OSspc | SDG | WRf | New | CZ14 | 4.24 | 0.000466 | 0 | 6.01 | 0.000577 | 0 | 4.24 | 0.000466 | 0 | 6.01 | 0.000577 | 0 |  | CFL | AllSpc | 4240 | 0.466 | 4240 | 0.466 | 1.42 | 1.24 | 0 | 4240 | 0.466 | 4240 | 0.466 | 1.42 | 1.24 | 0
CFLAllSpcSDGWRfNewCZ15 | Com-Iltg-dWatt-CFL_OSspc | SDG | WRf | New | CZ15 | 4.24 | 0.000466 | 0 | 6.45 | 0.000581 | 0 | 4.24 | 0.000466 | 0 | 6.45 | 0.000581 | 0 |  | CFL | AllSpc | 4240 | 0.466 | 4240 | 0.466 | 1.52 | 1.25 | 0 | 4240 | 0.466 | 4240 | 0.466 | 1.52 | 1.25 | 0
CFLAllSpcSDGWRfNewIOU | Com-Iltg-dWatt-CFL_OSspc | SDG | WRf | New | IOU | 4.24 | 0.000466 | 0 | 6.4347 | 0.00057652 | 0 | 4.24 | 0.000466 | 0 | 6.4347 | 0.00057652 | 0 |  | CFL | AllSpc | 4240 | 0.466 | 4240 | 0.466 | 1.52 | 1.24 | 0 | 4240 | 0.466 | 4240 | 0.466 | 1.52 | 1.24 | 0
ExitNonePGEAsmExCZ01 | Com-Iltg-dWatt-Exit | PGE | Asm | Ex | CZ01 | 8.76 | 0.001 | 0 | 8.26 | 0.00121 | -0.188 | 8.76 | 0.001 | 0 | 8.26 | 0.00121 | -0.188 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.943 | 1.21 | -0.021461 | 8760 | 1 | 8760 | 1 | 0.943 | 1.21 | -0.0215
ExitNonePGEAsmExCZ02 | Com-Iltg-dWatt-Exit | PGE | Asm | Ex | CZ02 | 8.76 | 0.001 | 0 | 8.95 | 0.00125 | -0.106 | 8.76 | 0.001 | 0 | 8.95 | 0.00125 | -0.106 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.02 | 1.25 | -0.0121 | 8760 | 1 | 8760 | 1 | 1.02 | 1.25 | -0.0121
ExitNonePGEAsmExCZ03 | Com-Iltg-dWatt-Exit | PGE | Asm | Ex | CZ03 | 8.76 | 0.001 | 0 | 8.9 | 0.00127 | -0.112 | 8.76 | 0.001 | 0 | 8.9 | 0.00127 | -0.112 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.02 | 1.27 | -0.012785 | 8760 | 1 | 8760 | 1 | 1.02 | 1.27 | -0.0128
ExitNonePGEAsmExCZ04 | Com-Iltg-dWatt-Exit | PGE | Asm | Ex | CZ04 | 8.76 | 0.001 | 0 | 9.15 | 0.00126 | -0.0866 | 8.76 | 0.001 | 0 | 9.15 | 0.00126 | -0.0866 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.04 | 1.26 | -0.0098858 | 8760 | 1 | 8760 | 1 | 1.04 | 1.26 | -0.00989
ExitNonePGEAsmExCZ05 | Com-Iltg-dWatt-Exit | PGE | Asm | Ex | CZ05 | 8.76 | 0.001 | 0 | 8.94 | 0.00124 | -0.109 | 8.76 | 0.001 | 0 | 8.94 | 0.00124 | -0.109 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.02 | 1.24 | -0.012443 | 8760 | 1 | 8760 | 1 | 1.02 | 1.24 | -0.0124
ExitNonePGEAsmExCZ11 | Com-Iltg-dWatt-Exit | PGE | Asm | Ex | CZ11 | 8.76 | 0.001 | 0 | 9.18 | 0.00125 | -0.087 | 8.76 | 0.001 | 0 | 9.18 | 0.00125 | -0.087 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.05 | 1.25 | -0.0099315 | 8760 | 1 | 8760 | 1 | 1.05 | 1.25 | -0.00993
ExitNonePGEAsmExCZ12 | Com-Iltg-dWatt-Exit | PGE | Asm | Ex | CZ12 | 8.76 | 0.001 | 0 | 9.01 | 0.00127 | -0.0876 | 8.76 | 0.001 | 0 | 9.01 | 0.00127 | -0.0876 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.03 | 1.27 | -0.01 | 8760 | 1 | 8760 | 1 | 1.03 | 1.27 | -0.01
ExitNonePGEAsmExCZ13 | Com-Iltg-dWatt-Exit | PGE | Asm | Ex | CZ13 | 8.76 | 0.001 | 0 | 9.21 | 0.00125 | -0.0843 | 8.76 | 0.001 | 0 | 9.21 | 0.00125 | -0.0843 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.05 | 1.25 | -0.0096233 | 8760 | 1 | 8760 | 1 | 1.05 | 1.25 | -0.00962
ExitNonePGEAsmExCZ16 | Com-Iltg-dWatt-Exit | PGE | Asm | Ex | CZ16 | 8.76 | 0.001 | 0 | 8.42 | 0.00123 | -0.13 | 8.76 | 0.001 | 0 | 8.42 | 0.00123 | -0.13 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.961 | 1.23 | -0.01484 | 8760 | 1 | 8760 | 1 | 0.961 | 1.23 | -0.0148
ExitNonePGEAsmExIOU | Com-Iltg-dWatt-Exit | PGE | Asm | Ex | IOU | 8.76 | 0.001 | 0 | 9.01 | 0.00126 | -0.0981 | 8.76 | 0.001 | 0 | 9.01 | 0.00126 | -0.0981 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.03 | 1.26 | -0.011199 | 8760 | 1 | 8760 | 1 | 1.03 | 1.26 | -0.0112
ExitNonePGEAsmNewCZ01 | Com-Iltg-dWatt-Exit | PGE | Asm | New | CZ01 | 8.76 | 0.001 | 0 | 8.29 | 0.00125 | -0.2 | 8.76 | 0.001 | 0 | 8.29 | 0.00125 | -0.2 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.946 | 1.25 | -0.022831 | 8760 | 1 | 8760 | 1 | 0.946 | 1.25 | -0.0228
ExitNonePGEAsmNewCZ02 | Com-Iltg-dWatt-Exit | PGE | Asm | New | CZ02 | 8.76 | 0.001 | 0 | 8.83 | 0.00126 | -0.111 | 8.76 | 0.001 | 0 | 8.83 | 0.00126 | -0.111 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.01 | 1.26 | -0.012671 | 8760 | 1 | 8760 | 1 | 1.01 | 1.26 | -0.0127
ExitNonePGEAsmNewCZ03 | Com-Iltg-dWatt-Exit | PGE | Asm | New | CZ03 | 8.76 | 0.001 | 0 | 8.8 | 0.00125 | -0.127 | 8.76 | 0.001 | 0 | 8.8 | 0.00125 | -0.127 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1 | 1.25 | -0.014498 | 8760 | 1 | 8760 | 1 | 1 | 1.25 | -0.0145
ExitNonePGEAsmNewCZ04 | Com-Iltg-dWatt-Exit | PGE | Asm | New | CZ04 | 8.76 | 0.001 | 0 | 8.99 | 0.00125 | -0.099 | 8.76 | 0.001 | 0 | 8.99 | 0.00125 | -0.099 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.03 | 1.25 | -0.011301 | 8760 | 1 | 8760 | 1 | 1.03 | 1.25 | -0.0113
ExitNonePGEAsmNewCZ05 | Com-Iltg-dWatt-Exit | PGE | Asm | New | CZ05 | 8.76 | 0.001 | 0 | 8.87 | 0.00122 | -0.124 | 8.76 | 0.001 | 0 | 8.87 | 0.00122 | -0.124 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.01 | 1.22 | -0.014155 | 8760 | 1 | 8760 | 1 | 1.01 | 1.22 | -0.0142
ExitNonePGEAsmNewCZ11 | Com-Iltg-dWatt-Exit | PGE | Asm | New | CZ11 | 8.76 | 0.001 | 0 | 9.08 | 0.00128 | -0.092 | 8.76 | 0.001 | 0 | 9.08 | 0.00128 | -0.092 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.04 | 1.28 | -0.010502 | 8760 | 1 | 8760 | 1 | 1.04 | 1.28 | -0.0105
ExitNonePGEAsmNewCZ12 | Com-Iltg-dWatt-Exit | PGE | Asm | New | CZ12 | 8.76 | 0.001 | 0 | 9.05 | 0.00128 | -0.0999 | 8.76 | 0.001 | 0 | 9.05 | 0.00128 | -0.0999 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.03 | 1.28 | -0.011404 | 8760 | 1 | 8760 | 1 | 1.03 | 1.28 | -0.0114
ExitNonePGEAsmNewCZ13 | Com-Iltg-dWatt-Exit | PGE | Asm | New | CZ13 | 8.76 | 0.001 | 0 | 9.22 | 0.00128 | -0.099 | 8.76 | 0.001 | 0 | 9.22 | 0.00128 | -0.099 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.05 | 1.28 | -0.011301 | 8760 | 1 | 8760 | 1 | 1.05 | 1.28 | -0.0113
ExitNonePGEAsmNewCZ16 | Com-Iltg-dWatt-Exit | PGE | Asm | New | CZ16 | 8.76 | 0.001 | 0 | 8.53 | 0.00123 | -0.138 | 8.76 | 0.001 | 0 | 8.53 | 0.00123 | -0.138 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.974 | 1.23 | -0.015753 | 8760 | 1 | 8760 | 1 | 0.974 | 1.23 | -0.0158
ExitNonePGEAsmNewIOU | Com-Iltg-dWatt-Exit | PGE | Asm | New | IOU | 8.76 | 0.001 | 0 | 8.98 | 0.00126 | -0.108 | 8.76 | 0.001 | 0 | 8.98 | 0.00126 | -0.108 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.03 | 1.26 | -0.012329 | 8760 | 1 | 8760 | 1 | 1.03 | 1.26 | -0.0123
ExitNonePGEComExCZ01 | Com-Iltg-dWatt-Exit | PGE | Com | Ex | CZ01 | 8.76 | 0.001 | 0 | 8.4515 | 0.0012186 | -0.1177 | 8.76 | 0.001 | 0 | 8.4515 | 0.0012186 | -0.1177 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.965 | 1.22 | -0.013437 | 8760 | 1 | 8760 | 1 | 0.965 | 1.22 | -0.0134
ExitNonePGEComExCZ02 | Com-Iltg-dWatt-Exit | PGE | Com | Ex | CZ02 | 8.76 | 0.001 | 0 | 9.0065 | 0.0012617 | -0.073223 | 8.76 | 0.001 | 0 | 9.0065 | 0.0012617 | -0.073223 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.03 | 1.26 | -0.0083588 | 8760 | 1 | 8760 | 1 | 1.03 | 1.26 | -0.00836
ExitNonePGEComExCZ03 | Com-Iltg-dWatt-Exit | PGE | Com | Ex | CZ03 | 8.76 | 0.001 | 0 | 9.0979 | 0.0012919 | -0.068218 | 8.76 | 0.001 | 0 | 9.0979 | 0.0012919 | -0.068218 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.04 | 1.29 | -0.0077874 | 8760 | 1 | 8760 | 1 | 1.04 | 1.29 | -0.00779
ExitNonePGEComExCZ04 | Com-Iltg-dWatt-Exit | PGE | Com | Ex | CZ04 | 8.76 | 0.001 | 0 | 9.212 | 0.0012851 | -0.056973 | 8.76 | 0.001 | 0 | 9.212 | 0.0012851 | -0.056973 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.05 | 1.29 | -0.0065038 | 8760 | 1 | 8760 | 1 | 1.05 | 1.29 | -0.0065
ExitNonePGEComExCZ05 | Com-Iltg-dWatt-Exit | PGE | Com | Ex | CZ05 | 8.76 | 0.001 | 0 | 9.0749 | 0.0012894 | -0.074008 | 8.76 | 0.001 | 0 | 9.0749 | 0.0012894 | -0.074008 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.04 | 1.29 | -0.0084484 | 8760 | 1 | 8760 | 1 | 1.04 | 1.29 | -0.00845
ExitNonePGEComExCZ11 | Com-Iltg-dWatt-Exit | PGE | Com | Ex | CZ11 | 8.76 | 0.001 | 0 | 9.2269 | 0.0012539 | -0.06558 | 8.76 | 0.001 | 0 | 9.2269 | 0.0012539 | -0.06558 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.05 | 1.25 | -0.0074863 | 8760 | 1 | 8760 | 1 | 1.05 | 1.25 | -0.00749
ExitNonePGEComExCZ12 | Com-Iltg-dWatt-Exit | PGE | Com | Ex | CZ12 | 8.76 | 0.001 | 0 | 9.1548 | 0.00126 | -0.063179 | 8.76 | 0.001 | 0 | 9.1548 | 0.00126 | -0.063179 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.05 | 1.26 | -0.0072122 | 8760 | 1 | 8760 | 1 | 1.05 | 1.26 | -0.00721
ExitNonePGEComExCZ13 | Com-Iltg-dWatt-Exit | PGE | Com | Ex | CZ13 | 8.76 | 0.001 | 0 | 9.3593 | 0.001249 | -0.058219 | 8.76 | 0.001 | 0 | 9.3593 | 0.001249 | -0.058219 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.07 | 1.25 | -0.006646 | 8760 | 1 | 8760 | 1 | 1.07 | 1.25 | -0.00665
ExitNonePGEComExCZ16 | Com-Iltg-dWatt-Exit | PGE | Com | Ex | CZ16 | 8.76 | 0.001 | 0 | 8.5225 | 0.0011986 | -0.095825 | 8.76 | 0.001 | 0 | 8.5225 | 0.0011986 | -0.095825 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.973 | 1.2 | -0.010939 | 8760 | 1 | 8760 | 1 | 0.973 | 1.2 | -0.0109
ExitNonePGEComExIOU | Com-Iltg-dWatt-Exit | PGE | Com | Ex | IOU | 8.76 | 0.001 | 0 | 9.151 | 0.0012738 | -0.06506 | 8.76 | 0.001 | 0 | 9.151 | 0.0012738 | -0.06506 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.04 | 1.27 | -0.0074269 | 8760 | 1 | 8760 | 1 | 1.04 | 1.27 | -0.00743
ExitNonePGEComNewCZ05 | Com-Iltg-dWatt-Exit | PGE | Com | New | CZ05 | 8.76 | 0.001 | 0 | 8.918 | 0.0012849 | -0.08255 | 8.76 | 0.001 | 0 | 8.918 | 0.0012849 | -0.08255 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.02 | 1.28 | -0.0094235 | 8760 | 1 | 8760 | 1 | 1.02 | 1.28 | -0.00942
ExitNonePGEComNewCZ11 | Com-Iltg-dWatt-Exit | PGE | Com | New | CZ11 | 8.76 | 0.001 | 0 | 9.1573 | 0.0012568 | -0.064179 | 8.76 | 0.001 | 0 | 9.1573 | 0.0012568 | -0.064179 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.05 | 1.26 | -0.0073264 | 8760 | 1 | 8760 | 1 | 1.05 | 1.26 | -0.00733
ExitNonePGEComNewCZ12 | Com-Iltg-dWatt-Exit | PGE | Com | New | CZ12 | 8.76 | 0.001 | 0 | 9.1548 | 0.0012558 | -0.064312 | 8.76 | 0.001 | 0 | 9.1548 | 0.0012558 | -0.064312 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.05 | 1.26 | -0.0073416 | 8760 | 1 | 8760 | 1 | 1.05 | 1.26 | -0.00734
ExitNonePGEComNewCZ13 | Com-Iltg-dWatt-Exit | PGE | Com | New | CZ13 | 8.76 | 0.001 | 0 | 9.2471 | 0.0012536 | -0.060793 | 8.76 | 0.001 | 0 | 9.2471 | 0.0012536 | -0.060793 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.06 | 1.25 | -0.0069398 | 8760 | 1 | 8760 | 1 | 1.06 | 1.25 | -0.00694
ExitNonePGEComNewCZ16 | Com-Iltg-dWatt-Exit | PGE | Com | New | CZ16 | 8.76 | 0.001 | 0 | 8.462 | 0.0012113 | -0.093433 | 8.76 | 0.001 | 0 | 8.462 | 0.0012113 | -0.093433 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.966 | 1.21 | -0.010666 | 8760 | 1 | 8760 | 1 | 0.966 | 1.21 | -0.0107
ExitNonePGEComNewIOU | Com-Iltg-dWatt-Exit | PGE | Com | New | IOU | 8.76 | 0.001 | 0 | 9.09 | 0.0012692 | -0.067241 | 8.76 | 0.001 | 0 | 9.09 | 0.0012692 | -0.067241 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.04 | 1.27 | -0.0076759 | 8760 | 1 | 8760 | 1 | 1.04 | 1.27 | -0.00768
ExitNonePGEECCExCZ01 | Com-Iltg-dWatt-Exit | PGE | ECC | Ex | CZ01 | 8.76 | 0.001 | 0 | 8.25 | 0.00127 | -0.204 | 8.76 | 0.001 | 0 | 8.25 | 0.00127 | -0.204 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.942 | 1.27 | -0.023288 | 8760 | 1 | 8760 | 1 | 0.942 | 1.27 | -0.0233
ExitNonePGEECCExCZ02 | Com-Iltg-dWatt-Exit | PGE | ECC | Ex | CZ02 | 8.76 | 0.001 | 0 | 9.09 | 0.00143 | -0.115 | 8.76 | 0.001 | 0 | 9.09 | 0.00143 | -0.115 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.04 | 1.43 | -0.013128 | 8760 | 1 | 8760 | 1 | 1.04 | 1.43 | -0.0131
ExitNonePGEECCExCZ03 | Com-Iltg-dWatt-Exit | PGE | ECC | Ex | CZ03 | 8.76 | 0.001 | 0 | 9.01 | 0.00138 | -0.131 | 8.76 | 0.001 | 0 | 9.01 | 0.00138 | -0.131 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.03 | 1.38 | -0.014954 | 8760 | 1 | 8760 | 1 | 1.03 | 1.38 | -0.015
ExitNonePGEECCExCZ04 | Com-Iltg-dWatt-Exit | PGE | ECC | Ex | CZ04 | 8.76 | 0.001 | 0 | 9.22 | 0.00131 | -0.0981 | 8.76 | 0.001 | 0 | 9.22 | 0.00131 | -0.0981 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.05 | 1.31 | -0.011199 | 8760 | 1 | 8760 | 1 | 1.05 | 1.31 | -0.0112
ExitNonePGEECCExCZ05 | Com-Iltg-dWatt-Exit | PGE | ECC | Ex | CZ05 | 8.76 | 0.001 | 0 | 9.06 | 0.00143 | -0.124 | 8.76 | 0.001 | 0 | 9.06 | 0.00143 | -0.124 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.03 | 1.43 | -0.014155 | 8760 | 1 | 8760 | 1 | 1.03 | 1.43 | -0.0142
ExitNonePGEECCExCZ11 | Com-Iltg-dWatt-Exit | PGE | ECC | Ex | CZ11 | 8.76 | 0.001 | 0 | 9.3 | 0.00136 | -0.109 | 8.76 | 0.001 | 0 | 9.3 | 0.00136 | -0.109 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.06 | 1.36 | -0.012443 | 8760 | 1 | 8760 | 1 | 1.06 | 1.36 | -0.0124
ExitNonePGEECCExCZ12 | Com-Iltg-dWatt-Exit | PGE | ECC | Ex | CZ12 | 8.76 | 0.001 | 0 | 9.51 | 0.0015 | -0.0999 | 8.76 | 0.001 | 0 | 9.51 | 0.0015 | -0.0999 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.09 | 1.5 | -0.011404 | 8760 | 1 | 8760 | 1 | 1.09 | 1.5 | -0.0114
ExitNonePGEECCExCZ13 | Com-Iltg-dWatt-Exit | PGE | ECC | Ex | CZ13 | 8.76 | 0.001 | 0 | 9.5 | 0.00147 | -0.0946 | 8.76 | 0.001 | 0 | 9.5 | 0.00147 | -0.0946 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.08 | 1.47 | -0.010799 | 8760 | 1 | 8760 | 1 | 1.08 | 1.47 | -0.0108
ExitNonePGEECCExCZ16 | Com-Iltg-dWatt-Exit | PGE | ECC | Ex | CZ16 | 8.76 | 0.001 | 0 | 9.06 | 0.00126 | -0.165 | 8.76 | 0.001 | 0 | 9.06 | 0.00126 | -0.165 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.03 | 1.26 | -0.018836 | 8760 | 1 | 8760 | 1 | 1.03 | 1.26 | -0.0188
ExitNonePGEECCExIOU | Com-Iltg-dWatt-Exit | PGE | ECC | Ex | IOU | 8.76 | 0.001 | 0 | 9.17 | 0.0014 | -0.117 | 8.76 | 0.001 | 0 | 9.17 | 0.0014 | -0.117 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.05 | 1.4 | -0.013356 | 8760 | 1 | 8760 | 1 | 1.05 | 1.4 | -0.0134
ExitNonePGEECCNewCZ01 | Com-Iltg-dWatt-Exit | PGE | ECC | New | CZ01 | 8.76 | 0.001 | 0 | 8.61 | 0.00126 | -0.201 | 8.76 | 0.001 | 0 | 8.61 | 0.00126 | -0.201 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.983 | 1.26 | -0.022945 | 8760 | 1 | 8760 | 1 | 0.983 | 1.26 | -0.0229
ExitNonePGEECCNewCZ02 | Com-Iltg-dWatt-Exit | PGE | ECC | New | CZ02 | 8.76 | 0.001 | 0 | 9.17 | 0.00149 | -0.143 | 8.76 | 0.001 | 0 | 9.17 | 0.00149 | -0.143 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.05 | 1.49 | -0.016324 | 8760 | 1 | 8760 | 1 | 1.05 | 1.49 | -0.0163
ExitNonePGEECCNewCZ03 | Com-Iltg-dWatt-Exit | PGE | ECC | New | CZ03 | 8.76 | 0.001 | 0 | 9.04 | 0.00144 | -0.123 | 8.76 | 0.001 | 0 | 9.04 | 0.00144 | -0.123 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.03 | 1.44 | -0.014041 | 8760 | 1 | 8760 | 1 | 1.03 | 1.44 | -0.014
ExitNonePGEECCNewCZ04 | Com-Iltg-dWatt-Exit | PGE | ECC | New | CZ04 | 8.76 | 0.001 | 0 | 9.36 | 0.00143 | -0.0845 | 8.76 | 0.001 | 0 | 9.36 | 0.00143 | -0.0845 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.07 | 1.43 | -0.0096461 | 8760 | 1 | 8760 | 1 | 1.07 | 1.43 | -0.00965
ExitNonePGEECCNewCZ05 | Com-Iltg-dWatt-Exit | PGE | ECC | New | CZ05 | 8.76 | 0.001 | 0 | 9.01 | 0.00144 | -0.138 | 8.76 | 0.001 | 0 | 9.01 | 0.00144 | -0.138 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.03 | 1.44 | -0.015753 | 8760 | 1 | 8760 | 1 | 1.03 | 1.44 | -0.0158
ExitNonePGEECCNewCZ11 | Com-Iltg-dWatt-Exit | PGE | ECC | New | CZ11 | 8.76 | 0.001 | 0 | 9.47 | 0.00143 | -0.0803 | 8.76 | 0.001 | 0 | 9.47 | 0.00143 | -0.0803 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.08 | 1.43 | -0.0091667 | 8760 | 1 | 8760 | 1 | 1.08 | 1.43 | -0.00917
ExitNonePGEECCNewCZ12 | Com-Iltg-dWatt-Exit | PGE | ECC | New | CZ12 | 8.76 | 0.001 | 0 | 9.33 | 0.00149 | -0.126 | 8.76 | 0.001 | 0 | 9.33 | 0.00149 | -0.126 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.07 | 1.49 | -0.014384 | 8760 | 1 | 8760 | 1 | 1.07 | 1.49 | -0.0144
ExitNonePGEECCNewCZ13 | Com-Iltg-dWatt-Exit | PGE | ECC | New | CZ13 | 8.76 | 0.001 | 0 | 9.97 | 0.00145 | -0.0832 | 8.76 | 0.001 | 0 | 9.97 | 0.00145 | -0.0832 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.14 | 1.45 | -0.0094977 | 8760 | 1 | 8760 | 1 | 1.14 | 1.45 | -0.0095
ExitNonePGEECCNewCZ16 | Com-Iltg-dWatt-Exit | PGE | ECC | New | CZ16 | 8.76 | 0.001 | 0 | 9.23 | 0.0014 | -0.156 | 8.76 | 0.001 | 0 | 9.23 | 0.0014 | -0.156 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.05 | 1.4 | -0.017808 | 8760 | 1 | 8760 | 1 | 1.05 | 1.4 | -0.0178
ExitNonePGEECCNewIOU | Com-Iltg-dWatt-Exit | PGE | ECC | New | IOU | 8.76 | 0.001 | 0 | 9.33 | 0.00145 | -0.112 | 8.76 | 0.001 | 0 | 9.33 | 0.00145 | -0.112 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.07 | 1.45 | -0.012785 | 8760 | 1 | 8760 | 1 | 1.07 | 1.45 | -0.0128
ExitNonePGEEPrExCZ01 | Com-Iltg-dWatt-Exit | PGE | EPr | Ex | CZ01 | 8.76 | 0.001 | 0 | 8.26 | 0.00126 | -0.145 | 8.76 | 0.001 | 0 | 8.26 | 0.00126 | -0.145 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.943 | 1.26 | -0.016553 | 8760 | 1 | 8760 | 1 | 0.943 | 1.26 | -0.0166
ExitNonePGEEPrExCZ02 | Com-Iltg-dWatt-Exit | PGE | EPr | Ex | CZ02 | 8.76 | 0.001 | 0 | 8.8 | 0.001 | -0.0872 | 8.76 | 0.001 | 0 | 8.8 | 0.001 | -0.0872 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1 | 1 | -0.0099543 | 8760 | 1 | 8760 | 1 | 1 | 1 | -0.00995
ExitNonePGEEPrExCZ03 | Com-Iltg-dWatt-Exit | PGE | EPr | Ex | CZ03 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | -0.0872 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | -0.0872 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1 | 1 | -0.0099543 | 8760 | 1 | 8760 | 1 | 1 | 1 | -0.00995
ExitNonePGEEPrExCZ04 | Com-Iltg-dWatt-Exit | PGE | EPr | Ex | CZ04 | 8.76 | 0.001 | 0 | 9.02 | 0.00135 | -0.0703 | 8.76 | 0.001 | 0 | 9.02 | 0.00135 | -0.0703 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.03 | 1.35 | -0.0080251 | 8760 | 1 | 8760 | 1 | 1.03 | 1.35 | -0.00803
ExitNonePGEEPrExCZ05 | Com-Iltg-dWatt-Exit | PGE | EPr | Ex | CZ05 | 8.76 | 0.001 | 0 | 8.8 | 0.00136 | -0.0885 | 8.76 | 0.001 | 0 | 8.8 | 0.00136 | -0.0885 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1 | 1.36 | -0.010103 | 8760 | 1 | 8760 | 1 | 1 | 1.36 | -0.0101
ExitNonePGEEPrExCZ11 | Com-Iltg-dWatt-Exit | PGE | EPr | Ex | CZ11 | 8.76 | 0.001 | 0 | 9.38 | 0.001 | -0.08 | 8.76 | 0.001 | 0 | 9.38 | 0.001 | -0.08 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.07 | 1 | -0.0091324 | 8760 | 1 | 8760 | 1 | 1.07 | 1 | -0.00913
ExitNonePGEEPrExCZ12 | Com-Iltg-dWatt-Exit | PGE | EPr | Ex | CZ12 | 8.76 | 0.001 | 0 | 9.12 | 0.001 | -0.0853 | 8.76 | 0.001 | 0 | 9.12 | 0.001 | -0.0853 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.04 | 1 | -0.0097374 | 8760 | 1 | 8760 | 1 | 1.04 | 1 | -0.00974
ExitNonePGEEPrExCZ13 | Com-Iltg-dWatt-Exit | PGE | EPr | Ex | CZ13 | 8.76 | 0.001 | 0 | 9.49 | 0.001 | -0.0758 | 8.76 | 0.001 | 0 | 9.49 | 0.001 | -0.0758 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.08 | 1 | -0.008653 | 8760 | 1 | 8760 | 1 | 1.08 | 1 | -0.00865
ExitNonePGEEPrExCZ16 | Com-Iltg-dWatt-Exit | PGE | EPr | Ex | CZ16 | 8.76 | 0.001 | 0 | 8.28 | 0.001 | -0.145 | 8.76 | 0.001 | 0 | 8.28 | 0.001 | -0.145 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.945 | 1 | -0.016553 | 8760 | 1 | 8760 | 1 | 0.945 | 1 | -0.0166
ExitNonePGEEPrExIOU | Com-Iltg-dWatt-Exit | PGE | EPr | Ex | IOU | 8.76 | 0.001 | 0 | 9.03 | 0.00106 | -0.0831 | 8.76 | 0.001 | 0 | 9.03 | 0.00106 | -0.0831 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.03 | 1.06 | -0.0094863 | 8760 | 1 | 8760 | 1 | 1.03 | 1.06 | -0.00949
ExitNonePGEEPrNewCZ01 | Com-Iltg-dWatt-Exit | PGE | EPr | New | CZ01 | 8.76 | 0.001 | 0 | 8.32 | 0.0012 | -0.168 | 8.76 | 0.001 | 0 | 8.32 | 0.0012 | -0.168 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.95 | 1.2 | -0.019178 | 8760 | 1 | 8760 | 1 | 0.95 | 1.2 | -0.0192
ExitNonePGEEPrNewCZ02 | Com-Iltg-dWatt-Exit | PGE | EPr | New | CZ02 | 8.76 | 0.001 | 0 | 8.66 | 0.001 | -0.115 | 8.76 | 0.001 | 0 | 8.66 | 0.001 | -0.115 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.989 | 1 | -0.013128 | 8760 | 1 | 8760 | 1 | 0.989 | 1 | -0.0131
ExitNonePGEEPrNewCZ03 | Com-Iltg-dWatt-Exit | PGE | EPr | New | CZ03 | 8.76 | 0.001 | 0 | 8.65 | 0.001 | -0.113 | 8.76 | 0.001 | 0 | 8.65 | 0.001 | -0.113 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.987 | 1 | -0.0129 | 8760 | 1 | 8760 | 1 | 0.987 | 1 | -0.0129
ExitNonePGEEPrNewCZ04 | Com-Iltg-dWatt-Exit | PGE | EPr | New | CZ04 | 8.76 | 0.001 | 0 | 8.85 | 0.00139 | -0.0972 | 8.76 | 0.001 | 0 | 8.85 | 0.00139 | -0.0972 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.01 | 1.39 | -0.011096 | 8760 | 1 | 8760 | 1 | 1.01 | 1.39 | -0.0111
ExitNonePGEEPrNewCZ05 | Com-Iltg-dWatt-Exit | PGE | EPr | New | CZ05 | 8.76 | 0.001 | 0 | 8.67 | 0.00137 | -0.107 | 8.76 | 0.001 | 0 | 8.67 | 0.00137 | -0.107 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.99 | 1.37 | -0.012215 | 8760 | 1 | 8760 | 1 | 0.99 | 1.37 | -0.0122
ExitNonePGEEPrNewCZ11 | Com-Iltg-dWatt-Exit | PGE | EPr | New | CZ11 | 8.76 | 0.001 | 0 | 9.33 | 0.001 | -0.101 | 8.76 | 0.001 | 0 | 9.33 | 0.001 | -0.101 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.07 | 1 | -0.01153 | 8760 | 1 | 8760 | 1 | 1.07 | 1 | -0.0115
ExitNonePGEEPrNewCZ12 | Com-Iltg-dWatt-Exit | PGE | EPr | New | CZ12 | 8.76 | 0.001 | 0 | 9.02 | 0.001 | -0.107 | 8.76 | 0.001 | 0 | 9.02 | 0.001 | -0.107 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.03 | 1 | -0.012215 | 8760 | 1 | 8760 | 1 | 1.03 | 1 | -0.0122
ExitNonePGEEPrNewCZ13 | Com-Iltg-dWatt-Exit | PGE | EPr | New | CZ13 | 8.76 | 0.001 | 0 | 9.39 | 0.001 | -0.0955 | 8.76 | 0.001 | 0 | 9.39 | 0.001 | -0.0955 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.07 | 1 | -0.010902 | 8760 | 1 | 8760 | 1 | 1.07 | 1 | -0.0109
ExitNonePGEEPrNewCZ16 | Com-Iltg-dWatt-Exit | PGE | EPr | New | CZ16 | 8.76 | 0.001 | 0 | 8.31 | 0.001 | -0.159 | 8.76 | 0.001 | 0 | 8.31 | 0.001 | -0.159 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.949 | 1 | -0.018151 | 8760 | 1 | 8760 | 1 | 0.949 | 1 | -0.0182
ExitNonePGEEPrNewIOU | Com-Iltg-dWatt-Exit | PGE | EPr | New | IOU | 8.76 | 0.001 | 0 | 9.01 | 0.00105 | -0.105 | 8.76 | 0.001 | 0 | 9.01 | 0.00105 | -0.105 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.03 | 1.05 | -0.011986 | 8760 | 1 | 8760 | 1 | 1.03 | 1.05 | -0.012
ExitNonePGEERCExCZ01 | Com-Iltg-dWatt-Exit | PGE | ERC | Ex | CZ01 | 8.76 | 0.001 | 0 | 7.82 | 0.00116 | -0.185 | 8.76 | 0.001 | 0 | 7.82 | 0.00116 | -0.185 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.893 | 1.16 | -0.021119 | 8760 | 1 | 8760 | 1 | 0.893 | 1.16 | -0.0211
ExitNonePGEERCExCZ02 | Com-Iltg-dWatt-Exit | PGE | ERC | Ex | CZ02 | 8.76 | 0.001 | 0 | 8.31 | 0.001 | -0.126 | 8.76 | 0.001 | 0 | 8.31 | 0.001 | -0.126 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.949 | 1 | -0.014384 | 8760 | 1 | 8760 | 1 | 0.949 | 1 | -0.0144
ExitNonePGEERCExCZ03 | Com-Iltg-dWatt-Exit | PGE | ERC | Ex | CZ03 | 8.76 | 0.001 | 0 | 7.78 | 0.001 | -0.136 | 8.76 | 0.001 | 0 | 7.78 | 0.001 | -0.136 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.888 | 1 | -0.015525 | 8760 | 1 | 8760 | 1 | 0.888 | 1 | -0.0155
ExitNonePGEERCExCZ04 | Com-Iltg-dWatt-Exit | PGE | ERC | Ex | CZ04 | 8.76 | 0.001 | 0 | 8.42 | 0.00122 | -0.112 | 8.76 | 0.001 | 0 | 8.42 | 0.00122 | -0.112 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.961 | 1.22 | -0.012785 | 8760 | 1 | 8760 | 1 | 0.961 | 1.22 | -0.0128
ExitNonePGEERCExCZ05 | Com-Iltg-dWatt-Exit | PGE | ERC | Ex | CZ05 | 8.76 | 0.001 | 0 | 8.17 | 0.00118 | -0.144 | 8.76 | 0.001 | 0 | 8.17 | 0.00118 | -0.144 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.933 | 1.18 | -0.016438 | 8760 | 1 | 8760 | 1 | 0.933 | 1.18 | -0.0164
ExitNonePGEERCExCZ11 | Com-Iltg-dWatt-Exit | PGE | ERC | Ex | CZ11 | 8.76 | 0.001 | 0 | 8.95 | 0.001 | -0.103 | 8.76 | 0.001 | 0 | 8.95 | 0.001 | -0.103 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.02 | 1 | -0.011758 | 8760 | 1 | 8760 | 1 | 1.02 | 1 | -0.0118
ExitNonePGEERCExCZ12 | Com-Iltg-dWatt-Exit | PGE | ERC | Ex | CZ12 | 8.76 | 0.001 | 0 | 8.5 | 0.001 | -0.11 | 8.76 | 0.001 | 0 | 8.5 | 0.001 | -0.11 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.97 | 1 | -0.012557 | 8760 | 1 | 8760 | 1 | 0.97 | 1 | -0.0126
ExitNonePGEERCExCZ13 | Com-Iltg-dWatt-Exit | PGE | ERC | Ex | CZ13 | 8.76 | 0.001 | 0 | 8.81 | 0.001 | -0.0937 | 8.76 | 0.001 | 0 | 8.81 | 0.001 | -0.0937 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.01 | 1 | -0.010696 | 8760 | 1 | 8760 | 1 | 1.01 | 1 | -0.0107
ExitNonePGEERCExCZ16 | Com-Iltg-dWatt-Exit | PGE | ERC | Ex | CZ16 | 8.76 | 0.001 | 0 | 8.54 | 0.001 | -0.148 | 8.76 | 0.001 | 0 | 8.54 | 0.001 | -0.148 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.975 | 1 | -0.016895 | 8760 | 1 | 8760 | 1 | 0.975 | 1 | -0.0169
ExitNonePGEERCExIOU | Com-Iltg-dWatt-Exit | PGE | ERC | Ex | IOU | 8.76 | 0.001 | 0 | 8.33 | 0.00104 | -0.117 | 8.76 | 0.001 | 0 | 8.33 | 0.00104 | -0.117 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.951 | 1.04 | -0.013356 | 8760 | 1 | 8760 | 1 | 0.951 | 1.04 | -0.0134
ExitNonePGEERCNewCZ01 | Com-Iltg-dWatt-Exit | PGE | ERC | New | CZ01 | 8.76 | 0.001 | 0 | 8.1 | 0.00119 | -0.192 | 8.76 | 0.001 | 0 | 8.1 | 0.00119 | -0.192 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.925 | 1.19 | -0.021918 | 8760 | 1 | 8760 | 1 | 0.925 | 1.19 | -0.0219
ExitNonePGEERCNewCZ02 | Com-Iltg-dWatt-Exit | PGE | ERC | New | CZ02 | 8.76 | 0.001 | 0 | 8.37 | 0.001 | -0.121 | 8.76 | 0.001 | 0 | 8.37 | 0.001 | -0.121 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.955 | 1 | -0.013813 | 8760 | 1 | 8760 | 1 | 0.955 | 1 | -0.0138
ExitNonePGEERCNewCZ03 | Com-Iltg-dWatt-Exit | PGE | ERC | New | CZ03 | 8.76 | 0.001 | 0 | 8.31 | 0.001 | -0.115 | 8.76 | 0.001 | 0 | 8.31 | 0.001 | -0.115 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.949 | 1 | -0.013128 | 8760 | 1 | 8760 | 1 | 0.949 | 1 | -0.0131
ExitNonePGEERCNewCZ04 | Com-Iltg-dWatt-Exit | PGE | ERC | New | CZ04 | 8.76 | 0.001 | 0 | 8.68 | 0.00127 | -0.0999 | 8.76 | 0.001 | 0 | 8.68 | 0.00127 | -0.0999 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.991 | 1.27 | -0.011404 | 8760 | 1 | 8760 | 1 | 0.991 | 1.27 | -0.0114
ExitNonePGEERCNewCZ05 | Com-Iltg-dWatt-Exit | PGE | ERC | New | CZ05 | 8.76 | 0.001 | 0 | 8.43 | 0.00121 | -0.12 | 8.76 | 0.001 | 0 | 8.43 | 0.00121 | -0.12 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.962 | 1.21 | -0.013699 | 8760 | 1 | 8760 | 1 | 0.962 | 1.21 | -0.0137
ExitNonePGEERCNewCZ11 | Com-Iltg-dWatt-Exit | PGE | ERC | New | CZ11 | 8.76 | 0.001 | 0 | 9.01 | 0.001 | -0.104 | 8.76 | 0.001 | 0 | 9.01 | 0.001 | -0.104 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.03 | 1 | -0.011872 | 8760 | 1 | 8760 | 1 | 1.03 | 1 | -0.0119
ExitNonePGEERCNewCZ12 | Com-Iltg-dWatt-Exit | PGE | ERC | New | CZ12 | 8.76 | 0.001 | 0 | 8.96 | 0.001 | -0.107 | 8.76 | 0.001 | 0 | 8.96 | 0.001 | -0.107 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.02 | 1 | -0.012215 | 8760 | 1 | 8760 | 1 | 1.02 | 1 | -0.0122
ExitNonePGEERCNewCZ13 | Com-Iltg-dWatt-Exit | PGE | ERC | New | CZ13 | 8.76 | 0.001 | 0 | 9.28 | 0.001 | -0.0981 | 8.76 | 0.001 | 0 | 9.28 | 0.001 | -0.0981 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.06 | 1 | -0.011199 | 8760 | 1 | 8760 | 1 | 1.06 | 1 | -0.0112
ExitNonePGEERCNewCZ16 | Com-Iltg-dWatt-Exit | PGE | ERC | New | CZ16 | 8.76 | 0.001 | 0 | 8.42 | 0.001 | -0.158 | 8.76 | 0.001 | 0 | 8.42 | 0.001 | -0.158 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.961 | 1 | -0.018037 | 8760 | 1 | 8760 | 1 | 0.961 | 1 | -0.018
ExitNonePGEERCNewIOU | Com-Iltg-dWatt-Exit | PGE | ERC | New | IOU | 8.76 | 0.001 | 0 | 8.84 | 0.00104 | -0.108 | 8.76 | 0.001 | 0 | 8.84 | 0.00104 | -0.108 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.01 | 1.04 | -0.012329 | 8760 | 1 | 8760 | 1 | 1.01 | 1.04 | -0.0123
ExitNonePGEESeExCZ01 | Com-Iltg-dWatt-Exit | PGE | ESe | Ex | CZ01 | 8.76 | 0.001 | 0 | 8.3 | 0.00128 | -0.152 | 8.76 | 0.001 | 0 | 8.3 | 0.00128 | -0.152 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.947 | 1.28 | -0.017352 | 8760 | 1 | 8760 | 1 | 0.947 | 1.28 | -0.0174
ExitNonePGEESeExCZ02 | Com-Iltg-dWatt-Exit | PGE | ESe | Ex | CZ02 | 8.76 | 0.001 | 0 | 8.81 | 0.001 | -0.0999 | 8.76 | 0.001 | 0 | 8.81 | 0.001 | -0.0999 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.01 | 1 | -0.011404 | 8760 | 1 | 8760 | 1 | 1.01 | 1 | -0.0114
ExitNonePGEESeExCZ03 | Com-Iltg-dWatt-Exit | PGE | ESe | Ex | CZ03 | 8.76 | 0.001 | 0 | 8.7 | 0.001 | -0.102 | 8.76 | 0.001 | 0 | 8.7 | 0.001 | -0.102 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.993 | 1 | -0.011644 | 8760 | 1 | 8760 | 1 | 0.993 | 1 | -0.0116
ExitNonePGEESeExCZ04 | Com-Iltg-dWatt-Exit | PGE | ESe | Ex | CZ04 | 8.76 | 0.001 | 0 | 9.01 | 0.00133 | -0.0804 | 8.76 | 0.001 | 0 | 9.01 | 0.00133 | -0.0804 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.03 | 1.33 | -0.0091781 | 8760 | 1 | 8760 | 1 | 1.03 | 1.33 | -0.00918
ExitNonePGEESeExCZ05 | Com-Iltg-dWatt-Exit | PGE | ESe | Ex | CZ05 | 8.76 | 0.001 | 0 | 8.75 | 0.00134 | -0.0981 | 8.76 | 0.001 | 0 | 8.75 | 0.00134 | -0.0981 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.999 | 1.34 | -0.011199 | 8760 | 1 | 8760 | 1 | 0.999 | 1.34 | -0.0112
ExitNonePGEESeExCZ11 | Com-Iltg-dWatt-Exit | PGE | ESe | Ex | CZ11 | 8.76 | 0.001 | 0 | 9.59 | 0.001 | -0.0894 | 8.76 | 0.001 | 0 | 9.59 | 0.001 | -0.0894 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.09 | 1 | -0.010205 | 8760 | 1 | 8760 | 1 | 1.09 | 1 | -0.0102
ExitNonePGEESeExCZ12 | Com-Iltg-dWatt-Exit | PGE | ESe | Ex | CZ12 | 8.76 | 0.001 | 0 | 9.22 | 0.001 | -0.0955 | 8.76 | 0.001 | 0 | 9.22 | 0.001 | -0.0955 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.05 | 1 | -0.010902 | 8760 | 1 | 8760 | 1 | 1.05 | 1 | -0.0109
ExitNonePGEESeExCZ13 | Com-Iltg-dWatt-Exit | PGE | ESe | Ex | CZ13 | 8.76 | 0.001 | 0 | 9.61 | 0.001 | -0.0816 | 8.76 | 0.001 | 0 | 9.61 | 0.001 | -0.0816 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.1 | 1 | -0.0093151 | 8760 | 1 | 8760 | 1 | 1.1 | 1 | -0.00932
ExitNonePGEESeExCZ16 | Com-Iltg-dWatt-Exit | PGE | ESe | Ex | CZ16 | 8.76 | 0.001 | 0 | 8.58 | 0.001 | -0.137 | 8.76 | 0.001 | 0 | 8.58 | 0.001 | -0.137 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.979 | 1 | -0.015639 | 8760 | 1 | 8760 | 1 | 0.979 | 1 | -0.0156
ExitNonePGEESeExIOU | Com-Iltg-dWatt-Exit | PGE | ESe | Ex | IOU | 8.76 | 0.001 | 0 | 9.08 | 0.00106 | -0.0937 | 8.76 | 0.001 | 0 | 9.08 | 0.00106 | -0.0937 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.04 | 1.06 | -0.010696 | 8760 | 1 | 8760 | 1 | 1.04 | 1.06 | -0.0107
ExitNonePGEESeNewCZ01 | Com-Iltg-dWatt-Exit | PGE | ESe | New | CZ01 | 8.76 | 0.001 | 0 | 8.45 | 0.00121 | -0.149 | 8.76 | 0.001 | 0 | 8.45 | 0.00121 | -0.149 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.965 | 1.21 | -0.017009 | 8760 | 1 | 8760 | 1 | 0.965 | 1.21 | -0.017
ExitNonePGEESeNewCZ02 | Com-Iltg-dWatt-Exit | PGE | ESe | New | CZ02 | 8.76 | 0.001 | 0 | 8.74 | 0.001 | -0.116 | 8.76 | 0.001 | 0 | 8.74 | 0.001 | -0.116 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.998 | 1 | -0.013242 | 8760 | 1 | 8760 | 1 | 0.998 | 1 | -0.0132
ExitNonePGEESeNewCZ03 | Com-Iltg-dWatt-Exit | PGE | ESe | New | CZ03 | 8.76 | 0.001 | 0 | 8.73 | 0.001 | -0.116 | 8.76 | 0.001 | 0 | 8.73 | 0.001 | -0.116 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.997 | 1 | -0.013242 | 8760 | 1 | 8760 | 1 | 0.997 | 1 | -0.0132
ExitNonePGEESeNewCZ04 | Com-Iltg-dWatt-Exit | PGE | ESe | New | CZ04 | 8.76 | 0.001 | 0 | 8.98 | 0.00141 | -0.0955 | 8.76 | 0.001 | 0 | 8.98 | 0.00141 | -0.0955 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.03 | 1.41 | -0.010902 | 8760 | 1 | 8760 | 1 | 1.03 | 1.41 | -0.0109
ExitNonePGEESeNewCZ05 | Com-Iltg-dWatt-Exit | PGE | ESe | New | CZ05 | 8.76 | 0.001 | 0 | 8.71 | 0.00134 | -0.112 | 8.76 | 0.001 | 0 | 8.71 | 0.00134 | -0.112 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.994 | 1.34 | -0.012785 | 8760 | 1 | 8760 | 1 | 0.994 | 1.34 | -0.0128
ExitNonePGEESeNewCZ11 | Com-Iltg-dWatt-Exit | PGE | ESe | New | CZ11 | 8.76 | 0.001 | 0 | 9.55 | 0.001 | -0.104 | 8.76 | 0.001 | 0 | 9.55 | 0.001 | -0.104 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.09 | 1 | -0.011872 | 8760 | 1 | 8760 | 1 | 1.09 | 1 | -0.0119
ExitNonePGEESeNewCZ12 | Com-Iltg-dWatt-Exit | PGE | ESe | New | CZ12 | 8.76 | 0.001 | 0 | 9.15 | 0.001 | -0.11 | 8.76 | 0.001 | 0 | 9.15 | 0.001 | -0.11 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.04 | 1 | -0.012557 | 8760 | 1 | 8760 | 1 | 1.04 | 1 | -0.0126
ExitNonePGEESeNewCZ13 | Com-Iltg-dWatt-Exit | PGE | ESe | New | CZ13 | 8.76 | 0.001 | 0 | 9.56 | 0.001 | -0.0999 | 8.76 | 0.001 | 0 | 9.56 | 0.001 | -0.0999 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.09 | 1 | -0.011404 | 8760 | 1 | 8760 | 1 | 1.09 | 1 | -0.0114
ExitNonePGEESeNewCZ16 | Com-Iltg-dWatt-Exit | PGE | ESe | New | CZ16 | 8.76 | 0.001 | 0 | 8.59 | 0.001 | -0.134 | 8.76 | 0.001 | 0 | 8.59 | 0.001 | -0.134 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.981 | 1 | -0.015297 | 8760 | 1 | 8760 | 1 | 0.981 | 1 | -0.0153
ExitNonePGEESeNewIOU | Com-Iltg-dWatt-Exit | PGE | ESe | New | IOU | 8.76 | 0.001 | 0 | 9.15 | 0.00106 | -0.108 | 8.76 | 0.001 | 0 | 9.15 | 0.00106 | -0.108 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.04 | 1.06 | -0.012329 | 8760 | 1 | 8760 | 1 | 1.04 | 1.06 | -0.0123
ExitNonePGEEUnExCZ01 | Com-Iltg-dWatt-Exit | PGE | EUn | Ex | CZ01 | 8.76 | 0.001 | 0 | 8.62 | 0.00134 | -0.119 | 8.76 | 0.001 | 0 | 8.62 | 0.00134 | -0.119 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.984 | 1.34 | -0.013584 | 8760 | 1 | 8760 | 1 | 0.984 | 1.34 | -0.0136
ExitNonePGEEUnExCZ02 | Com-Iltg-dWatt-Exit | PGE | EUn | Ex | CZ02 | 8.76 | 0.001 | 0 | 9.27 | 0.00135 | -0.092 | 8.76 | 0.001 | 0 | 9.27 | 0.00135 | -0.092 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.06 | 1.35 | -0.010502 | 8760 | 1 | 8760 | 1 | 1.06 | 1.35 | -0.0105
ExitNonePGEEUnExCZ03 | Com-Iltg-dWatt-Exit | PGE | EUn | Ex | CZ03 | 8.76 | 0.001 | 0 | 9.32 | 0.00132 | -0.0858 | 8.76 | 0.001 | 0 | 9.32 | 0.00132 | -0.0858 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.06 | 1.32 | -0.0097945 | 8760 | 1 | 8760 | 1 | 1.06 | 1.32 | -0.00979
ExitNonePGEEUnExCZ04 | Com-Iltg-dWatt-Exit | PGE | EUn | Ex | CZ04 | 8.76 | 0.001 | 0 | 9.5 | 0.00141 | -0.0692 | 8.76 | 0.001 | 0 | 9.5 | 0.00141 | -0.0692 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.08 | 1.41 | -0.0078995 | 8760 | 1 | 8760 | 1 | 1.08 | 1.41 | -0.0079
ExitNonePGEEUnExCZ05 | Com-Iltg-dWatt-Exit | PGE | EUn | Ex | CZ05 | 8.76 | 0.001 | 0 | 9.29 | 0.00129 | -0.0813 | 8.76 | 0.001 | 0 | 9.29 | 0.00129 | -0.0813 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.06 | 1.29 | -0.0092808 | 8760 | 1 | 8760 | 1 | 1.06 | 1.29 | -0.00928
ExitNonePGEEUnExCZ11 | Com-Iltg-dWatt-Exit | PGE | EUn | Ex | CZ11 | 8.76 | 0.001 | 0 | 9.5 | 0.00142 | -0.0781 | 8.76 | 0.001 | 0 | 9.5 | 0.00142 | -0.0781 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.08 | 1.42 | -0.0089155 | 8760 | 1 | 8760 | 1 | 1.08 | 1.42 | -0.00892
ExitNonePGEEUnExCZ12 | Com-Iltg-dWatt-Exit | PGE | EUn | Ex | CZ12 | 8.76 | 0.001 | 0 | 9.38 | 0.00141 | -0.0803 | 8.76 | 0.001 | 0 | 9.38 | 0.00141 | -0.0803 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.07 | 1.41 | -0.0091667 | 8760 | 1 | 8760 | 1 | 1.07 | 1.41 | -0.00917
ExitNonePGEEUnExCZ13 | Com-Iltg-dWatt-Exit | PGE | EUn | Ex | CZ13 | 8.76 | 0.001 | 0 | 9.49 | 0.00142 | -0.0735 | 8.76 | 0.001 | 0 | 9.49 | 0.00142 | -0.0735 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.08 | 1.42 | -0.0083904 | 8760 | 1 | 8760 | 1 | 1.08 | 1.42 | -0.00839
ExitNonePGEEUnExCZ16 | Com-Iltg-dWatt-Exit | PGE | EUn | Ex | CZ16 | 8.76 | 0.001 | 0 | 8.98 | 0.00133 | -0.117 | 8.76 | 0.001 | 0 | 8.98 | 0.00133 | -0.117 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.03 | 1.33 | -0.013356 | 8760 | 1 | 8760 | 1 | 1.03 | 1.33 | -0.0134
ExitNonePGEEUnExIOU | Com-Iltg-dWatt-Exit | PGE | EUn | Ex | IOU | 8.76 | 0.001 | 0 | 9.36 | 0.00136 | -0.0824 | 8.76 | 0.001 | 0 | 9.36 | 0.00136 | -0.0824 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.07 | 1.36 | -0.0094064 | 8760 | 1 | 8760 | 1 | 1.07 | 1.36 | -0.00941
ExitNonePGEEUnNewCZ01 | Com-Iltg-dWatt-Exit | PGE | EUn | New | CZ01 | 8.76 | 0.001 | 0 | 8.96 | 0.00127 | -0.142 | 8.76 | 0.001 | 0 | 8.96 | 0.00127 | -0.142 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.02 | 1.27 | -0.01621 | 8760 | 1 | 8760 | 1 | 1.02 | 1.27 | -0.0162
ExitNonePGEEUnNewCZ02 | Com-Iltg-dWatt-Exit | PGE | EUn | New | CZ02 | 8.76 | 0.001 | 0 | 9.61 | 0.00137 | -0.0894 | 8.76 | 0.001 | 0 | 9.61 | 0.00137 | -0.0894 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.1 | 1.37 | -0.010205 | 8760 | 1 | 8760 | 1 | 1.1 | 1.37 | -0.0102
ExitNonePGEEUnNewCZ03 | Com-Iltg-dWatt-Exit | PGE | EUn | New | CZ03 | 8.76 | 0.001 | 0 | 9.44 | 0.00137 | -0.0835 | 8.76 | 0.001 | 0 | 9.44 | 0.00137 | -0.0835 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.08 | 1.37 | -0.009532 | 8760 | 1 | 8760 | 1 | 1.08 | 1.37 | -0.00953
ExitNonePGEEUnNewCZ04 | Com-Iltg-dWatt-Exit | PGE | EUn | New | CZ04 | 8.76 | 0.001 | 0 | 9.55 | 0.00137 | -0.0728 | 8.76 | 0.001 | 0 | 9.55 | 0.00137 | -0.0728 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.09 | 1.37 | -0.0083105 | 8760 | 1 | 8760 | 1 | 1.09 | 1.37 | -0.00831
ExitNonePGEEUnNewCZ05 | Com-Iltg-dWatt-Exit | PGE | EUn | New | CZ05 | 8.76 | 0.001 | 0 | 9.26 | 0.00133 | -0.0964 | 8.76 | 0.001 | 0 | 9.26 | 0.00133 | -0.0964 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.06 | 1.33 | -0.011005 | 8760 | 1 | 8760 | 1 | 1.06 | 1.33 | -0.011
ExitNonePGEEUnNewCZ11 | Com-Iltg-dWatt-Exit | PGE | EUn | New | CZ11 | 8.76 | 0.001 | 0 | 9.91 | 0.00138 | -0.0937 | 8.76 | 0.001 | 0 | 9.91 | 0.00138 | -0.0937 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.13 | 1.38 | -0.010696 | 8760 | 1 | 8760 | 1 | 1.13 | 1.38 | -0.0107
ExitNonePGEEUnNewCZ12 | Com-Iltg-dWatt-Exit | PGE | EUn | New | CZ12 | 8.76 | 0.001 | 0 | 9.87 | 0.00139 | -0.0946 | 8.76 | 0.001 | 0 | 9.87 | 0.00139 | -0.0946 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.13 | 1.39 | -0.010799 | 8760 | 1 | 8760 | 1 | 1.13 | 1.39 | -0.0108
ExitNonePGEEUnNewCZ13 | Com-Iltg-dWatt-Exit | PGE | EUn | New | CZ13 | 8.76 | 0.001 | 0 | 9.58 | 0.00139 | -0.0858 | 8.76 | 0.001 | 0 | 9.58 | 0.00139 | -0.0858 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.09 | 1.39 | -0.0097945 | 8760 | 1 | 8760 | 1 | 1.09 | 1.39 | -0.00979
ExitNonePGEEUnNewCZ16 | Com-Iltg-dWatt-Exit | PGE | EUn | New | CZ16 | 8.76 | 0.001 | 0 | 9.25 | 0.00133 | -0.115 | 8.76 | 0.001 | 0 | 9.25 | 0.00133 | -0.115 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.06 | 1.33 | -0.013128 | 8760 | 1 | 8760 | 1 | 1.06 | 1.33 | -0.0131
ExitNonePGEEUnNewIOU | Com-Iltg-dWatt-Exit | PGE | EUn | New | IOU | 8.76 | 0.001 | 0 | 9.59 | 0.00137 | -0.0885 | 8.76 | 0.001 | 0 | 9.59 | 0.00137 | -0.0885 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.09 | 1.37 | -0.010103 | 8760 | 1 | 8760 | 1 | 1.09 | 1.37 | -0.0101
ExitNonePGEGroExCZ01 | Com-Iltg-dWatt-Exit | PGE | Gro | Ex | CZ01 | 8.76 | 0.001 | 0 | 7.27 | 0.000911 | -0.146 | 8.76 | 0.001 | 0 | 7.27 | 0.000911 | -0.146 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.83 | 0.911 | -0.016667 | 8760 | 1 | 8760 | 1 | 0.83 | 0.911 | -0.0167
ExitNonePGEGroExCZ02 | Com-Iltg-dWatt-Exit | PGE | Gro | Ex | CZ02 | 8.76 | 0.001 | 0 | 8.03 | 0.00133 | -0.116 | 8.76 | 0.001 | 0 | 8.03 | 0.00133 | -0.116 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.917 | 1.33 | -0.013242 | 8760 | 1 | 8760 | 1 | 0.917 | 1.33 | -0.0132
ExitNonePGEGroExCZ03 | Com-Iltg-dWatt-Exit | PGE | Gro | Ex | CZ03 | 8.76 | 0.001 | 0 | 7.71 | 0.00135 | -0.131 | 8.76 | 0.001 | 0 | 7.71 | 0.00135 | -0.131 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.88 | 1.35 | -0.014954 | 8760 | 1 | 8760 | 1 | 0.88 | 1.35 | -0.015
ExitNonePGEGroExCZ04 | Com-Iltg-dWatt-Exit | PGE | Gro | Ex | CZ04 | 8.76 | 0.001 | 0 | 8.16 | 0.00128 | -0.11 | 8.76 | 0.001 | 0 | 8.16 | 0.00128 | -0.11 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.932 | 1.28 | -0.012557 | 8760 | 1 | 8760 | 1 | 0.932 | 1.28 | -0.0126
ExitNonePGEGroExCZ05 | Com-Iltg-dWatt-Exit | PGE | Gro | Ex | CZ05 | 8.76 | 0.001 | 0 | 7.67 | 0.00125 | -0.131 | 8.76 | 0.001 | 0 | 7.67 | 0.00125 | -0.131 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.876 | 1.25 | -0.014954 | 8760 | 1 | 8760 | 1 | 0.876 | 1.25 | -0.015
ExitNonePGEGroExCZ11 | Com-Iltg-dWatt-Exit | PGE | Gro | Ex | CZ11 | 8.76 | 0.001 | 0 | 8.67 | 0.00131 | -0.0929 | 8.76 | 0.001 | 0 | 8.67 | 0.00131 | -0.0929 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.99 | 1.31 | -0.010605 | 8760 | 1 | 8760 | 1 | 0.99 | 1.31 | -0.0106
ExitNonePGEGroExCZ12 | Com-Iltg-dWatt-Exit | PGE | Gro | Ex | CZ12 | 8.76 | 0.001 | 0 | 8.5 | 0.00129 | -0.102 | 8.76 | 0.001 | 0 | 8.5 | 0.00129 | -0.102 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.97 | 1.29 | -0.011644 | 8760 | 1 | 8760 | 1 | 0.97 | 1.29 | -0.0116
ExitNonePGEGroExCZ13 | Com-Iltg-dWatt-Exit | PGE | Gro | Ex | CZ13 | 8.76 | 0.001 | 0 | 8.74 | 0.00132 | -0.0929 | 8.76 | 0.001 | 0 | 8.74 | 0.00132 | -0.0929 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.998 | 1.32 | -0.010605 | 8760 | 1 | 8760 | 1 | 0.998 | 1.32 | -0.0106
ExitNonePGEGroExCZ16 | Com-Iltg-dWatt-Exit | PGE | Gro | Ex | CZ16 | 8.76 | 0.001 | 0 | 7.73 | 0.00126 | -0.122 | 8.76 | 0.001 | 0 | 7.73 | 0.00126 | -0.122 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.882 | 1.26 | -0.013927 | 8760 | 1 | 8760 | 1 | 0.882 | 1.26 | -0.0139
ExitNonePGEGroExIOU | Com-Iltg-dWatt-Exit | PGE | Gro | Ex | IOU | 8.76 | 0.001 | 0 | 8.21 | 0.00131 | -0.111 | 8.76 | 0.001 | 0 | 8.21 | 0.00131 | -0.111 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.937 | 1.31 | -0.012671 | 8760 | 1 | 8760 | 1 | 0.937 | 1.31 | -0.0127
ExitNonePGEGroNewCZ01 | Com-Iltg-dWatt-Exit | PGE | Gro | New | CZ01 | 8.76 | 0.001 | 0 | 7.24 | 0.000978 | -0.161 | 8.76 | 0.001 | 0 | 7.24 | 0.000978 | -0.161 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.826 | 0.978 | -0.018379 | 8760 | 1 | 8760 | 1 | 0.826 | 0.978 | -0.0184
ExitNonePGEGroNewCZ02 | Com-Iltg-dWatt-Exit | PGE | Gro | New | CZ02 | 8.76 | 0.001 | 0 | 8.17 | 0.00157 | -0.121 | 8.76 | 0.001 | 0 | 8.17 | 0.00157 | -0.121 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.933 | 1.57 | -0.013813 | 8760 | 1 | 8760 | 1 | 0.933 | 1.57 | -0.0138
ExitNonePGEGroNewCZ03 | Com-Iltg-dWatt-Exit | PGE | Gro | New | CZ03 | 8.76 | 0.001 | 0 | 7.75 | 0.00146 | -0.138 | 8.76 | 0.001 | 0 | 7.75 | 0.00146 | -0.138 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.885 | 1.46 | -0.015753 | 8760 | 1 | 8760 | 1 | 0.885 | 1.46 | -0.0158
ExitNonePGEGroNewCZ04 | Com-Iltg-dWatt-Exit | PGE | Gro | New | CZ04 | 8.76 | 0.001 | 0 | 8.46 | 0.00132 | -0.114 | 8.76 | 0.001 | 0 | 8.46 | 0.00132 | -0.114 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.966 | 1.32 | -0.013014 | 8760 | 1 | 8760 | 1 | 0.966 | 1.32 | -0.013
ExitNonePGEGroNewCZ05 | Com-Iltg-dWatt-Exit | PGE | Gro | New | CZ05 | 8.76 | 0.001 | 0 | 7.8 | 0.00124 | -0.134 | 8.76 | 0.001 | 0 | 7.8 | 0.00124 | -0.134 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.89 | 1.24 | -0.015297 | 8760 | 1 | 8760 | 1 | 0.89 | 1.24 | -0.0153
ExitNonePGEGroNewCZ11 | Com-Iltg-dWatt-Exit | PGE | Gro | New | CZ11 | 8.76 | 0.001 | 0 | 8.87 | 0.0014 | -0.0937 | 8.76 | 0.001 | 0 | 8.87 | 0.0014 | -0.0937 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.01 | 1.4 | -0.010696 | 8760 | 1 | 8760 | 1 | 1.01 | 1.4 | -0.0107
ExitNonePGEGroNewCZ12 | Com-Iltg-dWatt-Exit | PGE | Gro | New | CZ12 | 8.76 | 0.001 | 0 | 8.67 | 0.00134 | -0.102 | 8.76 | 0.001 | 0 | 8.67 | 0.00134 | -0.102 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.99 | 1.34 | -0.011644 | 8760 | 1 | 8760 | 1 | 0.99 | 1.34 | -0.0116
ExitNonePGEGroNewCZ13 | Com-Iltg-dWatt-Exit | PGE | Gro | New | CZ13 | 8.76 | 0.001 | 0 | 8.96 | 0.00137 | -0.0964 | 8.76 | 0.001 | 0 | 8.96 | 0.00137 | -0.0964 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.02 | 1.37 | -0.011005 | 8760 | 1 | 8760 | 1 | 1.02 | 1.37 | -0.011
ExitNonePGEGroNewCZ16 | Com-Iltg-dWatt-Exit | PGE | Gro | New | CZ16 | 8.76 | 0.001 | 0 | 7.95 | 0.00139 | -0.118 | 8.76 | 0.001 | 0 | 7.95 | 0.00139 | -0.118 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.908 | 1.39 | -0.01347 | 8760 | 1 | 8760 | 1 | 0.908 | 1.39 | -0.0135
ExitNonePGEGroNewIOU | Com-Iltg-dWatt-Exit | PGE | Gro | New | IOU | 8.76 | 0.001 | 0 | 8.46 | 0.00139 | -0.111 | 8.76 | 0.001 | 0 | 8.46 | 0.00139 | -0.111 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.966 | 1.39 | -0.012671 | 8760 | 1 | 8760 | 1 | 0.966 | 1.39 | -0.0127
ExitNonePGEHspExCZ01 | Com-Iltg-dWatt-Exit | PGE | Hsp | Ex | CZ01 | 8.76 | 0.001 | 0 | 9.16 | 0.00117 | -0.102 | 8.76 | 0.001 | 0 | 9.16 | 0.00117 | -0.102 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.05 | 1.17 | -0.011644 | 8760 | 1 | 8760 | 1 | 1.05 | 1.17 | -0.0116
ExitNonePGEHspExCZ02 | Com-Iltg-dWatt-Exit | PGE | Hsp | Ex | CZ02 | 8.76 | 0.001 | 0 | 9.5 | 0.00126 | -0.0794 | 8.76 | 0.001 | 0 | 9.5 | 0.00126 | -0.0794 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.08 | 1.26 | -0.0090639 | 8760 | 1 | 8760 | 1 | 1.08 | 1.26 | -0.00906
ExitNonePGEHspExCZ03 | Com-Iltg-dWatt-Exit | PGE | Hsp | Ex | CZ03 | 8.76 | 0.001 | 0 | 9.57 | 0.00123 | -0.0767 | 8.76 | 0.001 | 0 | 9.57 | 0.00123 | -0.0767 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.09 | 1.23 | -0.0087557 | 8760 | 1 | 8760 | 1 | 1.09 | 1.23 | -0.00876
ExitNonePGEHspExCZ04 | Com-Iltg-dWatt-Exit | PGE | Hsp | Ex | CZ04 | 8.76 | 0.001 | 0 | 9.55 | 0.00125 | -0.0721 | 8.76 | 0.001 | 0 | 9.55 | 0.00125 | -0.0721 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.09 | 1.25 | -0.0082306 | 8760 | 1 | 8760 | 1 | 1.09 | 1.25 | -0.00823
ExitNonePGEHspExCZ05 | Com-Iltg-dWatt-Exit | PGE | Hsp | Ex | CZ05 | 8.76 | 0.001 | 0 | 9.41 | 0.00121 | -0.0822 | 8.76 | 0.001 | 0 | 9.41 | 0.00121 | -0.0822 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.07 | 1.21 | -0.0093836 | 8760 | 1 | 8760 | 1 | 1.07 | 1.21 | -0.00938
ExitNonePGEHspExCZ11 | Com-Iltg-dWatt-Exit | PGE | Hsp | Ex | CZ11 | 8.76 | 0.001 | 0 | 9.64 | 0.00125 | -0.0738 | 8.76 | 0.001 | 0 | 9.64 | 0.00125 | -0.0738 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.1 | 1.25 | -0.0084247 | 8760 | 1 | 8760 | 1 | 1.1 | 1.25 | -0.00842
ExitNonePGEHspExCZ12 | Com-Iltg-dWatt-Exit | PGE | Hsp | Ex | CZ12 | 8.76 | 0.001 | 0 | 9.61 | 0.00126 | -0.0713 | 8.76 | 0.001 | 0 | 9.61 | 0.00126 | -0.0713 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.1 | 1.26 | -0.0081393 | 8760 | 1 | 8760 | 1 | 1.1 | 1.26 | -0.00814
ExitNonePGEHspExCZ13 | Com-Iltg-dWatt-Exit | PGE | Hsp | Ex | CZ13 | 8.76 | 0.001 | 0 | 9.67 | 0.00126 | -0.0685 | 8.76 | 0.001 | 0 | 9.67 | 0.00126 | -0.0685 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.1 | 1.26 | -0.0078196 | 8760 | 1 | 8760 | 1 | 1.1 | 1.26 | -0.00782
ExitNonePGEHspExCZ16 | Com-Iltg-dWatt-Exit | PGE | Hsp | Ex | CZ16 | 8.76 | 0.001 | 0 | 9.05 | 0.00121 | -0.107 | 8.76 | 0.001 | 0 | 9.05 | 0.00121 | -0.107 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.03 | 1.21 | -0.012215 | 8760 | 1 | 8760 | 1 | 1.03 | 1.21 | -0.0122
ExitNonePGEHspExIOU | Com-Iltg-dWatt-Exit | PGE | Hsp | Ex | IOU | 8.76 | 0.001 | 0 | 9.58 | 0.00125 | -0.0742 | 8.76 | 0.001 | 0 | 9.58 | 0.00125 | -0.0742 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.09 | 1.25 | -0.0084703 | 8760 | 1 | 8760 | 1 | 1.09 | 1.25 | -0.00847
ExitNonePGEHspNewCZ01 | Com-Iltg-dWatt-Exit | PGE | Hsp | New | CZ01 | 8.76 | 0.001 | 0 | 8.74 | 0.00111 | -0.115 | 8.76 | 0.001 | 0 | 8.74 | 0.00111 | -0.115 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.998 | 1.11 | -0.013128 | 8760 | 1 | 8760 | 1 | 0.998 | 1.11 | -0.0131
ExitNonePGEHspNewCZ02 | Com-Iltg-dWatt-Exit | PGE | Hsp | New | CZ02 | 8.76 | 0.001 | 0 | 9.12 | 0.00122 | -0.092 | 8.76 | 0.001 | 0 | 9.12 | 0.00122 | -0.092 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.04 | 1.22 | -0.010502 | 8760 | 1 | 8760 | 1 | 1.04 | 1.22 | -0.0105
ExitNonePGEHspNewCZ03 | Com-Iltg-dWatt-Exit | PGE | Hsp | New | CZ03 | 8.76 | 0.001 | 0 | 9.12 | 0.00119 | -0.0813 | 8.76 | 0.001 | 0 | 9.12 | 0.00119 | -0.0813 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.04 | 1.19 | -0.0092808 | 8760 | 1 | 8760 | 1 | 1.04 | 1.19 | -0.00928
ExitNonePGEHspNewCZ04 | Com-Iltg-dWatt-Exit | PGE | Hsp | New | CZ04 | 8.76 | 0.001 | 0 | 9.25 | 0.00121 | -0.0788 | 8.76 | 0.001 | 0 | 9.25 | 0.00121 | -0.0788 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.06 | 1.21 | -0.0089954 | 8760 | 1 | 8760 | 1 | 1.06 | 1.21 | -0.009
ExitNonePGEHspNewCZ05 | Com-Iltg-dWatt-Exit | PGE | Hsp | New | CZ05 | 8.76 | 0.001 | 0 | 9.01 | 0.00117 | -0.0929 | 8.76 | 0.001 | 0 | 9.01 | 0.00117 | -0.0929 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.03 | 1.17 | -0.010605 | 8760 | 1 | 8760 | 1 | 1.03 | 1.17 | -0.0106
ExitNonePGEHspNewCZ11 | Com-Iltg-dWatt-Exit | PGE | Hsp | New | CZ11 | 8.76 | 0.001 | 0 | 9.38 | 0.00122 | -0.0828 | 8.76 | 0.001 | 0 | 9.38 | 0.00122 | -0.0828 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.07 | 1.22 | -0.0094521 | 8760 | 1 | 8760 | 1 | 1.07 | 1.22 | -0.00945
ExitNonePGEHspNewCZ12 | Com-Iltg-dWatt-Exit | PGE | Hsp | New | CZ12 | 8.76 | 0.001 | 0 | 9.22 | 0.00122 | -0.0788 | 8.76 | 0.001 | 0 | 9.22 | 0.00122 | -0.0788 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.05 | 1.22 | -0.0089954 | 8760 | 1 | 8760 | 1 | 1.05 | 1.22 | -0.009
ExitNonePGEHspNewCZ13 | Com-Iltg-dWatt-Exit | PGE | Hsp | New | CZ13 | 8.76 | 0.001 | 0 | 9.38 | 0.00125 | -0.0762 | 8.76 | 0.001 | 0 | 9.38 | 0.00125 | -0.0762 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.07 | 1.25 | -0.0086986 | 8760 | 1 | 8760 | 1 | 1.07 | 1.25 | -0.0087
ExitNonePGEHspNewCZ16 | Com-Iltg-dWatt-Exit | PGE | Hsp | New | CZ16 | 8.76 | 0.001 | 0 | 8.64 | 0.00118 | -0.12 | 8.76 | 0.001 | 0 | 8.64 | 0.00118 | -0.12 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.986 | 1.18 | -0.013699 | 8760 | 1 | 8760 | 1 | 0.986 | 1.18 | -0.0137
ExitNonePGEHspNewIOU | Com-Iltg-dWatt-Exit | PGE | Hsp | New | IOU | 8.76 | 0.001 | 0 | 9.22 | 0.00122 | -0.0811 | 8.76 | 0.001 | 0 | 9.22 | 0.00122 | -0.0811 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.05 | 1.22 | -0.009258 | 8760 | 1 | 8760 | 1 | 1.05 | 1.22 | -0.00926
ExitNonePGEHtlExCZ01 | Com-Iltg-dWatt-Exit | PGE | Htl | Ex | CZ01 | 8.76 | 0.001 | 0 | 8.27 | 0.00121 | -0.0611 | 8.76 | 0.001 | 0 | 8.27 | 0.00121 | -0.0611 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.944 | 1.21 | -0.0069749 | 8760 | 1 | 8760 | 1 | 0.944 | 1.21 | -0.00697
ExitNonePGEHtlExCZ02 | Com-Iltg-dWatt-Exit | PGE | Htl | Ex | CZ02 | 8.76 | 0.001 | 0 | 8.83 | 0.00125 | -0.045 | 8.76 | 0.001 | 0 | 8.83 | 0.00125 | -0.045 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.01 | 1.25 | -0.005137 | 8760 | 1 | 8760 | 1 | 1.01 | 1.25 | -0.00514
ExitNonePGEHtlExCZ03 | Com-Iltg-dWatt-Exit | PGE | Htl | Ex | CZ03 | 8.76 | 0.001 | 0 | 8.97 | 0.00124 | -0.0427 | 8.76 | 0.001 | 0 | 8.97 | 0.00124 | -0.0427 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.02 | 1.24 | -0.0048744 | 8760 | 1 | 8760 | 1 | 1.02 | 1.24 | -0.00487
ExitNonePGEHtlExCZ04 | Com-Iltg-dWatt-Exit | PGE | Htl | Ex | CZ04 | 8.76 | 0.001 | 0 | 9.08 | 0.00125 | -0.0378 | 8.76 | 0.001 | 0 | 9.08 | 0.00125 | -0.0378 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.04 | 1.25 | -0.0043151 | 8760 | 1 | 8760 | 1 | 1.04 | 1.25 | -0.00432
ExitNonePGEHtlExCZ05 | Com-Iltg-dWatt-Exit | PGE | Htl | Ex | CZ05 | 8.76 | 0.001 | 0 | 8.81 | 0.00123 | -0.0453 | 8.76 | 0.001 | 0 | 8.81 | 0.00123 | -0.0453 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.01 | 1.23 | -0.0051712 | 8760 | 1 | 8760 | 1 | 1.01 | 1.23 | -0.00517
ExitNonePGEHtlExCZ11 | Com-Iltg-dWatt-Exit | PGE | Htl | Ex | CZ11 | 8.76 | 0.001 | 0 | 9.14 | 0.00127 | -0.0382 | 8.76 | 0.001 | 0 | 9.14 | 0.00127 | -0.0382 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.04 | 1.27 | -0.0043607 | 8760 | 1 | 8760 | 1 | 1.04 | 1.27 | -0.00436
ExitNonePGEHtlExCZ12 | Com-Iltg-dWatt-Exit | PGE | Htl | Ex | CZ12 | 8.76 | 0.001 | 0 | 9.02 | 0.00127 | -0.0393 | 8.76 | 0.001 | 0 | 9.02 | 0.00127 | -0.0393 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.03 | 1.27 | -0.0044863 | 8760 | 1 | 8760 | 1 | 1.03 | 1.27 | -0.00449
ExitNonePGEHtlExCZ13 | Com-Iltg-dWatt-Exit | PGE | Htl | Ex | CZ13 | 8.76 | 0.001 | 0 | 9.29 | 0.00127 | -0.0343 | 8.76 | 0.001 | 0 | 9.29 | 0.00127 | -0.0343 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.06 | 1.27 | -0.0039155 | 8760 | 1 | 8760 | 1 | 1.06 | 1.27 | -0.00392
ExitNonePGEHtlExCZ16 | Com-Iltg-dWatt-Exit | PGE | Htl | Ex | CZ16 | 8.76 | 0.001 | 0 | 8.3 | 0.00122 | -0.0684 | 8.76 | 0.001 | 0 | 8.3 | 0.00122 | -0.0684 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.947 | 1.22 | -0.0078082 | 8760 | 1 | 8760 | 1 | 0.947 | 1.22 | -0.00781
ExitNonePGEHtlExIOU | Com-Iltg-dWatt-Exit | PGE | Htl | Ex | IOU | 8.76 | 0.001 | 0 | 8.99 | 0.00125 | -0.0417 | 8.76 | 0.001 | 0 | 8.99 | 0.00125 | -0.0417 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.03 | 1.25 | -0.0047603 | 8760 | 1 | 8760 | 1 | 1.03 | 1.25 | -0.00476
ExitNonePGEHtlNewCZ01 | Com-Iltg-dWatt-Exit | PGE | Htl | New | CZ01 | 8.76 | 0.001 | 0 | 7.7 | 0.00117 | -0.0821 | 8.76 | 0.001 | 0 | 7.7 | 0.00117 | -0.0821 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.879 | 1.17 | -0.0093721 | 8760 | 1 | 8760 | 1 | 0.879 | 1.17 | -0.00937
ExitNonePGEHtlNewCZ02 | Com-Iltg-dWatt-Exit | PGE | Htl | New | CZ02 | 8.76 | 0.001 | 0 | 8.42 | 0.0013 | -0.0678 | 8.76 | 0.001 | 0 | 8.42 | 0.0013 | -0.0678 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.961 | 1.3 | -0.0077397 | 8760 | 1 | 8760 | 1 | 0.961 | 1.3 | -0.00774
ExitNonePGEHtlNewCZ03 | Com-Iltg-dWatt-Exit | PGE | Htl | New | CZ03 | 8.76 | 0.001 | 0 | 8.44 | 0.00125 | -0.0607 | 8.76 | 0.001 | 0 | 8.44 | 0.00125 | -0.0607 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.963 | 1.25 | -0.0069292 | 8760 | 1 | 8760 | 1 | 0.963 | 1.25 | -0.00693
ExitNonePGEHtlNewCZ04 | Com-Iltg-dWatt-Exit | PGE | Htl | New | CZ04 | 8.76 | 0.001 | 0 | 8.69 | 0.00127 | -0.0571 | 8.76 | 0.001 | 0 | 8.69 | 0.00127 | -0.0571 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.992 | 1.27 | -0.0065183 | 8760 | 1 | 8760 | 1 | 0.992 | 1.27 | -0.00652
ExitNonePGEHtlNewCZ05 | Com-Iltg-dWatt-Exit | PGE | Htl | New | CZ05 | 8.76 | 0.001 | 0 | 8.42 | 0.00124 | -0.0631 | 8.76 | 0.001 | 0 | 8.42 | 0.00124 | -0.0631 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.961 | 1.24 | -0.0072032 | 8760 | 1 | 8760 | 1 | 0.961 | 1.24 | -0.0072
ExitNonePGEHtlNewCZ11 | Com-Iltg-dWatt-Exit | PGE | Htl | New | CZ11 | 8.76 | 0.001 | 0 | 8.87 | 0.00129 | -0.0682 | 8.76 | 0.001 | 0 | 8.87 | 0.00129 | -0.0682 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.01 | 1.29 | -0.0077854 | 8760 | 1 | 8760 | 1 | 1.01 | 1.29 | -0.00779
ExitNonePGEHtlNewCZ12 | Com-Iltg-dWatt-Exit | PGE | Htl | New | CZ12 | 8.76 | 0.001 | 0 | 8.79 | 0.00129 | -0.0571 | 8.76 | 0.001 | 0 | 8.79 | 0.00129 | -0.0571 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1 | 1.29 | -0.0065183 | 8760 | 1 | 8760 | 1 | 1 | 1.29 | -0.00652
ExitNonePGEHtlNewCZ13 | Com-Iltg-dWatt-Exit | PGE | Htl | New | CZ13 | 8.76 | 0.001 | 0 | 8.94 | 0.00132 | -0.0525 | 8.76 | 0.001 | 0 | 8.94 | 0.00132 | -0.0525 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.02 | 1.32 | -0.0059932 | 8760 | 1 | 8760 | 1 | 1.02 | 1.32 | -0.00599
ExitNonePGEHtlNewCZ16 | Com-Iltg-dWatt-Exit | PGE | Htl | New | CZ16 | 8.76 | 0.001 | 0 | 8.1 | 0.00123 | -0.0857 | 8.76 | 0.001 | 0 | 8.1 | 0.00123 | -0.0857 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.925 | 1.23 | -0.0097831 | 8760 | 1 | 8760 | 1 | 0.925 | 1.23 | -0.00978
ExitNonePGEHtlNewIOU | Com-Iltg-dWatt-Exit | PGE | Htl | New | IOU | 8.76 | 0.001 | 0 | 8.62 | 0.00127 | -0.0604 | 8.76 | 0.001 | 0 | 8.62 | 0.00127 | -0.0604 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.984 | 1.27 | -0.006895 | 8760 | 1 | 8760 | 1 | 0.984 | 1.27 | -0.0069
ExitNonePGEMBTExCZ01 | Com-Iltg-dWatt-Exit | PGE | MBT | Ex | CZ01 | 8.76 | 0.001 | 0 | 9.4 | 0.00129 | -0.0166 | 8.76 | 0.001 | 0 | 9.4 | 0.00129 | -0.0166 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.07 | 1.29 | -0.001895 | 8760 | 1 | 8760 | 1 | 1.07 | 1.29 | -0.0019
ExitNonePGEMBTExCZ02 | Com-Iltg-dWatt-Exit | PGE | MBT | Ex | CZ02 | 8.76 | 0.001 | 0 | 9.67 | 0.00124 | -0.00894 | 8.76 | 0.001 | 0 | 9.67 | 0.00124 | -0.00894 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.1 | 1.24 | -0.0010205 | 8760 | 1 | 8760 | 1 | 1.1 | 1.24 | -0.00102
ExitNonePGEMBTExCZ03 | Com-Iltg-dWatt-Exit | PGE | MBT | Ex | CZ03 | 8.76 | 0.001 | 0 | 9.77 | 0.00128 | -0.00645 | 8.76 | 0.001 | 0 | 9.77 | 0.00128 | -0.00645 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.12 | 1.28 | -0.0007363 | 8760 | 1 | 8760 | 1 | 1.12 | 1.28 | -0.000736
ExitNonePGEMBTExCZ04 | Com-Iltg-dWatt-Exit | PGE | MBT | Ex | CZ04 | 8.76 | 0.001 | 0 | 9.75 | 0.00131 | -0.00519 | 8.76 | 0.001 | 0 | 9.75 | 0.00131 | -0.00519 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.11 | 1.31 | -0.00059247 | 8760 | 1 | 8760 | 1 | 1.11 | 1.31 | -0.000592
ExitNonePGEMBTExCZ05 | Com-Iltg-dWatt-Exit | PGE | MBT | Ex | CZ05 | 8.76 | 0.001 | 0 | 9.7 | 0.00136 | -0.00541 | 8.76 | 0.001 | 0 | 9.7 | 0.00136 | -0.00541 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.11 | 1.36 | -0.00061758 | 8760 | 1 | 8760 | 1 | 1.11 | 1.36 | -0.000618
ExitNonePGEMBTExCZ11 | Com-Iltg-dWatt-Exit | PGE | MBT | Ex | CZ11 | 8.76 | 0.001 | 0 | 9.8 | 0.00129 | -0.00937 | 8.76 | 0.001 | 0 | 9.8 | 0.00129 | -0.00937 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.12 | 1.29 | -0.0010696 | 8760 | 1 | 8760 | 1 | 1.12 | 1.29 | -0.00107
ExitNonePGEMBTExCZ12 | Com-Iltg-dWatt-Exit | PGE | MBT | Ex | CZ12 | 8.76 | 0.001 | 0 | 9.71 | 0.00121 | -0.00937 | 8.76 | 0.001 | 0 | 9.71 | 0.00121 | -0.00937 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.11 | 1.21 | -0.0010696 | 8760 | 1 | 8760 | 1 | 1.11 | 1.21 | -0.00107
ExitNonePGEMBTExCZ13 | Com-Iltg-dWatt-Exit | PGE | MBT | Ex | CZ13 | 8.76 | 0.001 | 0 | 9.87 | 0.00121 | -0.00858 | 8.76 | 0.001 | 0 | 9.87 | 0.00121 | -0.00858 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.13 | 1.21 | -0.00097945 | 8760 | 1 | 8760 | 1 | 1.13 | 1.21 | -0.000979
ExitNonePGEMBTExCZ16 | Com-Iltg-dWatt-Exit | PGE | MBT | Ex | CZ16 | 8.76 | 0.001 | 0 | 9.32 | 0.00121 | -0.0335 | 8.76 | 0.001 | 0 | 9.32 | 0.00121 | -0.0335 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.06 | 1.21 | -0.0038242 | 8760 | 1 | 8760 | 1 | 1.06 | 1.21 | -0.00382
ExitNonePGEMBTExIOU | Com-Iltg-dWatt-Exit | PGE | MBT | Ex | IOU | 8.76 | 0.001 | 0 | 9.75 | 0.00126 | -0.00769 | 8.76 | 0.001 | 0 | 9.75 | 0.00126 | -0.00769 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.11 | 1.26 | -0.00087785 | 8760 | 1 | 8760 | 1 | 1.11 | 1.26 | -0.000878
ExitNonePGEMBTNewCZ01 | Com-Iltg-dWatt-Exit | PGE | MBT | New | CZ01 | 8.76 | 0.001 | 0 | 8.9 | 0.00124 | -0.0175 | 8.76 | 0.001 | 0 | 8.9 | 0.00124 | -0.0175 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.02 | 1.24 | -0.0019977 | 8760 | 1 | 8760 | 1 | 1.02 | 1.24 | -0.002
ExitNonePGEMBTNewCZ02 | Com-Iltg-dWatt-Exit | PGE | MBT | New | CZ02 | 8.76 | 0.001 | 0 | 9.27 | 0.00131 | -0.00837 | 8.76 | 0.001 | 0 | 9.27 | 0.00131 | -0.00837 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.06 | 1.31 | -0.00095548 | 8760 | 1 | 8760 | 1 | 1.06 | 1.31 | -0.000955
ExitNonePGEMBTNewCZ03 | Com-Iltg-dWatt-Exit | PGE | MBT | New | CZ03 | 8.76 | 0.001 | 0 | 9.28 | 0.00128 | -0.00714 | 8.76 | 0.001 | 0 | 9.28 | 0.00128 | -0.00714 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.06 | 1.28 | -0.00081507 | 8760 | 1 | 8760 | 1 | 1.06 | 1.28 | -0.000815
ExitNonePGEMBTNewCZ04 | Com-Iltg-dWatt-Exit | PGE | MBT | New | CZ04 | 8.76 | 0.001 | 0 | 9.38 | 0.00131 | -0.00552 | 8.76 | 0.001 | 0 | 9.38 | 0.00131 | -0.00552 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.07 | 1.31 | -0.00063014 | 8760 | 1 | 8760 | 1 | 1.07 | 1.31 | -0.00063
ExitNonePGEMBTNewCZ05 | Com-Iltg-dWatt-Exit | PGE | MBT | New | CZ05 | 8.76 | 0.001 | 0 | 9.29 | 0.00131 | -0.00499 | 8.76 | 0.001 | 0 | 9.29 | 0.00131 | -0.00499 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.06 | 1.31 | -0.00056963 | 8760 | 1 | 8760 | 1 | 1.06 | 1.31 | -0.00057
ExitNonePGEMBTNewCZ11 | Com-Iltg-dWatt-Exit | PGE | MBT | New | CZ11 | 8.76 | 0.001 | 0 | 9.48 | 0.00133 | -0.0069 | 8.76 | 0.001 | 0 | 9.48 | 0.00133 | -0.0069 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.08 | 1.33 | -0.00078767 | 8760 | 1 | 8760 | 1 | 1.08 | 1.33 | -0.000788
ExitNonePGEMBTNewCZ12 | Com-Iltg-dWatt-Exit | PGE | MBT | New | CZ12 | 8.76 | 0.001 | 0 | 9.37 | 0.00131 | -0.00819 | 8.76 | 0.001 | 0 | 9.37 | 0.00131 | -0.00819 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.07 | 1.31 | -0.00093493 | 8760 | 1 | 8760 | 1 | 1.07 | 1.31 | -0.000935
ExitNonePGEMBTNewCZ13 | Com-Iltg-dWatt-Exit | PGE | MBT | New | CZ13 | 8.76 | 0.001 | 0 | 9.42 | 0.0013 | -0.00745 | 8.76 | 0.001 | 0 | 9.42 | 0.0013 | -0.00745 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.08 | 1.3 | -0.00085046 | 8760 | 1 | 8760 | 1 | 1.08 | 1.3 | -0.00085
ExitNonePGEMBTNewCZ16 | Com-Iltg-dWatt-Exit | PGE | MBT | New | CZ16 | 8.76 | 0.001 | 0 | 9.04 | 0.00126 | -0.0276 | 8.76 | 0.001 | 0 | 9.04 | 0.00126 | -0.0276 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.03 | 1.26 | -0.0031507 | 8760 | 1 | 8760 | 1 | 1.03 | 1.26 | -0.00315
ExitNonePGEMBTNewIOU | Com-Iltg-dWatt-Exit | PGE | MBT | New | IOU | 8.76 | 0.001 | 0 | 9.35 | 0.0013 | -0.00753 | 8.76 | 0.001 | 0 | 9.35 | 0.0013 | -0.00753 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.07 | 1.3 | -0.00085959 | 8760 | 1 | 8760 | 1 | 1.07 | 1.3 | -0.00086
ExitNonePGEMLIExCZ01 | Com-Iltg-dWatt-Exit | PGE | MLI | Ex | CZ01 | 8.76 | 0.001 | 0 | 8.45 | 0.00126 | -0.102 | 8.76 | 0.001 | 0 | 8.45 | 0.00126 | -0.102 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.965 | 1.26 | -0.011644 | 8760 | 1 | 8760 | 1 | 0.965 | 1.26 | -0.0116
ExitNonePGEMLIExCZ02 | Com-Iltg-dWatt-Exit | PGE | MLI | Ex | CZ02 | 8.76 | 0.001 | 0 | 8.96 | 0.00126 | -0.054 | 8.76 | 0.001 | 0 | 8.96 | 0.00126 | -0.054 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.02 | 1.26 | -0.0061644 | 8760 | 1 | 8760 | 1 | 1.02 | 1.26 | -0.00616
ExitNonePGEMLIExCZ03 | Com-Iltg-dWatt-Exit | PGE | MLI | Ex | CZ03 | 8.76 | 0.001 | 0 | 8.94 | 0.00129 | -0.0528 | 8.76 | 0.001 | 0 | 8.94 | 0.00129 | -0.0528 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.02 | 1.29 | -0.0060274 | 8760 | 1 | 8760 | 1 | 1.02 | 1.29 | -0.00603
ExitNonePGEMLIExCZ04 | Com-Iltg-dWatt-Exit | PGE | MLI | Ex | CZ04 | 8.76 | 0.001 | 0 | 9.04 | 0.00127 | -0.0432 | 8.76 | 0.001 | 0 | 9.04 | 0.00127 | -0.0432 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.03 | 1.27 | -0.0049315 | 8760 | 1 | 8760 | 1 | 1.03 | 1.27 | -0.00493
ExitNonePGEMLIExCZ05 | Com-Iltg-dWatt-Exit | PGE | MLI | Ex | CZ05 | 8.76 | 0.001 | 0 | 8.91 | 0.00136 | -0.0524 | 8.76 | 0.001 | 0 | 8.91 | 0.00136 | -0.0524 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.02 | 1.36 | -0.0059817 | 8760 | 1 | 8760 | 1 | 1.02 | 1.36 | -0.00598
ExitNonePGEMLIExCZ11 | Com-Iltg-dWatt-Exit | PGE | MLI | Ex | CZ11 | 8.76 | 0.001 | 0 | 9.03 | 0.00127 | -0.0562 | 8.76 | 0.001 | 0 | 9.03 | 0.00127 | -0.0562 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.03 | 1.27 | -0.0064155 | 8760 | 1 | 8760 | 1 | 1.03 | 1.27 | -0.00642
ExitNonePGEMLIExCZ12 | Com-Iltg-dWatt-Exit | PGE | MLI | Ex | CZ12 | 8.76 | 0.001 | 0 | 8.96 | 0.00127 | -0.0533 | 8.76 | 0.001 | 0 | 8.96 | 0.00127 | -0.0533 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.02 | 1.27 | -0.0060845 | 8760 | 1 | 8760 | 1 | 1.02 | 1.27 | -0.00608
ExitNonePGEMLIExCZ13 | Com-Iltg-dWatt-Exit | PGE | MLI | Ex | CZ13 | 8.76 | 0.001 | 0 | 9.15 | 0.00122 | -0.0476 | 8.76 | 0.001 | 0 | 9.15 | 0.00122 | -0.0476 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.04 | 1.22 | -0.0054338 | 8760 | 1 | 8760 | 1 | 1.04 | 1.22 | -0.00543
ExitNonePGEMLIExCZ16 | Com-Iltg-dWatt-Exit | PGE | MLI | Ex | CZ16 | 8.76 | 0.001 | 0 | 8.46 | 0.00123 | -0.102 | 8.76 | 0.001 | 0 | 8.46 | 0.00123 | -0.102 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.966 | 1.23 | -0.011644 | 8760 | 1 | 8760 | 1 | 0.966 | 1.23 | -0.0116
ExitNonePGEMLIExIOU | Com-Iltg-dWatt-Exit | PGE | MLI | Ex | IOU | 8.76 | 0.001 | 0 | 8.99 | 0.00127 | -0.0517 | 8.76 | 0.001 | 0 | 8.99 | 0.00127 | -0.0517 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.03 | 1.27 | -0.0059018 | 8760 | 1 | 8760 | 1 | 1.03 | 1.27 | -0.0059
ExitNonePGEMLINewCZ01 | Com-Iltg-dWatt-Exit | PGE | MLI | New | CZ01 | 8.76 | 0.001 | 0 | 8.26 | 0.00115 | -0.136 | 8.76 | 0.001 | 0 | 8.26 | 0.00115 | -0.136 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.943 | 1.15 | -0.015525 | 8760 | 1 | 8760 | 1 | 0.943 | 1.15 | -0.0155
ExitNonePGEMLINewCZ02 | Com-Iltg-dWatt-Exit | PGE | MLI | New | CZ02 | 8.76 | 0.001 | 0 | 8.71 | 0.00128 | -0.0745 | 8.76 | 0.001 | 0 | 8.71 | 0.00128 | -0.0745 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.994 | 1.28 | -0.0085046 | 8760 | 1 | 8760 | 1 | 0.994 | 1.28 | -0.0085
ExitNonePGEMLINewCZ03 | Com-Iltg-dWatt-Exit | PGE | MLI | New | CZ03 | 8.76 | 0.001 | 0 | 8.59 | 0.00134 | -0.0775 | 8.76 | 0.001 | 0 | 8.59 | 0.00134 | -0.0775 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.981 | 1.34 | -0.008847 | 8760 | 1 | 8760 | 1 | 0.981 | 1.34 | -0.00885
ExitNonePGEMLINewCZ04 | Com-Iltg-dWatt-Exit | PGE | MLI | New | CZ04 | 8.76 | 0.001 | 0 | 8.8 | 0.00128 | -0.0632 | 8.76 | 0.001 | 0 | 8.8 | 0.00128 | -0.0632 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1 | 1.28 | -0.0072146 | 8760 | 1 | 8760 | 1 | 1 | 1.28 | -0.00721
ExitNonePGEMLINewCZ05 | Com-Iltg-dWatt-Exit | PGE | MLI | New | CZ05 | 8.76 | 0.001 | 0 | 8.58 | 0.00134 | -0.083 | 8.76 | 0.001 | 0 | 8.58 | 0.00134 | -0.083 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.979 | 1.34 | -0.0094749 | 8760 | 1 | 8760 | 1 | 0.979 | 1.34 | -0.00947
ExitNonePGEMLINewCZ11 | Com-Iltg-dWatt-Exit | PGE | MLI | New | CZ11 | 8.76 | 0.001 | 0 | 8.93 | 0.00128 | -0.0645 | 8.76 | 0.001 | 0 | 8.93 | 0.00128 | -0.0645 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.02 | 1.28 | -0.007363 | 8760 | 1 | 8760 | 1 | 1.02 | 1.28 | -0.00736
ExitNonePGEMLINewCZ12 | Com-Iltg-dWatt-Exit | PGE | MLI | New | CZ12 | 8.76 | 0.001 | 0 | 8.85 | 0.00127 | -0.0677 | 8.76 | 0.001 | 0 | 8.85 | 0.00127 | -0.0677 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.01 | 1.27 | -0.0077283 | 8760 | 1 | 8760 | 1 | 1.01 | 1.27 | -0.00773
ExitNonePGEMLINewCZ13 | Com-Iltg-dWatt-Exit | PGE | MLI | New | CZ13 | 8.76 | 0.001 | 0 | 8.96 | 0.00124 | -0.0608 | 8.76 | 0.001 | 0 | 8.96 | 0.00124 | -0.0608 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.02 | 1.24 | -0.0069406 | 8760 | 1 | 8760 | 1 | 1.02 | 1.24 | -0.00694
ExitNonePGEMLINewCZ16 | Com-Iltg-dWatt-Exit | PGE | MLI | New | CZ16 | 8.76 | 0.001 | 0 | 8.51 | 0.00125 | -0.11 | 8.76 | 0.001 | 0 | 8.51 | 0.00125 | -0.11 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.971 | 1.25 | -0.012557 | 8760 | 1 | 8760 | 1 | 0.971 | 1.25 | -0.0126
ExitNonePGEMLINewIOU | Com-Iltg-dWatt-Exit | PGE | MLI | New | IOU | 8.76 | 0.001 | 0 | 8.79 | 0.00128 | -0.0696 | 8.76 | 0.001 | 0 | 8.79 | 0.00128 | -0.0696 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1 | 1.28 | -0.0079452 | 8760 | 1 | 8760 | 1 | 1 | 1.28 | -0.00795
ExitNonePGEMtlExCZ01 | Com-Iltg-dWatt-Exit | PGE | Mtl | Ex | CZ01 | 8.76 | 0.001 | 0 | 8.94 | 0.00119 | -0.068 | 8.76 | 0.001 | 0 | 8.94 | 0.00119 | -0.068 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.02 | 1.19 | -0.0077626 | 8760 | 1 | 8760 | 1 | 1.02 | 1.19 | -0.00776
ExitNonePGEMtlExCZ02 | Com-Iltg-dWatt-Exit | PGE | Mtl | Ex | CZ02 | 8.76 | 0.001 | 0 | 9.36 | 0.00124 | -0.0441 | 8.76 | 0.001 | 0 | 9.36 | 0.00124 | -0.0441 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.07 | 1.24 | -0.0050342 | 8760 | 1 | 8760 | 1 | 1.07 | 1.24 | -0.00503
ExitNonePGEMtlExCZ03 | Com-Iltg-dWatt-Exit | PGE | Mtl | Ex | CZ03 | 8.76 | 0.001 | 0 | 9.5 | 0.00121 | -0.041 | 8.76 | 0.001 | 0 | 9.5 | 0.00121 | -0.041 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.08 | 1.21 | -0.0046804 | 8760 | 1 | 8760 | 1 | 1.08 | 1.21 | -0.00468
ExitNonePGEMtlExCZ04 | Com-Iltg-dWatt-Exit | PGE | Mtl | Ex | CZ04 | 8.76 | 0.001 | 0 | 9.5 | 0.00123 | -0.036 | 8.76 | 0.001 | 0 | 9.5 | 0.00123 | -0.036 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.08 | 1.23 | -0.0041096 | 8760 | 1 | 8760 | 1 | 1.08 | 1.23 | -0.00411
ExitNonePGEMtlExCZ05 | Com-Iltg-dWatt-Exit | PGE | Mtl | Ex | CZ05 | 8.76 | 0.001 | 0 | 9.36 | 0.0012 | -0.0451 | 8.76 | 0.001 | 0 | 9.36 | 0.0012 | -0.0451 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.07 | 1.2 | -0.0051484 | 8760 | 1 | 8760 | 1 | 1.07 | 1.2 | -0.00515
ExitNonePGEMtlExCZ11 | Com-Iltg-dWatt-Exit | PGE | Mtl | Ex | CZ11 | 8.76 | 0.001 | 0 | 9.57 | 0.00125 | -0.0373 | 8.76 | 0.001 | 0 | 9.57 | 0.00125 | -0.0373 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.09 | 1.25 | -0.004258 | 8760 | 1 | 8760 | 1 | 1.09 | 1.25 | -0.00426
ExitNonePGEMtlExCZ12 | Com-Iltg-dWatt-Exit | PGE | Mtl | Ex | CZ12 | 8.76 | 0.001 | 0 | 9.45 | 0.00124 | -0.0387 | 8.76 | 0.001 | 0 | 9.45 | 0.00124 | -0.0387 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.08 | 1.24 | -0.0044178 | 8760 | 1 | 8760 | 1 | 1.08 | 1.24 | -0.00442
ExitNonePGEMtlExCZ13 | Com-Iltg-dWatt-Exit | PGE | Mtl | Ex | CZ13 | 8.76 | 0.001 | 0 | 9.63 | 0.00125 | -0.0344 | 8.76 | 0.001 | 0 | 9.63 | 0.00125 | -0.0344 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.1 | 1.25 | -0.0039269 | 8760 | 1 | 8760 | 1 | 1.1 | 1.25 | -0.00393
ExitNonePGEMtlExCZ16 | Com-Iltg-dWatt-Exit | PGE | Mtl | Ex | CZ16 | 8.76 | 0.001 | 0 | 8.76 | 0.0012 | -0.0652 | 8.76 | 0.001 | 0 | 8.76 | 0.0012 | -0.0652 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1 | 1.2 | -0.0074429 | 8760 | 1 | 8760 | 1 | 1 | 1.2 | -0.00744
ExitNonePGEMtlExIOU | Com-Iltg-dWatt-Exit | PGE | Mtl | Ex | IOU | 8.76 | 0.001 | 0 | 9.47 | 0.00123 | -0.0406 | 8.76 | 0.001 | 0 | 9.47 | 0.00123 | -0.0406 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.08 | 1.23 | -0.0046347 | 8760 | 1 | 8760 | 1 | 1.08 | 1.23 | -0.00463
ExitNonePGEMtlNewCZ01 | Com-Iltg-dWatt-Exit | PGE | Mtl | New | CZ01 | 8.76 | 0.001 | 0 | 8.37 | 0.00119 | -0.0964 | 8.76 | 0.001 | 0 | 8.37 | 0.00119 | -0.0964 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.955 | 1.19 | -0.011005 | 8760 | 1 | 8760 | 1 | 0.955 | 1.19 | -0.011
ExitNonePGEMtlNewCZ02 | Com-Iltg-dWatt-Exit | PGE | Mtl | New | CZ02 | 8.76 | 0.001 | 0 | 9 | 0.00126 | -0.0632 | 8.76 | 0.001 | 0 | 9 | 0.00126 | -0.0632 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.03 | 1.26 | -0.0072146 | 8760 | 1 | 8760 | 1 | 1.03 | 1.26 | -0.00721
ExitNonePGEMtlNewCZ03 | Com-Iltg-dWatt-Exit | PGE | Mtl | New | CZ03 | 8.76 | 0.001 | 0 | 9.14 | 0.00122 | -0.0601 | 8.76 | 0.001 | 0 | 9.14 | 0.00122 | -0.0601 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.04 | 1.22 | -0.0068607 | 8760 | 1 | 8760 | 1 | 1.04 | 1.22 | -0.00686
ExitNonePGEMtlNewCZ04 | Com-Iltg-dWatt-Exit | PGE | Mtl | New | CZ04 | 8.76 | 0.001 | 0 | 9.23 | 0.00124 | -0.0509 | 8.76 | 0.001 | 0 | 9.23 | 0.00124 | -0.0509 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.05 | 1.24 | -0.0058105 | 8760 | 1 | 8760 | 1 | 1.05 | 1.24 | -0.00581
ExitNonePGEMtlNewCZ05 | Com-Iltg-dWatt-Exit | PGE | Mtl | New | CZ05 | 8.76 | 0.001 | 0 | 8.97 | 0.00122 | -0.0692 | 8.76 | 0.001 | 0 | 8.97 | 0.00122 | -0.0692 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.02 | 1.22 | -0.0078995 | 8760 | 1 | 8760 | 1 | 1.02 | 1.22 | -0.0079
ExitNonePGEMtlNewCZ11 | Com-Iltg-dWatt-Exit | PGE | Mtl | New | CZ11 | 8.76 | 0.001 | 0 | 9.31 | 0.00126 | -0.0512 | 8.76 | 0.001 | 0 | 9.31 | 0.00126 | -0.0512 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.06 | 1.26 | -0.0058447 | 8760 | 1 | 8760 | 1 | 1.06 | 1.26 | -0.00584
ExitNonePGEMtlNewCZ12 | Com-Iltg-dWatt-Exit | PGE | Mtl | New | CZ12 | 8.76 | 0.001 | 0 | 9.26 | 0.00125 | -0.0531 | 8.76 | 0.001 | 0 | 9.26 | 0.00125 | -0.0531 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.06 | 1.25 | -0.0060616 | 8760 | 1 | 8760 | 1 | 1.06 | 1.25 | -0.00606
ExitNonePGEMtlNewCZ13 | Com-Iltg-dWatt-Exit | PGE | Mtl | New | CZ13 | 8.76 | 0.001 | 0 | 9.38 | 0.00125 | -0.0484 | 8.76 | 0.001 | 0 | 9.38 | 0.00125 | -0.0484 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.07 | 1.25 | -0.0055251 | 8760 | 1 | 8760 | 1 | 1.07 | 1.25 | -0.00553
ExitNonePGEMtlNewCZ16 | Com-Iltg-dWatt-Exit | PGE | Mtl | New | CZ16 | 8.76 | 0.001 | 0 | 8.4 | 0.00121 | -0.083 | 8.76 | 0.001 | 0 | 8.4 | 0.00121 | -0.083 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.959 | 1.21 | -0.0094749 | 8760 | 1 | 8760 | 1 | 0.959 | 1.21 | -0.00947
ExitNonePGEMtlNewIOU | Com-Iltg-dWatt-Exit | PGE | Mtl | New | IOU | 8.76 | 0.001 | 0 | 9.16 | 0.00124 | -0.0573 | 8.76 | 0.001 | 0 | 9.16 | 0.00124 | -0.0573 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.05 | 1.24 | -0.0065411 | 8760 | 1 | 8760 | 1 | 1.05 | 1.24 | -0.00654
ExitNonePGENrsExCZ01 | Com-Iltg-dWatt-Exit | PGE | Nrs | Ex | CZ01 | 8.76 | 0.001 | 0 | 8.3 | 0.00113 | -0.224 | 8.76 | 0.001 | 0 | 8.3 | 0.00113 | -0.224 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.947 | 1.13 | -0.025571 | 8760 | 1 | 8760 | 1 | 0.947 | 1.13 | -0.0256
ExitNonePGENrsExCZ02 | Com-Iltg-dWatt-Exit | PGE | Nrs | Ex | CZ02 | 8.76 | 0.001 | 0 | 8.76 | 0.00131 | -0.174 | 8.76 | 0.001 | 0 | 8.76 | 0.00131 | -0.174 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1 | 1.31 | -0.019863 | 8760 | 1 | 8760 | 1 | 1 | 1.31 | -0.0199
ExitNonePGENrsExCZ03 | Com-Iltg-dWatt-Exit | PGE | Nrs | Ex | CZ03 | 8.76 | 0.001 | 0 | 8.66 | 0.00126 | -0.18 | 8.76 | 0.001 | 0 | 8.66 | 0.00126 | -0.18 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.989 | 1.26 | -0.020548 | 8760 | 1 | 8760 | 1 | 0.989 | 1.26 | -0.0205
ExitNonePGENrsExCZ04 | Com-Iltg-dWatt-Exit | PGE | Nrs | Ex | CZ04 | 8.76 | 0.001 | 0 | 8.9 | 0.00129 | -0.153 | 8.76 | 0.001 | 0 | 8.9 | 0.00129 | -0.153 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.02 | 1.29 | -0.017466 | 8760 | 1 | 8760 | 1 | 1.02 | 1.29 | -0.0175
ExitNonePGENrsExCZ05 | Com-Iltg-dWatt-Exit | PGE | Nrs | Ex | CZ05 | 8.76 | 0.001 | 0 | 8.58 | 0.00121 | -0.187 | 8.76 | 0.001 | 0 | 8.58 | 0.00121 | -0.187 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.979 | 1.21 | -0.021347 | 8760 | 1 | 8760 | 1 | 0.979 | 1.21 | -0.0213
ExitNonePGENrsExCZ11 | Com-Iltg-dWatt-Exit | PGE | Nrs | Ex | CZ11 | 8.76 | 0.001 | 0 | 9.1 | 0.0013 | -0.139 | 8.76 | 0.001 | 0 | 9.1 | 0.0013 | -0.139 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.04 | 1.3 | -0.015868 | 8760 | 1 | 8760 | 1 | 1.04 | 1.3 | -0.0159
ExitNonePGENrsExCZ12 | Com-Iltg-dWatt-Exit | PGE | Nrs | Ex | CZ12 | 8.76 | 0.001 | 0 | 8.97 | 0.0013 | -0.152 | 8.76 | 0.001 | 0 | 8.97 | 0.0013 | -0.152 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.02 | 1.3 | -0.017352 | 8760 | 1 | 8760 | 1 | 1.02 | 1.3 | -0.0174
ExitNonePGENrsExCZ13 | Com-Iltg-dWatt-Exit | PGE | Nrs | Ex | CZ13 | 8.76 | 0.001 | 0 | 9.15 | 0.00131 | -0.133 | 8.76 | 0.001 | 0 | 9.15 | 0.00131 | -0.133 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.04 | 1.31 | -0.015183 | 8760 | 1 | 8760 | 1 | 1.04 | 1.31 | -0.0152
ExitNonePGENrsExCZ16 | Com-Iltg-dWatt-Exit | PGE | Nrs | Ex | CZ16 | 8.76 | 0.001 | 0 | 8.58 | 0.00124 | -0.187 | 8.76 | 0.001 | 0 | 8.58 | 0.00124 | -0.187 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.979 | 1.24 | -0.021347 | 8760 | 1 | 8760 | 1 | 0.979 | 1.24 | -0.0213
ExitNonePGENrsExIOU | Com-Iltg-dWatt-Exit | PGE | Nrs | Ex | IOU | 8.76 | 0.001 | 0 | 8.87 | 0.00129 | -0.159 | 8.76 | 0.001 | 0 | 8.87 | 0.00129 | -0.159 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.01 | 1.29 | -0.018151 | 8760 | 1 | 8760 | 1 | 1.01 | 1.29 | -0.0182
ExitNonePGENrsNewCZ01 | Com-Iltg-dWatt-Exit | PGE | Nrs | New | CZ01 | 8.76 | 0.001 | 0 | 8.07 | 0.00108 | -0.237 | 8.76 | 0.001 | 0 | 8.07 | 0.00108 | -0.237 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.921 | 1.08 | -0.027055 | 8760 | 1 | 8760 | 1 | 0.921 | 1.08 | -0.0271
ExitNonePGENrsNewCZ02 | Com-Iltg-dWatt-Exit | PGE | Nrs | New | CZ02 | 8.76 | 0.001 | 0 | 8.52 | 0.00133 | -0.198 | 8.76 | 0.001 | 0 | 8.52 | 0.00133 | -0.198 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.973 | 1.33 | -0.022603 | 8760 | 1 | 8760 | 1 | 0.973 | 1.33 | -0.0226
ExitNonePGENrsNewCZ03 | Com-Iltg-dWatt-Exit | PGE | Nrs | New | CZ03 | 8.76 | 0.001 | 0 | 8.33 | 0.00126 | -0.208 | 8.76 | 0.001 | 0 | 8.33 | 0.00126 | -0.208 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.951 | 1.26 | -0.023744 | 8760 | 1 | 8760 | 1 | 0.951 | 1.26 | -0.0237
ExitNonePGENrsNewCZ04 | Com-Iltg-dWatt-Exit | PGE | Nrs | New | CZ04 | 8.76 | 0.001 | 0 | 8.67 | 0.00131 | -0.172 | 8.76 | 0.001 | 0 | 8.67 | 0.00131 | -0.172 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.99 | 1.31 | -0.019635 | 8760 | 1 | 8760 | 1 | 0.99 | 1.31 | -0.0196
ExitNonePGENrsNewCZ05 | Com-Iltg-dWatt-Exit | PGE | Nrs | New | CZ05 | 8.76 | 0.001 | 0 | 8.35 | 0.00121 | -0.209 | 8.76 | 0.001 | 0 | 8.35 | 0.00121 | -0.209 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.953 | 1.21 | -0.023858 | 8760 | 1 | 8760 | 1 | 0.953 | 1.21 | -0.0239
ExitNonePGENrsNewCZ11 | Com-Iltg-dWatt-Exit | PGE | Nrs | New | CZ11 | 8.76 | 0.001 | 0 | 8.92 | 0.0013 | -0.149 | 8.76 | 0.001 | 0 | 8.92 | 0.0013 | -0.149 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.02 | 1.3 | -0.017009 | 8760 | 1 | 8760 | 1 | 1.02 | 1.3 | -0.017
ExitNonePGENrsNewCZ12 | Com-Iltg-dWatt-Exit | PGE | Nrs | New | CZ12 | 8.76 | 0.001 | 0 | 8.78 | 0.00133 | -0.166 | 8.76 | 0.001 | 0 | 8.78 | 0.00133 | -0.166 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1 | 1.33 | -0.01895 | 8760 | 1 | 8760 | 1 | 1 | 1.33 | -0.019
ExitNonePGENrsNewCZ13 | Com-Iltg-dWatt-Exit | PGE | Nrs | New | CZ13 | 8.76 | 0.001 | 0 | 8.98 | 0.00132 | -0.145 | 8.76 | 0.001 | 0 | 8.98 | 0.00132 | -0.145 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.03 | 1.32 | -0.016553 | 8760 | 1 | 8760 | 1 | 1.03 | 1.32 | -0.0166
ExitNonePGENrsNewCZ16 | Com-Iltg-dWatt-Exit | PGE | Nrs | New | CZ16 | 8.76 | 0.001 | 0 | 8.43 | 0.00125 | -0.198 | 8.76 | 0.001 | 0 | 8.43 | 0.00125 | -0.198 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.962 | 1.25 | -0.022603 | 8760 | 1 | 8760 | 1 | 0.962 | 1.25 | -0.0226
ExitNonePGENrsNewIOU | Com-Iltg-dWatt-Exit | PGE | Nrs | New | IOU | 8.76 | 0.001 | 0 | 8.66 | 0.0013 | -0.176 | 8.76 | 0.001 | 0 | 8.66 | 0.0013 | -0.176 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.989 | 1.3 | -0.020091 | 8760 | 1 | 8760 | 1 | 0.989 | 1.3 | -0.0201
ExitNonePGEOfLExCZ01 | Com-Iltg-dWatt-Exit | PGE | OfL | Ex | CZ01 | 8.76 | 0.001 | 0 | 9.26 | 0.00133 | -0.0858 | 8.76 | 0.001 | 0 | 9.26 | 0.00133 | -0.0858 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.06 | 1.33 | -0.0097945 | 8760 | 1 | 8760 | 1 | 1.06 | 1.33 | -0.00979
ExitNonePGEOfLExCZ02 | Com-Iltg-dWatt-Exit | PGE | OfL | Ex | CZ02 | 8.76 | 0.001 | 0 | 9.45 | 0.00145 | -0.0679 | 8.76 | 0.001 | 0 | 9.45 | 0.00145 | -0.0679 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.08 | 1.45 | -0.0077511 | 8760 | 1 | 8760 | 1 | 1.08 | 1.45 | -0.00775
ExitNonePGEOfLExCZ03 | Com-Iltg-dWatt-Exit | PGE | OfL | Ex | CZ03 | 8.76 | 0.001 | 0 | 9.55 | 0.00142 | -0.0599 | 8.76 | 0.001 | 0 | 9.55 | 0.00142 | -0.0599 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.09 | 1.42 | -0.0068379 | 8760 | 1 | 8760 | 1 | 1.09 | 1.42 | -0.00684
ExitNonePGEOfLExCZ04 | Com-Iltg-dWatt-Exit | PGE | OfL | Ex | CZ04 | 8.76 | 0.001 | 0 | 9.5 | 0.00132 | -0.0604 | 8.76 | 0.001 | 0 | 9.5 | 0.00132 | -0.0604 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.08 | 1.32 | -0.006895 | 8760 | 1 | 8760 | 1 | 1.08 | 1.32 | -0.0069
ExitNonePGEOfLExCZ05 | Com-Iltg-dWatt-Exit | PGE | OfL | Ex | CZ05 | 8.76 | 0.001 | 0 | 9.49 | 0.00136 | -0.0632 | 8.76 | 0.001 | 0 | 9.49 | 0.00136 | -0.0632 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.08 | 1.36 | -0.0072146 | 8760 | 1 | 8760 | 1 | 1.08 | 1.36 | -0.00721
ExitNonePGEOfLExCZ11 | Com-Iltg-dWatt-Exit | PGE | OfL | Ex | CZ11 | 8.76 | 0.001 | 0 | 9.71 | 0.00144 | -0.0706 | 8.76 | 0.001 | 0 | 9.71 | 0.00144 | -0.0706 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.11 | 1.44 | -0.0080594 | 8760 | 1 | 8760 | 1 | 1.11 | 1.44 | -0.00806
ExitNonePGEOfLExCZ12 | Com-Iltg-dWatt-Exit | PGE | OfL | Ex | CZ12 | 8.76 | 0.001 | 0 | 9.52 | 0.00144 | -0.0624 | 8.76 | 0.001 | 0 | 9.52 | 0.00144 | -0.0624 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.09 | 1.44 | -0.0071233 | 8760 | 1 | 8760 | 1 | 1.09 | 1.44 | -0.00712
ExitNonePGEOfLExCZ13 | Com-Iltg-dWatt-Exit | PGE | OfL | Ex | CZ13 | 8.76 | 0.001 | 0 | 9.79 | 0.0015 | -0.0591 | 8.76 | 0.001 | 0 | 9.79 | 0.0015 | -0.0591 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.12 | 1.5 | -0.0067466 | 8760 | 1 | 8760 | 1 | 1.12 | 1.5 | -0.00675
ExitNonePGEOfLExCZ16 | Com-Iltg-dWatt-Exit | PGE | OfL | Ex | CZ16 | 8.76 | 0.001 | 0 | 9.15 | 0.00136 | -0.117 | 8.76 | 0.001 | 0 | 9.15 | 0.00136 | -0.117 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.04 | 1.36 | -0.013356 | 8760 | 1 | 8760 | 1 | 1.04 | 1.36 | -0.0134
ExitNonePGEOfLExIOU | Com-Iltg-dWatt-Exit | PGE | OfL | Ex | IOU | 8.76 | 0.001 | 0 | 9.54 | 0.00141 | -0.0611 | 8.76 | 0.001 | 0 | 9.54 | 0.00141 | -0.0611 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.09 | 1.41 | -0.0069749 | 8760 | 1 | 8760 | 1 | 1.09 | 1.41 | -0.00697
ExitNonePGEOfLNewCZ01 | Com-Iltg-dWatt-Exit | PGE | OfL | New | CZ01 | 8.76 | 0.001 | 0 | 9.24 | 0.00127 | -0.0653 | 8.76 | 0.001 | 0 | 9.24 | 0.00127 | -0.0653 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.05 | 1.27 | -0.0074543 | 8760 | 1 | 8760 | 1 | 1.05 | 1.27 | -0.00745
ExitNonePGEOfLNewCZ02 | Com-Iltg-dWatt-Exit | PGE | OfL | New | CZ02 | 8.76 | 0.001 | 0 | 9.69 | 0.00132 | -0.0777 | 8.76 | 0.001 | 0 | 9.69 | 0.00132 | -0.0777 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.11 | 1.32 | -0.0088699 | 8760 | 1 | 8760 | 1 | 1.11 | 1.32 | -0.00887
ExitNonePGEOfLNewCZ03 | Com-Iltg-dWatt-Exit | PGE | OfL | New | CZ03 | 8.76 | 0.001 | 0 | 9.47 | 0.00132 | -0.0635 | 8.76 | 0.001 | 0 | 9.47 | 0.00132 | -0.0635 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.08 | 1.32 | -0.0072489 | 8760 | 1 | 8760 | 1 | 1.08 | 1.32 | -0.00725
ExitNonePGEOfLNewCZ04 | Com-Iltg-dWatt-Exit | PGE | OfL | New | CZ04 | 8.76 | 0.001 | 0 | 9.71 | 0.00134 | -0.0362 | 8.76 | 0.001 | 0 | 9.71 | 0.00134 | -0.0362 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.11 | 1.34 | -0.0041324 | 8760 | 1 | 8760 | 1 | 1.11 | 1.34 | -0.00413
ExitNonePGEOfLNewCZ05 | Com-Iltg-dWatt-Exit | PGE | OfL | New | CZ05 | 8.76 | 0.001 | 0 | 9.55 | 0.00134 | -0.0548 | 8.76 | 0.001 | 0 | 9.55 | 0.00134 | -0.0548 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.09 | 1.34 | -0.0062557 | 8760 | 1 | 8760 | 1 | 1.09 | 1.34 | -0.00626
ExitNonePGEOfLNewCZ11 | Com-Iltg-dWatt-Exit | PGE | OfL | New | CZ11 | 8.76 | 0.001 | 0 | 9.78 | 0.00131 | -0.0385 | 8.76 | 0.001 | 0 | 9.78 | 0.00131 | -0.0385 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.12 | 1.31 | -0.004395 | 8760 | 1 | 8760 | 1 | 1.12 | 1.31 | -0.0044
ExitNonePGEOfLNewCZ12 | Com-Iltg-dWatt-Exit | PGE | OfL | New | CZ12 | 8.76 | 0.001 | 0 | 9.78 | 0.00131 | -0.0572 | 8.76 | 0.001 | 0 | 9.78 | 0.00131 | -0.0572 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.12 | 1.31 | -0.0065297 | 8760 | 1 | 8760 | 1 | 1.12 | 1.31 | -0.00653
ExitNonePGEOfLNewCZ13 | Com-Iltg-dWatt-Exit | PGE | OfL | New | CZ13 | 8.76 | 0.001 | 0 | 9.82 | 0.00133 | -0.0522 | 8.76 | 0.001 | 0 | 9.82 | 0.00133 | -0.0522 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.12 | 1.33 | -0.0059589 | 8760 | 1 | 8760 | 1 | 1.12 | 1.33 | -0.00596
ExitNonePGEOfLNewCZ16 | Com-Iltg-dWatt-Exit | PGE | OfL | New | CZ16 | 8.76 | 0.001 | 0 | 9.25 | 0.00131 | -0.0818 | 8.76 | 0.001 | 0 | 9.25 | 0.00131 | -0.0818 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.06 | 1.31 | -0.0093379 | 8760 | 1 | 8760 | 1 | 1.06 | 1.31 | -0.00934
ExitNonePGEOfLNewIOU | Com-Iltg-dWatt-Exit | PGE | OfL | New | IOU | 8.76 | 0.001 | 0 | 9.64 | 0.00132 | -0.0551 | 8.76 | 0.001 | 0 | 9.64 | 0.00132 | -0.0551 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.1 | 1.32 | -0.00629 | 8760 | 1 | 8760 | 1 | 1.1 | 1.32 | -0.00629
ExitNonePGEOfSExCZ01 | Com-Iltg-dWatt-Exit | PGE | OfS | Ex | CZ01 | 8.76 | 0.001 | 0 | 8.61 | 0.00128 | -0.0636 | 8.76 | 0.001 | 0 | 8.61 | 0.00128 | -0.0636 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.983 | 1.28 | -0.0072603 | 8760 | 1 | 8760 | 1 | 0.983 | 1.28 | -0.00726
ExitNonePGEOfSExCZ02 | Com-Iltg-dWatt-Exit | PGE | OfS | Ex | CZ02 | 8.76 | 0.001 | 0 | 9.05 | 0.00131 | -0.0406 | 8.76 | 0.001 | 0 | 9.05 | 0.00131 | -0.0406 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.03 | 1.31 | -0.0046347 | 8760 | 1 | 8760 | 1 | 1.03 | 1.31 | -0.00463
ExitNonePGEOfSExCZ03 | Com-Iltg-dWatt-Exit | PGE | OfS | Ex | CZ03 | 8.76 | 0.001 | 0 | 9.04 | 0.00129 | -0.0366 | 8.76 | 0.001 | 0 | 9.04 | 0.00129 | -0.0366 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.03 | 1.29 | -0.0041781 | 8760 | 1 | 8760 | 1 | 1.03 | 1.29 | -0.00418
ExitNonePGEOfSExCZ04 | Com-Iltg-dWatt-Exit | PGE | OfS | Ex | CZ04 | 8.76 | 0.001 | 0 | 9.21 | 0.00132 | -0.0307 | 8.76 | 0.001 | 0 | 9.21 | 0.00132 | -0.0307 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.05 | 1.32 | -0.0035046 | 8760 | 1 | 8760 | 1 | 1.05 | 1.32 | -0.0035
ExitNonePGEOfSExCZ05 | Com-Iltg-dWatt-Exit | PGE | OfS | Ex | CZ05 | 8.76 | 0.001 | 0 | 9.07 | 0.00134 | -0.0333 | 8.76 | 0.001 | 0 | 9.07 | 0.00134 | -0.0333 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.04 | 1.34 | -0.0038014 | 8760 | 1 | 8760 | 1 | 1.04 | 1.34 | -0.0038
ExitNonePGEOfSExCZ11 | Com-Iltg-dWatt-Exit | PGE | OfS | Ex | CZ11 | 8.76 | 0.001 | 0 | 9.27 | 0.0013 | -0.0434 | 8.76 | 0.001 | 0 | 9.27 | 0.0013 | -0.0434 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.06 | 1.3 | -0.0049543 | 8760 | 1 | 8760 | 1 | 1.06 | 1.3 | -0.00495
ExitNonePGEOfSExCZ12 | Com-Iltg-dWatt-Exit | PGE | OfS | Ex | CZ12 | 8.76 | 0.001 | 0 | 9.17 | 0.00129 | -0.0409 | 8.76 | 0.001 | 0 | 9.17 | 0.00129 | -0.0409 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.05 | 1.29 | -0.0046689 | 8760 | 1 | 8760 | 1 | 1.05 | 1.29 | -0.00467
ExitNonePGEOfSExCZ13 | Com-Iltg-dWatt-Exit | PGE | OfS | Ex | CZ13 | 8.76 | 0.001 | 0 | 9.32 | 0.00127 | -0.037 | 8.76 | 0.001 | 0 | 9.32 | 0.00127 | -0.037 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.06 | 1.27 | -0.0042237 | 8760 | 1 | 8760 | 1 | 1.06 | 1.27 | -0.00422
ExitNonePGEOfSExCZ16 | Com-Iltg-dWatt-Exit | PGE | OfS | Ex | CZ16 | 8.76 | 0.001 | 0 | 8.58 | 0.00127 | -0.0709 | 8.76 | 0.001 | 0 | 8.58 | 0.00127 | -0.0709 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.979 | 1.27 | -0.0080936 | 8760 | 1 | 8760 | 1 | 0.979 | 1.27 | -0.00809
ExitNonePGEOfSExIOU | Com-Iltg-dWatt-Exit | PGE | OfS | Ex | IOU | 8.76 | 0.001 | 0 | 9.16 | 0.00129 | -0.0378 | 8.76 | 0.001 | 0 | 9.16 | 0.00129 | -0.0378 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.05 | 1.29 | -0.0043151 | 8760 | 1 | 8760 | 1 | 1.05 | 1.29 | -0.00432
ExitNonePGEOfSNewCZ01 | Com-Iltg-dWatt-Exit | PGE | OfS | New | CZ01 | 8.76 | 0.001 | 0 | 8.44 | 0.00129 | -0.0617 | 8.76 | 0.001 | 0 | 8.44 | 0.00129 | -0.0617 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.963 | 1.29 | -0.0070434 | 8760 | 1 | 8760 | 1 | 0.963 | 1.29 | -0.00704
ExitNonePGEOfSNewCZ02 | Com-Iltg-dWatt-Exit | PGE | OfS | New | CZ02 | 8.76 | 0.001 | 0 | 8.97 | 0.00134 | -0.0377 | 8.76 | 0.001 | 0 | 8.97 | 0.00134 | -0.0377 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.02 | 1.34 | -0.0043037 | 8760 | 1 | 8760 | 1 | 1.02 | 1.34 | -0.0043
ExitNonePGEOfSNewCZ03 | Com-Iltg-dWatt-Exit | PGE | OfS | New | CZ03 | 8.76 | 0.001 | 0 | 8.89 | 0.0013 | -0.0389 | 8.76 | 0.001 | 0 | 8.89 | 0.0013 | -0.0389 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.01 | 1.3 | -0.0044406 | 8760 | 1 | 8760 | 1 | 1.01 | 1.3 | -0.00444
ExitNonePGEOfSNewCZ04 | Com-Iltg-dWatt-Exit | PGE | OfS | New | CZ04 | 8.76 | 0.001 | 0 | 9.09 | 0.00134 | -0.023 | 8.76 | 0.001 | 0 | 9.09 | 0.00134 | -0.023 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.04 | 1.34 | -0.0026256 | 8760 | 1 | 8760 | 1 | 1.04 | 1.34 | -0.00263
ExitNonePGEOfSNewCZ05 | Com-Iltg-dWatt-Exit | PGE | OfS | New | CZ05 | 8.76 | 0.001 | 0 | 8.93 | 0.00134 | -0.0333 | 8.76 | 0.001 | 0 | 8.93 | 0.00134 | -0.0333 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.02 | 1.34 | -0.0038014 | 8760 | 1 | 8760 | 1 | 1.02 | 1.34 | -0.0038
ExitNonePGEOfSNewCZ11 | Com-Iltg-dWatt-Exit | PGE | OfS | New | CZ11 | 8.76 | 0.001 | 0 | 9.24 | 0.00135 | -0.0414 | 8.76 | 0.001 | 0 | 9.24 | 0.00135 | -0.0414 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.05 | 1.35 | -0.004726 | 8760 | 1 | 8760 | 1 | 1.05 | 1.35 | -0.00473
ExitNonePGEOfSNewCZ12 | Com-Iltg-dWatt-Exit | PGE | OfS | New | CZ12 | 8.76 | 0.001 | 0 | 9.12 | 0.00134 | -0.038 | 8.76 | 0.001 | 0 | 9.12 | 0.00134 | -0.038 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.04 | 1.34 | -0.0043379 | 8760 | 1 | 8760 | 1 | 1.04 | 1.34 | -0.00434
ExitNonePGEOfSNewCZ13 | Com-Iltg-dWatt-Exit | PGE | OfS | New | CZ13 | 8.76 | 0.001 | 0 | 9.24 | 0.00133 | -0.0357 | 8.76 | 0.001 | 0 | 9.24 | 0.00133 | -0.0357 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.05 | 1.33 | -0.0040753 | 8760 | 1 | 8760 | 1 | 1.05 | 1.33 | -0.00408
ExitNonePGEOfSNewCZ16 | Com-Iltg-dWatt-Exit | PGE | OfS | New | CZ16 | 8.76 | 0.001 | 0 | 8.56 | 0.00129 | -0.0719 | 8.76 | 0.001 | 0 | 8.56 | 0.00129 | -0.0719 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.977 | 1.29 | -0.0082078 | 8760 | 1 | 8760 | 1 | 0.977 | 1.29 | -0.00821
ExitNonePGEOfSNewIOU | Com-Iltg-dWatt-Exit | PGE | OfS | New | IOU | 8.76 | 0.001 | 0 | 9.08 | 0.00133 | -0.0357 | 8.76 | 0.001 | 0 | 9.08 | 0.00133 | -0.0357 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.04 | 1.33 | -0.0040753 | 8760 | 1 | 8760 | 1 | 1.04 | 1.33 | -0.00408
ExitNonePGERFFExCZ01 | Com-Iltg-dWatt-Exit | PGE | RFF | Ex | CZ01 | 8.76 | 0.001 | 0 | 8.41 | 0.00119 | -0.12 | 8.76 | 0.001 | 0 | 8.41 | 0.00119 | -0.12 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.96 | 1.19 | -0.013699 | 8760 | 1 | 8760 | 1 | 0.96 | 1.19 | -0.0137
ExitNonePGERFFExCZ02 | Com-Iltg-dWatt-Exit | PGE | RFF | Ex | CZ02 | 8.76 | 0.001 | 0 | 8.92 | 0.00121 | -0.0766 | 8.76 | 0.001 | 0 | 8.92 | 0.00121 | -0.0766 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.02 | 1.21 | -0.0087443 | 8760 | 1 | 8760 | 1 | 1.02 | 1.21 | -0.00874
ExitNonePGERFFExCZ03 | Com-Iltg-dWatt-Exit | PGE | RFF | Ex | CZ03 | 8.76 | 0.001 | 0 | 8.87 | 0.0012 | -0.0785 | 8.76 | 0.001 | 0 | 8.87 | 0.0012 | -0.0785 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.01 | 1.2 | -0.0089612 | 8760 | 1 | 8760 | 1 | 1.01 | 1.2 | -0.00896
ExitNonePGERFFExCZ04 | Com-Iltg-dWatt-Exit | PGE | RFF | Ex | CZ04 | 8.76 | 0.001 | 0 | 9.1 | 0.00121 | -0.0626 | 8.76 | 0.001 | 0 | 9.1 | 0.00121 | -0.0626 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.04 | 1.21 | -0.0071461 | 8760 | 1 | 8760 | 1 | 1.04 | 1.21 | -0.00715
ExitNonePGERFFExCZ05 | Com-Iltg-dWatt-Exit | PGE | RFF | Ex | CZ05 | 8.76 | 0.001 | 0 | 8.81 | 0.00119 | -0.0823 | 8.76 | 0.001 | 0 | 8.81 | 0.00119 | -0.0823 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.01 | 1.19 | -0.009395 | 8760 | 1 | 8760 | 1 | 1.01 | 1.19 | -0.0094
ExitNonePGERFFExCZ11 | Com-Iltg-dWatt-Exit | PGE | RFF | Ex | CZ11 | 8.76 | 0.001 | 0 | 9.16 | 0.00122 | -0.0617 | 8.76 | 0.001 | 0 | 9.16 | 0.00122 | -0.0617 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.05 | 1.22 | -0.0070434 | 8760 | 1 | 8760 | 1 | 1.05 | 1.22 | -0.00704
ExitNonePGERFFExCZ12 | Com-Iltg-dWatt-Exit | PGE | RFF | Ex | CZ12 | 8.76 | 0.001 | 0 | 9.11 | 0.00122 | -0.0636 | 8.76 | 0.001 | 0 | 9.11 | 0.00122 | -0.0636 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.04 | 1.22 | -0.0072603 | 8760 | 1 | 8760 | 1 | 1.04 | 1.22 | -0.00726
ExitNonePGERFFExCZ13 | Com-Iltg-dWatt-Exit | PGE | RFF | Ex | CZ13 | 8.76 | 0.001 | 0 | 9.21 | 0.00121 | -0.0566 | 8.76 | 0.001 | 0 | 9.21 | 0.00121 | -0.0566 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.05 | 1.21 | -0.0064612 | 8760 | 1 | 8760 | 1 | 1.05 | 1.21 | -0.00646
ExitNonePGERFFExCZ16 | Com-Iltg-dWatt-Exit | PGE | RFF | Ex | CZ16 | 8.76 | 0.001 | 0 | 8.49 | 0.00119 | -0.109 | 8.76 | 0.001 | 0 | 8.49 | 0.00119 | -0.109 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.969 | 1.19 | -0.012443 | 8760 | 1 | 8760 | 1 | 0.969 | 1.19 | -0.0124
ExitNonePGERFFExIOU | Com-Iltg-dWatt-Exit | PGE | RFF | Ex | IOU | 8.76 | 0.001 | 0 | 9.01 | 0.00121 | -0.0698 | 8.76 | 0.001 | 0 | 9.01 | 0.00121 | -0.0698 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.03 | 1.21 | -0.007968 | 8760 | 1 | 8760 | 1 | 1.03 | 1.21 | -0.00797
ExitNonePGERFFNewCZ01 | Com-Iltg-dWatt-Exit | PGE | RFF | New | CZ01 | 8.76 | 0.001 | 0 | 8.16 | 0.00113 | -0.135 | 8.76 | 0.001 | 0 | 8.16 | 0.00113 | -0.135 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.932 | 1.13 | -0.015411 | 8760 | 1 | 8760 | 1 | 0.932 | 1.13 | -0.0154
ExitNonePGERFFNewCZ02 | Com-Iltg-dWatt-Exit | PGE | RFF | New | CZ02 | 8.76 | 0.001 | 0 | 8.8 | 0.00128 | -0.0972 | 8.76 | 0.001 | 0 | 8.8 | 0.00128 | -0.0972 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1 | 1.28 | -0.011096 | 8760 | 1 | 8760 | 1 | 1 | 1.28 | -0.0111
ExitNonePGERFFNewCZ03 | Com-Iltg-dWatt-Exit | PGE | RFF | New | CZ03 | 8.76 | 0.001 | 0 | 8.62 | 0.00123 | -0.0972 | 8.76 | 0.001 | 0 | 8.62 | 0.00123 | -0.0972 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.984 | 1.23 | -0.011096 | 8760 | 1 | 8760 | 1 | 0.984 | 1.23 | -0.0111
ExitNonePGERFFNewCZ04 | Com-Iltg-dWatt-Exit | PGE | RFF | New | CZ04 | 8.76 | 0.001 | 0 | 8.91 | 0.00126 | -0.0775 | 8.76 | 0.001 | 0 | 8.91 | 0.00126 | -0.0775 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.02 | 1.26 | -0.008847 | 8760 | 1 | 8760 | 1 | 1.02 | 1.26 | -0.00885
ExitNonePGERFFNewCZ05 | Com-Iltg-dWatt-Exit | PGE | RFF | New | CZ05 | 8.76 | 0.001 | 0 | 8.62 | 0.00121 | -0.0885 | 8.76 | 0.001 | 0 | 8.62 | 0.00121 | -0.0885 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.984 | 1.21 | -0.010103 | 8760 | 1 | 8760 | 1 | 0.984 | 1.21 | -0.0101
ExitNonePGERFFNewCZ11 | Com-Iltg-dWatt-Exit | PGE | RFF | New | CZ11 | 8.76 | 0.001 | 0 | 9.16 | 0.00131 | -0.0746 | 8.76 | 0.001 | 0 | 9.16 | 0.00131 | -0.0746 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.05 | 1.31 | -0.008516 | 8760 | 1 | 8760 | 1 | 1.05 | 1.31 | -0.00852
ExitNonePGERFFNewCZ12 | Com-Iltg-dWatt-Exit | PGE | RFF | New | CZ12 | 8.76 | 0.001 | 0 | 9.01 | 0.0013 | -0.0835 | 8.76 | 0.001 | 0 | 9.01 | 0.0013 | -0.0835 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.03 | 1.3 | -0.009532 | 8760 | 1 | 8760 | 1 | 1.03 | 1.3 | -0.00953
ExitNonePGERFFNewCZ13 | Com-Iltg-dWatt-Exit | PGE | RFF | New | CZ13 | 8.76 | 0.001 | 0 | 9.2 | 0.00129 | -0.0725 | 8.76 | 0.001 | 0 | 9.2 | 0.00129 | -0.0725 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.05 | 1.29 | -0.0082763 | 8760 | 1 | 8760 | 1 | 1.05 | 1.29 | -0.00828
ExitNonePGERFFNewCZ16 | Com-Iltg-dWatt-Exit | PGE | RFF | New | CZ16 | 8.76 | 0.001 | 0 | 8.51 | 0.00124 | -0.127 | 8.76 | 0.001 | 0 | 8.51 | 0.00124 | -0.127 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.971 | 1.24 | -0.014498 | 8760 | 1 | 8760 | 1 | 0.971 | 1.24 | -0.0145
ExitNonePGERFFNewIOU | Com-Iltg-dWatt-Exit | PGE | RFF | New | IOU | 8.76 | 0.001 | 0 | 8.87 | 0.00126 | -0.087 | 8.76 | 0.001 | 0 | 8.87 | 0.00126 | -0.087 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.01 | 1.26 | -0.0099315 | 8760 | 1 | 8760 | 1 | 1.01 | 1.26 | -0.00993
ExitNonePGERSDExCZ01 | Com-Iltg-dWatt-Exit | PGE | RSD | Ex | CZ01 | 8.76 | 0.001 | 0 | 8.2 | 0.0012 | -0.141 | 8.76 | 0.001 | 0 | 8.2 | 0.0012 | -0.141 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.936 | 1.2 | -0.016096 | 8760 | 1 | 8760 | 1 | 0.936 | 1.2 | -0.0161
ExitNonePGERSDExCZ02 | Com-Iltg-dWatt-Exit | PGE | RSD | Ex | CZ02 | 8.76 | 0.001 | 0 | 9 | 0.00124 | -0.0782 | 8.76 | 0.001 | 0 | 9 | 0.00124 | -0.0782 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.03 | 1.24 | -0.0089269 | 8760 | 1 | 8760 | 1 | 1.03 | 1.24 | -0.00893
ExitNonePGERSDExCZ03 | Com-Iltg-dWatt-Exit | PGE | RSD | Ex | CZ03 | 8.76 | 0.001 | 0 | 8.82 | 0.00126 | -0.0852 | 8.76 | 0.001 | 0 | 8.82 | 0.00126 | -0.0852 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.01 | 1.26 | -0.009726 | 8760 | 1 | 8760 | 1 | 1.01 | 1.26 | -0.00973
ExitNonePGERSDExCZ04 | Com-Iltg-dWatt-Exit | PGE | RSD | Ex | CZ04 | 8.76 | 0.001 | 0 | 9.14 | 0.00125 | -0.0629 | 8.76 | 0.001 | 0 | 9.14 | 0.00125 | -0.0629 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.04 | 1.25 | -0.0071804 | 8760 | 1 | 8760 | 1 | 1.04 | 1.25 | -0.00718
ExitNonePGERSDExCZ05 | Com-Iltg-dWatt-Exit | PGE | RSD | Ex | CZ05 | 8.76 | 0.001 | 0 | 8.86 | 0.00124 | -0.0844 | 8.76 | 0.001 | 0 | 8.86 | 0.00124 | -0.0844 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.01 | 1.24 | -0.0096347 | 8760 | 1 | 8760 | 1 | 1.01 | 1.24 | -0.00963
ExitNonePGERSDExCZ11 | Com-Iltg-dWatt-Exit | PGE | RSD | Ex | CZ11 | 8.76 | 0.001 | 0 | 9.13 | 0.00123 | -0.0672 | 8.76 | 0.001 | 0 | 9.13 | 0.00123 | -0.0672 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.04 | 1.23 | -0.0076712 | 8760 | 1 | 8760 | 1 | 1.04 | 1.23 | -0.00767
ExitNonePGERSDExCZ12 | Com-Iltg-dWatt-Exit | PGE | RSD | Ex | CZ12 | 8.76 | 0.001 | 0 | 9.06 | 0.00118 | -0.0688 | 8.76 | 0.001 | 0 | 9.06 | 0.00118 | -0.0688 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.03 | 1.18 | -0.0078539 | 8760 | 1 | 8760 | 1 | 1.03 | 1.18 | -0.00785
ExitNonePGERSDExCZ13 | Com-Iltg-dWatt-Exit | PGE | RSD | Ex | CZ13 | 8.76 | 0.001 | 0 | 9.15 | 0.00126 | -0.0604 | 8.76 | 0.001 | 0 | 9.15 | 0.00126 | -0.0604 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.04 | 1.26 | -0.006895 | 8760 | 1 | 8760 | 1 | 1.04 | 1.26 | -0.0069
ExitNonePGERSDExCZ16 | Com-Iltg-dWatt-Exit | PGE | RSD | Ex | CZ16 | 8.76 | 0.001 | 0 | 8.39 | 0.00118 | -0.118 | 8.76 | 0.001 | 0 | 8.39 | 0.00118 | -0.118 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.958 | 1.18 | -0.01347 | 8760 | 1 | 8760 | 1 | 0.958 | 1.18 | -0.0135
ExitNonePGERSDExIOU | Com-Iltg-dWatt-Exit | PGE | RSD | Ex | IOU | 8.76 | 0.001 | 0 | 8.98 | 0.00123 | -0.0745 | 8.76 | 0.001 | 0 | 8.98 | 0.00123 | -0.0745 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.03 | 1.23 | -0.0085046 | 8760 | 1 | 8760 | 1 | 1.03 | 1.23 | -0.0085
ExitNonePGERSDNewCZ01 | Com-Iltg-dWatt-Exit | PGE | RSD | New | CZ01 | 8.76 | 0.001 | 0 | 8.14 | 0.00125 | -0.105 | 8.76 | 0.001 | 0 | 8.14 | 0.00125 | -0.105 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.929 | 1.25 | -0.011986 | 8760 | 1 | 8760 | 1 | 0.929 | 1.25 | -0.012
ExitNonePGERSDNewCZ02 | Com-Iltg-dWatt-Exit | PGE | RSD | New | CZ02 | 8.76 | 0.001 | 0 | 8.83 | 0.00132 | -0.0894 | 8.76 | 0.001 | 0 | 8.83 | 0.00132 | -0.0894 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.01 | 1.32 | -0.010205 | 8760 | 1 | 8760 | 1 | 1.01 | 1.32 | -0.0102
ExitNonePGERSDNewCZ03 | Com-Iltg-dWatt-Exit | PGE | RSD | New | CZ03 | 8.76 | 0.001 | 0 | 8.62 | 0.0013 | -0.102 | 8.76 | 0.001 | 0 | 8.62 | 0.0013 | -0.102 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.984 | 1.3 | -0.011644 | 8760 | 1 | 8760 | 1 | 0.984 | 1.3 | -0.0116
ExitNonePGERSDNewCZ04 | Com-Iltg-dWatt-Exit | PGE | RSD | New | CZ04 | 8.76 | 0.001 | 0 | 9.11 | 0.00132 | -0.0739 | 8.76 | 0.001 | 0 | 9.11 | 0.00132 | -0.0739 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.04 | 1.32 | -0.0084361 | 8760 | 1 | 8760 | 1 | 1.04 | 1.32 | -0.00844
ExitNonePGERSDNewCZ05 | Com-Iltg-dWatt-Exit | PGE | RSD | New | CZ05 | 8.76 | 0.001 | 0 | 8.58 | 0.00126 | -0.102 | 8.76 | 0.001 | 0 | 8.58 | 0.00126 | -0.102 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.979 | 1.26 | -0.011644 | 8760 | 1 | 8760 | 1 | 0.979 | 1.26 | -0.0116
ExitNonePGERSDNewCZ11 | Com-Iltg-dWatt-Exit | PGE | RSD | New | CZ11 | 8.76 | 0.001 | 0 | 9.11 | 0.00136 | -0.0768 | 8.76 | 0.001 | 0 | 9.11 | 0.00136 | -0.0768 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.04 | 1.36 | -0.0087671 | 8760 | 1 | 8760 | 1 | 1.04 | 1.36 | -0.00877
ExitNonePGERSDNewCZ12 | Com-Iltg-dWatt-Exit | PGE | RSD | New | CZ12 | 8.76 | 0.001 | 0 | 9.02 | 0.00132 | -0.0764 | 8.76 | 0.001 | 0 | 9.02 | 0.00132 | -0.0764 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.03 | 1.32 | -0.0087215 | 8760 | 1 | 8760 | 1 | 1.03 | 1.32 | -0.00872
ExitNonePGERSDNewCZ13 | Com-Iltg-dWatt-Exit | PGE | RSD | New | CZ13 | 8.76 | 0.001 | 0 | 9.17 | 0.00136 | -0.0724 | 8.76 | 0.001 | 0 | 9.17 | 0.00136 | -0.0724 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.05 | 1.36 | -0.0082648 | 8760 | 1 | 8760 | 1 | 1.05 | 1.36 | -0.00826
ExitNonePGERSDNewCZ16 | Com-Iltg-dWatt-Exit | PGE | RSD | New | CZ16 | 8.76 | 0.001 | 0 | 8.32 | 0.00127 | -0.106 | 8.76 | 0.001 | 0 | 8.32 | 0.00127 | -0.106 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.95 | 1.27 | -0.0121 | 8760 | 1 | 8760 | 1 | 0.95 | 1.27 | -0.0121
ExitNonePGERSDNewIOU | Com-Iltg-dWatt-Exit | PGE | RSD | New | IOU | 8.76 | 0.001 | 0 | 8.9 | 0.00132 | -0.0857 | 8.76 | 0.001 | 0 | 8.9 | 0.00132 | -0.0857 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.02 | 1.32 | -0.0097831 | 8760 | 1 | 8760 | 1 | 1.02 | 1.32 | -0.00978
ExitNonePGERt3ExCZ01 | Com-Iltg-dWatt-Exit | PGE | Rt3 | Ex | CZ01 | 8.76 | 0.001 | 0 | 8.29 | 0.00138 | -0.151 | 8.76 | 0.001 | 0 | 8.29 | 0.00138 | -0.151 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.946 | 1.38 | -0.017237 | 8760 | 1 | 8760 | 1 | 0.946 | 1.38 | -0.0172
ExitNonePGERt3ExCZ02 | Com-Iltg-dWatt-Exit | PGE | Rt3 | Ex | CZ02 | 8.76 | 0.001 | 0 | 9.18 | 0.0013 | -0.0752 | 8.76 | 0.001 | 0 | 9.18 | 0.0013 | -0.0752 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.05 | 1.3 | -0.0085845 | 8760 | 1 | 8760 | 1 | 1.05 | 1.3 | -0.00858
ExitNonePGERt3ExCZ03 | Com-Iltg-dWatt-Exit | PGE | Rt3 | Ex | CZ03 | 8.76 | 0.001 | 0 | 9.24 | 0.00133 | -0.0754 | 8.76 | 0.001 | 0 | 9.24 | 0.00133 | -0.0754 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.05 | 1.33 | -0.0086073 | 8760 | 1 | 8760 | 1 | 1.05 | 1.33 | -0.00861
ExitNonePGERt3ExCZ04 | Com-Iltg-dWatt-Exit | PGE | Rt3 | Ex | CZ04 | 8.76 | 0.001 | 0 | 9.42 | 0.00132 | -0.0518 | 8.76 | 0.001 | 0 | 9.42 | 0.00132 | -0.0518 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.08 | 1.32 | -0.0059132 | 8760 | 1 | 8760 | 1 | 1.08 | 1.32 | -0.00591
ExitNonePGERt3ExCZ05 | Com-Iltg-dWatt-Exit | PGE | Rt3 | Ex | CZ05 | 8.76 | 0.001 | 0 | 9.24 | 0.00132 | -0.0649 | 8.76 | 0.001 | 0 | 9.24 | 0.00132 | -0.0649 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.05 | 1.32 | -0.0074087 | 8760 | 1 | 8760 | 1 | 1.05 | 1.32 | -0.00741
ExitNonePGERt3ExCZ11 | Com-Iltg-dWatt-Exit | PGE | Rt3 | Ex | CZ11 | 8.76 | 0.001 | 0 | 9.24 | 0.00132 | -0.0689 | 8.76 | 0.001 | 0 | 9.24 | 0.00132 | -0.0689 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.05 | 1.32 | -0.0078653 | 8760 | 1 | 8760 | 1 | 1.05 | 1.32 | -0.00787
ExitNonePGERt3ExCZ12 | Com-Iltg-dWatt-Exit | PGE | Rt3 | Ex | CZ12 | 8.76 | 0.001 | 0 | 9.24 | 0.00134 | -0.0682 | 8.76 | 0.001 | 0 | 9.24 | 0.00134 | -0.0682 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.05 | 1.34 | -0.0077854 | 8760 | 1 | 8760 | 1 | 1.05 | 1.34 | -0.00779
ExitNonePGERt3ExCZ13 | Com-Iltg-dWatt-Exit | PGE | Rt3 | Ex | CZ13 | 8.76 | 0.001 | 0 | 9.31 | 0.00131 | -0.0649 | 8.76 | 0.001 | 0 | 9.31 | 0.00131 | -0.0649 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.06 | 1.31 | -0.0074087 | 8760 | 1 | 8760 | 1 | 1.06 | 1.31 | -0.00741
ExitNonePGERt3ExCZ16 | Com-Iltg-dWatt-Exit | PGE | Rt3 | Ex | CZ16 | 8.76 | 0.001 | 0 | 8.51 | 0.00128 | -0.129 | 8.76 | 0.001 | 0 | 8.51 | 0.00128 | -0.129 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.971 | 1.28 | -0.014726 | 8760 | 1 | 8760 | 1 | 0.971 | 1.28 | -0.0147
ExitNonePGERt3ExIOU | Com-Iltg-dWatt-Exit | PGE | Rt3 | Ex | IOU | 8.76 | 0.001 | 0 | 9.26 | 0.00133 | -0.0692 | 8.76 | 0.001 | 0 | 9.26 | 0.00133 | -0.0692 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.06 | 1.33 | -0.0078995 | 8760 | 1 | 8760 | 1 | 1.06 | 1.33 | -0.0079
ExitNonePGERt3NewCZ01 | Com-Iltg-dWatt-Exit | PGE | Rt3 | New | CZ01 | 8.76 | 0.001 | 0 | 8.12 | 0.00136 | -0.166 | 8.76 | 0.001 | 0 | 8.12 | 0.00136 | -0.166 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.927 | 1.36 | -0.01895 | 8760 | 1 | 8760 | 1 | 0.927 | 1.36 | -0.019
ExitNonePGERt3NewCZ02 | Com-Iltg-dWatt-Exit | PGE | Rt3 | New | CZ02 | 8.76 | 0.001 | 0 | 8.89 | 0.00125 | -0.0867 | 8.76 | 0.001 | 0 | 8.89 | 0.00125 | -0.0867 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.01 | 1.25 | -0.0098973 | 8760 | 1 | 8760 | 1 | 1.01 | 1.25 | -0.0099
ExitNonePGERt3NewCZ03 | Com-Iltg-dWatt-Exit | PGE | Rt3 | New | CZ03 | 8.76 | 0.001 | 0 | 8.85 | 0.00128 | -0.092 | 8.76 | 0.001 | 0 | 8.85 | 0.00128 | -0.092 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.01 | 1.28 | -0.010502 | 8760 | 1 | 8760 | 1 | 1.01 | 1.28 | -0.0105
ExitNonePGERt3NewCZ04 | Com-Iltg-dWatt-Exit | PGE | Rt3 | New | CZ04 | 8.76 | 0.001 | 0 | 9.13 | 0.00129 | -0.067 | 8.76 | 0.001 | 0 | 9.13 | 0.00129 | -0.067 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.04 | 1.29 | -0.0076484 | 8760 | 1 | 8760 | 1 | 1.04 | 1.29 | -0.00765
ExitNonePGERt3NewCZ05 | Com-Iltg-dWatt-Exit | PGE | Rt3 | New | CZ05 | 8.76 | 0.001 | 0 | 8.89 | 0.00129 | -0.0803 | 8.76 | 0.001 | 0 | 8.89 | 0.00129 | -0.0803 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.01 | 1.29 | -0.0091667 | 8760 | 1 | 8760 | 1 | 1.01 | 1.29 | -0.00917
ExitNonePGERt3NewCZ11 | Com-Iltg-dWatt-Exit | PGE | Rt3 | New | CZ11 | 8.76 | 0.001 | 0 | 9.19 | 0.00131 | -0.0765 | 8.76 | 0.001 | 0 | 9.19 | 0.00131 | -0.0765 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.05 | 1.31 | -0.0087329 | 8760 | 1 | 8760 | 1 | 1.05 | 1.31 | -0.00873
ExitNonePGERt3NewCZ12 | Com-Iltg-dWatt-Exit | PGE | Rt3 | New | CZ12 | 8.76 | 0.001 | 0 | 9.08 | 0.00131 | -0.0778 | 8.76 | 0.001 | 0 | 9.08 | 0.00131 | -0.0778 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.04 | 1.31 | -0.0088813 | 8760 | 1 | 8760 | 1 | 1.04 | 1.31 | -0.00888
ExitNonePGERt3NewCZ13 | Com-Iltg-dWatt-Exit | PGE | Rt3 | New | CZ13 | 8.76 | 0.001 | 0 | 9.18 | 0.00129 | -0.0708 | 8.76 | 0.001 | 0 | 9.18 | 0.00129 | -0.0708 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.05 | 1.29 | -0.0080822 | 8760 | 1 | 8760 | 1 | 1.05 | 1.29 | -0.00808
ExitNonePGERt3NewCZ16 | Com-Iltg-dWatt-Exit | PGE | Rt3 | New | CZ16 | 8.76 | 0.001 | 0 | 8.43 | 0.00127 | -0.128 | 8.76 | 0.001 | 0 | 8.43 | 0.00127 | -0.128 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.962 | 1.27 | -0.014612 | 8760 | 1 | 8760 | 1 | 0.962 | 1.27 | -0.0146
ExitNonePGERt3NewIOU | Com-Iltg-dWatt-Exit | PGE | Rt3 | New | IOU | 8.76 | 0.001 | 0 | 9.02 | 0.00129 | -0.0803 | 8.76 | 0.001 | 0 | 9.02 | 0.00129 | -0.0803 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.03 | 1.29 | -0.0091667 | 8760 | 1 | 8760 | 1 | 1.03 | 1.29 | -0.00917
ExitNonePGERtLExCZ01 | Com-Iltg-dWatt-Exit | PGE | RtL | Ex | CZ01 | 8.76 | 0.001 | 0 | 8.26 | 0.00128 | -0.15 | 8.76 | 0.001 | 0 | 8.26 | 0.00128 | -0.15 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.943 | 1.28 | -0.017123 | 8760 | 1 | 8760 | 1 | 0.943 | 1.28 | -0.0171
ExitNonePGERtLExCZ02 | Com-Iltg-dWatt-Exit | PGE | RtL | Ex | CZ02 | 8.76 | 0.001 | 0 | 9.01 | 0.00126 | -0.0752 | 8.76 | 0.001 | 0 | 9.01 | 0.00126 | -0.0752 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.03 | 1.26 | -0.0085845 | 8760 | 1 | 8760 | 1 | 1.03 | 1.26 | -0.00858
ExitNonePGERtLExCZ03 | Com-Iltg-dWatt-Exit | PGE | RtL | Ex | CZ03 | 8.76 | 0.001 | 0 | 9.02 | 0.00127 | -0.077 | 8.76 | 0.001 | 0 | 9.02 | 0.00127 | -0.077 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.03 | 1.27 | -0.00879 | 8760 | 1 | 8760 | 1 | 1.03 | 1.27 | -0.00879
ExitNonePGERtLExCZ04 | Com-Iltg-dWatt-Exit | PGE | RtL | Ex | CZ04 | 8.76 | 0.001 | 0 | 9.2 | 0.00127 | -0.0572 | 8.76 | 0.001 | 0 | 9.2 | 0.00127 | -0.0572 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.05 | 1.27 | -0.0065297 | 8760 | 1 | 8760 | 1 | 1.05 | 1.27 | -0.00653
ExitNonePGERtLExCZ05 | Com-Iltg-dWatt-Exit | PGE | RtL | Ex | CZ05 | 8.76 | 0.001 | 0 | 8.95 | 0.00125 | -0.0792 | 8.76 | 0.001 | 0 | 8.95 | 0.00125 | -0.0792 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.02 | 1.25 | -0.0090411 | 8760 | 1 | 8760 | 1 | 1.02 | 1.25 | -0.00904
ExitNonePGERtLExCZ11 | Com-Iltg-dWatt-Exit | PGE | RtL | Ex | CZ11 | 8.76 | 0.001 | 0 | 9.11 | 0.00128 | -0.0724 | 8.76 | 0.001 | 0 | 9.11 | 0.00128 | -0.0724 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.04 | 1.28 | -0.0082648 | 8760 | 1 | 8760 | 1 | 1.04 | 1.28 | -0.00826
ExitNonePGERtLExCZ12 | Com-Iltg-dWatt-Exit | PGE | RtL | Ex | CZ12 | 8.76 | 0.001 | 0 | 9.1 | 0.00129 | -0.0681 | 8.76 | 0.001 | 0 | 9.1 | 0.00129 | -0.0681 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.04 | 1.29 | -0.007774 | 8760 | 1 | 8760 | 1 | 1.04 | 1.29 | -0.00777
ExitNonePGERtLExCZ13 | Com-Iltg-dWatt-Exit | PGE | RtL | Ex | CZ13 | 8.76 | 0.001 | 0 | 9.17 | 0.00128 | -0.0663 | 8.76 | 0.001 | 0 | 9.17 | 0.00128 | -0.0663 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.05 | 1.28 | -0.0075685 | 8760 | 1 | 8760 | 1 | 1.05 | 1.28 | -0.00757
ExitNonePGERtLExCZ16 | Com-Iltg-dWatt-Exit | PGE | RtL | Ex | CZ16 | 8.76 | 0.001 | 0 | 8.41 | 0.00121 | -0.123 | 8.76 | 0.001 | 0 | 8.41 | 0.00121 | -0.123 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.96 | 1.21 | -0.014041 | 8760 | 1 | 8760 | 1 | 0.96 | 1.21 | -0.014
ExitNonePGERtLExIOU | Com-Iltg-dWatt-Exit | PGE | RtL | Ex | IOU | 8.76 | 0.001 | 0 | 9.08 | 0.00127 | -0.0712 | 8.76 | 0.001 | 0 | 9.08 | 0.00127 | -0.0712 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.04 | 1.27 | -0.0081279 | 8760 | 1 | 8760 | 1 | 1.04 | 1.27 | -0.00813
ExitNonePGERtLNewCZ01 | Com-Iltg-dWatt-Exit | PGE | RtL | New | CZ01 | 8.76 | 0.001 | 0 | 8.44 | 0.00124 | -0.0811 | 8.76 | 0.001 | 0 | 8.44 | 0.00124 | -0.0811 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.963 | 1.24 | -0.009258 | 8760 | 1 | 8760 | 1 | 0.963 | 1.24 | -0.00926
ExitNonePGERtLNewCZ02 | Com-Iltg-dWatt-Exit | PGE | RtL | New | CZ02 | 8.76 | 0.001 | 0 | 8.91 | 0.00133 | -0.0846 | 8.76 | 0.001 | 0 | 8.91 | 0.00133 | -0.0846 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.02 | 1.33 | -0.0096575 | 8760 | 1 | 8760 | 1 | 1.02 | 1.33 | -0.00966
ExitNonePGERtLNewCZ03 | Com-Iltg-dWatt-Exit | PGE | RtL | New | CZ03 | 8.76 | 0.001 | 0 | 8.8 | 0.00129 | -0.092 | 8.76 | 0.001 | 0 | 8.8 | 0.00129 | -0.092 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1 | 1.29 | -0.010502 | 8760 | 1 | 8760 | 1 | 1 | 1.29 | -0.0105
ExitNonePGERtLNewCZ04 | Com-Iltg-dWatt-Exit | PGE | RtL | New | CZ04 | 8.76 | 0.001 | 0 | 9.12 | 0.00132 | -0.0718 | 8.76 | 0.001 | 0 | 9.12 | 0.00132 | -0.0718 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.04 | 1.32 | -0.0081963 | 8760 | 1 | 8760 | 1 | 1.04 | 1.32 | -0.0082
ExitNonePGERtLNewCZ05 | Com-Iltg-dWatt-Exit | PGE | RtL | New | CZ05 | 8.76 | 0.001 | 0 | 8.81 | 0.00126 | -0.0964 | 8.76 | 0.001 | 0 | 8.81 | 0.00126 | -0.0964 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.01 | 1.26 | -0.011005 | 8760 | 1 | 8760 | 1 | 1.01 | 1.26 | -0.011
ExitNonePGERtLNewCZ11 | Com-Iltg-dWatt-Exit | PGE | RtL | New | CZ11 | 8.76 | 0.001 | 0 | 9.22 | 0.00133 | -0.0823 | 8.76 | 0.001 | 0 | 9.22 | 0.00133 | -0.0823 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.05 | 1.33 | -0.009395 | 8760 | 1 | 8760 | 1 | 1.05 | 1.33 | -0.0094
ExitNonePGERtLNewCZ12 | Com-Iltg-dWatt-Exit | PGE | RtL | New | CZ12 | 8.76 | 0.001 | 0 | 9.15 | 0.00135 | -0.0796 | 8.76 | 0.001 | 0 | 9.15 | 0.00135 | -0.0796 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.04 | 1.35 | -0.0090868 | 8760 | 1 | 8760 | 1 | 1.04 | 1.35 | -0.00909
ExitNonePGERtLNewCZ13 | Com-Iltg-dWatt-Exit | PGE | RtL | New | CZ13 | 8.76 | 0.001 | 0 | 9.27 | 0.00134 | -0.0752 | 8.76 | 0.001 | 0 | 9.27 | 0.00134 | -0.0752 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.06 | 1.34 | -0.0085845 | 8760 | 1 | 8760 | 1 | 1.06 | 1.34 | -0.00858
ExitNonePGERtLNewCZ16 | Com-Iltg-dWatt-Exit | PGE | RtL | New | CZ16 | 8.76 | 0.001 | 0 | 8.46 | 0.00126 | -0.125 | 8.76 | 0.001 | 0 | 8.46 | 0.00126 | -0.125 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.966 | 1.26 | -0.014269 | 8760 | 1 | 8760 | 1 | 0.966 | 1.26 | -0.0143
ExitNonePGERtLNewIOU | Com-Iltg-dWatt-Exit | PGE | RtL | New | IOU | 8.76 | 0.001 | 0 | 9.05 | 0.00132 | -0.0822 | 8.76 | 0.001 | 0 | 9.05 | 0.00132 | -0.0822 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.03 | 1.32 | -0.0093836 | 8760 | 1 | 8760 | 1 | 1.03 | 1.32 | -0.00938
ExitNonePGERtSExCZ01 | Com-Iltg-dWatt-Exit | PGE | RtS | Ex | CZ01 | 8.76 | 0.001 | 0 | 8.3 | 0.00124 | -0.126 | 8.76 | 0.001 | 0 | 8.3 | 0.00124 | -0.126 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.947 | 1.24 | -0.014384 | 8760 | 1 | 8760 | 1 | 0.947 | 1.24 | -0.0144
ExitNonePGERtSExCZ02 | Com-Iltg-dWatt-Exit | PGE | RtS | Ex | CZ02 | 8.76 | 0.001 | 0 | 9.02 | 0.00124 | -0.0695 | 8.76 | 0.001 | 0 | 9.02 | 0.00124 | -0.0695 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.03 | 1.24 | -0.0079338 | 8760 | 1 | 8760 | 1 | 1.03 | 1.24 | -0.00793
ExitNonePGERtSExCZ03 | Com-Iltg-dWatt-Exit | PGE | RtS | Ex | CZ03 | 8.76 | 0.001 | 0 | 8.98 | 0.0013 | -0.0734 | 8.76 | 0.001 | 0 | 8.98 | 0.0013 | -0.0734 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.03 | 1.3 | -0.008379 | 8760 | 1 | 8760 | 1 | 1.03 | 1.3 | -0.00838
ExitNonePGERtSExCZ04 | Com-Iltg-dWatt-Exit | PGE | RtS | Ex | CZ04 | 8.76 | 0.001 | 0 | 9.23 | 0.00129 | -0.054 | 8.76 | 0.001 | 0 | 9.23 | 0.00129 | -0.054 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.05 | 1.29 | -0.0061644 | 8760 | 1 | 8760 | 1 | 1.05 | 1.29 | -0.00616
ExitNonePGERtSExCZ05 | Com-Iltg-dWatt-Exit | PGE | RtS | Ex | CZ05 | 8.76 | 0.001 | 0 | 9.01 | 0.00127 | -0.0653 | 8.76 | 0.001 | 0 | 9.01 | 0.00127 | -0.0653 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.03 | 1.27 | -0.0074543 | 8760 | 1 | 8760 | 1 | 1.03 | 1.27 | -0.00745
ExitNonePGERtSExCZ11 | Com-Iltg-dWatt-Exit | PGE | RtS | Ex | CZ11 | 8.76 | 0.001 | 0 | 9.15 | 0.0013 | -0.0634 | 8.76 | 0.001 | 0 | 9.15 | 0.0013 | -0.0634 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.04 | 1.3 | -0.0072374 | 8760 | 1 | 8760 | 1 | 1.04 | 1.3 | -0.00724
ExitNonePGERtSExCZ12 | Com-Iltg-dWatt-Exit | PGE | RtS | Ex | CZ12 | 8.76 | 0.001 | 0 | 9.1 | 0.00126 | -0.0669 | 8.76 | 0.001 | 0 | 9.1 | 0.00126 | -0.0669 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.04 | 1.26 | -0.007637 | 8760 | 1 | 8760 | 1 | 1.04 | 1.26 | -0.00764
ExitNonePGERtSExCZ13 | Com-Iltg-dWatt-Exit | PGE | RtS | Ex | CZ13 | 8.76 | 0.001 | 0 | 9.18 | 0.00126 | -0.0588 | 8.76 | 0.001 | 0 | 9.18 | 0.00126 | -0.0588 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.05 | 1.26 | -0.0067123 | 8760 | 1 | 8760 | 1 | 1.05 | 1.26 | -0.00671
ExitNonePGERtSExCZ16 | Com-Iltg-dWatt-Exit | PGE | RtS | Ex | CZ16 | 8.76 | 0.001 | 0 | 8.46 | 0.00123 | -0.106 | 8.76 | 0.001 | 0 | 8.46 | 0.00123 | -0.106 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.966 | 1.23 | -0.0121 | 8760 | 1 | 8760 | 1 | 0.966 | 1.23 | -0.0121
ExitNonePGERtSExIOU | Com-Iltg-dWatt-Exit | PGE | RtS | Ex | IOU | 8.76 | 0.001 | 0 | 9.08 | 0.00128 | -0.0668 | 8.76 | 0.001 | 0 | 9.08 | 0.00128 | -0.0668 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.04 | 1.28 | -0.0076256 | 8760 | 1 | 8760 | 1 | 1.04 | 1.28 | -0.00763
ExitNonePGERtSNewCZ01 | Com-Iltg-dWatt-Exit | PGE | RtS | New | CZ01 | 8.76 | 0.001 | 0 | 8.27 | 0.00122 | -0.144 | 8.76 | 0.001 | 0 | 8.27 | 0.00122 | -0.144 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.944 | 1.22 | -0.016438 | 8760 | 1 | 8760 | 1 | 0.944 | 1.22 | -0.0164
ExitNonePGERtSNewCZ02 | Com-Iltg-dWatt-Exit | PGE | RtS | New | CZ02 | 8.76 | 0.001 | 0 | 8.96 | 0.00132 | -0.0777 | 8.76 | 0.001 | 0 | 8.96 | 0.00132 | -0.0777 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.02 | 1.32 | -0.0088699 | 8760 | 1 | 8760 | 1 | 1.02 | 1.32 | -0.00887
ExitNonePGERtSNewCZ03 | Com-Iltg-dWatt-Exit | PGE | RtS | New | CZ03 | 8.76 | 0.001 | 0 | 8.8 | 0.00129 | -0.0791 | 8.76 | 0.001 | 0 | 8.8 | 0.00129 | -0.0791 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1 | 1.29 | -0.0090297 | 8760 | 1 | 8760 | 1 | 1 | 1.29 | -0.00903
ExitNonePGERtSNewCZ04 | Com-Iltg-dWatt-Exit | PGE | RtS | New | CZ04 | 8.76 | 0.001 | 0 | 9.09 | 0.00131 | -0.0618 | 8.76 | 0.001 | 0 | 9.09 | 0.00131 | -0.0618 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.04 | 1.31 | -0.0070548 | 8760 | 1 | 8760 | 1 | 1.04 | 1.31 | -0.00705
ExitNonePGERtSNewCZ05 | Com-Iltg-dWatt-Exit | PGE | RtS | New | CZ05 | 8.76 | 0.001 | 0 | 8.8 | 0.00127 | -0.0738 | 8.76 | 0.001 | 0 | 8.8 | 0.00127 | -0.0738 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1 | 1.27 | -0.0084247 | 8760 | 1 | 8760 | 1 | 1 | 1.27 | -0.00842
ExitNonePGERtSNewCZ11 | Com-Iltg-dWatt-Exit | PGE | RtS | New | CZ11 | 8.76 | 0.001 | 0 | 9.2 | 0.00135 | -0.0625 | 8.76 | 0.001 | 0 | 9.2 | 0.00135 | -0.0625 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.05 | 1.35 | -0.0071347 | 8760 | 1 | 8760 | 1 | 1.05 | 1.35 | -0.00713
ExitNonePGERtSNewCZ12 | Com-Iltg-dWatt-Exit | PGE | RtS | New | CZ12 | 8.76 | 0.001 | 0 | 9.12 | 0.00134 | -0.0716 | 8.76 | 0.001 | 0 | 9.12 | 0.00134 | -0.0716 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.04 | 1.34 | -0.0081735 | 8760 | 1 | 8760 | 1 | 1.04 | 1.34 | -0.00817
ExitNonePGERtSNewCZ13 | Com-Iltg-dWatt-Exit | PGE | RtS | New | CZ13 | 8.76 | 0.001 | 0 | 9.23 | 0.00134 | -0.0624 | 8.76 | 0.001 | 0 | 9.23 | 0.00134 | -0.0624 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.05 | 1.34 | -0.0071233 | 8760 | 1 | 8760 | 1 | 1.05 | 1.34 | -0.00712
ExitNonePGERtSNewCZ16 | Com-Iltg-dWatt-Exit | PGE | RtS | New | CZ16 | 8.76 | 0.001 | 0 | 8.47 | 0.00127 | -0.114 | 8.76 | 0.001 | 0 | 8.47 | 0.00127 | -0.114 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.967 | 1.27 | -0.013014 | 8760 | 1 | 8760 | 1 | 0.967 | 1.27 | -0.013
ExitNonePGERtSNewIOU | Com-Iltg-dWatt-Exit | PGE | RtS | New | IOU | 8.76 | 0.001 | 0 | 9.03 | 0.00132 | -0.0711 | 8.76 | 0.001 | 0 | 9.03 | 0.00132 | -0.0711 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.03 | 1.32 | -0.0081164 | 8760 | 1 | 8760 | 1 | 1.03 | 1.32 | -0.00812
ExitNonePGESCnExCZ01 | Com-Iltg-dWatt-Exit | PGE | SCn | Ex | CZ01 | 8.76 | 0.001 | 0 | 7.45 | 0.001 | -0.145 | 8.76 | 0.001 | 0 | 7.45 | 0.001 | -0.145 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.85 | 1 | -0.016553 | 8760 | 1 | 8760 | 1 | 0.85 | 1 | -0.0166
ExitNonePGESCnExCZ02 | Com-Iltg-dWatt-Exit | PGE | SCn | Ex | CZ02 | 8.76 | 0.001 | 0 | 8.26 | 0.00139 | -0.0781 | 8.76 | 0.001 | 0 | 8.26 | 0.00139 | -0.0781 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.943 | 1.39 | -0.0089155 | 8760 | 1 | 8760 | 1 | 0.943 | 1.39 | -0.00892
ExitNonePGESCnExCZ03 | Com-Iltg-dWatt-Exit | PGE | SCn | Ex | CZ03 | 8.76 | 0.001 | 0 | 8.01 | 0.00147 | -0.0838 | 8.76 | 0.001 | 0 | 8.01 | 0.00147 | -0.0838 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.914 | 1.47 | -0.0095662 | 8760 | 1 | 8760 | 1 | 0.914 | 1.47 | -0.00957
ExitNonePGESCnExCZ04 | Com-Iltg-dWatt-Exit | PGE | SCn | Ex | CZ04 | 8.76 | 0.001 | 0 | 8.52 | 0.00139 | -0.0662 | 8.76 | 0.001 | 0 | 8.52 | 0.00139 | -0.0662 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.973 | 1.39 | -0.0075571 | 8760 | 1 | 8760 | 1 | 0.973 | 1.39 | -0.00756
ExitNonePGESCnExCZ05 | Com-Iltg-dWatt-Exit | PGE | SCn | Ex | CZ05 | 8.76 | 0.001 | 0 | 7.94 | 0.00134 | -0.0894 | 8.76 | 0.001 | 0 | 7.94 | 0.00134 | -0.0894 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.906 | 1.34 | -0.010205 | 8760 | 1 | 8760 | 1 | 0.906 | 1.34 | -0.0102
ExitNonePGESCnExCZ11 | Com-Iltg-dWatt-Exit | PGE | SCn | Ex | CZ11 | 8.76 | 0.001 | 0 | 8.54 | 0.00132 | -0.0698 | 8.76 | 0.001 | 0 | 8.54 | 0.00132 | -0.0698 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.975 | 1.32 | -0.007968 | 8760 | 1 | 8760 | 1 | 0.975 | 1.32 | -0.00797
ExitNonePGESCnExCZ12 | Com-Iltg-dWatt-Exit | PGE | SCn | Ex | CZ12 | 8.76 | 0.001 | 0 | 8.55 | 0.00136 | -0.0705 | 8.76 | 0.001 | 0 | 8.55 | 0.00136 | -0.0705 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.976 | 1.36 | -0.0080479 | 8760 | 1 | 8760 | 1 | 0.976 | 1.36 | -0.00805
ExitNonePGESCnExCZ13 | Com-Iltg-dWatt-Exit | PGE | SCn | Ex | CZ13 | 8.76 | 0.001 | 0 | 8.63 | 0.00131 | -0.0653 | 8.76 | 0.001 | 0 | 8.63 | 0.00131 | -0.0653 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.985 | 1.31 | -0.0074543 | 8760 | 1 | 8760 | 1 | 0.985 | 1.31 | -0.00745
ExitNonePGESCnExCZ16 | Com-Iltg-dWatt-Exit | PGE | SCn | Ex | CZ16 | 8.76 | 0.001 | 0 | 7.66 | 0.00129 | -0.103 | 8.76 | 0.001 | 0 | 7.66 | 0.00129 | -0.103 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.874 | 1.29 | -0.011758 | 8760 | 1 | 8760 | 1 | 0.874 | 1.29 | -0.0118
ExitNonePGESCnExIOU | Com-Iltg-dWatt-Exit | PGE | SCn | Ex | IOU | 8.76 | 0.001 | 0 | 8.33 | 0.00139 | -0.0752 | 8.76 | 0.001 | 0 | 8.33 | 0.00139 | -0.0752 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.951 | 1.39 | -0.0085845 | 8760 | 1 | 8760 | 1 | 0.951 | 1.39 | -0.00858
ExitNonePGESCnNewCZ01 | Com-Iltg-dWatt-Exit | PGE | SCn | New | CZ01 | 8.76 | 0.001 | 0 | 7.52 | 0.001 | -0.155 | 8.76 | 0.001 | 0 | 7.52 | 0.001 | -0.155 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.858 | 1 | -0.017694 | 8760 | 1 | 8760 | 1 | 0.858 | 1 | -0.0177
ExitNonePGESCnNewCZ02 | Com-Iltg-dWatt-Exit | PGE | SCn | New | CZ02 | 8.76 | 0.001 | 0 | 8.33 | 0.00134 | -0.0981 | 8.76 | 0.001 | 0 | 8.33 | 0.00134 | -0.0981 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.951 | 1.34 | -0.011199 | 8760 | 1 | 8760 | 1 | 0.951 | 1.34 | -0.0112
ExitNonePGESCnNewCZ03 | Com-Iltg-dWatt-Exit | PGE | SCn | New | CZ03 | 8.76 | 0.001 | 0 | 7.88 | 0.00129 | -0.0937 | 8.76 | 0.001 | 0 | 7.88 | 0.00129 | -0.0937 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.9 | 1.29 | -0.010696 | 8760 | 1 | 8760 | 1 | 0.9 | 1.29 | -0.0107
ExitNonePGESCnNewCZ04 | Com-Iltg-dWatt-Exit | PGE | SCn | New | CZ04 | 8.76 | 0.001 | 0 | 8.5 | 0.00133 | -0.0894 | 8.76 | 0.001 | 0 | 8.5 | 0.00133 | -0.0894 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.97 | 1.33 | -0.010205 | 8760 | 1 | 8760 | 1 | 0.97 | 1.33 | -0.0102
ExitNonePGESCnNewCZ05 | Com-Iltg-dWatt-Exit | PGE | SCn | New | CZ05 | 8.76 | 0.001 | 0 | 7.95 | 0.00133 | -0.105 | 8.76 | 0.001 | 0 | 7.95 | 0.00133 | -0.105 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.908 | 1.33 | -0.011986 | 8760 | 1 | 8760 | 1 | 0.908 | 1.33 | -0.012
ExitNonePGESCnNewCZ11 | Com-Iltg-dWatt-Exit | PGE | SCn | New | CZ11 | 8.76 | 0.001 | 0 | 8.45 | 0.00128 | -0.0737 | 8.76 | 0.001 | 0 | 8.45 | 0.00128 | -0.0737 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.965 | 1.28 | -0.0084132 | 8760 | 1 | 8760 | 1 | 0.965 | 1.28 | -0.00841
ExitNonePGESCnNewCZ12 | Com-Iltg-dWatt-Exit | PGE | SCn | New | CZ12 | 8.76 | 0.001 | 0 | 8.51 | 0.00131 | -0.0739 | 8.76 | 0.001 | 0 | 8.51 | 0.00131 | -0.0739 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.971 | 1.31 | -0.0084361 | 8760 | 1 | 8760 | 1 | 0.971 | 1.31 | -0.00844
ExitNonePGESCnNewCZ13 | Com-Iltg-dWatt-Exit | PGE | SCn | New | CZ13 | 8.76 | 0.001 | 0 | 8.52 | 0.00127 | -0.0731 | 8.76 | 0.001 | 0 | 8.52 | 0.00127 | -0.0731 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.973 | 1.27 | -0.0083447 | 8760 | 1 | 8760 | 1 | 0.973 | 1.27 | -0.00834
ExitNonePGESCnNewCZ16 | Com-Iltg-dWatt-Exit | PGE | SCn | New | CZ16 | 8.76 | 0.001 | 0 | 7.72 | 0.00125 | -0.104 | 8.76 | 0.001 | 0 | 7.72 | 0.00125 | -0.104 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.881 | 1.25 | -0.011872 | 8760 | 1 | 8760 | 1 | 0.881 | 1.25 | -0.0119
ExitNonePGESCnNewIOU | Com-Iltg-dWatt-Exit | PGE | SCn | New | IOU | 8.76 | 0.001 | 0 | 8.33 | 0.0013 | -0.082 | 8.76 | 0.001 | 0 | 8.33 | 0.0013 | -0.082 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.951 | 1.3 | -0.0093607 | 8760 | 1 | 8760 | 1 | 0.951 | 1.3 | -0.00936
ExitNonePGESUnExCZ01 | Com-Iltg-dWatt-Exit | PGE | SUn | Ex | CZ01 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1 | 1 | 0 | 8760 | 1 | 8760 | 1 | 1 | 1 | 0
ExitNonePGESUnExCZ02 | Com-Iltg-dWatt-Exit | PGE | SUn | Ex | CZ02 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1 | 1 | 0 | 8760 | 1 | 8760 | 1 | 1 | 1 | 0
ExitNonePGESUnExCZ03 | Com-Iltg-dWatt-Exit | PGE | SUn | Ex | CZ03 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1 | 1 | 0 | 8760 | 1 | 8760 | 1 | 1 | 1 | 0
ExitNonePGESUnExCZ04 | Com-Iltg-dWatt-Exit | PGE | SUn | Ex | CZ04 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1 | 1 | 0 | 8760 | 1 | 8760 | 1 | 1 | 1 | 0
ExitNonePGESUnExCZ05 | Com-Iltg-dWatt-Exit | PGE | SUn | Ex | CZ05 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1 | 1 | 0 | 8760 | 1 | 8760 | 1 | 1 | 1 | 0
ExitNonePGESUnExCZ11 | Com-Iltg-dWatt-Exit | PGE | SUn | Ex | CZ11 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1 | 1 | 0 | 8760 | 1 | 8760 | 1 | 1 | 1 | 0
ExitNonePGESUnExCZ12 | Com-Iltg-dWatt-Exit | PGE | SUn | Ex | CZ12 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1 | 1 | 0 | 8760 | 1 | 8760 | 1 | 1 | 1 | 0
ExitNonePGESUnExCZ13 | Com-Iltg-dWatt-Exit | PGE | SUn | Ex | CZ13 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1 | 1 | 0 | 8760 | 1 | 8760 | 1 | 1 | 1 | 0
ExitNonePGESUnExCZ16 | Com-Iltg-dWatt-Exit | PGE | SUn | Ex | CZ16 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1 | 1 | 0 | 8760 | 1 | 8760 | 1 | 1 | 1 | 0
ExitNonePGESUnExIOU | Com-Iltg-dWatt-Exit | PGE | SUn | Ex | IOU | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1 | 1 | 0 | 8760 | 1 | 8760 | 1 | 1 | 1 | 0
ExitNonePGESUnNewCZ01 | Com-Iltg-dWatt-Exit | PGE | SUn | New | CZ01 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1 | 1 | 0 | 8760 | 1 | 8760 | 1 | 1 | 1 | 0
ExitNonePGESUnNewCZ02 | Com-Iltg-dWatt-Exit | PGE | SUn | New | CZ02 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1 | 1 | 0 | 8760 | 1 | 8760 | 1 | 1 | 1 | 0
ExitNonePGESUnNewCZ03 | Com-Iltg-dWatt-Exit | PGE | SUn | New | CZ03 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1 | 1 | 0 | 8760 | 1 | 8760 | 1 | 1 | 1 | 0
ExitNonePGESUnNewCZ04 | Com-Iltg-dWatt-Exit | PGE | SUn | New | CZ04 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1 | 1 | 0 | 8760 | 1 | 8760 | 1 | 1 | 1 | 0
ExitNonePGESUnNewCZ05 | Com-Iltg-dWatt-Exit | PGE | SUn | New | CZ05 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1 | 1 | 0 | 8760 | 1 | 8760 | 1 | 1 | 1 | 0
ExitNonePGESUnNewCZ11 | Com-Iltg-dWatt-Exit | PGE | SUn | New | CZ11 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1 | 1 | 0 | 8760 | 1 | 8760 | 1 | 1 | 1 | 0
ExitNonePGESUnNewCZ12 | Com-Iltg-dWatt-Exit | PGE | SUn | New | CZ12 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1 | 1 | 0 | 8760 | 1 | 8760 | 1 | 1 | 1 | 0
ExitNonePGESUnNewCZ13 | Com-Iltg-dWatt-Exit | PGE | SUn | New | CZ13 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1 | 1 | 0 | 8760 | 1 | 8760 | 1 | 1 | 1 | 0
ExitNonePGESUnNewCZ16 | Com-Iltg-dWatt-Exit | PGE | SUn | New | CZ16 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1 | 1 | 0 | 8760 | 1 | 8760 | 1 | 1 | 1 | 0
ExitNonePGESUnNewIOU | Com-Iltg-dWatt-Exit | PGE | SUn | New | IOU | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1 | 1 | 0 | 8760 | 1 | 8760 | 1 | 1 | 1 | 0
ExitNonePGEWRfExCZ01 | Com-Iltg-dWatt-Exit | PGE | WRf | Ex | CZ01 | 8.76 | 0.001 | 0 | 12.7 | 0.00124 | 0 | 8.76 | 0.001 | 0 | 12.7 | 0.00124 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.45 | 1.24 | 0 | 8760 | 1 | 8760 | 1 | 1.45 | 1.24 | 0
ExitNonePGEWRfExCZ02 | Com-Iltg-dWatt-Exit | PGE | WRf | Ex | CZ02 | 8.76 | 0.001 | 0 | 13.7 | 0.00126 | 0 | 8.76 | 0.001 | 0 | 13.7 | 0.00126 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.56 | 1.26 | 0 | 8760 | 1 | 8760 | 1 | 1.56 | 1.26 | 0
ExitNonePGEWRfExCZ03 | Com-Iltg-dWatt-Exit | PGE | WRf | Ex | CZ03 | 8.76 | 0.001 | 0 | 13.8 | 0.00129 | 0 | 8.76 | 0.001 | 0 | 13.8 | 0.00129 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.58 | 1.29 | 0 | 8760 | 1 | 8760 | 1 | 1.58 | 1.29 | 0
ExitNonePGEWRfExCZ04 | Com-Iltg-dWatt-Exit | PGE | WRf | Ex | CZ04 | 8.76 | 0.001 | 0 | 14.2 | 0.00125 | 0 | 8.76 | 0.001 | 0 | 14.2 | 0.00125 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.62 | 1.25 | 0 | 8760 | 1 | 8760 | 1 | 1.62 | 1.25 | 0
ExitNonePGEWRfExCZ05 | Com-Iltg-dWatt-Exit | PGE | WRf | Ex | CZ05 | 8.76 | 0.001 | 0 | 13.2 | 0.00127 | 0 | 8.76 | 0.001 | 0 | 13.2 | 0.00127 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.51 | 1.27 | 0 | 8760 | 1 | 8760 | 1 | 1.51 | 1.27 | 0
ExitNonePGEWRfExCZ11 | Com-Iltg-dWatt-Exit | PGE | WRf | Ex | CZ11 | 8.76 | 0.001 | 0 | 13.5 | 0.00124 | 0 | 8.76 | 0.001 | 0 | 13.5 | 0.00124 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.54 | 1.24 | 0 | 8760 | 1 | 8760 | 1 | 1.54 | 1.24 | 0
ExitNonePGEWRfExCZ12 | Com-Iltg-dWatt-Exit | PGE | WRf | Ex | CZ12 | 8.76 | 0.001 | 0 | 13.6 | 0.00123 | 0 | 8.76 | 0.001 | 0 | 13.6 | 0.00123 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.55 | 1.23 | 0 | 8760 | 1 | 8760 | 1 | 1.55 | 1.23 | 0
ExitNonePGEWRfExCZ13 | Com-Iltg-dWatt-Exit | PGE | WRf | Ex | CZ13 | 8.76 | 0.001 | 0 | 13.5 | 0.00127 | 0 | 8.76 | 0.001 | 0 | 13.5 | 0.00127 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.54 | 1.27 | 0 | 8760 | 1 | 8760 | 1 | 1.54 | 1.27 | 0
ExitNonePGEWRfExCZ16 | Com-Iltg-dWatt-Exit | PGE | WRf | Ex | CZ16 | 8.76 | 0.001 | 0 | 12.5 | 0.00127 | -0.00321 | 8.76 | 0.001 | 0 | 12.5 | 0.00127 | -0.00321 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.43 | 1.27 | -0.00036644 | 8760 | 1 | 8760 | 1 | 1.43 | 1.27 | -0.000366
ExitNonePGEWRfExIOU | Com-Iltg-dWatt-Exit | PGE | WRf | Ex | IOU | 8.76 | 0.001 | 0 | 13.7 | 0.00127 | -8.76e-07 | 8.76 | 0.001 | 0 | 13.7 | 0.00127 | -8.76e-07 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.56 | 1.27 | -1e-07 | 8760 | 1 | 8760 | 1 | 1.56 | 1.27 | -1e-07
ExitNonePGEWRfNewCZ01 | Com-Iltg-dWatt-Exit | PGE | WRf | New | CZ01 | 8.76 | 0.001 | 0 | 11 | 0.00128 | 0 | 8.76 | 0.001 | 0 | 11 | 0.00128 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.26 | 1.28 | 0 | 8760 | 1 | 8760 | 1 | 1.26 | 1.28 | 0
ExitNonePGEWRfNewCZ02 | Com-Iltg-dWatt-Exit | PGE | WRf | New | CZ02 | 8.76 | 0.001 | 0 | 11.2 | 0.00124 | 0 | 8.76 | 0.001 | 0 | 11.2 | 0.00124 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.28 | 1.24 | 0 | 8760 | 1 | 8760 | 1 | 1.28 | 1.24 | 0
ExitNonePGEWRfNewCZ03 | Com-Iltg-dWatt-Exit | PGE | WRf | New | CZ03 | 8.76 | 0.001 | 0 | 11.6 | 0.002 | 0 | 8.76 | 0.001 | 0 | 11.6 | 0.002 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.32 | 2 | 0 | 8760 | 1 | 8760 | 1 | 1.32 | 2 | 0
ExitNonePGEWRfNewCZ04 | Com-Iltg-dWatt-Exit | PGE | WRf | New | CZ04 | 8.76 | 0.001 | 0 | 12.3 | 0.00129 | 0 | 8.76 | 0.001 | 0 | 12.3 | 0.00129 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.4 | 1.29 | 0 | 8760 | 1 | 8760 | 1 | 1.4 | 1.29 | 0
ExitNonePGEWRfNewCZ05 | Com-Iltg-dWatt-Exit | PGE | WRf | New | CZ05 | 8.76 | 0.001 | 0 | 11.4 | 0.00118 | 0 | 8.76 | 0.001 | 0 | 11.4 | 0.00118 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.3 | 1.18 | 0 | 8760 | 1 | 8760 | 1 | 1.3 | 1.18 | 0
ExitNonePGEWRfNewCZ11 | Com-Iltg-dWatt-Exit | PGE | WRf | New | CZ11 | 8.76 | 0.001 | 0 | 11.7 | 0.00125 | 0 | 8.76 | 0.001 | 0 | 11.7 | 0.00125 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.34 | 1.25 | 0 | 8760 | 1 | 8760 | 1 | 1.34 | 1.25 | 0
ExitNonePGEWRfNewCZ12 | Com-Iltg-dWatt-Exit | PGE | WRf | New | CZ12 | 8.76 | 0.001 | 0 | 12.4 | 0.00126 | 0 | 8.76 | 0.001 | 0 | 12.4 | 0.00126 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.42 | 1.26 | 0 | 8760 | 1 | 8760 | 1 | 1.42 | 1.26 | 0
ExitNonePGEWRfNewCZ13 | Com-Iltg-dWatt-Exit | PGE | WRf | New | CZ13 | 8.76 | 0.001 | 0 | 11.2 | 0.00127 | 0 | 8.76 | 0.001 | 0 | 11.2 | 0.00127 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.28 | 1.27 | 0 | 8760 | 1 | 8760 | 1 | 1.28 | 1.27 | 0
ExitNonePGEWRfNewCZ16 | Com-Iltg-dWatt-Exit | PGE | WRf | New | CZ16 | 8.76 | 0.001 | 0 | 10.9 | 0.00121 | -0.0039 | 8.76 | 0.001 | 0 | 10.9 | 0.00121 | -0.0039 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.24 | 1.21 | -0.00044521 | 8760 | 1 | 8760 | 1 | 1.24 | 1.21 | -0.000445
ExitNonePGEWRfNewIOU | Com-Iltg-dWatt-Exit | PGE | WRf | New | IOU | 8.76 | 0.001 | 0 | 11.8 | 0.00142 | -1.75e-06 | 8.76 | 0.001 | 0 | 11.8 | 0.00142 | -1.75e-06 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.35 | 1.42 | -1.9977e-07 | 8760 | 1 | 8760 | 1 | 1.35 | 1.42 | -2e-07
ExitNoneSCEAsmExCZ05 | Com-Iltg-dWatt-Exit | SCE | Asm | Ex | CZ05 | 8.76 | 0.001 | 0 | 9.11 | 0.00132 | -0.106 | 8.76 | 0.001 | 0 | 9.11 | 0.00132 | -0.106 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.04 | 1.32 | -0.0121 | 8760 | 1 | 8760 | 1 | 1.04 | 1.32 | -0.0121
ExitNoneSCEAsmExCZ06 | Com-Iltg-dWatt-Exit | SCE | Asm | Ex | CZ06 | 8.76 | 0.001 | 0 | 9.75 | 0.00138 | -0.0526 | 8.76 | 0.001 | 0 | 9.75 | 0.00138 | -0.0526 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.11 | 1.38 | -0.0060046 | 8760 | 1 | 8760 | 1 | 1.11 | 1.38 | -0.006
ExitNoneSCEAsmExCZ08 | Com-Iltg-dWatt-Exit | SCE | Asm | Ex | CZ08 | 8.76 | 0.001 | 0 | 9.81 | 0.00132 | -0.0422 | 8.76 | 0.001 | 0 | 9.81 | 0.00132 | -0.0422 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.12 | 1.32 | -0.0048174 | 8760 | 1 | 8760 | 1 | 1.12 | 1.32 | -0.00482
ExitNoneSCEAsmExCZ09 | Com-Iltg-dWatt-Exit | SCE | Asm | Ex | CZ09 | 8.76 | 0.001 | 0 | 9.76 | 0.00137 | -0.0517 | 8.76 | 0.001 | 0 | 9.76 | 0.00137 | -0.0517 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.11 | 1.37 | -0.0059018 | 8760 | 1 | 8760 | 1 | 1.11 | 1.37 | -0.0059
ExitNoneSCEAsmExCZ10 | Com-Iltg-dWatt-Exit | SCE | Asm | Ex | CZ10 | 8.76 | 0.001 | 0 | 9.45 | 0.00131 | -0.0565 | 8.76 | 0.001 | 0 | 9.45 | 0.00131 | -0.0565 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.08 | 1.31 | -0.0064498 | 8760 | 1 | 8760 | 1 | 1.08 | 1.31 | -0.00645
ExitNoneSCEAsmExCZ13 | Com-Iltg-dWatt-Exit | SCE | Asm | Ex | CZ13 | 8.76 | 0.001 | 0 | 9.37 | 0.00132 | -0.0857 | 8.76 | 0.001 | 0 | 9.37 | 0.00132 | -0.0857 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.07 | 1.32 | -0.0097831 | 8760 | 1 | 8760 | 1 | 1.07 | 1.32 | -0.00978
ExitNoneSCEAsmExCZ14 | Com-Iltg-dWatt-Exit | SCE | Asm | Ex | CZ14 | 8.76 | 0.001 | 0 | 9.31 | 0.00119 | -0.0847 | 8.76 | 0.001 | 0 | 9.31 | 0.00119 | -0.0847 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.06 | 1.19 | -0.0096689 | 8760 | 1 | 8760 | 1 | 1.06 | 1.19 | -0.00967
ExitNoneSCEAsmExCZ15 | Com-Iltg-dWatt-Exit | SCE | Asm | Ex | CZ15 | 8.76 | 0.001 | 0 | 11.1 | 0.00127 | -0.0289 | 8.76 | 0.001 | 0 | 11.1 | 0.00127 | -0.0289 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.27 | 1.27 | -0.0032991 | 8760 | 1 | 8760 | 1 | 1.27 | 1.27 | -0.0033
ExitNoneSCEAsmExCZ16 | Com-Iltg-dWatt-Exit | SCE | Asm | Ex | CZ16 | 8.76 | 0.001 | 0 | 8.54 | 0.0013 | -0.129 | 8.76 | 0.001 | 0 | 8.54 | 0.0013 | -0.129 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.975 | 1.3 | -0.014726 | 8760 | 1 | 8760 | 1 | 0.975 | 1.3 | -0.0147
ExitNoneSCEAsmExIOU | Com-Iltg-dWatt-Exit | SCE | Asm | Ex | IOU | 8.76 | 0.001 | 0 | 9.75 | 0.00133 | -0.0521 | 8.76 | 0.001 | 0 | 9.75 | 0.00133 | -0.0521 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.11 | 1.33 | -0.0059475 | 8760 | 1 | 8760 | 1 | 1.11 | 1.33 | -0.00595
ExitNoneSCEAsmNewCZ05 | Com-Iltg-dWatt-Exit | SCE | Asm | New | CZ05 | 8.76 | 0.001 | 0 | 9 | 0.00129 | -0.127 | 8.76 | 0.001 | 0 | 9 | 0.00129 | -0.127 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.03 | 1.29 | -0.014498 | 8760 | 1 | 8760 | 1 | 1.03 | 1.29 | -0.0145
ExitNoneSCEAsmNewCZ06 | Com-Iltg-dWatt-Exit | SCE | Asm | New | CZ06 | 8.76 | 0.001 | 0 | 9.39 | 0.00134 | -0.0682 | 8.76 | 0.001 | 0 | 9.39 | 0.00134 | -0.0682 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.07 | 1.34 | -0.0077854 | 8760 | 1 | 8760 | 1 | 1.07 | 1.34 | -0.00779
ExitNoneSCEAsmNewCZ08 | Com-Iltg-dWatt-Exit | SCE | Asm | New | CZ08 | 8.76 | 0.001 | 0 | 9.54 | 0.00131 | -0.0634 | 8.76 | 0.001 | 0 | 9.54 | 0.00131 | -0.0634 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.09 | 1.31 | -0.0072374 | 8760 | 1 | 8760 | 1 | 1.09 | 1.31 | -0.00724
ExitNoneSCEAsmNewCZ09 | Com-Iltg-dWatt-Exit | SCE | Asm | New | CZ09 | 8.76 | 0.001 | 0 | 9.4 | 0.00137 | -0.0619 | 8.76 | 0.001 | 0 | 9.4 | 0.00137 | -0.0619 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.07 | 1.37 | -0.0070662 | 8760 | 1 | 8760 | 1 | 1.07 | 1.37 | -0.00707
ExitNoneSCEAsmNewCZ10 | Com-Iltg-dWatt-Exit | SCE | Asm | New | CZ10 | 8.76 | 0.001 | 0 | 9.43 | 0.00134 | -0.0577 | 8.76 | 0.001 | 0 | 9.43 | 0.00134 | -0.0577 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.08 | 1.34 | -0.0065868 | 8760 | 1 | 8760 | 1 | 1.08 | 1.34 | -0.00659
ExitNoneSCEAsmNewCZ13 | Com-Iltg-dWatt-Exit | SCE | Asm | New | CZ13 | 8.76 | 0.001 | 0 | 9.43 | 0.00136 | -0.0999 | 8.76 | 0.001 | 0 | 9.43 | 0.00136 | -0.0999 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.08 | 1.36 | -0.011404 | 8760 | 1 | 8760 | 1 | 1.08 | 1.36 | -0.0114
ExitNoneSCEAsmNewCZ14 | Com-Iltg-dWatt-Exit | SCE | Asm | New | CZ14 | 8.76 | 0.001 | 0 | 9.22 | 0.0013 | -0.0902 | 8.76 | 0.001 | 0 | 9.22 | 0.0013 | -0.0902 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.05 | 1.3 | -0.010297 | 8760 | 1 | 8760 | 1 | 1.05 | 1.3 | -0.0103
ExitNoneSCEAsmNewCZ15 | Com-Iltg-dWatt-Exit | SCE | Asm | New | CZ15 | 8.76 | 0.001 | 0 | 10.3 | 0.00136 | -0.0277 | 8.76 | 0.001 | 0 | 10.3 | 0.00136 | -0.0277 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.18 | 1.36 | -0.0031621 | 8760 | 1 | 8760 | 1 | 1.18 | 1.36 | -0.00316
ExitNoneSCEAsmNewCZ16 | Com-Iltg-dWatt-Exit | SCE | Asm | New | CZ16 | 8.76 | 0.001 | 0 | 8.61 | 0.0013 | -0.139 | 8.76 | 0.001 | 0 | 8.61 | 0.0013 | -0.139 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.983 | 1.3 | -0.015868 | 8760 | 1 | 8760 | 1 | 0.983 | 1.3 | -0.0159
ExitNoneSCEAsmNewIOU | Com-Iltg-dWatt-Exit | SCE | Asm | New | IOU | 8.76 | 0.001 | 0 | 9.51 | 0.00134 | -0.063 | 8.76 | 0.001 | 0 | 9.51 | 0.00134 | -0.063 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.09 | 1.34 | -0.0071918 | 8760 | 1 | 8760 | 1 | 1.09 | 1.34 | -0.00719
ExitNoneSCEComExCZ05 | Com-Iltg-dWatt-Exit | SCE | Com | Ex | CZ05 | 8.76 | 0.001 | 0 | 9.1982 | 0.0013453 | -0.085294 | 8.76 | 0.001 | 0 | 9.1982 | 0.0013453 | -0.085294 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.05 | 1.35 | -0.0097368 | 8760 | 1 | 8760 | 1 | 1.05 | 1.35 | -0.00974
ExitNoneSCEComExCZ06 | Com-Iltg-dWatt-Exit | SCE | Com | Ex | CZ06 | 8.76 | 0.001 | 0 | 9.777 | 0.0013441 | -0.03922 | 8.76 | 0.001 | 0 | 9.777 | 0.0013441 | -0.03922 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.12 | 1.34 | -0.0044771 | 8760 | 1 | 8760 | 1 | 1.12 | 1.34 | -0.00448
ExitNoneSCEComExCZ08 | Com-Iltg-dWatt-Exit | SCE | Com | Ex | CZ08 | 8.76 | 0.001 | 0 | 9.7521 | 0.0013515 | -0.033686 | 8.76 | 0.001 | 0 | 9.7521 | 0.0013515 | -0.033686 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.11 | 1.35 | -0.0038454 | 8760 | 1 | 8760 | 1 | 1.11 | 1.35 | -0.00385
ExitNoneSCEComExCZ09 | Com-Iltg-dWatt-Exit | SCE | Com | Ex | CZ09 | 8.76 | 0.001 | 0 | 9.7612 | 0.0013732 | -0.038147 | 8.76 | 0.001 | 0 | 9.7612 | 0.0013732 | -0.038147 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.11 | 1.37 | -0.0043547 | 8760 | 1 | 8760 | 1 | 1.11 | 1.37 | -0.00435
ExitNoneSCEComExCZ10 | Com-Iltg-dWatt-Exit | SCE | Com | Ex | CZ10 | 8.76 | 0.001 | 0 | 9.4657 | 0.0013237 | -0.038474 | 8.76 | 0.001 | 0 | 9.4657 | 0.0013237 | -0.038474 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.08 | 1.32 | -0.004392 | 8760 | 1 | 8760 | 1 | 1.08 | 1.32 | -0.00439
ExitNoneSCEComExCZ13 | Com-Iltg-dWatt-Exit | SCE | Com | Ex | CZ13 | 8.76 | 0.001 | 0 | 9.6401 | 0.0012835 | -0.058 | 8.76 | 0.001 | 0 | 9.6401 | 0.0012835 | -0.058 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.1 | 1.28 | -0.006621 | 8760 | 1 | 8760 | 1 | 1.1 | 1.28 | -0.00662
ExitNoneSCEComExCZ14 | Com-Iltg-dWatt-Exit | SCE | Com | Ex | CZ14 | 8.76 | 0.001 | 0 | 9.4789 | 0.0013479 | -0.063913 | 8.76 | 0.001 | 0 | 9.4789 | 0.0013479 | -0.063913 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.08 | 1.35 | -0.007296 | 8760 | 1 | 8760 | 1 | 1.08 | 1.35 | -0.0073
ExitNoneSCEComExCZ15 | Com-Iltg-dWatt-Exit | SCE | Com | Ex | CZ15 | 8.76 | 0.001 | 0 | 10.4682 | 0.0013417 | -0.017607 | 8.76 | 0.001 | 0 | 10.4682 | 0.0013417 | -0.017607 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.19 | 1.34 | -0.0020099 | 8760 | 1 | 8760 | 1 | 1.19 | 1.34 | -0.00201
ExitNoneSCEComExCZ16 | Com-Iltg-dWatt-Exit | SCE | Com | Ex | CZ16 | 8.76 | 0.001 | 0 | 8.7201 | 0.0012684 | -0.10606 | 8.76 | 0.001 | 0 | 8.7201 | 0.0012684 | -0.10606 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.995 | 1.27 | -0.012108 | 8760 | 1 | 8760 | 1 | 0.995 | 1.27 | -0.0121
ExitNoneSCEComExIOU | Com-Iltg-dWatt-Exit | SCE | Com | Ex | IOU | 8.76 | 0.001 | 0 | 9.6932 | 0.0013452 | -0.038899 | 8.76 | 0.001 | 0 | 9.6932 | 0.0013452 | -0.038899 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.11 | 1.35 | -0.0044406 | 8760 | 1 | 8760 | 1 | 1.11 | 1.35 | -0.00444
ExitNoneSCEComNewCZ05 | Com-Iltg-dWatt-Exit | SCE | Com | New | CZ05 | 8.76 | 0.001 | 0 | 8.9195 | 0.001323 | -0.092541 | 8.76 | 0.001 | 0 | 8.9195 | 0.001323 | -0.092541 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.02 | 1.32 | -0.010564 | 8760 | 1 | 8760 | 1 | 1.02 | 1.32 | -0.0106
ExitNoneSCEComNewCZ06 | Com-Iltg-dWatt-Exit | SCE | Com | New | CZ06 | 8.76 | 0.001 | 0 | 9.4898 | 0.001313 | -0.041455 | 8.76 | 0.001 | 0 | 9.4898 | 0.001313 | -0.041455 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.08 | 1.31 | -0.0047323 | 8760 | 1 | 8760 | 1 | 1.08 | 1.31 | -0.00473
ExitNoneSCEComNewCZ08 | Com-Iltg-dWatt-Exit | SCE | Com | New | CZ08 | 8.76 | 0.001 | 0 | 9.4805 | 0.0013052 | -0.033787 | 8.76 | 0.001 | 0 | 9.4805 | 0.0013052 | -0.033787 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.08 | 1.31 | -0.0038569 | 8760 | 1 | 8760 | 1 | 1.08 | 1.31 | -0.00386
ExitNoneSCEComNewCZ09 | Com-Iltg-dWatt-Exit | SCE | Com | New | CZ09 | 8.76 | 0.001 | 0 | 9.5102 | 0.001363 | -0.039624 | 8.76 | 0.001 | 0 | 9.5102 | 0.001363 | -0.039624 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.09 | 1.36 | -0.0045233 | 8760 | 1 | 8760 | 1 | 1.09 | 1.36 | -0.00452
ExitNoneSCEComNewCZ10 | Com-Iltg-dWatt-Exit | SCE | Com | New | CZ10 | 8.76 | 0.001 | 0 | 9.2983 | 0.0013187 | -0.037843 | 8.76 | 0.001 | 0 | 9.2983 | 0.0013187 | -0.037843 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.06 | 1.32 | -0.00432 | 8760 | 1 | 8760 | 1 | 1.06 | 1.32 | -0.00432
ExitNoneSCEComNewCZ13 | Com-Iltg-dWatt-Exit | SCE | Com | New | CZ13 | 8.76 | 0.001 | 0 | 9.4763 | 0.0013088 | -0.059396 | 8.76 | 0.001 | 0 | 9.4763 | 0.0013088 | -0.059396 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.08 | 1.31 | -0.0067804 | 8760 | 1 | 8760 | 1 | 1.08 | 1.31 | -0.00678
ExitNoneSCEComNewCZ14 | Com-Iltg-dWatt-Exit | SCE | Com | New | CZ14 | 8.76 | 0.001 | 0 | 9.3807 | 0.0013739 | -0.065321 | 8.76 | 0.001 | 0 | 9.3807 | 0.0013739 | -0.065321 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.07 | 1.37 | -0.0074568 | 8760 | 1 | 8760 | 1 | 1.07 | 1.37 | -0.00746
ExitNoneSCEComNewCZ15 | Com-Iltg-dWatt-Exit | SCE | Com | New | CZ15 | 8.76 | 0.001 | 0 | 10.1923 | 0.0014221 | -0.015922 | 8.76 | 0.001 | 0 | 10.1923 | 0.0014221 | -0.015922 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.16 | 1.42 | -0.0018176 | 8760 | 1 | 8760 | 1 | 1.16 | 1.42 | -0.00182
ExitNoneSCEComNewCZ16 | Com-Iltg-dWatt-Exit | SCE | Com | New | CZ16 | 8.76 | 0.001 | 0 | 8.7062 | 0.0012977 | -0.10259 | 8.76 | 0.001 | 0 | 8.7062 | 0.0012977 | -0.10259 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.994 | 1.3 | -0.011712 | 8760 | 1 | 8760 | 1 | 0.994 | 1.3 | -0.0117
ExitNoneSCEComNewIOU | Com-Iltg-dWatt-Exit | SCE | Com | New | IOU | 8.76 | 0.001 | 0 | 9.4315 | 0.0013282 | -0.039842 | 8.76 | 0.001 | 0 | 9.4315 | 0.0013282 | -0.039842 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.08 | 1.33 | -0.0045482 | 8760 | 1 | 8760 | 1 | 1.08 | 1.33 | -0.00455
ExitNoneSCEECCExCZ05 | Com-Iltg-dWatt-Exit | SCE | ECC | Ex | CZ05 | 8.76 | 0.001 | 0 | 9.06 | 0.0015 | -0.118 | 8.76 | 0.001 | 0 | 9.06 | 0.0015 | -0.118 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.03 | 1.5 | -0.01347 | 8760 | 1 | 8760 | 1 | 1.03 | 1.5 | -0.0135
ExitNoneSCEECCExCZ06 | Com-Iltg-dWatt-Exit | SCE | ECC | Ex | CZ06 | 8.76 | 0.001 | 0 | 10.2 | 0.00146 | -0.0558 | 8.76 | 0.001 | 0 | 10.2 | 0.00146 | -0.0558 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.16 | 1.46 | -0.0063699 | 8760 | 1 | 8760 | 1 | 1.16 | 1.46 | -0.00637
ExitNoneSCEECCExCZ08 | Com-Iltg-dWatt-Exit | SCE | ECC | Ex | CZ08 | 8.76 | 0.001 | 0 | 10.3 | 0.00145 | -0.0563 | 8.76 | 0.001 | 0 | 10.3 | 0.00145 | -0.0563 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.18 | 1.45 | -0.0064269 | 8760 | 1 | 8760 | 1 | 1.18 | 1.45 | -0.00643
ExitNoneSCEECCExCZ09 | Com-Iltg-dWatt-Exit | SCE | ECC | Ex | CZ09 | 8.76 | 0.001 | 0 | 9.98 | 0.00149 | -0.0567 | 8.76 | 0.001 | 0 | 9.98 | 0.00149 | -0.0567 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.14 | 1.49 | -0.0064726 | 8760 | 1 | 8760 | 1 | 1.14 | 1.49 | -0.00647
ExitNoneSCEECCExCZ10 | Com-Iltg-dWatt-Exit | SCE | ECC | Ex | CZ10 | 8.76 | 0.001 | 0 | 10 | 0.00147 | -0.0553 | 8.76 | 0.001 | 0 | 10 | 0.00147 | -0.0553 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.14 | 1.47 | -0.0063128 | 8760 | 1 | 8760 | 1 | 1.14 | 1.47 | -0.00631
ExitNoneSCEECCExCZ13 | Com-Iltg-dWatt-Exit | SCE | ECC | Ex | CZ13 | 8.76 | 0.001 | 0 | 9.71 | 0.00144 | -0.0872 | 8.76 | 0.001 | 0 | 9.71 | 0.00144 | -0.0872 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.11 | 1.44 | -0.0099543 | 8760 | 1 | 8760 | 1 | 1.11 | 1.44 | -0.00995
ExitNoneSCEECCExCZ14 | Com-Iltg-dWatt-Exit | SCE | ECC | Ex | CZ14 | 8.76 | 0.001 | 0 | 9.74 | 0.0014 | -0.0902 | 8.76 | 0.001 | 0 | 9.74 | 0.0014 | -0.0902 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.11 | 1.4 | -0.010297 | 8760 | 1 | 8760 | 1 | 1.11 | 1.4 | -0.0103
ExitNoneSCEECCExCZ15 | Com-Iltg-dWatt-Exit | SCE | ECC | Ex | CZ15 | 8.76 | 0.001 | 0 | 11 | 0.00141 | -0.0279 | 8.76 | 0.001 | 0 | 11 | 0.00141 | -0.0279 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.26 | 1.41 | -0.0031849 | 8760 | 1 | 8760 | 1 | 1.26 | 1.41 | -0.00318
ExitNoneSCEECCExCZ16 | Com-Iltg-dWatt-Exit | SCE | ECC | Ex | CZ16 | 8.76 | 0.001 | 0 | 8.94 | 0.00139 | -0.157 | 8.76 | 0.001 | 0 | 8.94 | 0.00139 | -0.157 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.02 | 1.39 | -0.017922 | 8760 | 1 | 8760 | 1 | 1.02 | 1.39 | -0.0179
ExitNoneSCEECCExIOU | Com-Iltg-dWatt-Exit | SCE | ECC | Ex | IOU | 8.76 | 0.001 | 0 | 10.1 | 0.00145 | -0.0646 | 8.76 | 0.001 | 0 | 10.1 | 0.00145 | -0.0646 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.15 | 1.45 | -0.0073744 | 8760 | 1 | 8760 | 1 | 1.15 | 1.45 | -0.00737
ExitNoneSCEECCNewCZ05 | Com-Iltg-dWatt-Exit | SCE | ECC | New | CZ05 | 8.76 | 0.001 | 0 | 8.99 | 0.00151 | -0.143 | 8.76 | 0.001 | 0 | 8.99 | 0.00151 | -0.143 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.03 | 1.51 | -0.016324 | 8760 | 1 | 8760 | 1 | 1.03 | 1.51 | -0.0163
ExitNoneSCEECCNewCZ06 | Com-Iltg-dWatt-Exit | SCE | ECC | New | CZ06 | 8.76 | 0.001 | 0 | 9.54 | 0.00147 | -0.0805 | 8.76 | 0.001 | 0 | 9.54 | 0.00147 | -0.0805 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.09 | 1.47 | -0.0091895 | 8760 | 1 | 8760 | 1 | 1.09 | 1.47 | -0.00919
ExitNoneSCEECCNewCZ08 | Com-Iltg-dWatt-Exit | SCE | ECC | New | CZ08 | 8.76 | 0.001 | 0 | 9.79 | 0.00146 | -0.0676 | 8.76 | 0.001 | 0 | 9.79 | 0.00146 | -0.0676 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.12 | 1.46 | -0.0077169 | 8760 | 1 | 8760 | 1 | 1.12 | 1.46 | -0.00772
ExitNoneSCEECCNewCZ09 | Com-Iltg-dWatt-Exit | SCE | ECC | New | CZ09 | 8.76 | 0.001 | 0 | 9.93 | 0.00148 | -0.0569 | 8.76 | 0.001 | 0 | 9.93 | 0.00148 | -0.0569 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.13 | 1.48 | -0.0064954 | 8760 | 1 | 8760 | 1 | 1.13 | 1.48 | -0.0065
ExitNoneSCEECCNewCZ10 | Com-Iltg-dWatt-Exit | SCE | ECC | New | CZ10 | 8.76 | 0.001 | 0 | 9.93 | 0.00153 | -0.0644 | 8.76 | 0.001 | 0 | 9.93 | 0.00153 | -0.0644 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.13 | 1.53 | -0.0073516 | 8760 | 1 | 8760 | 1 | 1.13 | 1.53 | -0.00735
ExitNoneSCEECCNewCZ13 | Com-Iltg-dWatt-Exit | SCE | ECC | New | CZ13 | 8.76 | 0.001 | 0 | 9.96 | 0.00153 | -0.0858 | 8.76 | 0.001 | 0 | 9.96 | 0.00153 | -0.0858 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.14 | 1.53 | -0.0097945 | 8760 | 1 | 8760 | 1 | 1.14 | 1.53 | -0.00979
ExitNoneSCEECCNewCZ14 | Com-Iltg-dWatt-Exit | SCE | ECC | New | CZ14 | 8.76 | 0.001 | 0 | 10.1 | 0.00143 | -0.101 | 8.76 | 0.001 | 0 | 10.1 | 0.00143 | -0.101 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.15 | 1.43 | -0.01153 | 8760 | 1 | 8760 | 1 | 1.15 | 1.43 | -0.0115
ExitNoneSCEECCNewCZ15 | Com-Iltg-dWatt-Exit | SCE | ECC | New | CZ15 | 8.76 | 0.001 | 0 | 10.8 | 0.0015 | -0.0215 | 8.76 | 0.001 | 0 | 10.8 | 0.0015 | -0.0215 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.23 | 1.5 | -0.0024543 | 8760 | 1 | 8760 | 1 | 1.23 | 1.5 | -0.00245
ExitNoneSCEECCNewCZ16 | Com-Iltg-dWatt-Exit | SCE | ECC | New | CZ16 | 8.76 | 0.001 | 0 | 9.18 | 0.00147 | -0.159 | 8.76 | 0.001 | 0 | 9.18 | 0.00147 | -0.159 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.05 | 1.47 | -0.018151 | 8760 | 1 | 8760 | 1 | 1.05 | 1.47 | -0.0182
ExitNoneSCEECCNewIOU | Com-Iltg-dWatt-Exit | SCE | ECC | New | IOU | 8.76 | 0.001 | 0 | 9.78 | 0.00148 | -0.0797 | 8.76 | 0.001 | 0 | 9.78 | 0.00148 | -0.0797 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.12 | 1.48 | -0.0090982 | 8760 | 1 | 8760 | 1 | 1.12 | 1.48 | -0.0091
ExitNoneSCEEPrExCZ05 | Com-Iltg-dWatt-Exit | SCE | EPr | Ex | CZ05 | 8.76 | 0.001 | 0 | 8.94 | 0.00147 | -0.0822 | 8.76 | 0.001 | 0 | 8.94 | 0.00147 | -0.0822 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.02 | 1.47 | -0.0093836 | 8760 | 1 | 8760 | 1 | 1.02 | 1.47 | -0.00938
ExitNoneSCEEPrExCZ06 | Com-Iltg-dWatt-Exit | SCE | EPr | Ex | CZ06 | 8.76 | 0.001 | 0 | 9.7 | 0.00144 | -0.0455 | 8.76 | 0.001 | 0 | 9.7 | 0.00144 | -0.0455 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.11 | 1.44 | -0.0051941 | 8760 | 1 | 8760 | 1 | 1.11 | 1.44 | -0.00519
ExitNoneSCEEPrExCZ08 | Com-Iltg-dWatt-Exit | SCE | EPr | Ex | CZ08 | 8.76 | 0.001 | 0 | 10.1 | 0.00147 | -0.0362 | 8.76 | 0.001 | 0 | 10.1 | 0.00147 | -0.0362 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.15 | 1.47 | -0.0041324 | 8760 | 1 | 8760 | 1 | 1.15 | 1.47 | -0.00413
ExitNoneSCEEPrExCZ09 | Com-Iltg-dWatt-Exit | SCE | EPr | Ex | CZ09 | 8.76 | 0.001 | 0 | 10.1 | 0.00146 | -0.0384 | 8.76 | 0.001 | 0 | 10.1 | 0.00146 | -0.0384 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.15 | 1.46 | -0.0043836 | 8760 | 1 | 8760 | 1 | 1.15 | 1.46 | -0.00438
ExitNoneSCEEPrExCZ10 | Com-Iltg-dWatt-Exit | SCE | EPr | Ex | CZ10 | 8.76 | 0.001 | 0 | 9.92 | 0.00142 | -0.0466 | 8.76 | 0.001 | 0 | 9.92 | 0.00142 | -0.0466 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.13 | 1.42 | -0.0053196 | 8760 | 1 | 8760 | 1 | 1.13 | 1.42 | -0.00532
ExitNoneSCEEPrExCZ13 | Com-Iltg-dWatt-Exit | SCE | EPr | Ex | CZ13 | 8.76 | 0.001 | 0 | 9.83 | 0.001 | -0.0718 | 8.76 | 0.001 | 0 | 9.83 | 0.001 | -0.0718 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.12 | 1 | -0.0081963 | 8760 | 1 | 8760 | 1 | 1.12 | 1 | -0.0082
ExitNoneSCEEPrExCZ14 | Com-Iltg-dWatt-Exit | SCE | EPr | Ex | CZ14 | 8.76 | 0.001 | 0 | 9.66 | 0.0014 | -0.0711 | 8.76 | 0.001 | 0 | 9.66 | 0.0014 | -0.0711 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.1 | 1.4 | -0.0081164 | 8760 | 1 | 8760 | 1 | 1.1 | 1.4 | -0.00812
ExitNoneSCEEPrExCZ15 | Com-Iltg-dWatt-Exit | SCE | EPr | Ex | CZ15 | 8.76 | 0.001 | 0 | 11.3 | 0.00138 | -0.0194 | 8.76 | 0.001 | 0 | 11.3 | 0.00138 | -0.0194 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.29 | 1.38 | -0.0022146 | 8760 | 1 | 8760 | 1 | 1.29 | 1.38 | -0.00221
ExitNoneSCEEPrExCZ16 | Com-Iltg-dWatt-Exit | SCE | EPr | Ex | CZ16 | 8.76 | 0.001 | 0 | 8.3 | 0.001 | -0.134 | 8.76 | 0.001 | 0 | 8.3 | 0.001 | -0.134 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.947 | 1 | -0.015297 | 8760 | 1 | 8760 | 1 | 0.947 | 1 | -0.0153
ExitNoneSCEEPrExIOU | Com-Iltg-dWatt-Exit | SCE | EPr | Ex | IOU | 8.76 | 0.001 | 0 | 9.93 | 0.00142 | -0.0458 | 8.76 | 0.001 | 0 | 9.93 | 0.00142 | -0.0458 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.13 | 1.42 | -0.0052283 | 8760 | 1 | 8760 | 1 | 1.13 | 1.42 | -0.00523
ExitNoneSCEEPrNewCZ05 | Com-Iltg-dWatt-Exit | SCE | EPr | New | CZ05 | 8.76 | 0.001 | 0 | 8.68 | 0.00146 | -0.099 | 8.76 | 0.001 | 0 | 8.68 | 0.00146 | -0.099 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.991 | 1.46 | -0.011301 | 8760 | 1 | 8760 | 1 | 0.991 | 1.46 | -0.0113
ExitNoneSCEEPrNewCZ06 | Com-Iltg-dWatt-Exit | SCE | EPr | New | CZ06 | 8.76 | 0.001 | 0 | 9.19 | 0.00148 | -0.0613 | 8.76 | 0.001 | 0 | 9.19 | 0.00148 | -0.0613 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.05 | 1.48 | -0.0069977 | 8760 | 1 | 8760 | 1 | 1.05 | 1.48 | -0.007
ExitNoneSCEEPrNewCZ08 | Com-Iltg-dWatt-Exit | SCE | EPr | New | CZ08 | 8.76 | 0.001 | 0 | 9.57 | 0.00149 | -0.0521 | 8.76 | 0.001 | 0 | 9.57 | 0.00149 | -0.0521 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.09 | 1.49 | -0.0059475 | 8760 | 1 | 8760 | 1 | 1.09 | 1.49 | -0.00595
ExitNoneSCEEPrNewCZ09 | Com-Iltg-dWatt-Exit | SCE | EPr | New | CZ09 | 8.76 | 0.001 | 0 | 9.64 | 0.0015 | -0.0544 | 8.76 | 0.001 | 0 | 9.64 | 0.0015 | -0.0544 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.1 | 1.5 | -0.00621 | 8760 | 1 | 8760 | 1 | 1.1 | 1.5 | -0.00621
ExitNoneSCEEPrNewCZ10 | Com-Iltg-dWatt-Exit | SCE | EPr | New | CZ10 | 8.76 | 0.001 | 0 | 9.63 | 0.00155 | -0.0613 | 8.76 | 0.001 | 0 | 9.63 | 0.00155 | -0.0613 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.1 | 1.55 | -0.0069977 | 8760 | 1 | 8760 | 1 | 1.1 | 1.55 | -0.007
ExitNoneSCEEPrNewCZ13 | Com-Iltg-dWatt-Exit | SCE | EPr | New | CZ13 | 8.76 | 0.001 | 0 | 9.61 | 0.001 | -0.0902 | 8.76 | 0.001 | 0 | 9.61 | 0.001 | -0.0902 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.1 | 1 | -0.010297 | 8760 | 1 | 8760 | 1 | 1.1 | 1 | -0.0103
ExitNoneSCEEPrNewCZ14 | Com-Iltg-dWatt-Exit | SCE | EPr | New | CZ14 | 8.76 | 0.001 | 0 | 9.55 | 0.00149 | -0.092 | 8.76 | 0.001 | 0 | 9.55 | 0.00149 | -0.092 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.09 | 1.49 | -0.010502 | 8760 | 1 | 8760 | 1 | 1.09 | 1.49 | -0.0105
ExitNoneSCEEPrNewCZ15 | Com-Iltg-dWatt-Exit | SCE | EPr | New | CZ15 | 8.76 | 0.001 | 0 | 10.8 | 0.00154 | -0.0266 | 8.76 | 0.001 | 0 | 10.8 | 0.00154 | -0.0266 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.23 | 1.54 | -0.0030365 | 8760 | 1 | 8760 | 1 | 1.23 | 1.54 | -0.00304
ExitNoneSCEEPrNewCZ16 | Com-Iltg-dWatt-Exit | SCE | EPr | New | CZ16 | 8.76 | 0.001 | 0 | 8.28 | 0.001 | -0.148 | 8.76 | 0.001 | 0 | 8.28 | 0.001 | -0.148 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.945 | 1 | -0.016895 | 8760 | 1 | 8760 | 1 | 0.945 | 1 | -0.0169
ExitNoneSCEEPrNewIOU | Com-Iltg-dWatt-Exit | SCE | EPr | New | IOU | 8.76 | 0.001 | 0 | 9.54 | 0.00146 | -0.0653 | 8.76 | 0.001 | 0 | 9.54 | 0.00146 | -0.0653 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.09 | 1.46 | -0.0074543 | 8760 | 1 | 8760 | 1 | 1.09 | 1.46 | -0.00745
ExitNoneSCEERCExCZ05 | Com-Iltg-dWatt-Exit | SCE | ERC | Ex | CZ05 | 8.76 | 0.001 | 0 | 8.29 | 0.00123 | -0.132 | 8.76 | 0.001 | 0 | 8.29 | 0.00123 | -0.132 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.946 | 1.23 | -0.015068 | 8760 | 1 | 8760 | 1 | 0.946 | 1.23 | -0.0151
ExitNoneSCEERCExCZ06 | Com-Iltg-dWatt-Exit | SCE | ERC | Ex | CZ06 | 8.76 | 0.001 | 0 | 8.61 | 0.00128 | -0.0781 | 8.76 | 0.001 | 0 | 8.61 | 0.00128 | -0.0781 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.983 | 1.28 | -0.0089155 | 8760 | 1 | 8760 | 1 | 0.983 | 1.28 | -0.00892
ExitNoneSCEERCExCZ08 | Com-Iltg-dWatt-Exit | SCE | ERC | Ex | CZ08 | 8.76 | 0.001 | 0 | 9.14 | 0.00129 | -0.0678 | 8.76 | 0.001 | 0 | 9.14 | 0.00129 | -0.0678 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.04 | 1.29 | -0.0077397 | 8760 | 1 | 8760 | 1 | 1.04 | 1.29 | -0.00774
ExitNoneSCEERCExCZ09 | Com-Iltg-dWatt-Exit | SCE | ERC | Ex | CZ09 | 8.76 | 0.001 | 0 | 9.09 | 0.00127 | -0.0698 | 8.76 | 0.001 | 0 | 9.09 | 0.00127 | -0.0698 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.04 | 1.27 | -0.007968 | 8760 | 1 | 8760 | 1 | 1.04 | 1.27 | -0.00797
ExitNoneSCEERCExCZ10 | Com-Iltg-dWatt-Exit | SCE | ERC | Ex | CZ10 | 8.76 | 0.001 | 0 | 9.11 | 0.00128 | -0.0704 | 8.76 | 0.001 | 0 | 9.11 | 0.00128 | -0.0704 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.04 | 1.28 | -0.0080365 | 8760 | 1 | 8760 | 1 | 1.04 | 1.28 | -0.00804
ExitNoneSCEERCExCZ13 | Com-Iltg-dWatt-Exit | SCE | ERC | Ex | CZ13 | 8.76 | 0.001 | 0 | 8.99 | 0.001 | -0.0862 | 8.76 | 0.001 | 0 | 8.99 | 0.001 | -0.0862 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.03 | 1 | -0.0098402 | 8760 | 1 | 8760 | 1 | 1.03 | 1 | -0.00984
ExitNoneSCEERCExCZ14 | Com-Iltg-dWatt-Exit | SCE | ERC | Ex | CZ14 | 8.76 | 0.001 | 0 | 9.29 | 0.00129 | -0.0902 | 8.76 | 0.001 | 0 | 9.29 | 0.00129 | -0.0902 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.06 | 1.29 | -0.010297 | 8760 | 1 | 8760 | 1 | 1.06 | 1.29 | -0.0103
ExitNoneSCEERCExCZ15 | Com-Iltg-dWatt-Exit | SCE | ERC | Ex | CZ15 | 8.76 | 0.001 | 0 | 10.5 | 0.00131 | -0.042 | 8.76 | 0.001 | 0 | 10.5 | 0.00131 | -0.042 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.2 | 1.31 | -0.0047945 | 8760 | 1 | 8760 | 1 | 1.2 | 1.31 | -0.00479
ExitNoneSCEERCExCZ16 | Com-Iltg-dWatt-Exit | SCE | ERC | Ex | CZ16 | 8.76 | 0.001 | 0 | 8.64 | 0.001 | -0.138 | 8.76 | 0.001 | 0 | 8.64 | 0.001 | -0.138 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.986 | 1 | -0.015753 | 8760 | 1 | 8760 | 1 | 0.986 | 1 | -0.0158
ExitNoneSCEERCExIOU | Com-Iltg-dWatt-Exit | SCE | ERC | Ex | IOU | 8.76 | 0.001 | 0 | 9.04 | 0.00126 | -0.0738 | 8.76 | 0.001 | 0 | 9.04 | 0.00126 | -0.0738 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.03 | 1.26 | -0.0084247 | 8760 | 1 | 8760 | 1 | 1.03 | 1.26 | -0.00842
ExitNoneSCEERCNewCZ05 | Com-Iltg-dWatt-Exit | SCE | ERC | New | CZ05 | 8.76 | 0.001 | 0 | 8.46 | 0.00125 | -0.111 | 8.76 | 0.001 | 0 | 8.46 | 0.00125 | -0.111 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.966 | 1.25 | -0.012671 | 8760 | 1 | 8760 | 1 | 0.966 | 1.25 | -0.0127
ExitNoneSCEERCNewCZ06 | Com-Iltg-dWatt-Exit | SCE | ERC | New | CZ06 | 8.76 | 0.001 | 0 | 9.09 | 0.00127 | -0.0753 | 8.76 | 0.001 | 0 | 9.09 | 0.00127 | -0.0753 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.04 | 1.27 | -0.0085959 | 8760 | 1 | 8760 | 1 | 1.04 | 1.27 | -0.0086
ExitNoneSCEERCNewCZ08 | Com-Iltg-dWatt-Exit | SCE | ERC | New | CZ08 | 8.76 | 0.001 | 0 | 9.22 | 0.00132 | -0.0596 | 8.76 | 0.001 | 0 | 9.22 | 0.00132 | -0.0596 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.05 | 1.32 | -0.0068037 | 8760 | 1 | 8760 | 1 | 1.05 | 1.32 | -0.0068
ExitNoneSCEERCNewCZ09 | Com-Iltg-dWatt-Exit | SCE | ERC | New | CZ09 | 8.76 | 0.001 | 0 | 9.01 | 0.00136 | -0.0616 | 8.76 | 0.001 | 0 | 9.01 | 0.00136 | -0.0616 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.03 | 1.36 | -0.007032 | 8760 | 1 | 8760 | 1 | 1.03 | 1.36 | -0.00703
ExitNoneSCEERCNewCZ10 | Com-Iltg-dWatt-Exit | SCE | ERC | New | CZ10 | 8.76 | 0.001 | 0 | 9.05 | 0.00139 | -0.0709 | 8.76 | 0.001 | 0 | 9.05 | 0.00139 | -0.0709 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.03 | 1.39 | -0.0080936 | 8760 | 1 | 8760 | 1 | 1.03 | 1.39 | -0.00809
ExitNoneSCEERCNewCZ13 | Com-Iltg-dWatt-Exit | SCE | ERC | New | CZ13 | 8.76 | 0.001 | 0 | 9.51 | 0.001 | -0.0911 | 8.76 | 0.001 | 0 | 9.51 | 0.001 | -0.0911 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.09 | 1 | -0.0104 | 8760 | 1 | 8760 | 1 | 1.09 | 1 | -0.0104
ExitNoneSCEERCNewCZ14 | Com-Iltg-dWatt-Exit | SCE | ERC | New | CZ14 | 8.76 | 0.001 | 0 | 9.42 | 0.00137 | -0.0929 | 8.76 | 0.001 | 0 | 9.42 | 0.00137 | -0.0929 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.08 | 1.37 | -0.010605 | 8760 | 1 | 8760 | 1 | 1.08 | 1.37 | -0.0106
ExitNoneSCEERCNewCZ15 | Com-Iltg-dWatt-Exit | SCE | ERC | New | CZ15 | 8.76 | 0.001 | 0 | 10.3 | 0.00138 | -0.0309 | 8.76 | 0.001 | 0 | 10.3 | 0.00138 | -0.0309 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.18 | 1.38 | -0.0035274 | 8760 | 1 | 8760 | 1 | 1.18 | 1.38 | -0.00353
ExitNoneSCEERCNewCZ16 | Com-Iltg-dWatt-Exit | SCE | ERC | New | CZ16 | 8.76 | 0.001 | 0 | 8.45 | 0.001 | -0.145 | 8.76 | 0.001 | 0 | 8.45 | 0.001 | -0.145 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.965 | 1 | -0.016553 | 8760 | 1 | 8760 | 1 | 0.965 | 1 | -0.0166
ExitNoneSCEERCNewIOU | Com-Iltg-dWatt-Exit | SCE | ERC | New | IOU | 8.76 | 0.001 | 0 | 9.15 | 0.00131 | -0.0728 | 8.76 | 0.001 | 0 | 9.15 | 0.00131 | -0.0728 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.04 | 1.31 | -0.0083105 | 8760 | 1 | 8760 | 1 | 1.04 | 1.31 | -0.00831
ExitNoneSCEESeExCZ05 | Com-Iltg-dWatt-Exit | SCE | ESe | Ex | CZ05 | 8.76 | 0.001 | 0 | 8.85 | 0.00144 | -0.0937 | 8.76 | 0.001 | 0 | 8.85 | 0.00144 | -0.0937 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.01 | 1.44 | -0.010696 | 8760 | 1 | 8760 | 1 | 1.01 | 1.44 | -0.0107
ExitNoneSCEESeExCZ06 | Com-Iltg-dWatt-Exit | SCE | ESe | Ex | CZ06 | 8.76 | 0.001 | 0 | 9.6 | 0.00144 | -0.0533 | 8.76 | 0.001 | 0 | 9.6 | 0.00144 | -0.0533 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.1 | 1.44 | -0.0060845 | 8760 | 1 | 8760 | 1 | 1.1 | 1.44 | -0.00608
ExitNoneSCEESeExCZ08 | Com-Iltg-dWatt-Exit | SCE | ESe | Ex | CZ08 | 8.76 | 0.001 | 0 | 10 | 0.00144 | -0.0449 | 8.76 | 0.001 | 0 | 10 | 0.00144 | -0.0449 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.14 | 1.44 | -0.0051256 | 8760 | 1 | 8760 | 1 | 1.14 | 1.44 | -0.00513
ExitNoneSCEESeExCZ09 | Com-Iltg-dWatt-Exit | SCE | ESe | Ex | CZ09 | 8.76 | 0.001 | 0 | 10 | 0.00142 | -0.049 | 8.76 | 0.001 | 0 | 10 | 0.00142 | -0.049 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.14 | 1.42 | -0.0055936 | 8760 | 1 | 8760 | 1 | 1.14 | 1.42 | -0.00559
ExitNoneSCEESeExCZ10 | Com-Iltg-dWatt-Exit | SCE | ESe | Ex | CZ10 | 8.76 | 0.001 | 0 | 10 | 0.0014 | -0.0534 | 8.76 | 0.001 | 0 | 10 | 0.0014 | -0.0534 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.14 | 1.4 | -0.0060959 | 8760 | 1 | 8760 | 1 | 1.14 | 1.4 | -0.0061
ExitNoneSCEESeExCZ13 | Com-Iltg-dWatt-Exit | SCE | ESe | Ex | CZ13 | 8.76 | 0.001 | 0 | 9.94 | 0.001 | -0.0794 | 8.76 | 0.001 | 0 | 9.94 | 0.001 | -0.0794 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.13 | 1 | -0.0090639 | 8760 | 1 | 8760 | 1 | 1.13 | 1 | -0.00906
ExitNoneSCEESeExCZ14 | Com-Iltg-dWatt-Exit | SCE | ESe | Ex | CZ14 | 8.76 | 0.001 | 0 | 9.85 | 0.00132 | -0.0828 | 8.76 | 0.001 | 0 | 9.85 | 0.00132 | -0.0828 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.12 | 1.32 | -0.0094521 | 8760 | 1 | 8760 | 1 | 1.12 | 1.32 | -0.00945
ExitNoneSCEESeExCZ15 | Com-Iltg-dWatt-Exit | SCE | ESe | Ex | CZ15 | 8.76 | 0.001 | 0 | 11.1 | 0.00131 | -0.0256 | 8.76 | 0.001 | 0 | 11.1 | 0.00131 | -0.0256 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.27 | 1.31 | -0.0029224 | 8760 | 1 | 8760 | 1 | 1.27 | 1.31 | -0.00292
ExitNoneSCEESeExCZ16 | Com-Iltg-dWatt-Exit | SCE | ESe | Ex | CZ16 | 8.76 | 0.001 | 0 | 8.61 | 0.001 | -0.131 | 8.76 | 0.001 | 0 | 8.61 | 0.001 | -0.131 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.983 | 1 | -0.014954 | 8760 | 1 | 8760 | 1 | 0.983 | 1 | -0.015
ExitNoneSCEESeExIOU | Com-Iltg-dWatt-Exit | SCE | ESe | Ex | IOU | 8.76 | 0.001 | 0 | 9.92 | 0.00139 | -0.054 | 8.76 | 0.001 | 0 | 9.92 | 0.00139 | -0.054 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.13 | 1.39 | -0.0061644 | 8760 | 1 | 8760 | 1 | 1.13 | 1.39 | -0.00616
ExitNoneSCEESeNewCZ05 | Com-Iltg-dWatt-Exit | SCE | ESe | New | CZ05 | 8.76 | 0.001 | 0 | 8.72 | 0.00142 | -0.107 | 8.76 | 0.001 | 0 | 8.72 | 0.00142 | -0.107 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.995 | 1.42 | -0.012215 | 8760 | 1 | 8760 | 1 | 0.995 | 1.42 | -0.0122
ExitNoneSCEESeNewCZ06 | Com-Iltg-dWatt-Exit | SCE | ESe | New | CZ06 | 8.76 | 0.001 | 0 | 9.22 | 0.00141 | -0.0699 | 8.76 | 0.001 | 0 | 9.22 | 0.00141 | -0.0699 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.05 | 1.41 | -0.0079795 | 8760 | 1 | 8760 | 1 | 1.05 | 1.41 | -0.00798
ExitNoneSCEESeNewCZ08 | Com-Iltg-dWatt-Exit | SCE | ESe | New | CZ08 | 8.76 | 0.001 | 0 | 9.49 | 0.00148 | -0.0517 | 8.76 | 0.001 | 0 | 9.49 | 0.00148 | -0.0517 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.08 | 1.48 | -0.0059018 | 8760 | 1 | 8760 | 1 | 1.08 | 1.48 | -0.0059
ExitNoneSCEESeNewCZ09 | Com-Iltg-dWatt-Exit | SCE | ESe | New | CZ09 | 8.76 | 0.001 | 0 | 9.66 | 0.0015 | -0.0614 | 8.76 | 0.001 | 0 | 9.66 | 0.0015 | -0.0614 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.1 | 1.5 | -0.0070091 | 8760 | 1 | 8760 | 1 | 1.1 | 1.5 | -0.00701
ExitNoneSCEESeNewCZ10 | Com-Iltg-dWatt-Exit | SCE | ESe | New | CZ10 | 8.76 | 0.001 | 0 | 9.63 | 0.00155 | -0.0573 | 8.76 | 0.001 | 0 | 9.63 | 0.00155 | -0.0573 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.1 | 1.55 | -0.0065411 | 8760 | 1 | 8760 | 1 | 1.1 | 1.55 | -0.00654
ExitNoneSCEESeNewCZ13 | Com-Iltg-dWatt-Exit | SCE | ESe | New | CZ13 | 8.76 | 0.001 | 0 | 9.77 | 0.001 | -0.0946 | 8.76 | 0.001 | 0 | 9.77 | 0.001 | -0.0946 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.12 | 1 | -0.010799 | 8760 | 1 | 8760 | 1 | 1.12 | 1 | -0.0108
ExitNoneSCEESeNewCZ14 | Com-Iltg-dWatt-Exit | SCE | ESe | New | CZ14 | 8.76 | 0.001 | 0 | 9.7 | 0.00149 | -0.0972 | 8.76 | 0.001 | 0 | 9.7 | 0.00149 | -0.0972 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.11 | 1.49 | -0.011096 | 8760 | 1 | 8760 | 1 | 1.11 | 1.49 | -0.0111
ExitNoneSCEESeNewCZ15 | Com-Iltg-dWatt-Exit | SCE | ESe | New | CZ15 | 8.76 | 0.001 | 0 | 10.9 | 0.00138 | -0.0417 | 8.76 | 0.001 | 0 | 10.9 | 0.00138 | -0.0417 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.24 | 1.38 | -0.0047603 | 8760 | 1 | 8760 | 1 | 1.24 | 1.38 | -0.00476
ExitNoneSCEESeNewCZ16 | Com-Iltg-dWatt-Exit | SCE | ESe | New | CZ16 | 8.76 | 0.001 | 0 | 8.58 | 0.001 | -0.127 | 8.76 | 0.001 | 0 | 8.58 | 0.001 | -0.127 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.979 | 1 | -0.014498 | 8760 | 1 | 8760 | 1 | 0.979 | 1 | -0.0145
ExitNoneSCEESeNewIOU | Com-Iltg-dWatt-Exit | SCE | ESe | New | IOU | 8.76 | 0.001 | 0 | 9.57 | 0.00144 | -0.0661 | 8.76 | 0.001 | 0 | 9.57 | 0.00144 | -0.0661 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.09 | 1.44 | -0.0075457 | 8760 | 1 | 8760 | 1 | 1.09 | 1.44 | -0.00755
ExitNoneSCEEUnExCZ05 | Com-Iltg-dWatt-Exit | SCE | EUn | Ex | CZ05 | 8.76 | 0.001 | 0 | 9.48 | 0.00134 | -0.083 | 8.76 | 0.001 | 0 | 9.48 | 0.00134 | -0.083 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.08 | 1.34 | -0.0094749 | 8760 | 1 | 8760 | 1 | 1.08 | 1.34 | -0.00947
ExitNoneSCEEUnExCZ06 | Com-Iltg-dWatt-Exit | SCE | EUn | Ex | CZ06 | 8.76 | 0.001 | 0 | 10.2 | 0.00139 | -0.0456 | 8.76 | 0.001 | 0 | 10.2 | 0.00139 | -0.0456 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.16 | 1.39 | -0.0052055 | 8760 | 1 | 8760 | 1 | 1.16 | 1.39 | -0.00521
ExitNoneSCEEUnExCZ08 | Com-Iltg-dWatt-Exit | SCE | EUn | Ex | CZ08 | 8.76 | 0.001 | 0 | 10.3 | 0.0014 | -0.0447 | 8.76 | 0.001 | 0 | 10.3 | 0.0014 | -0.0447 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.18 | 1.4 | -0.0051027 | 8760 | 1 | 8760 | 1 | 1.18 | 1.4 | -0.0051
ExitNoneSCEEUnExCZ09 | Com-Iltg-dWatt-Exit | SCE | EUn | Ex | CZ09 | 8.76 | 0.001 | 0 | 10.1 | 0.00142 | -0.0519 | 8.76 | 0.001 | 0 | 10.1 | 0.00142 | -0.0519 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.15 | 1.42 | -0.0059247 | 8760 | 1 | 8760 | 1 | 1.15 | 1.42 | -0.00592
ExitNoneSCEEUnExCZ10 | Com-Iltg-dWatt-Exit | SCE | EUn | Ex | CZ10 | 8.76 | 0.001 | 0 | 10.2 | 0.00142 | -0.0463 | 8.76 | 0.001 | 0 | 10.2 | 0.00142 | -0.0463 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.16 | 1.42 | -0.0052854 | 8760 | 1 | 8760 | 1 | 1.16 | 1.42 | -0.00529
ExitNoneSCEEUnExCZ13 | Com-Iltg-dWatt-Exit | SCE | EUn | Ex | CZ13 | 8.76 | 0.001 | 0 | 9.64 | 0.00139 | -0.0667 | 8.76 | 0.001 | 0 | 9.64 | 0.00139 | -0.0667 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.1 | 1.39 | -0.0076142 | 8760 | 1 | 8760 | 1 | 1.1 | 1.39 | -0.00761
ExitNoneSCEEUnExCZ14 | Com-Iltg-dWatt-Exit | SCE | EUn | Ex | CZ14 | 8.76 | 0.001 | 0 | 9.7 | 0.00139 | -0.0668 | 8.76 | 0.001 | 0 | 9.7 | 0.00139 | -0.0668 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.11 | 1.39 | -0.0076256 | 8760 | 1 | 8760 | 1 | 1.11 | 1.39 | -0.00763
ExitNoneSCEEUnExCZ15 | Com-Iltg-dWatt-Exit | SCE | EUn | Ex | CZ15 | 8.76 | 0.001 | 0 | 10.8 | 0.00144 | -0.0227 | 8.76 | 0.001 | 0 | 10.8 | 0.00144 | -0.0227 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.23 | 1.44 | -0.0025913 | 8760 | 1 | 8760 | 1 | 1.23 | 1.44 | -0.00259
ExitNoneSCEEUnExCZ16 | Com-Iltg-dWatt-Exit | SCE | EUn | Ex | CZ16 | 8.76 | 0.001 | 0 | 8.98 | 0.00133 | -0.117 | 8.76 | 0.001 | 0 | 8.98 | 0.00133 | -0.117 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.03 | 1.33 | -0.013356 | 8760 | 1 | 8760 | 1 | 1.03 | 1.33 | -0.0134
ExitNoneSCEEUnExIOU | Com-Iltg-dWatt-Exit | SCE | EUn | Ex | IOU | 8.76 | 0.001 | 0 | 10.1 | 0.0014 | -0.0517 | 8.76 | 0.001 | 0 | 10.1 | 0.0014 | -0.0517 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.15 | 1.4 | -0.0059018 | 8760 | 1 | 8760 | 1 | 1.15 | 1.4 | -0.0059
ExitNoneSCEEUnNewCZ05 | Com-Iltg-dWatt-Exit | SCE | EUn | New | CZ05 | 8.76 | 0.001 | 0 | 9.2 | 0.00138 | -0.0955 | 8.76 | 0.001 | 0 | 9.2 | 0.00138 | -0.0955 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.05 | 1.38 | -0.010902 | 8760 | 1 | 8760 | 1 | 1.05 | 1.38 | -0.0109
ExitNoneSCEEUnNewCZ06 | Com-Iltg-dWatt-Exit | SCE | EUn | New | CZ06 | 8.76 | 0.001 | 0 | 9.9 | 0.00138 | -0.0505 | 8.76 | 0.001 | 0 | 9.9 | 0.00138 | -0.0505 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.13 | 1.38 | -0.0057648 | 8760 | 1 | 8760 | 1 | 1.13 | 1.38 | -0.00576
ExitNoneSCEEUnNewCZ08 | Com-Iltg-dWatt-Exit | SCE | EUn | New | CZ08 | 8.76 | 0.001 | 0 | 10.1 | 0.0014 | -0.0293 | 8.76 | 0.001 | 0 | 10.1 | 0.0014 | -0.0293 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.15 | 1.4 | -0.0033447 | 8760 | 1 | 8760 | 1 | 1.15 | 1.4 | -0.00334
ExitNoneSCEEUnNewCZ09 | Com-Iltg-dWatt-Exit | SCE | EUn | New | CZ09 | 8.76 | 0.001 | 0 | 10.1 | 0.00145 | -0.0375 | 8.76 | 0.001 | 0 | 10.1 | 0.00145 | -0.0375 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.15 | 1.45 | -0.0042808 | 8760 | 1 | 8760 | 1 | 1.15 | 1.45 | -0.00428
ExitNoneSCEEUnNewCZ10 | Com-Iltg-dWatt-Exit | SCE | EUn | New | CZ10 | 8.76 | 0.001 | 0 | 10.3 | 0.00148 | -0.0433 | 8.76 | 0.001 | 0 | 10.3 | 0.00148 | -0.0433 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.18 | 1.48 | -0.0049429 | 8760 | 1 | 8760 | 1 | 1.18 | 1.48 | -0.00494
ExitNoneSCEEUnNewCZ13 | Com-Iltg-dWatt-Exit | SCE | EUn | New | CZ13 | 8.76 | 0.001 | 0 | 9.64 | 0.00146 | -0.0902 | 8.76 | 0.001 | 0 | 9.64 | 0.00146 | -0.0902 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.1 | 1.46 | -0.010297 | 8760 | 1 | 8760 | 1 | 1.1 | 1.46 | -0.0103
ExitNoneSCEEUnNewCZ14 | Com-Iltg-dWatt-Exit | SCE | EUn | New | CZ14 | 8.76 | 0.001 | 0 | 9.79 | 0.00143 | -0.0697 | 8.76 | 0.001 | 0 | 9.79 | 0.00143 | -0.0697 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.12 | 1.43 | -0.0079566 | 8760 | 1 | 8760 | 1 | 1.12 | 1.43 | -0.00796
ExitNoneSCEEUnNewCZ15 | Com-Iltg-dWatt-Exit | SCE | EUn | New | CZ15 | 8.76 | 0.001 | 0 | 10.7 | 0.00149 | -0.0187 | 8.76 | 0.001 | 0 | 10.7 | 0.00149 | -0.0187 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.22 | 1.49 | -0.0021347 | 8760 | 1 | 8760 | 1 | 1.22 | 1.49 | -0.00213
ExitNoneSCEEUnNewCZ16 | Com-Iltg-dWatt-Exit | SCE | EUn | New | CZ16 | 8.76 | 0.001 | 0 | 9.09 | 0.00138 | -0.118 | 8.76 | 0.001 | 0 | 9.09 | 0.00138 | -0.118 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.04 | 1.38 | -0.01347 | 8760 | 1 | 8760 | 1 | 1.04 | 1.38 | -0.0135
ExitNoneSCEEUnNewIOU | Com-Iltg-dWatt-Exit | SCE | EUn | New | IOU | 8.76 | 0.001 | 0 | 9.95 | 0.00142 | -0.0514 | 8.76 | 0.001 | 0 | 9.95 | 0.00142 | -0.0514 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.14 | 1.42 | -0.0058676 | 8760 | 1 | 8760 | 1 | 1.14 | 1.42 | -0.00587
ExitNoneSCEGroExCZ05 | Com-Iltg-dWatt-Exit | SCE | Gro | Ex | CZ05 | 8.76 | 0.001 | 0 | 8.51 | 0.00126 | -0.145 | 8.76 | 0.001 | 0 | 8.51 | 0.00126 | -0.145 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.971 | 1.26 | -0.016553 | 8760 | 1 | 8760 | 1 | 0.971 | 1.26 | -0.0166
ExitNoneSCEGroExCZ06 | Com-Iltg-dWatt-Exit | SCE | Gro | Ex | CZ06 | 8.76 | 0.001 | 0 | 9.01 | 0.00127 | -0.126 | 8.76 | 0.001 | 0 | 9.01 | 0.00127 | -0.126 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.03 | 1.27 | -0.014384 | 8760 | 1 | 8760 | 1 | 1.03 | 1.27 | -0.0144
ExitNoneSCEGroExCZ08 | Com-Iltg-dWatt-Exit | SCE | Gro | Ex | CZ08 | 8.76 | 0.001 | 0 | 9.17 | 0.00145 | -0.102 | 8.76 | 0.001 | 0 | 9.17 | 0.00145 | -0.102 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.05 | 1.45 | -0.011644 | 8760 | 1 | 8760 | 1 | 1.05 | 1.45 | -0.0116
ExitNoneSCEGroExCZ09 | Com-Iltg-dWatt-Exit | SCE | Gro | Ex | CZ09 | 8.76 | 0.001 | 0 | 9.15 | 0.00133 | -0.104 | 8.76 | 0.001 | 0 | 9.15 | 0.00133 | -0.104 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.04 | 1.33 | -0.011872 | 8760 | 1 | 8760 | 1 | 1.04 | 1.33 | -0.0119
ExitNoneSCEGroExCZ10 | Com-Iltg-dWatt-Exit | SCE | Gro | Ex | CZ10 | 8.76 | 0.001 | 0 | 9.26 | 0.00133 | -0.108 | 8.76 | 0.001 | 0 | 9.26 | 0.00133 | -0.108 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.06 | 1.33 | -0.012329 | 8760 | 1 | 8760 | 1 | 1.06 | 1.33 | -0.0123
ExitNoneSCEGroExCZ13 | Com-Iltg-dWatt-Exit | SCE | Gro | Ex | CZ13 | 8.76 | 0.001 | 0 | 9.24 | 0.00133 | -0.105 | 8.76 | 0.001 | 0 | 9.24 | 0.00133 | -0.105 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.05 | 1.33 | -0.011986 | 8760 | 1 | 8760 | 1 | 1.05 | 1.33 | -0.012
ExitNoneSCEGroExCZ14 | Com-Iltg-dWatt-Exit | SCE | Gro | Ex | CZ14 | 8.76 | 0.001 | 0 | 9.22 | 0.0015 | -0.103 | 8.76 | 0.001 | 0 | 9.22 | 0.0015 | -0.103 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.05 | 1.5 | -0.011758 | 8760 | 1 | 8760 | 1 | 1.05 | 1.5 | -0.0118
ExitNoneSCEGroExCZ15 | Com-Iltg-dWatt-Exit | SCE | Gro | Ex | CZ15 | 8.76 | 0.001 | 0 | 9.93 | 0.00134 | -0.0633 | 8.76 | 0.001 | 0 | 9.93 | 0.00134 | -0.0633 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.13 | 1.34 | -0.007226 | 8760 | 1 | 8760 | 1 | 1.13 | 1.34 | -0.00723
ExitNoneSCEGroExCZ16 | Com-Iltg-dWatt-Exit | SCE | Gro | Ex | CZ16 | 8.76 | 0.001 | 0 | 8.45 | 0.00128 | -0.137 | 8.76 | 0.001 | 0 | 8.45 | 0.00128 | -0.137 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.965 | 1.28 | -0.015639 | 8760 | 1 | 8760 | 1 | 0.965 | 1.28 | -0.0156
ExitNoneSCEGroExIOU | Com-Iltg-dWatt-Exit | SCE | Gro | Ex | IOU | 8.76 | 0.001 | 0 | 9.16 | 0.00136 | -0.109 | 8.76 | 0.001 | 0 | 9.16 | 0.00136 | -0.109 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.05 | 1.36 | -0.012443 | 8760 | 1 | 8760 | 1 | 1.05 | 1.36 | -0.0124
ExitNoneSCEGroNewCZ05 | Com-Iltg-dWatt-Exit | SCE | Gro | New | CZ05 | 8.76 | 0.001 | 0 | 8.59 | 0.00126 | -0.146 | 8.76 | 0.001 | 0 | 8.59 | 0.00126 | -0.146 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.981 | 1.26 | -0.016667 | 8760 | 1 | 8760 | 1 | 0.981 | 1.26 | -0.0167
ExitNoneSCEGroNewCZ06 | Com-Iltg-dWatt-Exit | SCE | Gro | New | CZ06 | 8.76 | 0.001 | 0 | 9.22 | 0.0013 | -0.119 | 8.76 | 0.001 | 0 | 9.22 | 0.0013 | -0.119 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.05 | 1.3 | -0.013584 | 8760 | 1 | 8760 | 1 | 1.05 | 1.3 | -0.0136
ExitNoneSCEGroNewCZ08 | Com-Iltg-dWatt-Exit | SCE | Gro | New | CZ08 | 8.76 | 0.001 | 0 | 9.38 | 0.00131 | -0.0937 | 8.76 | 0.001 | 0 | 9.38 | 0.00131 | -0.0937 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.07 | 1.31 | -0.010696 | 8760 | 1 | 8760 | 1 | 1.07 | 1.31 | -0.0107
ExitNoneSCEGroNewCZ09 | Com-Iltg-dWatt-Exit | SCE | Gro | New | CZ09 | 8.76 | 0.001 | 0 | 9.32 | 0.00137 | -0.0946 | 8.76 | 0.001 | 0 | 9.32 | 0.00137 | -0.0946 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.06 | 1.37 | -0.010799 | 8760 | 1 | 8760 | 1 | 1.06 | 1.37 | -0.0108
ExitNoneSCEGroNewCZ10 | Com-Iltg-dWatt-Exit | SCE | Gro | New | CZ10 | 8.76 | 0.001 | 0 | 9.5 | 0.00142 | -0.0981 | 8.76 | 0.001 | 0 | 9.5 | 0.00142 | -0.0981 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.08 | 1.42 | -0.011199 | 8760 | 1 | 8760 | 1 | 1.08 | 1.42 | -0.0112
ExitNoneSCEGroNewCZ13 | Com-Iltg-dWatt-Exit | SCE | Gro | New | CZ13 | 8.76 | 0.001 | 0 | 9.48 | 0.00139 | -0.106 | 8.76 | 0.001 | 0 | 9.48 | 0.00139 | -0.106 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.08 | 1.39 | -0.0121 | 8760 | 1 | 8760 | 1 | 1.08 | 1.39 | -0.0121
ExitNoneSCEGroNewCZ14 | Com-Iltg-dWatt-Exit | SCE | Gro | New | CZ14 | 8.76 | 0.001 | 0 | 9.44 | 0.00142 | -0.108 | 8.76 | 0.001 | 0 | 9.44 | 0.00142 | -0.108 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.08 | 1.42 | -0.012329 | 8760 | 1 | 8760 | 1 | 1.08 | 1.42 | -0.0123
ExitNoneSCEGroNewCZ15 | Com-Iltg-dWatt-Exit | SCE | Gro | New | CZ15 | 8.76 | 0.001 | 0 | 10.3 | 0.00141 | -0.0517 | 8.76 | 0.001 | 0 | 10.3 | 0.00141 | -0.0517 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.18 | 1.41 | -0.0059018 | 8760 | 1 | 8760 | 1 | 1.18 | 1.41 | -0.0059
ExitNoneSCEGroNewCZ16 | Com-Iltg-dWatt-Exit | SCE | Gro | New | CZ16 | 8.76 | 0.001 | 0 | 8.62 | 0.00135 | -0.129 | 8.76 | 0.001 | 0 | 8.62 | 0.00135 | -0.129 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.984 | 1.35 | -0.014726 | 8760 | 1 | 8760 | 1 | 0.984 | 1.35 | -0.0147
ExitNoneSCEGroNewIOU | Com-Iltg-dWatt-Exit | SCE | Gro | New | IOU | 8.76 | 0.001 | 0 | 9.41 | 0.00137 | -0.0999 | 8.76 | 0.001 | 0 | 9.41 | 0.00137 | -0.0999 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.07 | 1.37 | -0.011404 | 8760 | 1 | 8760 | 1 | 1.07 | 1.37 | -0.0114
ExitNoneSCEHspExCZ05 | Com-Iltg-dWatt-Exit | SCE | Hsp | Ex | CZ05 | 8.76 | 0.001 | 0 | 9.78 | 0.00125 | -0.0837 | 8.76 | 0.001 | 0 | 9.78 | 0.00125 | -0.0837 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.12 | 1.25 | -0.0095548 | 8760 | 1 | 8760 | 1 | 1.12 | 1.25 | -0.00955
ExitNoneSCEHspExCZ06 | Com-Iltg-dWatt-Exit | SCE | Hsp | Ex | CZ06 | 8.76 | 0.001 | 0 | 10.1 | 0.00128 | -0.062 | 8.76 | 0.001 | 0 | 10.1 | 0.00128 | -0.062 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.15 | 1.28 | -0.0070776 | 8760 | 1 | 8760 | 1 | 1.15 | 1.28 | -0.00708
ExitNoneSCEHspExCZ08 | Com-Iltg-dWatt-Exit | SCE | Hsp | Ex | CZ08 | 8.76 | 0.001 | 0 | 10.2 | 0.00128 | -0.0596 | 8.76 | 0.001 | 0 | 10.2 | 0.00128 | -0.0596 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.16 | 1.28 | -0.0068037 | 8760 | 1 | 8760 | 1 | 1.16 | 1.28 | -0.0068
ExitNoneSCEHspExCZ09 | Com-Iltg-dWatt-Exit | SCE | Hsp | Ex | CZ09 | 8.76 | 0.001 | 0 | 10.3 | 0.00132 | -0.061 | 8.76 | 0.001 | 0 | 10.3 | 0.00132 | -0.061 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.18 | 1.32 | -0.0069635 | 8760 | 1 | 8760 | 1 | 1.18 | 1.32 | -0.00696
ExitNoneSCEHspExCZ10 | Com-Iltg-dWatt-Exit | SCE | Hsp | Ex | CZ10 | 8.76 | 0.001 | 0 | 9.93 | 0.0013 | -0.0654 | 8.76 | 0.001 | 0 | 9.93 | 0.0013 | -0.0654 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.13 | 1.3 | -0.0074658 | 8760 | 1 | 8760 | 1 | 1.13 | 1.3 | -0.00747
ExitNoneSCEHspExCZ13 | Com-Iltg-dWatt-Exit | SCE | Hsp | Ex | CZ13 | 8.76 | 0.001 | 0 | 9.91 | 0.00129 | -0.0722 | 8.76 | 0.001 | 0 | 9.91 | 0.00129 | -0.0722 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.13 | 1.29 | -0.008242 | 8760 | 1 | 8760 | 1 | 1.13 | 1.29 | -0.00824
ExitNoneSCEHspExCZ14 | Com-Iltg-dWatt-Exit | SCE | Hsp | Ex | CZ14 | 8.76 | 0.001 | 0 | 9.72 | 0.00129 | -0.0792 | 8.76 | 0.001 | 0 | 9.72 | 0.00129 | -0.0792 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.11 | 1.29 | -0.0090411 | 8760 | 1 | 8760 | 1 | 1.11 | 1.29 | -0.00904
ExitNoneSCEHspExCZ15 | Com-Iltg-dWatt-Exit | SCE | Hsp | Ex | CZ15 | 8.76 | 0.001 | 0 | 10.4 | 0.00131 | -0.0509 | 8.76 | 0.001 | 0 | 10.4 | 0.00131 | -0.0509 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.19 | 1.31 | -0.0058105 | 8760 | 1 | 8760 | 1 | 1.19 | 1.31 | -0.00581
ExitNoneSCEHspExCZ16 | Com-Iltg-dWatt-Exit | SCE | Hsp | Ex | CZ16 | 8.76 | 0.001 | 0 | 9.04 | 0.00125 | -0.104 | 8.76 | 0.001 | 0 | 9.04 | 0.00125 | -0.104 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.03 | 1.25 | -0.011872 | 8760 | 1 | 8760 | 1 | 1.03 | 1.25 | -0.0119
ExitNoneSCEHspExIOU | Com-Iltg-dWatt-Exit | SCE | Hsp | Ex | IOU | 8.76 | 0.001 | 0 | 10.1 | 0.00129 | -0.0633 | 8.76 | 0.001 | 0 | 10.1 | 0.00129 | -0.0633 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.15 | 1.29 | -0.007226 | 8760 | 1 | 8760 | 1 | 1.15 | 1.29 | -0.00723
ExitNoneSCEHspNewCZ05 | Com-Iltg-dWatt-Exit | SCE | Hsp | New | CZ05 | 8.76 | 0.001 | 0 | 9.03 | 0.00121 | -0.0911 | 8.76 | 0.001 | 0 | 9.03 | 0.00121 | -0.0911 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.03 | 1.21 | -0.0104 | 8760 | 1 | 8760 | 1 | 1.03 | 1.21 | -0.0104
ExitNoneSCEHspNewCZ06 | Com-Iltg-dWatt-Exit | SCE | Hsp | New | CZ06 | 8.76 | 0.001 | 0 | 9.52 | 0.00123 | -0.0679 | 8.76 | 0.001 | 0 | 9.52 | 0.00123 | -0.0679 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.09 | 1.23 | -0.0077511 | 8760 | 1 | 8760 | 1 | 1.09 | 1.23 | -0.00775
ExitNoneSCEHspNewCZ08 | Com-Iltg-dWatt-Exit | SCE | Hsp | New | CZ08 | 8.76 | 0.001 | 0 | 9.58 | 0.00123 | -0.0635 | 8.76 | 0.001 | 0 | 9.58 | 0.00123 | -0.0635 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.09 | 1.23 | -0.0072489 | 8760 | 1 | 8760 | 1 | 1.09 | 1.23 | -0.00725
ExitNoneSCEHspNewCZ09 | Com-Iltg-dWatt-Exit | SCE | Hsp | New | CZ09 | 8.76 | 0.001 | 0 | 9.51 | 0.00127 | -0.0635 | 8.76 | 0.001 | 0 | 9.51 | 0.00127 | -0.0635 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.09 | 1.27 | -0.0072489 | 8760 | 1 | 8760 | 1 | 1.09 | 1.27 | -0.00725
ExitNoneSCEHspNewCZ10 | Com-Iltg-dWatt-Exit | SCE | Hsp | New | CZ10 | 8.76 | 0.001 | 0 | 9.44 | 0.00131 | -0.0708 | 8.76 | 0.001 | 0 | 9.44 | 0.00131 | -0.0708 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.08 | 1.31 | -0.0080822 | 8760 | 1 | 8760 | 1 | 1.08 | 1.31 | -0.00808
ExitNoneSCEHspNewCZ13 | Com-Iltg-dWatt-Exit | SCE | Hsp | New | CZ13 | 8.76 | 0.001 | 0 | 9.49 | 0.0013 | -0.0763 | 8.76 | 0.001 | 0 | 9.49 | 0.0013 | -0.0763 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.08 | 1.3 | -0.00871 | 8760 | 1 | 8760 | 1 | 1.08 | 1.3 | -0.00871
ExitNoneSCEHspNewCZ14 | Com-Iltg-dWatt-Exit | SCE | Hsp | New | CZ14 | 8.76 | 0.001 | 0 | 9.49 | 0.00126 | -0.0847 | 8.76 | 0.001 | 0 | 9.49 | 0.00126 | -0.0847 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.08 | 1.26 | -0.0096689 | 8760 | 1 | 8760 | 1 | 1.08 | 1.26 | -0.00967
ExitNoneSCEHspNewCZ15 | Com-Iltg-dWatt-Exit | SCE | Hsp | New | CZ15 | 8.76 | 0.001 | 0 | 10.1 | 0.00129 | -0.0549 | 8.76 | 0.001 | 0 | 10.1 | 0.00129 | -0.0549 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.15 | 1.29 | -0.0062671 | 8760 | 1 | 8760 | 1 | 1.15 | 1.29 | -0.00627
ExitNoneSCEHspNewCZ16 | Com-Iltg-dWatt-Exit | SCE | Hsp | New | CZ16 | 8.76 | 0.001 | 0 | 8.59 | 0.00122 | -0.115 | 8.76 | 0.001 | 0 | 8.59 | 0.00122 | -0.115 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.981 | 1.22 | -0.013128 | 8760 | 1 | 8760 | 1 | 0.981 | 1.22 | -0.0131
ExitNoneSCEHspNewIOU | Com-Iltg-dWatt-Exit | SCE | Hsp | New | IOU | 8.76 | 0.001 | 0 | 9.5 | 0.00126 | -0.069 | 8.76 | 0.001 | 0 | 9.5 | 0.00126 | -0.069 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.08 | 1.26 | -0.0078767 | 8760 | 1 | 8760 | 1 | 1.08 | 1.26 | -0.00788
ExitNoneSCEHtlExCZ05 | Com-Iltg-dWatt-Exit | SCE | Htl | Ex | CZ05 | 8.76 | 0.001 | 0 | 8.87 | 0.00127 | -0.0421 | 8.76 | 0.001 | 0 | 8.87 | 0.00127 | -0.0421 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.01 | 1.27 | -0.0048059 | 8760 | 1 | 8760 | 1 | 1.01 | 1.27 | -0.00481
ExitNoneSCEHtlExCZ06 | Com-Iltg-dWatt-Exit | SCE | Htl | Ex | CZ06 | 8.76 | 0.001 | 0 | 9.5 | 0.00127 | -0.0276 | 8.76 | 0.001 | 0 | 9.5 | 0.00127 | -0.0276 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.08 | 1.27 | -0.0031507 | 8760 | 1 | 8760 | 1 | 1.08 | 1.27 | -0.00315
ExitNoneSCEHtlExCZ08 | Com-Iltg-dWatt-Exit | SCE | Htl | Ex | CZ08 | 8.76 | 0.001 | 0 | 9.57 | 0.00129 | -0.0255 | 8.76 | 0.001 | 0 | 9.57 | 0.00129 | -0.0255 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.09 | 1.29 | -0.002911 | 8760 | 1 | 8760 | 1 | 1.09 | 1.29 | -0.00291
ExitNoneSCEHtlExCZ09 | Com-Iltg-dWatt-Exit | SCE | Htl | Ex | CZ09 | 8.76 | 0.001 | 0 | 9.54 | 0.0013 | -0.0276 | 8.76 | 0.001 | 0 | 9.54 | 0.0013 | -0.0276 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.09 | 1.3 | -0.0031507 | 8760 | 1 | 8760 | 1 | 1.09 | 1.3 | -0.00315
ExitNoneSCEHtlExCZ10 | Com-Iltg-dWatt-Exit | SCE | Htl | Ex | CZ10 | 8.76 | 0.001 | 0 | 9.35 | 0.0013 | -0.0272 | 8.76 | 0.001 | 0 | 9.35 | 0.0013 | -0.0272 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.07 | 1.3 | -0.003105 | 8760 | 1 | 8760 | 1 | 1.07 | 1.3 | -0.00311
ExitNoneSCEHtlExCZ13 | Com-Iltg-dWatt-Exit | SCE | Htl | Ex | CZ13 | 8.76 | 0.001 | 0 | 9.29 | 0.00128 | -0.0365 | 8.76 | 0.001 | 0 | 9.29 | 0.00128 | -0.0365 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.06 | 1.28 | -0.0041667 | 8760 | 1 | 8760 | 1 | 1.06 | 1.28 | -0.00417
ExitNoneSCEHtlExCZ14 | Com-Iltg-dWatt-Exit | SCE | Htl | Ex | CZ14 | 8.76 | 0.001 | 0 | 9.21 | 0.00131 | -0.0363 | 8.76 | 0.001 | 0 | 9.21 | 0.00131 | -0.0363 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.05 | 1.31 | -0.0041438 | 8760 | 1 | 8760 | 1 | 1.05 | 1.31 | -0.00414
ExitNoneSCEHtlExCZ15 | Com-Iltg-dWatt-Exit | SCE | Htl | Ex | CZ15 | 8.76 | 0.001 | 0 | 10.1 | 0.0013 | -0.0151 | 8.76 | 0.001 | 0 | 10.1 | 0.0013 | -0.0151 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.15 | 1.3 | -0.0017237 | 8760 | 1 | 8760 | 1 | 1.15 | 1.3 | -0.00172
ExitNoneSCEHtlExCZ16 | Com-Iltg-dWatt-Exit | SCE | Htl | Ex | CZ16 | 8.76 | 0.001 | 0 | 8.26 | 0.00127 | -0.0601 | 8.76 | 0.001 | 0 | 8.26 | 0.00127 | -0.0601 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.943 | 1.27 | -0.0068607 | 8760 | 1 | 8760 | 1 | 0.943 | 1.27 | -0.00686
ExitNoneSCEHtlExIOU | Com-Iltg-dWatt-Exit | SCE | Htl | Ex | IOU | 8.76 | 0.001 | 0 | 9.54 | 0.00129 | -0.0269 | 8.76 | 0.001 | 0 | 9.54 | 0.00129 | -0.0269 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.09 | 1.29 | -0.0030708 | 8760 | 1 | 8760 | 1 | 1.09 | 1.29 | -0.00307
ExitNoneSCEHtlNewCZ05 | Com-Iltg-dWatt-Exit | SCE | Htl | New | CZ05 | 8.76 | 0.001 | 0 | 8.4 | 0.00129 | -0.0519 | 8.76 | 0.001 | 0 | 8.4 | 0.00129 | -0.0519 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.959 | 1.29 | -0.0059247 | 8760 | 1 | 8760 | 1 | 0.959 | 1.29 | -0.00592
ExitNoneSCEHtlNewCZ06 | Com-Iltg-dWatt-Exit | SCE | Htl | New | CZ06 | 8.76 | 0.001 | 0 | 9.22 | 0.0013 | -0.03 | 8.76 | 0.001 | 0 | 9.22 | 0.0013 | -0.03 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.05 | 1.3 | -0.0034247 | 8760 | 1 | 8760 | 1 | 1.05 | 1.3 | -0.00342
ExitNoneSCEHtlNewCZ08 | Com-Iltg-dWatt-Exit | SCE | Htl | New | CZ08 | 8.76 | 0.001 | 0 | 9.36 | 0.00131 | -0.028 | 8.76 | 0.001 | 0 | 9.36 | 0.00131 | -0.028 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.07 | 1.31 | -0.0031963 | 8760 | 1 | 8760 | 1 | 1.07 | 1.31 | -0.0032
ExitNoneSCEHtlNewCZ09 | Com-Iltg-dWatt-Exit | SCE | Htl | New | CZ09 | 8.76 | 0.001 | 0 | 9.31 | 0.00137 | -0.0303 | 8.76 | 0.001 | 0 | 9.31 | 0.00137 | -0.0303 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.06 | 1.37 | -0.0034589 | 8760 | 1 | 8760 | 1 | 1.06 | 1.37 | -0.00346
ExitNoneSCEHtlNewCZ10 | Com-Iltg-dWatt-Exit | SCE | Htl | New | CZ10 | 8.76 | 0.001 | 0 | 9.29 | 0.00136 | -0.0285 | 8.76 | 0.001 | 0 | 9.29 | 0.00136 | -0.0285 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.06 | 1.36 | -0.0032534 | 8760 | 1 | 8760 | 1 | 1.06 | 1.36 | -0.00325
ExitNoneSCEHtlNewCZ13 | Com-Iltg-dWatt-Exit | SCE | Htl | New | CZ13 | 8.76 | 0.001 | 0 | 9.02 | 0.00136 | -0.0449 | 8.76 | 0.001 | 0 | 9.02 | 0.00136 | -0.0449 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.03 | 1.36 | -0.0051256 | 8760 | 1 | 8760 | 1 | 1.03 | 1.36 | -0.00513
ExitNoneSCEHtlNewCZ14 | Com-Iltg-dWatt-Exit | SCE | Htl | New | CZ14 | 8.76 | 0.001 | 0 | 8.98 | 0.00135 | -0.0463 | 8.76 | 0.001 | 0 | 8.98 | 0.00135 | -0.0463 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.03 | 1.35 | -0.0052854 | 8760 | 1 | 8760 | 1 | 1.03 | 1.35 | -0.00529
ExitNoneSCEHtlNewCZ15 | Com-Iltg-dWatt-Exit | SCE | Htl | New | CZ15 | 8.76 | 0.001 | 0 | 10.2 | 0.00137 | -0.0147 | 8.76 | 0.001 | 0 | 10.2 | 0.00137 | -0.0147 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.16 | 1.37 | -0.0016781 | 8760 | 1 | 8760 | 1 | 1.16 | 1.37 | -0.00168
ExitNoneSCEHtlNewCZ16 | Com-Iltg-dWatt-Exit | SCE | Htl | New | CZ16 | 8.76 | 0.001 | 0 | 8.02 | 0.00128 | -0.0741 | 8.76 | 0.001 | 0 | 8.02 | 0.00128 | -0.0741 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.916 | 1.28 | -0.0084589 | 8760 | 1 | 8760 | 1 | 0.916 | 1.28 | -0.00846
ExitNoneSCEHtlNewIOU | Com-Iltg-dWatt-Exit | SCE | Htl | New | IOU | 8.76 | 0.001 | 0 | 9.43 | 0.00134 | -0.029 | 8.76 | 0.001 | 0 | 9.43 | 0.00134 | -0.029 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.08 | 1.34 | -0.0033105 | 8760 | 1 | 8760 | 1 | 1.08 | 1.34 | -0.00331
ExitNoneSCEMBTExCZ05 | Com-Iltg-dWatt-Exit | SCE | MBT | Ex | CZ05 | 8.76 | 0.001 | 0 | 10 | 0.00148 | -0.00722 | 8.76 | 0.001 | 0 | 10 | 0.00148 | -0.00722 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.14 | 1.48 | -0.0008242 | 8760 | 1 | 8760 | 1 | 1.14 | 1.48 | -0.000824
ExitNoneSCEMBTExCZ06 | Com-Iltg-dWatt-Exit | SCE | MBT | Ex | CZ06 | 8.76 | 0.001 | 0 | 10.3 | 0.00128 | -0.00341 | 8.76 | 0.001 | 0 | 10.3 | 0.00128 | -0.00341 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.18 | 1.28 | -0.00038927 | 8760 | 1 | 8760 | 1 | 1.18 | 1.28 | -0.000389
ExitNoneSCEMBTExCZ08 | Com-Iltg-dWatt-Exit | SCE | MBT | Ex | CZ08 | 8.76 | 0.001 | 0 | 10.3 | 0.0014 | -0.00241 | 8.76 | 0.001 | 0 | 10.3 | 0.0014 | -0.00241 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.18 | 1.4 | -0.00027511 | 8760 | 1 | 8760 | 1 | 1.18 | 1.4 | -0.000275
ExitNoneSCEMBTExCZ09 | Com-Iltg-dWatt-Exit | SCE | MBT | Ex | CZ09 | 8.76 | 0.001 | 0 | 10.3 | 0.0014 | -0.00412 | 8.76 | 0.001 | 0 | 10.3 | 0.0014 | -0.00412 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.18 | 1.4 | -0.00047032 | 8760 | 1 | 8760 | 1 | 1.18 | 1.4 | -0.00047
ExitNoneSCEMBTExCZ10 | Com-Iltg-dWatt-Exit | SCE | MBT | Ex | CZ10 | 8.76 | 0.001 | 0 | 9.98 | 0.0014 | -0.00445 | 8.76 | 0.001 | 0 | 9.98 | 0.0014 | -0.00445 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.14 | 1.4 | -0.00050799 | 8760 | 1 | 8760 | 1 | 1.14 | 1.4 | -0.000508
ExitNoneSCEMBTExCZ13 | Com-Iltg-dWatt-Exit | SCE | MBT | Ex | CZ13 | 8.76 | 0.001 | 0 | 10.1 | 0.00127 | -0.00972 | 8.76 | 0.001 | 0 | 10.1 | 0.00127 | -0.00972 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.15 | 1.27 | -0.0011096 | 8760 | 1 | 8760 | 1 | 1.15 | 1.27 | -0.00111
ExitNoneSCEMBTExCZ14 | Com-Iltg-dWatt-Exit | SCE | MBT | Ex | CZ14 | 8.76 | 0.001 | 0 | 10 | 0.00138 | -0.0103 | 8.76 | 0.001 | 0 | 10 | 0.00138 | -0.0103 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.14 | 1.38 | -0.0011758 | 8760 | 1 | 8760 | 1 | 1.14 | 1.38 | -0.00118
ExitNoneSCEMBTExCZ15 | Com-Iltg-dWatt-Exit | SCE | MBT | Ex | CZ15 | 8.76 | 0.001 | 0 | 10.7 | 0.00142 | -0.00071 | 8.76 | 0.001 | 0 | 10.7 | 0.00142 | -0.00071 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.22 | 1.42 | -8.105e-05 | 8760 | 1 | 8760 | 1 | 1.22 | 1.42 | -8.11e-05
ExitNoneSCEMBTExCZ16 | Com-Iltg-dWatt-Exit | SCE | MBT | Ex | CZ16 | 8.76 | 0.001 | 0 | 9.34 | 0.00126 | -0.0338 | 8.76 | 0.001 | 0 | 9.34 | 0.00126 | -0.0338 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.07 | 1.26 | -0.0038584 | 8760 | 1 | 8760 | 1 | 1.07 | 1.26 | -0.00386
ExitNoneSCEMBTExIOU | Com-Iltg-dWatt-Exit | SCE | MBT | Ex | IOU | 8.76 | 0.001 | 0 | 10.2 | 0.00137 | -0.00429 | 8.76 | 0.001 | 0 | 10.2 | 0.00137 | -0.00429 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.16 | 1.37 | -0.00048973 | 8760 | 1 | 8760 | 1 | 1.16 | 1.37 | -0.00049
ExitNoneSCEMBTNewCZ05 | Com-Iltg-dWatt-Exit | SCE | MBT | New | CZ05 | 8.76 | 0.001 | 0 | 9.45 | 0.0014 | -0.00646 | 8.76 | 0.001 | 0 | 9.45 | 0.0014 | -0.00646 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.08 | 1.4 | -0.00073744 | 8760 | 1 | 8760 | 1 | 1.08 | 1.4 | -0.000737
ExitNoneSCEMBTNewCZ06 | Com-Iltg-dWatt-Exit | SCE | MBT | New | CZ06 | 8.76 | 0.001 | 0 | 9.8 | 0.00134 | -0.00537 | 8.76 | 0.001 | 0 | 9.8 | 0.00134 | -0.00537 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.12 | 1.34 | -0.00061301 | 8760 | 1 | 8760 | 1 | 1.12 | 1.34 | -0.000613
ExitNoneSCEMBTNewCZ08 | Com-Iltg-dWatt-Exit | SCE | MBT | New | CZ08 | 8.76 | 0.001 | 0 | 9.8 | 0.0014 | -0.00387 | 8.76 | 0.001 | 0 | 9.8 | 0.0014 | -0.00387 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.12 | 1.4 | -0.00044178 | 8760 | 1 | 8760 | 1 | 1.12 | 1.4 | -0.000442
ExitNoneSCEMBTNewCZ09 | Com-Iltg-dWatt-Exit | SCE | MBT | New | CZ09 | 8.76 | 0.001 | 0 | 9.76 | 0.00142 | -0.00473 | 8.76 | 0.001 | 0 | 9.76 | 0.00142 | -0.00473 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.11 | 1.42 | -0.00053995 | 8760 | 1 | 8760 | 1 | 1.11 | 1.42 | -0.00054
ExitNoneSCEMBTNewCZ10 | Com-Iltg-dWatt-Exit | SCE | MBT | New | CZ10 | 8.76 | 0.001 | 0 | 9.78 | 0.00147 | -0.00535 | 8.76 | 0.001 | 0 | 9.78 | 0.00147 | -0.00535 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.12 | 1.47 | -0.00061073 | 8760 | 1 | 8760 | 1 | 1.12 | 1.47 | -0.000611
ExitNoneSCEMBTNewCZ13 | Com-Iltg-dWatt-Exit | SCE | MBT | New | CZ13 | 8.76 | 0.001 | 0 | 9.61 | 0.00139 | -0.00843 | 8.76 | 0.001 | 0 | 9.61 | 0.00139 | -0.00843 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.1 | 1.39 | -0.00096233 | 8760 | 1 | 8760 | 1 | 1.1 | 1.39 | -0.000962
ExitNoneSCEMBTNewCZ14 | Com-Iltg-dWatt-Exit | SCE | MBT | New | CZ14 | 8.76 | 0.001 | 0 | 9.64 | 0.00144 | -0.00851 | 8.76 | 0.001 | 0 | 9.64 | 0.00144 | -0.00851 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.1 | 1.44 | -0.00097146 | 8760 | 1 | 8760 | 1 | 1.1 | 1.44 | -0.000971
ExitNoneSCEMBTNewCZ15 | Com-Iltg-dWatt-Exit | SCE | MBT | New | CZ15 | 8.76 | 0.001 | 0 | 10.3 | 0.0015 | -0.00187 | 8.76 | 0.001 | 0 | 10.3 | 0.0015 | -0.00187 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.18 | 1.5 | -0.00021347 | 8760 | 1 | 8760 | 1 | 1.18 | 1.5 | -0.000213
ExitNoneSCEMBTNewCZ16 | Com-Iltg-dWatt-Exit | SCE | MBT | New | CZ16 | 8.76 | 0.001 | 0 | 9.15 | 0.00134 | -0.0283 | 8.76 | 0.001 | 0 | 9.15 | 0.00134 | -0.0283 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.04 | 1.34 | -0.0032306 | 8760 | 1 | 8760 | 1 | 1.04 | 1.34 | -0.00323
ExitNoneSCEMBTNewIOU | Com-Iltg-dWatt-Exit | SCE | MBT | New | IOU | 8.76 | 0.001 | 0 | 9.81 | 0.00142 | -0.00554 | 8.76 | 0.001 | 0 | 9.81 | 0.00142 | -0.00554 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.12 | 1.42 | -0.00063242 | 8760 | 1 | 8760 | 1 | 1.12 | 1.42 | -0.000632
ExitNoneSCEMLIExCZ05 | Com-Iltg-dWatt-Exit | SCE | MLI | Ex | CZ05 | 8.76 | 0.001 | 0 | 9.01 | 0.00147 | -0.053 | 8.76 | 0.001 | 0 | 9.01 | 0.00147 | -0.053 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.03 | 1.47 | -0.0060502 | 8760 | 1 | 8760 | 1 | 1.03 | 1.47 | -0.00605
ExitNoneSCEMLIExCZ06 | Com-Iltg-dWatt-Exit | SCE | MLI | Ex | CZ06 | 8.76 | 0.001 | 0 | 9.48 | 0.00133 | -0.0205 | 8.76 | 0.001 | 0 | 9.48 | 0.00133 | -0.0205 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.08 | 1.33 | -0.0023402 | 8760 | 1 | 8760 | 1 | 1.08 | 1.33 | -0.00234
ExitNoneSCEMLIExCZ08 | Com-Iltg-dWatt-Exit | SCE | MLI | Ex | CZ08 | 8.76 | 0.001 | 0 | 9.56 | 0.00132 | -0.0175 | 8.76 | 0.001 | 0 | 9.56 | 0.00132 | -0.0175 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.09 | 1.32 | -0.0019977 | 8760 | 1 | 8760 | 1 | 1.09 | 1.32 | -0.002
ExitNoneSCEMLIExCZ09 | Com-Iltg-dWatt-Exit | SCE | MLI | Ex | CZ09 | 8.76 | 0.001 | 0 | 9.46 | 0.00136 | -0.022 | 8.76 | 0.001 | 0 | 9.46 | 0.00136 | -0.022 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.08 | 1.36 | -0.0025114 | 8760 | 1 | 8760 | 1 | 1.08 | 1.36 | -0.00251
ExitNoneSCEMLIExCZ10 | Com-Iltg-dWatt-Exit | SCE | MLI | Ex | CZ10 | 8.76 | 0.001 | 0 | 9.23 | 0.00135 | -0.0292 | 8.76 | 0.001 | 0 | 9.23 | 0.00135 | -0.0292 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.05 | 1.35 | -0.0033333 | 8760 | 1 | 8760 | 1 | 1.05 | 1.35 | -0.00333
ExitNoneSCEMLIExCZ13 | Com-Iltg-dWatt-Exit | SCE | MLI | Ex | CZ13 | 8.76 | 0.001 | 0 | 9.23 | 0.00129 | -0.0493 | 8.76 | 0.001 | 0 | 9.23 | 0.00129 | -0.0493 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.05 | 1.29 | -0.0056279 | 8760 | 1 | 8760 | 1 | 1.05 | 1.29 | -0.00563
ExitNoneSCEMLIExCZ14 | Com-Iltg-dWatt-Exit | SCE | MLI | Ex | CZ14 | 8.76 | 0.001 | 0 | 9.1 | 0.00131 | -0.0577 | 8.76 | 0.001 | 0 | 9.1 | 0.00131 | -0.0577 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.04 | 1.31 | -0.0065868 | 8760 | 1 | 8760 | 1 | 1.04 | 1.31 | -0.00659
ExitNoneSCEMLIExCZ15 | Com-Iltg-dWatt-Exit | SCE | MLI | Ex | CZ15 | 8.76 | 0.001 | 0 | 10.2 | 0.00123 | -0.00955 | 8.76 | 0.001 | 0 | 10.2 | 0.00123 | -0.00955 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.16 | 1.23 | -0.0010902 | 8760 | 1 | 8760 | 1 | 1.16 | 1.23 | -0.00109
ExitNoneSCEMLIExCZ16 | Com-Iltg-dWatt-Exit | SCE | MLI | Ex | CZ16 | 8.76 | 0.001 | 0 | 8.48 | 0.0013 | -0.102 | 8.76 | 0.001 | 0 | 8.48 | 0.0013 | -0.102 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.968 | 1.3 | -0.011644 | 8760 | 1 | 8760 | 1 | 0.968 | 1.3 | -0.0116
ExitNoneSCEMLIExIOU | Com-Iltg-dWatt-Exit | SCE | MLI | Ex | IOU | 8.76 | 0.001 | 0 | 9.46 | 0.00133 | -0.0244 | 8.76 | 0.001 | 0 | 9.46 | 0.00133 | -0.0244 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.08 | 1.33 | -0.0027854 | 8760 | 1 | 8760 | 1 | 1.08 | 1.33 | -0.00279
ExitNoneSCEMLINewCZ05 | Com-Iltg-dWatt-Exit | SCE | MLI | New | CZ05 | 8.76 | 0.001 | 0 | 8.6 | 0.00144 | -0.0827 | 8.76 | 0.001 | 0 | 8.6 | 0.00144 | -0.0827 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.982 | 1.44 | -0.0094406 | 8760 | 1 | 8760 | 1 | 0.982 | 1.44 | -0.00944
ExitNoneSCEMLINewCZ06 | Com-Iltg-dWatt-Exit | SCE | MLI | New | CZ06 | 8.76 | 0.001 | 0 | 9.01 | 0.00129 | -0.0385 | 8.76 | 0.001 | 0 | 9.01 | 0.00129 | -0.0385 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.03 | 1.29 | -0.004395 | 8760 | 1 | 8760 | 1 | 1.03 | 1.29 | -0.0044
ExitNoneSCEMLINewCZ08 | Com-Iltg-dWatt-Exit | SCE | MLI | New | CZ08 | 8.76 | 0.001 | 0 | 9.12 | 0.00129 | -0.0334 | 8.76 | 0.001 | 0 | 9.12 | 0.00129 | -0.0334 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.04 | 1.29 | -0.0038128 | 8760 | 1 | 8760 | 1 | 1.04 | 1.29 | -0.00381
ExitNoneSCEMLINewCZ09 | Com-Iltg-dWatt-Exit | SCE | MLI | New | CZ09 | 8.76 | 0.001 | 0 | 9.11 | 0.00134 | -0.0362 | 8.76 | 0.001 | 0 | 9.11 | 0.00134 | -0.0362 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.04 | 1.34 | -0.0041324 | 8760 | 1 | 8760 | 1 | 1.04 | 1.34 | -0.00413
ExitNoneSCEMLINewCZ10 | Com-Iltg-dWatt-Exit | SCE | MLI | New | CZ10 | 8.76 | 0.001 | 0 | 9.28 | 0.00147 | -0.0394 | 8.76 | 0.001 | 0 | 9.28 | 0.00147 | -0.0394 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.06 | 1.47 | -0.0044977 | 8760 | 1 | 8760 | 1 | 1.06 | 1.47 | -0.0045
ExitNoneSCEMLINewCZ13 | Com-Iltg-dWatt-Exit | SCE | MLI | New | CZ13 | 8.76 | 0.001 | 0 | 9.09 | 0.00131 | -0.0604 | 8.76 | 0.001 | 0 | 9.09 | 0.00131 | -0.0604 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.04 | 1.31 | -0.006895 | 8760 | 1 | 8760 | 1 | 1.04 | 1.31 | -0.0069
ExitNoneSCEMLINewCZ14 | Com-Iltg-dWatt-Exit | SCE | MLI | New | CZ14 | 8.76 | 0.001 | 0 | 9.03 | 0.00133 | -0.0682 | 8.76 | 0.001 | 0 | 9.03 | 0.00133 | -0.0682 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.03 | 1.33 | -0.0077854 | 8760 | 1 | 8760 | 1 | 1.03 | 1.33 | -0.00779
ExitNoneSCEMLINewCZ15 | Com-Iltg-dWatt-Exit | SCE | MLI | New | CZ15 | 8.76 | 0.001 | 0 | 9.88 | 0.00151 | -0.0106 | 8.76 | 0.001 | 0 | 9.88 | 0.00151 | -0.0106 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.13 | 1.51 | -0.00121 | 8760 | 1 | 8760 | 1 | 1.13 | 1.51 | -0.00121
ExitNoneSCEMLINewCZ16 | Com-Iltg-dWatt-Exit | SCE | MLI | New | CZ16 | 8.76 | 0.001 | 0 | 8.56 | 0.00132 | -0.11 | 8.76 | 0.001 | 0 | 8.56 | 0.00132 | -0.11 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.977 | 1.32 | -0.012557 | 8760 | 1 | 8760 | 1 | 0.977 | 1.32 | -0.0126
ExitNoneSCEMLINewIOU | Com-Iltg-dWatt-Exit | SCE | MLI | New | IOU | 8.76 | 0.001 | 0 | 9.21 | 0.00138 | -0.0387 | 8.76 | 0.001 | 0 | 9.21 | 0.00138 | -0.0387 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.05 | 1.38 | -0.0044178 | 8760 | 1 | 8760 | 1 | 1.05 | 1.38 | -0.00442
ExitNoneSCEMtlExCZ05 | Com-Iltg-dWatt-Exit | SCE | Mtl | Ex | CZ05 | 8.76 | 0.001 | 0 | 9.59 | 0.00127 | -0.0336 | 8.76 | 0.001 | 0 | 9.59 | 0.00127 | -0.0336 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.09 | 1.27 | -0.0038356 | 8760 | 1 | 8760 | 1 | 1.09 | 1.27 | -0.00384
ExitNoneSCEMtlExCZ06 | Com-Iltg-dWatt-Exit | SCE | Mtl | Ex | CZ06 | 8.76 | 0.001 | 0 | 10.2 | 0.00127 | -0.0174 | 8.76 | 0.001 | 0 | 10.2 | 0.00127 | -0.0174 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.16 | 1.27 | -0.0019863 | 8760 | 1 | 8760 | 1 | 1.16 | 1.27 | -0.00199
ExitNoneSCEMtlExCZ08 | Com-Iltg-dWatt-Exit | SCE | Mtl | Ex | CZ08 | 8.76 | 0.001 | 0 | 10.3 | 0.00129 | -0.0148 | 8.76 | 0.001 | 0 | 10.3 | 0.00129 | -0.0148 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.18 | 1.29 | -0.0016895 | 8760 | 1 | 8760 | 1 | 1.18 | 1.29 | -0.00169
ExitNoneSCEMtlExCZ09 | Com-Iltg-dWatt-Exit | SCE | Mtl | Ex | CZ09 | 8.76 | 0.001 | 0 | 10.3 | 0.00132 | -0.0148 | 8.76 | 0.001 | 0 | 10.3 | 0.00132 | -0.0148 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.18 | 1.32 | -0.0016895 | 8760 | 1 | 8760 | 1 | 1.18 | 1.32 | -0.00169
ExitNoneSCEMtlExCZ10 | Com-Iltg-dWatt-Exit | SCE | Mtl | Ex | CZ10 | 8.76 | 0.001 | 0 | 10 | 0.00132 | -0.0184 | 8.76 | 0.001 | 0 | 10 | 0.00132 | -0.0184 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.14 | 1.32 | -0.0021005 | 8760 | 1 | 8760 | 1 | 1.14 | 1.32 | -0.0021
ExitNoneSCEMtlExCZ13 | Com-Iltg-dWatt-Exit | SCE | Mtl | Ex | CZ13 | 8.76 | 0.001 | 0 | 9.83 | 0.00132 | -0.0277 | 8.76 | 0.001 | 0 | 9.83 | 0.00132 | -0.0277 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.12 | 1.32 | -0.0031621 | 8760 | 1 | 8760 | 1 | 1.12 | 1.32 | -0.00316
ExitNoneSCEMtlExCZ14 | Com-Iltg-dWatt-Exit | SCE | Mtl | Ex | CZ14 | 8.76 | 0.001 | 0 | 9.81 | 0.00132 | -0.0265 | 8.76 | 0.001 | 0 | 9.81 | 0.00132 | -0.0265 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.12 | 1.32 | -0.0030251 | 8760 | 1 | 8760 | 1 | 1.12 | 1.32 | -0.00303
ExitNoneSCEMtlExCZ15 | Com-Iltg-dWatt-Exit | SCE | Mtl | Ex | CZ15 | 8.76 | 0.001 | 0 | 10.7 | 0.00134 | -0.00711 | 8.76 | 0.001 | 0 | 10.7 | 0.00134 | -0.00711 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.22 | 1.34 | -0.00081164 | 8760 | 1 | 8760 | 1 | 1.22 | 1.34 | -0.000812
ExitNoneSCEMtlExCZ16 | Com-Iltg-dWatt-Exit | SCE | Mtl | Ex | CZ16 | 8.76 | 0.001 | 0 | 8.85 | 0.00126 | -0.0539 | 8.76 | 0.001 | 0 | 8.85 | 0.00126 | -0.0539 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.01 | 1.26 | -0.006153 | 8760 | 1 | 8760 | 1 | 1.01 | 1.26 | -0.00615
ExitNoneSCEMtlExIOU | Com-Iltg-dWatt-Exit | SCE | Mtl | Ex | IOU | 8.76 | 0.001 | 0 | 10.2 | 0.0013 | -0.0168 | 8.76 | 0.001 | 0 | 10.2 | 0.0013 | -0.0168 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.16 | 1.3 | -0.0019178 | 8760 | 1 | 8760 | 1 | 1.16 | 1.3 | -0.00192
ExitNoneSCEMtlNewCZ05 | Com-Iltg-dWatt-Exit | SCE | Mtl | New | CZ05 | 8.76 | 0.001 | 0 | 9.05 | 0.00127 | -0.054 | 8.76 | 0.001 | 0 | 9.05 | 0.00127 | -0.054 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.03 | 1.27 | -0.0061644 | 8760 | 1 | 8760 | 1 | 1.03 | 1.27 | -0.00616
ExitNoneSCEMtlNewCZ06 | Com-Iltg-dWatt-Exit | SCE | Mtl | New | CZ06 | 8.76 | 0.001 | 0 | 9.89 | 0.00129 | -0.0287 | 8.76 | 0.001 | 0 | 9.89 | 0.00129 | -0.0287 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.13 | 1.29 | -0.0032763 | 8760 | 1 | 8760 | 1 | 1.13 | 1.29 | -0.00328
ExitNoneSCEMtlNewCZ08 | Com-Iltg-dWatt-Exit | SCE | Mtl | New | CZ08 | 8.76 | 0.001 | 0 | 10 | 0.00132 | -0.0242 | 8.76 | 0.001 | 0 | 10 | 0.00132 | -0.0242 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.14 | 1.32 | -0.0027626 | 8760 | 1 | 8760 | 1 | 1.14 | 1.32 | -0.00276
ExitNoneSCEMtlNewCZ09 | Com-Iltg-dWatt-Exit | SCE | Mtl | New | CZ09 | 8.76 | 0.001 | 0 | 9.97 | 0.00133 | -0.0218 | 8.76 | 0.001 | 0 | 9.97 | 0.00133 | -0.0218 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.14 | 1.33 | -0.0024886 | 8760 | 1 | 8760 | 1 | 1.14 | 1.33 | -0.00249
ExitNoneSCEMtlNewCZ10 | Com-Iltg-dWatt-Exit | SCE | Mtl | New | CZ10 | 8.76 | 0.001 | 0 | 9.9 | 0.00134 | -0.0281 | 8.76 | 0.001 | 0 | 9.9 | 0.00134 | -0.0281 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.13 | 1.34 | -0.0032078 | 8760 | 1 | 8760 | 1 | 1.13 | 1.34 | -0.00321
ExitNoneSCEMtlNewCZ13 | Com-Iltg-dWatt-Exit | SCE | Mtl | New | CZ13 | 8.76 | 0.001 | 0 | 9.57 | 0.00132 | -0.0394 | 8.76 | 0.001 | 0 | 9.57 | 0.00132 | -0.0394 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.09 | 1.32 | -0.0044977 | 8760 | 1 | 8760 | 1 | 1.09 | 1.32 | -0.0045
ExitNoneSCEMtlNewCZ14 | Com-Iltg-dWatt-Exit | SCE | Mtl | New | CZ14 | 8.76 | 0.001 | 0 | 9.46 | 0.00133 | -0.0398 | 8.76 | 0.001 | 0 | 9.46 | 0.00133 | -0.0398 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.08 | 1.33 | -0.0045434 | 8760 | 1 | 8760 | 1 | 1.08 | 1.33 | -0.00454
ExitNoneSCEMtlNewCZ15 | Com-Iltg-dWatt-Exit | SCE | Mtl | New | CZ15 | 8.76 | 0.001 | 0 | 10.5 | 0.00136 | -0.0128 | 8.76 | 0.001 | 0 | 10.5 | 0.00136 | -0.0128 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.2 | 1.36 | -0.0014612 | 8760 | 1 | 8760 | 1 | 1.2 | 1.36 | -0.00146
ExitNoneSCEMtlNewCZ16 | Com-Iltg-dWatt-Exit | SCE | Mtl | New | CZ16 | 8.76 | 0.001 | 0 | 8.38 | 0.00126 | -0.0701 | 8.76 | 0.001 | 0 | 8.38 | 0.00126 | -0.0701 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.957 | 1.26 | -0.0080023 | 8760 | 1 | 8760 | 1 | 0.957 | 1.26 | -0.008
ExitNoneSCEMtlNewIOU | Com-Iltg-dWatt-Exit | SCE | Mtl | New | IOU | 8.76 | 0.001 | 0 | 9.99 | 0.00132 | -0.0258 | 8.76 | 0.001 | 0 | 9.99 | 0.00132 | -0.0258 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.14 | 1.32 | -0.0029452 | 8760 | 1 | 8760 | 1 | 1.14 | 1.32 | -0.00295
ExitNoneSCENrsExCZ05 | Com-Iltg-dWatt-Exit | SCE | Nrs | Ex | CZ05 | 8.76 | 0.001 | 0 | 8.56 | 0.00127 | -0.18 | 8.76 | 0.001 | 0 | 8.56 | 0.00127 | -0.18 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.977 | 1.27 | -0.020548 | 8760 | 1 | 8760 | 1 | 0.977 | 1.27 | -0.0205
ExitNoneSCENrsExCZ06 | Com-Iltg-dWatt-Exit | SCE | Nrs | Ex | CZ06 | 8.76 | 0.001 | 0 | 9.19 | 0.00132 | -0.124 | 8.76 | 0.001 | 0 | 9.19 | 0.00132 | -0.124 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.05 | 1.32 | -0.014155 | 8760 | 1 | 8760 | 1 | 1.05 | 1.32 | -0.0142
ExitNoneSCENrsExCZ08 | Com-Iltg-dWatt-Exit | SCE | Nrs | Ex | CZ08 | 8.76 | 0.001 | 0 | 9.31 | 0.00134 | -0.12 | 8.76 | 0.001 | 0 | 9.31 | 0.00134 | -0.12 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.06 | 1.34 | -0.013699 | 8760 | 1 | 8760 | 1 | 1.06 | 1.34 | -0.0137
ExitNoneSCENrsExCZ09 | Com-Iltg-dWatt-Exit | SCE | Nrs | Ex | CZ09 | 8.76 | 0.001 | 0 | 9.36 | 0.00138 | -0.121 | 8.76 | 0.001 | 0 | 9.36 | 0.00138 | -0.121 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.07 | 1.38 | -0.013813 | 8760 | 1 | 8760 | 1 | 1.07 | 1.38 | -0.0138
ExitNoneSCENrsExCZ10 | Com-Iltg-dWatt-Exit | SCE | Nrs | Ex | CZ10 | 8.76 | 0.001 | 0 | 9.21 | 0.00137 | -0.124 | 8.76 | 0.001 | 0 | 9.21 | 0.00137 | -0.124 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.05 | 1.37 | -0.014155 | 8760 | 1 | 8760 | 1 | 1.05 | 1.37 | -0.0142
ExitNoneSCENrsExCZ13 | Com-Iltg-dWatt-Exit | SCE | Nrs | Ex | CZ13 | 8.76 | 0.001 | 0 | 9.18 | 0.00139 | -0.13 | 8.76 | 0.001 | 0 | 9.18 | 0.00139 | -0.13 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.05 | 1.39 | -0.01484 | 8760 | 1 | 8760 | 1 | 1.05 | 1.39 | -0.0148
ExitNoneSCENrsExCZ14 | Com-Iltg-dWatt-Exit | SCE | Nrs | Ex | CZ14 | 8.76 | 0.001 | 0 | 9.15 | 0.00136 | -0.135 | 8.76 | 0.001 | 0 | 9.15 | 0.00136 | -0.135 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.04 | 1.36 | -0.015411 | 8760 | 1 | 8760 | 1 | 1.04 | 1.36 | -0.0154
ExitNoneSCENrsExCZ15 | Com-Iltg-dWatt-Exit | SCE | Nrs | Ex | CZ15 | 8.76 | 0.001 | 0 | 9.96 | 0.00139 | -0.0753 | 8.76 | 0.001 | 0 | 9.96 | 0.00139 | -0.0753 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.14 | 1.39 | -0.0085959 | 8760 | 1 | 8760 | 1 | 1.14 | 1.39 | -0.0086
ExitNoneSCENrsExCZ16 | Com-Iltg-dWatt-Exit | SCE | Nrs | Ex | CZ16 | 8.76 | 0.001 | 0 | 8.5 | 0.0013 | -0.178 | 8.76 | 0.001 | 0 | 8.5 | 0.0013 | -0.178 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.97 | 1.3 | -0.02032 | 8760 | 1 | 8760 | 1 | 0.97 | 1.3 | -0.0203
ExitNoneSCENrsExIOU | Com-Iltg-dWatt-Exit | SCE | Nrs | Ex | IOU | 8.76 | 0.001 | 0 | 9.25 | 0.00135 | -0.124 | 8.76 | 0.001 | 0 | 9.25 | 0.00135 | -0.124 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.06 | 1.35 | -0.014155 | 8760 | 1 | 8760 | 1 | 1.06 | 1.35 | -0.0142
ExitNoneSCENrsNewCZ05 | Com-Iltg-dWatt-Exit | SCE | Nrs | New | CZ05 | 8.76 | 0.001 | 0 | 8.26 | 0.00125 | -0.204 | 8.76 | 0.001 | 0 | 8.26 | 0.00125 | -0.204 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.943 | 1.25 | -0.023288 | 8760 | 1 | 8760 | 1 | 0.943 | 1.25 | -0.0233
ExitNoneSCENrsNewCZ06 | Com-Iltg-dWatt-Exit | SCE | Nrs | New | CZ06 | 8.76 | 0.001 | 0 | 8.73 | 0.00131 | -0.142 | 8.76 | 0.001 | 0 | 8.73 | 0.00131 | -0.142 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.997 | 1.31 | -0.01621 | 8760 | 1 | 8760 | 1 | 0.997 | 1.31 | -0.0162
ExitNoneSCENrsNewCZ08 | Com-Iltg-dWatt-Exit | SCE | Nrs | New | CZ08 | 8.76 | 0.001 | 0 | 8.9 | 0.00133 | -0.131 | 8.76 | 0.001 | 0 | 8.9 | 0.00133 | -0.131 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.02 | 1.33 | -0.014954 | 8760 | 1 | 8760 | 1 | 1.02 | 1.33 | -0.015
ExitNoneSCENrsNewCZ09 | Com-Iltg-dWatt-Exit | SCE | Nrs | New | CZ09 | 8.76 | 0.001 | 0 | 9 | 0.00138 | -0.134 | 8.76 | 0.001 | 0 | 9 | 0.00138 | -0.134 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.03 | 1.38 | -0.015297 | 8760 | 1 | 8760 | 1 | 1.03 | 1.38 | -0.0153
ExitNoneSCENrsNewCZ10 | Com-Iltg-dWatt-Exit | SCE | Nrs | New | CZ10 | 8.76 | 0.001 | 0 | 9.02 | 0.00139 | -0.141 | 8.76 | 0.001 | 0 | 9.02 | 0.00139 | -0.141 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.03 | 1.39 | -0.016096 | 8760 | 1 | 8760 | 1 | 1.03 | 1.39 | -0.0161
ExitNoneSCENrsNewCZ13 | Com-Iltg-dWatt-Exit | SCE | Nrs | New | CZ13 | 8.76 | 0.001 | 0 | 9.01 | 0.00137 | -0.142 | 8.76 | 0.001 | 0 | 9.01 | 0.00137 | -0.142 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.03 | 1.37 | -0.01621 | 8760 | 1 | 8760 | 1 | 1.03 | 1.37 | -0.0162
ExitNoneSCENrsNewCZ14 | Com-Iltg-dWatt-Exit | SCE | Nrs | New | CZ14 | 8.76 | 0.001 | 0 | 8.99 | 0.00135 | -0.148 | 8.76 | 0.001 | 0 | 8.99 | 0.00135 | -0.148 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.03 | 1.35 | -0.016895 | 8760 | 1 | 8760 | 1 | 1.03 | 1.35 | -0.0169
ExitNoneSCENrsNewCZ15 | Com-Iltg-dWatt-Exit | SCE | Nrs | New | CZ15 | 8.76 | 0.001 | 0 | 9.84 | 0.00138 | -0.0788 | 8.76 | 0.001 | 0 | 9.84 | 0.00138 | -0.0788 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.12 | 1.38 | -0.0089954 | 8760 | 1 | 8760 | 1 | 1.12 | 1.38 | -0.009
ExitNoneSCENrsNewCZ16 | Com-Iltg-dWatt-Exit | SCE | Nrs | New | CZ16 | 8.76 | 0.001 | 0 | 8.36 | 0.00129 | -0.192 | 8.76 | 0.001 | 0 | 8.36 | 0.00129 | -0.192 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.954 | 1.29 | -0.021918 | 8760 | 1 | 8760 | 1 | 0.954 | 1.29 | -0.0219
ExitNoneSCENrsNewIOU | Com-Iltg-dWatt-Exit | SCE | Nrs | New | IOU | 8.76 | 0.001 | 0 | 8.94 | 0.00135 | -0.138 | 8.76 | 0.001 | 0 | 8.94 | 0.00135 | -0.138 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.02 | 1.35 | -0.015753 | 8760 | 1 | 8760 | 1 | 1.02 | 1.35 | -0.0158
ExitNoneSCEOfLExCZ05 | Com-Iltg-dWatt-Exit | SCE | OfL | Ex | CZ05 | 8.76 | 0.001 | 0 | 9.39 | 0.00141 | -0.0735 | 8.76 | 0.001 | 0 | 9.39 | 0.00141 | -0.0735 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.07 | 1.41 | -0.0083904 | 8760 | 1 | 8760 | 1 | 1.07 | 1.41 | -0.00839
ExitNoneSCEOfLExCZ06 | Com-Iltg-dWatt-Exit | SCE | OfL | Ex | CZ06 | 8.76 | 0.001 | 0 | 10.1 | 0.00142 | -0.0424 | 8.76 | 0.001 | 0 | 10.1 | 0.00142 | -0.0424 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.15 | 1.42 | -0.0048402 | 8760 | 1 | 8760 | 1 | 1.15 | 1.42 | -0.00484
ExitNoneSCEOfLExCZ08 | Com-Iltg-dWatt-Exit | SCE | OfL | Ex | CZ08 | 8.76 | 0.001 | 0 | 10.2 | 0.00147 | -0.0389 | 8.76 | 0.001 | 0 | 10.2 | 0.00147 | -0.0389 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.16 | 1.47 | -0.0044406 | 8760 | 1 | 8760 | 1 | 1.16 | 1.47 | -0.00444
ExitNoneSCEOfLExCZ09 | Com-Iltg-dWatt-Exit | SCE | OfL | Ex | CZ09 | 8.76 | 0.001 | 0 | 10.1 | 0.00146 | -0.0436 | 8.76 | 0.001 | 0 | 10.1 | 0.00146 | -0.0436 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.15 | 1.46 | -0.0049772 | 8760 | 1 | 8760 | 1 | 1.15 | 1.46 | -0.00498
ExitNoneSCEOfLExCZ10 | Com-Iltg-dWatt-Exit | SCE | OfL | Ex | CZ10 | 8.76 | 0.001 | 0 | 10 | 0.00147 | -0.0409 | 8.76 | 0.001 | 0 | 10 | 0.00147 | -0.0409 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.14 | 1.47 | -0.0046689 | 8760 | 1 | 8760 | 1 | 1.14 | 1.47 | -0.00467
ExitNoneSCEOfLExCZ13 | Com-Iltg-dWatt-Exit | SCE | OfL | Ex | CZ13 | 8.76 | 0.001 | 0 | 9.86 | 0.00146 | -0.0641 | 8.76 | 0.001 | 0 | 9.86 | 0.00146 | -0.0641 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.13 | 1.46 | -0.0073174 | 8760 | 1 | 8760 | 1 | 1.13 | 1.46 | -0.00732
ExitNoneSCEOfLExCZ14 | Com-Iltg-dWatt-Exit | SCE | OfL | Ex | CZ14 | 8.76 | 0.001 | 0 | 10 | 0.00144 | -0.0577 | 8.76 | 0.001 | 0 | 10 | 0.00144 | -0.0577 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.14 | 1.44 | -0.0065868 | 8760 | 1 | 8760 | 1 | 1.14 | 1.44 | -0.00659
ExitNoneSCEOfLExCZ15 | Com-Iltg-dWatt-Exit | SCE | OfL | Ex | CZ15 | 8.76 | 0.001 | 0 | 10.6 | 0.00146 | -0.0217 | 8.76 | 0.001 | 0 | 10.6 | 0.00146 | -0.0217 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.21 | 1.46 | -0.0024772 | 8760 | 1 | 8760 | 1 | 1.21 | 1.46 | -0.00248
ExitNoneSCEOfLExCZ16 | Com-Iltg-dWatt-Exit | SCE | OfL | Ex | CZ16 | 8.76 | 0.001 | 0 | 9.05 | 0.00137 | -0.111 | 8.76 | 0.001 | 0 | 9.05 | 0.00137 | -0.111 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.03 | 1.37 | -0.012671 | 8760 | 1 | 8760 | 1 | 1.03 | 1.37 | -0.0127
ExitNoneSCEOfLExIOU | Com-Iltg-dWatt-Exit | SCE | OfL | Ex | IOU | 8.76 | 0.001 | 0 | 10.1 | 0.00145 | -0.042 | 8.76 | 0.001 | 0 | 10.1 | 0.00145 | -0.042 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.15 | 1.45 | -0.0047945 | 8760 | 1 | 8760 | 1 | 1.15 | 1.45 | -0.00479
ExitNoneSCEOfLNewCZ05 | Com-Iltg-dWatt-Exit | SCE | OfL | New | CZ05 | 8.76 | 0.001 | 0 | 9.64 | 0.00139 | -0.0557 | 8.76 | 0.001 | 0 | 9.64 | 0.00139 | -0.0557 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.1 | 1.39 | -0.0063584 | 8760 | 1 | 8760 | 1 | 1.1 | 1.39 | -0.00636
ExitNoneSCEOfLNewCZ06 | Com-Iltg-dWatt-Exit | SCE | OfL | New | CZ06 | 8.76 | 0.001 | 0 | 10.1 | 0.00135 | -0.0192 | 8.76 | 0.001 | 0 | 10.1 | 0.00135 | -0.0192 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.15 | 1.35 | -0.0021918 | 8760 | 1 | 8760 | 1 | 1.15 | 1.35 | -0.00219
ExitNoneSCEOfLNewCZ08 | Com-Iltg-dWatt-Exit | SCE | OfL | New | CZ08 | 8.76 | 0.001 | 0 | 10.1 | 0.00137 | -0.0211 | 8.76 | 0.001 | 0 | 10.1 | 0.00137 | -0.0211 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.15 | 1.37 | -0.0024087 | 8760 | 1 | 8760 | 1 | 1.15 | 1.37 | -0.00241
ExitNoneSCEOfLNewCZ09 | Com-Iltg-dWatt-Exit | SCE | OfL | New | CZ09 | 8.76 | 0.001 | 0 | 9.99 | 0.00142 | -0.0372 | 8.76 | 0.001 | 0 | 9.99 | 0.00142 | -0.0372 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.14 | 1.42 | -0.0042466 | 8760 | 1 | 8760 | 1 | 1.14 | 1.42 | -0.00425
ExitNoneSCEOfLNewCZ10 | Com-Iltg-dWatt-Exit | SCE | OfL | New | CZ10 | 8.76 | 0.001 | 0 | 10 | 0.0014 | -0.0438 | 8.76 | 0.001 | 0 | 10 | 0.0014 | -0.0438 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.14 | 1.4 | -0.005 | 8760 | 1 | 8760 | 1 | 1.14 | 1.4 | -0.005
ExitNoneSCEOfLNewCZ13 | Com-Iltg-dWatt-Exit | SCE | OfL | New | CZ13 | 8.76 | 0.001 | 0 | 9.93 | 0.00138 | -0.0512 | 8.76 | 0.001 | 0 | 9.93 | 0.00138 | -0.0512 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.13 | 1.38 | -0.0058447 | 8760 | 1 | 8760 | 1 | 1.13 | 1.38 | -0.00584
ExitNoneSCEOfLNewCZ14 | Com-Iltg-dWatt-Exit | SCE | OfL | New | CZ14 | 8.76 | 0.001 | 0 | 9.84 | 0.00141 | -0.0329 | 8.76 | 0.001 | 0 | 9.84 | 0.00141 | -0.0329 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.12 | 1.41 | -0.0037557 | 8760 | 1 | 8760 | 1 | 1.12 | 1.41 | -0.00376
ExitNoneSCEOfLNewCZ15 | Com-Iltg-dWatt-Exit | SCE | OfL | New | CZ15 | 8.76 | 0.001 | 0 | 10.4 | 0.00141 | -0.0183 | 8.76 | 0.001 | 0 | 10.4 | 0.00141 | -0.0183 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.19 | 1.41 | -0.002089 | 8760 | 1 | 8760 | 1 | 1.19 | 1.41 | -0.00209
ExitNoneSCEOfLNewCZ16 | Com-Iltg-dWatt-Exit | SCE | OfL | New | CZ16 | 8.76 | 0.001 | 0 | 9.3 | 0.00134 | -0.0812 | 8.76 | 0.001 | 0 | 9.3 | 0.00134 | -0.0812 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.06 | 1.34 | -0.0092694 | 8760 | 1 | 8760 | 1 | 1.06 | 1.34 | -0.00927
ExitNoneSCEOfLNewIOU | Com-Iltg-dWatt-Exit | SCE | OfL | New | IOU | 8.76 | 0.001 | 0 | 10 | 0.00139 | -0.0307 | 8.76 | 0.001 | 0 | 10 | 0.00139 | -0.0307 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.14 | 1.39 | -0.0035046 | 8760 | 1 | 8760 | 1 | 1.14 | 1.39 | -0.0035
ExitNoneSCEOfSExCZ05 | Com-Iltg-dWatt-Exit | SCE | OfS | Ex | CZ05 | 8.76 | 0.001 | 0 | 9.36 | 0.00143 | -0.0349 | 8.76 | 0.001 | 0 | 9.36 | 0.00143 | -0.0349 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.07 | 1.43 | -0.003984 | 8760 | 1 | 8760 | 1 | 1.07 | 1.43 | -0.00398
ExitNoneSCEOfSExCZ06 | Com-Iltg-dWatt-Exit | SCE | OfS | Ex | CZ06 | 8.76 | 0.001 | 0 | 9.88 | 0.00139 | -0.0172 | 8.76 | 0.001 | 0 | 9.88 | 0.00139 | -0.0172 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.13 | 1.39 | -0.0019635 | 8760 | 1 | 8760 | 1 | 1.13 | 1.39 | -0.00196
ExitNoneSCEOfSExCZ08 | Com-Iltg-dWatt-Exit | SCE | OfS | Ex | CZ08 | 8.76 | 0.001 | 0 | 9.96 | 0.0014 | -0.0151 | 8.76 | 0.001 | 0 | 9.96 | 0.0014 | -0.0151 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.14 | 1.4 | -0.0017237 | 8760 | 1 | 8760 | 1 | 1.14 | 1.4 | -0.00172
ExitNoneSCEOfSExCZ09 | Com-Iltg-dWatt-Exit | SCE | OfS | Ex | CZ09 | 8.76 | 0.001 | 0 | 9.91 | 0.00142 | -0.0178 | 8.76 | 0.001 | 0 | 9.91 | 0.00142 | -0.0178 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.13 | 1.42 | -0.002032 | 8760 | 1 | 8760 | 1 | 1.13 | 1.42 | -0.00203
ExitNoneSCEOfSExCZ10 | Com-Iltg-dWatt-Exit | SCE | OfS | Ex | CZ10 | 8.76 | 0.001 | 0 | 9.78 | 0.00141 | -0.0182 | 8.76 | 0.001 | 0 | 9.78 | 0.00141 | -0.0182 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.12 | 1.41 | -0.0020776 | 8760 | 1 | 8760 | 1 | 1.12 | 1.41 | -0.00208
ExitNoneSCEOfSExCZ13 | Com-Iltg-dWatt-Exit | SCE | OfS | Ex | CZ13 | 8.76 | 0.001 | 0 | 9.62 | 0.00136 | -0.0353 | 8.76 | 0.001 | 0 | 9.62 | 0.00136 | -0.0353 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.1 | 1.36 | -0.0040297 | 8760 | 1 | 8760 | 1 | 1.1 | 1.36 | -0.00403
ExitNoneSCEOfSExCZ14 | Com-Iltg-dWatt-Exit | SCE | OfS | Ex | CZ14 | 8.76 | 0.001 | 0 | 9.58 | 0.00139 | -0.0309 | 8.76 | 0.001 | 0 | 9.58 | 0.00139 | -0.0309 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.09 | 1.39 | -0.0035274 | 8760 | 1 | 8760 | 1 | 1.09 | 1.39 | -0.00353
ExitNoneSCEOfSExCZ15 | Com-Iltg-dWatt-Exit | SCE | OfS | Ex | CZ15 | 8.76 | 0.001 | 0 | 10.6 | 0.00136 | -0.00568 | 8.76 | 0.001 | 0 | 10.6 | 0.00136 | -0.00568 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.21 | 1.36 | -0.0006484 | 8760 | 1 | 8760 | 1 | 1.21 | 1.36 | -0.000648
ExitNoneSCEOfSExCZ16 | Com-Iltg-dWatt-Exit | SCE | OfS | Ex | CZ16 | 8.76 | 0.001 | 0 | 8.66 | 0.00134 | -0.0663 | 8.76 | 0.001 | 0 | 8.66 | 0.00134 | -0.0663 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.989 | 1.34 | -0.0075685 | 8760 | 1 | 8760 | 1 | 0.989 | 1.34 | -0.00757
ExitNoneSCEOfSExIOU | Com-Iltg-dWatt-Exit | SCE | OfS | Ex | IOU | 8.76 | 0.001 | 0 | 9.88 | 0.0014 | -0.0184 | 8.76 | 0.001 | 0 | 9.88 | 0.0014 | -0.0184 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.13 | 1.4 | -0.0021005 | 8760 | 1 | 8760 | 1 | 1.13 | 1.4 | -0.0021
ExitNoneSCEOfSNewCZ05 | Com-Iltg-dWatt-Exit | SCE | OfS | New | CZ05 | 8.76 | 0.001 | 0 | 9.01 | 0.00142 | -0.0348 | 8.76 | 0.001 | 0 | 9.01 | 0.00142 | -0.0348 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.03 | 1.42 | -0.0039726 | 8760 | 1 | 8760 | 1 | 1.03 | 1.42 | -0.00397
ExitNoneSCEOfSNewCZ06 | Com-Iltg-dWatt-Exit | SCE | OfS | New | CZ06 | 8.76 | 0.001 | 0 | 9.57 | 0.00136 | -0.0152 | 8.76 | 0.001 | 0 | 9.57 | 0.00136 | -0.0152 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.09 | 1.36 | -0.0017352 | 8760 | 1 | 8760 | 1 | 1.09 | 1.36 | -0.00174
ExitNoneSCEOfSNewCZ08 | Com-Iltg-dWatt-Exit | SCE | OfS | New | CZ08 | 8.76 | 0.001 | 0 | 9.61 | 0.00139 | -0.0134 | 8.76 | 0.001 | 0 | 9.61 | 0.00139 | -0.0134 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.1 | 1.39 | -0.0015297 | 8760 | 1 | 8760 | 1 | 1.1 | 1.39 | -0.00153
ExitNoneSCEOfSNewCZ09 | Com-Iltg-dWatt-Exit | SCE | OfS | New | CZ09 | 8.76 | 0.001 | 0 | 9.57 | 0.00141 | -0.0161 | 8.76 | 0.001 | 0 | 9.57 | 0.00141 | -0.0161 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.09 | 1.41 | -0.0018379 | 8760 | 1 | 8760 | 1 | 1.09 | 1.41 | -0.00184
ExitNoneSCEOfSNewCZ10 | Com-Iltg-dWatt-Exit | SCE | OfS | New | CZ10 | 8.76 | 0.001 | 0 | 9.71 | 0.00146 | -0.0131 | 8.76 | 0.001 | 0 | 9.71 | 0.00146 | -0.0131 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.11 | 1.46 | -0.0014954 | 8760 | 1 | 8760 | 1 | 1.11 | 1.46 | -0.0015
ExitNoneSCEOfSNewCZ13 | Com-Iltg-dWatt-Exit | SCE | OfS | New | CZ13 | 8.76 | 0.001 | 0 | 9.41 | 0.0014 | -0.0341 | 8.76 | 0.001 | 0 | 9.41 | 0.0014 | -0.0341 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.07 | 1.4 | -0.0038927 | 8760 | 1 | 8760 | 1 | 1.07 | 1.4 | -0.00389
ExitNoneSCEOfSNewCZ14 | Com-Iltg-dWatt-Exit | SCE | OfS | New | CZ14 | 8.76 | 0.001 | 0 | 9.46 | 0.00144 | -0.0315 | 8.76 | 0.001 | 0 | 9.46 | 0.00144 | -0.0315 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.08 | 1.44 | -0.0035959 | 8760 | 1 | 8760 | 1 | 1.08 | 1.44 | -0.0036
ExitNoneSCEOfSNewCZ15 | Com-Iltg-dWatt-Exit | SCE | OfS | New | CZ15 | 8.76 | 0.001 | 0 | 10.2 | 0.00146 | -0.00299 | 8.76 | 0.001 | 0 | 10.2 | 0.00146 | -0.00299 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.16 | 1.46 | -0.00034132 | 8760 | 1 | 8760 | 1 | 1.16 | 1.46 | -0.000341
ExitNoneSCEOfSNewCZ16 | Com-Iltg-dWatt-Exit | SCE | OfS | New | CZ16 | 8.76 | 0.001 | 0 | 8.64 | 0.00136 | -0.0666 | 8.76 | 0.001 | 0 | 8.64 | 0.00136 | -0.0666 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.986 | 1.36 | -0.0076027 | 8760 | 1 | 8760 | 1 | 0.986 | 1.36 | -0.0076
ExitNoneSCEOfSNewIOU | Com-Iltg-dWatt-Exit | SCE | OfS | New | IOU | 8.76 | 0.001 | 0 | 9.64 | 0.00141 | -0.0158 | 8.76 | 0.001 | 0 | 9.64 | 0.00141 | -0.0158 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.1 | 1.41 | -0.0018037 | 8760 | 1 | 8760 | 1 | 1.1 | 1.41 | -0.0018
ExitNoneSCERFFExCZ05 | Com-Iltg-dWatt-Exit | SCE | RFF | Ex | CZ05 | 8.76 | 0.001 | 0 | 9.04 | 0.00125 | -0.0946 | 8.76 | 0.001 | 0 | 9.04 | 0.00125 | -0.0946 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.03 | 1.25 | -0.010799 | 8760 | 1 | 8760 | 1 | 1.03 | 1.25 | -0.0108
ExitNoneSCERFFExCZ06 | Com-Iltg-dWatt-Exit | SCE | RFF | Ex | CZ06 | 8.76 | 0.001 | 0 | 9.52 | 0.00127 | -0.05 | 8.76 | 0.001 | 0 | 9.52 | 0.00127 | -0.05 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.09 | 1.27 | -0.0057078 | 8760 | 1 | 8760 | 1 | 1.09 | 1.27 | -0.00571
ExitNoneSCERFFExCZ08 | Com-Iltg-dWatt-Exit | SCE | RFF | Ex | CZ08 | 8.76 | 0.001 | 0 | 9.61 | 0.00126 | -0.045 | 8.76 | 0.001 | 0 | 9.61 | 0.00126 | -0.045 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.1 | 1.26 | -0.005137 | 8760 | 1 | 8760 | 1 | 1.1 | 1.26 | -0.00514
ExitNoneSCERFFExCZ09 | Com-Iltg-dWatt-Exit | SCE | RFF | Ex | CZ09 | 8.76 | 0.001 | 0 | 9.57 | 0.00128 | -0.0434 | 8.76 | 0.001 | 0 | 9.57 | 0.00128 | -0.0434 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.09 | 1.28 | -0.0049543 | 8760 | 1 | 8760 | 1 | 1.09 | 1.28 | -0.00495
ExitNoneSCERFFExCZ10 | Com-Iltg-dWatt-Exit | SCE | RFF | Ex | CZ10 | 8.76 | 0.001 | 0 | 9.41 | 0.00127 | -0.0524 | 8.76 | 0.001 | 0 | 9.41 | 0.00127 | -0.0524 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.07 | 1.27 | -0.0059817 | 8760 | 1 | 8760 | 1 | 1.07 | 1.27 | -0.00598
ExitNoneSCERFFExCZ13 | Com-Iltg-dWatt-Exit | SCE | RFF | Ex | CZ13 | 8.76 | 0.001 | 0 | 9.42 | 0.00128 | -0.0673 | 8.76 | 0.001 | 0 | 9.42 | 0.00128 | -0.0673 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.08 | 1.28 | -0.0076826 | 8760 | 1 | 8760 | 1 | 1.08 | 1.28 | -0.00768
ExitNoneSCERFFExCZ14 | Com-Iltg-dWatt-Exit | SCE | RFF | Ex | CZ14 | 8.76 | 0.001 | 0 | 9.3 | 0.00128 | -0.0742 | 8.76 | 0.001 | 0 | 9.3 | 0.00128 | -0.0742 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.06 | 1.28 | -0.0084703 | 8760 | 1 | 8760 | 1 | 1.06 | 1.28 | -0.00847
ExitNoneSCERFFExCZ15 | Com-Iltg-dWatt-Exit | SCE | RFF | Ex | CZ15 | 8.76 | 0.001 | 0 | 10.2 | 0.00126 | -0.0235 | 8.76 | 0.001 | 0 | 10.2 | 0.00126 | -0.0235 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.16 | 1.26 | -0.0026826 | 8760 | 1 | 8760 | 1 | 1.16 | 1.26 | -0.00268
ExitNoneSCERFFExCZ16 | Com-Iltg-dWatt-Exit | SCE | RFF | Ex | CZ16 | 8.76 | 0.001 | 0 | 8.72 | 0.00124 | -0.129 | 8.76 | 0.001 | 0 | 8.72 | 0.00124 | -0.129 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.995 | 1.24 | -0.014726 | 8760 | 1 | 8760 | 1 | 0.995 | 1.24 | -0.0147
ExitNoneSCERFFExIOU | Com-Iltg-dWatt-Exit | SCE | RFF | Ex | IOU | 8.76 | 0.001 | 0 | 9.53 | 0.00127 | -0.0501 | 8.76 | 0.001 | 0 | 9.53 | 0.00127 | -0.0501 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.09 | 1.27 | -0.0057192 | 8760 | 1 | 8760 | 1 | 1.09 | 1.27 | -0.00572
ExitNoneSCERFFNewCZ05 | Com-Iltg-dWatt-Exit | SCE | RFF | New | CZ05 | 8.76 | 0.001 | 0 | 8.94 | 0.00128 | -0.0999 | 8.76 | 0.001 | 0 | 8.94 | 0.00128 | -0.0999 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.02 | 1.28 | -0.011404 | 8760 | 1 | 8760 | 1 | 1.02 | 1.28 | -0.0114
ExitNoneSCERFFNewCZ06 | Com-Iltg-dWatt-Exit | SCE | RFF | New | CZ06 | 8.76 | 0.001 | 0 | 9.36 | 0.00131 | -0.0639 | 8.76 | 0.001 | 0 | 9.36 | 0.00131 | -0.0639 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.07 | 1.31 | -0.0072945 | 8760 | 1 | 8760 | 1 | 1.07 | 1.31 | -0.00729
ExitNoneSCERFFNewCZ08 | Com-Iltg-dWatt-Exit | SCE | RFF | New | CZ08 | 8.76 | 0.001 | 0 | 9.51 | 0.00132 | -0.0561 | 8.76 | 0.001 | 0 | 9.51 | 0.00132 | -0.0561 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.09 | 1.32 | -0.0064041 | 8760 | 1 | 8760 | 1 | 1.09 | 1.32 | -0.0064
ExitNoneSCERFFNewCZ09 | Com-Iltg-dWatt-Exit | SCE | RFF | New | CZ09 | 8.76 | 0.001 | 0 | 9.5 | 0.00137 | -0.0621 | 8.76 | 0.001 | 0 | 9.5 | 0.00137 | -0.0621 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.08 | 1.37 | -0.007089 | 8760 | 1 | 8760 | 1 | 1.08 | 1.37 | -0.00709
ExitNoneSCERFFNewCZ10 | Com-Iltg-dWatt-Exit | SCE | RFF | New | CZ10 | 8.76 | 0.001 | 0 | 9.56 | 0.00139 | -0.0639 | 8.76 | 0.001 | 0 | 9.56 | 0.00139 | -0.0639 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.09 | 1.39 | -0.0072945 | 8760 | 1 | 8760 | 1 | 1.09 | 1.39 | -0.00729
ExitNoneSCERFFNewCZ13 | Com-Iltg-dWatt-Exit | SCE | RFF | New | CZ13 | 8.76 | 0.001 | 0 | 9.57 | 0.00138 | -0.0823 | 8.76 | 0.001 | 0 | 9.57 | 0.00138 | -0.0823 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.09 | 1.38 | -0.009395 | 8760 | 1 | 8760 | 1 | 1.09 | 1.38 | -0.0094
ExitNoneSCERFFNewCZ14 | Com-Iltg-dWatt-Exit | SCE | RFF | New | CZ14 | 8.76 | 0.001 | 0 | 9.53 | 0.0014 | -0.0872 | 8.76 | 0.001 | 0 | 9.53 | 0.0014 | -0.0872 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.09 | 1.4 | -0.0099543 | 8760 | 1 | 8760 | 1 | 1.09 | 1.4 | -0.00995
ExitNoneSCERFFNewCZ15 | Com-Iltg-dWatt-Exit | SCE | RFF | New | CZ15 | 8.76 | 0.001 | 0 | 10.3 | 0.00137 | -0.0247 | 8.76 | 0.001 | 0 | 10.3 | 0.00137 | -0.0247 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.18 | 1.37 | -0.0028196 | 8760 | 1 | 8760 | 1 | 1.18 | 1.37 | -0.00282
ExitNoneSCERFFNewCZ16 | Com-Iltg-dWatt-Exit | SCE | RFF | New | CZ16 | 8.76 | 0.001 | 0 | 8.86 | 0.00131 | -0.145 | 8.76 | 0.001 | 0 | 8.86 | 0.00131 | -0.145 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.01 | 1.31 | -0.016553 | 8760 | 1 | 8760 | 1 | 1.01 | 1.31 | -0.0166
ExitNoneSCERFFNewIOU | Com-Iltg-dWatt-Exit | SCE | RFF | New | IOU | 8.76 | 0.001 | 0 | 9.52 | 0.00135 | -0.0631 | 8.76 | 0.001 | 0 | 9.52 | 0.00135 | -0.0631 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.09 | 1.35 | -0.0072032 | 8760 | 1 | 8760 | 1 | 1.09 | 1.35 | -0.0072
ExitNoneSCERSDExCZ05 | Com-Iltg-dWatt-Exit | SCE | RSD | Ex | CZ05 | 8.76 | 0.001 | 0 | 9.13 | 0.00132 | -0.0964 | 8.76 | 0.001 | 0 | 9.13 | 0.00132 | -0.0964 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.04 | 1.32 | -0.011005 | 8760 | 1 | 8760 | 1 | 1.04 | 1.32 | -0.011
ExitNoneSCERSDExCZ06 | Com-Iltg-dWatt-Exit | SCE | RSD | Ex | CZ06 | 8.76 | 0.001 | 0 | 9.72 | 0.00133 | -0.0495 | 8.76 | 0.001 | 0 | 9.72 | 0.00133 | -0.0495 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.11 | 1.33 | -0.0056507 | 8760 | 1 | 8760 | 1 | 1.11 | 1.33 | -0.00565
ExitNoneSCERSDExCZ08 | Com-Iltg-dWatt-Exit | SCE | RSD | Ex | CZ08 | 8.76 | 0.001 | 0 | 9.78 | 0.00127 | -0.0426 | 8.76 | 0.001 | 0 | 9.78 | 0.00127 | -0.0426 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.12 | 1.27 | -0.004863 | 8760 | 1 | 8760 | 1 | 1.12 | 1.27 | -0.00486
ExitNoneSCERSDExCZ09 | Com-Iltg-dWatt-Exit | SCE | RSD | Ex | CZ09 | 8.76 | 0.001 | 0 | 9.71 | 0.00128 | -0.046 | 8.76 | 0.001 | 0 | 9.71 | 0.00128 | -0.046 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.11 | 1.28 | -0.0052511 | 8760 | 1 | 8760 | 1 | 1.11 | 1.28 | -0.00525
ExitNoneSCERSDExCZ10 | Com-Iltg-dWatt-Exit | SCE | RSD | Ex | CZ10 | 8.76 | 0.001 | 0 | 9.59 | 0.00118 | -0.0486 | 8.76 | 0.001 | 0 | 9.59 | 0.00118 | -0.0486 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.09 | 1.18 | -0.0055479 | 8760 | 1 | 8760 | 1 | 1.09 | 1.18 | -0.00555
ExitNoneSCERSDExCZ13 | Com-Iltg-dWatt-Exit | SCE | RSD | Ex | CZ13 | 8.76 | 0.001 | 0 | 9.48 | 0.00134 | -0.0714 | 8.76 | 0.001 | 0 | 9.48 | 0.00134 | -0.0714 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.08 | 1.34 | -0.0081507 | 8760 | 1 | 8760 | 1 | 1.08 | 1.34 | -0.00815
ExitNoneSCERSDExCZ14 | Com-Iltg-dWatt-Exit | SCE | RSD | Ex | CZ14 | 8.76 | 0.001 | 0 | 9.37 | 0.0012 | -0.0778 | 8.76 | 0.001 | 0 | 9.37 | 0.0012 | -0.0778 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.07 | 1.2 | -0.0088813 | 8760 | 1 | 8760 | 1 | 1.07 | 1.2 | -0.00888
ExitNoneSCERSDExCZ15 | Com-Iltg-dWatt-Exit | SCE | RSD | Ex | CZ15 | 8.76 | 0.001 | 0 | 10.4 | 0.00135 | -0.0189 | 8.76 | 0.001 | 0 | 10.4 | 0.00135 | -0.0189 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.19 | 1.35 | -0.0021575 | 8760 | 1 | 8760 | 1 | 1.19 | 1.35 | -0.00216
ExitNoneSCERSDExCZ16 | Com-Iltg-dWatt-Exit | SCE | RSD | Ex | CZ16 | 8.76 | 0.001 | 0 | 8.73 | 0.00124 | -0.138 | 8.76 | 0.001 | 0 | 8.73 | 0.00124 | -0.138 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.997 | 1.24 | -0.015753 | 8760 | 1 | 8760 | 1 | 0.997 | 1.24 | -0.0158
ExitNoneSCERSDExIOU | Com-Iltg-dWatt-Exit | SCE | RSD | Ex | IOU | 8.76 | 0.001 | 0 | 9.7 | 0.00127 | -0.0491 | 8.76 | 0.001 | 0 | 9.7 | 0.00127 | -0.0491 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.11 | 1.27 | -0.005605 | 8760 | 1 | 8760 | 1 | 1.11 | 1.27 | -0.00561
ExitNoneSCERSDNewCZ05 | Com-Iltg-dWatt-Exit | SCE | RSD | New | CZ05 | 8.76 | 0.001 | 0 | 8.99 | 0.00135 | -0.115 | 8.76 | 0.001 | 0 | 8.99 | 0.00135 | -0.115 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.03 | 1.35 | -0.013128 | 8760 | 1 | 8760 | 1 | 1.03 | 1.35 | -0.0131
ExitNoneSCERSDNewCZ06 | Com-Iltg-dWatt-Exit | SCE | RSD | New | CZ06 | 8.76 | 0.001 | 0 | 9.59 | 0.00137 | -0.0621 | 8.76 | 0.001 | 0 | 9.59 | 0.00137 | -0.0621 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.09 | 1.37 | -0.007089 | 8760 | 1 | 8760 | 1 | 1.09 | 1.37 | -0.00709
ExitNoneSCERSDNewCZ08 | Com-Iltg-dWatt-Exit | SCE | RSD | New | CZ08 | 8.76 | 0.001 | 0 | 9.67 | 0.00137 | -0.0505 | 8.76 | 0.001 | 0 | 9.67 | 0.00137 | -0.0505 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.1 | 1.37 | -0.0057648 | 8760 | 1 | 8760 | 1 | 1.1 | 1.37 | -0.00576
ExitNoneSCERSDNewCZ09 | Com-Iltg-dWatt-Exit | SCE | RSD | New | CZ09 | 8.76 | 0.001 | 0 | 9.74 | 0.00143 | -0.0554 | 8.76 | 0.001 | 0 | 9.74 | 0.00143 | -0.0554 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.11 | 1.43 | -0.0063242 | 8760 | 1 | 8760 | 1 | 1.11 | 1.43 | -0.00632
ExitNoneSCERSDNewCZ10 | Com-Iltg-dWatt-Exit | SCE | RSD | New | CZ10 | 8.76 | 0.001 | 0 | 9.77 | 0.00144 | -0.0556 | 8.76 | 0.001 | 0 | 9.77 | 0.00144 | -0.0556 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.12 | 1.44 | -0.006347 | 8760 | 1 | 8760 | 1 | 1.12 | 1.44 | -0.00635
ExitNoneSCERSDNewCZ13 | Com-Iltg-dWatt-Exit | SCE | RSD | New | CZ13 | 8.76 | 0.001 | 0 | 9.62 | 0.00148 | -0.0821 | 8.76 | 0.001 | 0 | 9.62 | 0.00148 | -0.0821 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.1 | 1.48 | -0.0093721 | 8760 | 1 | 8760 | 1 | 1.1 | 1.48 | -0.00937
ExitNoneSCERSDNewCZ14 | Com-Iltg-dWatt-Exit | SCE | RSD | New | CZ14 | 8.76 | 0.001 | 0 | 9.54 | 0.00143 | -0.0894 | 8.76 | 0.001 | 0 | 9.54 | 0.00143 | -0.0894 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.09 | 1.43 | -0.010205 | 8760 | 1 | 8760 | 1 | 1.09 | 1.43 | -0.0102
ExitNoneSCERSDNewCZ15 | Com-Iltg-dWatt-Exit | SCE | RSD | New | CZ15 | 8.76 | 0.001 | 0 | 10.5 | 0.00152 | -0.0231 | 8.76 | 0.001 | 0 | 10.5 | 0.00152 | -0.0231 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.2 | 1.52 | -0.002637 | 8760 | 1 | 8760 | 1 | 1.2 | 1.52 | -0.00264
ExitNoneSCERSDNewCZ16 | Com-Iltg-dWatt-Exit | SCE | RSD | New | CZ16 | 8.76 | 0.001 | 0 | 8.8 | 0.00136 | -0.121 | 8.76 | 0.001 | 0 | 8.8 | 0.00136 | -0.121 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1 | 1.36 | -0.013813 | 8760 | 1 | 8760 | 1 | 1 | 1.36 | -0.0138
ExitNoneSCERSDNewIOU | Com-Iltg-dWatt-Exit | SCE | RSD | New | IOU | 8.76 | 0.001 | 0 | 9.71 | 0.00141 | -0.0578 | 8.76 | 0.001 | 0 | 9.71 | 0.00141 | -0.0578 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.11 | 1.41 | -0.0065982 | 8760 | 1 | 8760 | 1 | 1.11 | 1.41 | -0.0066
ExitNoneSCERt3ExCZ05 | Com-Iltg-dWatt-Exit | SCE | Rt3 | Ex | CZ05 | 8.76 | 0.001 | 0 | 9.41 | 0.00141 | -0.061 | 8.76 | 0.001 | 0 | 9.41 | 0.00141 | -0.061 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.07 | 1.41 | -0.0069635 | 8760 | 1 | 8760 | 1 | 1.07 | 1.41 | -0.00696
ExitNoneSCERt3ExCZ06 | Com-Iltg-dWatt-Exit | SCE | Rt3 | Ex | CZ06 | 8.76 | 0.001 | 0 | 10.2 | 0.00138 | -0.017 | 8.76 | 0.001 | 0 | 10.2 | 0.00138 | -0.017 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.16 | 1.38 | -0.0019406 | 8760 | 1 | 8760 | 1 | 1.16 | 1.38 | -0.00194
ExitNoneSCERt3ExCZ08 | Com-Iltg-dWatt-Exit | SCE | Rt3 | Ex | CZ08 | 8.76 | 0.001 | 0 | 10.2 | 0.00135 | -0.0138 | 8.76 | 0.001 | 0 | 10.2 | 0.00135 | -0.0138 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.16 | 1.35 | -0.0015753 | 8760 | 1 | 8760 | 1 | 1.16 | 1.35 | -0.00158
ExitNoneSCERt3ExCZ09 | Com-Iltg-dWatt-Exit | SCE | Rt3 | Ex | CZ09 | 8.76 | 0.001 | 0 | 10 | 0.00137 | -0.0212 | 8.76 | 0.001 | 0 | 10 | 0.00137 | -0.0212 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.14 | 1.37 | -0.0024201 | 8760 | 1 | 8760 | 1 | 1.14 | 1.37 | -0.00242
ExitNoneSCERt3ExCZ10 | Com-Iltg-dWatt-Exit | SCE | Rt3 | Ex | CZ10 | 8.76 | 0.001 | 0 | 9.78 | 0.00135 | -0.0259 | 8.76 | 0.001 | 0 | 9.78 | 0.00135 | -0.0259 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.12 | 1.35 | -0.0029566 | 8760 | 1 | 8760 | 1 | 1.12 | 1.35 | -0.00296
ExitNoneSCERt3ExCZ13 | Com-Iltg-dWatt-Exit | SCE | Rt3 | Ex | CZ13 | 8.76 | 0.001 | 0 | 9.51 | 0.00139 | -0.0625 | 8.76 | 0.001 | 0 | 9.51 | 0.00139 | -0.0625 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.09 | 1.39 | -0.0071347 | 8760 | 1 | 8760 | 1 | 1.09 | 1.39 | -0.00713
ExitNoneSCERt3ExCZ14 | Com-Iltg-dWatt-Exit | SCE | Rt3 | Ex | CZ14 | 8.76 | 0.001 | 0 | 9.38 | 0.00136 | -0.0661 | 8.76 | 0.001 | 0 | 9.38 | 0.00136 | -0.0661 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.07 | 1.36 | -0.0075457 | 8760 | 1 | 8760 | 1 | 1.07 | 1.36 | -0.00755
ExitNoneSCERt3ExCZ15 | Com-Iltg-dWatt-Exit | SCE | Rt3 | Ex | CZ15 | 8.76 | 0.001 | 0 | 10.2 | 0.00139 | -0.0067 | 8.76 | 0.001 | 0 | 10.2 | 0.00139 | -0.0067 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.16 | 1.39 | -0.00076484 | 8760 | 1 | 8760 | 1 | 1.16 | 1.39 | -0.000765
ExitNoneSCERt3ExCZ16 | Com-Iltg-dWatt-Exit | SCE | Rt3 | Ex | CZ16 | 8.76 | 0.001 | 0 | 8.56 | 0.00134 | -0.122 | 8.76 | 0.001 | 0 | 8.56 | 0.00134 | -0.122 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.977 | 1.34 | -0.013927 | 8760 | 1 | 8760 | 1 | 0.977 | 1.34 | -0.0139
ExitNoneSCERt3ExIOU | Com-Iltg-dWatt-Exit | SCE | Rt3 | Ex | IOU | 8.76 | 0.001 | 0 | 10 | 0.00136 | -0.0227 | 8.76 | 0.001 | 0 | 10 | 0.00136 | -0.0227 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.14 | 1.36 | -0.0025913 | 8760 | 1 | 8760 | 1 | 1.14 | 1.36 | -0.00259
ExitNoneSCERt3NewCZ05 | Com-Iltg-dWatt-Exit | SCE | Rt3 | New | CZ05 | 8.76 | 0.001 | 0 | 9.03 | 0.00136 | -0.0761 | 8.76 | 0.001 | 0 | 9.03 | 0.00136 | -0.0761 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.03 | 1.36 | -0.0086872 | 8760 | 1 | 8760 | 1 | 1.03 | 1.36 | -0.00869
ExitNoneSCERt3NewCZ06 | Com-Iltg-dWatt-Exit | SCE | Rt3 | New | CZ06 | 8.76 | 0.001 | 0 | 9.76 | 0.00132 | -0.0258 | 8.76 | 0.001 | 0 | 9.76 | 0.00132 | -0.0258 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.11 | 1.32 | -0.0029452 | 8760 | 1 | 8760 | 1 | 1.11 | 1.32 | -0.00295
ExitNoneSCERt3NewCZ08 | Com-Iltg-dWatt-Exit | SCE | Rt3 | New | CZ08 | 8.76 | 0.001 | 0 | 9.86 | 0.00128 | -0.0201 | 8.76 | 0.001 | 0 | 9.86 | 0.00128 | -0.0201 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.13 | 1.28 | -0.0022945 | 8760 | 1 | 8760 | 1 | 1.13 | 1.28 | -0.00229
ExitNoneSCERt3NewCZ09 | Com-Iltg-dWatt-Exit | SCE | Rt3 | New | CZ09 | 8.76 | 0.001 | 0 | 9.67 | 0.00131 | -0.0259 | 8.76 | 0.001 | 0 | 9.67 | 0.00131 | -0.0259 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.1 | 1.31 | -0.0029566 | 8760 | 1 | 8760 | 1 | 1.1 | 1.31 | -0.00296
ExitNoneSCERt3NewCZ10 | Com-Iltg-dWatt-Exit | SCE | Rt3 | New | CZ10 | 8.76 | 0.001 | 0 | 9.66 | 0.00132 | -0.0322 | 8.76 | 0.001 | 0 | 9.66 | 0.00132 | -0.0322 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.1 | 1.32 | -0.0036758 | 8760 | 1 | 8760 | 1 | 1.1 | 1.32 | -0.00368
ExitNoneSCERt3NewCZ13 | Com-Iltg-dWatt-Exit | SCE | Rt3 | New | CZ13 | 8.76 | 0.001 | 0 | 9.37 | 0.00136 | -0.0674 | 8.76 | 0.001 | 0 | 9.37 | 0.00136 | -0.0674 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.07 | 1.36 | -0.0076941 | 8760 | 1 | 8760 | 1 | 1.07 | 1.36 | -0.00769
ExitNoneSCERt3NewCZ14 | Com-Iltg-dWatt-Exit | SCE | Rt3 | New | CZ14 | 8.76 | 0.001 | 0 | 9.29 | 0.00134 | -0.0676 | 8.76 | 0.001 | 0 | 9.29 | 0.00134 | -0.0676 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.06 | 1.34 | -0.0077169 | 8760 | 1 | 8760 | 1 | 1.06 | 1.34 | -0.00772
ExitNoneSCERt3NewCZ15 | Com-Iltg-dWatt-Exit | SCE | Rt3 | New | CZ15 | 8.76 | 0.001 | 0 | 10.2 | 0.00144 | -0.00566 | 8.76 | 0.001 | 0 | 10.2 | 0.00144 | -0.00566 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.16 | 1.44 | -0.00064612 | 8760 | 1 | 8760 | 1 | 1.16 | 1.44 | -0.000646
ExitNoneSCERt3NewCZ16 | Com-Iltg-dWatt-Exit | SCE | Rt3 | New | CZ16 | 8.76 | 0.001 | 0 | 8.52 | 0.00133 | -0.12 | 8.76 | 0.001 | 0 | 8.52 | 0.00133 | -0.12 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.973 | 1.33 | -0.013699 | 8760 | 1 | 8760 | 1 | 0.973 | 1.33 | -0.0137
ExitNoneSCERt3NewIOU | Com-Iltg-dWatt-Exit | SCE | Rt3 | New | IOU | 8.76 | 0.001 | 0 | 9.71 | 0.00132 | -0.0306 | 8.76 | 0.001 | 0 | 9.71 | 0.00132 | -0.0306 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.11 | 1.32 | -0.0034932 | 8760 | 1 | 8760 | 1 | 1.11 | 1.32 | -0.00349
ExitNoneSCERtLExCZ05 | Com-Iltg-dWatt-Exit | SCE | RtL | Ex | CZ05 | 8.76 | 0.001 | 0 | 9.09 | 0.00132 | -0.0752 | 8.76 | 0.001 | 0 | 9.09 | 0.00132 | -0.0752 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.04 | 1.32 | -0.0085845 | 8760 | 1 | 8760 | 1 | 1.04 | 1.32 | -0.00858
ExitNoneSCERtLExCZ06 | Com-Iltg-dWatt-Exit | SCE | RtL | Ex | CZ06 | 8.76 | 0.001 | 0 | 9.78 | 0.00133 | -0.0335 | 8.76 | 0.001 | 0 | 9.78 | 0.00133 | -0.0335 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.12 | 1.33 | -0.0038242 | 8760 | 1 | 8760 | 1 | 1.12 | 1.33 | -0.00382
ExitNoneSCERtLExCZ08 | Com-Iltg-dWatt-Exit | SCE | RtL | Ex | CZ08 | 8.76 | 0.001 | 0 | 9.81 | 0.00133 | -0.0321 | 8.76 | 0.001 | 0 | 9.81 | 0.00133 | -0.0321 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.12 | 1.33 | -0.0036644 | 8760 | 1 | 8760 | 1 | 1.12 | 1.33 | -0.00366
ExitNoneSCERtLExCZ09 | Com-Iltg-dWatt-Exit | SCE | RtL | Ex | CZ09 | 8.76 | 0.001 | 0 | 9.71 | 0.00136 | -0.0336 | 8.76 | 0.001 | 0 | 9.71 | 0.00136 | -0.0336 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.11 | 1.36 | -0.0038356 | 8760 | 1 | 8760 | 1 | 1.11 | 1.36 | -0.00384
ExitNoneSCERtLExCZ10 | Com-Iltg-dWatt-Exit | SCE | RtL | Ex | CZ10 | 8.76 | 0.001 | 0 | 9.54 | 0.00134 | -0.0384 | 8.76 | 0.001 | 0 | 9.54 | 0.00134 | -0.0384 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.09 | 1.34 | -0.0043836 | 8760 | 1 | 8760 | 1 | 1.09 | 1.34 | -0.00438
ExitNoneSCERtLExCZ13 | Com-Iltg-dWatt-Exit | SCE | RtL | Ex | CZ13 | 8.76 | 0.001 | 0 | 9.37 | 0.00135 | -0.0624 | 8.76 | 0.001 | 0 | 9.37 | 0.00135 | -0.0624 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.07 | 1.35 | -0.0071233 | 8760 | 1 | 8760 | 1 | 1.07 | 1.35 | -0.00712
ExitNoneSCERtLExCZ14 | Com-Iltg-dWatt-Exit | SCE | RtL | Ex | CZ14 | 8.76 | 0.001 | 0 | 9.35 | 0.00137 | -0.0625 | 8.76 | 0.001 | 0 | 9.35 | 0.00137 | -0.0625 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.07 | 1.37 | -0.0071347 | 8760 | 1 | 8760 | 1 | 1.07 | 1.37 | -0.00713
ExitNoneSCERtLExCZ15 | Com-Iltg-dWatt-Exit | SCE | RtL | Ex | CZ15 | 8.76 | 0.001 | 0 | 10 | 0.00137 | -0.0152 | 8.76 | 0.001 | 0 | 10 | 0.00137 | -0.0152 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.14 | 1.37 | -0.0017352 | 8760 | 1 | 8760 | 1 | 1.14 | 1.37 | -0.00174
ExitNoneSCERtLExCZ16 | Com-Iltg-dWatt-Exit | SCE | RtL | Ex | CZ16 | 8.76 | 0.001 | 0 | 8.47 | 0.00127 | -0.118 | 8.76 | 0.001 | 0 | 8.47 | 0.00127 | -0.118 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.967 | 1.27 | -0.01347 | 8760 | 1 | 8760 | 1 | 0.967 | 1.27 | -0.0135
ExitNoneSCERtLExIOU | Com-Iltg-dWatt-Exit | SCE | RtL | Ex | IOU | 8.76 | 0.001 | 0 | 9.7 | 0.00134 | -0.0365 | 8.76 | 0.001 | 0 | 9.7 | 0.00134 | -0.0365 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.11 | 1.34 | -0.0041667 | 8760 | 1 | 8760 | 1 | 1.11 | 1.34 | -0.00417
ExitNoneSCERtLNewCZ05 | Com-Iltg-dWatt-Exit | SCE | RtL | New | CZ05 | 8.76 | 0.001 | 0 | 8.91 | 0.00132 | -0.0911 | 8.76 | 0.001 | 0 | 8.91 | 0.00132 | -0.0911 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.02 | 1.32 | -0.0104 | 8760 | 1 | 8760 | 1 | 1.02 | 1.32 | -0.0104
ExitNoneSCERtLNewCZ06 | Com-Iltg-dWatt-Exit | SCE | RtL | New | CZ06 | 8.76 | 0.001 | 0 | 9.44 | 0.00133 | -0.0393 | 8.76 | 0.001 | 0 | 9.44 | 0.00133 | -0.0393 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.08 | 1.33 | -0.0044863 | 8760 | 1 | 8760 | 1 | 1.08 | 1.33 | -0.00449
ExitNoneSCERtLNewCZ08 | Com-Iltg-dWatt-Exit | SCE | RtL | New | CZ08 | 8.76 | 0.001 | 0 | 9.56 | 0.00136 | -0.0301 | 8.76 | 0.001 | 0 | 9.56 | 0.00136 | -0.0301 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.09 | 1.36 | -0.0034361 | 8760 | 1 | 8760 | 1 | 1.09 | 1.36 | -0.00344
ExitNoneSCERtLNewCZ09 | Com-Iltg-dWatt-Exit | SCE | RtL | New | CZ09 | 8.76 | 0.001 | 0 | 9.57 | 0.00143 | -0.0353 | 8.76 | 0.001 | 0 | 9.57 | 0.00143 | -0.0353 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.09 | 1.43 | -0.0040297 | 8760 | 1 | 8760 | 1 | 1.09 | 1.43 | -0.00403
ExitNoneSCERtLNewCZ10 | Com-Iltg-dWatt-Exit | SCE | RtL | New | CZ10 | 8.76 | 0.001 | 0 | 9.62 | 0.00142 | -0.0443 | 8.76 | 0.001 | 0 | 9.62 | 0.00142 | -0.0443 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.1 | 1.42 | -0.0050571 | 8760 | 1 | 8760 | 1 | 1.1 | 1.42 | -0.00506
ExitNoneSCERtLNewCZ13 | Com-Iltg-dWatt-Exit | SCE | RtL | New | CZ13 | 8.76 | 0.001 | 0 | 9.44 | 0.00142 | -0.0702 | 8.76 | 0.001 | 0 | 9.44 | 0.00142 | -0.0702 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.08 | 1.42 | -0.0080137 | 8760 | 1 | 8760 | 1 | 1.08 | 1.42 | -0.00801
ExitNoneSCERtLNewCZ14 | Com-Iltg-dWatt-Exit | SCE | RtL | New | CZ14 | 8.76 | 0.001 | 0 | 9.36 | 0.00142 | -0.0713 | 8.76 | 0.001 | 0 | 9.36 | 0.00142 | -0.0713 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.07 | 1.42 | -0.0081393 | 8760 | 1 | 8760 | 1 | 1.07 | 1.42 | -0.00814
ExitNoneSCERtLNewCZ15 | Com-Iltg-dWatt-Exit | SCE | RtL | New | CZ15 | 8.76 | 0.001 | 0 | 10.2 | 0.00145 | -0.0167 | 8.76 | 0.001 | 0 | 10.2 | 0.00145 | -0.0167 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.16 | 1.45 | -0.0019064 | 8760 | 1 | 8760 | 1 | 1.16 | 1.45 | -0.00191
ExitNoneSCERtLNewCZ16 | Com-Iltg-dWatt-Exit | SCE | RtL | New | CZ16 | 8.76 | 0.001 | 0 | 8.53 | 0.00132 | -0.117 | 8.76 | 0.001 | 0 | 8.53 | 0.00132 | -0.117 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.974 | 1.32 | -0.013356 | 8760 | 1 | 8760 | 1 | 0.974 | 1.32 | -0.0134
ExitNoneSCERtLNewIOU | Com-Iltg-dWatt-Exit | SCE | RtL | New | IOU | 8.76 | 0.001 | 0 | 9.56 | 0.00139 | -0.0412 | 8.76 | 0.001 | 0 | 9.56 | 0.00139 | -0.0412 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.09 | 1.39 | -0.0047032 | 8760 | 1 | 8760 | 1 | 1.09 | 1.39 | -0.0047
ExitNoneSCERtSExCZ05 | Com-Iltg-dWatt-Exit | SCE | RtS | Ex | CZ05 | 8.76 | 0.001 | 0 | 9.11 | 0.00135 | -0.0624 | 8.76 | 0.001 | 0 | 9.11 | 0.00135 | -0.0624 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.04 | 1.35 | -0.0071233 | 8760 | 1 | 8760 | 1 | 1.04 | 1.35 | -0.00712
ExitNoneSCERtSExCZ06 | Com-Iltg-dWatt-Exit | SCE | RtS | Ex | CZ06 | 8.76 | 0.001 | 0 | 9.73 | 0.00135 | -0.0264 | 8.76 | 0.001 | 0 | 9.73 | 0.00135 | -0.0264 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.11 | 1.35 | -0.0030137 | 8760 | 1 | 8760 | 1 | 1.11 | 1.35 | -0.00301
ExitNoneSCERtSExCZ08 | Com-Iltg-dWatt-Exit | SCE | RtS | Ex | CZ08 | 8.76 | 0.001 | 0 | 9.8 | 0.00136 | -0.0239 | 8.76 | 0.001 | 0 | 9.8 | 0.00136 | -0.0239 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.12 | 1.36 | -0.0027283 | 8760 | 1 | 8760 | 1 | 1.12 | 1.36 | -0.00273
ExitNoneSCERtSExCZ09 | Com-Iltg-dWatt-Exit | SCE | RtS | Ex | CZ09 | 8.76 | 0.001 | 0 | 9.67 | 0.00138 | -0.0268 | 8.76 | 0.001 | 0 | 9.67 | 0.00138 | -0.0268 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.1 | 1.38 | -0.0030594 | 8760 | 1 | 8760 | 1 | 1.1 | 1.38 | -0.00306
ExitNoneSCERtSExCZ10 | Com-Iltg-dWatt-Exit | SCE | RtS | Ex | CZ10 | 8.76 | 0.001 | 0 | 9.53 | 0.00135 | -0.031 | 8.76 | 0.001 | 0 | 9.53 | 0.00135 | -0.031 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.09 | 1.35 | -0.0035388 | 8760 | 1 | 8760 | 1 | 1.09 | 1.35 | -0.00354
ExitNoneSCERtSExCZ13 | Com-Iltg-dWatt-Exit | SCE | RtS | Ex | CZ13 | 8.76 | 0.001 | 0 | 9.37 | 0.00134 | -0.0563 | 8.76 | 0.001 | 0 | 9.37 | 0.00134 | -0.0563 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.07 | 1.34 | -0.0064269 | 8760 | 1 | 8760 | 1 | 1.07 | 1.34 | -0.00643
ExitNoneSCERtSExCZ14 | Com-Iltg-dWatt-Exit | SCE | RtS | Ex | CZ14 | 8.76 | 0.001 | 0 | 9.35 | 0.00136 | -0.0549 | 8.76 | 0.001 | 0 | 9.35 | 0.00136 | -0.0549 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.07 | 1.36 | -0.0062671 | 8760 | 1 | 8760 | 1 | 1.07 | 1.36 | -0.00627
ExitNoneSCERtSExCZ15 | Com-Iltg-dWatt-Exit | SCE | RtS | Ex | CZ15 | 8.76 | 0.001 | 0 | 10.1 | 0.00135 | -0.0106 | 8.76 | 0.001 | 0 | 10.1 | 0.00135 | -0.0106 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.15 | 1.35 | -0.00121 | 8760 | 1 | 8760 | 1 | 1.15 | 1.35 | -0.00121
ExitNoneSCERtSExCZ16 | Com-Iltg-dWatt-Exit | SCE | RtS | Ex | CZ16 | 8.76 | 0.001 | 0 | 8.55 | 0.00128 | -0.101 | 8.76 | 0.001 | 0 | 8.55 | 0.00128 | -0.101 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.976 | 1.28 | -0.01153 | 8760 | 1 | 8760 | 1 | 0.976 | 1.28 | -0.0115
ExitNoneSCERtSExIOU | Com-Iltg-dWatt-Exit | SCE | RtS | Ex | IOU | 8.76 | 0.001 | 0 | 9.67 | 0.00136 | -0.0291 | 8.76 | 0.001 | 0 | 9.67 | 0.00136 | -0.0291 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.1 | 1.36 | -0.0033219 | 8760 | 1 | 8760 | 1 | 1.1 | 1.36 | -0.00332
ExitNoneSCERtSNewCZ05 | Com-Iltg-dWatt-Exit | SCE | RtS | New | CZ05 | 8.76 | 0.001 | 0 | 8.88 | 0.00132 | -0.0695 | 8.76 | 0.001 | 0 | 8.88 | 0.00132 | -0.0695 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.01 | 1.32 | -0.0079338 | 8760 | 1 | 8760 | 1 | 1.01 | 1.32 | -0.00793
ExitNoneSCERtSNewCZ06 | Com-Iltg-dWatt-Exit | SCE | RtS | New | CZ06 | 8.76 | 0.001 | 0 | 9.43 | 0.00132 | -0.0321 | 8.76 | 0.001 | 0 | 9.43 | 0.00132 | -0.0321 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.08 | 1.32 | -0.0036644 | 8760 | 1 | 8760 | 1 | 1.08 | 1.32 | -0.00366
ExitNoneSCERtSNewCZ08 | Com-Iltg-dWatt-Exit | SCE | RtS | New | CZ08 | 8.76 | 0.001 | 0 | 9.5 | 0.00135 | -0.0272 | 8.76 | 0.001 | 0 | 9.5 | 0.00135 | -0.0272 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.08 | 1.35 | -0.003105 | 8760 | 1 | 8760 | 1 | 1.08 | 1.35 | -0.00311
ExitNoneSCERtSNewCZ09 | Com-Iltg-dWatt-Exit | SCE | RtS | New | CZ09 | 8.76 | 0.001 | 0 | 9.44 | 0.0014 | -0.0337 | 8.76 | 0.001 | 0 | 9.44 | 0.0014 | -0.0337 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.08 | 1.4 | -0.003847 | 8760 | 1 | 8760 | 1 | 1.08 | 1.4 | -0.00385
ExitNoneSCERtSNewCZ10 | Com-Iltg-dWatt-Exit | SCE | RtS | New | CZ10 | 8.76 | 0.001 | 0 | 9.57 | 0.00143 | -0.0392 | 8.76 | 0.001 | 0 | 9.57 | 0.00143 | -0.0392 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.09 | 1.43 | -0.0044749 | 8760 | 1 | 8760 | 1 | 1.09 | 1.43 | -0.00447
ExitNoneSCERtSNewCZ13 | Com-Iltg-dWatt-Exit | SCE | RtS | New | CZ13 | 8.76 | 0.001 | 0 | 9.38 | 0.00141 | -0.0577 | 8.76 | 0.001 | 0 | 9.38 | 0.00141 | -0.0577 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.07 | 1.41 | -0.0065868 | 8760 | 1 | 8760 | 1 | 1.07 | 1.41 | -0.00659
ExitNoneSCERtSNewCZ14 | Com-Iltg-dWatt-Exit | SCE | RtS | New | CZ14 | 8.76 | 0.001 | 0 | 9.38 | 0.00141 | -0.0583 | 8.76 | 0.001 | 0 | 9.38 | 0.00141 | -0.0583 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.07 | 1.41 | -0.0066553 | 8760 | 1 | 8760 | 1 | 1.07 | 1.41 | -0.00666
ExitNoneSCERtSNewCZ15 | Com-Iltg-dWatt-Exit | SCE | RtS | New | CZ15 | 8.76 | 0.001 | 0 | 10.1 | 0.00146 | -0.00525 | 8.76 | 0.001 | 0 | 10.1 | 0.00146 | -0.00525 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.15 | 1.46 | -0.00059932 | 8760 | 1 | 8760 | 1 | 1.15 | 1.46 | -0.000599
ExitNoneSCERtSNewCZ16 | Com-Iltg-dWatt-Exit | SCE | RtS | New | CZ16 | 8.76 | 0.001 | 0 | 8.51 | 0.00133 | -0.108 | 8.76 | 0.001 | 0 | 8.51 | 0.00133 | -0.108 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.971 | 1.33 | -0.012329 | 8760 | 1 | 8760 | 1 | 0.971 | 1.33 | -0.0123
ExitNoneSCERtSNewIOU | Com-Iltg-dWatt-Exit | SCE | RtS | New | IOU | 8.76 | 0.001 | 0 | 9.5 | 0.00139 | -0.0355 | 8.76 | 0.001 | 0 | 9.5 | 0.00139 | -0.0355 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.08 | 1.39 | -0.0040525 | 8760 | 1 | 8760 | 1 | 1.08 | 1.39 | -0.00405
ExitNoneSCEs_AgrExCZ05 | Com-Iltg-dWatt-Exit | SCE | s_Agr | Ex | CZ05 | 8.76 | 0.001 | 0 | 9.08 | 0.001462 | -0.04938 | 8.76 | 0.001 | 0 | 9.08 | 0.001462 | -0.04938 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.04 | 1.46 | -0.005637 | 8760 | 1 | 8760 | 1 | 1.04 | 1.46 | -0.00564
ExitNoneSCEs_AgrExCZ06 | Com-Iltg-dWatt-Exit | SCE | s_Agr | Ex | CZ06 | 8.76 | 0.001 | 0 | 9.56 | 0.001342 | -0.01984 | 8.76 | 0.001 | 0 | 9.56 | 0.001342 | -0.01984 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.09 | 1.34 | -0.0022648 | 8760 | 1 | 8760 | 1 | 1.09 | 1.34 | -0.00226
ExitNoneSCEs_AgrExCZ08 | Com-Iltg-dWatt-Exit | SCE | s_Agr | Ex | CZ08 | 8.76 | 0.001 | 0 | 9.64 | 0.001336 | -0.01702 | 8.76 | 0.001 | 0 | 9.64 | 0.001336 | -0.01702 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.1 | 1.34 | -0.0019429 | 8760 | 1 | 8760 | 1 | 1.1 | 1.34 | -0.00194
ExitNoneSCEs_AgrExCZ09 | Com-Iltg-dWatt-Exit | SCE | s_Agr | Ex | CZ09 | 8.76 | 0.001 | 0 | 9.55 | 0.001372 | -0.02116 | 8.76 | 0.001 | 0 | 9.55 | 0.001372 | -0.02116 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.09 | 1.37 | -0.0024155 | 8760 | 1 | 8760 | 1 | 1.09 | 1.37 | -0.00242
ExitNoneSCEs_AgrExCZ10 | Com-Iltg-dWatt-Exit | SCE | s_Agr | Ex | CZ10 | 8.76 | 0.001 | 0 | 9.34 | 0.001362 | -0.027 | 8.76 | 0.001 | 0 | 9.34 | 0.001362 | -0.027 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.07 | 1.36 | -0.0030822 | 8760 | 1 | 8760 | 1 | 1.07 | 1.36 | -0.00308
ExitNoneSCEs_AgrExCZ13 | Com-Iltg-dWatt-Exit | SCE | s_Agr | Ex | CZ13 | 8.76 | 0.001 | 0 | 9.308 | 0.001304 | -0.0465 | 8.76 | 0.001 | 0 | 9.308 | 0.001304 | -0.0465 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.06 | 1.3 | -0.0053082 | 8760 | 1 | 8760 | 1 | 1.06 | 1.3 | -0.00531
ExitNoneSCEs_AgrExCZ14 | Com-Iltg-dWatt-Exit | SCE | s_Agr | Ex | CZ14 | 8.76 | 0.001 | 0 | 9.196 | 0.001326 | -0.05234 | 8.76 | 0.001 | 0 | 9.196 | 0.001326 | -0.05234 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.05 | 1.33 | -0.0059749 | 8760 | 1 | 8760 | 1 | 1.05 | 1.33 | -0.00597
ExitNoneSCEs_AgrExCZ15 | Com-Iltg-dWatt-Exit | SCE | s_Agr | Ex | CZ15 | 8.76 | 0.001 | 0 | 10.28 | 0.001256 | -0.008776 | 8.76 | 0.001 | 0 | 10.28 | 0.001256 | -0.008776 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.17 | 1.26 | -0.0010018 | 8760 | 1 | 8760 | 1 | 1.17 | 1.26 | -0.001
ExitNoneSCEs_AgrExCZ16 | Com-Iltg-dWatt-Exit | SCE | s_Agr | Ex | CZ16 | 8.76 | 0.001 | 0 | 8.516 | 0.001308 | -0.09486 | 8.76 | 0.001 | 0 | 8.516 | 0.001308 | -0.09486 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.972 | 1.31 | -0.010829 | 8760 | 1 | 8760 | 1 | 0.972 | 1.31 | -0.0108
ExitNoneSCEs_AgrExIOU | Com-Iltg-dWatt-Exit | SCE | s_Agr | Ex | IOU | 8.76 | 0.001 | 0 | 9.544 | 0.001344 | -0.0232 | 8.76 | 0.001 | 0 | 9.544 | 0.001344 | -0.0232 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.09 | 1.34 | -0.0026484 | 8760 | 1 | 8760 | 1 | 1.09 | 1.34 | -0.00265
ExitNoneSCEs_CliExCZ05 | Com-Iltg-dWatt-Exit | SCE | s_Cli | Ex | CZ05 | 8.76 | 0.001 | 0 | 8.96 | 0.00135 | -0.10745 | 8.76 | 0.001 | 0 | 8.96 | 0.00135 | -0.10745 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.02 | 1.35 | -0.012266 | 8760 | 1 | 8760 | 1 | 1.02 | 1.35 | -0.0123
ExitNoneSCEs_CliExCZ06 | Com-Iltg-dWatt-Exit | SCE | s_Cli | Ex | CZ06 | 8.76 | 0.001 | 0 | 9.535 | 0.001355 | -0.0706 | 8.76 | 0.001 | 0 | 9.535 | 0.001355 | -0.0706 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.09 | 1.35 | -0.0080594 | 8760 | 1 | 8760 | 1 | 1.09 | 1.35 | -0.00806
ExitNoneSCEs_CliExCZ08 | Com-Iltg-dWatt-Exit | SCE | s_Cli | Ex | CZ08 | 8.76 | 0.001 | 0 | 9.635 | 0.00137 | -0.06755 | 8.76 | 0.001 | 0 | 9.635 | 0.00137 | -0.06755 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.1 | 1.37 | -0.0077112 | 8760 | 1 | 8760 | 1 | 1.1 | 1.37 | -0.00771
ExitNoneSCEs_CliExCZ09 | Com-Iltg-dWatt-Exit | SCE | s_Cli | Ex | CZ09 | 8.76 | 0.001 | 0 | 9.635 | 0.0014 | -0.0694 | 8.76 | 0.001 | 0 | 9.635 | 0.0014 | -0.0694 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.1 | 1.4 | -0.0079224 | 8760 | 1 | 8760 | 1 | 1.1 | 1.4 | -0.00792
ExitNoneSCEs_CliExCZ10 | Com-Iltg-dWatt-Exit | SCE | s_Cli | Ex | CZ10 | 8.76 | 0.001 | 0 | 9.495 | 0.00139 | -0.0711 | 8.76 | 0.001 | 0 | 9.495 | 0.00139 | -0.0711 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.08 | 1.39 | -0.0081164 | 8760 | 1 | 8760 | 1 | 1.08 | 1.39 | -0.00812
ExitNoneSCEs_CliExCZ13 | Com-Iltg-dWatt-Exit | SCE | s_Cli | Ex | CZ13 | 8.76 | 0.001 | 0 | 9.4 | 0.001375 | -0.08265 | 8.76 | 0.001 | 0 | 9.4 | 0.001375 | -0.08265 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.07 | 1.37 | -0.0094349 | 8760 | 1 | 8760 | 1 | 1.07 | 1.37 | -0.00943
ExitNoneSCEs_CliExCZ14 | Com-Iltg-dWatt-Exit | SCE | s_Cli | Ex | CZ14 | 8.76 | 0.001 | 0 | 9.365 | 0.001375 | -0.08295 | 8.76 | 0.001 | 0 | 9.365 | 0.001375 | -0.08295 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.07 | 1.37 | -0.0094692 | 8760 | 1 | 8760 | 1 | 1.07 | 1.37 | -0.00947
ExitNoneSCEs_CliExCZ15 | Com-Iltg-dWatt-Exit | SCE | s_Cli | Ex | CZ15 | 8.76 | 0.001 | 0 | 10.28 | 0.001375 | -0.04049 | 8.76 | 0.001 | 0 | 10.28 | 0.001375 | -0.04049 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.17 | 1.37 | -0.0046221 | 8760 | 1 | 8760 | 1 | 1.17 | 1.37 | -0.00462
ExitNoneSCEs_CliExCZ16 | Com-Iltg-dWatt-Exit | SCE | s_Cli | Ex | CZ16 | 8.76 | 0.001 | 0 | 8.58 | 0.00132 | -0.12215 | 8.76 | 0.001 | 0 | 8.58 | 0.00132 | -0.12215 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.979 | 1.32 | -0.013944 | 8760 | 1 | 8760 | 1 | 0.979 | 1.32 | -0.0139
ExitNoneSCEs_CliExIOU | Com-Iltg-dWatt-Exit | SCE | s_Cli | Ex | IOU | 8.76 | 0.001 | 0 | 9.565 | 0.001375 | -0.0712 | 8.76 | 0.001 | 0 | 9.565 | 0.001375 | -0.0712 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.09 | 1.37 | -0.0081279 | 8760 | 1 | 8760 | 1 | 1.09 | 1.37 | -0.00813
ExitNoneSCEs_FStExCZ05 | Com-Iltg-dWatt-Exit | SCE | s_FSt | Ex | CZ05 | 8.76 | 0.001 | 0 | 8.81 | 0.001305 | -0.1037 | 8.76 | 0.001 | 0 | 8.81 | 0.001305 | -0.1037 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.01 | 1.3 | -0.011838 | 8760 | 1 | 8760 | 1 | 1.01 | 1.3 | -0.0118
ExitNoneSCEs_FStExCZ06 | Com-Iltg-dWatt-Exit | SCE | s_FSt | Ex | CZ06 | 8.76 | 0.001 | 0 | 9.37 | 0.00131 | -0.0762 | 8.76 | 0.001 | 0 | 9.37 | 0.00131 | -0.0762 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.07 | 1.31 | -0.0086986 | 8760 | 1 | 8760 | 1 | 1.07 | 1.31 | -0.0087
ExitNoneSCEs_FStExCZ08 | Com-Iltg-dWatt-Exit | SCE | s_FSt | Ex | CZ08 | 8.76 | 0.001 | 0 | 9.485 | 0.001405 | -0.06295 | 8.76 | 0.001 | 0 | 9.485 | 0.001405 | -0.06295 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.08 | 1.4 | -0.0071861 | 8760 | 1 | 8760 | 1 | 1.08 | 1.4 | -0.00719
ExitNoneSCEs_FStExCZ09 | Com-Iltg-dWatt-Exit | SCE | s_FSt | Ex | CZ09 | 8.76 | 0.001 | 0 | 9.41 | 0.001355 | -0.0654 | 8.76 | 0.001 | 0 | 9.41 | 0.001355 | -0.0654 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.07 | 1.35 | -0.0074658 | 8760 | 1 | 8760 | 1 | 1.07 | 1.35 | -0.00747
ExitNoneSCEs_FStExCZ10 | Com-Iltg-dWatt-Exit | SCE | s_FSt | Ex | CZ10 | 8.76 | 0.001 | 0 | 9.395 | 0.00134 | -0.0695 | 8.76 | 0.001 | 0 | 9.395 | 0.00134 | -0.0695 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.07 | 1.34 | -0.0079338 | 8760 | 1 | 8760 | 1 | 1.07 | 1.34 | -0.00793
ExitNoneSCEs_FStExCZ13 | Com-Iltg-dWatt-Exit | SCE | s_FSt | Ex | CZ13 | 8.76 | 0.001 | 0 | 9.305 | 0.001335 | -0.08065 | 8.76 | 0.001 | 0 | 9.305 | 0.001335 | -0.08065 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.06 | 1.33 | -0.0092066 | 8760 | 1 | 8760 | 1 | 1.06 | 1.33 | -0.00921
ExitNoneSCEs_FStExCZ14 | Com-Iltg-dWatt-Exit | SCE | s_FSt | Ex | CZ14 | 8.76 | 0.001 | 0 | 9.285 | 0.00143 | -0.07895 | 8.76 | 0.001 | 0 | 9.285 | 0.00143 | -0.07895 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.06 | 1.43 | -0.0090126 | 8760 | 1 | 8760 | 1 | 1.06 | 1.43 | -0.00901
ExitNoneSCEs_FStExCZ15 | Com-Iltg-dWatt-Exit | SCE | s_FSt | Ex | CZ15 | 8.76 | 0.001 | 0 | 10.015 | 0.001345 | -0.03695 | 8.76 | 0.001 | 0 | 10.015 | 0.001345 | -0.03695 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.14 | 1.34 | -0.004218 | 8760 | 1 | 8760 | 1 | 1.14 | 1.34 | -0.00422
ExitNoneSCEs_FStExCZ16 | Com-Iltg-dWatt-Exit | SCE | s_FSt | Ex | CZ16 | 8.76 | 0.001 | 0 | 8.5 | 0.00128 | -0.119 | 8.76 | 0.001 | 0 | 8.5 | 0.00128 | -0.119 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.97 | 1.28 | -0.013584 | 8760 | 1 | 8760 | 1 | 0.97 | 1.28 | -0.0136
ExitNoneSCEs_FStExIOU | Com-Iltg-dWatt-Exit | SCE | s_FSt | Ex | IOU | 8.76 | 0.001 | 0 | 9.415 | 0.00136 | -0.06905 | 8.76 | 0.001 | 0 | 9.415 | 0.00136 | -0.06905 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.07 | 1.36 | -0.0078824 | 8760 | 1 | 8760 | 1 | 1.07 | 1.36 | -0.00788
ExitNoneSCEs_IndExCZ05 | Com-Iltg-dWatt-Exit | SCE | s_Ind | Ex | CZ05 | 8.76 | 0.001 | 0 | 9.505 | 0.001475 | -0.03011 | 8.76 | 0.001 | 0 | 9.505 | 0.001475 | -0.03011 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.09 | 1.47 | -0.0034372 | 8760 | 1 | 8760 | 1 | 1.09 | 1.47 | -0.00344
ExitNoneSCEs_IndExCZ06 | Com-Iltg-dWatt-Exit | SCE | s_Ind | Ex | CZ06 | 8.76 | 0.001 | 0 | 9.89 | 0.001305 | -0.011955 | 8.76 | 0.001 | 0 | 9.89 | 0.001305 | -0.011955 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.13 | 1.3 | -0.0013647 | 8760 | 1 | 8760 | 1 | 1.13 | 1.3 | -0.00136
ExitNoneSCEs_IndExCZ08 | Com-Iltg-dWatt-Exit | SCE | s_Ind | Ex | CZ08 | 8.76 | 0.001 | 0 | 9.93 | 0.00136 | -0.009955 | 8.76 | 0.001 | 0 | 9.93 | 0.00136 | -0.009955 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.13 | 1.36 | -0.0011364 | 8760 | 1 | 8760 | 1 | 1.13 | 1.36 | -0.00114
ExitNoneSCEs_IndExCZ09 | Com-Iltg-dWatt-Exit | SCE | s_Ind | Ex | CZ09 | 8.76 | 0.001 | 0 | 9.88 | 0.00138 | -0.01306 | 8.76 | 0.001 | 0 | 9.88 | 0.00138 | -0.01306 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.13 | 1.38 | -0.0014909 | 8760 | 1 | 8760 | 1 | 1.13 | 1.38 | -0.00149
ExitNoneSCEs_IndExCZ10 | Com-Iltg-dWatt-Exit | SCE | s_Ind | Ex | CZ10 | 8.76 | 0.001 | 0 | 9.605 | 0.001375 | -0.016825 | 8.76 | 0.001 | 0 | 9.605 | 0.001375 | -0.016825 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.1 | 1.37 | -0.0019207 | 8760 | 1 | 8760 | 1 | 1.1 | 1.37 | -0.00192
ExitNoneSCEs_IndExCZ13 | Com-Iltg-dWatt-Exit | SCE | s_Ind | Ex | CZ13 | 8.76 | 0.001 | 0 | 9.665 | 0.00128 | -0.02951 | 8.76 | 0.001 | 0 | 9.665 | 0.00128 | -0.02951 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.1 | 1.28 | -0.0033687 | 8760 | 1 | 8760 | 1 | 1.1 | 1.28 | -0.00337
ExitNoneSCEs_IndExCZ14 | Com-Iltg-dWatt-Exit | SCE | s_Ind | Ex | CZ14 | 8.76 | 0.001 | 0 | 9.55 | 0.001345 | -0.034 | 8.76 | 0.001 | 0 | 9.55 | 0.001345 | -0.034 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.09 | 1.34 | -0.0038813 | 8760 | 1 | 8760 | 1 | 1.09 | 1.34 | -0.00388
ExitNoneSCEs_IndExCZ15 | Com-Iltg-dWatt-Exit | SCE | s_Ind | Ex | CZ15 | 8.76 | 0.001 | 0 | 10.45 | 0.001325 | -0.00513 | 8.76 | 0.001 | 0 | 10.45 | 0.001325 | -0.00513 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.19 | 1.32 | -0.00058562 | 8760 | 1 | 8760 | 1 | 1.19 | 1.32 | -0.000586
ExitNoneSCEs_IndExCZ16 | Com-Iltg-dWatt-Exit | SCE | s_Ind | Ex | CZ16 | 8.76 | 0.001 | 0 | 8.91 | 0.00128 | -0.0679 | 8.76 | 0.001 | 0 | 8.91 | 0.00128 | -0.0679 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.02 | 1.28 | -0.0077511 | 8760 | 1 | 8760 | 1 | 1.02 | 1.28 | -0.00775
ExitNoneSCEs_IndExIOU | Com-Iltg-dWatt-Exit | SCE | s_Ind | Ex | IOU | 8.76 | 0.001 | 0 | 9.83 | 0.00135 | -0.014345 | 8.76 | 0.001 | 0 | 9.83 | 0.00135 | -0.014345 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.12 | 1.35 | -0.0016376 | 8760 | 1 | 8760 | 1 | 1.12 | 1.35 | -0.00164
ExitNoneSCEs_MiCExCZ05 | Com-Iltg-dWatt-Exit | SCE | s_MiC | Ex | CZ05 | 8.76 | 0.001 | 0 | 9.2 | 0.0013667 | -0.064567 | 8.76 | 0.001 | 0 | 9.2 | 0.0013667 | -0.064567 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.05 | 1.37 | -0.0073706 | 8760 | 1 | 8760 | 1 | 1.05 | 1.37 | -0.00737
ExitNoneSCEs_MiCExCZ06 | Com-Iltg-dWatt-Exit | SCE | s_MiC | Ex | CZ06 | 8.76 | 0.001 | 0 | 9.7767 | 0.0013567 | -0.031033 | 8.76 | 0.001 | 0 | 9.7767 | 0.0013567 | -0.031033 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.12 | 1.36 | -0.0035426 | 8760 | 1 | 8760 | 1 | 1.12 | 1.36 | -0.00354
ExitNoneSCEs_MiCExCZ08 | Com-Iltg-dWatt-Exit | SCE | s_MiC | Ex | CZ08 | 8.76 | 0.001 | 0 | 9.8467 | 0.0013433 | -0.0272 | 8.76 | 0.001 | 0 | 9.8467 | 0.0013433 | -0.0272 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.12 | 1.34 | -0.003105 | 8760 | 1 | 8760 | 1 | 1.12 | 1.34 | -0.00311
ExitNoneSCEs_MiCExCZ09 | Com-Iltg-dWatt-Exit | SCE | s_MiC | Ex | CZ09 | 8.76 | 0.001 | 0 | 9.7633 | 0.00136 | -0.0302 | 8.76 | 0.001 | 0 | 9.7633 | 0.00136 | -0.0302 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.11 | 1.36 | -0.0034475 | 8760 | 1 | 8760 | 1 | 1.11 | 1.36 | -0.00345
ExitNoneSCEs_MiCExCZ10 | Com-Iltg-dWatt-Exit | SCE | s_MiC | Ex | CZ10 | 8.76 | 0.001 | 0 | 9.6333 | 0.0013133 | -0.0326 | 8.76 | 0.001 | 0 | 9.6333 | 0.0013133 | -0.0326 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.1 | 1.31 | -0.0037215 | 8760 | 1 | 8760 | 1 | 1.1 | 1.31 | -0.00372
ExitNoneSCEs_MiCExCZ13 | Com-Iltg-dWatt-Exit | SCE | s_MiC | Ex | CZ13 | 8.76 | 0.001 | 0 | 9.49 | 0.0013467 | -0.054333 | 8.76 | 0.001 | 0 | 9.49 | 0.0013467 | -0.054333 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.08 | 1.35 | -0.0062024 | 8760 | 1 | 8760 | 1 | 1.08 | 1.35 | -0.0062
ExitNoneSCEs_MiCExCZ14 | Com-Iltg-dWatt-Exit | SCE | s_MiC | Ex | CZ14 | 8.76 | 0.001 | 0 | 9.4333 | 0.0013167 | -0.054533 | 8.76 | 0.001 | 0 | 9.4333 | 0.0013167 | -0.054533 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.08 | 1.32 | -0.0062253 | 8760 | 1 | 8760 | 1 | 1.08 | 1.32 | -0.00623
ExitNoneSCEs_MiCExCZ15 | Com-Iltg-dWatt-Exit | SCE | s_MiC | Ex | CZ15 | 8.76 | 0.001 | 0 | 10.3667 | 0.0013533 | -0.011727 | 8.76 | 0.001 | 0 | 10.3667 | 0.0013533 | -0.011727 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.18 | 1.35 | -0.0013387 | 8760 | 1 | 8760 | 1 | 1.18 | 1.35 | -0.00134
ExitNoneSCEs_MiCExCZ16 | Com-Iltg-dWatt-Exit | SCE | s_MiC | Ex | CZ16 | 8.76 | 0.001 | 0 | 8.6467 | 0.0012867 | -0.10177 | 8.76 | 0.001 | 0 | 8.6467 | 0.0012867 | -0.10177 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.987 | 1.29 | -0.011617 | 8760 | 1 | 8760 | 1 | 0.987 | 1.29 | -0.0116
ExitNoneSCEs_MiCExIOU | Com-Iltg-dWatt-Exit | SCE | s_MiC | Ex | IOU | 8.76 | 0.001 | 0 | 9.75 | 0.0013433 | -0.0322 | 8.76 | 0.001 | 0 | 9.75 | 0.0013433 | -0.0322 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.11 | 1.34 | -0.0036758 | 8760 | 1 | 8760 | 1 | 1.11 | 1.34 | -0.00368
ExitNoneSCEs_TCUExCZ05 | Com-Iltg-dWatt-Exit | SCE | s_TCU | Ex | CZ05 | 8.76 | 0.001 | 0 | 8.922 | 0.00135 | -0.05068 | 8.76 | 0.001 | 0 | 8.922 | 0.00135 | -0.05068 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.02 | 1.35 | -0.0057854 | 8760 | 1 | 8760 | 1 | 1.02 | 1.35 | -0.00579
ExitNoneSCEs_TCUExCZ06 | Com-Iltg-dWatt-Exit | SCE | s_TCU | Ex | CZ06 | 8.76 | 0.001 | 0 | 9.44 | 0.00132 | -0.0261 | 8.76 | 0.001 | 0 | 9.44 | 0.00132 | -0.0261 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.08 | 1.32 | -0.0029795 | 8760 | 1 | 8760 | 1 | 1.08 | 1.32 | -0.00298
ExitNoneSCEs_TCUExCZ08 | Com-Iltg-dWatt-Exit | SCE | s_TCU | Ex | CZ08 | 8.76 | 0.001 | 0 | 9.51 | 0.001328 | -0.02258 | 8.76 | 0.001 | 0 | 9.51 | 0.001328 | -0.02258 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.09 | 1.33 | -0.0025776 | 8760 | 1 | 8760 | 1 | 1.09 | 1.33 | -0.00258
ExitNoneSCEs_TCUExCZ09 | Com-Iltg-dWatt-Exit | SCE | s_TCU | Ex | CZ09 | 8.76 | 0.001 | 0 | 9.452 | 0.001342 | -0.02592 | 8.76 | 0.001 | 0 | 9.452 | 0.001342 | -0.02592 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.08 | 1.34 | -0.0029589 | 8760 | 1 | 8760 | 1 | 1.08 | 1.34 | -0.00296
ExitNoneSCEs_TCUExCZ10 | Com-Iltg-dWatt-Exit | SCE | s_TCU | Ex | CZ10 | 8.76 | 0.001 | 0 | 9.364 | 0.001338 | -0.02808 | 8.76 | 0.001 | 0 | 9.364 | 0.001338 | -0.02808 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.07 | 1.34 | -0.0032055 | 8760 | 1 | 8760 | 1 | 1.07 | 1.34 | -0.00321
ExitNoneSCEs_TCUExCZ13 | Com-Iltg-dWatt-Exit | SCE | s_TCU | Ex | CZ13 | 8.76 | 0.001 | 0 | 9.27 | 0.001306 | -0.04348 | 8.76 | 0.001 | 0 | 9.27 | 0.001306 | -0.04348 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.06 | 1.31 | -0.0049635 | 8760 | 1 | 8760 | 1 | 1.06 | 1.31 | -0.00496
ExitNoneSCEs_TCUExCZ14 | Com-Iltg-dWatt-Exit | SCE | s_TCU | Ex | CZ14 | 8.76 | 0.001 | 0 | 9.238 | 0.001312 | -0.04426 | 8.76 | 0.001 | 0 | 9.238 | 0.001312 | -0.04426 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.05 | 1.31 | -0.0050525 | 8760 | 1 | 8760 | 1 | 1.05 | 1.31 | -0.00505
ExitNoneSCEs_TCUExCZ15 | Com-Iltg-dWatt-Exit | SCE | s_TCU | Ex | CZ15 | 8.76 | 0.001 | 0 | 9.96 | 0.001296 | -0.011546 | 8.76 | 0.001 | 0 | 9.96 | 0.001296 | -0.011546 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.14 | 1.3 | -0.001318 | 8760 | 1 | 8760 | 1 | 1.14 | 1.3 | -0.00132
ExitNoneSCEs_TCUExCZ16 | Com-Iltg-dWatt-Exit | SCE | s_TCU | Ex | CZ16 | 8.76 | 0.001 | 0 | 8.57 | 0.00128 | -0.07706 | 8.76 | 0.001 | 0 | 8.57 | 0.00128 | -0.07706 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.978 | 1.28 | -0.0087968 | 8760 | 1 | 8760 | 1 | 0.978 | 1.28 | -0.0088
ExitNoneSCEs_TCUExIOU | Com-Iltg-dWatt-Exit | SCE | s_TCU | Ex | IOU | 8.76 | 0.001 | 0 | 9.448 | 0.001328 | -0.02648 | 8.76 | 0.001 | 0 | 9.448 | 0.001328 | -0.02648 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.08 | 1.33 | -0.0030228 | 8760 | 1 | 8760 | 1 | 1.08 | 1.33 | -0.00302
ExitNoneSCESCnExCZ05 | Com-Iltg-dWatt-Exit | SCE | SCn | Ex | CZ05 | 8.76 | 0.001 | 0 | 8.09 | 0.00144 | -0.092 | 8.76 | 0.001 | 0 | 8.09 | 0.00144 | -0.092 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.924 | 1.44 | -0.010502 | 8760 | 1 | 8760 | 1 | 0.924 | 1.44 | -0.0105
ExitNoneSCESCnExCZ06 | Com-Iltg-dWatt-Exit | SCE | SCn | Ex | CZ06 | 8.76 | 0.001 | 0 | 8.98 | 0.00146 | -0.0504 | 8.76 | 0.001 | 0 | 8.98 | 0.00146 | -0.0504 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.03 | 1.46 | -0.0057534 | 8760 | 1 | 8760 | 1 | 1.03 | 1.46 | -0.00575
ExitNoneSCESCnExCZ08 | Com-Iltg-dWatt-Exit | SCE | SCn | Ex | CZ08 | 8.76 | 0.001 | 0 | 9.07 | 0.00145 | -0.0414 | 8.76 | 0.001 | 0 | 9.07 | 0.00145 | -0.0414 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.04 | 1.45 | -0.004726 | 8760 | 1 | 8760 | 1 | 1.04 | 1.45 | -0.00473
ExitNoneSCESCnExCZ09 | Com-Iltg-dWatt-Exit | SCE | SCn | Ex | CZ09 | 8.76 | 0.001 | 0 | 9.03 | 0.00147 | -0.0462 | 8.76 | 0.001 | 0 | 9.03 | 0.00147 | -0.0462 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.03 | 1.47 | -0.005274 | 8760 | 1 | 8760 | 1 | 1.03 | 1.47 | -0.00527
ExitNoneSCESCnExCZ10 | Com-Iltg-dWatt-Exit | SCE | SCn | Ex | CZ10 | 8.76 | 0.001 | 0 | 9.05 | 0.00146 | -0.0521 | 8.76 | 0.001 | 0 | 9.05 | 0.00146 | -0.0521 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.03 | 1.46 | -0.0059475 | 8760 | 1 | 8760 | 1 | 1.03 | 1.46 | -0.00595
ExitNoneSCESCnExCZ13 | Com-Iltg-dWatt-Exit | SCE | SCn | Ex | CZ13 | 8.76 | 0.001 | 0 | 8.88 | 0.00142 | -0.0687 | 8.76 | 0.001 | 0 | 8.88 | 0.00142 | -0.0687 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.01 | 1.42 | -0.0078425 | 8760 | 1 | 8760 | 1 | 1.01 | 1.42 | -0.00784
ExitNoneSCESCnExCZ14 | Com-Iltg-dWatt-Exit | SCE | SCn | Ex | CZ14 | 8.76 | 0.001 | 0 | 8.75 | 0.00142 | -0.075 | 8.76 | 0.001 | 0 | 8.75 | 0.00142 | -0.075 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.999 | 1.42 | -0.0085616 | 8760 | 1 | 8760 | 1 | 0.999 | 1.42 | -0.00856
ExitNoneSCESCnExCZ15 | Com-Iltg-dWatt-Exit | SCE | SCn | Ex | CZ15 | 8.76 | 0.001 | 0 | 9.64 | 0.00143 | -0.0208 | 8.76 | 0.001 | 0 | 9.64 | 0.00143 | -0.0208 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.1 | 1.43 | -0.0023744 | 8760 | 1 | 8760 | 1 | 1.1 | 1.43 | -0.00237
ExitNoneSCESCnExCZ16 | Com-Iltg-dWatt-Exit | SCE | SCn | Ex | CZ16 | 8.76 | 0.001 | 0 | 7.9 | 0.00139 | -0.106 | 8.76 | 0.001 | 0 | 7.9 | 0.00139 | -0.106 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.902 | 1.39 | -0.0121 | 8760 | 1 | 8760 | 1 | 0.902 | 1.39 | -0.0121
ExitNoneSCESCnExIOU | Com-Iltg-dWatt-Exit | SCE | SCn | Ex | IOU | 8.76 | 0.001 | 0 | 9.04 | 0.00146 | -0.0476 | 8.76 | 0.001 | 0 | 9.04 | 0.00146 | -0.0476 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.03 | 1.46 | -0.0054338 | 8760 | 1 | 8760 | 1 | 1.03 | 1.46 | -0.00543
ExitNoneSCESCnNewCZ05 | Com-Iltg-dWatt-Exit | SCE | SCn | New | CZ05 | 8.76 | 0.001 | 0 | 8.09 | 0.00144 | -0.108 | 8.76 | 0.001 | 0 | 8.09 | 0.00144 | -0.108 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.924 | 1.44 | -0.012329 | 8760 | 1 | 8760 | 1 | 0.924 | 1.44 | -0.0123
ExitNoneSCESCnNewCZ06 | Com-Iltg-dWatt-Exit | SCE | SCn | New | CZ06 | 8.76 | 0.001 | 0 | 8.86 | 0.00135 | -0.0579 | 8.76 | 0.001 | 0 | 8.86 | 0.00135 | -0.0579 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.01 | 1.35 | -0.0066096 | 8760 | 1 | 8760 | 1 | 1.01 | 1.35 | -0.00661
ExitNoneSCESCnNewCZ08 | Com-Iltg-dWatt-Exit | SCE | SCn | New | CZ08 | 8.76 | 0.001 | 0 | 8.93 | 0.00134 | -0.0422 | 8.76 | 0.001 | 0 | 8.93 | 0.00134 | -0.0422 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.02 | 1.34 | -0.0048174 | 8760 | 1 | 8760 | 1 | 1.02 | 1.34 | -0.00482
ExitNoneSCESCnNewCZ09 | Com-Iltg-dWatt-Exit | SCE | SCn | New | CZ09 | 8.76 | 0.001 | 0 | 8.98 | 0.0014 | -0.0576 | 8.76 | 0.001 | 0 | 8.98 | 0.0014 | -0.0576 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.03 | 1.4 | -0.0065753 | 8760 | 1 | 8760 | 1 | 1.03 | 1.4 | -0.00658
ExitNoneSCESCnNewCZ10 | Com-Iltg-dWatt-Exit | SCE | SCn | New | CZ10 | 8.76 | 0.001 | 0 | 9.02 | 0.00139 | -0.0574 | 8.76 | 0.001 | 0 | 9.02 | 0.00139 | -0.0574 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.03 | 1.39 | -0.0065525 | 8760 | 1 | 8760 | 1 | 1.03 | 1.39 | -0.00655
ExitNoneSCESCnNewCZ13 | Com-Iltg-dWatt-Exit | SCE | SCn | New | CZ13 | 8.76 | 0.001 | 0 | 8.74 | 0.00136 | -0.0762 | 8.76 | 0.001 | 0 | 8.74 | 0.00136 | -0.0762 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.998 | 1.36 | -0.0086986 | 8760 | 1 | 8760 | 1 | 0.998 | 1.36 | -0.0087
ExitNoneSCESCnNewCZ14 | Com-Iltg-dWatt-Exit | SCE | SCn | New | CZ14 | 8.76 | 0.001 | 0 | 8.77 | 0.00137 | -0.0774 | 8.76 | 0.001 | 0 | 8.77 | 0.00137 | -0.0774 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1 | 1.37 | -0.0088356 | 8760 | 1 | 8760 | 1 | 1 | 1.37 | -0.00884
ExitNoneSCESCnNewCZ15 | Com-Iltg-dWatt-Exit | SCE | SCn | New | CZ15 | 8.76 | 0.001 | 0 | 9.39 | 0.00139 | -0.0183 | 8.76 | 0.001 | 0 | 9.39 | 0.00139 | -0.0183 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.07 | 1.39 | -0.002089 | 8760 | 1 | 8760 | 1 | 1.07 | 1.39 | -0.00209
ExitNoneSCESCnNewCZ16 | Com-Iltg-dWatt-Exit | SCE | SCn | New | CZ16 | 8.76 | 0.001 | 0 | 7.89 | 0.00133 | -0.107 | 8.76 | 0.001 | 0 | 7.89 | 0.00133 | -0.107 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.901 | 1.33 | -0.012215 | 8760 | 1 | 8760 | 1 | 0.901 | 1.33 | -0.0122
ExitNoneSCESCnNewIOU | Com-Iltg-dWatt-Exit | SCE | SCn | New | IOU | 8.76 | 0.001 | 0 | 8.97 | 0.00138 | -0.0553 | 8.76 | 0.001 | 0 | 8.97 | 0.00138 | -0.0553 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.02 | 1.38 | -0.0063128 | 8760 | 1 | 8760 | 1 | 1.02 | 1.38 | -0.00631
ExitNoneSCESUnExCZ05 | Com-Iltg-dWatt-Exit | SCE | SUn | Ex | CZ05 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1 | 1 | 0 | 8760 | 1 | 8760 | 1 | 1 | 1 | 0
ExitNoneSCESUnExCZ06 | Com-Iltg-dWatt-Exit | SCE | SUn | Ex | CZ06 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1 | 1 | 0 | 8760 | 1 | 8760 | 1 | 1 | 1 | 0
ExitNoneSCESUnExCZ08 | Com-Iltg-dWatt-Exit | SCE | SUn | Ex | CZ08 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1 | 1 | 0 | 8760 | 1 | 8760 | 1 | 1 | 1 | 0
ExitNoneSCESUnExCZ09 | Com-Iltg-dWatt-Exit | SCE | SUn | Ex | CZ09 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1 | 1 | 0 | 8760 | 1 | 8760 | 1 | 1 | 1 | 0
ExitNoneSCESUnExCZ10 | Com-Iltg-dWatt-Exit | SCE | SUn | Ex | CZ10 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1 | 1 | 0 | 8760 | 1 | 8760 | 1 | 1 | 1 | 0
ExitNoneSCESUnExCZ13 | Com-Iltg-dWatt-Exit | SCE | SUn | Ex | CZ13 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1 | 1 | 0 | 8760 | 1 | 8760 | 1 | 1 | 1 | 0
ExitNoneSCESUnExCZ14 | Com-Iltg-dWatt-Exit | SCE | SUn | Ex | CZ14 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1 | 1 | 0 | 8760 | 1 | 8760 | 1 | 1 | 1 | 0
ExitNoneSCESUnExCZ15 | Com-Iltg-dWatt-Exit | SCE | SUn | Ex | CZ15 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1 | 1 | 0 | 8760 | 1 | 8760 | 1 | 1 | 1 | 0
ExitNoneSCESUnExCZ16 | Com-Iltg-dWatt-Exit | SCE | SUn | Ex | CZ16 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1 | 1 | 0 | 8760 | 1 | 8760 | 1 | 1 | 1 | 0
ExitNoneSCESUnExIOU | Com-Iltg-dWatt-Exit | SCE | SUn | Ex | IOU | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1 | 1 | 0 | 8760 | 1 | 8760 | 1 | 1 | 1 | 0
ExitNoneSCESUnNewCZ05 | Com-Iltg-dWatt-Exit | SCE | SUn | New | CZ05 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1 | 1 | 0 | 8760 | 1 | 8760 | 1 | 1 | 1 | 0
ExitNoneSCESUnNewCZ06 | Com-Iltg-dWatt-Exit | SCE | SUn | New | CZ06 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1 | 1 | 0 | 8760 | 1 | 8760 | 1 | 1 | 1 | 0
ExitNoneSCESUnNewCZ08 | Com-Iltg-dWatt-Exit | SCE | SUn | New | CZ08 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1 | 1 | 0 | 8760 | 1 | 8760 | 1 | 1 | 1 | 0
ExitNoneSCESUnNewCZ09 | Com-Iltg-dWatt-Exit | SCE | SUn | New | CZ09 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1 | 1 | 0 | 8760 | 1 | 8760 | 1 | 1 | 1 | 0
ExitNoneSCESUnNewCZ10 | Com-Iltg-dWatt-Exit | SCE | SUn | New | CZ10 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1 | 1 | 0 | 8760 | 1 | 8760 | 1 | 1 | 1 | 0
ExitNoneSCESUnNewCZ13 | Com-Iltg-dWatt-Exit | SCE | SUn | New | CZ13 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1 | 1 | 0 | 8760 | 1 | 8760 | 1 | 1 | 1 | 0
ExitNoneSCESUnNewCZ14 | Com-Iltg-dWatt-Exit | SCE | SUn | New | CZ14 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1 | 1 | 0 | 8760 | 1 | 8760 | 1 | 1 | 1 | 0
ExitNoneSCESUnNewCZ15 | Com-Iltg-dWatt-Exit | SCE | SUn | New | CZ15 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1 | 1 | 0 | 8760 | 1 | 8760 | 1 | 1 | 1 | 0
ExitNoneSCESUnNewCZ16 | Com-Iltg-dWatt-Exit | SCE | SUn | New | CZ16 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1 | 1 | 0 | 8760 | 1 | 8760 | 1 | 1 | 1 | 0
ExitNoneSCESUnNewIOU | Com-Iltg-dWatt-Exit | SCE | SUn | New | IOU | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1 | 1 | 0 | 8760 | 1 | 8760 | 1 | 1 | 1 | 0
ExitNoneSCEWRfExCZ05 | Com-Iltg-dWatt-Exit | SCE | WRf | Ex | CZ05 | 8.76 | 0.001 | 0 | 12.3 | 0.00126 | 0 | 8.76 | 0.001 | 0 | 12.3 | 0.00126 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.4 | 1.26 | 0 | 8760 | 1 | 8760 | 1 | 1.4 | 1.26 | 0
ExitNoneSCEWRfExCZ06 | Com-Iltg-dWatt-Exit | SCE | WRf | Ex | CZ06 | 8.76 | 0.001 | 0 | 13.7 | 0.00125 | 0 | 8.76 | 0.001 | 0 | 13.7 | 0.00125 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.56 | 1.25 | 0 | 8760 | 1 | 8760 | 1 | 1.56 | 1.25 | 0
ExitNoneSCEWRfExCZ08 | Com-Iltg-dWatt-Exit | SCE | WRf | Ex | CZ08 | 8.76 | 0.001 | 0 | 13.4 | 0.00126 | 0 | 8.76 | 0.001 | 0 | 13.4 | 0.00126 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.53 | 1.26 | 0 | 8760 | 1 | 8760 | 1 | 1.53 | 1.26 | 0
ExitNoneSCEWRfExCZ09 | Com-Iltg-dWatt-Exit | SCE | WRf | Ex | CZ09 | 8.76 | 0.001 | 0 | 12.3 | 0.00129 | 0 | 8.76 | 0.001 | 0 | 12.3 | 0.00129 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.4 | 1.29 | 0 | 8760 | 1 | 8760 | 1 | 1.4 | 1.29 | 0
ExitNoneSCEWRfExCZ10 | Com-Iltg-dWatt-Exit | SCE | WRf | Ex | CZ10 | 8.76 | 0.001 | 0 | 14.2 | 0.00124 | 0 | 8.76 | 0.001 | 0 | 14.2 | 0.00124 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.62 | 1.24 | 0 | 8760 | 1 | 8760 | 1 | 1.62 | 1.24 | 0
ExitNoneSCEWRfExCZ13 | Com-Iltg-dWatt-Exit | SCE | WRf | Ex | CZ13 | 8.76 | 0.001 | 0 | 13.4 | 0.00127 | 0 | 8.76 | 0.001 | 0 | 13.4 | 0.00127 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.53 | 1.27 | 0 | 8760 | 1 | 8760 | 1 | 1.53 | 1.27 | 0
ExitNoneSCEWRfExCZ14 | Com-Iltg-dWatt-Exit | SCE | WRf | Ex | CZ14 | 8.76 | 0.001 | 0 | 12.6 | 0.00125 | 0 | 8.76 | 0.001 | 0 | 12.6 | 0.00125 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.44 | 1.25 | 0 | 8760 | 1 | 8760 | 1 | 1.44 | 1.25 | 0
ExitNoneSCEWRfExCZ15 | Com-Iltg-dWatt-Exit | SCE | WRf | Ex | CZ15 | 8.76 | 0.001 | 0 | 15.5 | 0.00126 | 0 | 8.76 | 0.001 | 0 | 15.5 | 0.00126 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.77 | 1.26 | 0 | 8760 | 1 | 8760 | 1 | 1.77 | 1.26 | 0
ExitNoneSCEWRfExCZ16 | Com-Iltg-dWatt-Exit | SCE | WRf | Ex | CZ16 | 8.76 | 0.001 | 0 | 12.4 | 0.00127 | -0.0031 | 8.76 | 0.001 | 0 | 12.4 | 0.00127 | -0.0031 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.42 | 1.27 | -0.00035388 | 8760 | 1 | 8760 | 1 | 1.42 | 1.27 | -0.000354
ExitNoneSCEWRfExIOU | Com-Iltg-dWatt-Exit | SCE | WRf | Ex | IOU | 8.76 | 0.001 | 0 | 13.5 | 0.00126 | -9.64e-06 | 8.76 | 0.001 | 0 | 13.5 | 0.00126 | -9.64e-06 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.54 | 1.26 | -1.1005e-06 | 8760 | 1 | 8760 | 1 | 1.54 | 1.26 | -1.1e-06
ExitNoneSCEWRfNewCZ05 | Com-Iltg-dWatt-Exit | SCE | WRf | New | CZ05 | 8.76 | 0.001 | 0 | 11.4 | 0.00118 | 0 | 8.76 | 0.001 | 0 | 11.4 | 0.00118 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.3 | 1.18 | 0 | 8760 | 1 | 8760 | 1 | 1.3 | 1.18 | 0
ExitNoneSCEWRfNewCZ06 | Com-Iltg-dWatt-Exit | SCE | WRf | New | CZ06 | 8.76 | 0.001 | 0 | 13.3 | 0.00126 | 0 | 8.76 | 0.001 | 0 | 13.3 | 0.00126 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.52 | 1.26 | 0 | 8760 | 1 | 8760 | 1 | 1.52 | 1.26 | 0
ExitNoneSCEWRfNewCZ08 | Com-Iltg-dWatt-Exit | SCE | WRf | New | CZ08 | 8.76 | 0.001 | 0 | 13.5 | 0.00126 | 0 | 8.76 | 0.001 | 0 | 13.5 | 0.00126 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.54 | 1.26 | 0 | 8760 | 1 | 8760 | 1 | 1.54 | 1.26 | 0
ExitNoneSCEWRfNewCZ09 | Com-Iltg-dWatt-Exit | SCE | WRf | New | CZ09 | 8.76 | 0.001 | 0 | 12.2 | 0.00128 | 0 | 8.76 | 0.001 | 0 | 12.2 | 0.00128 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.39 | 1.28 | 0 | 8760 | 1 | 8760 | 1 | 1.39 | 1.28 | 0
ExitNoneSCEWRfNewCZ10 | Com-Iltg-dWatt-Exit | SCE | WRf | New | CZ10 | 8.76 | 0.001 | 0 | 12.3 | 0.00122 | 0 | 8.76 | 0.001 | 0 | 12.3 | 0.00122 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.4 | 1.22 | 0 | 8760 | 1 | 8760 | 1 | 1.4 | 1.22 | 0
ExitNoneSCEWRfNewCZ13 | Com-Iltg-dWatt-Exit | SCE | WRf | New | CZ13 | 8.76 | 0.001 | 0 | 11.2 | 0.00127 | 0 | 8.76 | 0.001 | 0 | 11.2 | 0.00127 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.28 | 1.27 | 0 | 8760 | 1 | 8760 | 1 | 1.28 | 1.27 | 0
ExitNoneSCEWRfNewCZ14 | Com-Iltg-dWatt-Exit | SCE | WRf | New | CZ14 | 8.76 | 0.001 | 0 | 11.3 | 0.00124 | 0 | 8.76 | 0.001 | 0 | 11.3 | 0.00124 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.29 | 1.24 | 0 | 8760 | 1 | 8760 | 1 | 1.29 | 1.24 | 0
ExitNoneSCEWRfNewCZ15 | Com-Iltg-dWatt-Exit | SCE | WRf | New | CZ15 | 8.76 | 0.001 | 0 | 13.2 | 0.00127 | 0 | 8.76 | 0.001 | 0 | 13.2 | 0.00127 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.51 | 1.27 | 0 | 8760 | 1 | 8760 | 1 | 1.51 | 1.27 | 0
ExitNoneSCEWRfNewCZ16 | Com-Iltg-dWatt-Exit | SCE | WRf | New | CZ16 | 8.76 | 0.001 | 0 | 10.9 | 0.00121 | -0.0039 | 8.76 | 0.001 | 0 | 10.9 | 0.00121 | -0.0039 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.24 | 1.21 | -0.00044521 | 8760 | 1 | 8760 | 1 | 1.24 | 1.21 | -0.000445
ExitNoneSCEWRfNewIOU | Com-Iltg-dWatt-Exit | SCE | WRf | New | IOU | 8.76 | 0.001 | 0 | 12.5 | 0.00126 | -2.1e-05 | 8.76 | 0.001 | 0 | 12.5 | 0.00126 | -2.1e-05 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.43 | 1.26 | -2.3973e-06 | 8760 | 1 | 8760 | 1 | 1.43 | 1.26 | -2.4e-06
ExitNoneSDGAsmExCZ06 | Com-Iltg-dWatt-Exit | SDG | Asm | Ex | CZ06 | 8.76 | 0.001 | 0 | 9.58 | 0.00138 | -0.0597 | 8.76 | 0.001 | 0 | 9.58 | 0.00138 | -0.0597 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.09 | 1.38 | -0.0068151 | 8760 | 1 | 8760 | 1 | 1.09 | 1.38 | -0.00682
ExitNoneSDGAsmExCZ07 | Com-Iltg-dWatt-Exit | SDG | Asm | Ex | CZ07 | 8.76 | 0.001 | 0 | 9.63 | 0.00138 | -0.0577 | 8.76 | 0.001 | 0 | 9.63 | 0.00138 | -0.0577 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.1 | 1.38 | -0.0065868 | 8760 | 1 | 8760 | 1 | 1.1 | 1.38 | -0.00659
ExitNoneSDGAsmExCZ08 | Com-Iltg-dWatt-Exit | SDG | Asm | Ex | CZ08 | 8.76 | 0.001 | 0 | 9.66 | 0.00131 | -0.0482 | 8.76 | 0.001 | 0 | 9.66 | 0.00131 | -0.0482 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.1 | 1.31 | -0.0055023 | 8760 | 1 | 8760 | 1 | 1.1 | 1.31 | -0.0055
ExitNoneSDGAsmExCZ10 | Com-Iltg-dWatt-Exit | SDG | Asm | Ex | CZ10 | 8.76 | 0.001 | 0 | 9.54 | 0.00133 | -0.0593 | 8.76 | 0.001 | 0 | 9.54 | 0.00133 | -0.0593 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.09 | 1.33 | -0.0067694 | 8760 | 1 | 8760 | 1 | 1.09 | 1.33 | -0.00677
ExitNoneSDGAsmExCZ14 | Com-Iltg-dWatt-Exit | SDG | Asm | Ex | CZ14 | 8.76 | 0.001 | 0 | 9.3 | 0.00119 | -0.0902 | 8.76 | 0.001 | 0 | 9.3 | 0.00119 | -0.0902 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.06 | 1.19 | -0.010297 | 8760 | 1 | 8760 | 1 | 1.06 | 1.19 | -0.0103
ExitNoneSDGAsmExCZ15 | Com-Iltg-dWatt-Exit | SDG | Asm | Ex | CZ15 | 8.76 | 0.001 | 0 | 11.4 | 0.00128 | -0.0305 | 8.76 | 0.001 | 0 | 11.4 | 0.00128 | -0.0305 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.3 | 1.28 | -0.0034817 | 8760 | 1 | 8760 | 1 | 1.3 | 1.28 | -0.00348
ExitNoneSDGAsmExIOU | Com-Iltg-dWatt-Exit | SDG | Asm | Ex | IOU | 8.76 | 0.001 | 0 | 9.6 | 0.00136 | -0.0583 | 8.76 | 0.001 | 0 | 9.6 | 0.00136 | -0.0583 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.1 | 1.36 | -0.0066553 | 8760 | 1 | 8760 | 1 | 1.1 | 1.36 | -0.00666
ExitNoneSDGAsmNewCZ06 | Com-Iltg-dWatt-Exit | SDG | Asm | New | CZ06 | 8.76 | 0.001 | 0 | 9.41 | 0.00135 | -0.0731 | 8.76 | 0.001 | 0 | 9.41 | 0.00135 | -0.0731 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.07 | 1.35 | -0.0083447 | 8760 | 1 | 8760 | 1 | 1.07 | 1.35 | -0.00834
ExitNoneSDGAsmNewCZ07 | Com-Iltg-dWatt-Exit | SDG | Asm | New | CZ07 | 8.76 | 0.001 | 0 | 9.55 | 0.00137 | -0.0652 | 8.76 | 0.001 | 0 | 9.55 | 0.00137 | -0.0652 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.09 | 1.37 | -0.0074429 | 8760 | 1 | 8760 | 1 | 1.09 | 1.37 | -0.00744
ExitNoneSDGAsmNewCZ08 | Com-Iltg-dWatt-Exit | SDG | Asm | New | CZ08 | 8.76 | 0.001 | 0 | 9.57 | 0.00133 | -0.0682 | 8.76 | 0.001 | 0 | 9.57 | 0.00133 | -0.0682 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.09 | 1.33 | -0.0077854 | 8760 | 1 | 8760 | 1 | 1.09 | 1.33 | -0.00779
ExitNoneSDGAsmNewCZ10 | Com-Iltg-dWatt-Exit | SDG | Asm | New | CZ10 | 8.76 | 0.001 | 0 | 9.45 | 0.00136 | -0.0618 | 8.76 | 0.001 | 0 | 9.45 | 0.00136 | -0.0618 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.08 | 1.36 | -0.0070548 | 8760 | 1 | 8760 | 1 | 1.08 | 1.36 | -0.00705
ExitNoneSDGAsmNewCZ14 | Com-Iltg-dWatt-Exit | SDG | Asm | New | CZ14 | 8.76 | 0.001 | 0 | 9.23 | 0.00131 | -0.0964 | 8.76 | 0.001 | 0 | 9.23 | 0.00131 | -0.0964 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.05 | 1.31 | -0.011005 | 8760 | 1 | 8760 | 1 | 1.05 | 1.31 | -0.011
ExitNoneSDGAsmNewCZ15 | Com-Iltg-dWatt-Exit | SDG | Asm | New | CZ15 | 8.76 | 0.001 | 0 | 10.4 | 0.00137 | -0.0299 | 8.76 | 0.001 | 0 | 10.4 | 0.00137 | -0.0299 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.19 | 1.37 | -0.0034132 | 8760 | 1 | 8760 | 1 | 1.19 | 1.37 | -0.00341
ExitNoneSDGAsmNewIOU | Com-Iltg-dWatt-Exit | SDG | Asm | New | IOU | 8.76 | 0.001 | 0 | 9.51 | 0.00136 | -0.0646 | 8.76 | 0.001 | 0 | 9.51 | 0.00136 | -0.0646 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.09 | 1.36 | -0.0073744 | 8760 | 1 | 8760 | 1 | 1.09 | 1.36 | -0.00737
ExitNoneSDGComExCZ06 | Com-Iltg-dWatt-Exit | SDG | Com | Ex | CZ06 | 8.76 | 0.001 | 0 | 9.5598 | 0.0013138 | -0.041892 | 8.76 | 0.001 | 0 | 9.5598 | 0.0013138 | -0.041892 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.09 | 1.31 | -0.0047822 | 8760 | 1 | 8760 | 1 | 1.09 | 1.31 | -0.00478
ExitNoneSDGComExCZ07 | Com-Iltg-dWatt-Exit | SDG | Com | Ex | CZ07 | 8.76 | 0.001 | 0 | 9.702 | 0.0013132 | -0.029847 | 8.76 | 0.001 | 0 | 9.702 | 0.0013132 | -0.029847 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.11 | 1.31 | -0.0034072 | 8760 | 1 | 8760 | 1 | 1.11 | 1.31 | -0.00341
ExitNoneSDGComExCZ08 | Com-Iltg-dWatt-Exit | SDG | Com | Ex | CZ08 | 8.76 | 0.001 | 0 | 9.7432 | 0.0013428 | -0.035557 | 8.76 | 0.001 | 0 | 9.7432 | 0.0013428 | -0.035557 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.11 | 1.34 | -0.0040591 | 8760 | 1 | 8760 | 1 | 1.11 | 1.34 | -0.00406
ExitNoneSDGComExCZ10 | Com-Iltg-dWatt-Exit | SDG | Com | Ex | CZ10 | 8.76 | 0.001 | 0 | 9.6378 | 0.001349 | -0.038987 | 8.76 | 0.001 | 0 | 9.6378 | 0.001349 | -0.038987 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.1 | 1.35 | -0.0044505 | 8760 | 1 | 8760 | 1 | 1.1 | 1.35 | -0.00445
ExitNoneSDGComExCZ14 | Com-Iltg-dWatt-Exit | SDG | Com | Ex | CZ14 | 8.76 | 0.001 | 0 | 9.535 | 0.0013292 | -0.053775 | 8.76 | 0.001 | 0 | 9.535 | 0.0013292 | -0.053775 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.09 | 1.33 | -0.0061387 | 8760 | 1 | 8760 | 1 | 1.09 | 1.33 | -0.00614
ExitNoneSDGComExCZ15 | Com-Iltg-dWatt-Exit | SDG | Com | Ex | CZ15 | 8.76 | 0.001 | 0 | 10.4891 | 0.0013207 | -0.014739 | 8.76 | 0.001 | 0 | 10.4891 | 0.0013207 | -0.014739 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.2 | 1.32 | -0.0016825 | 8760 | 1 | 8760 | 1 | 1.2 | 1.32 | -0.00168
ExitNoneSDGComExIOU | Com-Iltg-dWatt-Exit | SDG | Com | Ex | IOU | 8.76 | 0.001 | 0 | 9.6905 | 0.0013234 | -0.032605 | 8.76 | 0.001 | 0 | 9.6905 | 0.0013234 | -0.032605 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.11 | 1.32 | -0.003722 | 8760 | 1 | 8760 | 1 | 1.11 | 1.32 | -0.00372
ExitNoneSDGComNewCZ06 | Com-Iltg-dWatt-Exit | SDG | Com | New | CZ06 | 8.76 | 0.001 | 0 | 9.4139 | 0.0013049 | -0.045759 | 8.76 | 0.001 | 0 | 9.4139 | 0.0013049 | -0.045759 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.07 | 1.3 | -0.0052236 | 8760 | 1 | 8760 | 1 | 1.07 | 1.3 | -0.00522
ExitNoneSDGComNewCZ07 | Com-Iltg-dWatt-Exit | SDG | Com | New | CZ07 | 8.76 | 0.001 | 0 | 9.4842 | 0.0013007 | -0.033785 | 8.76 | 0.001 | 0 | 9.4842 | 0.0013007 | -0.033785 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.08 | 1.3 | -0.0038567 | 8760 | 1 | 8760 | 1 | 1.08 | 1.3 | -0.00386
ExitNoneSDGComNewCZ08 | Com-Iltg-dWatt-Exit | SDG | Com | New | CZ08 | 8.76 | 0.001 | 0 | 9.5429 | 0.0013288 | -0.036139 | 8.76 | 0.001 | 0 | 9.5429 | 0.0013288 | -0.036139 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.09 | 1.33 | -0.0041255 | 8760 | 1 | 8760 | 1 | 1.09 | 1.33 | -0.00413
ExitNoneSDGComNewCZ10 | Com-Iltg-dWatt-Exit | SDG | Com | New | CZ10 | 8.76 | 0.001 | 0 | 9.5197 | 0.0013824 | -0.042381 | 8.76 | 0.001 | 0 | 9.5197 | 0.0013824 | -0.042381 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.09 | 1.38 | -0.0048381 | 8760 | 1 | 8760 | 1 | 1.09 | 1.38 | -0.00484
ExitNoneSDGComNewCZ14 | Com-Iltg-dWatt-Exit | SDG | Com | New | CZ14 | 8.76 | 0.001 | 0 | 9.3712 | 0.0013631 | -0.055899 | 8.76 | 0.001 | 0 | 9.3712 | 0.0013631 | -0.055899 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.07 | 1.36 | -0.0063811 | 8760 | 1 | 8760 | 1 | 1.07 | 1.36 | -0.00638
ExitNoneSDGComNewCZ15 | Com-Iltg-dWatt-Exit | SDG | Com | New | CZ15 | 8.76 | 0.001 | 0 | 10.2161 | 0.0013841 | -0.015071 | 8.76 | 0.001 | 0 | 10.2161 | 0.0013841 | -0.015071 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.17 | 1.38 | -0.0017205 | 8760 | 1 | 8760 | 1 | 1.17 | 1.38 | -0.00172
ExitNoneSDGComNewIOU | Com-Iltg-dWatt-Exit | SDG | Com | New | IOU | 8.76 | 0.001 | 0 | 9.4928 | 0.0013217 | -0.036246 | 8.76 | 0.001 | 0 | 9.4928 | 0.0013217 | -0.036246 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.08 | 1.32 | -0.0041377 | 8760 | 1 | 8760 | 1 | 1.08 | 1.32 | -0.00414
ExitNoneSDGECCExCZ06 | Com-Iltg-dWatt-Exit | SDG | ECC | Ex | CZ06 | 8.76 | 0.001 | 0 | 10.2 | 0.00144 | -0.0587 | 8.76 | 0.001 | 0 | 10.2 | 0.00144 | -0.0587 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.16 | 1.44 | -0.0067009 | 8760 | 1 | 8760 | 1 | 1.16 | 1.44 | -0.0067
ExitNoneSDGECCExCZ07 | Com-Iltg-dWatt-Exit | SDG | ECC | Ex | CZ07 | 8.76 | 0.001 | 0 | 10.4 | 0.00138 | -0.0419 | 8.76 | 0.001 | 0 | 10.4 | 0.00138 | -0.0419 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.19 | 1.38 | -0.0047831 | 8760 | 1 | 8760 | 1 | 1.19 | 1.38 | -0.00478
ExitNoneSDGECCExCZ08 | Com-Iltg-dWatt-Exit | SDG | ECC | Ex | CZ08 | 8.76 | 0.001 | 0 | 10.2 | 0.00143 | -0.0591 | 8.76 | 0.001 | 0 | 10.2 | 0.00143 | -0.0591 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.16 | 1.43 | -0.0067466 | 8760 | 1 | 8760 | 1 | 1.16 | 1.43 | -0.00675
ExitNoneSDGECCExCZ10 | Com-Iltg-dWatt-Exit | SDG | ECC | Ex | CZ10 | 8.76 | 0.001 | 0 | 9.93 | 0.00147 | -0.0591 | 8.76 | 0.001 | 0 | 9.93 | 0.00147 | -0.0591 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.13 | 1.47 | -0.0067466 | 8760 | 1 | 8760 | 1 | 1.13 | 1.47 | -0.00675
ExitNoneSDGECCExCZ14 | Com-Iltg-dWatt-Exit | SDG | ECC | Ex | CZ14 | 8.76 | 0.001 | 0 | 9.94 | 0.0014 | -0.0946 | 8.76 | 0.001 | 0 | 9.94 | 0.0014 | -0.0946 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.13 | 1.4 | -0.010799 | 8760 | 1 | 8760 | 1 | 1.13 | 1.4 | -0.0108
ExitNoneSDGECCExCZ15 | Com-Iltg-dWatt-Exit | SDG | ECC | Ex | CZ15 | 8.76 | 0.001 | 0 | 10.7 | 0.00139 | -0.0291 | 8.76 | 0.001 | 0 | 10.7 | 0.00139 | -0.0291 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.22 | 1.39 | -0.0033219 | 8760 | 1 | 8760 | 1 | 1.22 | 1.39 | -0.00332
ExitNoneSDGECCExIOU | Com-Iltg-dWatt-Exit | SDG | ECC | Ex | IOU | 8.76 | 0.001 | 0 | 10.3 | 0.0014 | -0.0464 | 8.76 | 0.001 | 0 | 10.3 | 0.0014 | -0.0464 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.18 | 1.4 | -0.0052968 | 8760 | 1 | 8760 | 1 | 1.18 | 1.4 | -0.0053
ExitNoneSDGECCNewCZ06 | Com-Iltg-dWatt-Exit | SDG | ECC | New | CZ06 | 8.76 | 0.001 | 0 | 9.53 | 0.00145 | -0.0955 | 8.76 | 0.001 | 0 | 9.53 | 0.00145 | -0.0955 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.09 | 1.45 | -0.010902 | 8760 | 1 | 8760 | 1 | 1.09 | 1.45 | -0.0109
ExitNoneSDGECCNewCZ07 | Com-Iltg-dWatt-Exit | SDG | ECC | New | CZ07 | 8.76 | 0.001 | 0 | 9.7 | 0.00145 | -0.0593 | 8.76 | 0.001 | 0 | 9.7 | 0.00145 | -0.0593 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.11 | 1.45 | -0.0067694 | 8760 | 1 | 8760 | 1 | 1.11 | 1.45 | -0.00677
ExitNoneSDGECCNewCZ08 | Com-Iltg-dWatt-Exit | SDG | ECC | New | CZ08 | 8.76 | 0.001 | 0 | 9.83 | 0.00143 | -0.0728 | 8.76 | 0.001 | 0 | 9.83 | 0.00143 | -0.0728 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.12 | 1.43 | -0.0083105 | 8760 | 1 | 8760 | 1 | 1.12 | 1.43 | -0.00831
ExitNoneSDGECCNewCZ10 | Com-Iltg-dWatt-Exit | SDG | ECC | New | CZ10 | 8.76 | 0.001 | 0 | 10 | 0.00151 | -0.0664 | 8.76 | 0.001 | 0 | 10 | 0.00151 | -0.0664 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.14 | 1.51 | -0.0075799 | 8760 | 1 | 8760 | 1 | 1.14 | 1.51 | -0.00758
ExitNoneSDGECCNewCZ14 | Com-Iltg-dWatt-Exit | SDG | ECC | New | CZ14 | 8.76 | 0.001 | 0 | 10.4 | 0.0014 | -0.0819 | 8.76 | 0.001 | 0 | 10.4 | 0.0014 | -0.0819 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.19 | 1.4 | -0.0093493 | 8760 | 1 | 8760 | 1 | 1.19 | 1.4 | -0.00935
ExitNoneSDGECCNewCZ15 | Com-Iltg-dWatt-Exit | SDG | ECC | New | CZ15 | 8.76 | 0.001 | 0 | 10.9 | 0.00147 | -0.0238 | 8.76 | 0.001 | 0 | 10.9 | 0.00147 | -0.0238 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.24 | 1.47 | -0.0027169 | 8760 | 1 | 8760 | 1 | 1.24 | 1.47 | -0.00272
ExitNoneSDGECCNewIOU | Com-Iltg-dWatt-Exit | SDG | ECC | New | IOU | 8.76 | 0.001 | 0 | 9.78 | 0.00146 | -0.0614 | 8.76 | 0.001 | 0 | 9.78 | 0.00146 | -0.0614 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.12 | 1.46 | -0.0070091 | 8760 | 1 | 8760 | 1 | 1.12 | 1.46 | -0.00701
ExitNoneSDGEPrExCZ06 | Com-Iltg-dWatt-Exit | SDG | EPr | Ex | CZ06 | 8.76 | 0.001 | 0 | 9.53 | 0.00142 | -0.0468 | 8.76 | 0.001 | 0 | 9.53 | 0.00142 | -0.0468 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.09 | 1.42 | -0.0053425 | 8760 | 1 | 8760 | 1 | 1.09 | 1.42 | -0.00534
ExitNoneSDGEPrExCZ07 | Com-Iltg-dWatt-Exit | SDG | EPr | Ex | CZ07 | 8.76 | 0.001 | 0 | 9.57 | 0.00144 | -0.0387 | 8.76 | 0.001 | 0 | 9.57 | 0.00144 | -0.0387 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.09 | 1.44 | -0.0044178 | 8760 | 1 | 8760 | 1 | 1.09 | 1.44 | -0.00442
ExitNoneSDGEPrExCZ08 | Com-Iltg-dWatt-Exit | SDG | EPr | Ex | CZ08 | 8.76 | 0.001 | 0 | 9.9 | 0.00144 | -0.0377 | 8.76 | 0.001 | 0 | 9.9 | 0.00144 | -0.0377 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.13 | 1.44 | -0.0043037 | 8760 | 1 | 8760 | 1 | 1.13 | 1.44 | -0.0043
ExitNoneSDGEPrExCZ10 | Com-Iltg-dWatt-Exit | SDG | EPr | Ex | CZ10 | 8.76 | 0.001 | 0 | 10 | 0.00142 | -0.0453 | 8.76 | 0.001 | 0 | 10 | 0.00142 | -0.0453 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.14 | 1.42 | -0.0051712 | 8760 | 1 | 8760 | 1 | 1.14 | 1.42 | -0.00517
ExitNoneSDGEPrExCZ14 | Com-Iltg-dWatt-Exit | SDG | EPr | Ex | CZ14 | 8.76 | 0.001 | 0 | 9.66 | 0.0014 | -0.0705 | 8.76 | 0.001 | 0 | 9.66 | 0.0014 | -0.0705 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.1 | 1.4 | -0.0080479 | 8760 | 1 | 8760 | 1 | 1.1 | 1.4 | -0.00805
ExitNoneSDGEPrExCZ15 | Com-Iltg-dWatt-Exit | SDG | EPr | Ex | CZ15 | 8.76 | 0.001 | 0 | 11.4 | 0.00138 | -0.0187 | 8.76 | 0.001 | 0 | 11.4 | 0.00138 | -0.0187 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.3 | 1.38 | -0.0021347 | 8760 | 1 | 8760 | 1 | 1.3 | 1.38 | -0.00213
ExitNoneSDGEPrExIOU | Com-Iltg-dWatt-Exit | SDG | EPr | Ex | IOU | 8.76 | 0.001 | 0 | 9.73 | 0.00143 | -0.0414 | 8.76 | 0.001 | 0 | 9.73 | 0.00143 | -0.0414 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.11 | 1.43 | -0.004726 | 8760 | 1 | 8760 | 1 | 1.11 | 1.43 | -0.00473
ExitNoneSDGEPrNewCZ06 | Com-Iltg-dWatt-Exit | SDG | EPr | New | CZ06 | 8.76 | 0.001 | 0 | 9.18 | 0.00146 | -0.0618 | 8.76 | 0.001 | 0 | 9.18 | 0.00146 | -0.0618 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.05 | 1.46 | -0.0070548 | 8760 | 1 | 8760 | 1 | 1.05 | 1.46 | -0.00705
ExitNoneSDGEPrNewCZ07 | Com-Iltg-dWatt-Exit | SDG | EPr | New | CZ07 | 8.76 | 0.001 | 0 | 9.2 | 0.00143 | -0.0514 | 8.76 | 0.001 | 0 | 9.2 | 0.00143 | -0.0514 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.05 | 1.43 | -0.0058676 | 8760 | 1 | 8760 | 1 | 1.05 | 1.43 | -0.00587
ExitNoneSDGEPrNewCZ08 | Com-Iltg-dWatt-Exit | SDG | EPr | New | CZ08 | 8.76 | 0.001 | 0 | 9.54 | 0.00148 | -0.0526 | 8.76 | 0.001 | 0 | 9.54 | 0.00148 | -0.0526 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.09 | 1.48 | -0.0060046 | 8760 | 1 | 8760 | 1 | 1.09 | 1.48 | -0.006
ExitNoneSDGEPrNewCZ10 | Com-Iltg-dWatt-Exit | SDG | EPr | New | CZ10 | 8.76 | 0.001 | 0 | 9.59 | 0.00153 | -0.062 | 8.76 | 0.001 | 0 | 9.59 | 0.00153 | -0.062 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.09 | 1.53 | -0.0070776 | 8760 | 1 | 8760 | 1 | 1.09 | 1.53 | -0.00708
ExitNoneSDGEPrNewCZ14 | Com-Iltg-dWatt-Exit | SDG | EPr | New | CZ14 | 8.76 | 0.001 | 0 | 9.51 | 0.00147 | -0.0929 | 8.76 | 0.001 | 0 | 9.51 | 0.00147 | -0.0929 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.09 | 1.47 | -0.010605 | 8760 | 1 | 8760 | 1 | 1.09 | 1.47 | -0.0106
ExitNoneSDGEPrNewCZ15 | Com-Iltg-dWatt-Exit | SDG | EPr | New | CZ15 | 8.76 | 0.001 | 0 | 10.7 | 0.00153 | -0.0269 | 8.76 | 0.001 | 0 | 10.7 | 0.00153 | -0.0269 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.22 | 1.53 | -0.0030708 | 8760 | 1 | 8760 | 1 | 1.22 | 1.53 | -0.00307
ExitNoneSDGEPrNewIOU | Com-Iltg-dWatt-Exit | SDG | EPr | New | IOU | 8.76 | 0.001 | 0 | 9.35 | 0.00147 | -0.0558 | 8.76 | 0.001 | 0 | 9.35 | 0.00147 | -0.0558 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.07 | 1.47 | -0.0063699 | 8760 | 1 | 8760 | 1 | 1.07 | 1.47 | -0.00637
ExitNoneSDGERCExCZ06 | Com-Iltg-dWatt-Exit | SDG | ERC | Ex | CZ06 | 8.76 | 0.001 | 0 | 8.66 | 0.00126 | -0.0787 | 8.76 | 0.001 | 0 | 8.66 | 0.00126 | -0.0787 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.989 | 1.26 | -0.008984 | 8760 | 1 | 8760 | 1 | 0.989 | 1.26 | -0.00898
ExitNoneSDGERCExCZ07 | Com-Iltg-dWatt-Exit | SDG | ERC | Ex | CZ07 | 8.76 | 0.001 | 0 | 8.6 | 0.00126 | -0.0593 | 8.76 | 0.001 | 0 | 8.6 | 0.00126 | -0.0593 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.982 | 1.26 | -0.0067694 | 8760 | 1 | 8760 | 1 | 0.982 | 1.26 | -0.00677
ExitNoneSDGERCExCZ08 | Com-Iltg-dWatt-Exit | SDG | ERC | Ex | CZ08 | 8.76 | 0.001 | 0 | 9.15 | 0.00128 | -0.0668 | 8.76 | 0.001 | 0 | 9.15 | 0.00128 | -0.0668 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.04 | 1.28 | -0.0076256 | 8760 | 1 | 8760 | 1 | 1.04 | 1.28 | -0.00763
ExitNoneSDGERCExCZ10 | Com-Iltg-dWatt-Exit | SDG | ERC | Ex | CZ10 | 8.76 | 0.001 | 0 | 9.15 | 0.00128 | -0.0714 | 8.76 | 0.001 | 0 | 9.15 | 0.00128 | -0.0714 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.04 | 1.28 | -0.0081507 | 8760 | 1 | 8760 | 1 | 1.04 | 1.28 | -0.00815
ExitNoneSDGERCExCZ14 | Com-Iltg-dWatt-Exit | SDG | ERC | Ex | CZ14 | 8.76 | 0.001 | 0 | 9.29 | 0.00129 | -0.0911 | 8.76 | 0.001 | 0 | 9.29 | 0.00129 | -0.0911 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.06 | 1.29 | -0.0104 | 8760 | 1 | 8760 | 1 | 1.06 | 1.29 | -0.0104
ExitNoneSDGERCExCZ15 | Com-Iltg-dWatt-Exit | SDG | ERC | Ex | CZ15 | 8.76 | 0.001 | 0 | 10.5 | 0.00131 | -0.0434 | 8.76 | 0.001 | 0 | 10.5 | 0.00131 | -0.0434 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.2 | 1.31 | -0.0049543 | 8760 | 1 | 8760 | 1 | 1.2 | 1.31 | -0.00495
ExitNoneSDGERCExIOU | Com-Iltg-dWatt-Exit | SDG | ERC | Ex | IOU | 8.76 | 0.001 | 0 | 8.82 | 0.00127 | -0.0648 | 8.76 | 0.001 | 0 | 8.82 | 0.00127 | -0.0648 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.01 | 1.27 | -0.0073973 | 8760 | 1 | 8760 | 1 | 1.01 | 1.27 | -0.0074
ExitNoneSDGERCNewCZ06 | Com-Iltg-dWatt-Exit | SDG | ERC | New | CZ06 | 8.76 | 0.001 | 0 | 9.08 | 0.00126 | -0.0759 | 8.76 | 0.001 | 0 | 9.08 | 0.00126 | -0.0759 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.04 | 1.26 | -0.0086644 | 8760 | 1 | 8760 | 1 | 1.04 | 1.26 | -0.00866
ExitNoneSDGERCNewCZ07 | Com-Iltg-dWatt-Exit | SDG | ERC | New | CZ07 | 8.76 | 0.001 | 0 | 9.05 | 0.00127 | -0.0553 | 8.76 | 0.001 | 0 | 9.05 | 0.00127 | -0.0553 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.03 | 1.27 | -0.0063128 | 8760 | 1 | 8760 | 1 | 1.03 | 1.27 | -0.00631
ExitNoneSDGERCNewCZ08 | Com-Iltg-dWatt-Exit | SDG | ERC | New | CZ08 | 8.76 | 0.001 | 0 | 9.19 | 0.00132 | -0.0604 | 8.76 | 0.001 | 0 | 9.19 | 0.00132 | -0.0604 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.05 | 1.32 | -0.006895 | 8760 | 1 | 8760 | 1 | 1.05 | 1.32 | -0.0069
ExitNoneSDGERCNewCZ10 | Com-Iltg-dWatt-Exit | SDG | ERC | New | CZ10 | 8.76 | 0.001 | 0 | 9.02 | 0.00138 | -0.0714 | 8.76 | 0.001 | 0 | 9.02 | 0.00138 | -0.0714 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.03 | 1.38 | -0.0081507 | 8760 | 1 | 8760 | 1 | 1.03 | 1.38 | -0.00815
ExitNoneSDGERCNewCZ14 | Com-Iltg-dWatt-Exit | SDG | ERC | New | CZ14 | 8.76 | 0.001 | 0 | 9.38 | 0.00136 | -0.0937 | 8.76 | 0.001 | 0 | 9.38 | 0.00136 | -0.0937 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.07 | 1.36 | -0.010696 | 8760 | 1 | 8760 | 1 | 1.07 | 1.36 | -0.0107
ExitNoneSDGERCNewCZ15 | Com-Iltg-dWatt-Exit | SDG | ERC | New | CZ15 | 8.76 | 0.001 | 0 | 10.2 | 0.00137 | -0.0314 | 8.76 | 0.001 | 0 | 10.2 | 0.00137 | -0.0314 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.16 | 1.37 | -0.0035845 | 8760 | 1 | 8760 | 1 | 1.16 | 1.37 | -0.00358
ExitNoneSDGERCNewIOU | Com-Iltg-dWatt-Exit | SDG | ERC | New | IOU | 8.76 | 0.001 | 0 | 9.06 | 0.00131 | -0.062 | 8.76 | 0.001 | 0 | 9.06 | 0.00131 | -0.062 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.03 | 1.31 | -0.0070776 | 8760 | 1 | 8760 | 1 | 1.03 | 1.31 | -0.00708
ExitNoneSDGESeExCZ06 | Com-Iltg-dWatt-Exit | SDG | ESe | Ex | CZ06 | 8.76 | 0.001 | 0 | 9.46 | 0.00141 | -0.0514 | 8.76 | 0.001 | 0 | 9.46 | 0.00141 | -0.0514 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.08 | 1.41 | -0.0058676 | 8760 | 1 | 8760 | 1 | 1.08 | 1.41 | -0.00587
ExitNoneSDGESeExCZ07 | Com-Iltg-dWatt-Exit | SDG | ESe | Ex | CZ07 | 8.76 | 0.001 | 0 | 9.57 | 0.00138 | -0.0421 | 8.76 | 0.001 | 0 | 9.57 | 0.00138 | -0.0421 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.09 | 1.38 | -0.0048059 | 8760 | 1 | 8760 | 1 | 1.09 | 1.38 | -0.00481
ExitNoneSDGESeExCZ08 | Com-Iltg-dWatt-Exit | SDG | ESe | Ex | CZ08 | 8.76 | 0.001 | 0 | 9.83 | 0.00141 | -0.0431 | 8.76 | 0.001 | 0 | 9.83 | 0.00141 | -0.0431 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.12 | 1.41 | -0.0049201 | 8760 | 1 | 8760 | 1 | 1.12 | 1.41 | -0.00492
ExitNoneSDGESeExCZ10 | Com-Iltg-dWatt-Exit | SDG | ESe | Ex | CZ10 | 8.76 | 0.001 | 0 | 10.1 | 0.00139 | -0.0507 | 8.76 | 0.001 | 0 | 10.1 | 0.00139 | -0.0507 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.15 | 1.39 | -0.0057877 | 8760 | 1 | 8760 | 1 | 1.15 | 1.39 | -0.00579
ExitNoneSDGESeExCZ14 | Com-Iltg-dWatt-Exit | SDG | ESe | Ex | CZ14 | 8.76 | 0.001 | 0 | 9.84 | 0.00131 | -0.0796 | 8.76 | 0.001 | 0 | 9.84 | 0.00131 | -0.0796 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.12 | 1.31 | -0.0090868 | 8760 | 1 | 8760 | 1 | 1.12 | 1.31 | -0.00909
ExitNoneSDGESeExCZ15 | Com-Iltg-dWatt-Exit | SDG | ESe | Ex | CZ15 | 8.76 | 0.001 | 0 | 11.2 | 0.00131 | -0.0239 | 8.76 | 0.001 | 0 | 11.2 | 0.00131 | -0.0239 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.28 | 1.31 | -0.0027283 | 8760 | 1 | 8760 | 1 | 1.28 | 1.31 | -0.00273
ExitNoneSDGESeExIOU | Com-Iltg-dWatt-Exit | SDG | ESe | Ex | IOU | 8.76 | 0.001 | 0 | 9.76 | 0.00139 | -0.0457 | 8.76 | 0.001 | 0 | 9.76 | 0.00139 | -0.0457 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.11 | 1.39 | -0.0052169 | 8760 | 1 | 8760 | 1 | 1.11 | 1.39 | -0.00522
ExitNoneSDGESeNewCZ06 | Com-Iltg-dWatt-Exit | SDG | ESe | New | CZ06 | 8.76 | 0.001 | 0 | 9.2 | 0.0014 | -0.0678 | 8.76 | 0.001 | 0 | 9.2 | 0.0014 | -0.0678 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.05 | 1.4 | -0.0077397 | 8760 | 1 | 8760 | 1 | 1.05 | 1.4 | -0.00774
ExitNoneSDGESeNewCZ07 | Com-Iltg-dWatt-Exit | SDG | ESe | New | CZ07 | 8.76 | 0.001 | 0 | 9.21 | 0.00136 | -0.0611 | 8.76 | 0.001 | 0 | 9.21 | 0.00136 | -0.0611 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.05 | 1.36 | -0.0069749 | 8760 | 1 | 8760 | 1 | 1.05 | 1.36 | -0.00697
ExitNoneSDGESeNewCZ08 | Com-Iltg-dWatt-Exit | SDG | ESe | New | CZ08 | 8.76 | 0.001 | 0 | 9.44 | 0.00146 | -0.0514 | 8.76 | 0.001 | 0 | 9.44 | 0.00146 | -0.0514 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.08 | 1.46 | -0.0058676 | 8760 | 1 | 8760 | 1 | 1.08 | 1.46 | -0.00587
ExitNoneSDGESeNewCZ10 | Com-Iltg-dWatt-Exit | SDG | ESe | New | CZ10 | 8.76 | 0.001 | 0 | 9.58 | 0.00152 | -0.0587 | 8.76 | 0.001 | 0 | 9.58 | 0.00152 | -0.0587 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.09 | 1.52 | -0.0067009 | 8760 | 1 | 8760 | 1 | 1.09 | 1.52 | -0.0067
ExitNoneSDGESeNewCZ14 | Com-Iltg-dWatt-Exit | SDG | ESe | New | CZ14 | 8.76 | 0.001 | 0 | 9.63 | 0.00147 | -0.0964 | 8.76 | 0.001 | 0 | 9.63 | 0.00147 | -0.0964 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.1 | 1.47 | -0.011005 | 8760 | 1 | 8760 | 1 | 1.1 | 1.47 | -0.011
ExitNoneSDGESeNewCZ15 | Com-Iltg-dWatt-Exit | SDG | ESe | New | CZ15 | 8.76 | 0.001 | 0 | 10.8 | 0.00138 | -0.0388 | 8.76 | 0.001 | 0 | 10.8 | 0.00138 | -0.0388 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.23 | 1.38 | -0.0044292 | 8760 | 1 | 8760 | 1 | 1.23 | 1.38 | -0.00443
ExitNoneSDGESeNewIOU | Com-Iltg-dWatt-Exit | SDG | ESe | New | IOU | 8.76 | 0.001 | 0 | 9.36 | 0.00142 | -0.0604 | 8.76 | 0.001 | 0 | 9.36 | 0.00142 | -0.0604 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.07 | 1.42 | -0.006895 | 8760 | 1 | 8760 | 1 | 1.07 | 1.42 | -0.0069
ExitNoneSDGEUnExCZ06 | Com-Iltg-dWatt-Exit | SDG | EUn | Ex | CZ06 | 8.76 | 0.001 | 0 | 10.1 | 0.00139 | -0.0449 | 8.76 | 0.001 | 0 | 10.1 | 0.00139 | -0.0449 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.15 | 1.39 | -0.0051256 | 8760 | 1 | 8760 | 1 | 1.15 | 1.39 | -0.00513
ExitNoneSDGEUnExCZ07 | Com-Iltg-dWatt-Exit | SDG | EUn | Ex | CZ07 | 8.76 | 0.001 | 0 | 10.1 | 0.00137 | -0.0395 | 8.76 | 0.001 | 0 | 10.1 | 0.00137 | -0.0395 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.15 | 1.37 | -0.0045091 | 8760 | 1 | 8760 | 1 | 1.15 | 1.37 | -0.00451
ExitNoneSDGEUnExCZ08 | Com-Iltg-dWatt-Exit | SDG | EUn | Ex | CZ08 | 8.76 | 0.001 | 0 | 10.2 | 0.0014 | -0.0479 | 8.76 | 0.001 | 0 | 10.2 | 0.0014 | -0.0479 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.16 | 1.4 | -0.005468 | 8760 | 1 | 8760 | 1 | 1.16 | 1.4 | -0.00547
ExitNoneSDGEUnExCZ10 | Com-Iltg-dWatt-Exit | SDG | EUn | Ex | CZ10 | 8.76 | 0.001 | 0 | 10.3 | 0.00144 | -0.0545 | 8.76 | 0.001 | 0 | 10.3 | 0.00144 | -0.0545 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.18 | 1.44 | -0.0062215 | 8760 | 1 | 8760 | 1 | 1.18 | 1.44 | -0.00622
ExitNoneSDGEUnExCZ14 | Com-Iltg-dWatt-Exit | SDG | EUn | Ex | CZ14 | 8.76 | 0.001 | 0 | 9.8 | 0.00139 | -0.0745 | 8.76 | 0.001 | 0 | 9.8 | 0.00139 | -0.0745 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.12 | 1.39 | -0.0085046 | 8760 | 1 | 8760 | 1 | 1.12 | 1.39 | -0.0085
ExitNoneSDGEUnExCZ15 | Com-Iltg-dWatt-Exit | SDG | EUn | Ex | CZ15 | 8.76 | 0.001 | 0 | 10.7 | 0.0014 | -0.0249 | 8.76 | 0.001 | 0 | 10.7 | 0.0014 | -0.0249 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.22 | 1.4 | -0.0028425 | 8760 | 1 | 8760 | 1 | 1.22 | 1.4 | -0.00284
ExitNoneSDGEUnExIOU | Com-Iltg-dWatt-Exit | SDG | EUn | Ex | IOU | 8.76 | 0.001 | 0 | 10.2 | 0.00139 | -0.0434 | 8.76 | 0.001 | 0 | 10.2 | 0.00139 | -0.0434 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.16 | 1.39 | -0.0049543 | 8760 | 1 | 8760 | 1 | 1.16 | 1.39 | -0.00495
ExitNoneSDGEUnNewCZ06 | Com-Iltg-dWatt-Exit | SDG | EUn | New | CZ06 | 8.76 | 0.001 | 0 | 9.96 | 0.00136 | -0.0652 | 8.76 | 0.001 | 0 | 9.96 | 0.00136 | -0.0652 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.14 | 1.36 | -0.0074429 | 8760 | 1 | 8760 | 1 | 1.14 | 1.36 | -0.00744
ExitNoneSDGEUnNewCZ07 | Com-Iltg-dWatt-Exit | SDG | EUn | New | CZ07 | 8.76 | 0.001 | 0 | 10.1 | 0.00136 | -0.0303 | 8.76 | 0.001 | 0 | 10.1 | 0.00136 | -0.0303 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.15 | 1.36 | -0.0034589 | 8760 | 1 | 8760 | 1 | 1.15 | 1.36 | -0.00346
ExitNoneSDGEUnNewCZ08 | Com-Iltg-dWatt-Exit | SDG | EUn | New | CZ08 | 8.76 | 0.001 | 0 | 10.1 | 0.00138 | -0.0312 | 8.76 | 0.001 | 0 | 10.1 | 0.00138 | -0.0312 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.15 | 1.38 | -0.0035616 | 8760 | 1 | 8760 | 1 | 1.15 | 1.38 | -0.00356
ExitNoneSDGEUnNewCZ10 | Com-Iltg-dWatt-Exit | SDG | EUn | New | CZ10 | 8.76 | 0.001 | 0 | 10.5 | 0.00145 | -0.0442 | 8.76 | 0.001 | 0 | 10.5 | 0.00145 | -0.0442 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.2 | 1.45 | -0.0050457 | 8760 | 1 | 8760 | 1 | 1.2 | 1.45 | -0.00505
ExitNoneSDGEUnNewCZ14 | Com-Iltg-dWatt-Exit | SDG | EUn | New | CZ14 | 8.76 | 0.001 | 0 | 10 | 0.00139 | -0.0665 | 8.76 | 0.001 | 0 | 10 | 0.00139 | -0.0665 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.14 | 1.39 | -0.0075913 | 8760 | 1 | 8760 | 1 | 1.14 | 1.39 | -0.00759
ExitNoneSDGEUnNewCZ15 | Com-Iltg-dWatt-Exit | SDG | EUn | New | CZ15 | 8.76 | 0.001 | 0 | 10.7 | 0.00144 | -0.0201 | 8.76 | 0.001 | 0 | 10.7 | 0.00144 | -0.0201 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.22 | 1.44 | -0.0022945 | 8760 | 1 | 8760 | 1 | 1.22 | 1.44 | -0.00229
ExitNoneSDGEUnNewIOU | Com-Iltg-dWatt-Exit | SDG | EUn | New | IOU | 8.76 | 0.001 | 0 | 10.2 | 0.00138 | -0.0339 | 8.76 | 0.001 | 0 | 10.2 | 0.00138 | -0.0339 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.16 | 1.38 | -0.0038699 | 8760 | 1 | 8760 | 1 | 1.16 | 1.38 | -0.00387
ExitNoneSDGGroExCZ06 | Com-Iltg-dWatt-Exit | SDG | Gro | Ex | CZ06 | 8.76 | 0.001 | 0 | 8.85 | 0.00125 | -0.124 | 8.76 | 0.001 | 0 | 8.85 | 0.00125 | -0.124 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.01 | 1.25 | -0.014155 | 8760 | 1 | 8760 | 1 | 1.01 | 1.25 | -0.0142
ExitNoneSDGGroExCZ07 | Com-Iltg-dWatt-Exit | SDG | Gro | Ex | CZ07 | 8.76 | 0.001 | 0 | 8.66 | 0.00128 | -0.124 | 8.76 | 0.001 | 0 | 8.66 | 0.00128 | -0.124 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.989 | 1.28 | -0.014155 | 8760 | 1 | 8760 | 1 | 0.989 | 1.28 | -0.0142
ExitNoneSDGGroExCZ08 | Com-Iltg-dWatt-Exit | SDG | Gro | Ex | CZ08 | 8.76 | 0.001 | 0 | 9.01 | 0.00133 | -0.102 | 8.76 | 0.001 | 0 | 9.01 | 0.00133 | -0.102 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.03 | 1.33 | -0.011644 | 8760 | 1 | 8760 | 1 | 1.03 | 1.33 | -0.0116
ExitNoneSDGGroExCZ10 | Com-Iltg-dWatt-Exit | SDG | Gro | Ex | CZ10 | 8.76 | 0.001 | 0 | 9.2 | 0.00133 | -0.105 | 8.76 | 0.001 | 0 | 9.2 | 0.00133 | -0.105 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.05 | 1.33 | -0.011986 | 8760 | 1 | 8760 | 1 | 1.05 | 1.33 | -0.012
ExitNoneSDGGroExCZ14 | Com-Iltg-dWatt-Exit | SDG | Gro | Ex | CZ14 | 8.76 | 0.001 | 0 | 9.15 | 0.00152 | -0.102 | 8.76 | 0.001 | 0 | 9.15 | 0.00152 | -0.102 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.04 | 1.52 | -0.011644 | 8760 | 1 | 8760 | 1 | 1.04 | 1.52 | -0.0116
ExitNoneSDGGroExCZ15 | Com-Iltg-dWatt-Exit | SDG | Gro | Ex | CZ15 | 8.76 | 0.001 | 0 | 9.89 | 0.00133 | -0.0618 | 8.76 | 0.001 | 0 | 9.89 | 0.00133 | -0.0618 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.13 | 1.33 | -0.0070548 | 8760 | 1 | 8760 | 1 | 1.13 | 1.33 | -0.00705
ExitNoneSDGGroExIOU | Com-Iltg-dWatt-Exit | SDG | Gro | Ex | IOU | 8.76 | 0.001 | 0 | 8.83 | 0.00129 | -0.118 | 8.76 | 0.001 | 0 | 8.83 | 0.00129 | -0.118 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.01 | 1.29 | -0.01347 | 8760 | 1 | 8760 | 1 | 1.01 | 1.29 | -0.0135
ExitNoneSDGGroNewCZ06 | Com-Iltg-dWatt-Exit | SDG | Gro | New | CZ06 | 8.76 | 0.001 | 0 | 9.15 | 0.00129 | -0.114 | 8.76 | 0.001 | 0 | 9.15 | 0.00129 | -0.114 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.04 | 1.29 | -0.013014 | 8760 | 1 | 8760 | 1 | 1.04 | 1.29 | -0.013
ExitNoneSDGGroNewCZ07 | Com-Iltg-dWatt-Exit | SDG | Gro | New | CZ07 | 8.76 | 0.001 | 0 | 9.01 | 0.00131 | -0.106 | 8.76 | 0.001 | 0 | 9.01 | 0.00131 | -0.106 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.03 | 1.31 | -0.0121 | 8760 | 1 | 8760 | 1 | 1.03 | 1.31 | -0.0121
ExitNoneSDGGroNewCZ08 | Com-Iltg-dWatt-Exit | SDG | Gro | New | CZ08 | 8.76 | 0.001 | 0 | 9.3 | 0.0013 | -0.0894 | 8.76 | 0.001 | 0 | 9.3 | 0.0013 | -0.0894 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.06 | 1.3 | -0.010205 | 8760 | 1 | 8760 | 1 | 1.06 | 1.3 | -0.0102
ExitNoneSDGGroNewCZ10 | Com-Iltg-dWatt-Exit | SDG | Gro | New | CZ10 | 8.76 | 0.001 | 0 | 9.42 | 0.0014 | -0.0937 | 8.76 | 0.001 | 0 | 9.42 | 0.0014 | -0.0937 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.08 | 1.4 | -0.010696 | 8760 | 1 | 8760 | 1 | 1.08 | 1.4 | -0.0107
ExitNoneSDGGroNewCZ14 | Com-Iltg-dWatt-Exit | SDG | Gro | New | CZ14 | 8.76 | 0.001 | 0 | 9.36 | 0.00141 | -0.103 | 8.76 | 0.001 | 0 | 9.36 | 0.00141 | -0.103 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.07 | 1.41 | -0.011758 | 8760 | 1 | 8760 | 1 | 1.07 | 1.41 | -0.0118
ExitNoneSDGGroNewCZ15 | Com-Iltg-dWatt-Exit | SDG | Gro | New | CZ15 | 8.76 | 0.001 | 0 | 10.2 | 0.0014 | -0.0497 | 8.76 | 0.001 | 0 | 10.2 | 0.0014 | -0.0497 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.16 | 1.4 | -0.0056735 | 8760 | 1 | 8760 | 1 | 1.16 | 1.4 | -0.00567
ExitNoneSDGGroNewIOU | Com-Iltg-dWatt-Exit | SDG | Gro | New | IOU | 8.76 | 0.001 | 0 | 9.14 | 0.00134 | -0.102 | 8.76 | 0.001 | 0 | 9.14 | 0.00134 | -0.102 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.04 | 1.34 | -0.011644 | 8760 | 1 | 8760 | 1 | 1.04 | 1.34 | -0.0116
ExitNoneSDGHspExCZ06 | Com-Iltg-dWatt-Exit | SDG | Hsp | Ex | CZ06 | 8.76 | 0.001 | 0 | 9.96 | 0.00126 | -0.0635 | 8.76 | 0.001 | 0 | 9.96 | 0.00126 | -0.0635 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.14 | 1.26 | -0.0072489 | 8760 | 1 | 8760 | 1 | 1.14 | 1.26 | -0.00725
ExitNoneSDGHspExCZ07 | Com-Iltg-dWatt-Exit | SDG | Hsp | Ex | CZ07 | 8.76 | 0.001 | 0 | 10 | 0.00126 | -0.0572 | 8.76 | 0.001 | 0 | 10 | 0.00126 | -0.0572 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.14 | 1.26 | -0.0065297 | 8760 | 1 | 8760 | 1 | 1.14 | 1.26 | -0.00653
ExitNoneSDGHspExCZ08 | Com-Iltg-dWatt-Exit | SDG | Hsp | Ex | CZ08 | 8.76 | 0.001 | 0 | 10.1 | 0.00127 | -0.0611 | 8.76 | 0.001 | 0 | 10.1 | 0.00127 | -0.0611 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.15 | 1.27 | -0.0069749 | 8760 | 1 | 8760 | 1 | 1.15 | 1.27 | -0.00697
ExitNoneSDGHspExCZ10 | Com-Iltg-dWatt-Exit | SDG | Hsp | Ex | CZ10 | 8.76 | 0.001 | 0 | 10.1 | 0.0013 | -0.0661 | 8.76 | 0.001 | 0 | 10.1 | 0.0013 | -0.0661 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.15 | 1.3 | -0.0075457 | 8760 | 1 | 8760 | 1 | 1.15 | 1.3 | -0.00755
ExitNoneSDGHspExCZ14 | Com-Iltg-dWatt-Exit | SDG | Hsp | Ex | CZ14 | 8.76 | 0.001 | 0 | 9.76 | 0.00129 | -0.08 | 8.76 | 0.001 | 0 | 9.76 | 0.00129 | -0.08 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.11 | 1.29 | -0.0091324 | 8760 | 1 | 8760 | 1 | 1.11 | 1.29 | -0.00913
ExitNoneSDGHspExCZ15 | Com-Iltg-dWatt-Exit | SDG | Hsp | Ex | CZ15 | 8.76 | 0.001 | 0 | 10.2 | 0.00128 | -0.0514 | 8.76 | 0.001 | 0 | 10.2 | 0.00128 | -0.0514 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.16 | 1.28 | -0.0058676 | 8760 | 1 | 8760 | 1 | 1.16 | 1.28 | -0.00587
ExitNoneSDGHspExIOU | Com-Iltg-dWatt-Exit | SDG | Hsp | Ex | IOU | 8.76 | 0.001 | 0 | 10 | 0.00126 | -0.0588 | 8.76 | 0.001 | 0 | 10 | 0.00126 | -0.0588 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.14 | 1.26 | -0.0067123 | 8760 | 1 | 8760 | 1 | 1.14 | 1.26 | -0.00671
ExitNoneSDGHspNewCZ06 | Com-Iltg-dWatt-Exit | SDG | Hsp | New | CZ06 | 8.76 | 0.001 | 0 | 9.53 | 0.00122 | -0.0682 | 8.76 | 0.001 | 0 | 9.53 | 0.00122 | -0.0682 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.09 | 1.22 | -0.0077854 | 8760 | 1 | 8760 | 1 | 1.09 | 1.22 | -0.00779
ExitNoneSDGHspNewCZ07 | Com-Iltg-dWatt-Exit | SDG | Hsp | New | CZ07 | 8.76 | 0.001 | 0 | 9.54 | 0.00121 | -0.0578 | 8.76 | 0.001 | 0 | 9.54 | 0.00121 | -0.0578 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.09 | 1.21 | -0.0065982 | 8760 | 1 | 8760 | 1 | 1.09 | 1.21 | -0.0066
ExitNoneSDGHspNewCZ08 | Com-Iltg-dWatt-Exit | SDG | Hsp | New | CZ08 | 8.76 | 0.001 | 0 | 9.58 | 0.00122 | -0.0638 | 8.76 | 0.001 | 0 | 9.58 | 0.00122 | -0.0638 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.09 | 1.22 | -0.0072831 | 8760 | 1 | 8760 | 1 | 1.09 | 1.22 | -0.00728
ExitNoneSDGHspNewCZ10 | Com-Iltg-dWatt-Exit | SDG | Hsp | New | CZ10 | 8.76 | 0.001 | 0 | 9.43 | 0.0013 | -0.0708 | 8.76 | 0.001 | 0 | 9.43 | 0.0013 | -0.0708 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.08 | 1.3 | -0.0080822 | 8760 | 1 | 8760 | 1 | 1.08 | 1.3 | -0.00808
ExitNoneSDGHspNewCZ14 | Com-Iltg-dWatt-Exit | SDG | Hsp | New | CZ14 | 8.76 | 0.001 | 0 | 9.53 | 0.00125 | -0.0858 | 8.76 | 0.001 | 0 | 9.53 | 0.00125 | -0.0858 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.09 | 1.25 | -0.0097945 | 8760 | 1 | 8760 | 1 | 1.09 | 1.25 | -0.00979
ExitNoneSDGHspNewCZ15 | Com-Iltg-dWatt-Exit | SDG | Hsp | New | CZ15 | 8.76 | 0.001 | 0 | 10.1 | 0.00128 | -0.0553 | 8.76 | 0.001 | 0 | 10.1 | 0.00128 | -0.0553 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.15 | 1.28 | -0.0063128 | 8760 | 1 | 8760 | 1 | 1.15 | 1.28 | -0.00631
ExitNoneSDGHspNewIOU | Com-Iltg-dWatt-Exit | SDG | Hsp | New | IOU | 8.76 | 0.001 | 0 | 9.52 | 0.00123 | -0.0602 | 8.76 | 0.001 | 0 | 9.52 | 0.00123 | -0.0602 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.09 | 1.23 | -0.0068721 | 8760 | 1 | 8760 | 1 | 1.09 | 1.23 | -0.00687
ExitNoneSDGHtlExCZ06 | Com-Iltg-dWatt-Exit | SDG | Htl | Ex | CZ06 | 8.76 | 0.001 | 0 | 9.31 | 0.00126 | -0.0306 | 8.76 | 0.001 | 0 | 9.31 | 0.00126 | -0.0306 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.06 | 1.26 | -0.0034932 | 8760 | 1 | 8760 | 1 | 1.06 | 1.26 | -0.00349
ExitNoneSDGHtlExCZ07 | Com-Iltg-dWatt-Exit | SDG | Htl | Ex | CZ07 | 8.76 | 0.001 | 0 | 9.44 | 0.00125 | -0.024 | 8.76 | 0.001 | 0 | 9.44 | 0.00125 | -0.024 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.08 | 1.25 | -0.0027397 | 8760 | 1 | 8760 | 1 | 1.08 | 1.25 | -0.00274
ExitNoneSDGHtlExCZ08 | Com-Iltg-dWatt-Exit | SDG | Htl | Ex | CZ08 | 8.76 | 0.001 | 0 | 9.4 | 0.00127 | -0.0283 | 8.76 | 0.001 | 0 | 9.4 | 0.00127 | -0.0283 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.07 | 1.27 | -0.0032306 | 8760 | 1 | 8760 | 1 | 1.07 | 1.27 | -0.00323
ExitNoneSDGHtlExCZ10 | Com-Iltg-dWatt-Exit | SDG | Htl | Ex | CZ10 | 8.76 | 0.001 | 0 | 9.35 | 0.00129 | -0.029 | 8.76 | 0.001 | 0 | 9.35 | 0.00129 | -0.029 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.07 | 1.29 | -0.0033105 | 8760 | 1 | 8760 | 1 | 1.07 | 1.29 | -0.00331
ExitNoneSDGHtlExCZ14 | Com-Iltg-dWatt-Exit | SDG | Htl | Ex | CZ14 | 8.76 | 0.001 | 0 | 9.17 | 0.0013 | -0.0383 | 8.76 | 0.001 | 0 | 9.17 | 0.0013 | -0.0383 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.05 | 1.3 | -0.0043721 | 8760 | 1 | 8760 | 1 | 1.05 | 1.3 | -0.00437
ExitNoneSDGHtlExCZ15 | Com-Iltg-dWatt-Exit | SDG | Htl | Ex | CZ15 | 8.76 | 0.001 | 0 | 10.1 | 0.00129 | -0.0166 | 8.76 | 0.001 | 0 | 10.1 | 0.00129 | -0.0166 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.15 | 1.29 | -0.001895 | 8760 | 1 | 8760 | 1 | 1.15 | 1.29 | -0.0019
ExitNoneSDGHtlExIOU | Com-Iltg-dWatt-Exit | SDG | Htl | Ex | IOU | 8.76 | 0.001 | 0 | 9.43 | 0.00125 | -0.0248 | 8.76 | 0.001 | 0 | 9.43 | 0.00125 | -0.0248 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.08 | 1.25 | -0.0028311 | 8760 | 1 | 8760 | 1 | 1.08 | 1.25 | -0.00283
ExitNoneSDGHtlNewCZ06 | Com-Iltg-dWatt-Exit | SDG | Htl | New | CZ06 | 8.76 | 0.001 | 0 | 9.21 | 0.00129 | -0.0321 | 8.76 | 0.001 | 0 | 9.21 | 0.00129 | -0.0321 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.05 | 1.29 | -0.0036644 | 8760 | 1 | 8760 | 1 | 1.05 | 1.29 | -0.00366
ExitNoneSDGHtlNewCZ07 | Com-Iltg-dWatt-Exit | SDG | Htl | New | CZ07 | 8.76 | 0.001 | 0 | 9.26 | 0.00127 | -0.0362 | 8.76 | 0.001 | 0 | 9.26 | 0.00127 | -0.0362 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.06 | 1.27 | -0.0041324 | 8760 | 1 | 8760 | 1 | 1.06 | 1.27 | -0.00413
ExitNoneSDGHtlNewCZ08 | Com-Iltg-dWatt-Exit | SDG | Htl | New | CZ08 | 8.76 | 0.001 | 0 | 9.34 | 0.0013 | -0.0302 | 8.76 | 0.001 | 0 | 9.34 | 0.0013 | -0.0302 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.07 | 1.3 | -0.0034475 | 8760 | 1 | 8760 | 1 | 1.07 | 1.3 | -0.00345
ExitNoneSDGHtlNewCZ10 | Com-Iltg-dWatt-Exit | SDG | Htl | New | CZ10 | 8.76 | 0.001 | 0 | 9.28 | 0.00134 | -0.0293 | 8.76 | 0.001 | 0 | 9.28 | 0.00134 | -0.0293 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.06 | 1.34 | -0.0033447 | 8760 | 1 | 8760 | 1 | 1.06 | 1.34 | -0.00334
ExitNoneSDGHtlNewCZ14 | Com-Iltg-dWatt-Exit | SDG | Htl | New | CZ14 | 8.76 | 0.001 | 0 | 8.97 | 0.00134 | -0.0479 | 8.76 | 0.001 | 0 | 8.97 | 0.00134 | -0.0479 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.02 | 1.34 | -0.005468 | 8760 | 1 | 8760 | 1 | 1.02 | 1.34 | -0.00547
ExitNoneSDGHtlNewCZ15 | Com-Iltg-dWatt-Exit | SDG | Htl | New | CZ15 | 8.76 | 0.001 | 0 | 10.1 | 0.00136 | -0.0149 | 8.76 | 0.001 | 0 | 10.1 | 0.00136 | -0.0149 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.15 | 1.36 | -0.0017009 | 8760 | 1 | 8760 | 1 | 1.15 | 1.36 | -0.0017
ExitNoneSDGHtlNewIOU | Com-Iltg-dWatt-Exit | SDG | Htl | New | IOU | 8.76 | 0.001 | 0 | 9.27 | 0.00128 | -0.0351 | 8.76 | 0.001 | 0 | 9.27 | 0.00128 | -0.0351 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.06 | 1.28 | -0.0040068 | 8760 | 1 | 8760 | 1 | 1.06 | 1.28 | -0.00401
ExitNoneSDGMBTExCZ06 | Com-Iltg-dWatt-Exit | SDG | MBT | Ex | CZ06 | 8.76 | 0.001 | 0 | 10.2 | 0.00127 | -0.00363 | 8.76 | 0.001 | 0 | 10.2 | 0.00127 | -0.00363 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.16 | 1.27 | -0.00041438 | 8760 | 1 | 8760 | 1 | 1.16 | 1.27 | -0.000414
ExitNoneSDGMBTExCZ07 | Com-Iltg-dWatt-Exit | SDG | MBT | Ex | CZ07 | 8.76 | 0.001 | 0 | 10.2 | 0.00125 | -0.00248 | 8.76 | 0.001 | 0 | 10.2 | 0.00125 | -0.00248 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.16 | 1.25 | -0.00028311 | 8760 | 1 | 8760 | 1 | 1.16 | 1.25 | -0.000283
ExitNoneSDGMBTExCZ08 | Com-Iltg-dWatt-Exit | SDG | MBT | Ex | CZ08 | 8.76 | 0.001 | 0 | 10.2 | 0.00139 | -0.00232 | 8.76 | 0.001 | 0 | 10.2 | 0.00139 | -0.00232 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.16 | 1.39 | -0.00026484 | 8760 | 1 | 8760 | 1 | 1.16 | 1.39 | -0.000265
ExitNoneSDGMBTExCZ10 | Com-Iltg-dWatt-Exit | SDG | MBT | Ex | CZ10 | 8.76 | 0.001 | 0 | 10.1 | 0.00143 | -0.0047 | 8.76 | 0.001 | 0 | 10.1 | 0.00143 | -0.0047 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.15 | 1.43 | -0.00053653 | 8760 | 1 | 8760 | 1 | 1.15 | 1.43 | -0.000537
ExitNoneSDGMBTExCZ14 | Com-Iltg-dWatt-Exit | SDG | MBT | Ex | CZ14 | 8.76 | 0.001 | 0 | 10 | 0.0014 | -0.0107 | 8.76 | 0.001 | 0 | 10 | 0.0014 | -0.0107 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.14 | 1.4 | -0.0012215 | 8760 | 1 | 8760 | 1 | 1.14 | 1.4 | -0.00122
ExitNoneSDGMBTExCZ15 | Com-Iltg-dWatt-Exit | SDG | MBT | Ex | CZ15 | 8.76 | 0.001 | 0 | 10.9 | 0.00144 | -0.000479 | 8.76 | 0.001 | 0 | 10.9 | 0.00144 | -0.000479 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.24 | 1.44 | -5.468e-05 | 8760 | 1 | 8760 | 1 | 1.24 | 1.44 | -5.47e-05
ExitNoneSDGMBTExIOU | Com-Iltg-dWatt-Exit | SDG | MBT | Ex | IOU | 8.76 | 0.001 | 0 | 10.2 | 0.00131 | -0.00326 | 8.76 | 0.001 | 0 | 10.2 | 0.00131 | -0.00326 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.16 | 1.31 | -0.00037215 | 8760 | 1 | 8760 | 1 | 1.16 | 1.31 | -0.000372
ExitNoneSDGMBTNewCZ06 | Com-Iltg-dWatt-Exit | SDG | MBT | New | CZ06 | 8.76 | 0.001 | 0 | 9.84 | 0.00135 | -0.00555 | 8.76 | 0.001 | 0 | 9.84 | 0.00135 | -0.00555 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.12 | 1.35 | -0.00063356 | 8760 | 1 | 8760 | 1 | 1.12 | 1.35 | -0.000634
ExitNoneSDGMBTNewCZ07 | Com-Iltg-dWatt-Exit | SDG | MBT | New | CZ07 | 8.76 | 0.001 | 0 | 9.88 | 0.00133 | -0.00307 | 8.76 | 0.001 | 0 | 9.88 | 0.00133 | -0.00307 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.13 | 1.33 | -0.00035046 | 8760 | 1 | 8760 | 1 | 1.13 | 1.33 | -0.00035
ExitNoneSDGMBTNewCZ08 | Com-Iltg-dWatt-Exit | SDG | MBT | New | CZ08 | 8.76 | 0.001 | 0 | 9.85 | 0.00141 | -0.004 | 8.76 | 0.001 | 0 | 9.85 | 0.00141 | -0.004 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.12 | 1.41 | -0.00045662 | 8760 | 1 | 8760 | 1 | 1.12 | 1.41 | -0.000457
ExitNoneSDGMBTNewCZ10 | Com-Iltg-dWatt-Exit | SDG | MBT | New | CZ10 | 8.76 | 0.001 | 0 | 9.82 | 0.00148 | -0.00553 | 8.76 | 0.001 | 0 | 9.82 | 0.00148 | -0.00553 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.12 | 1.48 | -0.00063128 | 8760 | 1 | 8760 | 1 | 1.12 | 1.48 | -0.000631
ExitNoneSDGMBTNewCZ14 | Com-Iltg-dWatt-Exit | SDG | MBT | New | CZ14 | 8.76 | 0.001 | 0 | 9.68 | 0.00145 | -0.00902 | 8.76 | 0.001 | 0 | 9.68 | 0.00145 | -0.00902 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.11 | 1.45 | -0.0010297 | 8760 | 1 | 8760 | 1 | 1.11 | 1.45 | -0.00103
ExitNoneSDGMBTNewCZ15 | Com-Iltg-dWatt-Exit | SDG | MBT | New | CZ15 | 8.76 | 0.001 | 0 | 10.4 | 0.00152 | -0.00193 | 8.76 | 0.001 | 0 | 10.4 | 0.00152 | -0.00193 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.19 | 1.52 | -0.00022032 | 8760 | 1 | 8760 | 1 | 1.19 | 1.52 | -0.00022
ExitNoneSDGMBTNewIOU | Com-Iltg-dWatt-Exit | SDG | MBT | New | IOU | 8.76 | 0.001 | 0 | 9.86 | 0.00138 | -0.00397 | 8.76 | 0.001 | 0 | 9.86 | 0.00138 | -0.00397 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.13 | 1.38 | -0.0004532 | 8760 | 1 | 8760 | 1 | 1.13 | 1.38 | -0.000453
ExitNoneSDGMLIExCZ06 | Com-Iltg-dWatt-Exit | SDG | MLI | Ex | CZ06 | 8.76 | 0.001 | 0 | 9.28 | 0.00132 | -0.0257 | 8.76 | 0.001 | 0 | 9.28 | 0.00132 | -0.0257 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.06 | 1.32 | -0.0029338 | 8760 | 1 | 8760 | 1 | 1.06 | 1.32 | -0.00293
ExitNoneSDGMLIExCZ07 | Com-Iltg-dWatt-Exit | SDG | MLI | Ex | CZ07 | 8.76 | 0.001 | 0 | 9.27 | 0.00132 | -0.0146 | 8.76 | 0.001 | 0 | 9.27 | 0.00132 | -0.0146 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.06 | 1.32 | -0.0016667 | 8760 | 1 | 8760 | 1 | 1.06 | 1.32 | -0.00167
ExitNoneSDGMLIExCZ08 | Com-Iltg-dWatt-Exit | SDG | MLI | Ex | CZ08 | 8.76 | 0.001 | 0 | 9.36 | 0.00132 | -0.0221 | 8.76 | 0.001 | 0 | 9.36 | 0.00132 | -0.0221 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.07 | 1.32 | -0.0025228 | 8760 | 1 | 8760 | 1 | 1.07 | 1.32 | -0.00252
ExitNoneSDGMLIExCZ10 | Com-Iltg-dWatt-Exit | SDG | MLI | Ex | CZ10 | 8.76 | 0.001 | 0 | 9.32 | 0.00137 | -0.0293 | 8.76 | 0.001 | 0 | 9.32 | 0.00137 | -0.0293 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.06 | 1.37 | -0.0033447 | 8760 | 1 | 8760 | 1 | 1.06 | 1.37 | -0.00334
ExitNoneSDGMLIExCZ14 | Com-Iltg-dWatt-Exit | SDG | MLI | Ex | CZ14 | 8.76 | 0.001 | 0 | 9.08 | 0.00132 | -0.0618 | 8.76 | 0.001 | 0 | 9.08 | 0.00132 | -0.0618 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.04 | 1.32 | -0.0070548 | 8760 | 1 | 8760 | 1 | 1.04 | 1.32 | -0.00705
ExitNoneSDGMLIExCZ15 | Com-Iltg-dWatt-Exit | SDG | MLI | Ex | CZ15 | 8.76 | 0.001 | 0 | 10.4 | 0.00122 | -0.00946 | 8.76 | 0.001 | 0 | 10.4 | 0.00122 | -0.00946 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.19 | 1.22 | -0.0010799 | 8760 | 1 | 8760 | 1 | 1.19 | 1.22 | -0.00108
ExitNoneSDGMLIExIOU | Com-Iltg-dWatt-Exit | SDG | MLI | Ex | IOU | 8.76 | 0.001 | 0 | 9.29 | 0.00134 | -0.0201 | 8.76 | 0.001 | 0 | 9.29 | 0.00134 | -0.0201 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.06 | 1.34 | -0.0022945 | 8760 | 1 | 8760 | 1 | 1.06 | 1.34 | -0.00229
ExitNoneSDGMLINewCZ06 | Com-Iltg-dWatt-Exit | SDG | MLI | New | CZ06 | 8.76 | 0.001 | 0 | 9.01 | 0.0013 | -0.0413 | 8.76 | 0.001 | 0 | 9.01 | 0.0013 | -0.0413 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.03 | 1.3 | -0.0047146 | 8760 | 1 | 8760 | 1 | 1.03 | 1.3 | -0.00471
ExitNoneSDGMLINewCZ07 | Com-Iltg-dWatt-Exit | SDG | MLI | New | CZ07 | 8.76 | 0.001 | 0 | 8.97 | 0.00131 | -0.0265 | 8.76 | 0.001 | 0 | 8.97 | 0.00131 | -0.0265 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.02 | 1.31 | -0.0030251 | 8760 | 1 | 8760 | 1 | 1.02 | 1.31 | -0.00303
ExitNoneSDGMLINewCZ08 | Com-Iltg-dWatt-Exit | SDG | MLI | New | CZ08 | 8.76 | 0.001 | 0 | 9.12 | 0.0013 | -0.0357 | 8.76 | 0.001 | 0 | 9.12 | 0.0013 | -0.0357 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.04 | 1.3 | -0.0040753 | 8760 | 1 | 8760 | 1 | 1.04 | 1.3 | -0.00408
ExitNoneSDGMLINewCZ10 | Com-Iltg-dWatt-Exit | SDG | MLI | New | CZ10 | 8.76 | 0.001 | 0 | 9.29 | 0.00149 | -0.0424 | 8.76 | 0.001 | 0 | 9.29 | 0.00149 | -0.0424 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.06 | 1.49 | -0.0048402 | 8760 | 1 | 8760 | 1 | 1.06 | 1.49 | -0.00484
ExitNoneSDGMLINewCZ14 | Com-Iltg-dWatt-Exit | SDG | MLI | New | CZ14 | 8.76 | 0.001 | 0 | 9.03 | 0.00134 | -0.073 | 8.76 | 0.001 | 0 | 9.03 | 0.00134 | -0.073 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.03 | 1.34 | -0.0083333 | 8760 | 1 | 8760 | 1 | 1.03 | 1.34 | -0.00833
ExitNoneSDGMLINewCZ15 | Com-Iltg-dWatt-Exit | SDG | MLI | New | CZ15 | 8.76 | 0.001 | 0 | 9.93 | 0.00152 | -0.0113 | 8.76 | 0.001 | 0 | 9.93 | 0.00152 | -0.0113 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.13 | 1.52 | -0.00129 | 8760 | 1 | 8760 | 1 | 1.13 | 1.52 | -0.00129
ExitNoneSDGMLINewIOU | Com-Iltg-dWatt-Exit | SDG | MLI | New | IOU | 8.76 | 0.001 | 0 | 9.08 | 0.00136 | -0.0323 | 8.76 | 0.001 | 0 | 9.08 | 0.00136 | -0.0323 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.04 | 1.36 | -0.0036872 | 8760 | 1 | 8760 | 1 | 1.04 | 1.36 | -0.00369
ExitNoneSDGMtlExCZ06 | Com-Iltg-dWatt-Exit | SDG | Mtl | Ex | CZ06 | 8.76 | 0.001 | 0 | 10 | 0.00126 | -0.0196 | 8.76 | 0.001 | 0 | 10 | 0.00126 | -0.0196 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.14 | 1.26 | -0.0022374 | 8760 | 1 | 8760 | 1 | 1.14 | 1.26 | -0.00224
ExitNoneSDGMtlExCZ07 | Com-Iltg-dWatt-Exit | SDG | Mtl | Ex | CZ07 | 8.76 | 0.001 | 0 | 10.2 | 0.00125 | -0.0137 | 8.76 | 0.001 | 0 | 10.2 | 0.00125 | -0.0137 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.16 | 1.25 | -0.0015639 | 8760 | 1 | 8760 | 1 | 1.16 | 1.25 | -0.00156
ExitNoneSDGMtlExCZ08 | Com-Iltg-dWatt-Exit | SDG | Mtl | Ex | CZ08 | 8.76 | 0.001 | 0 | 10.2 | 0.00128 | -0.0165 | 8.76 | 0.001 | 0 | 10.2 | 0.00128 | -0.0165 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.16 | 1.28 | -0.0018836 | 8760 | 1 | 8760 | 1 | 1.16 | 1.28 | -0.00188
ExitNoneSDGMtlExCZ10 | Com-Iltg-dWatt-Exit | SDG | Mtl | Ex | CZ10 | 8.76 | 0.001 | 0 | 10 | 0.00132 | -0.0189 | 8.76 | 0.001 | 0 | 10 | 0.00132 | -0.0189 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.14 | 1.32 | -0.0021575 | 8760 | 1 | 8760 | 1 | 1.14 | 1.32 | -0.00216
ExitNoneSDGMtlExCZ14 | Com-Iltg-dWatt-Exit | SDG | Mtl | Ex | CZ14 | 8.76 | 0.001 | 0 | 9.76 | 0.00131 | -0.0279 | 8.76 | 0.001 | 0 | 9.76 | 0.00131 | -0.0279 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.11 | 1.31 | -0.0031849 | 8760 | 1 | 8760 | 1 | 1.11 | 1.31 | -0.00318
ExitNoneSDGMtlExCZ15 | Com-Iltg-dWatt-Exit | SDG | Mtl | Ex | CZ15 | 8.76 | 0.001 | 0 | 10.6 | 0.00133 | -0.00741 | 8.76 | 0.001 | 0 | 10.6 | 0.00133 | -0.00741 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.21 | 1.33 | -0.00084589 | 8760 | 1 | 8760 | 1 | 1.21 | 1.33 | -0.000846
ExitNoneSDGMtlExIOU | Com-Iltg-dWatt-Exit | SDG | Mtl | Ex | IOU | 8.76 | 0.001 | 0 | 10.2 | 0.00126 | -0.0145 | 8.76 | 0.001 | 0 | 10.2 | 0.00126 | -0.0145 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.16 | 1.26 | -0.0016553 | 8760 | 1 | 8760 | 1 | 1.16 | 1.26 | -0.00166
ExitNoneSDGMtlNewCZ06 | Com-Iltg-dWatt-Exit | SDG | Mtl | New | CZ06 | 8.76 | 0.001 | 0 | 9.86 | 0.00128 | -0.0299 | 8.76 | 0.001 | 0 | 9.86 | 0.00128 | -0.0299 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.13 | 1.28 | -0.0034132 | 8760 | 1 | 8760 | 1 | 1.13 | 1.28 | -0.00341
ExitNoneSDGMtlNewCZ07 | Com-Iltg-dWatt-Exit | SDG | Mtl | New | CZ07 | 8.76 | 0.001 | 0 | 9.93 | 0.00125 | -0.0208 | 8.76 | 0.001 | 0 | 9.93 | 0.00125 | -0.0208 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.13 | 1.25 | -0.0023744 | 8760 | 1 | 8760 | 1 | 1.13 | 1.25 | -0.00237
ExitNoneSDGMtlNewCZ08 | Com-Iltg-dWatt-Exit | SDG | Mtl | New | CZ08 | 8.76 | 0.001 | 0 | 10 | 0.00131 | -0.0251 | 8.76 | 0.001 | 0 | 10 | 0.00131 | -0.0251 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.14 | 1.31 | -0.0028653 | 8760 | 1 | 8760 | 1 | 1.14 | 1.31 | -0.00287
ExitNoneSDGMtlNewCZ10 | Com-Iltg-dWatt-Exit | SDG | Mtl | New | CZ10 | 8.76 | 0.001 | 0 | 9.86 | 0.00133 | -0.0293 | 8.76 | 0.001 | 0 | 9.86 | 0.00133 | -0.0293 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.13 | 1.33 | -0.0033447 | 8760 | 1 | 8760 | 1 | 1.13 | 1.33 | -0.00334
ExitNoneSDGMtlNewCZ14 | Com-Iltg-dWatt-Exit | SDG | Mtl | New | CZ14 | 8.76 | 0.001 | 0 | 9.43 | 0.00132 | -0.0412 | 8.76 | 0.001 | 0 | 9.43 | 0.00132 | -0.0412 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.08 | 1.32 | -0.0047032 | 8760 | 1 | 8760 | 1 | 1.08 | 1.32 | -0.0047
ExitNoneSDGMtlNewCZ15 | Com-Iltg-dWatt-Exit | SDG | Mtl | New | CZ15 | 8.76 | 0.001 | 0 | 10.5 | 0.00135 | -0.0134 | 8.76 | 0.001 | 0 | 10.5 | 0.00135 | -0.0134 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.2 | 1.35 | -0.0015297 | 8760 | 1 | 8760 | 1 | 1.2 | 1.35 | -0.00153
ExitNoneSDGMtlNewIOU | Com-Iltg-dWatt-Exit | SDG | Mtl | New | IOU | 8.76 | 0.001 | 0 | 9.92 | 0.00126 | -0.0222 | 8.76 | 0.001 | 0 | 9.92 | 0.00126 | -0.0222 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.13 | 1.26 | -0.0025342 | 8760 | 1 | 8760 | 1 | 1.13 | 1.26 | -0.00253
ExitNoneSDGNrsExCZ06 | Com-Iltg-dWatt-Exit | SDG | Nrs | Ex | CZ06 | 8.76 | 0.001 | 0 | 9.11 | 0.00132 | -0.123 | 8.76 | 0.001 | 0 | 9.11 | 0.00132 | -0.123 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.04 | 1.32 | -0.014041 | 8760 | 1 | 8760 | 1 | 1.04 | 1.32 | -0.014
ExitNoneSDGNrsExCZ07 | Com-Iltg-dWatt-Exit | SDG | Nrs | Ex | CZ07 | 8.76 | 0.001 | 0 | 9.12 | 0.00131 | -0.114 | 8.76 | 0.001 | 0 | 9.12 | 0.00131 | -0.114 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.04 | 1.31 | -0.013014 | 8760 | 1 | 8760 | 1 | 1.04 | 1.31 | -0.013
ExitNoneSDGNrsExCZ08 | Com-Iltg-dWatt-Exit | SDG | Nrs | Ex | CZ08 | 8.76 | 0.001 | 0 | 9.24 | 0.00134 | -0.12 | 8.76 | 0.001 | 0 | 9.24 | 0.00134 | -0.12 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.05 | 1.34 | -0.013699 | 8760 | 1 | 8760 | 1 | 1.05 | 1.34 | -0.0137
ExitNoneSDGNrsExCZ10 | Com-Iltg-dWatt-Exit | SDG | Nrs | Ex | CZ10 | 8.76 | 0.001 | 0 | 9.26 | 0.00138 | -0.124 | 8.76 | 0.001 | 0 | 9.26 | 0.00138 | -0.124 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.06 | 1.38 | -0.014155 | 8760 | 1 | 8760 | 1 | 1.06 | 1.38 | -0.0142
ExitNoneSDGNrsExCZ14 | Com-Iltg-dWatt-Exit | SDG | Nrs | Ex | CZ14 | 8.76 | 0.001 | 0 | 9.17 | 0.00136 | -0.136 | 8.76 | 0.001 | 0 | 9.17 | 0.00136 | -0.136 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.05 | 1.36 | -0.015525 | 8760 | 1 | 8760 | 1 | 1.05 | 1.36 | -0.0155
ExitNoneSDGNrsExCZ15 | Com-Iltg-dWatt-Exit | SDG | Nrs | Ex | CZ15 | 8.76 | 0.001 | 0 | 9.87 | 0.00138 | -0.0752 | 8.76 | 0.001 | 0 | 9.87 | 0.00138 | -0.0752 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.13 | 1.38 | -0.0085845 | 8760 | 1 | 8760 | 1 | 1.13 | 1.38 | -0.00858
ExitNoneSDGNrsExIOU | Com-Iltg-dWatt-Exit | SDG | Nrs | Ex | IOU | 8.76 | 0.001 | 0 | 9.15 | 0.00132 | -0.117 | 8.76 | 0.001 | 0 | 9.15 | 0.00132 | -0.117 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.04 | 1.32 | -0.013356 | 8760 | 1 | 8760 | 1 | 1.04 | 1.32 | -0.0134
ExitNoneSDGNrsNewCZ06 | Com-Iltg-dWatt-Exit | SDG | Nrs | New | CZ06 | 8.76 | 0.001 | 0 | 8.74 | 0.00131 | -0.144 | 8.76 | 0.001 | 0 | 8.74 | 0.00131 | -0.144 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.998 | 1.31 | -0.016438 | 8760 | 1 | 8760 | 1 | 0.998 | 1.31 | -0.0164
ExitNoneSDGNrsNewCZ07 | Com-Iltg-dWatt-Exit | SDG | Nrs | New | CZ07 | 8.76 | 0.001 | 0 | 8.71 | 0.00131 | -0.146 | 8.76 | 0.001 | 0 | 8.71 | 0.00131 | -0.146 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.994 | 1.31 | -0.016667 | 8760 | 1 | 8760 | 1 | 0.994 | 1.31 | -0.0167
ExitNoneSDGNrsNewCZ08 | Com-Iltg-dWatt-Exit | SDG | Nrs | New | CZ08 | 8.76 | 0.001 | 0 | 8.91 | 0.00133 | -0.132 | 8.76 | 0.001 | 0 | 8.91 | 0.00133 | -0.132 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.02 | 1.33 | -0.015068 | 8760 | 1 | 8760 | 1 | 1.02 | 1.33 | -0.0151
ExitNoneSDGNrsNewCZ10 | Com-Iltg-dWatt-Exit | SDG | Nrs | New | CZ10 | 8.76 | 0.001 | 0 | 9.02 | 0.00139 | -0.143 | 8.76 | 0.001 | 0 | 9.02 | 0.00139 | -0.143 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.03 | 1.39 | -0.016324 | 8760 | 1 | 8760 | 1 | 1.03 | 1.39 | -0.0163
ExitNoneSDGNrsNewCZ14 | Com-Iltg-dWatt-Exit | SDG | Nrs | New | CZ14 | 8.76 | 0.001 | 0 | 8.99 | 0.00134 | -0.149 | 8.76 | 0.001 | 0 | 8.99 | 0.00134 | -0.149 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.03 | 1.34 | -0.017009 | 8760 | 1 | 8760 | 1 | 1.03 | 1.34 | -0.017
ExitNoneSDGNrsNewCZ15 | Com-Iltg-dWatt-Exit | SDG | Nrs | New | CZ15 | 8.76 | 0.001 | 0 | 9.84 | 0.00138 | -0.0792 | 8.76 | 0.001 | 0 | 9.84 | 0.00138 | -0.0792 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.12 | 1.38 | -0.0090411 | 8760 | 1 | 8760 | 1 | 1.12 | 1.38 | -0.00904
ExitNoneSDGNrsNewIOU | Com-Iltg-dWatt-Exit | SDG | Nrs | New | IOU | 8.76 | 0.001 | 0 | 8.76 | 0.00132 | -0.145 | 8.76 | 0.001 | 0 | 8.76 | 0.00132 | -0.145 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1 | 1.32 | -0.016553 | 8760 | 1 | 8760 | 1 | 1 | 1.32 | -0.0166
ExitNoneSDGOfLExCZ06 | Com-Iltg-dWatt-Exit | SDG | OfL | Ex | CZ06 | 8.76 | 0.001 | 0 | 10.1 | 0.00135 | -0.0209 | 8.76 | 0.001 | 0 | 10.1 | 0.00135 | -0.0209 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.15 | 1.35 | -0.0023858 | 8760 | 1 | 8760 | 1 | 1.15 | 1.35 | -0.00239
ExitNoneSDGOfLExCZ07 | Com-Iltg-dWatt-Exit | SDG | OfL | Ex | CZ07 | 8.76 | 0.001 | 0 | 10.1 | 0.00134 | -0.0143 | 8.76 | 0.001 | 0 | 10.1 | 0.00134 | -0.0143 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.15 | 1.34 | -0.0016324 | 8760 | 1 | 8760 | 1 | 1.15 | 1.34 | -0.00163
ExitNoneSDGOfLExCZ08 | Com-Iltg-dWatt-Exit | SDG | OfL | Ex | CZ08 | 8.76 | 0.001 | 0 | 10.1 | 0.0014 | -0.0223 | 8.76 | 0.001 | 0 | 10.1 | 0.0014 | -0.0223 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.15 | 1.4 | -0.0025457 | 8760 | 1 | 8760 | 1 | 1.15 | 1.4 | -0.00255
ExitNoneSDGOfLExCZ10 | Com-Iltg-dWatt-Exit | SDG | OfL | Ex | CZ10 | 8.76 | 0.001 | 0 | 10 | 0.00141 | -0.0279 | 8.76 | 0.001 | 0 | 10 | 0.00141 | -0.0279 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.14 | 1.41 | -0.0031849 | 8760 | 1 | 8760 | 1 | 1.14 | 1.41 | -0.00318
ExitNoneSDGOfLExCZ14 | Com-Iltg-dWatt-Exit | SDG | OfL | Ex | CZ14 | 8.76 | 0.001 | 0 | 9.98 | 0.00136 | -0.0402 | 8.76 | 0.001 | 0 | 9.98 | 0.00136 | -0.0402 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.14 | 1.36 | -0.004589 | 8760 | 1 | 8760 | 1 | 1.14 | 1.36 | -0.00459
ExitNoneSDGOfLExCZ15 | Com-Iltg-dWatt-Exit | SDG | OfL | Ex | CZ15 | 8.76 | 0.001 | 0 | 10.7 | 0.00142 | -0.0132 | 8.76 | 0.001 | 0 | 10.7 | 0.00142 | -0.0132 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.22 | 1.42 | -0.0015068 | 8760 | 1 | 8760 | 1 | 1.22 | 1.42 | -0.00151
ExitNoneSDGOfLExIOU | Com-Iltg-dWatt-Exit | SDG | OfL | Ex | IOU | 8.76 | 0.001 | 0 | 10.1 | 0.00136 | -0.0171 | 8.76 | 0.001 | 0 | 10.1 | 0.00136 | -0.0171 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.15 | 1.36 | -0.0019521 | 8760 | 1 | 8760 | 1 | 1.15 | 1.36 | -0.00195
ExitNoneSDGOfLNewCZ06 | Com-Iltg-dWatt-Exit | SDG | OfL | New | CZ06 | 8.76 | 0.001 | 0 | 10 | 0.00133 | -0.0154 | 8.76 | 0.001 | 0 | 10 | 0.00133 | -0.0154 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.14 | 1.33 | -0.001758 | 8760 | 1 | 8760 | 1 | 1.14 | 1.33 | -0.00176
ExitNoneSDGOfLNewCZ07 | Com-Iltg-dWatt-Exit | SDG | OfL | New | CZ07 | 8.76 | 0.001 | 0 | 10 | 0.00132 | -0.015 | 8.76 | 0.001 | 0 | 10 | 0.00132 | -0.015 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.14 | 1.32 | -0.0017123 | 8760 | 1 | 8760 | 1 | 1.14 | 1.32 | -0.00171
ExitNoneSDGOfLNewCZ08 | Com-Iltg-dWatt-Exit | SDG | OfL | New | CZ08 | 8.76 | 0.001 | 0 | 10 | 0.00135 | -0.0164 | 8.76 | 0.001 | 0 | 10 | 0.00135 | -0.0164 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.14 | 1.35 | -0.0018721 | 8760 | 1 | 8760 | 1 | 1.14 | 1.35 | -0.00187
ExitNoneSDGOfLNewCZ10 | Com-Iltg-dWatt-Exit | SDG | OfL | New | CZ10 | 8.76 | 0.001 | 0 | 10 | 0.0014 | -0.0331 | 8.76 | 0.001 | 0 | 10 | 0.0014 | -0.0331 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.14 | 1.4 | -0.0037785 | 8760 | 1 | 8760 | 1 | 1.14 | 1.4 | -0.00378
ExitNoneSDGOfLNewCZ14 | Com-Iltg-dWatt-Exit | SDG | OfL | New | CZ14 | 8.76 | 0.001 | 0 | 9.81 | 0.00141 | -0.0293 | 8.76 | 0.001 | 0 | 9.81 | 0.00141 | -0.0293 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.12 | 1.41 | -0.0033447 | 8760 | 1 | 8760 | 1 | 1.12 | 1.41 | -0.00334
ExitNoneSDGOfLNewCZ15 | Com-Iltg-dWatt-Exit | SDG | OfL | New | CZ15 | 8.76 | 0.001 | 0 | 10.4 | 0.00139 | -0.0132 | 8.76 | 0.001 | 0 | 10.4 | 0.00139 | -0.0132 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.19 | 1.39 | -0.0015068 | 8760 | 1 | 8760 | 1 | 1.19 | 1.39 | -0.00151
ExitNoneSDGOfLNewIOU | Com-Iltg-dWatt-Exit | SDG | OfL | New | IOU | 8.76 | 0.001 | 0 | 10 | 0.00134 | -0.0182 | 8.76 | 0.001 | 0 | 10 | 0.00134 | -0.0182 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.14 | 1.34 | -0.0020776 | 8760 | 1 | 8760 | 1 | 1.14 | 1.34 | -0.00208
ExitNoneSDGOfSExCZ06 | Com-Iltg-dWatt-Exit | SDG | OfS | Ex | CZ06 | 8.76 | 0.001 | 0 | 9.93 | 0.00137 | -0.0111 | 8.76 | 0.001 | 0 | 9.93 | 0.00137 | -0.0111 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.13 | 1.37 | -0.0012671 | 8760 | 1 | 8760 | 1 | 1.13 | 1.37 | -0.00127
ExitNoneSDGOfSExCZ07 | Com-Iltg-dWatt-Exit | SDG | OfS | Ex | CZ07 | 8.76 | 0.001 | 0 | 10 | 0.00135 | -0.00347 | 8.76 | 0.001 | 0 | 10 | 0.00135 | -0.00347 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.14 | 1.35 | -0.00039612 | 8760 | 1 | 8760 | 1 | 1.14 | 1.35 | -0.000396
ExitNoneSDGOfSExCZ08 | Com-Iltg-dWatt-Exit | SDG | OfS | Ex | CZ08 | 8.76 | 0.001 | 0 | 10 | 0.00138 | -0.00885 | 8.76 | 0.001 | 0 | 10 | 0.00138 | -0.00885 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.14 | 1.38 | -0.0010103 | 8760 | 1 | 8760 | 1 | 1.14 | 1.38 | -0.00101
ExitNoneSDGOfSExCZ10 | Com-Iltg-dWatt-Exit | SDG | OfS | Ex | CZ10 | 8.76 | 0.001 | 0 | 9.96 | 0.00138 | -0.0127 | 8.76 | 0.001 | 0 | 9.96 | 0.00138 | -0.0127 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.14 | 1.38 | -0.0014498 | 8760 | 1 | 8760 | 1 | 1.14 | 1.38 | -0.00145
ExitNoneSDGOfSExCZ14 | Com-Iltg-dWatt-Exit | SDG | OfS | Ex | CZ14 | 8.76 | 0.001 | 0 | 9.71 | 0.00136 | -0.0271 | 8.76 | 0.001 | 0 | 9.71 | 0.00136 | -0.0271 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.11 | 1.36 | -0.0030936 | 8760 | 1 | 8760 | 1 | 1.11 | 1.36 | -0.00309
ExitNoneSDGOfSExCZ15 | Com-Iltg-dWatt-Exit | SDG | OfS | Ex | CZ15 | 8.76 | 0.001 | 0 | 10.8 | 0.00134 | -0.00358 | 8.76 | 0.001 | 0 | 10.8 | 0.00134 | -0.00358 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.23 | 1.34 | -0.00040868 | 8760 | 1 | 8760 | 1 | 1.23 | 1.34 | -0.000409
ExitNoneSDGOfSExIOU | Com-Iltg-dWatt-Exit | SDG | OfS | Ex | IOU | 8.76 | 0.001 | 0 | 10 | 0.00136 | -0.00545 | 8.76 | 0.001 | 0 | 10 | 0.00136 | -0.00545 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.14 | 1.36 | -0.00062215 | 8760 | 1 | 8760 | 1 | 1.14 | 1.36 | -0.000622
ExitNoneSDGOfSNewCZ06 | Com-Iltg-dWatt-Exit | SDG | OfS | New | CZ06 | 8.76 | 0.001 | 0 | 9.52 | 0.00134 | -0.0131 | 8.76 | 0.001 | 0 | 9.52 | 0.00134 | -0.0131 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.09 | 1.34 | -0.0014954 | 8760 | 1 | 8760 | 1 | 1.09 | 1.34 | -0.0015
ExitNoneSDGOfSNewCZ07 | Com-Iltg-dWatt-Exit | SDG | OfS | New | CZ07 | 8.76 | 0.001 | 0 | 9.56 | 0.00133 | -0.00399 | 8.76 | 0.001 | 0 | 9.56 | 0.00133 | -0.00399 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.09 | 1.33 | -0.00045548 | 8760 | 1 | 8760 | 1 | 1.09 | 1.33 | -0.000455
ExitNoneSDGOfSNewCZ08 | Com-Iltg-dWatt-Exit | SDG | OfS | New | CZ08 | 8.76 | 0.001 | 0 | 9.57 | 0.00136 | -0.0107 | 8.76 | 0.001 | 0 | 9.57 | 0.00136 | -0.0107 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.09 | 1.36 | -0.0012215 | 8760 | 1 | 8760 | 1 | 1.09 | 1.36 | -0.00122
ExitNoneSDGOfSNewCZ10 | Com-Iltg-dWatt-Exit | SDG | OfS | New | CZ10 | 8.76 | 0.001 | 0 | 9.64 | 0.00143 | -0.00902 | 8.76 | 0.001 | 0 | 9.64 | 0.00143 | -0.00902 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.1 | 1.43 | -0.0010297 | 8760 | 1 | 8760 | 1 | 1.1 | 1.43 | -0.00103
ExitNoneSDGOfSNewCZ14 | Com-Iltg-dWatt-Exit | SDG | OfS | New | CZ14 | 8.76 | 0.001 | 0 | 9.41 | 0.00142 | -0.0274 | 8.76 | 0.001 | 0 | 9.41 | 0.00142 | -0.0274 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.07 | 1.42 | -0.0031279 | 8760 | 1 | 8760 | 1 | 1.07 | 1.42 | -0.00313
ExitNoneSDGOfSNewCZ15 | Com-Iltg-dWatt-Exit | SDG | OfS | New | CZ15 | 8.76 | 0.001 | 0 | 10.2 | 0.00145 | -0.00191 | 8.76 | 0.001 | 0 | 10.2 | 0.00145 | -0.00191 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.16 | 1.45 | -0.00021804 | 8760 | 1 | 8760 | 1 | 1.16 | 1.45 | -0.000218
ExitNoneSDGOfSNewIOU | Com-Iltg-dWatt-Exit | SDG | OfS | New | IOU | 8.76 | 0.001 | 0 | 9.57 | 0.00135 | -0.0053 | 8.76 | 0.001 | 0 | 9.57 | 0.00135 | -0.0053 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.09 | 1.35 | -0.00060502 | 8760 | 1 | 8760 | 1 | 1.09 | 1.35 | -0.000605
ExitNoneSDGRFFExCZ06 | Com-Iltg-dWatt-Exit | SDG | RFF | Ex | CZ06 | 8.76 | 0.001 | 0 | 9.69 | 0.00128 | -0.0508 | 8.76 | 0.001 | 0 | 9.69 | 0.00128 | -0.0508 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.11 | 1.28 | -0.0057991 | 8760 | 1 | 8760 | 1 | 1.11 | 1.28 | -0.0058
ExitNoneSDGRFFExCZ07 | Com-Iltg-dWatt-Exit | SDG | RFF | Ex | CZ07 | 8.76 | 0.001 | 0 | 9.74 | 0.00127 | -0.0468 | 8.76 | 0.001 | 0 | 9.74 | 0.00127 | -0.0468 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.11 | 1.27 | -0.0053425 | 8760 | 1 | 8760 | 1 | 1.11 | 1.27 | -0.00534
ExitNoneSDGRFFExCZ08 | Com-Iltg-dWatt-Exit | SDG | RFF | Ex | CZ08 | 8.76 | 0.001 | 0 | 9.77 | 0.00127 | -0.0461 | 8.76 | 0.001 | 0 | 9.77 | 0.00127 | -0.0461 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.12 | 1.27 | -0.0052626 | 8760 | 1 | 8760 | 1 | 1.12 | 1.27 | -0.00526
ExitNoneSDGRFFExCZ10 | Com-Iltg-dWatt-Exit | SDG | RFF | Ex | CZ10 | 8.76 | 0.001 | 0 | 9.73 | 0.0013 | -0.0512 | 8.76 | 0.001 | 0 | 9.73 | 0.0013 | -0.0512 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.11 | 1.3 | -0.0058447 | 8760 | 1 | 8760 | 1 | 1.11 | 1.3 | -0.00584
ExitNoneSDGRFFExCZ14 | Com-Iltg-dWatt-Exit | SDG | RFF | Ex | CZ14 | 8.76 | 0.001 | 0 | 9.5 | 0.00131 | -0.073 | 8.76 | 0.001 | 0 | 9.5 | 0.00131 | -0.073 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.08 | 1.31 | -0.0083333 | 8760 | 1 | 8760 | 1 | 1.08 | 1.31 | -0.00833
ExitNoneSDGRFFExCZ15 | Com-Iltg-dWatt-Exit | SDG | RFF | Ex | CZ15 | 8.76 | 0.001 | 0 | 10.5 | 0.00127 | -0.0225 | 8.76 | 0.001 | 0 | 10.5 | 0.00127 | -0.0225 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.2 | 1.27 | -0.0025685 | 8760 | 1 | 8760 | 1 | 1.2 | 1.27 | -0.00257
ExitNoneSDGRFFExIOU | Com-Iltg-dWatt-Exit | SDG | RFF | Ex | IOU | 8.76 | 0.001 | 0 | 9.74 | 0.00128 | -0.0479 | 8.76 | 0.001 | 0 | 9.74 | 0.00128 | -0.0479 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.11 | 1.28 | -0.005468 | 8760 | 1 | 8760 | 1 | 1.11 | 1.28 | -0.00547
ExitNoneSDGRFFNewCZ06 | Com-Iltg-dWatt-Exit | SDG | RFF | New | CZ06 | 8.76 | 0.001 | 0 | 9.35 | 0.00132 | -0.0664 | 8.76 | 0.001 | 0 | 9.35 | 0.00132 | -0.0664 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.07 | 1.32 | -0.0075799 | 8760 | 1 | 8760 | 1 | 1.07 | 1.32 | -0.00758
ExitNoneSDGRFFNewCZ07 | Com-Iltg-dWatt-Exit | SDG | RFF | New | CZ07 | 8.76 | 0.001 | 0 | 9.37 | 0.0013 | -0.0569 | 8.76 | 0.001 | 0 | 9.37 | 0.0013 | -0.0569 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.07 | 1.3 | -0.0064954 | 8760 | 1 | 8760 | 1 | 1.07 | 1.3 | -0.0065
ExitNoneSDGRFFNewCZ08 | Com-Iltg-dWatt-Exit | SDG | RFF | New | CZ08 | 8.76 | 0.001 | 0 | 9.5 | 0.00133 | -0.0581 | 8.76 | 0.001 | 0 | 9.5 | 0.00133 | -0.0581 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.08 | 1.33 | -0.0066324 | 8760 | 1 | 8760 | 1 | 1.08 | 1.33 | -0.00663
ExitNoneSDGRFFNewCZ10 | Com-Iltg-dWatt-Exit | SDG | RFF | New | CZ10 | 8.76 | 0.001 | 0 | 9.54 | 0.0014 | -0.0663 | 8.76 | 0.001 | 0 | 9.54 | 0.0014 | -0.0663 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.09 | 1.4 | -0.0075685 | 8760 | 1 | 8760 | 1 | 1.09 | 1.4 | -0.00757
ExitNoneSDGRFFNewCZ14 | Com-Iltg-dWatt-Exit | SDG | RFF | New | CZ14 | 8.76 | 0.001 | 0 | 9.5 | 0.0014 | -0.0902 | 8.76 | 0.001 | 0 | 9.5 | 0.0014 | -0.0902 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.08 | 1.4 | -0.010297 | 8760 | 1 | 8760 | 1 | 1.08 | 1.4 | -0.0103
ExitNoneSDGRFFNewCZ15 | Com-Iltg-dWatt-Exit | SDG | RFF | New | CZ15 | 8.76 | 0.001 | 0 | 10.3 | 0.00137 | -0.0258 | 8.76 | 0.001 | 0 | 10.3 | 0.00137 | -0.0258 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.18 | 1.37 | -0.0029452 | 8760 | 1 | 8760 | 1 | 1.18 | 1.37 | -0.00295
ExitNoneSDGRFFNewIOU | Com-Iltg-dWatt-Exit | SDG | RFF | New | IOU | 8.76 | 0.001 | 0 | 9.41 | 0.00133 | -0.0596 | 8.76 | 0.001 | 0 | 9.41 | 0.00133 | -0.0596 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.07 | 1.33 | -0.0068037 | 8760 | 1 | 8760 | 1 | 1.07 | 1.33 | -0.0068
ExitNoneSDGRSDExCZ06 | Com-Iltg-dWatt-Exit | SDG | RSD | Ex | CZ06 | 8.76 | 0.001 | 0 | 9.85 | 0.00134 | -0.0515 | 8.76 | 0.001 | 0 | 9.85 | 0.00134 | -0.0515 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.12 | 1.34 | -0.005879 | 8760 | 1 | 8760 | 1 | 1.12 | 1.34 | -0.00588
ExitNoneSDGRSDExCZ07 | Com-Iltg-dWatt-Exit | SDG | RSD | Ex | CZ07 | 8.76 | 0.001 | 0 | 9.86 | 0.00137 | -0.05 | 8.76 | 0.001 | 0 | 9.86 | 0.00137 | -0.05 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.13 | 1.37 | -0.0057078 | 8760 | 1 | 8760 | 1 | 1.13 | 1.37 | -0.00571
ExitNoneSDGRSDExCZ08 | Com-Iltg-dWatt-Exit | SDG | RSD | Ex | CZ08 | 8.76 | 0.001 | 0 | 9.92 | 0.00128 | -0.0442 | 8.76 | 0.001 | 0 | 9.92 | 0.00128 | -0.0442 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.13 | 1.28 | -0.0050457 | 8760 | 1 | 8760 | 1 | 1.13 | 1.28 | -0.00505
ExitNoneSDGRSDExCZ10 | Com-Iltg-dWatt-Exit | SDG | RSD | Ex | CZ10 | 8.76 | 0.001 | 0 | 9.83 | 0.00119 | -0.0505 | 8.76 | 0.001 | 0 | 9.83 | 0.00119 | -0.0505 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.12 | 1.19 | -0.0057648 | 8760 | 1 | 8760 | 1 | 1.12 | 1.19 | -0.00576
ExitNoneSDGRSDExCZ14 | Com-Iltg-dWatt-Exit | SDG | RSD | Ex | CZ14 | 8.76 | 0.001 | 0 | 9.5 | 0.00118 | -0.0796 | 8.76 | 0.001 | 0 | 9.5 | 0.00118 | -0.0796 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.08 | 1.18 | -0.0090868 | 8760 | 1 | 8760 | 1 | 1.08 | 1.18 | -0.00909
ExitNoneSDGRSDExCZ15 | Com-Iltg-dWatt-Exit | SDG | RSD | Ex | CZ15 | 8.76 | 0.001 | 0 | 10.7 | 0.00138 | -0.0199 | 8.76 | 0.001 | 0 | 10.7 | 0.00138 | -0.0199 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.22 | 1.38 | -0.0022717 | 8760 | 1 | 8760 | 1 | 1.22 | 1.38 | -0.00227
ExitNoneSDGRSDExIOU | Com-Iltg-dWatt-Exit | SDG | RSD | Ex | IOU | 8.76 | 0.001 | 0 | 9.86 | 0.00133 | -0.05 | 8.76 | 0.001 | 0 | 9.86 | 0.00133 | -0.05 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.13 | 1.33 | -0.0057078 | 8760 | 1 | 8760 | 1 | 1.13 | 1.33 | -0.00571
ExitNoneSDGRSDNewCZ06 | Com-Iltg-dWatt-Exit | SDG | RSD | New | CZ06 | 8.76 | 0.001 | 0 | 9.58 | 0.00137 | -0.0645 | 8.76 | 0.001 | 0 | 9.58 | 0.00137 | -0.0645 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.09 | 1.37 | -0.007363 | 8760 | 1 | 8760 | 1 | 1.09 | 1.37 | -0.00736
ExitNoneSDGRSDNewCZ07 | Com-Iltg-dWatt-Exit | SDG | RSD | New | CZ07 | 8.76 | 0.001 | 0 | 9.56 | 0.0014 | -0.0634 | 8.76 | 0.001 | 0 | 9.56 | 0.0014 | -0.0634 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.09 | 1.4 | -0.0072374 | 8760 | 1 | 8760 | 1 | 1.09 | 1.4 | -0.00724
ExitNoneSDGRSDNewCZ08 | Com-Iltg-dWatt-Exit | SDG | RSD | New | CZ08 | 8.76 | 0.001 | 0 | 9.67 | 0.00137 | -0.0525 | 8.76 | 0.001 | 0 | 9.67 | 0.00137 | -0.0525 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.1 | 1.37 | -0.0059932 | 8760 | 1 | 8760 | 1 | 1.1 | 1.37 | -0.00599
ExitNoneSDGRSDNewCZ10 | Com-Iltg-dWatt-Exit | SDG | RSD | New | CZ10 | 8.76 | 0.001 | 0 | 9.77 | 0.00145 | -0.0577 | 8.76 | 0.001 | 0 | 9.77 | 0.00145 | -0.0577 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.12 | 1.45 | -0.0065868 | 8760 | 1 | 8760 | 1 | 1.12 | 1.45 | -0.00659
ExitNoneSDGRSDNewCZ14 | Com-Iltg-dWatt-Exit | SDG | RSD | New | CZ14 | 8.76 | 0.001 | 0 | 9.5 | 0.00144 | -0.0929 | 8.76 | 0.001 | 0 | 9.5 | 0.00144 | -0.0929 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.08 | 1.44 | -0.010605 | 8760 | 1 | 8760 | 1 | 1.08 | 1.44 | -0.0106
ExitNoneSDGRSDNewCZ15 | Com-Iltg-dWatt-Exit | SDG | RSD | New | CZ15 | 8.76 | 0.001 | 0 | 10.5 | 0.00153 | -0.024 | 8.76 | 0.001 | 0 | 10.5 | 0.00153 | -0.024 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.2 | 1.53 | -0.0027397 | 8760 | 1 | 8760 | 1 | 1.2 | 1.53 | -0.00274
ExitNoneSDGRSDNewIOU | Com-Iltg-dWatt-Exit | SDG | RSD | New | IOU | 8.76 | 0.001 | 0 | 9.61 | 0.00141 | -0.0619 | 8.76 | 0.001 | 0 | 9.61 | 0.00141 | -0.0619 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.1 | 1.41 | -0.0070662 | 8760 | 1 | 8760 | 1 | 1.1 | 1.41 | -0.00707
ExitNoneSDGRt3ExCZ06 | Com-Iltg-dWatt-Exit | SDG | Rt3 | Ex | CZ06 | 8.76 | 0.001 | 0 | 10.1 | 0.00137 | -0.0171 | 8.76 | 0.001 | 0 | 10.1 | 0.00137 | -0.0171 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.15 | 1.37 | -0.0019521 | 8760 | 1 | 8760 | 1 | 1.15 | 1.37 | -0.00195
ExitNoneSDGRt3ExCZ07 | Com-Iltg-dWatt-Exit | SDG | Rt3 | Ex | CZ07 | 8.76 | 0.001 | 0 | 10.2 | 0.00135 | -0.00863 | 8.76 | 0.001 | 0 | 10.2 | 0.00135 | -0.00863 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.16 | 1.35 | -0.00098516 | 8760 | 1 | 8760 | 1 | 1.16 | 1.35 | -0.000985
ExitNoneSDGRt3ExCZ08 | Com-Iltg-dWatt-Exit | SDG | Rt3 | Ex | CZ08 | 8.76 | 0.001 | 0 | 10.1 | 0.00134 | -0.0138 | 8.76 | 0.001 | 0 | 10.1 | 0.00134 | -0.0138 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.15 | 1.34 | -0.0015753 | 8760 | 1 | 8760 | 1 | 1.15 | 1.34 | -0.00158
ExitNoneSDGRt3ExCZ10 | Com-Iltg-dWatt-Exit | SDG | Rt3 | Ex | CZ10 | 8.76 | 0.001 | 0 | 9.92 | 0.00136 | -0.0249 | 8.76 | 0.001 | 0 | 9.92 | 0.00136 | -0.0249 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.13 | 1.36 | -0.0028425 | 8760 | 1 | 8760 | 1 | 1.13 | 1.36 | -0.00284
ExitNoneSDGRt3ExCZ14 | Com-Iltg-dWatt-Exit | SDG | Rt3 | Ex | CZ14 | 8.76 | 0.001 | 0 | 9.41 | 0.00137 | -0.067 | 8.76 | 0.001 | 0 | 9.41 | 0.00137 | -0.067 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.07 | 1.37 | -0.0076484 | 8760 | 1 | 8760 | 1 | 1.07 | 1.37 | -0.00765
ExitNoneSDGRt3ExCZ15 | Com-Iltg-dWatt-Exit | SDG | Rt3 | Ex | CZ15 | 8.76 | 0.001 | 0 | 10.3 | 0.0014 | -0.00657 | 8.76 | 0.001 | 0 | 10.3 | 0.0014 | -0.00657 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.18 | 1.4 | -0.00075 | 8760 | 1 | 8760 | 1 | 1.18 | 1.4 | -0.00075
ExitNoneSDGRt3ExIOU | Com-Iltg-dWatt-Exit | SDG | Rt3 | Ex | IOU | 8.76 | 0.001 | 0 | 10.1 | 0.00135 | -0.0133 | 8.76 | 0.001 | 0 | 10.1 | 0.00135 | -0.0133 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.15 | 1.35 | -0.0015183 | 8760 | 1 | 8760 | 1 | 1.15 | 1.35 | -0.00152
ExitNoneSDGRt3NewCZ06 | Com-Iltg-dWatt-Exit | SDG | Rt3 | New | CZ06 | 8.76 | 0.001 | 0 | 9.74 | 0.00131 | -0.0263 | 8.76 | 0.001 | 0 | 9.74 | 0.00131 | -0.0263 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.11 | 1.31 | -0.0030023 | 8760 | 1 | 8760 | 1 | 1.11 | 1.31 | -0.003
ExitNoneSDGRt3NewCZ07 | Com-Iltg-dWatt-Exit | SDG | Rt3 | New | CZ07 | 8.76 | 0.001 | 0 | 9.86 | 0.00126 | -0.014 | 8.76 | 0.001 | 0 | 9.86 | 0.00126 | -0.014 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.13 | 1.26 | -0.0015982 | 8760 | 1 | 8760 | 1 | 1.13 | 1.26 | -0.0016
ExitNoneSDGRt3NewCZ08 | Com-Iltg-dWatt-Exit | SDG | Rt3 | New | CZ08 | 8.76 | 0.001 | 0 | 9.84 | 0.00128 | -0.0202 | 8.76 | 0.001 | 0 | 9.84 | 0.00128 | -0.0202 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.12 | 1.28 | -0.0023059 | 8760 | 1 | 8760 | 1 | 1.12 | 1.28 | -0.00231
ExitNoneSDGRt3NewCZ10 | Com-Iltg-dWatt-Exit | SDG | Rt3 | New | CZ10 | 8.76 | 0.001 | 0 | 9.64 | 0.00131 | -0.0329 | 8.76 | 0.001 | 0 | 9.64 | 0.00131 | -0.0329 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.1 | 1.31 | -0.0037557 | 8760 | 1 | 8760 | 1 | 1.1 | 1.31 | -0.00376
ExitNoneSDGRt3NewCZ14 | Com-Iltg-dWatt-Exit | SDG | Rt3 | New | CZ14 | 8.76 | 0.001 | 0 | 9.26 | 0.00134 | -0.0697 | 8.76 | 0.001 | 0 | 9.26 | 0.00134 | -0.0697 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.06 | 1.34 | -0.0079566 | 8760 | 1 | 8760 | 1 | 1.06 | 1.34 | -0.00796
ExitNoneSDGRt3NewCZ15 | Com-Iltg-dWatt-Exit | SDG | Rt3 | New | CZ15 | 8.76 | 0.001 | 0 | 10.2 | 0.00144 | -0.00567 | 8.76 | 0.001 | 0 | 10.2 | 0.00144 | -0.00567 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.16 | 1.44 | -0.00064726 | 8760 | 1 | 8760 | 1 | 1.16 | 1.44 | -0.000647
ExitNoneSDGRt3NewIOU | Com-Iltg-dWatt-Exit | SDG | Rt3 | New | IOU | 8.76 | 0.001 | 0 | 9.8 | 0.00128 | -0.0195 | 8.76 | 0.001 | 0 | 9.8 | 0.00128 | -0.0195 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.12 | 1.28 | -0.002226 | 8760 | 1 | 8760 | 1 | 1.12 | 1.28 | -0.00223
ExitNoneSDGRtLExCZ06 | Com-Iltg-dWatt-Exit | SDG | RtL | Ex | CZ06 | 8.76 | 0.001 | 0 | 9.7 | 0.00133 | -0.0339 | 8.76 | 0.001 | 0 | 9.7 | 0.00133 | -0.0339 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.11 | 1.33 | -0.0038699 | 8760 | 1 | 8760 | 1 | 1.11 | 1.33 | -0.00387
ExitNoneSDGRtLExCZ07 | Com-Iltg-dWatt-Exit | SDG | RtL | Ex | CZ07 | 8.76 | 0.001 | 0 | 9.79 | 0.00133 | -0.0279 | 8.76 | 0.001 | 0 | 9.79 | 0.00133 | -0.0279 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.12 | 1.33 | -0.0031849 | 8760 | 1 | 8760 | 1 | 1.12 | 1.33 | -0.00318
ExitNoneSDGRtLExCZ08 | Com-Iltg-dWatt-Exit | SDG | RtL | Ex | CZ08 | 8.76 | 0.001 | 0 | 9.73 | 0.00133 | -0.0319 | 8.76 | 0.001 | 0 | 9.73 | 0.00133 | -0.0319 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.11 | 1.33 | -0.0036416 | 8760 | 1 | 8760 | 1 | 1.11 | 1.33 | -0.00364
ExitNoneSDGRtLExCZ10 | Com-Iltg-dWatt-Exit | SDG | RtL | Ex | CZ10 | 8.76 | 0.001 | 0 | 9.64 | 0.00135 | -0.0384 | 8.76 | 0.001 | 0 | 9.64 | 0.00135 | -0.0384 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.1 | 1.35 | -0.0043836 | 8760 | 1 | 8760 | 1 | 1.1 | 1.35 | -0.00438
ExitNoneSDGRtLExCZ14 | Com-Iltg-dWatt-Exit | SDG | RtL | Ex | CZ14 | 8.76 | 0.001 | 0 | 9.36 | 0.00137 | -0.0632 | 8.76 | 0.001 | 0 | 9.36 | 0.00137 | -0.0632 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.07 | 1.37 | -0.0072146 | 8760 | 1 | 8760 | 1 | 1.07 | 1.37 | -0.00721
ExitNoneSDGRtLExCZ15 | Com-Iltg-dWatt-Exit | SDG | RtL | Ex | CZ15 | 8.76 | 0.001 | 0 | 10.1 | 0.00137 | -0.0152 | 8.76 | 0.001 | 0 | 10.1 | 0.00137 | -0.0152 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.15 | 1.37 | -0.0017352 | 8760 | 1 | 8760 | 1 | 1.15 | 1.37 | -0.00174
ExitNoneSDGRtLExIOU | Com-Iltg-dWatt-Exit | SDG | RtL | Ex | IOU | 8.76 | 0.001 | 0 | 9.74 | 0.00133 | -0.031 | 8.76 | 0.001 | 0 | 9.74 | 0.00133 | -0.031 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.11 | 1.33 | -0.0035388 | 8760 | 1 | 8760 | 1 | 1.11 | 1.33 | -0.00354
ExitNoneSDGRtLNewCZ06 | Com-Iltg-dWatt-Exit | SDG | RtL | New | CZ06 | 8.76 | 0.001 | 0 | 9.43 | 0.00133 | -0.0406 | 8.76 | 0.001 | 0 | 9.43 | 0.00133 | -0.0406 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.08 | 1.33 | -0.0046347 | 8760 | 1 | 8760 | 1 | 1.08 | 1.33 | -0.00463
ExitNoneSDGRtLNewCZ07 | Com-Iltg-dWatt-Exit | SDG | RtL | New | CZ07 | 8.76 | 0.001 | 0 | 9.47 | 0.00133 | -0.0326 | 8.76 | 0.001 | 0 | 9.47 | 0.00133 | -0.0326 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.08 | 1.33 | -0.0037215 | 8760 | 1 | 8760 | 1 | 1.08 | 1.33 | -0.00372
ExitNoneSDGRtLNewCZ08 | Com-Iltg-dWatt-Exit | SDG | RtL | New | CZ08 | 8.76 | 0.001 | 0 | 9.55 | 0.00136 | -0.0312 | 8.76 | 0.001 | 0 | 9.55 | 0.00136 | -0.0312 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.09 | 1.36 | -0.0035616 | 8760 | 1 | 8760 | 1 | 1.09 | 1.36 | -0.00356
ExitNoneSDGRtLNewCZ10 | Com-Iltg-dWatt-Exit | SDG | RtL | New | CZ10 | 8.76 | 0.001 | 0 | 9.61 | 0.00142 | -0.0456 | 8.76 | 0.001 | 0 | 9.61 | 0.00142 | -0.0456 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.1 | 1.42 | -0.0052055 | 8760 | 1 | 8760 | 1 | 1.1 | 1.42 | -0.00521
ExitNoneSDGRtLNewCZ14 | Com-Iltg-dWatt-Exit | SDG | RtL | New | CZ14 | 8.76 | 0.001 | 0 | 9.34 | 0.00141 | -0.0733 | 8.76 | 0.001 | 0 | 9.34 | 0.00141 | -0.0733 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.07 | 1.41 | -0.0083676 | 8760 | 1 | 8760 | 1 | 1.07 | 1.41 | -0.00837
ExitNoneSDGRtLNewCZ15 | Com-Iltg-dWatt-Exit | SDG | RtL | New | CZ15 | 8.76 | 0.001 | 0 | 10.2 | 0.00145 | -0.017 | 8.76 | 0.001 | 0 | 10.2 | 0.00145 | -0.017 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.16 | 1.45 | -0.0019406 | 8760 | 1 | 8760 | 1 | 1.16 | 1.45 | -0.00194
ExitNoneSDGRtLNewIOU | Com-Iltg-dWatt-Exit | SDG | RtL | New | IOU | 8.76 | 0.001 | 0 | 9.5 | 0.00135 | -0.036 | 8.76 | 0.001 | 0 | 9.5 | 0.00135 | -0.036 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.08 | 1.35 | -0.0041096 | 8760 | 1 | 8760 | 1 | 1.08 | 1.35 | -0.00411
ExitNoneSDGRtSExCZ06 | Com-Iltg-dWatt-Exit | SDG | RtS | Ex | CZ06 | 8.76 | 0.001 | 0 | 9.63 | 0.00134 | -0.0275 | 8.76 | 0.001 | 0 | 9.63 | 0.00134 | -0.0275 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.1 | 1.34 | -0.0031393 | 8760 | 1 | 8760 | 1 | 1.1 | 1.34 | -0.00314
ExitNoneSDGRtSExCZ07 | Com-Iltg-dWatt-Exit | SDG | RtS | Ex | CZ07 | 8.76 | 0.001 | 0 | 9.7 | 0.0013 | -0.0198 | 8.76 | 0.001 | 0 | 9.7 | 0.0013 | -0.0198 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.11 | 1.3 | -0.0022603 | 8760 | 1 | 8760 | 1 | 1.11 | 1.3 | -0.00226
ExitNoneSDGRtSExCZ08 | Com-Iltg-dWatt-Exit | SDG | RtS | Ex | CZ08 | 8.76 | 0.001 | 0 | 9.71 | 0.00135 | -0.0242 | 8.76 | 0.001 | 0 | 9.71 | 0.00135 | -0.0242 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.11 | 1.35 | -0.0027626 | 8760 | 1 | 8760 | 1 | 1.11 | 1.35 | -0.00276
ExitNoneSDGRtSExCZ10 | Com-Iltg-dWatt-Exit | SDG | RtS | Ex | CZ10 | 8.76 | 0.001 | 0 | 9.63 | 0.00136 | -0.0311 | 8.76 | 0.001 | 0 | 9.63 | 0.00136 | -0.0311 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.1 | 1.36 | -0.0035502 | 8760 | 1 | 8760 | 1 | 1.1 | 1.36 | -0.00355
ExitNoneSDGRtSExCZ14 | Com-Iltg-dWatt-Exit | SDG | RtS | Ex | CZ14 | 8.76 | 0.001 | 0 | 9.37 | 0.00136 | -0.0556 | 8.76 | 0.001 | 0 | 9.37 | 0.00136 | -0.0556 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.07 | 1.36 | -0.006347 | 8760 | 1 | 8760 | 1 | 1.07 | 1.36 | -0.00635
ExitNoneSDGRtSExCZ15 | Com-Iltg-dWatt-Exit | SDG | RtS | Ex | CZ15 | 8.76 | 0.001 | 0 | 10.2 | 0.00133 | -0.0108 | 8.76 | 0.001 | 0 | 10.2 | 0.00133 | -0.0108 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.16 | 1.33 | -0.0012329 | 8760 | 1 | 8760 | 1 | 1.16 | 1.33 | -0.00123
ExitNoneSDGRtSExIOU | Com-Iltg-dWatt-Exit | SDG | RtS | Ex | IOU | 8.76 | 0.001 | 0 | 9.68 | 0.00132 | -0.0231 | 8.76 | 0.001 | 0 | 9.68 | 0.00132 | -0.0231 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.11 | 1.32 | -0.002637 | 8760 | 1 | 8760 | 1 | 1.11 | 1.32 | -0.00264
ExitNoneSDGRtSNewCZ06 | Com-Iltg-dWatt-Exit | SDG | RtS | New | CZ06 | 8.76 | 0.001 | 0 | 9.43 | 0.00132 | -0.0329 | 8.76 | 0.001 | 0 | 9.43 | 0.00132 | -0.0329 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.08 | 1.32 | -0.0037557 | 8760 | 1 | 8760 | 1 | 1.08 | 1.32 | -0.00376
ExitNoneSDGRtSNewCZ07 | Com-Iltg-dWatt-Exit | SDG | RtS | New | CZ07 | 8.76 | 0.001 | 0 | 9.39 | 0.00131 | -0.0278 | 8.76 | 0.001 | 0 | 9.39 | 0.00131 | -0.0278 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.07 | 1.31 | -0.0031735 | 8760 | 1 | 8760 | 1 | 1.07 | 1.31 | -0.00317
ExitNoneSDGRtSNewCZ08 | Com-Iltg-dWatt-Exit | SDG | RtS | New | CZ08 | 8.76 | 0.001 | 0 | 9.49 | 0.00135 | -0.0276 | 8.76 | 0.001 | 0 | 9.49 | 0.00135 | -0.0276 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.08 | 1.35 | -0.0031507 | 8760 | 1 | 8760 | 1 | 1.08 | 1.35 | -0.00315
ExitNoneSDGRtSNewCZ10 | Com-Iltg-dWatt-Exit | SDG | RtS | New | CZ10 | 8.76 | 0.001 | 0 | 9.57 | 0.00142 | -0.04 | 8.76 | 0.001 | 0 | 9.57 | 0.00142 | -0.04 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.09 | 1.42 | -0.0045662 | 8760 | 1 | 8760 | 1 | 1.09 | 1.42 | -0.00457
ExitNoneSDGRtSNewCZ14 | Com-Iltg-dWatt-Exit | SDG | RtS | New | CZ14 | 8.76 | 0.001 | 0 | 9.37 | 0.00141 | -0.06 | 8.76 | 0.001 | 0 | 9.37 | 0.00141 | -0.06 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.07 | 1.41 | -0.0068493 | 8760 | 1 | 8760 | 1 | 1.07 | 1.41 | -0.00685
ExitNoneSDGRtSNewCZ15 | Com-Iltg-dWatt-Exit | SDG | RtS | New | CZ15 | 8.76 | 0.001 | 0 | 10 | 0.00145 | -0.00528 | 8.76 | 0.001 | 0 | 10 | 0.00145 | -0.00528 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.14 | 1.45 | -0.00060274 | 8760 | 1 | 8760 | 1 | 1.14 | 1.45 | -0.000603
ExitNoneSDGRtSNewIOU | Com-Iltg-dWatt-Exit | SDG | RtS | New | IOU | 8.76 | 0.001 | 0 | 9.44 | 0.00134 | -0.031 | 8.76 | 0.001 | 0 | 9.44 | 0.00134 | -0.031 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.08 | 1.34 | -0.0035388 | 8760 | 1 | 8760 | 1 | 1.08 | 1.34 | -0.00354
ExitNoneSDGSCnExCZ06 | Com-Iltg-dWatt-Exit | SDG | SCn | Ex | CZ06 | 8.76 | 0.001 | 0 | 8.91 | 0.00144 | -0.0515 | 8.76 | 0.001 | 0 | 8.91 | 0.00144 | -0.0515 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.02 | 1.44 | -0.005879 | 8760 | 1 | 8760 | 1 | 1.02 | 1.44 | -0.00588
ExitNoneSDGSCnExCZ07 | Com-Iltg-dWatt-Exit | SDG | SCn | Ex | CZ07 | 8.76 | 0.001 | 0 | 8.8 | 0.00146 | -0.046 | 8.76 | 0.001 | 0 | 8.8 | 0.00146 | -0.046 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1 | 1.46 | -0.0052511 | 8760 | 1 | 8760 | 1 | 1 | 1.46 | -0.00525
ExitNoneSDGSCnExCZ08 | Com-Iltg-dWatt-Exit | SDG | SCn | Ex | CZ08 | 8.76 | 0.001 | 0 | 9.02 | 0.00143 | -0.0419 | 8.76 | 0.001 | 0 | 9.02 | 0.00143 | -0.0419 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.03 | 1.43 | -0.0047831 | 8760 | 1 | 8760 | 1 | 1.03 | 1.43 | -0.00478
ExitNoneSDGSCnExCZ10 | Com-Iltg-dWatt-Exit | SDG | SCn | Ex | CZ10 | 8.76 | 0.001 | 0 | 9.07 | 0.00146 | -0.0492 | 8.76 | 0.001 | 0 | 9.07 | 0.00146 | -0.0492 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.04 | 1.46 | -0.0056164 | 8760 | 1 | 8760 | 1 | 1.04 | 1.46 | -0.00562
ExitNoneSDGSCnExCZ14 | Com-Iltg-dWatt-Exit | SDG | SCn | Ex | CZ14 | 8.76 | 0.001 | 0 | 8.72 | 0.00141 | -0.0732 | 8.76 | 0.001 | 0 | 8.72 | 0.00141 | -0.0732 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.995 | 1.41 | -0.0083562 | 8760 | 1 | 8760 | 1 | 0.995 | 1.41 | -0.00836
ExitNoneSDGSCnExCZ15 | Com-Iltg-dWatt-Exit | SDG | SCn | Ex | CZ15 | 8.76 | 0.001 | 0 | 9.75 | 0.00142 | -0.0212 | 8.76 | 0.001 | 0 | 9.75 | 0.00142 | -0.0212 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.11 | 1.42 | -0.0024201 | 8760 | 1 | 8760 | 1 | 1.11 | 1.42 | -0.00242
ExitNoneSDGSCnExIOU | Com-Iltg-dWatt-Exit | SDG | SCn | Ex | IOU | 8.76 | 0.001 | 0 | 8.89 | 0.00146 | -0.047 | 8.76 | 0.001 | 0 | 8.89 | 0.00146 | -0.047 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.01 | 1.46 | -0.0053653 | 8760 | 1 | 8760 | 1 | 1.01 | 1.46 | -0.00537
ExitNoneSDGSCnNewCZ06 | Com-Iltg-dWatt-Exit | SDG | SCn | New | CZ06 | 8.76 | 0.001 | 0 | 8.83 | 0.00134 | -0.0583 | 8.76 | 0.001 | 0 | 8.83 | 0.00134 | -0.0583 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.01 | 1.34 | -0.0066553 | 8760 | 1 | 8760 | 1 | 1.01 | 1.34 | -0.00666
ExitNoneSDGSCnNewCZ07 | Com-Iltg-dWatt-Exit | SDG | SCn | New | CZ07 | 8.76 | 0.001 | 0 | 8.64 | 0.00137 | -0.0532 | 8.76 | 0.001 | 0 | 8.64 | 0.00137 | -0.0532 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.986 | 1.37 | -0.0060731 | 8760 | 1 | 8760 | 1 | 0.986 | 1.37 | -0.00607
ExitNoneSDGSCnNewCZ08 | Com-Iltg-dWatt-Exit | SDG | SCn | New | CZ08 | 8.76 | 0.001 | 0 | 8.9 | 0.00133 | -0.0425 | 8.76 | 0.001 | 0 | 8.9 | 0.00133 | -0.0425 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.02 | 1.33 | -0.0048516 | 8760 | 1 | 8760 | 1 | 1.02 | 1.33 | -0.00485
ExitNoneSDGSCnNewCZ10 | Com-Iltg-dWatt-Exit | SDG | SCn | New | CZ10 | 8.76 | 0.001 | 0 | 9 | 0.00138 | -0.0576 | 8.76 | 0.001 | 0 | 9 | 0.00138 | -0.0576 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.03 | 1.38 | -0.0065753 | 8760 | 1 | 8760 | 1 | 1.03 | 1.38 | -0.00658
ExitNoneSDGSCnNewCZ14 | Com-Iltg-dWatt-Exit | SDG | SCn | New | CZ14 | 8.76 | 0.001 | 0 | 8.73 | 0.00136 | -0.0779 | 8.76 | 0.001 | 0 | 8.73 | 0.00136 | -0.0779 |  | Exit | None | 8760 | 1 | 8760 | 1 | 0.997 | 1.36 | -0.0088927 | 8760 | 1 | 8760 | 1 | 0.997 | 1.36 | -0.00889
ExitNoneSDGSCnNewCZ15 | Com-Iltg-dWatt-Exit | SDG | SCn | New | CZ15 | 8.76 | 0.001 | 0 | 9.36 | 0.00138 | -0.0185 | 8.76 | 0.001 | 0 | 9.36 | 0.00138 | -0.0185 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.07 | 1.38 | -0.0021119 | 8760 | 1 | 8760 | 1 | 1.07 | 1.38 | -0.00211
ExitNoneSDGSCnNewIOU | Com-Iltg-dWatt-Exit | SDG | SCn | New | IOU | 8.76 | 0.001 | 0 | 8.76 | 0.00137 | -0.0545 | 8.76 | 0.001 | 0 | 8.76 | 0.00137 | -0.0545 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1 | 1.37 | -0.0062215 | 8760 | 1 | 8760 | 1 | 1 | 1.37 | -0.00622
ExitNoneSDGSUnExCZ06 | Com-Iltg-dWatt-Exit | SDG | SUn | Ex | CZ06 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1 | 1 | 0 | 8760 | 1 | 8760 | 1 | 1 | 1 | 0
ExitNoneSDGSUnExCZ07 | Com-Iltg-dWatt-Exit | SDG | SUn | Ex | CZ07 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1 | 1 | 0 | 8760 | 1 | 8760 | 1 | 1 | 1 | 0
ExitNoneSDGSUnExCZ08 | Com-Iltg-dWatt-Exit | SDG | SUn | Ex | CZ08 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1 | 1 | 0 | 8760 | 1 | 8760 | 1 | 1 | 1 | 0
ExitNoneSDGSUnExCZ10 | Com-Iltg-dWatt-Exit | SDG | SUn | Ex | CZ10 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1 | 1 | 0 | 8760 | 1 | 8760 | 1 | 1 | 1 | 0
ExitNoneSDGSUnExCZ14 | Com-Iltg-dWatt-Exit | SDG | SUn | Ex | CZ14 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1 | 1 | 0 | 8760 | 1 | 8760 | 1 | 1 | 1 | 0
ExitNoneSDGSUnExCZ15 | Com-Iltg-dWatt-Exit | SDG | SUn | Ex | CZ15 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1 | 1 | 0 | 8760 | 1 | 8760 | 1 | 1 | 1 | 0
ExitNoneSDGSUnExIOU | Com-Iltg-dWatt-Exit | SDG | SUn | Ex | IOU | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1 | 1 | 0 | 8760 | 1 | 8760 | 1 | 1 | 1 | 0
ExitNoneSDGSUnNewCZ06 | Com-Iltg-dWatt-Exit | SDG | SUn | New | CZ06 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1 | 1 | 0 | 8760 | 1 | 8760 | 1 | 1 | 1 | 0
ExitNoneSDGSUnNewCZ07 | Com-Iltg-dWatt-Exit | SDG | SUn | New | CZ07 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1 | 1 | 0 | 8760 | 1 | 8760 | 1 | 1 | 1 | 0
ExitNoneSDGSUnNewCZ08 | Com-Iltg-dWatt-Exit | SDG | SUn | New | CZ08 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1 | 1 | 0 | 8760 | 1 | 8760 | 1 | 1 | 1 | 0
ExitNoneSDGSUnNewCZ10 | Com-Iltg-dWatt-Exit | SDG | SUn | New | CZ10 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1 | 1 | 0 | 8760 | 1 | 8760 | 1 | 1 | 1 | 0
ExitNoneSDGSUnNewCZ14 | Com-Iltg-dWatt-Exit | SDG | SUn | New | CZ14 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1 | 1 | 0 | 8760 | 1 | 8760 | 1 | 1 | 1 | 0
ExitNoneSDGSUnNewCZ15 | Com-Iltg-dWatt-Exit | SDG | SUn | New | CZ15 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1 | 1 | 0 | 8760 | 1 | 8760 | 1 | 1 | 1 | 0
ExitNoneSDGSUnNewIOU | Com-Iltg-dWatt-Exit | SDG | SUn | New | IOU | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 | 8.76 | 0.001 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1 | 1 | 0 | 8760 | 1 | 8760 | 1 | 1 | 1 | 0
ExitNoneSDGWRfExCZ06 | Com-Iltg-dWatt-Exit | SDG | WRf | Ex | CZ06 | 8.76 | 0.001 | 0 | 13.3 | 0.00128 | 0 | 8.76 | 0.001 | 0 | 13.3 | 0.00128 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.52 | 1.28 | 0 | 8760 | 1 | 8760 | 1 | 1.52 | 1.28 | 0
ExitNoneSDGWRfExCZ07 | Com-Iltg-dWatt-Exit | SDG | WRf | Ex | CZ07 | 8.76 | 0.001 | 0 | 13.9 | 0.00124 | 0 | 8.76 | 0.001 | 0 | 13.9 | 0.00124 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.59 | 1.24 | 0 | 8760 | 1 | 8760 | 1 | 1.59 | 1.24 | 0
ExitNoneSDGWRfExCZ08 | Com-Iltg-dWatt-Exit | SDG | WRf | Ex | CZ08 | 8.76 | 0.001 | 0 | 13.4 | 0.00126 | 0 | 8.76 | 0.001 | 0 | 13.4 | 0.00126 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.53 | 1.26 | 0 | 8760 | 1 | 8760 | 1 | 1.53 | 1.26 | 0
ExitNoneSDGWRfExCZ10 | Com-Iltg-dWatt-Exit | SDG | WRf | Ex | CZ10 | 8.76 | 0.001 | 0 | 14.2 | 0.00124 | 0 | 8.76 | 0.001 | 0 | 14.2 | 0.00124 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.62 | 1.24 | 0 | 8760 | 1 | 8760 | 1 | 1.62 | 1.24 | 0
ExitNoneSDGWRfExCZ14 | Com-Iltg-dWatt-Exit | SDG | WRf | Ex | CZ14 | 8.76 | 0.001 | 0 | 12.4 | 0.00124 | 0 | 8.76 | 0.001 | 0 | 12.4 | 0.00124 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.42 | 1.24 | 0 | 8760 | 1 | 8760 | 1 | 1.42 | 1.24 | 0
ExitNoneSDGWRfExCZ15 | Com-Iltg-dWatt-Exit | SDG | WRf | Ex | CZ15 | 8.76 | 0.001 | 0 | 14.3 | 0.00126 | 0 | 8.76 | 0.001 | 0 | 14.3 | 0.00126 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.63 | 1.26 | 0 | 8760 | 1 | 8760 | 1 | 1.63 | 1.26 | 0
ExitNoneSDGWRfExIOU | Com-Iltg-dWatt-Exit | SDG | WRf | Ex | IOU | 8.76 | 0.001 | 0 | 13.9 | 0.00124 | 0 | 8.76 | 0.001 | 0 | 13.9 | 0.00124 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.59 | 1.24 | 0 | 8760 | 1 | 8760 | 1 | 1.59 | 1.24 | 0
ExitNoneSDGWRfNewCZ06 | Com-Iltg-dWatt-Exit | SDG | WRf | New | CZ06 | 8.76 | 0.001 | 0 | 13.3 | 0.00126 | 0 | 8.76 | 0.001 | 0 | 13.3 | 0.00126 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.52 | 1.26 | 0 | 8760 | 1 | 8760 | 1 | 1.52 | 1.26 | 0
ExitNoneSDGWRfNewCZ07 | Com-Iltg-dWatt-Exit | SDG | WRf | New | CZ07 | 8.76 | 0.001 | 0 | 12.2 | 0.00121 | 0 | 8.76 | 0.001 | 0 | 12.2 | 0.00121 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.39 | 1.21 | 0 | 8760 | 1 | 8760 | 1 | 1.39 | 1.21 | 0
ExitNoneSDGWRfNewCZ08 | Com-Iltg-dWatt-Exit | SDG | WRf | New | CZ08 | 8.76 | 0.001 | 0 | 13.5 | 0.00126 | 0 | 8.76 | 0.001 | 0 | 13.5 | 0.00126 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.54 | 1.26 | 0 | 8760 | 1 | 8760 | 1 | 1.54 | 1.26 | 0
ExitNoneSDGWRfNewCZ10 | Com-Iltg-dWatt-Exit | SDG | WRf | New | CZ10 | 8.76 | 0.001 | 0 | 12.3 | 0.00122 | 0 | 8.76 | 0.001 | 0 | 12.3 | 0.00122 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.4 | 1.22 | 0 | 8760 | 1 | 8760 | 1 | 1.4 | 1.22 | 0
ExitNoneSDGWRfNewCZ14 | Com-Iltg-dWatt-Exit | SDG | WRf | New | CZ14 | 8.76 | 0.001 | 0 | 11.3 | 0.00124 | 0 | 8.76 | 0.001 | 0 | 11.3 | 0.00124 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.29 | 1.24 | 0 | 8760 | 1 | 8760 | 1 | 1.29 | 1.24 | 0
ExitNoneSDGWRfNewCZ15 | Com-Iltg-dWatt-Exit | SDG | WRf | New | CZ15 | 8.76 | 0.001 | 0 | 13.2 | 0.00127 | 0 | 8.76 | 0.001 | 0 | 13.2 | 0.00127 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.51 | 1.27 | 0 | 8760 | 1 | 8760 | 1 | 1.51 | 1.27 | 0
ExitNoneSDGWRfNewIOU | Com-Iltg-dWatt-Exit | SDG | WRf | New | IOU | 8.76 | 0.001 | 0 | 12.2 | 0.00121 | 0 | 8.76 | 0.001 | 0 | 12.2 | 0.00121 | 0 |  | Exit | None | 8760 | 1 | 8760 | 1 | 1.39 | 1.21 | 0 | 8760 | 1 | 8760 | 1 | 1.39 | 1.21 | 0
LFBldgPGEAsmExCZ01 | Com-Iltg-dWatt-LF_OSbldg | PGE | Asm | Ex | CZ01 | 2.607 | 0.00053144 | 0 | 2.477 | 0.00060734 | -0.050039 | 2.531 | 0.0005191 | 0 | 2.4105 | 0.0005931 | -0.04871 |  | LF | Bldg | 2610 | 0.531 | 2530 | 0.519 | 0.952 | 1.14 | -0.019245 | 2610 | 0.531 | 2530 | 0.519 | 0.952 | 1.14 | -0.0192
LFBldgPGEAsmExCZ02 | Com-Iltg-dWatt-LF_OSbldg | PGE | Asm | Ex | CZ02 | 2.6076 | 0.00053156 | 0 | 2.6972 | 0.00061948 | -0.028172 | 2.5308 | 0.00051908 | 0 | 2.6204 | 0.00060508 | -0.027404 |  | LF | Bldg | 2610 | 0.532 | 2530 | 0.519 | 1.04 | 1.17 | -0.010828 | 2610 | 0.532 | 2530 | 0.519 | 1.04 | 1.17 | -0.0108
LFBldgPGEAsmExCZ03 | Com-Iltg-dWatt-LF_OSbldg | PGE | Asm | Ex | CZ03 | 2.6081 | 0.00053166 | 0 | 2.6681 | 0.00062059 | -0.031075 | 2.5306 | 0.00051906 | 0 | 2.6003 | 0.00060606 | -0.030203 |  | LF | Bldg | 2610 | 0.532 | 2530 | 0.519 | 1.03 | 1.17 | -0.011935 | 2610 | 0.532 | 2530 | 0.519 | 1.03 | 1.17 | -0.0119
LFBldgPGEAsmExCZ04 | Com-Iltg-dWatt-LF_OSbldg | PGE | Asm | Ex | CZ04 | 2.6074 | 0.00053151 | 0 | 2.7369 | 0.00061847 | -0.023178 | 2.5309 | 0.00051909 | 0 | 2.6604 | 0.00060509 | -0.022604 |  | LF | Bldg | 2610 | 0.532 | 2530 | 0.519 | 1.05 | 1.17 | -0.0089314 | 2610 | 0.532 | 2530 | 0.519 | 1.05 | 1.17 | -0.00893
LFBldgPGEAsmExCZ05 | Com-Iltg-dWatt-LF_OSbldg | PGE | Asm | Ex | CZ05 | 2.6074 | 0.00053151 | 0 | 2.6869 | 0.00060947 | -0.027869 | 2.5309 | 0.00051909 | 0 | 2.6104 | 0.00059609 | -0.027104 |  | LF | Bldg | 2610 | 0.532 | 2530 | 0.519 | 1.03 | 1.15 | -0.010709 | 2610 | 0.532 | 2530 | 0.519 | 1.03 | 1.15 | -0.0107
LFBldgPGEAsmExCZ11 | Com-Iltg-dWatt-LF_OSbldg | PGE | Asm | Ex | CZ11 | 2.6061 | 0.00053128 | 0 | 2.7354 | 0.00061815 | -0.024361 | 2.5313 | 0.00051913 | 0 | 2.6607 | 0.00060413 | -0.023707 |  | LF | Bldg | 2610 | 0.531 | 2530 | 0.519 | 1.05 | 1.16 | -0.0093653 | 2610 | 0.531 | 2530 | 0.519 | 1.05 | 1.16 | -0.00937
LFBldgPGEAsmExCZ12 | Com-Iltg-dWatt-LF_OSbldg | PGE | Asm | Ex | CZ12 | 2.6067 | 0.0005314 | 0 | 2.7167 | 0.00062329 | -0.025762 | 2.5311 | 0.00051911 | 0 | 2.6411 | 0.00060911 | -0.025005 |  | LF | Bldg | 2610 | 0.531 | 2530 | 0.519 | 1.04 | 1.17 | -0.0098793 | 2610 | 0.531 | 2530 | 0.519 | 1.04 | 1.17 | -0.00988
LFBldgPGEAsmExCZ13 | Com-Iltg-dWatt-LF_OSbldg | PGE | Asm | Ex | CZ13 | 2.6062 | 0.00053131 | 0 | 2.7362 | 0.00061725 | -0.023662 | 2.5312 | 0.00051913 | 0 | 2.6613 | 0.00060412 | -0.023006 |  | LF | Bldg | 2610 | 0.531 | 2530 | 0.519 | 1.05 | 1.16 | -0.0090889 | 2610 | 0.531 | 2530 | 0.519 | 1.05 | 1.16 | -0.00909
LFBldgPGEAsmExCZ16 | Com-Iltg-dWatt-LF_OSbldg | PGE | Asm | Ex | CZ16 | 2.6066 | 0.00053137 | 0 | 2.546 | 0.00060931 | -0.037249 | 2.5311 | 0.00051911 | 0 | 2.4706 | 0.00059611 | -0.036211 |  | LF | Bldg | 2610 | 0.531 | 2530 | 0.519 | 0.976 | 1.15 | -0.014306 | 2610 | 0.531 | 2530 | 0.519 | 0.976 | 1.15 | -0.0143
LFBldgPGEAsmExIOU | Com-Iltg-dWatt-LF_OSbldg | PGE | Asm | Ex | IOU | 2.6073 | 0.00053151 | 0 | 2.7015 | 0.00061966 | -0.0273 | 2.5309 | 0.00051909 | 0 | 2.6284 | 0.00060566 | -0.026547 |  | LF | Bldg | 2610 | 0.532 | 2530 | 0.519 | 1.04 | 1.17 | -0.010489 | 2610 | 0.532 | 2530 | 0.519 | 1.04 | 1.17 | -0.0105
LFBldgPGEAsmNewCZ01 | Com-Iltg-dWatt-LF_OSbldg | PGE | Asm | New | CZ01 | 2.55 | 0.000521 | 0 | 2.43 | 0.000599 | -0.0484 | 2.55 | 0.000521 | 0 | 2.43 | 0.000599 | -0.0484 |  | LF | Bldg | 2550 | 0.521 | 2550 | 0.521 | 0.953 | 1.15 | -0.01898 | 2550 | 0.521 | 2550 | 0.521 | 0.953 | 1.15 | -0.019
LFBldgPGEAsmNewCZ02 | Com-Iltg-dWatt-LF_OSbldg | PGE | Asm | New | CZ02 | 2.55 | 0.000521 | 0 | 2.59 | 0.000611 | -0.03 | 2.55 | 0.000521 | 0 | 2.59 | 0.000611 | -0.03 |  | LF | Bldg | 2550 | 0.521 | 2550 | 0.521 | 1.02 | 1.17 | -0.011765 | 2550 | 0.521 | 2550 | 0.521 | 1.02 | 1.17 | -0.0118
LFBldgPGEAsmNewCZ03 | Com-Iltg-dWatt-LF_OSbldg | PGE | Asm | New | CZ03 | 2.55 | 0.000521 | 0 | 2.57 | 0.000602 | -0.0318 | 2.55 | 0.000521 | 0 | 2.57 | 0.000602 | -0.0318 |  | LF | Bldg | 2550 | 0.521 | 2550 | 0.521 | 1.01 | 1.16 | -0.012471 | 2550 | 0.521 | 2550 | 0.521 | 1.01 | 1.16 | -0.0125
LFBldgPGEAsmNewCZ04 | Com-Iltg-dWatt-LF_OSbldg | PGE | Asm | New | CZ04 | 2.55 | 0.000521 | 0 | 2.64 | 0.000608 | -0.0249 | 2.55 | 0.000521 | 0 | 2.64 | 0.000608 | -0.0249 |  | LF | Bldg | 2550 | 0.521 | 2550 | 0.521 | 1.04 | 1.17 | -0.0097647 | 2550 | 0.521 | 2550 | 0.521 | 1.04 | 1.17 | -0.00976
LFBldgPGEAsmNewCZ05 | Com-Iltg-dWatt-LF_OSbldg | PGE | Asm | New | CZ05 | 2.55 | 0.000521 | 0 | 2.6 | 0.000595 | -0.0277 | 2.55 | 0.000521 | 0 | 2.6 | 0.000595 | -0.0277 |  | LF | Bldg | 2550 | 0.521 | 2550 | 0.521 | 1.02 | 1.14 | -0.010863 | 2550 | 0.521 | 2550 | 0.521 | 1.02 | 1.14 | -0.0109
LFBldgPGEAsmNewCZ11 | Com-Iltg-dWatt-LF_OSbldg | PGE | Asm | New | CZ11 | 2.55 | 0.000521 | 0 | 2.66 | 0.000618 | -0.0257 | 2.55 | 0.000521 | 0 | 2.66 | 0.000618 | -0.0257 |  | LF | Bldg | 2550 | 0.521 | 2550 | 0.521 | 1.04 | 1.19 | -0.010078 | 2550 | 0.521 | 2550 | 0.521 | 1.04 | 1.19 | -0.0101
LFBldgPGEAsmNewCZ12 | Com-Iltg-dWatt-LF_OSbldg | PGE | Asm | New | CZ12 | 2.55 | 0.000521 | 0 | 2.64 | 0.000617 | -0.0275 | 2.55 | 0.000521 | 0 | 2.64 | 0.000617 | -0.0275 |  | LF | Bldg | 2550 | 0.521 | 2550 | 0.521 | 1.04 | 1.18 | -0.010784 | 2550 | 0.521 | 2550 | 0.521 | 1.04 | 1.18 | -0.0108
LFBldgPGEAsmNewCZ13 | Com-Iltg-dWatt-LF_OSbldg | PGE | Asm | New | CZ13 | 2.55 | 0.000521 | 0 | 2.66 | 0.000617 | -0.0249 | 2.55 | 0.000521 | 0 | 2.66 | 0.000617 | -0.0249 |  | LF | Bldg | 2550 | 0.521 | 2550 | 0.521 | 1.04 | 1.18 | -0.0097647 | 2550 | 0.521 | 2550 | 0.521 | 1.04 | 1.18 | -0.00976
LFBldgPGEAsmNewCZ16 | Com-Iltg-dWatt-LF_OSbldg | PGE | Asm | New | CZ16 | 2.55 | 0.000521 | 0 | 2.5 | 0.000599 | -0.0367 | 2.55 | 0.000521 | 0 | 2.5 | 0.000599 | -0.0367 |  | LF | Bldg | 2550 | 0.521 | 2550 | 0.521 | 0.98 | 1.15 | -0.014392 | 2550 | 0.521 | 2550 | 0.521 | 0.98 | 1.15 | -0.0144
LFBldgPGEAsmNewIOU | Com-Iltg-dWatt-LF_OSbldg | PGE | Asm | New | IOU | 2.55 | 0.000521 | 0 | 2.6209 | 0.00061069 | -0.027916 | 2.55 | 0.000521 | 0 | 2.6209 | 0.00061069 | -0.027916 |  | LF | Bldg | 2550 | 0.521 | 2550 | 0.521 | 1.03 | 1.17 | -0.010948 | 2550 | 0.521 | 2550 | 0.521 | 1.03 | 1.17 | -0.0109
LFBldgPGEComExCZ01 | Com-Iltg-dWatt-LF_OSbldg | PGE | Com | Ex | CZ01 | 3.1222 | 0.00070422 | 0 | 3.0639 | 0.00081547 | -0.038416 | 3.0219 | 0.00067185 | 0 | 2.9631 | 0.00077721 | -0.037252 |  | LF | Bldg | 3120 | 0.704 | 3020 | 0.672 | 0.981 | 1.16 | -0.012328 | 3120 | 0.704 | 3020 | 0.672 | 0.981 | 1.16 | -0.0123
LFBldgPGEComExCZ02 | Com-Iltg-dWatt-LF_OSbldg | PGE | Com | Ex | CZ02 | 3.2392 | 0.00063338 | 0 | 3.3859 | 0.00076625 | -0.024444 | 3.1552 | 0.00061811 | 0 | 3.2982 | 0.00074783 | -0.023788 |  | LF | Bldg | 3240 | 0.633 | 3160 | 0.618 | 1.05 | 1.21 | -0.0075395 | 3240 | 0.633 | 3160 | 0.618 | 1.05 | 1.21 | -0.00754
LFBldgPGEComExCZ03 | Com-Iltg-dWatt-LF_OSbldg | PGE | Com | Ex | CZ03 | 3.0971 | 0.00064414 | 0 | 3.2629 | 0.00078017 | -0.021751 | 3.0036 | 0.00062516 | 0 | 3.1661 | 0.00075733 | -0.021106 |  | LF | Bldg | 3100 | 0.644 | 3000 | 0.625 | 1.05 | 1.21 | -0.0070267 | 3100 | 0.644 | 3000 | 0.625 | 1.05 | 1.21 | -0.00703
LFBldgPGEComExCZ04 | Com-Iltg-dWatt-LF_OSbldg | PGE | Com | Ex | CZ04 | 3.1014 | 0.00071338 | 0 | 3.319 | 0.00087265 | -0.017597 | 3.0033 | 0.00068741 | 0 | 3.2125 | 0.00083982 | -0.017043 |  | LF | Bldg | 3100 | 0.713 | 3000 | 0.687 | 1.07 | 1.22 | -0.0056747 | 3100 | 0.713 | 3000 | 0.687 | 1.07 | 1.22 | -0.00567
LFBldgPGEComExCZ05 | Com-Iltg-dWatt-LF_OSbldg | PGE | Com | Ex | CZ05 | 3.0426 | 0.00067781 | 0 | 3.2057 | 0.0008093 | -0.022265 | 2.9521 | 0.00064997 | 0 | 3.1088 | 0.00077549 | -0.021619 |  | LF | Bldg | 3040 | 0.678 | 2950 | 0.65 | 1.05 | 1.19 | -0.0073232 | 3040 | 0.678 | 2950 | 0.65 | 1.05 | 1.19 | -0.00732
LFBldgPGEComExCZ11 | Com-Iltg-dWatt-LF_OSbldg | PGE | Com | Ex | CZ11 | 3.2619 | 0.00062603 | 0 | 3.4644 | 0.00075593 | -0.022108 | 3.1728 | 0.0006093 | 0 | 3.368 | 0.00073538 | -0.021489 |  | LF | Bldg | 3260 | 0.626 | 3170 | 0.609 | 1.06 | 1.21 | -0.0067728 | 3260 | 0.626 | 3170 | 0.609 | 1.06 | 1.21 | -0.00677
LFBldgPGEComExCZ12 | Com-Iltg-dWatt-LF_OSbldg | PGE | Com | Ex | CZ12 | 3.2582 | 0.00064985 | 0 | 3.4567 | 0.00078568 | -0.021428 | 3.17 | 0.0006336 | 0 | 3.3618 | 0.00076518 | -0.020822 |  | LF | Bldg | 3260 | 0.65 | 3170 | 0.634 | 1.06 | 1.21 | -0.0065686 | 3260 | 0.65 | 3170 | 0.634 | 1.06 | 1.21 | -0.00657
LFBldgPGEComExCZ13 | Com-Iltg-dWatt-LF_OSbldg | PGE | Com | Ex | CZ13 | 3.2783 | 0.0006314 | 0 | 3.5467 | 0.00076016 | -0.019674 | 3.1827 | 0.00061422 | 0 | 3.4422 | 0.00073921 | -0.019095 |  | LF | Bldg | 3280 | 0.631 | 3180 | 0.614 | 1.08 | 1.2 | -0.0059996 | 3280 | 0.631 | 3180 | 0.614 | 1.08 | 1.2 | -0.006
LFBldgPGEComExCZ16 | Com-Iltg-dWatt-LF_OSbldg | PGE | Com | Ex | CZ16 | 3.1123 | 0.00059081 | 0 | 3.0347 | 0.0006896 | -0.033441 | 3.0249 | 0.00057656 | 0 | 2.9494 | 0.00067314 | -0.032451 |  | LF | Bldg | 3110 | 0.591 | 3020 | 0.577 | 0.975 | 1.17 | -0.010728 | 3110 | 0.591 | 3020 | 0.577 | 0.975 | 1.17 | -0.0107
LFBldgPGEComExIOU | Com-Iltg-dWatt-LF_OSbldg | PGE | Com | Ex | IOU | 3.1705 | 0.00065379 | 0 | 3.3611 | 0.00079131 | -0.021218 | 3.0779 | 0.00063455 | 0 | 3.2628 | 0.00076767 | -0.020596 |  | LF | Bldg | 3170 | 0.654 | 3080 | 0.635 | 1.06 | 1.21 | -0.0066916 | 3170 | 0.654 | 3080 | 0.635 | 1.06 | 1.21 | -0.00669
LFBldgPGEComNewCZ05 | Com-Iltg-dWatt-LF_OSbldg | PGE | Com | New | CZ05 | 2.908 | 0.00063417 | 0 | 3.0052 | 0.00075924 | -0.020757 | 2.908 | 0.00063417 | 0 | 3.0052 | 0.00075924 | -0.020757 |  | LF | Bldg | 2910 | 0.634 | 2910 | 0.634 | 1.03 | 1.2 | -0.0071379 | 2910 | 0.634 | 2910 | 0.634 | 1.03 | 1.2 | -0.00714
LFBldgPGEComNewCZ11 | Com-Iltg-dWatt-LF_OSbldg | PGE | Com | New | CZ11 | 3.2085 | 0.00062284 | 0 | 3.4045 | 0.00076328 | -0.020357 | 3.2085 | 0.00062284 | 0 | 3.4045 | 0.00076328 | -0.020357 |  | LF | Bldg | 3210 | 0.623 | 3210 | 0.623 | 1.06 | 1.23 | -0.0063447 | 3210 | 0.623 | 3210 | 0.623 | 1.06 | 1.23 | -0.00634
LFBldgPGEComNewCZ12 | Com-Iltg-dWatt-LF_OSbldg | PGE | Com | New | CZ12 | 3.1879 | 0.00064108 | 0 | 3.3835 | 0.00078287 | -0.019458 | 3.1879 | 0.00064108 | 0 | 3.3835 | 0.00078287 | -0.019458 |  | LF | Bldg | 3190 | 0.641 | 3190 | 0.641 | 1.06 | 1.22 | -0.0061035 | 3190 | 0.641 | 3190 | 0.641 | 1.06 | 1.22 | -0.0061
LFBldgPGEComNewCZ13 | Com-Iltg-dWatt-LF_OSbldg | PGE | Com | New | CZ13 | 3.2367 | 0.00063172 | 0 | 3.4862 | 0.00076522 | -0.018337 | 3.2367 | 0.00063172 | 0 | 3.4862 | 0.00076522 | -0.018337 |  | LF | Bldg | 3240 | 0.632 | 3240 | 0.632 | 1.08 | 1.21 | -0.0056654 | 3240 | 0.632 | 3240 | 0.632 | 1.08 | 1.21 | -0.00567
LFBldgPGEComNewCZ16 | Com-Iltg-dWatt-LF_OSbldg | PGE | Com | New | CZ16 | 3.0466 | 0.00058262 | 0 | 2.9694 | 0.0006801 | -0.030355 | 3.0466 | 0.00058262 | 0 | 2.9694 | 0.0006801 | -0.030355 |  | LF | Bldg | 3050 | 0.583 | 3050 | 0.583 | 0.975 | 1.17 | -0.0099638 | 3050 | 0.583 | 3050 | 0.583 | 0.975 | 1.17 | -0.00996
LFBldgPGEComNewIOU | Com-Iltg-dWatt-LF_OSbldg | PGE | Com | New | IOU | 3.1249 | 0.00064604 | 0 | 3.2961 | 0.00078416 | -0.019345 | 3.1249 | 0.00064604 | 0 | 3.2961 | 0.00078416 | -0.019345 |  | LF | Bldg | 3120 | 0.646 | 3120 | 0.646 | 1.05 | 1.21 | -0.0061904 | 3120 | 0.646 | 3120 | 0.646 | 1.05 | 1.21 | -0.00619
LFBldgPGEECCExCZ01 | Com-Iltg-dWatt-LF_OSbldg | PGE | ECC | Ex | CZ01 | 2.416 | 0.00080349 | 0 | 2.486 | 0.00096898 | -0.048616 | 2.27 | 0.00071592 | 0 | 2.34 | 0.00086389 | -0.045697 |  | LF | Bldg | 2420 | 0.803 | 2270 | 0.716 | 1.03 | 1.21 | -0.020131 | 2420 | 0.803 | 2270 | 0.716 | 1.03 | 1.21 | -0.0201
LFBldgPGEECCExCZ02 | Com-Iltg-dWatt-LF_OSbldg | PGE | ECC | Ex | CZ02 | 2.4128 | 0.00048431 | 0 | 2.6418 | 0.00063149 | -0.029213 | 2.27 | 0.0004329 | 0 | 2.48 | 0.0005639 | -0.0275 |  | LF | Bldg | 2410 | 0.484 | 2270 | 0.433 | 1.09 | 1.3 | -0.012115 | 2410 | 0.484 | 2270 | 0.433 | 1.09 | 1.3 | -0.0121
LFBldgPGEECCExCZ03 | Com-Iltg-dWatt-LF_OSbldg | PGE | ECC | Ex | CZ03 | 2.4145 | 0.00048494 | 0 | 2.6141 | 0.00060143 | -0.03043 | 2.27 | 0.00043293 | 0 | 2.46 | 0.00053689 | -0.0286 |  | LF | Bldg | 2410 | 0.485 | 2270 | 0.433 | 1.08 | 1.24 | -0.012599 | 2410 | 0.485 | 2270 | 0.433 | 1.08 | 1.24 | -0.0126
LFBldgPGEECCExCZ04 | Com-Iltg-dWatt-LF_OSbldg | PGE | ECC | Ex | CZ04 | 2.4122 | 0.00080116 | 0 | 2.6812 | 0.0010339 | -0.023022 | 2.27 | 0.00071584 | 0 | 2.52 | 0.00092679 | -0.0216 |  | LF | Bldg | 2410 | 0.801 | 2270 | 0.716 | 1.11 | 1.29 | -0.0095154 | 2410 | 0.801 | 2270 | 0.716 | 1.11 | 1.29 | -0.00952
LFBldgPGEECCExCZ05 | Com-Iltg-dWatt-LF_OSbldg | PGE | ECC | Ex | CZ05 | 2.4122 | 0.00080116 | 0 | 2.6117 | 0.00097707 | -0.029206 | 2.27 | 0.00071584 | 0 | 2.46 | 0.00087279 | -0.0275 |  | LF | Bldg | 2410 | 0.801 | 2270 | 0.716 | 1.08 | 1.22 | -0.012115 | 2410 | 0.801 | 2270 | 0.716 | 1.08 | 1.22 | -0.0121
LFBldgPGEECCExCZ11 | Com-Iltg-dWatt-LF_OSbldg | PGE | ECC | Ex | CZ11 | 2.4109 | 0.00048362 | 0 | 2.7097 | 0.00060177 | -0.026297 | 2.27 | 0.00043288 | 0 | 2.55 | 0.00053788 | -0.024794 |  | LF | Bldg | 2410 | 0.484 | 2270 | 0.433 | 1.12 | 1.24 | -0.010922 | 2410 | 0.484 | 2270 | 0.433 | 1.12 | 1.24 | -0.0109
LFBldgPGEECCExCZ12 | Com-Iltg-dWatt-LF_OSbldg | PGE | ECC | Ex | CZ12 | 2.4113 | 0.00048374 | 0 | 2.6801 | 0.00062281 | -0.026101 | 2.27 | 0.00043288 | 0 | 2.5294 | 0.00055688 | -0.024594 |  | LF | Bldg | 2410 | 0.484 | 2270 | 0.433 | 1.11 | 1.29 | -0.010834 | 2410 | 0.484 | 2270 | 0.433 | 1.11 | 1.29 | -0.0108
LFBldgPGEECCExCZ13 | Com-Iltg-dWatt-LF_OSbldg | PGE | ECC | Ex | CZ13 | 2.411 | 0.00048363 | 0 | 2.7298 | 0.00062861 | -0.023116 | 2.27 | 0.00043288 | 0 | 2.57 | 0.00056282 | -0.0218 |  | LF | Bldg | 2410 | 0.484 | 2270 | 0.433 | 1.13 | 1.3 | -0.0096035 | 2410 | 0.484 | 2270 | 0.433 | 1.13 | 1.3 | -0.0096
LFBldgPGEECCExCZ16 | Com-Iltg-dWatt-LF_OSbldg | PGE | ECC | Ex | CZ16 | 2.4133 | 0.0004845 | 0 | 2.5529 | 0.00059291 | -0.042484 | 2.27 | 0.00043291 | 0 | 2.4095 | 0.00052987 | -0.04 |  | LF | Bldg | 2410 | 0.484 | 2270 | 0.433 | 1.06 | 1.22 | -0.017621 | 2410 | 0.484 | 2270 | 0.433 | 1.06 | 1.22 | -0.0176
LFBldgPGEECCExIOU | Com-Iltg-dWatt-LF_OSbldg | PGE | ECC | Ex | IOU | 2.4128 | 0.00054481 | 0 | 2.6513 | 0.00068679 | -0.028195 | 2.27 | 0.00048686 | 0 | 2.4956 | 0.00061387 | -0.026528 |  | LF | Bldg | 2410 | 0.545 | 2270 | 0.487 | 1.1 | 1.26 | -0.011686 | 2410 | 0.545 | 2270 | 0.487 | 1.1 | 1.26 | -0.0117
LFBldgPGEECCNewCZ01 | Com-Iltg-dWatt-LF_OSbldg | PGE | ECC | New | CZ01 | 2.27 | 0.000713 | 0 | 2.34 | 0.000836 | -0.0438 | 2.27 | 0.000713 | 0 | 2.34 | 0.000836 | -0.0438 |  | LF | Bldg | 2270 | 0.713 | 2270 | 0.713 | 1.03 | 1.17 | -0.019295 | 2270 | 0.713 | 2270 | 0.713 | 1.03 | 1.17 | -0.0193
LFBldgPGEECCNewCZ02 | Com-Iltg-dWatt-LF_OSbldg | PGE | ECC | New | CZ02 | 2.27 | 0.000431 | 0 | 2.49 | 0.000577 | -0.0254 | 2.27 | 0.000431 | 0 | 2.49 | 0.000577 | -0.0254 |  | LF | Bldg | 2270 | 0.431 | 2270 | 0.431 | 1.1 | 1.34 | -0.011189 | 2270 | 0.431 | 2270 | 0.431 | 1.1 | 1.34 | -0.0112
LFBldgPGEECCNewCZ03 | Com-Iltg-dWatt-LF_OSbldg | PGE | ECC | New | CZ03 | 2.27 | 0.000431 | 0 | 2.44 | 0.000558 | -0.0268 | 2.27 | 0.000431 | 0 | 2.44 | 0.000558 | -0.0268 |  | LF | Bldg | 2270 | 0.431 | 2270 | 0.431 | 1.07 | 1.29 | -0.011806 | 2270 | 0.431 | 2270 | 0.431 | 1.07 | 1.29 | -0.0118
LFBldgPGEECCNewCZ04 | Com-Iltg-dWatt-LF_OSbldg | PGE | ECC | New | CZ04 | 2.27 | 0.000713 | 0 | 2.52 | 0.000897 | -0.0199 | 2.27 | 0.000713 | 0 | 2.52 | 0.000897 | -0.0199 |  | LF | Bldg | 2270 | 0.713 | 2270 | 0.713 | 1.11 | 1.26 | -0.0087665 | 2270 | 0.713 | 2270 | 0.713 | 1.11 | 1.26 | -0.00877
LFBldgPGEECCNewCZ05 | Com-Iltg-dWatt-LF_OSbldg | PGE | ECC | New | CZ05 | 2.27 | 0.000713 | 0 | 2.45 | 0.000867 | -0.0261 | 2.27 | 0.000713 | 0 | 2.45 | 0.000867 | -0.0261 |  | LF | Bldg | 2270 | 0.713 | 2270 | 0.713 | 1.08 | 1.22 | -0.011498 | 2270 | 0.713 | 2270 | 0.713 | 1.08 | 1.22 | -0.0115
LFBldgPGEECCNewCZ11 | Com-Iltg-dWatt-LF_OSbldg | PGE | ECC | New | CZ11 | 2.27 | 0.000431 | 0 | 2.55 | 0.000567 | -0.0215 | 2.27 | 0.000431 | 0 | 2.55 | 0.000567 | -0.0215 |  | LF | Bldg | 2270 | 0.431 | 2270 | 0.431 | 1.12 | 1.32 | -0.0094714 | 2270 | 0.431 | 2270 | 0.431 | 1.12 | 1.32 | -0.00947
LFBldgPGEECCNewCZ12 | Com-Iltg-dWatt-LF_OSbldg | PGE | ECC | New | CZ12 | 2.27 | 0.000431 | 0 | 2.54 | 0.000578 | -0.0217 | 2.27 | 0.000431 | 0 | 2.54 | 0.000578 | -0.0217 |  | LF | Bldg | 2270 | 0.431 | 2270 | 0.431 | 1.12 | 1.34 | -0.0095595 | 2270 | 0.431 | 2270 | 0.431 | 1.12 | 1.34 | -0.00956
LFBldgPGEECCNewCZ13 | Com-Iltg-dWatt-LF_OSbldg | PGE | ECC | New | CZ13 | 2.27 | 0.000431 | 0 | 2.57 | 0.000571 | -0.0189 | 2.27 | 0.000431 | 0 | 2.57 | 0.000571 | -0.0189 |  | LF | Bldg | 2270 | 0.431 | 2270 | 0.431 | 1.13 | 1.32 | -0.008326 | 2270 | 0.431 | 2270 | 0.431 | 1.13 | 1.32 | -0.00833
LFBldgPGEECCNewCZ16 | Com-Iltg-dWatt-LF_OSbldg | PGE | ECC | New | CZ16 | 2.27 | 0.000431 | 0 | 2.41 | 0.000548 | -0.037 | 2.27 | 0.000431 | 0 | 2.41 | 0.000548 | -0.037 |  | LF | Bldg | 2270 | 0.431 | 2270 | 0.431 | 1.06 | 1.27 | -0.0163 | 2270 | 0.431 | 2270 | 0.431 | 1.06 | 1.27 | -0.0163
LFBldgPGEECCNewIOU | Com-Iltg-dWatt-LF_OSbldg | PGE | ECC | New | IOU | 2.27 | 0.00048511 | 0 | 2.5019 | 0.00062766 | -0.023456 | 2.27 | 0.00048511 | 0 | 2.5019 | 0.00062766 | -0.023456 |  | LF | Bldg | 2270 | 0.485 | 2270 | 0.485 | 1.1 | 1.29 | -0.010333 | 2270 | 0.485 | 2270 | 0.485 | 1.1 | 1.29 | -0.0103
LFBldgPGEEPrExCZ01 | Com-Iltg-dWatt-LF_OSbldg | PGE | EPr | Ex | CZ01 | 2.1328 | 0.00061371 | 0 | 2.1128 | 0.00073325 | -0.038566 | 1.95 | 0.00055119 | 0 | 1.93 | 0.00065823 | -0.035296 |  | LF | Bldg | 2130 | 0.614 | 1950 | 0.551 | 0.99 | 1.19 | -0.018101 | 2130 | 0.614 | 1950 | 0.551 | 0.99 | 1.19 | -0.0181
LFBldgPGEEPrExCZ02 | Com-Iltg-dWatt-LF_OSbldg | PGE | EPr | Ex | CZ02 | 2.1342 | 1.9938e-05 | 0 | 2.2538 | 1.9938e-05 | -0.022635 | 1.95 | 1.7903e-05 | 0 | 2.06 | 1.7903e-05 | -0.020697 |  | LF | Bldg | 2130 | 0.0199 | 1950 | 0.0179 | 1.06 | 1 | -0.010614 | 2130 | 0.0199 | 1950 | 0.0179 | 1.06 | 1 | -0.0106
LFBldgPGEEPrExCZ03 | Com-Iltg-dWatt-LF_OSbldg | PGE | EPr | Ex | CZ03 | 2.1354 | 1.9952e-05 | 0 | 2.2752 | 1.9952e-05 | -0.021954 | 1.95 | 1.7902e-05 | 0 | 2.08 | 1.7902e-05 | -0.0201 |  | LF | Bldg | 2140 | 0.02 | 1950 | 0.0179 | 1.07 | 1 | -0.010308 | 2140 | 0.02 | 1950 | 0.0179 | 1.07 | 1 | -0.0103
LFBldgPGEEPrExCZ04 | Com-Iltg-dWatt-LF_OSbldg | PGE | EPr | Ex | CZ04 | 2.134 | 0.0006141 | 0 | 2.3133 | 0.00075762 | -0.017249 | 1.95 | 0.00055116 | 0 | 2.11 | 0.00067919 | -0.0157 |  | LF | Bldg | 2130 | 0.614 | 1950 | 0.551 | 1.08 | 1.23 | -0.0080513 | 2130 | 0.614 | 1950 | 0.551 | 1.08 | 1.23 | -0.00805
LFBldgPGEEPrExCZ05 | Com-Iltg-dWatt-LF_OSbldg | PGE | EPr | Ex | CZ05 | 2.1339 | 0.00061409 | 0 | 2.2733 | 0.00074167 | -0.020639 | 1.95 | 0.00055116 | 0 | 2.0797 | 0.00066519 | -0.0188 |  | LF | Bldg | 2130 | 0.614 | 1950 | 0.551 | 1.07 | 1.21 | -0.009641 | 2130 | 0.614 | 1950 | 0.551 | 1.07 | 1.21 | -0.00964
LFBldgPGEEPrExCZ11 | Com-Iltg-dWatt-LF_OSbldg | PGE | EPr | Ex | CZ11 | 2.1288 | 1.9882e-05 | 0 | 2.2676 | 1.9882e-05 | -0.020788 | 1.95 | 1.7906e-05 | 0 | 2.07 | 1.7906e-05 | -0.019094 |  | LF | Bldg | 2130 | 0.0199 | 1950 | 0.0179 | 1.06 | 1 | -0.0097918 | 2130 | 0.0199 | 1950 | 0.0179 | 1.06 | 1 | -0.00979
LFBldgPGEEPrExCZ12 | Com-Iltg-dWatt-LF_OSbldg | PGE | EPr | Ex | CZ12 | 2.1302 | 1.9896e-05 | 0 | 2.2696 | 1.9896e-05 | -0.021502 | 1.95 | 1.7905e-05 | 0 | 2.08 | 1.7905e-05 | -0.0197 |  | LF | Bldg | 2130 | 0.0199 | 1950 | 0.0179 | 1.07 | 1 | -0.010103 | 2130 | 0.0199 | 1950 | 0.0179 | 1.07 | 1 | -0.0101
LFBldgPGEEPrExCZ13 | Com-Iltg-dWatt-LF_OSbldg | PGE | EPr | Ex | CZ13 | 2.1298 | 1.9893e-05 | 0 | 2.2893 | 1.9893e-05 | -0.018609 | 1.95 | 1.7905e-05 | 0 | 2.1 | 1.7905e-05 | -0.017 |  | LF | Bldg | 2130 | 0.0199 | 1950 | 0.0179 | 1.08 | 1 | -0.0087179 | 2130 | 0.0199 | 1950 | 0.0179 | 1.08 | 1 | -0.00872
LFBldgPGEEPrExCZ16 | Com-Iltg-dWatt-LF_OSbldg | PGE | EPr | Ex | CZ16 | 2.1297 | 1.9892e-05 | 0 | 2.0702 | 1.9892e-05 | -0.038116 | 1.95 | 1.7905e-05 | 0 | 1.9 | 1.7905e-05 | -0.0349 |  | LF | Bldg | 2130 | 0.0199 | 1950 | 0.0179 | 0.974 | 1 | -0.017897 | 2130 | 0.0199 | 1950 | 0.0179 | 0.974 | 1 | -0.0179
LFBldgPGEEPrExIOU | Com-Iltg-dWatt-LF_OSbldg | PGE | EPr | Ex | IOU | 2.1325 | 0.00012447 | 0 | 2.2762 | 0.00014916 | -0.020877 | 1.95 | 0.00011174 | 0 | 2.0824 | 0.00013377 | -0.019097 |  | LF | Bldg | 2130 | 0.124 | 1950 | 0.112 | 1.07 | 1.2 | -0.0097935 | 2130 | 0.124 | 1950 | 0.112 | 1.07 | 1.2 | -0.00979
LFBldgPGEEPrNewCZ01 | Com-Iltg-dWatt-LF_OSbldg | PGE | EPr | New | CZ01 | 1.95 | 0.000556 | 0 | 1.93 | 0.000647 | -0.0384 | 1.95 | 0.000556 | 0 | 1.93 | 0.000647 | -0.0384 |  | LF | Bldg | 1950 | 0.556 | 1950 | 0.556 | 0.99 | 1.16 | -0.019692 | 1950 | 0.556 | 1950 | 0.556 | 0.99 | 1.16 | -0.0197
LFBldgPGEEPrNewCZ02 | Com-Iltg-dWatt-LF_OSbldg | PGE | EPr | New | CZ02 | 1.95 | 1.8e-05 | 0 | 2.05 | 1.8e-05 | -0.0249 | 1.95 | 1.8e-05 | 0 | 2.05 | 1.8e-05 | -0.0249 |  | LF | Bldg | 1950 | 0.018 | 1950 | 0.018 | 1.05 | 1 | -0.012769 | 1950 | 0.018 | 1950 | 0.018 | 1.05 | 1 | -0.0128
LFBldgPGEEPrNewCZ03 | Com-Iltg-dWatt-LF_OSbldg | PGE | EPr | New | CZ03 | 1.95 | 1.8e-05 | 0 | 2.02 | 1.8e-05 | -0.021 | 1.95 | 1.8e-05 | 0 | 2.02 | 1.8e-05 | -0.021 |  | LF | Bldg | 1950 | 0.018 | 1950 | 0.018 | 1.04 | 1 | -0.010769 | 1950 | 0.018 | 1950 | 0.018 | 1.04 | 1 | -0.0108
LFBldgPGEEPrNewCZ04 | Com-Iltg-dWatt-LF_OSbldg | PGE | EPr | New | CZ04 | 1.95 | 0.000556 | 0 | 2.09 | 0.000735 | -0.0188 | 1.95 | 0.000556 | 0 | 2.09 | 0.000735 | -0.0188 |  | LF | Bldg | 1950 | 0.556 | 1950 | 0.556 | 1.07 | 1.32 | -0.009641 | 1950 | 0.556 | 1950 | 0.556 | 1.07 | 1.32 | -0.00964
LFBldgPGEEPrNewCZ05 | Com-Iltg-dWatt-LF_OSbldg | PGE | EPr | New | CZ05 | 1.95 | 0.000556 | 0 | 2.04 | 0.000693 | -0.0183 | 1.95 | 0.000556 | 0 | 2.04 | 0.000693 | -0.0183 |  | LF | Bldg | 1950 | 0.556 | 1950 | 0.556 | 1.05 | 1.25 | -0.0093846 | 1950 | 0.556 | 1950 | 0.556 | 1.05 | 1.25 | -0.00938
LFBldgPGEEPrNewCZ11 | Com-Iltg-dWatt-LF_OSbldg | PGE | EPr | New | CZ11 | 1.95 | 1.8e-05 | 0 | 2.12 | 1.8e-05 | -0.0222 | 1.95 | 1.8e-05 | 0 | 2.12 | 1.8e-05 | -0.0222 |  | LF | Bldg | 1950 | 0.018 | 1950 | 0.018 | 1.09 | 1 | -0.011385 | 1950 | 0.018 | 1950 | 0.018 | 1.09 | 1 | -0.0114
LFBldgPGEEPrNewCZ12 | Com-Iltg-dWatt-LF_OSbldg | PGE | EPr | New | CZ12 | 1.95 | 1.8e-05 | 0 | 2.09 | 1.8e-05 | -0.0226 | 1.95 | 1.8e-05 | 0 | 2.09 | 1.8e-05 | -0.0226 |  | LF | Bldg | 1950 | 0.018 | 1950 | 0.018 | 1.07 | 1 | -0.01159 | 1950 | 0.018 | 1950 | 0.018 | 1.07 | 1 | -0.0116
LFBldgPGEEPrNewCZ13 | Com-Iltg-dWatt-LF_OSbldg | PGE | EPr | New | CZ13 | 1.95 | 1.8e-05 | 0 | 2.13 | 1.8e-05 | -0.0202 | 1.95 | 1.8e-05 | 0 | 2.13 | 1.8e-05 | -0.0202 |  | LF | Bldg | 1950 | 0.018 | 1950 | 0.018 | 1.09 | 1 | -0.010359 | 1950 | 0.018 | 1950 | 0.018 | 1.09 | 1 | -0.0104
LFBldgPGEEPrNewCZ16 | Com-Iltg-dWatt-LF_OSbldg | PGE | EPr | New | CZ16 | 1.95 | 1.8e-05 | 0 | 1.94 | 1.8e-05 | -0.0325 | 1.95 | 1.8e-05 | 0 | 1.94 | 1.8e-05 | -0.0325 |  | LF | Bldg | 1950 | 0.018 | 1950 | 0.018 | 0.995 | 1 | -0.016667 | 1950 | 0.018 | 1950 | 0.018 | 0.995 | 1 | -0.0167
LFBldgPGEEPrNewIOU | Com-Iltg-dWatt-LF_OSbldg | PGE | EPr | New | IOU | 1.95 | 9.3884e-05 | 0 | 2.0835 | 0.00011761 | -0.021643 | 1.95 | 9.3884e-05 | 0 | 2.0835 | 0.00011761 | -0.021643 |  | LF | Bldg | 1950 | 0.0939 | 1950 | 0.0939 | 1.07 | 1.25 | -0.011099 | 1950 | 0.0939 | 1950 | 0.0939 | 1.07 | 1.25 | -0.0111
LFBldgPGEERCExCZ01 | Com-Iltg-dWatt-LF_OSbldg | PGE | ERC | Ex | CZ01 | 2.4689 | 0.00069845 | 0 | 2.3893 | 0.0008288 | -0.042705 | 2.19 | 0.0006013 | 0 | 2.12 | 0.00071338 | -0.0378 |  | LF | Bldg | 2470 | 0.698 | 2190 | 0.601 | 0.968 | 1.19 | -0.01726 | 2470 | 0.698 | 2190 | 0.601 | 0.968 | 1.19 | -0.0173
LFBldgPGEERCExCZ02 | Com-Iltg-dWatt-LF_OSbldg | PGE | ERC | Ex | CZ02 | 2.4711 | 1.9917e-05 | 0 | 2.5208 | 1.9917e-05 | -0.030189 | 2.19 | 1.7106e-05 | 0 | 2.23 | 1.7106e-05 | -0.0267 |  | LF | Bldg | 2470 | 0.0199 | 2190 | 0.0171 | 1.02 | 1 | -0.012192 | 2470 | 0.0199 | 2190 | 0.0171 | 1.02 | 1 | -0.0122
LFBldgPGEERCExCZ03 | Com-Iltg-dWatt-LF_OSbldg | PGE | ERC | Ex | CZ03 | 2.473 | 1.9935e-05 | 0 | 2.483 | 1.9935e-05 | -0.027921 | 2.19 | 1.7105e-05 | 0 | 2.2 | 1.7105e-05 | -0.0247 |  | LF | Bldg | 2470 | 0.0199 | 2190 | 0.0171 | 1 | 1 | -0.011279 | 2470 | 0.0199 | 2190 | 0.0171 | 1 | 1 | -0.0113
LFBldgPGEERCExCZ04 | Com-Iltg-dWatt-LF_OSbldg | PGE | ERC | Ex | CZ04 | 2.4708 | 0.00069905 | 0 | 2.5805 | 0.00084741 | -0.023511 | 2.19 | 0.00060125 | 0 | 2.29 | 0.00072832 | -0.0208 |  | LF | Bldg | 2470 | 0.699 | 2190 | 0.601 | 1.05 | 1.21 | -0.0094977 | 2470 | 0.699 | 2190 | 0.601 | 1.05 | 1.21 | -0.0095
LFBldgPGEERCExCZ05 | Com-Iltg-dWatt-LF_OSbldg | PGE | ERC | Ex | CZ05 | 2.4708 | 0.00069904 | 0 | 2.5205 | 0.00085437 | -0.027398 | 2.19 | 0.00060125 | 0 | 2.23 | 0.00073432 | -0.0243 |  | LF | Bldg | 2470 | 0.699 | 2190 | 0.601 | 1.02 | 1.22 | -0.011096 | 2470 | 0.699 | 2190 | 0.601 | 1.02 | 1.22 | -0.0111
LFBldgPGEERCExCZ11 | Com-Iltg-dWatt-LF_OSbldg | PGE | ERC | Ex | CZ11 | 2.4629 | 1.9841e-05 | 0 | 2.5623 | 1.9841e-05 | -0.025323 | 2.19 | 1.7112e-05 | 0 | 2.28 | 1.7112e-05 | -0.0225 |  | LF | Bldg | 2460 | 0.0198 | 2190 | 0.0171 | 1.04 | 1 | -0.010274 | 2460 | 0.0198 | 2190 | 0.0171 | 1.04 | 1 | -0.0103
LFBldgPGEERCExCZ12 | Com-Iltg-dWatt-LF_OSbldg | PGE | ERC | Ex | CZ12 | 2.465 | 1.986e-05 | 0 | 2.5639 | 1.986e-05 | -0.026834 | 2.19 | 1.711e-05 | 0 | 2.27 | 1.711e-05 | -0.0238 |  | LF | Bldg | 2460 | 0.0199 | 2190 | 0.0171 | 1.04 | 1 | -0.010868 | 2460 | 0.0199 | 2190 | 0.0171 | 1.04 | 1 | -0.0109
LFBldgPGEERCExCZ13 | Com-Iltg-dWatt-LF_OSbldg | PGE | ERC | Ex | CZ13 | 2.4645 | 1.9856e-05 | 0 | 2.6034 | 1.9856e-05 | -0.023945 | 2.19 | 1.7111e-05 | 0 | 2.31 | 1.7111e-05 | -0.0212 |  | LF | Bldg | 2460 | 0.0199 | 2190 | 0.0171 | 1.05 | 1 | -0.0096804 | 2460 | 0.0199 | 2190 | 0.0171 | 1.05 | 1 | -0.00968
LFBldgPGEERCExCZ16 | Com-Iltg-dWatt-LF_OSbldg | PGE | ERC | Ex | CZ16 | 2.4643 | 1.9854e-05 | 0 | 2.4443 | 1.9854e-05 | -0.040934 | 2.19 | 1.7111e-05 | 0 | 2.17 | 1.7111e-05 | -0.0363 |  | LF | Bldg | 2460 | 0.0199 | 2190 | 0.0171 | 0.991 | 1 | -0.016575 | 2460 | 0.0199 | 2190 | 0.0171 | 0.991 | 1 | -0.0166
LFBldgPGEERCExIOU | Com-Iltg-dWatt-LF_OSbldg | PGE | ERC | Ex | IOU | 2.4685 | 0.00013939 | 0 | 2.5427 | 0.00016545 | -0.026636 | 2.19 | 0.0001199 | 0 | 2.2539 | 0.00014223 | -0.023588 |  | LF | Bldg | 2470 | 0.139 | 2190 | 0.12 | 1.03 | 1.19 | -0.010771 | 2470 | 0.139 | 2190 | 0.12 | 1.03 | 1.19 | -0.0108
LFBldgPGEERCNewCZ01 | Com-Iltg-dWatt-LF_OSbldg | PGE | ERC | New | CZ01 | 2.19 | 0.000609 | 0 | 2.27 | 0.000728 | -0.0422 | 2.19 | 0.000609 | 0 | 2.27 | 0.000728 | -0.0422 |  | LF | Bldg | 2190 | 0.609 | 2190 | 0.609 | 1.04 | 1.2 | -0.019269 | 2190 | 0.609 | 2190 | 0.609 | 1.04 | 1.2 | -0.0193
LFBldgPGEERCNewCZ02 | Com-Iltg-dWatt-LF_OSbldg | PGE | ERC | New | CZ02 | 2.19 | 1.73e-05 | 0 | 2.39 | 1.73e-05 | -0.0276 | 2.19 | 1.73e-05 | 0 | 2.39 | 1.73e-05 | -0.0276 |  | LF | Bldg | 2190 | 0.0173 | 2190 | 0.0173 | 1.09 | 1 | -0.012603 | 2190 | 0.0173 | 2190 | 0.0173 | 1.09 | 1 | -0.0126
LFBldgPGEERCNewCZ03 | Com-Iltg-dWatt-LF_OSbldg | PGE | ERC | New | CZ03 | 2.19 | 1.73e-05 | 0 | 2.39 | 1.73e-05 | -0.0247 | 2.19 | 1.73e-05 | 0 | 2.39 | 1.73e-05 | -0.0247 |  | LF | Bldg | 2190 | 0.0173 | 2190 | 0.0173 | 1.09 | 1 | -0.011279 | 2190 | 0.0173 | 2190 | 0.0173 | 1.09 | 1 | -0.0113
LFBldgPGEERCNewCZ04 | Com-Iltg-dWatt-LF_OSbldg | PGE | ERC | New | CZ04 | 2.19 | 0.000609 | 0 | 2.44 | 0.000777 | -0.0212 | 2.19 | 0.000609 | 0 | 2.44 | 0.000777 | -0.0212 |  | LF | Bldg | 2190 | 0.609 | 2190 | 0.609 | 1.11 | 1.28 | -0.0096804 | 2190 | 0.609 | 2190 | 0.609 | 1.11 | 1.28 | -0.00968
LFBldgPGEERCNewCZ05 | Com-Iltg-dWatt-LF_OSbldg | PGE | ERC | New | CZ05 | 2.19 | 0.000609 | 0 | 2.37 | 0.000754 | -0.0234 | 2.19 | 0.000609 | 0 | 2.37 | 0.000754 | -0.0234 |  | LF | Bldg | 2190 | 0.609 | 2190 | 0.609 | 1.08 | 1.24 | -0.010685 | 2190 | 0.609 | 2190 | 0.609 | 1.08 | 1.24 | -0.0107
LFBldgPGEERCNewCZ11 | Com-Iltg-dWatt-LF_OSbldg | PGE | ERC | New | CZ11 | 2.19 | 1.73e-05 | 0 | 2.47 | 1.73e-05 | -0.0247 | 2.19 | 1.73e-05 | 0 | 2.47 | 1.73e-05 | -0.0247 |  | LF | Bldg | 2190 | 0.0173 | 2190 | 0.0173 | 1.13 | 1 | -0.011279 | 2190 | 0.0173 | 2190 | 0.0173 | 1.13 | 1 | -0.0113
LFBldgPGEERCNewCZ12 | Com-Iltg-dWatt-LF_OSbldg | PGE | ERC | New | CZ12 | 2.19 | 1.73e-05 | 0 | 2.44 | 1.73e-05 | -0.0254 | 2.19 | 1.73e-05 | 0 | 2.44 | 1.73e-05 | -0.0254 |  | LF | Bldg | 2190 | 0.0173 | 2190 | 0.0173 | 1.11 | 1 | -0.011598 | 2190 | 0.0173 | 2190 | 0.0173 | 1.11 | 1 | -0.0116
LFBldgPGEERCNewCZ13 | Com-Iltg-dWatt-LF_OSbldg | PGE | ERC | New | CZ13 | 2.19 | 1.73e-05 | 0 | 2.49 | 1.73e-05 | -0.0225 | 2.19 | 1.73e-05 | 0 | 2.49 | 1.73e-05 | -0.0225 |  | LF | Bldg | 2190 | 0.0173 | 2190 | 0.0173 | 1.14 | 1 | -0.010274 | 2190 | 0.0173 | 2190 | 0.0173 | 1.14 | 1 | -0.0103
LFBldgPGEERCNewCZ16 | Com-Iltg-dWatt-LF_OSbldg | PGE | ERC | New | CZ16 | 2.19 | 1.73e-05 | 0 | 2.29 | 1.73e-05 | -0.0398 | 2.19 | 1.73e-05 | 0 | 2.29 | 1.73e-05 | -0.0398 |  | LF | Bldg | 2190 | 0.0173 | 2190 | 0.0173 | 1.05 | 1 | -0.018174 | 2190 | 0.0173 | 2190 | 0.0173 | 1.05 | 1 | -0.0182
LFBldgPGEERCNewIOU | Com-Iltg-dWatt-LF_OSbldg | PGE | ERC | New | IOU | 2.19 | 0.00010076 | 0 | 2.4382 | 0.00012361 | -0.024508 | 2.19 | 0.00010076 | 0 | 2.4382 | 0.00012361 | -0.024508 |  | LF | Bldg | 2190 | 0.101 | 2190 | 0.101 | 1.11 | 1.23 | -0.011191 | 2190 | 0.101 | 2190 | 0.101 | 1.11 | 1.23 | -0.0112
LFBldgPGEESeExCZ01 | Com-Iltg-dWatt-LF_OSbldg | PGE | ESe | Ex | CZ01 | 2.2735 | 0.00070682 | 0 | 2.2135 | 0.0008394 | -0.048063 | 2.11 | 0.00064719 | 0 | 2.05 | 0.00076919 | -0.0446 |  | LF | Bldg | 2270 | 0.707 | 2110 | 0.647 | 0.972 | 1.19 | -0.021137 | 2270 | 0.707 | 2110 | 0.647 | 0.972 | 1.19 | -0.0211
LFBldgPGEESeExCZ02 | Com-Iltg-dWatt-LF_OSbldg | PGE | ESe | Ex | CZ02 | 2.2748 | 1.9951e-05 | 0 | 2.3745 | 1.9951e-05 | -0.029629 | 2.11 | 1.8303e-05 | 0 | 2.2 | 1.8303e-05 | -0.027497 |  | LF | Bldg | 2270 | 0.02 | 2110 | 0.0183 | 1.04 | 1 | -0.013032 | 2270 | 0.02 | 2110 | 0.0183 | 1.04 | 1 | -0.013
LFBldgPGEESeExCZ03 | Com-Iltg-dWatt-LF_OSbldg | PGE | ESe | Ex | CZ03 | 2.2759 | 1.9962e-05 | 0 | 2.3757 | 1.9962e-05 | -0.030545 | 2.11 | 1.8302e-05 | 0 | 2.2 | 1.8302e-05 | -0.0283 |  | LF | Bldg | 2280 | 0.02 | 2110 | 0.0183 | 1.04 | 1 | -0.013412 | 2280 | 0.02 | 2110 | 0.0183 | 1.04 | 1 | -0.0134
LFBldgPGEESeExCZ04 | Com-Iltg-dWatt-LF_OSbldg | PGE | ESe | Ex | CZ04 | 2.2746 | 0.00070719 | 0 | 2.434 | 0.00086381 | -0.023243 | 2.11 | 0.00064716 | 0 | 2.25 | 0.00079119 | -0.0215 |  | LF | Bldg | 2270 | 0.707 | 2110 | 0.647 | 1.07 | 1.22 | -0.01019 | 2270 | 0.707 | 2110 | 0.647 | 1.07 | 1.22 | -0.0102
LFBldgPGEESeExCZ05 | Com-Iltg-dWatt-LF_OSbldg | PGE | ESe | Ex | CZ05 | 2.2746 | 0.00070719 | 0 | 2.3843 | 0.00084183 | -0.028033 | 2.11 | 0.00064716 | 0 | 2.21 | 0.00077116 | -0.026 |  | LF | Bldg | 2270 | 0.707 | 2110 | 0.647 | 1.05 | 1.19 | -0.012322 | 2270 | 0.707 | 2110 | 0.647 | 1.05 | 1.19 | -0.0123
LFBldgPGEESeExCZ11 | Com-Iltg-dWatt-LF_OSbldg | PGE | ESe | Ex | CZ11 | 2.27 | 1.9906e-05 | 0 | 2.4194 | 1.9906e-05 | -0.026182 | 2.11 | 1.8306e-05 | 0 | 2.25 | 1.8306e-05 | -0.0243 |  | LF | Bldg | 2270 | 0.0199 | 2110 | 0.0183 | 1.07 | 1 | -0.011517 | 2270 | 0.0199 | 2110 | 0.0183 | 1.07 | 1 | -0.0115
LFBldgPGEESeExCZ12 | Com-Iltg-dWatt-LF_OSbldg | PGE | ESe | Ex | CZ12 | 2.2712 | 1.9917e-05 | 0 | 2.4102 | 1.9917e-05 | -0.027091 | 2.11 | 1.8305e-05 | 0 | 2.23 | 1.8305e-05 | -0.0251 |  | LF | Bldg | 2270 | 0.0199 | 2110 | 0.0183 | 1.06 | 1 | -0.011896 | 2270 | 0.0199 | 2110 | 0.0183 | 1.06 | 1 | -0.0119
LFBldgPGEESeExCZ13 | Com-Iltg-dWatt-LF_OSbldg | PGE | ESe | Ex | CZ13 | 2.2709 | 1.9914e-05 | 0 | 2.4504 | 1.9914e-05 | -0.023704 | 2.11 | 1.8305e-05 | 0 | 2.28 | 1.8305e-05 | -0.022 |  | LF | Bldg | 2270 | 0.0199 | 2110 | 0.0183 | 1.08 | 1 | -0.010427 | 2270 | 0.0199 | 2110 | 0.0183 | 1.08 | 1 | -0.0104
LFBldgPGEESeExCZ16 | Com-Iltg-dWatt-LF_OSbldg | PGE | ESe | Ex | CZ16 | 2.2708 | 1.9913e-05 | 0 | 2.2308 | 1.9913e-05 | -0.041426 | 2.11 | 1.8305e-05 | 0 | 2.07 | 1.8305e-05 | -0.0384 |  | LF | Bldg | 2270 | 0.0199 | 2110 | 0.0183 | 0.981 | 1 | -0.018199 | 2270 | 0.0199 | 2110 | 0.0183 | 0.981 | 1 | -0.0182
LFBldgPGEESeExIOU | Com-Iltg-dWatt-LF_OSbldg | PGE | ESe | Ex | IOU | 2.2733 | 0.00014086 | 0 | 2.4042 | 0.00016774 | -0.02745 | 2.11 | 0.00012896 | 0 | 2.228 | 0.00015368 | -0.025442 |  | LF | Bldg | 2270 | 0.141 | 2110 | 0.129 | 1.06 | 1.19 | -0.012058 | 2270 | 0.141 | 2110 | 0.129 | 1.06 | 1.19 | -0.0121
LFBldgPGEESeNewCZ01 | Com-Iltg-dWatt-LF_OSbldg | PGE | ESe | New | CZ01 | 2.11 | 0.000652 | 0 | 2.1 | 0.000756 | -0.0327 | 2.11 | 0.000652 | 0 | 2.1 | 0.000756 | -0.0327 |  | LF | Bldg | 2110 | 0.652 | 2110 | 0.652 | 0.995 | 1.16 | -0.015498 | 2110 | 0.652 | 2110 | 0.652 | 0.995 | 1.16 | -0.0155
LFBldgPGEESeNewCZ02 | Com-Iltg-dWatt-LF_OSbldg | PGE | ESe | New | CZ02 | 2.11 | 1.84e-05 | 0 | 2.24 | 1.84e-05 | -0.0308 | 2.11 | 1.84e-05 | 0 | 2.24 | 1.84e-05 | -0.0308 |  | LF | Bldg | 2110 | 0.0184 | 2110 | 0.0184 | 1.06 | 1 | -0.014597 | 2110 | 0.0184 | 2110 | 0.0184 | 1.06 | 1 | -0.0146
LFBldgPGEESeNewCZ03 | Com-Iltg-dWatt-LF_OSbldg | PGE | ESe | New | CZ03 | 2.11 | 1.84e-05 | 0 | 2.21 | 1.84e-05 | -0.0287 | 2.11 | 1.84e-05 | 0 | 2.21 | 1.84e-05 | -0.0287 |  | LF | Bldg | 2110 | 0.0184 | 2110 | 0.0184 | 1.05 | 1 | -0.013602 | 2110 | 0.0184 | 2110 | 0.0184 | 1.05 | 1 | -0.0136
LFBldgPGEESeNewCZ04 | Com-Iltg-dWatt-LF_OSbldg | PGE | ESe | New | CZ04 | 2.11 | 0.000652 | 0 | 2.27 | 0.000856 | -0.0243 | 2.11 | 0.000652 | 0 | 2.27 | 0.000856 | -0.0243 |  | LF | Bldg | 2110 | 0.652 | 2110 | 0.652 | 1.08 | 1.31 | -0.011517 | 2110 | 0.652 | 2110 | 0.652 | 1.08 | 1.31 | -0.0115
LFBldgPGEESeNewCZ05 | Com-Iltg-dWatt-LF_OSbldg | PGE | ESe | New | CZ05 | 2.11 | 0.000652 | 0 | 2.21 | 0.000801 | -0.0232 | 2.11 | 0.000652 | 0 | 2.21 | 0.000801 | -0.0232 |  | LF | Bldg | 2110 | 0.652 | 2110 | 0.652 | 1.05 | 1.23 | -0.010995 | 2110 | 0.652 | 2110 | 0.652 | 1.05 | 1.23 | -0.011
LFBldgPGEESeNewCZ11 | Com-Iltg-dWatt-LF_OSbldg | PGE | ESe | New | CZ11 | 2.11 | 1.84e-05 | 0 | 2.31 | 1.84e-05 | -0.0264 | 2.11 | 1.84e-05 | 0 | 2.31 | 1.84e-05 | -0.0264 |  | LF | Bldg | 2110 | 0.0184 | 2110 | 0.0184 | 1.09 | 1 | -0.012512 | 2110 | 0.0184 | 2110 | 0.0184 | 1.09 | 1 | -0.0125
LFBldgPGEESeNewCZ12 | Com-Iltg-dWatt-LF_OSbldg | PGE | ESe | New | CZ12 | 2.11 | 1.84e-05 | 0 | 2.29 | 1.84e-05 | -0.0274 | 2.11 | 1.84e-05 | 0 | 2.29 | 1.84e-05 | -0.0274 |  | LF | Bldg | 2110 | 0.0184 | 2110 | 0.0184 | 1.09 | 1 | -0.012986 | 2110 | 0.0184 | 2110 | 0.0184 | 1.09 | 1 | -0.013
LFBldgPGEESeNewCZ13 | Com-Iltg-dWatt-LF_OSbldg | PGE | ESe | New | CZ13 | 2.11 | 1.84e-05 | 0 | 2.34 | 1.84e-05 | -0.0243 | 2.11 | 1.84e-05 | 0 | 2.34 | 1.84e-05 | -0.0243 |  | LF | Bldg | 2110 | 0.0184 | 2110 | 0.0184 | 1.11 | 1 | -0.011517 | 2110 | 0.0184 | 2110 | 0.0184 | 1.11 | 1 | -0.0115
LFBldgPGEESeNewCZ16 | Com-Iltg-dWatt-LF_OSbldg | PGE | ESe | New | CZ16 | 2.11 | 1.84e-05 | 0 | 2.12 | 1.84e-05 | -0.0317 | 2.11 | 1.84e-05 | 0 | 2.12 | 1.84e-05 | -0.0317 |  | LF | Bldg | 2110 | 0.0184 | 2110 | 0.0184 | 1 | 1 | -0.015024 | 2110 | 0.0184 | 2110 | 0.0184 | 1 | 1 | -0.015
LFBldgPGEESeNewIOU | Com-Iltg-dWatt-LF_OSbldg | PGE | ESe | New | IOU | 2.11 | 0.00010777 | 0 | 2.2792 | 0.0001347 | -0.026691 | 2.11 | 0.00010777 | 0 | 2.2792 | 0.0001347 | -0.026691 |  | LF | Bldg | 2110 | 0.108 | 2110 | 0.108 | 1.08 | 1.25 | -0.01265 | 2110 | 0.108 | 2110 | 0.108 | 1.08 | 1.25 | -0.0127
LFBldgPGEEUnExCZ01 | Com-Iltg-dWatt-LF_OSbldg | PGE | EUn | Ex | CZ01 | 2.346 | 0.00071776 | 0 | 2.4857 | 0.00087528 | -0.024657 | 2.2 | 0.00063992 | 0 | 2.33 | 0.00078089 | -0.0231 |  | LF | Bldg | 2350 | 0.718 | 2200 | 0.64 | 1.06 | 1.22 | -0.0105 | 2350 | 0.718 | 2200 | 0.64 | 1.06 | 1.22 | -0.0105
LFBldgPGEEUnExCZ02 | Com-Iltg-dWatt-LF_OSbldg | PGE | EUn | Ex | CZ02 | 2.3428 | 0.00043655 | 0 | 2.5914 | 0.00053702 | -0.017942 | 2.2 | 0.0003899 | 0 | 2.4295 | 0.0004799 | -0.016895 |  | LF | Bldg | 2340 | 0.437 | 2200 | 0.39 | 1.1 | 1.23 | -0.0076796 | 2340 | 0.437 | 2200 | 0.39 | 1.1 | 1.23 | -0.00768
LFBldgPGEEUnExCZ03 | Com-Iltg-dWatt-LF_OSbldg | PGE | EUn | Ex | CZ03 | 2.3445 | 0.00043713 | 0 | 2.5838 | 0.00051976 | -0.017556 | 2.2 | 0.00038993 | 0 | 2.42 | 0.00046389 | -0.016496 |  | LF | Bldg | 2340 | 0.437 | 2200 | 0.39 | 1.1 | 1.19 | -0.0074983 | 2340 | 0.437 | 2200 | 0.39 | 1.1 | 1.19 | -0.0075
LFBldgPGEEUnExCZ04 | Com-Iltg-dWatt-LF_OSbldg | PGE | EUn | Ex | CZ04 | 2.3422 | 0.00071568 | 0 | 2.6212 | 0.00091643 | -0.014053 | 2.2 | 0.00063984 | 0 | 2.46 | 0.00081974 | -0.0132 |  | LF | Bldg | 2340 | 0.716 | 2200 | 0.64 | 1.12 | 1.28 | -0.006 | 2340 | 0.716 | 2200 | 0.64 | 1.12 | 1.28 | -0.006
LFBldgPGEEUnExCZ05 | Com-Iltg-dWatt-LF_OSbldg | PGE | EUn | Ex | CZ05 | 2.3422 | 0.00071568 | 0 | 2.5712 | 0.00086875 | -0.016743 | 2.2 | 0.00063984 | 0 | 2.41 | 0.00077679 | -0.0157 |  | LF | Bldg | 2340 | 0.716 | 2200 | 0.64 | 1.1 | 1.21 | -0.0071364 | 2340 | 0.716 | 2200 | 0.64 | 1.1 | 1.21 | -0.00714
LFBldgPGEEUnExCZ11 | Com-Iltg-dWatt-LF_OSbldg | PGE | EUn | Ex | CZ11 | 2.3409 | 0.00043592 | 0 | 2.6297 | 0.00054319 | -0.016034 | 2.2 | 0.00038988 | 0 | 2.47 | 0.00048588 | -0.015 |  | LF | Bldg | 2340 | 0.436 | 2200 | 0.39 | 1.12 | 1.25 | -0.0068182 | 2340 | 0.436 | 2200 | 0.39 | 1.12 | 1.25 | -0.00682
LFBldgPGEEUnExCZ12 | Com-Iltg-dWatt-LF_OSbldg | PGE | EUn | Ex | CZ12 | 2.3413 | 0.00043603 | 0 | 2.6201 | 0.00053934 | -0.016136 | 2.2 | 0.00038988 | 0 | 2.46 | 0.00048283 | -0.0151 |  | LF | Bldg | 2340 | 0.436 | 2200 | 0.39 | 1.12 | 1.24 | -0.0068636 | 2340 | 0.436 | 2200 | 0.39 | 1.12 | 1.24 | -0.00686
LFBldgPGEEUnExCZ13 | Com-Iltg-dWatt-LF_OSbldg | PGE | EUn | Ex | CZ13 | 2.341 | 0.00043593 | 0 | 2.6492 | 0.00055209 | -0.01414 | 2.2 | 0.00038988 | 0 | 2.4894 | 0.00049382 | -0.0132 |  | LF | Bldg | 2340 | 0.436 | 2200 | 0.39 | 1.13 | 1.27 | -0.006 | 2340 | 0.436 | 2200 | 0.39 | 1.13 | 1.27 | -0.006
LFBldgPGEEUnExCZ16 | Com-Iltg-dWatt-LF_OSbldg | PGE | EUn | Ex | CZ16 | 2.3433 | 0.00043672 | 0 | 2.5024 | 0.00052427 | -0.025524 | 2.2 | 0.00038991 | 0 | 2.3496 | 0.00046791 | -0.023996 |  | LF | Bldg | 2340 | 0.437 | 2200 | 0.39 | 1.07 | 1.2 | -0.010907 | 2340 | 0.437 | 2200 | 0.39 | 1.07 | 1.2 | -0.0109
LFBldgPGEEUnExIOU | Com-Iltg-dWatt-LF_OSbldg | PGE | EUn | Ex | IOU | 2.3428 | 0.00048984 | 0 | 2.6016 | 0.00060126 | -0.016643 | 2.2 | 0.00043757 | 0 | 2.4401 | 0.00053737 | -0.015611 |  | LF | Bldg | 2340 | 0.49 | 2200 | 0.438 | 1.11 | 1.23 | -0.0070958 | 2340 | 0.49 | 2200 | 0.438 | 1.11 | 1.23 | -0.0071
LFBldgPGEEUnNewCZ01 | Com-Iltg-dWatt-LF_OSbldg | PGE | EUn | New | CZ01 | 2.2 | 0.000637 | 0 | 2.31 | 0.00075 | -0.018 | 2.2 | 0.000637 | 0 | 2.31 | 0.00075 | -0.018 |  | LF | Bldg | 2200 | 0.637 | 2200 | 0.637 | 1.05 | 1.18 | -0.0081818 | 2200 | 0.637 | 2200 | 0.637 | 1.05 | 1.18 | -0.00818
LFBldgPGEEUnNewCZ02 | Com-Iltg-dWatt-LF_OSbldg | PGE | EUn | New | CZ02 | 2.2 | 0.000388 | 0 | 2.45 | 0.000509 | -0.013 | 2.2 | 0.000388 | 0 | 2.45 | 0.000509 | -0.013 |  | LF | Bldg | 2200 | 0.388 | 2200 | 0.388 | 1.11 | 1.31 | -0.0059091 | 2200 | 0.388 | 2200 | 0.388 | 1.11 | 1.31 | -0.00591
LFBldgPGEEUnNewCZ03 | Com-Iltg-dWatt-LF_OSbldg | PGE | EUn | New | CZ03 | 2.2 | 0.000388 | 0 | 2.4 | 0.000494 | -0.0124 | 2.2 | 0.000388 | 0 | 2.4 | 0.000494 | -0.0124 |  | LF | Bldg | 2200 | 0.388 | 2200 | 0.388 | 1.09 | 1.27 | -0.0056364 | 2200 | 0.388 | 2200 | 0.388 | 1.09 | 1.27 | -0.00564
LFBldgPGEEUnNewCZ04 | Com-Iltg-dWatt-LF_OSbldg | PGE | EUn | New | CZ04 | 2.2 | 0.000637 | 0 | 2.47 | 0.000803 | -0.0103 | 2.2 | 0.000637 | 0 | 2.47 | 0.000803 | -0.0103 |  | LF | Bldg | 2200 | 0.637 | 2200 | 0.637 | 1.12 | 1.26 | -0.0046818 | 2200 | 0.637 | 2200 | 0.637 | 1.12 | 1.26 | -0.00468
LFBldgPGEEUnNewCZ05 | Com-Iltg-dWatt-LF_OSbldg | PGE | EUn | New | CZ05 | 2.2 | 0.000637 | 0 | 2.4 | 0.00077 | -0.0119 | 2.2 | 0.000637 | 0 | 2.4 | 0.00077 | -0.0119 |  | LF | Bldg | 2200 | 0.637 | 2200 | 0.637 | 1.09 | 1.21 | -0.0054091 | 2200 | 0.637 | 2200 | 0.637 | 1.09 | 1.21 | -0.00541
LFBldgPGEEUnNewCZ11 | Com-Iltg-dWatt-LF_OSbldg | PGE | EUn | New | CZ11 | 2.2 | 0.000388 | 0 | 2.51 | 0.00051 | -0.0117 | 2.2 | 0.000388 | 0 | 2.51 | 0.00051 | -0.0117 |  | LF | Bldg | 2200 | 0.388 | 2200 | 0.388 | 1.14 | 1.31 | -0.0053182 | 2200 | 0.388 | 2200 | 0.388 | 1.14 | 1.31 | -0.00532
LFBldgPGEEUnNewCZ12 | Com-Iltg-dWatt-LF_OSbldg | PGE | EUn | New | CZ12 | 2.2 | 0.000388 | 0 | 2.5 | 0.00051 | -0.0109 | 2.2 | 0.000388 | 0 | 2.5 | 0.00051 | -0.0109 |  | LF | Bldg | 2200 | 0.388 | 2200 | 0.388 | 1.14 | 1.31 | -0.0049545 | 2200 | 0.388 | 2200 | 0.388 | 1.14 | 1.31 | -0.00495
LFBldgPGEEUnNewCZ13 | Com-Iltg-dWatt-LF_OSbldg | PGE | EUn | New | CZ13 | 2.2 | 0.000388 | 0 | 2.53 | 0.00051 | -0.0105 | 2.2 | 0.000388 | 0 | 2.53 | 0.00051 | -0.0105 |  | LF | Bldg | 2200 | 0.388 | 2200 | 0.388 | 1.15 | 1.31 | -0.0047727 | 2200 | 0.388 | 2200 | 0.388 | 1.15 | 1.31 | -0.00477
LFBldgPGEEUnNewCZ16 | Com-Iltg-dWatt-LF_OSbldg | PGE | EUn | New | CZ16 | 2.2 | 0.000388 | 0 | 2.36 | 0.000489 | -0.021 | 2.2 | 0.000388 | 0 | 2.36 | 0.000489 | -0.021 |  | LF | Bldg | 2200 | 0.388 | 2200 | 0.388 | 1.07 | 1.26 | -0.0095455 | 2200 | 0.388 | 2200 | 0.388 | 1.07 | 1.26 | -0.00955
LFBldgPGEEUnNewIOU | Com-Iltg-dWatt-LF_OSbldg | PGE | EUn | New | IOU | 2.2 | 0.00043578 | 0 | 2.4603 | 0.00055821 | -0.01166 | 2.2 | 0.00043578 | 0 | 2.4603 | 0.00055821 | -0.01166 |  | LF | Bldg | 2200 | 0.436 | 2200 | 0.436 | 1.12 | 1.28 | -0.0052998 | 2200 | 0.436 | 2200 | 0.436 | 1.12 | 1.28 | -0.0053
LFBldgPGEGroExCZ01 | Com-Iltg-dWatt-LF_OSbldg | PGE | Gro | Ex | CZ01 | 4.9073 | 0.00068963 | 0 | 3.9182 | 0.00068463 | -0.088256 | 4.85 | 0.000682 | 0 | 3.88 | 0.00067795 | -0.087397 |  | LF | Bldg | 4910 | 0.69 | 4850 | 0.682 | 0.8 | 0.994 | -0.01802 | 4910 | 0.69 | 4850 | 0.682 | 0.8 | 0.994 | -0.018
LFBldgPGEGroExCZ02 | Com-Iltg-dWatt-LF_OSbldg | PGE | Gro | Ex | CZ02 | 4.9071 | 0.00068961 | 0 | 4.4777 | 0.00089251 | -0.065167 | 4.85 | 0.000682 | 0 | 4.4397 | 0.000883 | -0.064597 |  | LF | Bldg | 4910 | 0.69 | 4850 | 0.682 | 0.915 | 1.29 | -0.013319 | 4910 | 0.69 | 4850 | 0.682 | 0.915 | 1.29 | -0.0133
LFBldgPGEGroExCZ03 | Com-Iltg-dWatt-LF_OSbldg | PGE | Gro | Ex | CZ03 | 4.9073 | 0.00068964 | 0 | 4.2779 | 0.00085455 | -0.074561 | 4.85 | 0.000682 | 0 | 4.2397 | 0.000845 | -0.073797 |  | LF | Bldg | 4910 | 0.69 | 4850 | 0.682 | 0.874 | 1.24 | -0.015216 | 4910 | 0.69 | 4850 | 0.682 | 0.874 | 1.24 | -0.0152
LFBldgPGEGroExCZ04 | Com-Iltg-dWatt-LF_OSbldg | PGE | Gro | Ex | CZ04 | 4.9069 | 0.00068959 | 0 | 4.5875 | 0.00087949 | -0.06177 | 4.85 | 0.000682 | 0 | 4.54 | 0.00087 | -0.0612 |  | LF | Bldg | 4910 | 0.69 | 4850 | 0.682 | 0.936 | 1.28 | -0.012619 | 4910 | 0.69 | 4850 | 0.682 | 0.936 | 1.28 | -0.0126
LFBldgPGEGroExCZ05 | Com-Iltg-dWatt-LF_OSbldg | PGE | Gro | Ex | CZ05 | 4.9069 | 0.00068959 | 0 | 4.2475 | 0.00084149 | -0.074559 | 4.85 | 0.000682 | 0 | 4.2 | 0.000832 | -0.0738 |  | LF | Bldg | 4910 | 0.69 | 4850 | 0.682 | 0.866 | 1.22 | -0.015216 | 4910 | 0.69 | 4850 | 0.682 | 0.866 | 1.22 | -0.0152
LFBldgPGEGroExCZ11 | Com-Iltg-dWatt-LF_OSbldg | PGE | Gro | Ex | CZ11 | 4.9056 | 0.00068941 | 0 | 4.8263 | 0.00090826 | -0.052956 | 4.85 | 0.000682 | 0 | 4.78 | 0.000899 | -0.0524 |  | LF | Bldg | 4910 | 0.689 | 4850 | 0.682 | 0.986 | 1.32 | -0.010804 | 4910 | 0.689 | 4850 | 0.682 | 0.986 | 1.32 | -0.0108
LFBldgPGEGroExCZ12 | Com-Iltg-dWatt-LF_OSbldg | PGE | Gro | Ex | CZ12 | 4.9061 | 0.00068948 | 0 | 4.7267 | 0.00089035 | -0.057361 | 4.85 | 0.000682 | 0 | 4.68 | 0.00088194 | -0.0568 |  | LF | Bldg | 4910 | 0.689 | 4850 | 0.682 | 0.965 | 1.29 | -0.011711 | 4910 | 0.689 | 4850 | 0.682 | 0.965 | 1.29 | -0.0117
LFBldgPGEGroExCZ13 | Com-Iltg-dWatt-LF_OSbldg | PGE | Gro | Ex | CZ13 | 4.9055 | 0.0006894 | 0 | 4.8855 | 0.00089025 | -0.049962 | 4.85 | 0.000682 | 0 | 4.83 | 0.00088192 | -0.0495 |  | LF | Bldg | 4910 | 0.689 | 4850 | 0.682 | 0.996 | 1.29 | -0.010206 | 4910 | 0.689 | 4850 | 0.682 | 0.996 | 1.29 | -0.0102
LFBldgPGEGroExCZ16 | Com-Iltg-dWatt-LF_OSbldg | PGE | Gro | Ex | CZ16 | 4.9082 | 0.00068982 | 0 | 4.2889 | 0.00085678 | -0.069678 | 4.85 | 0.000682 | 0 | 4.24 | 0.00084789 | -0.0689 |  | LF | Bldg | 4910 | 0.69 | 4850 | 0.682 | 0.874 | 1.24 | -0.014206 | 4910 | 0.69 | 4850 | 0.682 | 0.874 | 1.24 | -0.0142
LFBldgPGEGroExIOU | Com-Iltg-dWatt-LF_OSbldg | PGE | Gro | Ex | IOU | 4.9065 | 0.00068954 | 0 | 4.5705 | 0.00087649 | -0.062752 | 4.85 | 0.000682 | 0 | 4.5254 | 0.00086747 | -0.062138 |  | LF | Bldg | 4910 | 0.69 | 4850 | 0.682 | 0.933 | 1.27 | -0.012812 | 4910 | 0.69 | 4850 | 0.682 | 0.933 | 1.27 | -0.0128
LFBldgPGEGroNewCZ01 | Com-Iltg-dWatt-LF_OSbldg | PGE | Gro | New | CZ01 | 4.85 | 0.000682 | 0 | 4.06 | 0.000773 | -0.0898 | 4.85 | 0.000682 | 0 | 4.06 | 0.000773 | -0.0898 |  | LF | Bldg | 4850 | 0.682 | 4850 | 0.682 | 0.837 | 1.13 | -0.018515 | 4850 | 0.682 | 4850 | 0.682 | 0.837 | 1.13 | -0.0185
LFBldgPGEGroNewCZ02 | Com-Iltg-dWatt-LF_OSbldg | PGE | Gro | New | CZ02 | 4.85 | 0.000682 | 0 | 4.66 | 0.000914 | -0.0626 | 4.85 | 0.000682 | 0 | 4.66 | 0.000914 | -0.0626 |  | LF | Bldg | 4850 | 0.682 | 4850 | 0.682 | 0.961 | 1.34 | -0.012907 | 4850 | 0.682 | 4850 | 0.682 | 0.961 | 1.34 | -0.0129
LFBldgPGEGroNewCZ03 | Com-Iltg-dWatt-LF_OSbldg | PGE | Gro | New | CZ03 | 4.85 | 0.000682 | 0 | 4.45 | 0.000864 | -0.0699 | 4.85 | 0.000682 | 0 | 4.45 | 0.000864 | -0.0699 |  | LF | Bldg | 4850 | 0.682 | 4850 | 0.682 | 0.918 | 1.27 | -0.014412 | 4850 | 0.682 | 4850 | 0.682 | 0.918 | 1.27 | -0.0144
LFBldgPGEGroNewCZ04 | Com-Iltg-dWatt-LF_OSbldg | PGE | Gro | New | CZ04 | 4.85 | 0.000682 | 0 | 4.81 | 0.00089 | -0.0558 | 4.85 | 0.000682 | 0 | 4.81 | 0.00089 | -0.0558 |  | LF | Bldg | 4850 | 0.682 | 4850 | 0.682 | 0.992 | 1.3 | -0.011505 | 4850 | 0.682 | 4850 | 0.682 | 0.992 | 1.3 | -0.0115
LFBldgPGEGroNewCZ05 | Com-Iltg-dWatt-LF_OSbldg | PGE | Gro | New | CZ05 | 4.85 | 0.000682 | 0 | 4.42 | 0.000845 | -0.0694 | 4.85 | 0.000682 | 0 | 4.42 | 0.000845 | -0.0694 |  | LF | Bldg | 4850 | 0.682 | 4850 | 0.682 | 0.911 | 1.24 | -0.014309 | 4850 | 0.682 | 4850 | 0.682 | 0.911 | 1.24 | -0.0143
LFBldgPGEGroNewCZ11 | Com-Iltg-dWatt-LF_OSbldg | PGE | Gro | New | CZ11 | 4.85 | 0.000682 | 0 | 4.98 | 0.000936 | -0.05 | 4.85 | 0.000682 | 0 | 4.98 | 0.000936 | -0.05 |  | LF | Bldg | 4850 | 0.682 | 4850 | 0.682 | 1.03 | 1.37 | -0.010309 | 4850 | 0.682 | 4850 | 0.682 | 1.03 | 1.37 | -0.0103
LFBldgPGEGroNewCZ12 | Com-Iltg-dWatt-LF_OSbldg | PGE | Gro | New | CZ12 | 4.85 | 0.000682 | 0 | 4.89 | 0.000922 | -0.0539 | 4.85 | 0.000682 | 0 | 4.89 | 0.000922 | -0.0539 |  | LF | Bldg | 4850 | 0.682 | 4850 | 0.682 | 1.01 | 1.35 | -0.011113 | 4850 | 0.682 | 4850 | 0.682 | 1.01 | 1.35 | -0.0111
LFBldgPGEGroNewCZ13 | Com-Iltg-dWatt-LF_OSbldg | PGE | Gro | New | CZ13 | 4.85 | 0.000682 | 0 | 5.03 | 0.000919 | -0.0473 | 4.85 | 0.000682 | 0 | 5.03 | 0.000919 | -0.0473 |  | LF | Bldg | 4850 | 0.682 | 4850 | 0.682 | 1.04 | 1.35 | -0.0097526 | 4850 | 0.682 | 4850 | 0.682 | 1.04 | 1.35 | -0.00975
LFBldgPGEGroNewCZ16 | Com-Iltg-dWatt-LF_OSbldg | PGE | Gro | New | CZ16 | 4.85 | 0.000682 | 0 | 4.45 | 0.000862 | -0.0655 | 4.85 | 0.000682 | 0 | 4.45 | 0.000862 | -0.0655 |  | LF | Bldg | 4850 | 0.682 | 4850 | 0.682 | 0.918 | 1.26 | -0.013505 | 4850 | 0.682 | 4850 | 0.682 | 0.918 | 1.26 | -0.0135
LFBldgPGEGroNewIOU | Com-Iltg-dWatt-LF_OSbldg | PGE | Gro | New | IOU | 4.85 | 0.000682 | 0 | 4.7865 | 0.00090246 | -0.057148 | 4.85 | 0.000682 | 0 | 4.7865 | 0.00090246 | -0.057148 |  | LF | Bldg | 4850 | 0.682 | 4850 | 0.682 | 0.987 | 1.32 | -0.011783 | 4850 | 0.682 | 4850 | 0.682 | 0.987 | 1.32 | -0.0118
LFBldgPGEHspExCZ01 | Com-Iltg-dWatt-LF_OSbldg | PGE | Hsp | Ex | CZ01 | 5.2597 | 0.00082697 | 0 | 5.6497 | 0.00096196 | -0.044997 | 5.24 | 0.00082204 | 0 | 5.6207 | 0.00095604 | -0.044803 |  | LF | Bldg | 5260 | 0.827 | 5240 | 0.822 | 1.07 | 1.16 | -0.0085502 | 5260 | 0.827 | 5240 | 0.822 | 1.07 | 1.16 | -0.00855
LFBldgPGEHspExCZ02 | Com-Iltg-dWatt-LF_OSbldg | PGE | Hsp | Ex | CZ02 | 5.2597 | 0.00082697 | 0 | 5.8 | 0.0010295 | -0.035202 | 5.24 | 0.00082205 | 0 | 5.78 | 0.00102 | -0.0351 |  | LF | Bldg | 5260 | 0.827 | 5240 | 0.822 | 1.1 | 1.24 | -0.0066985 | 5260 | 0.827 | 5240 | 0.822 | 1.1 | 1.24 | -0.0067
LFBldgPGEHspExCZ03 | Com-Iltg-dWatt-LF_OSbldg | PGE | Hsp | Ex | CZ03 | 5.2597 | 0.00082697 | 0 | 5.83 | 0.0010001 | -0.033198 | 5.24 | 0.00082205 | 0 | 5.81 | 0.00099597 | -0.033008 |  | LF | Bldg | 5260 | 0.827 | 5240 | 0.822 | 1.11 | 1.21 | -0.0062992 | 5260 | 0.827 | 5240 | 0.822 | 1.11 | 1.21 | -0.0063
LFBldgPGEHspExCZ04 | Com-Iltg-dWatt-LF_OSbldg | PGE | Hsp | Ex | CZ04 | 5.2677 | 0.00082896 | 0 | 5.842 | 0.0010195 | -0.031538 | 5.24 | 0.00082205 | 0 | 5.81 | 0.00101 | -0.0314 |  | LF | Bldg | 5270 | 0.829 | 5240 | 0.822 | 1.11 | 1.23 | -0.0059924 | 5270 | 0.829 | 5240 | 0.822 | 1.11 | 1.23 | -0.00599
LFBldgPGEHspExCZ05 | Com-Iltg-dWatt-LF_OSbldg | PGE | Hsp | Ex | CZ05 | 5.2677 | 0.00082896 | 0 | 5.752 | 0.00098535 | -0.035382 | 5.24 | 0.00082205 | 0 | 5.72 | 0.00097756 | -0.0352 |  | LF | Bldg | 5270 | 0.829 | 5240 | 0.822 | 1.09 | 1.19 | -0.0067176 | 5270 | 0.829 | 5240 | 0.822 | 1.09 | 1.19 | -0.00672
LFBldgPGEHspExCZ11 | Com-Iltg-dWatt-LF_OSbldg | PGE | Hsp | Ex | CZ11 | 5.2668 | 0.00082875 | 0 | 5.8668 | 0.0010334 | -0.032927 | 5.24 | 0.00082206 | 0 | 5.8346 | 0.00102 | -0.0327 |  | LF | Bldg | 5270 | 0.829 | 5240 | 0.822 | 1.11 | 1.24 | -0.0062405 | 5270 | 0.829 | 5240 | 0.822 | 1.11 | 1.24 | -0.00624
LFBldgPGEHspExCZ12 | Com-Iltg-dWatt-LF_OSbldg | PGE | Hsp | Ex | CZ12 | 5.2587 | 0.00082675 | 0 | 5.8387 | 0.0010294 | -0.031987 | 5.24 | 0.00082206 | 0 | 5.82 | 0.00102 | -0.0318 |  | LF | Bldg | 5260 | 0.827 | 5240 | 0.822 | 1.11 | 1.24 | -0.0060687 | 5260 | 0.827 | 5240 | 0.822 | 1.11 | 1.24 | -0.00607
LFBldgPGEHspExCZ13 | Com-Iltg-dWatt-LF_OSbldg | PGE | Hsp | Ex | CZ13 | 5.2587 | 0.00082675 | 0 | 5.8887 | 0.0010294 | -0.030787 | 5.24 | 0.00082206 | 0 | 5.87 | 0.00102 | -0.0306 |  | LF | Bldg | 5260 | 0.827 | 5240 | 0.822 | 1.12 | 1.24 | -0.0058397 | 5260 | 0.827 | 5240 | 0.822 | 1.12 | 1.24 | -0.00584
LFBldgPGEHspExCZ16 | Com-Iltg-dWatt-LF_OSbldg | PGE | Hsp | Ex | CZ16 | 5.261 | 0.00082731 | 0 | 5.562 | 0.00099699 | -0.05041 | 5.24 | 0.00082205 | 0 | 5.54 | 0.000991 | -0.05021 |  | LF | Bldg | 5260 | 0.827 | 5240 | 0.822 | 1.06 | 1.21 | -0.0095821 | 5260 | 0.827 | 5240 | 0.822 | 1.06 | 1.21 | -0.00958
LFBldgPGEHspExIOU | Com-Iltg-dWatt-LF_OSbldg | PGE | Hsp | Ex | IOU | 5.261 | 0.0008273 | 0 | 5.8382 | 0.0010182 | -0.032736 | 5.24 | 0.00082205 | 0 | 5.816 | 0.0010101 | -0.032559 |  | LF | Bldg | 5260 | 0.827 | 5240 | 0.822 | 1.11 | 1.23 | -0.0062136 | 5260 | 0.827 | 5240 | 0.822 | 1.11 | 1.23 | -0.00621
LFBldgPGEHspNewCZ01 | Com-Iltg-dWatt-LF_OSbldg | PGE | Hsp | New | CZ01 | 5.24 | 0.000823 | 0 | 5.37 | 0.000927 | -0.0442 | 5.24 | 0.000823 | 0 | 5.37 | 0.000927 | -0.0442 |  | LF | Bldg | 5240 | 0.823 | 5240 | 0.823 | 1.02 | 1.13 | -0.0084351 | 5240 | 0.823 | 5240 | 0.823 | 1.02 | 1.13 | -0.00844
LFBldgPGEHspNewCZ02 | Com-Iltg-dWatt-LF_OSbldg | PGE | Hsp | New | CZ02 | 5.24 | 0.000823 | 0 | 5.57 | 0.000989 | -0.0364 | 5.24 | 0.000823 | 0 | 5.57 | 0.000989 | -0.0364 |  | LF | Bldg | 5240 | 0.823 | 5240 | 0.823 | 1.06 | 1.2 | -0.0069466 | 5240 | 0.823 | 5240 | 0.823 | 1.06 | 1.2 | -0.00695
LFBldgPGEHspNewCZ03 | Com-Iltg-dWatt-LF_OSbldg | PGE | Hsp | New | CZ03 | 5.24 | 0.000823 | 0 | 5.55 | 0.000964 | -0.0328 | 5.24 | 0.000823 | 0 | 5.55 | 0.000964 | -0.0328 |  | LF | Bldg | 5240 | 0.823 | 5240 | 0.823 | 1.06 | 1.17 | -0.0062595 | 5240 | 0.823 | 5240 | 0.823 | 1.06 | 1.17 | -0.00626
LFBldgPGEHspNewCZ04 | Com-Iltg-dWatt-LF_OSbldg | PGE | Hsp | New | CZ04 | 5.24 | 0.000823 | 0 | 5.6 | 0.00098 | -0.0325 | 5.24 | 0.000823 | 0 | 5.6 | 0.00098 | -0.0325 |  | LF | Bldg | 5240 | 0.823 | 5240 | 0.823 | 1.07 | 1.19 | -0.0062023 | 5240 | 0.823 | 5240 | 0.823 | 1.07 | 1.19 | -0.0062
LFBldgPGEHspNewCZ05 | Com-Iltg-dWatt-LF_OSbldg | PGE | Hsp | New | CZ05 | 5.24 | 0.000823 | 0 | 5.52 | 0.000953 | -0.0361 | 5.24 | 0.000823 | 0 | 5.52 | 0.000953 | -0.0361 |  | LF | Bldg | 5240 | 0.823 | 5240 | 0.823 | 1.05 | 1.16 | -0.0068893 | 5240 | 0.823 | 5240 | 0.823 | 1.05 | 1.16 | -0.00689
LFBldgPGEHspNewCZ11 | Com-Iltg-dWatt-LF_OSbldg | PGE | Hsp | New | CZ11 | 5.24 | 0.000823 | 0 | 5.69 | 0.000993 | -0.0333 | 5.24 | 0.000823 | 0 | 5.69 | 0.000993 | -0.0333 |  | LF | Bldg | 5240 | 0.823 | 5240 | 0.823 | 1.09 | 1.21 | -0.006355 | 5240 | 0.823 | 5240 | 0.823 | 1.09 | 1.21 | -0.00636
LFBldgPGEHspNewCZ12 | Com-Iltg-dWatt-LF_OSbldg | PGE | Hsp | New | CZ12 | 5.24 | 0.000823 | 0 | 5.64 | 0.000996 | -0.0327 | 5.24 | 0.000823 | 0 | 5.64 | 0.000996 | -0.0327 |  | LF | Bldg | 5240 | 0.823 | 5240 | 0.823 | 1.08 | 1.21 | -0.0062405 | 5240 | 0.823 | 5240 | 0.823 | 1.08 | 1.21 | -0.00624
LFBldgPGEHspNewCZ13 | Com-Iltg-dWatt-LF_OSbldg | PGE | Hsp | New | CZ13 | 5.24 | 0.000823 | 0 | 5.7 | 0.000993 | -0.0317 | 5.24 | 0.000823 | 0 | 5.7 | 0.000993 | -0.0317 |  | LF | Bldg | 5240 | 0.823 | 5240 | 0.823 | 1.09 | 1.21 | -0.0060496 | 5240 | 0.823 | 5240 | 0.823 | 1.09 | 1.21 | -0.00605
LFBldgPGEHspNewCZ16 | Com-Iltg-dWatt-LF_OSbldg | PGE | Hsp | New | CZ16 | 5.24 | 0.000823 | 0 | 5.34 | 0.000961 | -0.0534 | 5.24 | 0.000823 | 0 | 5.34 | 0.000961 | -0.0534 |  | LF | Bldg | 5240 | 0.823 | 5240 | 0.823 | 1.02 | 1.17 | -0.010191 | 5240 | 0.823 | 5240 | 0.823 | 1.02 | 1.17 | -0.0102
LFBldgPGEHspNewIOU | Com-Iltg-dWatt-LF_OSbldg | PGE | Hsp | New | IOU | 5.24 | 0.000823 | 0 | 5.6167 | 0.0009833 | -0.033122 | 5.24 | 0.000823 | 0 | 5.6167 | 0.0009833 | -0.033122 |  | LF | Bldg | 5240 | 0.823 | 5240 | 0.823 | 1.07 | 1.19 | -0.006321 | 5240 | 0.823 | 5240 | 0.823 | 1.07 | 1.19 | -0.00632
LFBldgPGEHtlExCZ01 | Com-Iltg-dWatt-LF_OSbldg | PGE | Htl | Ex | CZ01 | 1.9475 | 0.00024169 | 0 | 1.7075 | 0.00029363 | -0.011981 | 1.91 | 0.000237 | 0 | 1.67 | 0.000288 | -0.0117 |  | LF | Bldg | 1950 | 0.242 | 1910 | 0.237 | 0.874 | 1.22 | -0.0061257 | 1950 | 0.242 | 1910 | 0.237 | 0.874 | 1.22 | -0.00613
LFBldgPGEHtlExCZ02 | Com-Iltg-dWatt-LF_OSbldg | PGE | Htl | Ex | CZ02 | 1.9476 | 0.00024171 | 0 | 1.8877 | 0.00030059 | -0.0085794 | 1.91 | 0.000237 | 0 | 1.85 | 0.00029494 | -0.0084288 |  | LF | Bldg | 1950 | 0.242 | 1910 | 0.237 | 0.969 | 1.24 | -0.004413 | 1950 | 0.242 | 1910 | 0.237 | 0.969 | 1.24 | -0.00441
LFBldgPGEHtlExCZ03 | Com-Iltg-dWatt-LF_OSbldg | PGE | Htl | Ex | CZ03 | 1.9489 | 0.00024186 | 0 | 1.9089 | 0.0002978 | -0.0084149 | 1.91 | 0.000237 | 0 | 1.8797 | 0.00029197 | -0.0082594 |  | LF | Bldg | 1950 | 0.242 | 1910 | 0.237 | 0.984 | 1.23 | -0.0043243 | 1950 | 0.242 | 1910 | 0.237 | 0.984 | 1.23 | -0.00432
LFBldgPGEHtlExCZ04 | Com-Iltg-dWatt-LF_OSbldg | PGE | Htl | Ex | CZ04 | 1.9475 | 0.00024169 | 0 | 1.9675 | 0.00029957 | -0.0069613 | 1.91 | 0.000237 | 0 | 1.93 | 0.00029394 | -0.0068394 |  | LF | Bldg | 1950 | 0.242 | 1910 | 0.237 | 1.01 | 1.24 | -0.0035808 | 1950 | 0.242 | 1910 | 0.237 | 1.01 | 1.24 | -0.00358
LFBldgPGEHtlExCZ05 | Com-Iltg-dWatt-LF_OSbldg | PGE | Htl | Ex | CZ05 | 1.9475 | 0.00024169 | 0 | 1.8875 | 0.00029456 | -0.0085588 | 1.91 | 0.000237 | 0 | 1.85 | 0.00028894 | -0.0084088 |  | LF | Bldg | 1950 | 0.242 | 1910 | 0.237 | 0.969 | 1.22 | -0.0044025 | 1950 | 0.242 | 1910 | 0.237 | 0.969 | 1.22 | -0.0044
LFBldgPGEHtlExCZ11 | Com-Iltg-dWatt-LF_OSbldg | PGE | Htl | Ex | CZ11 | 1.9473 | 0.00024166 | 0 | 1.9773 | 0.00030552 | -0.0072897 | 1.91 | 0.000237 | 0 | 1.9493 | 0.00029993 | -0.0071686 |  | LF | Bldg | 1950 | 0.242 | 1910 | 0.237 | 1.02 | 1.27 | -0.0037532 | 1950 | 0.242 | 1910 | 0.237 | 1.02 | 1.27 | -0.00375
LFBldgPGEHtlExCZ12 | Com-Iltg-dWatt-LF_OSbldg | PGE | Htl | Ex | CZ12 | 1.9469 | 0.00024162 | 0 | 1.9469 | 0.00030454 | -0.0075677 | 1.91 | 0.000237 | 0 | 1.9192 | 0.000299 | -0.0074385 |  | LF | Bldg | 1950 | 0.242 | 1910 | 0.237 | 1 | 1.26 | -0.0038945 | 1950 | 0.242 | 1910 | 0.237 | 1 | 1.26 | -0.00389
LFBldgPGEHtlExCZ13 | Com-Iltg-dWatt-LF_OSbldg | PGE | Htl | Ex | CZ13 | 1.9474 | 0.00024167 | 0 | 2.0074 | 0.0003026 | -0.0067908 | 1.91 | 0.000237 | 0 | 1.97 | 0.000297 | -0.0066693 |  | LF | Bldg | 1950 | 0.242 | 1910 | 0.237 | 1.03 | 1.25 | -0.0034918 | 1950 | 0.242 | 1910 | 0.237 | 1.03 | 1.25 | -0.00349
LFBldgPGEHtlExCZ16 | Com-Iltg-dWatt-LF_OSbldg | PGE | Htl | Ex | CZ16 | 1.9474 | 0.00024168 | 0 | 1.7474 | 0.00029461 | -0.012581 | 1.91 | 0.000237 | 0 | 1.71 | 0.00028994 | -0.012393 |  | LF | Bldg | 1950 | 0.242 | 1910 | 0.237 | 0.895 | 1.22 | -0.0064887 | 1950 | 0.242 | 1910 | 0.237 | 0.895 | 1.22 | -0.00649
LFBldgPGEHtlExIOU | Com-Iltg-dWatt-LF_OSbldg | PGE | Htl | Ex | IOU | 1.948 | 0.00024175 | 0 | 1.9249 | 0.00029952 | -0.008053 | 1.91 | 0.000237 | 0 | 1.8928 | 0.00029384 | -0.0079083 |  | LF | Bldg | 1950 | 0.242 | 1910 | 0.237 | 0.991 | 1.24 | -0.0041405 | 1950 | 0.242 | 1910 | 0.237 | 0.991 | 1.24 | -0.00414
LFBldgPGEHtlNewCZ01 | Com-Iltg-dWatt-LF_OSbldg | PGE | Htl | New | CZ01 | 1.91 | 0.000237 | 0 | 1.6 | 0.000281 | -0.0147 | 1.91 | 0.000237 | 0 | 1.6 | 0.000281 | -0.0147 |  | LF | Bldg | 1910 | 0.237 | 1910 | 0.237 | 0.838 | 1.19 | -0.0076963 | 1910 | 0.237 | 1910 | 0.237 | 0.838 | 1.19 | -0.0077
LFBldgPGEHtlNewCZ02 | Com-Iltg-dWatt-LF_OSbldg | PGE | Htl | New | CZ02 | 1.91 | 0.000237 | 0 | 1.81 | 0.000302 | -0.0106 | 1.91 | 0.000237 | 0 | 1.81 | 0.000302 | -0.0106 |  | LF | Bldg | 1910 | 0.237 | 1910 | 0.237 | 0.948 | 1.27 | -0.0055497 | 1910 | 0.237 | 1910 | 0.237 | 0.948 | 1.27 | -0.00555
LFBldgPGEHtlNewCZ03 | Com-Iltg-dWatt-LF_OSbldg | PGE | Htl | New | CZ03 | 1.91 | 0.000237 | 0 | 1.8 | 0.000293 | -0.00996 | 1.91 | 0.000237 | 0 | 1.8 | 0.000293 | -0.00996 |  | LF | Bldg | 1910 | 0.237 | 1910 | 0.237 | 0.942 | 1.24 | -0.0052147 | 1910 | 0.237 | 1910 | 0.237 | 0.942 | 1.24 | -0.00521
LFBldgPGEHtlNewCZ04 | Com-Iltg-dWatt-LF_OSbldg | PGE | Htl | New | CZ04 | 1.91 | 0.000237 | 0 | 1.89 | 0.000298 | -0.00858 | 1.91 | 0.000237 | 0 | 1.89 | 0.000298 | -0.00858 |  | LF | Bldg | 1910 | 0.237 | 1910 | 0.237 | 0.99 | 1.26 | -0.0044921 | 1910 | 0.237 | 1910 | 0.237 | 0.99 | 1.26 | -0.00449
LFBldgPGEHtlNewCZ05 | Com-Iltg-dWatt-LF_OSbldg | PGE | Htl | New | CZ05 | 1.91 | 0.000237 | 0 | 1.79 | 0.00029 | -0.0103 | 1.91 | 0.000237 | 0 | 1.79 | 0.00029 | -0.0103 |  | LF | Bldg | 1910 | 0.237 | 1910 | 0.237 | 0.937 | 1.22 | -0.0053927 | 1910 | 0.237 | 1910 | 0.237 | 0.937 | 1.22 | -0.00539
LFBldgPGEHtlNewCZ11 | Com-Iltg-dWatt-LF_OSbldg | PGE | Htl | New | CZ11 | 1.91 | 0.000237 | 0 | 1.91 | 0.000304 | -0.00919 | 1.91 | 0.000237 | 0 | 1.91 | 0.000304 | -0.00919 |  | LF | Bldg | 1910 | 0.237 | 1910 | 0.237 | 1 | 1.28 | -0.0048115 | 1910 | 0.237 | 1910 | 0.237 | 1 | 1.28 | -0.00481
LFBldgPGEHtlNewCZ12 | Com-Iltg-dWatt-LF_OSbldg | PGE | Htl | New | CZ12 | 1.91 | 0.000237 | 0 | 1.89 | 0.000303 | -0.00921 | 1.91 | 0.000237 | 0 | 1.89 | 0.000303 | -0.00921 |  | LF | Bldg | 1910 | 0.237 | 1910 | 0.237 | 0.99 | 1.28 | -0.004822 | 1910 | 0.237 | 1910 | 0.237 | 0.99 | 1.28 | -0.00482
LFBldgPGEHtlNewCZ13 | Com-Iltg-dWatt-LF_OSbldg | PGE | Htl | New | CZ13 | 1.91 | 0.000237 | 0 | 1.94 | 0.000301 | -0.00841 | 1.91 | 0.000237 | 0 | 1.94 | 0.000301 | -0.00841 |  | LF | Bldg | 1910 | 0.237 | 1910 | 0.237 | 1.02 | 1.27 | -0.0044031 | 1910 | 0.237 | 1910 | 0.237 | 1.02 | 1.27 | -0.0044
LFBldgPGEHtlNewCZ16 | Com-Iltg-dWatt-LF_OSbldg | PGE | Htl | New | CZ16 | 1.91 | 0.000237 | 0 | 1.68 | 0.000291 | -0.0154 | 1.91 | 0.000237 | 0 | 1.68 | 0.000291 | -0.0154 |  | LF | Bldg | 1910 | 0.237 | 1910 | 0.237 | 0.88 | 1.23 | -0.0080628 | 1910 | 0.237 | 1910 | 0.237 | 0.88 | 1.23 | -0.00806
LFBldgPGEHtlNewIOU | Com-Iltg-dWatt-LF_OSbldg | PGE | Htl | New | IOU | 1.91 | 0.000237 | 0 | 1.8505 | 0.00029772 | -0.0096192 | 1.91 | 0.000237 | 0 | 1.8505 | 0.00029772 | -0.0096192 |  | LF | Bldg | 1910 | 0.237 | 1910 | 0.237 | 0.969 | 1.26 | -0.0050362 | 1910 | 0.237 | 1910 | 0.237 | 0.969 | 1.26 | -0.00504
LFBldgPGEMBTExCZ01 | Com-Iltg-dWatt-LF_OSbldg | PGE | MBT | Ex | CZ01 | 3.5244 | 0.00085014 | 0 | 3.8039 | 0.0010187 | -0.0044029 | 3.42 | 0.000834 | 0 | 3.6995 | 0.000995 | -0.0042795 |  | LF | Bldg | 3520 | 0.85 | 3420 | 0.834 | 1.08 | 1.19 | -0.0012513 | 3520 | 0.85 | 3420 | 0.834 | 1.08 | 1.19 | -0.00125
LFBldgPGEMBTExCZ02 | Com-Iltg-dWatt-LF_OSbldg | PGE | MBT | Ex | CZ02 | 3.5256 | 0.00085031 | 0 | 3.9152 | 0.0010094 | -0.0022072 | 3.42 | 0.000834 | 0 | 3.8096 | 0.000995 | -0.0021496 |  | LF | Bldg | 3530 | 0.85 | 3420 | 0.834 | 1.11 | 1.19 | -0.00062854 | 3530 | 0.85 | 3420 | 0.834 | 1.11 | 1.19 | -0.000629
LFBldgPGEMBTExCZ03 | Com-Iltg-dWatt-LF_OSbldg | PGE | MBT | Ex | CZ03 | 3.5266 | 0.00085047 | 0 | 3.9462 | 0.0010095 | -0.0019281 | 3.42 | 0.000834 | 0 | 3.8397 | 0.000995 | -0.0018797 |  | LF | Bldg | 3530 | 0.85 | 3420 | 0.834 | 1.12 | 1.19 | -0.00054962 | 3530 | 0.85 | 3420 | 0.834 | 1.12 | 1.19 | -0.00055
LFBldgPGEMBTExCZ04 | Com-Iltg-dWatt-LF_OSbldg | PGE | MBT | Ex | CZ04 | 3.5251 | 0.00085025 | 0 | 3.9443 | 0.0010291 | -0.0014878 | 3.42 | 0.000834 | 0 | 3.8296 | 0.00101 | -0.00144 |  | LF | Bldg | 3530 | 0.85 | 3420 | 0.834 | 1.12 | 1.21 | -0.00042105 | 3530 | 0.85 | 3420 | 0.834 | 1.12 | 1.21 | -0.000421
LFBldgPGEMBTExCZ05 | Com-Iltg-dWatt-LF_OSbldg | PGE | MBT | Ex | CZ05 | 3.5251 | 0.00085025 | 0 | 3.9147 | 0.0010189 | -0.0014578 | 3.42 | 0.000834 | 0 | 3.8096 | 0.000995 | -0.0014196 |  | LF | Bldg | 3530 | 0.85 | 3420 | 0.834 | 1.11 | 1.19 | -0.00041508 | 3530 | 0.85 | 3420 | 0.834 | 1.11 | 1.19 | -0.000415
LFBldgPGEMBTExCZ11 | Com-Iltg-dWatt-LF_OSbldg | PGE | MBT | Ex | CZ11 | 3.5228 | 0.00084989 | 0 | 3.9321 | 0.0010287 | -0.0023154 | 3.42 | 0.000834 | 0 | 3.8293 | 0.00101 | -0.0022593 |  | LF | Bldg | 3520 | 0.85 | 3420 | 0.834 | 1.12 | 1.21 | -0.00066063 | 3520 | 0.85 | 3420 | 0.834 | 1.12 | 1.21 | -0.000661
LFBldgPGEMBTExCZ12 | Com-Iltg-dWatt-LF_OSbldg | PGE | MBT | Ex | CZ12 | 3.524 | 0.00085008 | 0 | 3.9229 | 0.0010088 | -0.0023162 | 3.42 | 0.000834 | 0 | 3.8095 | 0.000988 | -0.0022595 |  | LF | Bldg | 3520 | 0.85 | 3420 | 0.834 | 1.11 | 1.18 | -0.00066066 | 3520 | 0.85 | 3420 | 0.834 | 1.11 | 1.18 | -0.000661
LFBldgPGEMBTExCZ13 | Com-Iltg-dWatt-LF_OSbldg | PGE | MBT | Ex | CZ13 | 3.5231 | 0.00084993 | 0 | 3.9425 | 0.0010087 | -0.0020756 | 3.42 | 0.000834 | 0 | 3.8394 | 0.000989 | -0.0020194 |  | LF | Bldg | 3520 | 0.85 | 3420 | 0.834 | 1.12 | 1.19 | -0.00059046 | 3520 | 0.85 | 3420 | 0.834 | 1.12 | 1.19 | -0.00059
LFBldgPGEMBTExCZ16 | Com-Iltg-dWatt-LF_OSbldg | PGE | MBT | Ex | CZ16 | 3.5237 | 0.00085003 | 0 | 3.7637 | 0.00098791 | -0.0098623 | 3.42 | 0.000834 | 0 | 3.66 | 0.00097 | -0.0095889 |  | LF | Bldg | 3520 | 0.85 | 3420 | 0.834 | 1.07 | 1.16 | -0.0028038 | 3520 | 0.85 | 3420 | 0.834 | 1.07 | 1.16 | -0.0028
LFBldgPGEMBTExIOU | Com-Iltg-dWatt-LF_OSbldg | PGE | MBT | Ex | IOU | 3.5251 | 0.00085024 | 0 | 3.9344 | 0.0010138 | -0.0020714 | 3.42 | 0.000834 | 0 | 3.8258 | 0.00099614 | -0.0020168 |  | LF | Bldg | 3530 | 0.85 | 3420 | 0.834 | 1.12 | 1.19 | -0.0005897 | 3530 | 0.85 | 3420 | 0.834 | 1.12 | 1.19 | -0.00059
LFBldgPGEMBTNewCZ01 | Com-Iltg-dWatt-LF_OSbldg | PGE | MBT | New | CZ01 | 3.42 | 0.000834 | 0 | 3.51 | 0.000957 | -0.00369 | 3.42 | 0.000834 | 0 | 3.51 | 0.000957 | -0.00369 |  | LF | Bldg | 3420 | 0.834 | 3420 | 0.834 | 1.03 | 1.15 | -0.0010789 | 3420 | 0.834 | 3420 | 0.834 | 1.03 | 1.15 | -0.00108
LFBldgPGEMBTNewCZ02 | Com-Iltg-dWatt-LF_OSbldg | PGE | MBT | New | CZ02 | 3.42 | 0.000834 | 0 | 3.65 | 0.00103 | -0.00186 | 3.42 | 0.000834 | 0 | 3.65 | 0.00103 | -0.00186 |  | LF | Bldg | 3420 | 0.834 | 3420 | 0.834 | 1.07 | 1.24 | -0.00054386 | 3420 | 0.834 | 3420 | 0.834 | 1.07 | 1.24 | -0.000544
LFBldgPGEMBTNewCZ03 | Com-Iltg-dWatt-LF_OSbldg | PGE | MBT | New | CZ03 | 3.42 | 0.000834 | 0 | 3.63 | 0.001 | -0.00173 | 3.42 | 0.000834 | 0 | 3.63 | 0.001 | -0.00173 |  | LF | Bldg | 3420 | 0.834 | 3420 | 0.834 | 1.06 | 1.2 | -0.00050585 | 3420 | 0.834 | 3420 | 0.834 | 1.06 | 1.2 | -0.000506
LFBldgPGEMBTNewCZ04 | Com-Iltg-dWatt-LF_OSbldg | PGE | MBT | New | CZ04 | 3.42 | 0.000834 | 0 | 3.69 | 0.00102 | -0.00139 | 3.42 | 0.000834 | 0 | 3.69 | 0.00102 | -0.00139 |  | LF | Bldg | 3420 | 0.834 | 3420 | 0.834 | 1.08 | 1.22 | -0.00040643 | 3420 | 0.834 | 3420 | 0.834 | 1.08 | 1.22 | -0.000406
LFBldgPGEMBTNewCZ05 | Com-Iltg-dWatt-LF_OSbldg | PGE | MBT | New | CZ05 | 3.42 | 0.000834 | 0 | 3.64 | 0.000994 | -0.000885 | 3.42 | 0.000834 | 0 | 3.64 | 0.000994 | -0.000885 |  | LF | Bldg | 3420 | 0.834 | 3420 | 0.834 | 1.06 | 1.19 | -0.00025877 | 3420 | 0.834 | 3420 | 0.834 | 1.06 | 1.19 | -0.000259
LFBldgPGEMBTNewCZ11 | Com-Iltg-dWatt-LF_OSbldg | PGE | MBT | New | CZ11 | 3.42 | 0.000834 | 0 | 3.73 | 0.00104 | -0.00161 | 3.42 | 0.000834 | 0 | 3.73 | 0.00104 | -0.00161 |  | LF | Bldg | 3420 | 0.834 | 3420 | 0.834 | 1.09 | 1.25 | -0.00047076 | 3420 | 0.834 | 3420 | 0.834 | 1.09 | 1.25 | -0.000471
LFBldgPGEMBTNewCZ12 | Com-Iltg-dWatt-LF_OSbldg | PGE | MBT | New | CZ12 | 3.42 | 0.000834 | 0 | 3.7 | 0.00103 | -0.00167 | 3.42 | 0.000834 | 0 | 3.7 | 0.00103 | -0.00167 |  | LF | Bldg | 3420 | 0.834 | 3420 | 0.834 | 1.08 | 1.24 | -0.0004883 | 3420 | 0.834 | 3420 | 0.834 | 1.08 | 1.24 | -0.000488
LFBldgPGEMBTNewCZ13 | Com-Iltg-dWatt-LF_OSbldg | PGE | MBT | New | CZ13 | 3.42 | 0.000834 | 0 | 3.74 | 0.00103 | -0.00154 | 3.42 | 0.000834 | 0 | 3.74 | 0.00103 | -0.00154 |  | LF | Bldg | 3420 | 0.834 | 3420 | 0.834 | 1.09 | 1.24 | -0.00045029 | 3420 | 0.834 | 3420 | 0.834 | 1.09 | 1.24 | -0.00045
LFBldgPGEMBTNewCZ16 | Com-Iltg-dWatt-LF_OSbldg | PGE | MBT | New | CZ16 | 3.42 | 0.000834 | 0 | 3.58 | 0.000997 | -0.00653 | 3.42 | 0.000834 | 0 | 3.58 | 0.000997 | -0.00653 |  | LF | Bldg | 3420 | 0.834 | 3420 | 0.834 | 1.05 | 1.2 | -0.0019094 | 3420 | 0.834 | 3420 | 0.834 | 1.05 | 1.2 | -0.00191
LFBldgPGEMBTNewIOU | Com-Iltg-dWatt-LF_OSbldg | PGE | MBT | New | IOU | 3.42 | 0.000834 | 0 | 3.6833 | 0.0010201 | -0.0016854 | 3.42 | 0.000834 | 0 | 3.6833 | 0.0010201 | -0.0016854 |  | LF | Bldg | 3420 | 0.834 | 3420 | 0.834 | 1.08 | 1.22 | -0.00049281 | 3420 | 0.834 | 3420 | 0.834 | 1.08 | 1.22 | -0.000493
LFBldgPGEMLIExCZ01 | Com-Iltg-dWatt-LF_OSbldg | PGE | MLI | Ex | CZ01 | 3.2195 | 0.0009239 | 0 | 3.11 | 0.00107 | -0.0389 | 3.21 | 0.000922 | 0 | 3.11 | 0.00107 | -0.0389 |  | LF | Bldg | 3220 | 0.924 | 3210 | 0.922 | 0.969 | 1.16 | -0.012118 | 3220 | 0.924 | 3210 | 0.922 | 0.969 | 1.16 | -0.0121
LFBldgPGEMLIExCZ02 | Com-Iltg-dWatt-LF_OSbldg | PGE | MLI | Ex | CZ02 | 3.2196 | 0.00092392 | 0 | 3.34 | 0.00108 | -0.0199 | 3.21 | 0.000922 | 0 | 3.34 | 0.00108 | -0.0199 |  | LF | Bldg | 3220 | 0.924 | 3210 | 0.922 | 1.04 | 1.17 | -0.0061994 | 3220 | 0.924 | 3210 | 0.922 | 1.04 | 1.17 | -0.0062
LFBldgPGEMLIExCZ03 | Com-Iltg-dWatt-LF_OSbldg | PGE | MLI | Ex | CZ03 | 3.2197 | 0.00092394 | 0 | 3.33 | 0.00108 | -0.018697 | 3.21 | 0.000922 | 0 | 3.33 | 0.00108 | -0.0186 |  | LF | Bldg | 3220 | 0.924 | 3210 | 0.922 | 1.04 | 1.17 | -0.0057944 | 3220 | 0.924 | 3210 | 0.922 | 1.04 | 1.17 | -0.00579
LFBldgPGEMLIExCZ04 | Com-Iltg-dWatt-LF_OSbldg | PGE | MLI | Ex | CZ04 | 3.2196 | 0.00092391 | 0 | 3.37 | 0.0010796 | -0.0151 | 3.21 | 0.000922 | 0 | 3.37 | 0.00107 | -0.0151 |  | LF | Bldg | 3220 | 0.924 | 3210 | 0.922 | 1.05 | 1.16 | -0.004704 | 3220 | 0.924 | 3210 | 0.922 | 1.05 | 1.16 | -0.0047
LFBldgPGEMLIExCZ05 | Com-Iltg-dWatt-LF_OSbldg | PGE | MLI | Ex | CZ05 | 3.2196 | 0.00092391 | 0 | 3.32 | 0.0010796 | -0.0173 | 3.21 | 0.000922 | 0 | 3.32 | 0.0010796 | -0.0173 |  | LF | Bldg | 3220 | 0.924 | 3210 | 0.922 | 1.03 | 1.17 | -0.0053894 | 3220 | 0.924 | 3210 | 0.922 | 1.03 | 1.17 | -0.00539
LFBldgPGEMLIExCZ11 | Com-Iltg-dWatt-LF_OSbldg | PGE | MLI | Ex | CZ11 | 3.2193 | 0.00092387 | 0 | 3.3593 | 0.00108 | -0.0199 | 3.21 | 0.000922 | 0 | 3.35 | 0.00108 | -0.0199 |  | LF | Bldg | 3220 | 0.924 | 3210 | 0.922 | 1.04 | 1.17 | -0.0061994 | 3220 | 0.924 | 3210 | 0.922 | 1.04 | 1.17 | -0.0062
LFBldgPGEMLIExCZ12 | Com-Iltg-dWatt-LF_OSbldg | PGE | MLI | Ex | CZ12 | 3.2195 | 0.00092389 | 0 | 3.35 | 0.0010895 | -0.0196 | 3.21 | 0.000922 | 0 | 3.35 | 0.00108 | -0.0196 |  | LF | Bldg | 3220 | 0.924 | 3210 | 0.922 | 1.04 | 1.17 | -0.0061059 | 3220 | 0.924 | 3210 | 0.922 | 1.04 | 1.17 | -0.00611
LFBldgPGEMLIExCZ13 | Com-Iltg-dWatt-LF_OSbldg | PGE | MLI | Ex | CZ13 | 3.2194 | 0.00092387 | 0 | 3.39 | 0.00107 | -0.0175 | 3.21 | 0.000922 | 0 | 3.39 | 0.00107 | -0.0175 |  | LF | Bldg | 3220 | 0.924 | 3210 | 0.922 | 1.06 | 1.16 | -0.0054517 | 3220 | 0.924 | 3210 | 0.922 | 1.06 | 1.16 | -0.00545
LFBldgPGEMLIExCZ16 | Com-Iltg-dWatt-LF_OSbldg | PGE | MLI | Ex | CZ16 | 3.2194 | 0.00092389 | 0 | 3.16 | 0.00106 | -0.039594 | 3.21 | 0.000922 | 0 | 3.16 | 0.00106 | -0.0395 |  | LF | Bldg | 3220 | 0.924 | 3210 | 0.922 | 0.984 | 1.15 | -0.012305 | 3220 | 0.924 | 3210 | 0.922 | 0.984 | 1.15 | -0.0123
LFBldgPGEMLIExIOU | Com-Iltg-dWatt-LF_OSbldg | PGE | MLI | Ex | IOU | 3.2195 | 0.00092391 | 0 | 3.347 | 0.0010802 | -0.018545 | 3.21 | 0.000922 | 0 | 3.3466 | 0.0010766 | -0.01851 |  | LF | Bldg | 3220 | 0.924 | 3210 | 0.922 | 1.04 | 1.17 | -0.0057664 | 3220 | 0.924 | 3210 | 0.922 | 1.04 | 1.17 | -0.00577
LFBldgPGEMLINewCZ01 | Com-Iltg-dWatt-LF_OSbldg | PGE | MLI | New | CZ01 | 3.21 | 0.000922 | 0 | 3.07 | 0.000996 | -0.0424 | 3.21 | 0.000922 | 0 | 3.07 | 0.000996 | -0.0424 |  | LF | Bldg | 3210 | 0.922 | 3210 | 0.922 | 0.956 | 1.08 | -0.013209 | 3210 | 0.922 | 3210 | 0.922 | 0.956 | 1.08 | -0.0132
LFBldgPGEMLINewCZ02 | Com-Iltg-dWatt-LF_OSbldg | PGE | MLI | New | CZ02 | 3.21 | 0.000922 | 0 | 3.3 | 0.00111 | -0.0231 | 3.21 | 0.000922 | 0 | 3.3 | 0.00111 | -0.0231 |  | LF | Bldg | 3210 | 0.922 | 3210 | 0.922 | 1.03 | 1.2 | -0.0071963 | 3210 | 0.922 | 3210 | 0.922 | 1.03 | 1.2 | -0.0072
LFBldgPGEMLINewCZ03 | Com-Iltg-dWatt-LF_OSbldg | PGE | MLI | New | CZ03 | 3.21 | 0.000922 | 0 | 3.22 | 0.00107 | -0.0215 | 3.21 | 0.000922 | 0 | 3.22 | 0.00107 | -0.0215 |  | LF | Bldg | 3210 | 0.922 | 3210 | 0.922 | 1 | 1.16 | -0.0066978 | 3210 | 0.922 | 3210 | 0.922 | 1 | 1.16 | -0.0067
LFBldgPGEMLINewCZ04 | Com-Iltg-dWatt-LF_OSbldg | PGE | MLI | New | CZ04 | 3.21 | 0.000922 | 0 | 3.33 | 0.00109 | -0.0176 | 3.21 | 0.000922 | 0 | 3.33 | 0.00109 | -0.0176 |  | LF | Bldg | 3210 | 0.922 | 3210 | 0.922 | 1.04 | 1.18 | -0.0054829 | 3210 | 0.922 | 3210 | 0.922 | 1.04 | 1.18 | -0.00548
LFBldgPGEMLINewCZ05 | Com-Iltg-dWatt-LF_OSbldg | PGE | MLI | New | CZ05 | 3.21 | 0.000922 | 0 | 3.21 | 0.00106 | -0.0211 | 3.21 | 0.000922 | 0 | 3.21 | 0.00106 | -0.0211 |  | LF | Bldg | 3210 | 0.922 | 3210 | 0.922 | 1 | 1.15 | -0.0065732 | 3210 | 0.922 | 3210 | 0.922 | 1 | 1.15 | -0.00657
LFBldgPGEMLINewCZ11 | Com-Iltg-dWatt-LF_OSbldg | PGE | MLI | New | CZ11 | 3.21 | 0.000922 | 0 | 3.42 | 0.00114 | -0.0191 | 3.21 | 0.000922 | 0 | 3.42 | 0.00114 | -0.0191 |  | LF | Bldg | 3210 | 0.922 | 3210 | 0.922 | 1.07 | 1.24 | -0.0059502 | 3210 | 0.922 | 3210 | 0.922 | 1.07 | 1.24 | -0.00595
LFBldgPGEMLINewCZ12 | Com-Iltg-dWatt-LF_OSbldg | PGE | MLI | New | CZ12 | 3.21 | 0.000922 | 0 | 3.38 | 0.00113 | -0.0216 | 3.21 | 0.000922 | 0 | 3.38 | 0.00113 | -0.0216 |  | LF | Bldg | 3210 | 0.922 | 3210 | 0.922 | 1.05 | 1.23 | -0.006729 | 3210 | 0.922 | 3210 | 0.922 | 1.05 | 1.23 | -0.00673
LFBldgPGEMLINewCZ13 | Com-Iltg-dWatt-LF_OSbldg | PGE | MLI | New | CZ13 | 3.21 | 0.000922 | 0 | 3.44 | 0.00114 | -0.0178 | 3.21 | 0.000922 | 0 | 3.44 | 0.00114 | -0.0178 |  | LF | Bldg | 3210 | 0.922 | 3210 | 0.922 | 1.07 | 1.24 | -0.0055452 | 3210 | 0.922 | 3210 | 0.922 | 1.07 | 1.24 | -0.00555
LFBldgPGEMLINewCZ16 | Com-Iltg-dWatt-LF_OSbldg | PGE | MLI | New | CZ16 | 3.21 | 0.000922 | 0 | 3.19 | 0.00107 | -0.0389 | 3.21 | 0.000922 | 0 | 3.19 | 0.00107 | -0.0389 |  | LF | Bldg | 3210 | 0.922 | 3210 | 0.922 | 0.994 | 1.16 | -0.012118 | 3210 | 0.922 | 3210 | 0.922 | 0.994 | 1.16 | -0.0121
LFBldgPGEMLINewIOU | Com-Iltg-dWatt-LF_OSbldg | PGE | MLI | New | IOU | 3.21 | 0.000922 | 0 | 3.333 | 0.0011065 | -0.020505 | 3.21 | 0.000922 | 0 | 3.333 | 0.0011065 | -0.020505 |  | LF | Bldg | 3210 | 0.922 | 3210 | 0.922 | 1.04 | 1.2 | -0.0063878 | 3210 | 0.922 | 3210 | 0.922 | 1.04 | 1.2 | -0.00639
LFBldgPGEMtlExCZ01 | Com-Iltg-dWatt-LF_OSbldg | PGE | Mtl | Ex | CZ01 | 1.5469 | 0.00017163 | 0 | 1.4769 | 0.00020456 | -0.015369 | 1.5 | 0.000166 | 0 | 1.43 | 0.000198 | -0.0149 |  | LF | Bldg | 1550 | 0.172 | 1500 | 0.166 | 0.953 | 1.19 | -0.0099333 | 1550 | 0.172 | 1500 | 0.166 | 0.953 | 1.19 | -0.00993
LFBldgPGEMtlExCZ02 | Com-Iltg-dWatt-LF_OSbldg | PGE | Mtl | Ex | CZ02 | 1.5471 | 0.00017165 | 0 | 1.5771 | 0.00021259 | -0.010179 | 1.5 | 0.000166 | 0 | 1.53 | 0.000206 | -0.00985 |  | LF | Bldg | 1550 | 0.172 | 1500 | 0.166 | 1.02 | 1.24 | -0.0065667 | 1550 | 0.172 | 1500 | 0.166 | 1.02 | 1.24 | -0.00657
LFBldgPGEMtlExCZ03 | Com-Iltg-dWatt-LF_OSbldg | PGE | Mtl | Ex | CZ03 | 1.5486 | 0.00017183 | 0 | 1.5986 | 0.0002078 | -0.0099209 | 1.5 | 0.000166 | 0 | 1.55 | 0.000201 | -0.00961 |  | LF | Bldg | 1550 | 0.172 | 1500 | 0.166 | 1.03 | 1.21 | -0.0064067 | 1550 | 0.172 | 1500 | 0.166 | 1.03 | 1.21 | -0.00641
LFBldgPGEMtlExCZ04 | Com-Iltg-dWatt-LF_OSbldg | PGE | Mtl | Ex | CZ04 | 1.5469 | 0.00017163 | 0 | 1.6263 | 0.00021057 | -0.0082732 | 1.5 | 0.000166 | 0 | 1.57 | 0.000204 | -0.00802 |  | LF | Bldg | 1550 | 0.172 | 1500 | 0.166 | 1.05 | 1.23 | -0.0053467 | 1550 | 0.172 | 1500 | 0.166 | 1.05 | 1.23 | -0.00535
LFBldgPGEMtlExCZ05 | Com-Iltg-dWatt-LF_OSbldg | PGE | Mtl | Ex | CZ05 | 1.5469 | 0.00017163 | 0 | 1.5763 | 0.00020656 | -0.010581 | 1.5 | 0.000166 | 0 | 1.52 | 0.0002 | -0.0103 |  | LF | Bldg | 1550 | 0.172 | 1500 | 0.166 | 1.01 | 1.2 | -0.0068667 | 1550 | 0.172 | 1500 | 0.166 | 1.01 | 1.2 | -0.00687
LFBldgPGEMtlExCZ11 | Com-Iltg-dWatt-LF_OSbldg | PGE | Mtl | Ex | CZ11 | 1.5466 | 0.00017159 | 0 | 1.6359 | 0.00021445 | -0.0085615 | 1.5 | 0.000166 | 0 | 1.58 | 0.000207 | -0.0083007 |  | LF | Bldg | 1550 | 0.172 | 1500 | 0.166 | 1.05 | 1.25 | -0.0055338 | 1550 | 0.172 | 1500 | 0.166 | 1.05 | 1.25 | -0.00553
LFBldgPGEMtlExCZ12 | Com-Iltg-dWatt-LF_OSbldg | PGE | Mtl | Ex | CZ12 | 1.5462 | 0.00017154 | 0 | 1.6162 | 0.00021339 | -0.0090078 | 1.5 | 0.000166 | 0 | 1.57 | 0.000206 | -0.00874 |  | LF | Bldg | 1550 | 0.172 | 1500 | 0.166 | 1.05 | 1.24 | -0.0058267 | 1550 | 0.172 | 1500 | 0.166 | 1.05 | 1.24 | -0.00583
LFBldgPGEMtlExCZ13 | Com-Iltg-dWatt-LF_OSbldg | PGE | Mtl | Ex | CZ13 | 1.5467 | 0.0001716 | 0 | 1.656 | 0.00021354 | -0.0079928 | 1.5 | 0.000166 | 0 | 1.6 | 0.000207 | -0.00775 |  | LF | Bldg | 1550 | 0.172 | 1500 | 0.166 | 1.07 | 1.25 | -0.0051667 | 1550 | 0.172 | 1500 | 0.166 | 1.07 | 1.25 | -0.00517
LFBldgPGEMtlExCZ16 | Com-Iltg-dWatt-LF_OSbldg | PGE | Mtl | Ex | CZ16 | 1.5468 | 0.00017161 | 0 | 1.4768 | 0.00020655 | -0.013374 | 1.5 | 0.000166 | 0 | 1.43 | 0.0002 | -0.013 |  | LF | Bldg | 1550 | 0.172 | 1500 | 0.166 | 0.953 | 1.2 | -0.0086667 | 1550 | 0.172 | 1500 | 0.166 | 0.953 | 1.2 | -0.00867
LFBldgPGEMtlExIOU | Com-Iltg-dWatt-LF_OSbldg | PGE | Mtl | Ex | IOU | 1.5475 | 0.0001717 | 0 | 1.6046 | 0.00020986 | -0.0095417 | 1.5 | 0.000166 | 0 | 1.554 | 0.00020305 | -0.0092497 |  | LF | Bldg | 1550 | 0.172 | 1500 | 0.166 | 1.04 | 1.22 | -0.0061665 | 1550 | 0.172 | 1500 | 0.166 | 1.04 | 1.22 | -0.00617
LFBldgPGEMtlNewCZ01 | Com-Iltg-dWatt-LF_OSbldg | PGE | Mtl | New | CZ01 | 1.5 | 0.000166 | 0 | 1.35 | 0.000197 | -0.0194 | 1.5 | 0.000166 | 0 | 1.35 | 0.000197 | -0.0194 |  | LF | Bldg | 1500 | 0.166 | 1500 | 0.166 | 0.9 | 1.19 | -0.012933 | 1500 | 0.166 | 1500 | 0.166 | 0.9 | 1.19 | -0.0129
LFBldgPGEMtlNewCZ02 | Com-Iltg-dWatt-LF_OSbldg | PGE | Mtl | New | CZ02 | 1.5 | 0.000166 | 0 | 1.49 | 0.00021 | -0.0131 | 1.5 | 0.000166 | 0 | 1.49 | 0.00021 | -0.0131 |  | LF | Bldg | 1500 | 0.166 | 1500 | 0.166 | 0.993 | 1.27 | -0.0087333 | 1500 | 0.166 | 1500 | 0.166 | 0.993 | 1.27 | -0.00873
LFBldgPGEMtlNewCZ03 | Com-Iltg-dWatt-LF_OSbldg | PGE | Mtl | New | CZ03 | 1.5 | 0.000166 | 0 | 1.51 | 0.000204 | -0.0125 | 1.5 | 0.000166 | 0 | 1.51 | 0.000204 | -0.0125 |  | LF | Bldg | 1500 | 0.166 | 1500 | 0.166 | 1.01 | 1.23 | -0.0083333 | 1500 | 0.166 | 1500 | 0.166 | 1.01 | 1.23 | -0.00833
LFBldgPGEMtlNewCZ04 | Com-Iltg-dWatt-LF_OSbldg | PGE | Mtl | New | CZ04 | 1.5 | 0.000166 | 0 | 1.55 | 0.000208 | -0.0105 | 1.5 | 0.000166 | 0 | 1.55 | 0.000208 | -0.0105 |  | LF | Bldg | 1500 | 0.166 | 1500 | 0.166 | 1.03 | 1.25 | -0.007 | 1500 | 0.166 | 1500 | 0.166 | 1.03 | 1.25 | -0.007
LFBldgPGEMtlNewCZ05 | Com-Iltg-dWatt-LF_OSbldg | PGE | Mtl | New | CZ05 | 1.5 | 0.000166 | 0 | 1.47 | 0.000202 | -0.0141 | 1.5 | 0.000166 | 0 | 1.47 | 0.000202 | -0.0141 |  | LF | Bldg | 1500 | 0.166 | 1500 | 0.166 | 0.98 | 1.22 | -0.0094 | 1500 | 0.166 | 1500 | 0.166 | 0.98 | 1.22 | -0.0094
LFBldgPGEMtlNewCZ11 | Com-Iltg-dWatt-LF_OSbldg | PGE | Mtl | New | CZ11 | 1.5 | 0.000166 | 0 | 1.56 | 0.00021 | -0.0104 | 1.5 | 0.000166 | 0 | 1.56 | 0.00021 | -0.0104 |  | LF | Bldg | 1500 | 0.166 | 1500 | 0.166 | 1.04 | 1.27 | -0.0069333 | 1500 | 0.166 | 1500 | 0.166 | 1.04 | 1.27 | -0.00693
LFBldgPGEMtlNewCZ12 | Com-Iltg-dWatt-LF_OSbldg | PGE | Mtl | New | CZ12 | 1.5 | 0.000166 | 0 | 1.54 | 0.000209 | -0.0109 | 1.5 | 0.000166 | 0 | 1.54 | 0.000209 | -0.0109 |  | LF | Bldg | 1500 | 0.166 | 1500 | 0.166 | 1.03 | 1.26 | -0.0072667 | 1500 | 0.166 | 1500 | 0.166 | 1.03 | 1.26 | -0.00727
LFBldgPGEMtlNewCZ13 | Com-Iltg-dWatt-LF_OSbldg | PGE | Mtl | New | CZ13 | 1.5 | 0.000166 | 0 | 1.57 | 0.000209 | -0.00982 | 1.5 | 0.000166 | 0 | 1.57 | 0.000209 | -0.00982 |  | LF | Bldg | 1500 | 0.166 | 1500 | 0.166 | 1.05 | 1.26 | -0.0065467 | 1500 | 0.166 | 1500 | 0.166 | 1.05 | 1.26 | -0.00655
LFBldgPGEMtlNewCZ16 | Com-Iltg-dWatt-LF_OSbldg | PGE | Mtl | New | CZ16 | 1.5 | 0.000166 | 0 | 1.39 | 0.000202 | -0.0153 | 1.5 | 0.000166 | 0 | 1.39 | 0.000202 | -0.0153 |  | LF | Bldg | 1500 | 0.166 | 1500 | 0.166 | 0.927 | 1.22 | -0.0102 | 1500 | 0.166 | 1500 | 0.166 | 0.927 | 1.22 | -0.0102
LFBldgPGEMtlNewIOU | Com-Iltg-dWatt-LF_OSbldg | PGE | Mtl | New | IOU | 1.5 | 0.000166 | 0 | 1.5227 | 0.00020682 | -0.011749 | 1.5 | 0.000166 | 0 | 1.5227 | 0.00020682 | -0.011749 |  | LF | Bldg | 1500 | 0.166 | 1500 | 0.166 | 1.02 | 1.25 | -0.0078325 | 1500 | 0.166 | 1500 | 0.166 | 1.02 | 1.25 | -0.00783
LFBldgPGENrsExCZ01 | Com-Iltg-dWatt-LF_OSbldg | PGE | Nrs | Ex | CZ01 | 4.1569 | 0.00067551 | 0 | 4.0374 | 0.00077043 | -0.090938 | 4.0804 | 0.00066404 | 0 | 3.9704 | 0.00075704 | -0.089504 |  | LF | Bldg | 4160 | 0.676 | 4080 | 0.664 | 0.973 | 1.14 | -0.021935 | 4160 | 0.676 | 4080 | 0.664 | 0.973 | 1.14 | -0.0219
LFBldgPGENrsExCZ02 | Com-Iltg-dWatt-LF_OSbldg | PGE | Nrs | Ex | CZ02 | 4.1564 | 0.00067544 | 0 | 4.2764 | 0.00085428 | -0.065644 | 4.0805 | 0.00066405 | 0 | 4.21 | 0.00084005 | -0.064505 |  | LF | Bldg | 4160 | 0.675 | 4080 | 0.664 | 1.03 | 1.27 | -0.015808 | 4160 | 0.675 | 4080 | 0.664 | 1.03 | 1.27 | -0.0158
LFBldgPGENrsExCZ03 | Com-Iltg-dWatt-LF_OSbldg | PGE | Nrs | Ex | CZ03 | 4.1567 | 0.00067548 | 0 | 4.2272 | 0.00082234 | -0.067253 | 4.0805 | 0.00066405 | 0 | 4.1605 | 0.00080805 | -0.066205 |  | LF | Bldg | 4160 | 0.675 | 4080 | 0.664 | 1.02 | 1.22 | -0.016225 | 4160 | 0.675 | 4080 | 0.664 | 1.02 | 1.22 | -0.0162
LFBldgPGENrsExCZ04 | Com-Iltg-dWatt-LF_OSbldg | PGE | Nrs | Ex | CZ04 | 4.1563 | 0.00067542 | 0 | 4.3463 | 0.00084226 | -0.056453 | 4.0805 | 0.00066405 | 0 | 4.2705 | 0.00082805 | -0.0556 |  | LF | Bldg | 4160 | 0.675 | 4080 | 0.664 | 1.05 | 1.25 | -0.013626 | 4160 | 0.675 | 4080 | 0.664 | 1.05 | 1.25 | -0.0136
LFBldgPGENrsExCZ05 | Com-Iltg-dWatt-LF_OSbldg | PGE | Nrs | Ex | CZ05 | 4.1563 | 0.00067542 | 0 | 4.1963 | 0.00079831 | -0.068142 | 4.0805 | 0.00066405 | 0 | 4.13 | 0.00078505 | -0.067005 |  | LF | Bldg | 4160 | 0.675 | 4080 | 0.664 | 1.01 | 1.18 | -0.016421 | 4160 | 0.675 | 4080 | 0.664 | 1.01 | 1.18 | -0.0164
LFBldgPGENrsExCZ11 | Com-Iltg-dWatt-LF_OSbldg | PGE | Nrs | Ex | CZ11 | 4.1556 | 0.00067531 | 0 | 4.4056 | 0.00086206 | -0.05435 | 4.0806 | 0.00066406 | 0 | 4.3306 | 0.00084706 | -0.053506 |  | LF | Bldg | 4160 | 0.675 | 4080 | 0.664 | 1.06 | 1.28 | -0.013112 | 4160 | 0.675 | 4080 | 0.664 | 1.06 | 1.28 | -0.0131
LFBldgPGENrsExCZ12 | Com-Iltg-dWatt-LF_OSbldg | PGE | Nrs | Ex | CZ12 | 4.1556 | 0.00067531 | 0 | 4.3656 | 0.00086212 | -0.057337 | 4.0806 | 0.00066406 | 0 | 4.2906 | 0.00084806 | -0.0564 |  | LF | Bldg | 4160 | 0.675 | 4080 | 0.664 | 1.05 | 1.28 | -0.013821 | 4160 | 0.675 | 4080 | 0.664 | 1.05 | 1.28 | -0.0138
LFBldgPGENrsExCZ13 | Com-Iltg-dWatt-LF_OSbldg | PGE | Nrs | Ex | CZ13 | 4.1556 | 0.0006753 | 0 | 4.4256 | 0.00086111 | -0.052343 | 4.0806 | 0.00066406 | 0 | 4.3506 | 0.00084613 | -0.0515 |  | LF | Bldg | 4160 | 0.675 | 4080 | 0.664 | 1.07 | 1.27 | -0.012621 | 4160 | 0.675 | 4080 | 0.664 | 1.07 | 1.27 | -0.0126
LFBldgPGENrsExCZ16 | Com-Iltg-dWatt-LF_OSbldg | PGE | Nrs | Ex | CZ16 | 4.1563 | 0.00067542 | 0 | 4.1468 | 0.00081726 | -0.078436 | 4.0805 | 0.00066405 | 0 | 4.0805 | 0.00080305 | -0.077205 |  | LF | Bldg | 4160 | 0.675 | 4080 | 0.664 | 1 | 1.21 | -0.01892 | 4160 | 0.675 | 4080 | 0.664 | 1 | 1.21 | -0.0189
LFBldgPGENrsExIOU | Com-Iltg-dWatt-LF_OSbldg | PGE | Nrs | Ex | IOU | 4.1561 | 0.00067539 | 0 | 4.3194 | 0.00084466 | -0.060523 | 4.0806 | 0.00066405 | 0 | 4.2478 | 0.0008303 | -0.059557 |  | LF | Bldg | 4160 | 0.675 | 4080 | 0.664 | 1.04 | 1.25 | -0.014595 | 4160 | 0.675 | 4080 | 0.664 | 1.04 | 1.25 | -0.0146
LFBldgPGENrsNewCZ01 | Com-Iltg-dWatt-LF_OSbldg | PGE | Nrs | New | CZ01 | 4.09 | 0.000665 | 0 | 3.84 | 0.000723 | -0.1 | 4.09 | 0.000665 | 0 | 3.84 | 0.000723 | -0.1 |  | LF | Bldg | 4090 | 0.665 | 4090 | 0.665 | 0.939 | 1.09 | -0.02445 | 4090 | 0.665 | 4090 | 0.665 | 0.939 | 1.09 | -0.0245
LFBldgPGENrsNewCZ02 | Com-Iltg-dWatt-LF_OSbldg | PGE | Nrs | New | CZ02 | 4.09 | 0.000665 | 0 | 4.09 | 0.000849 | -0.0716 | 4.09 | 0.000665 | 0 | 4.09 | 0.000849 | -0.0716 |  | LF | Bldg | 4090 | 0.665 | 4090 | 0.665 | 1 | 1.28 | -0.017506 | 4090 | 0.665 | 4090 | 0.665 | 1 | 1.28 | -0.0175
LFBldgPGENrsNewCZ03 | Com-Iltg-dWatt-LF_OSbldg | PGE | Nrs | New | CZ03 | 4.09 | 0.000665 | 0 | 3.98 | 0.000822 | -0.0748 | 4.09 | 0.000665 | 0 | 3.98 | 0.000822 | -0.0748 |  | LF | Bldg | 4090 | 0.665 | 4090 | 0.665 | 0.973 | 1.24 | -0.018289 | 4090 | 0.665 | 4090 | 0.665 | 0.973 | 1.24 | -0.0183
LFBldgPGENrsNewCZ04 | Com-Iltg-dWatt-LF_OSbldg | PGE | Nrs | New | CZ04 | 4.09 | 0.000665 | 0 | 4.17 | 0.000838 | -0.0614 | 4.09 | 0.000665 | 0 | 4.17 | 0.000838 | -0.0614 |  | LF | Bldg | 4090 | 0.665 | 4090 | 0.665 | 1.02 | 1.26 | -0.015012 | 4090 | 0.665 | 4090 | 0.665 | 1.02 | 1.26 | -0.015
LFBldgPGENrsNewCZ05 | Com-Iltg-dWatt-LF_OSbldg | PGE | Nrs | New | CZ05 | 4.09 | 0.000665 | 0 | 3.99 | 0.000789 | -0.0753 | 4.09 | 0.000665 | 0 | 3.99 | 0.000789 | -0.0753 |  | LF | Bldg | 4090 | 0.665 | 4090 | 0.665 | 0.976 | 1.19 | -0.018411 | 4090 | 0.665 | 4090 | 0.665 | 0.976 | 1.19 | -0.0184
LFBldgPGENrsNewCZ11 | Com-Iltg-dWatt-LF_OSbldg | PGE | Nrs | New | CZ11 | 4.09 | 0.000665 | 0 | 4.27 | 0.000846 | -0.0569 | 4.09 | 0.000665 | 0 | 4.27 | 0.000846 | -0.0569 |  | LF | Bldg | 4090 | 0.665 | 4090 | 0.665 | 1.04 | 1.27 | -0.013912 | 4090 | 0.665 | 4090 | 0.665 | 1.04 | 1.27 | -0.0139
LFBldgPGENrsNewCZ12 | Com-Iltg-dWatt-LF_OSbldg | PGE | Nrs | New | CZ12 | 4.09 | 0.000665 | 0 | 4.21 | 0.000853 | -0.0601 | 4.09 | 0.000665 | 0 | 4.21 | 0.000853 | -0.0601 |  | LF | Bldg | 4090 | 0.665 | 4090 | 0.665 | 1.03 | 1.28 | -0.014694 | 4090 | 0.665 | 4090 | 0.665 | 1.03 | 1.28 | -0.0147
LFBldgPGENrsNewCZ13 | Com-Iltg-dWatt-LF_OSbldg | PGE | Nrs | New | CZ13 | 4.09 | 0.000665 | 0 | 4.29 | 0.000851 | -0.0544 | 4.09 | 0.000665 | 0 | 4.29 | 0.000851 | -0.0544 |  | LF | Bldg | 4090 | 0.665 | 4090 | 0.665 | 1.05 | 1.28 | -0.013301 | 4090 | 0.665 | 4090 | 0.665 | 1.05 | 1.28 | -0.0133
LFBldgPGENrsNewCZ16 | Com-Iltg-dWatt-LF_OSbldg | PGE | Nrs | New | CZ16 | 4.09 | 0.000665 | 0 | 4.01 | 0.00081 | -0.0818 | 4.09 | 0.000665 | 0 | 4.01 | 0.00081 | -0.0818 |  | LF | Bldg | 4090 | 0.665 | 4090 | 0.665 | 0.98 | 1.22 | -0.02 | 4090 | 0.665 | 4090 | 0.665 | 0.98 | 1.22 | -0.02
LFBldgPGENrsNewIOU | Com-Iltg-dWatt-LF_OSbldg | PGE | Nrs | New | IOU | 4.09 | 0.000665 | 0 | 4.1506 | 0.00083984 | -0.064217 | 4.09 | 0.000665 | 0 | 4.1506 | 0.00083984 | -0.064217 |  | LF | Bldg | 4090 | 0.665 | 4090 | 0.665 | 1.01 | 1.26 | -0.015701 | 4090 | 0.665 | 4090 | 0.665 | 1.01 | 1.26 | -0.0157
LFBldgPGEOfLExCZ01 | Com-Iltg-dWatt-LF_OSbldg | PGE | OfL | Ex | CZ01 | 2.6335 | 0.00070835 | 0 | 2.833 | 0.00087796 | -0.024635 | 2.49 | 0.00067296 | 0 | 2.68 | 0.00083491 | -0.023296 |  | LF | Bldg | 2630 | 0.708 | 2490 | 0.673 | 1.08 | 1.24 | -0.0093557 | 2630 | 0.708 | 2490 | 0.673 | 1.08 | 1.24 | -0.00936
LFBldgPGEOfLExCZ02 | Com-Iltg-dWatt-LF_OSbldg | PGE | OfL | Ex | CZ02 | 2.6318 | 0.00070792 | 0 | 2.9207 | 0.00093327 | -0.018045 | 2.49 | 0.00067294 | 0 | 2.76 | 0.00088789 | -0.0171 |  | LF | Bldg | 2630 | 0.708 | 2490 | 0.673 | 1.11 | 1.32 | -0.0068675 | 2630 | 0.708 | 2490 | 0.673 | 1.11 | 1.32 | -0.00687
LFBldgPGEOfLExCZ03 | Com-Iltg-dWatt-LF_OSbldg | PGE | OfL | Ex | CZ03 | 2.633 | 0.00070822 | 0 | 2.912 | 0.0009047 | -0.016753 | 2.49 | 0.00067295 | 0 | 2.7595 | 0.00085991 | -0.015895 |  | LF | Bldg | 2630 | 0.708 | 2490 | 0.673 | 1.11 | 1.28 | -0.0063837 | 2630 | 0.708 | 2490 | 0.673 | 1.11 | 1.28 | -0.00638
LFBldgPGEOfLExCZ04 | Com-Iltg-dWatt-LF_OSbldg | PGE | OfL | Ex | CZ04 | 2.6307 | 0.00070765 | 0 | 2.9495 | 0.00093091 | -0.015144 | 2.49 | 0.00067294 | 0 | 2.79 | 0.00088494 | -0.0143 |  | LF | Bldg | 2630 | 0.708 | 2490 | 0.673 | 1.12 | 1.32 | -0.005743 | 2630 | 0.708 | 2490 | 0.673 | 1.12 | 1.32 | -0.00574
LFBldgPGEOfLExCZ05 | Com-Iltg-dWatt-LF_OSbldg | PGE | OfL | Ex | CZ05 | 2.6307 | 0.00070765 | 0 | 2.8995 | 0.00088903 | -0.016244 | 2.49 | 0.00067294 | 0 | 2.7494 | 0.00084588 | -0.0154 |  | LF | Bldg | 2630 | 0.708 | 2490 | 0.673 | 1.1 | 1.26 | -0.0061847 | 2630 | 0.708 | 2490 | 0.673 | 1.1 | 1.26 | -0.00618
LFBldgPGEOfLExCZ11 | Com-Iltg-dWatt-LF_OSbldg | PGE | OfL | Ex | CZ11 | 2.6278 | 0.00070691 | 0 | 2.9754 | 0.00093986 | -0.017219 | 2.49 | 0.00067292 | 0 | 2.8192 | 0.00089484 | -0.0163 |  | LF | Bldg | 2630 | 0.707 | 2490 | 0.673 | 1.13 | 1.33 | -0.0065462 | 2630 | 0.707 | 2490 | 0.673 | 1.13 | 1.33 | -0.00655
LFBldgPGEOfLExCZ12 | Com-Iltg-dWatt-LF_OSbldg | PGE | OfL | Ex | CZ12 | 2.6282 | 0.00070701 | 0 | 2.9466 | 0.00092507 | -0.016721 | 2.49 | 0.00067292 | 0 | 2.79 | 0.00088084 | -0.0158 |  | LF | Bldg | 2630 | 0.707 | 2490 | 0.673 | 1.12 | 1.31 | -0.0063454 | 2630 | 0.707 | 2490 | 0.673 | 1.12 | 1.31 | -0.00635
LFBldgPGEOfLExCZ13 | Com-Iltg-dWatt-LF_OSbldg | PGE | OfL | Ex | CZ13 | 2.6282 | 0.00070701 | 0 | 3.0058 | 0.00093907 | -0.015629 | 2.49 | 0.00067292 | 0 | 2.8492 | 0.00089392 | -0.0148 |  | LF | Bldg | 2630 | 0.707 | 2490 | 0.673 | 1.14 | 1.33 | -0.0059438 | 2630 | 0.707 | 2490 | 0.673 | 1.14 | 1.33 | -0.00594
LFBldgPGEOfLExCZ16 | Com-Iltg-dWatt-LF_OSbldg | PGE | OfL | Ex | CZ16 | 2.6311 | 0.00070774 | 0 | 2.7905 | 0.00089614 | -0.029499 | 2.49 | 0.00067294 | 0 | 2.6494 | 0.00085194 | -0.0279 |  | LF | Bldg | 2630 | 0.708 | 2490 | 0.673 | 1.06 | 1.27 | -0.011205 | 2630 | 0.708 | 2490 | 0.673 | 1.06 | 1.27 | -0.0112
LFBldgPGEOfLExIOU | Com-Iltg-dWatt-LF_OSbldg | PGE | OfL | Ex | IOU | 2.6313 | 0.0007078 | 0 | 2.9315 | 0.00091688 | -0.016465 | 2.49 | 0.00067294 | 0 | 2.7763 | 0.0008719 | -0.015594 |  | LF | Bldg | 2630 | 0.708 | 2490 | 0.673 | 1.11 | 1.3 | -0.0062625 | 2630 | 0.708 | 2490 | 0.673 | 1.11 | 1.3 | -0.00626
LFBldgPGEOfLNewCZ01 | Com-Iltg-dWatt-LF_OSbldg | PGE | OfL | New | CZ01 | 2.49 | 0.000672 | 0 | 2.68 | 0.000809 | -0.0115 | 2.49 | 0.000672 | 0 | 2.68 | 0.000809 | -0.0115 |  | LF | Bldg | 2490 | 0.672 | 2490 | 0.672 | 1.08 | 1.2 | -0.0046185 | 2490 | 0.672 | 2490 | 0.672 | 1.08 | 1.2 | -0.00462
LFBldgPGEOfLNewCZ02 | Com-Iltg-dWatt-LF_OSbldg | PGE | OfL | New | CZ02 | 2.49 | 0.000672 | 0 | 2.79 | 0.00084 | -0.00831 | 2.49 | 0.000672 | 0 | 2.79 | 0.00084 | -0.00831 |  | LF | Bldg | 2490 | 0.672 | 2490 | 0.672 | 1.12 | 1.25 | -0.0033373 | 2490 | 0.672 | 2490 | 0.672 | 1.12 | 1.25 | -0.00334
LFBldgPGEOfLNewCZ03 | Com-Iltg-dWatt-LF_OSbldg | PGE | OfL | New | CZ03 | 2.49 | 0.000672 | 0 | 2.77 | 0.000827 | -0.00741 | 2.49 | 0.000672 | 0 | 2.77 | 0.000827 | -0.00741 |  | LF | Bldg | 2490 | 0.672 | 2490 | 0.672 | 1.11 | 1.23 | -0.0029759 | 2490 | 0.672 | 2490 | 0.672 | 1.11 | 1.23 | -0.00298
LFBldgPGEOfLNewCZ04 | Com-Iltg-dWatt-LF_OSbldg | PGE | OfL | New | CZ04 | 2.49 | 0.000672 | 0 | 2.81 | 0.000837 | -0.00689 | 2.49 | 0.000672 | 0 | 2.81 | 0.000837 | -0.00689 |  | LF | Bldg | 2490 | 0.672 | 2490 | 0.672 | 1.13 | 1.25 | -0.0027671 | 2490 | 0.672 | 2490 | 0.672 | 1.13 | 1.25 | -0.00277
LFBldgPGEOfLNewCZ05 | Com-Iltg-dWatt-LF_OSbldg | PGE | OfL | New | CZ05 | 2.49 | 0.000672 | 0 | 2.76 | 0.000817 | -0.00759 | 2.49 | 0.000672 | 0 | 2.76 | 0.000817 | -0.00759 |  | LF | Bldg | 2490 | 0.672 | 2490 | 0.672 | 1.11 | 1.22 | -0.0030482 | 2490 | 0.672 | 2490 | 0.672 | 1.11 | 1.22 | -0.00305
LFBldgPGEOfLNewCZ11 | Com-Iltg-dWatt-LF_OSbldg | PGE | OfL | New | CZ11 | 2.49 | 0.000672 | 0 | 2.83 | 0.000852 | -0.00674 | 2.49 | 0.000672 | 0 | 2.83 | 0.000852 | -0.00674 |  | LF | Bldg | 2490 | 0.672 | 2490 | 0.672 | 1.14 | 1.27 | -0.0027068 | 2490 | 0.672 | 2490 | 0.672 | 1.14 | 1.27 | -0.00271
LFBldgPGEOfLNewCZ12 | Com-Iltg-dWatt-LF_OSbldg | PGE | OfL | New | CZ12 | 2.49 | 0.000672 | 0 | 2.81 | 0.000845 | -0.00791 | 2.49 | 0.000672 | 0 | 2.81 | 0.000845 | -0.00791 |  | LF | Bldg | 2490 | 0.672 | 2490 | 0.672 | 1.13 | 1.26 | -0.0031767 | 2490 | 0.672 | 2490 | 0.672 | 1.13 | 1.26 | -0.00318
LFBldgPGEOfLNewCZ13 | Com-Iltg-dWatt-LF_OSbldg | PGE | OfL | New | CZ13 | 2.49 | 0.000672 | 0 | 2.83 | 0.000845 | -0.00741 | 2.49 | 0.000672 | 0 | 2.83 | 0.000845 | -0.00741 |  | LF | Bldg | 2490 | 0.672 | 2490 | 0.672 | 1.14 | 1.26 | -0.0029759 | 2490 | 0.672 | 2490 | 0.672 | 1.14 | 1.26 | -0.00298
LFBldgPGEOfLNewCZ16 | Com-Iltg-dWatt-LF_OSbldg | PGE | OfL | New | CZ16 | 2.49 | 0.000672 | 0 | 2.69 | 0.000828 | -0.0172 | 2.49 | 0.000672 | 0 | 2.69 | 0.000828 | -0.0172 |  | LF | Bldg | 2490 | 0.672 | 2490 | 0.672 | 1.08 | 1.23 | -0.0069076 | 2490 | 0.672 | 2490 | 0.672 | 1.08 | 1.23 | -0.00691
LFBldgPGEOfLNewIOU | Com-Iltg-dWatt-LF_OSbldg | PGE | OfL | New | IOU | 2.49 | 0.000672 | 0 | 2.794 | 0.00083546 | -0.0074566 | 2.49 | 0.000672 | 0 | 2.794 | 0.00083546 | -0.0074566 |  | LF | Bldg | 2490 | 0.672 | 2490 | 0.672 | 1.12 | 1.24 | -0.0029946 | 2490 | 0.672 | 2490 | 0.672 | 1.12 | 1.24 | -0.00299
LFBldgPGEOfSExCZ01 | Com-Iltg-dWatt-LF_OSbldg | PGE | OfS | Ex | CZ01 | 2.5737 | 0.00068993 | 0 | 2.5937 | 0.00081121 | -0.016595 | 2.25 | 0.00060805 | 0 | 2.2605 | 0.00071505 | -0.0145 |  | LF | Bldg | 2570 | 0.69 | 2250 | 0.608 | 1 | 1.18 | -0.0064444 | 2570 | 0.69 | 2250 | 0.608 | 1 | 1.18 | -0.00644
LFBldgPGEOfSExCZ02 | Com-Iltg-dWatt-LF_OSbldg | PGE | OfS | Ex | CZ02 | 2.5711 | 0.00068928 | 0 | 2.71 | 0.00083728 | -0.010719 | 2.25 | 0.00060806 | 0 | 2.37 | 0.00073906 | -0.0093311 |  | LF | Bldg | 2570 | 0.689 | 2250 | 0.608 | 1.05 | 1.22 | -0.0041472 | 2570 | 0.689 | 2250 | 0.608 | 1.05 | 1.22 | -0.00415
LFBldgPGEOfSExCZ03 | Com-Iltg-dWatt-LF_OSbldg | PGE | OfS | Ex | CZ03 | 2.5708 | 0.0006892 | 0 | 2.7097 | 0.00083418 | -0.0091911 | 2.25 | 0.00060806 | 0 | 2.3606 | 0.00073606 | -0.0080306 |  | LF | Bldg | 2570 | 0.689 | 2250 | 0.608 | 1.05 | 1.21 | -0.0035691 | 2570 | 0.689 | 2250 | 0.608 | 1.05 | 1.21 | -0.00357
LFBldgPGEOfSExCZ04 | Com-Iltg-dWatt-LF_OSbldg | PGE | OfS | Ex | CZ04 | 2.5702 | 0.00068906 | 0 | 2.7585 | 0.00084095 | -0.0073136 | 2.25 | 0.00060806 | 0 | 2.41 | 0.00074206 | -0.0063812 |  | LF | Bldg | 2570 | 0.689 | 2250 | 0.608 | 1.07 | 1.22 | -0.0028361 | 2570 | 0.689 | 2250 | 0.608 | 1.07 | 1.22 | -0.00284
LFBldgPGEOfSExCZ05 | Com-Iltg-dWatt-LF_OSbldg | PGE | OfS | Ex | CZ05 | 2.5702 | 0.00068905 | 0 | 2.719 | 0.00082112 | -0.0074918 | 2.25 | 0.00060806 | 0 | 2.38 | 0.00072506 | -0.0065406 |  | LF | Bldg | 2570 | 0.689 | 2250 | 0.608 | 1.06 | 1.19 | -0.0029069 | 2570 | 0.689 | 2250 | 0.608 | 1.06 | 1.19 | -0.00291
LFBldgPGEOfSExCZ11 | Com-Iltg-dWatt-LF_OSbldg | PGE | OfS | Ex | CZ11 | 2.5707 | 0.00068917 | 0 | 2.759 | 0.00084109 | -0.011314 | 2.25 | 0.00060806 | 0 | 2.41 | 0.00074206 | -0.0098711 |  | LF | Bldg | 2570 | 0.689 | 2250 | 0.608 | 1.07 | 1.22 | -0.0043872 | 2570 | 0.689 | 2250 | 0.608 | 1.07 | 1.22 | -0.00439
LFBldgPGEOfSExCZ12 | Com-Iltg-dWatt-LF_OSbldg | PGE | OfS | Ex | CZ12 | 2.5696 | 0.00068889 | 0 | 2.7383 | 0.0008388 | -0.011011 | 2.25 | 0.00060806 | 0 | 2.3906 | 0.00074012 | -0.0096012 |  | LF | Bldg | 2570 | 0.689 | 2250 | 0.608 | 1.06 | 1.22 | -0.0042672 | 2570 | 0.689 | 2250 | 0.608 | 1.06 | 1.22 | -0.00427
LFBldgPGEOfSExCZ13 | Com-Iltg-dWatt-LF_OSbldg | PGE | OfS | Ex | CZ13 | 2.5703 | 0.00068908 | 0 | 2.7686 | 0.00083203 | -0.010322 | 2.25 | 0.00060806 | 0 | 2.42 | 0.00073406 | -0.0090406 |  | LF | Bldg | 2570 | 0.689 | 2250 | 0.608 | 1.08 | 1.21 | -0.004018 | 2570 | 0.689 | 2250 | 0.608 | 1.08 | 1.21 | -0.00402
LFBldgPGEOfSExCZ16 | Com-Iltg-dWatt-LF_OSbldg | PGE | OfS | Ex | CZ16 | 2.5727 | 0.00068968 | 0 | 2.5627 | 0.00082381 | -0.020658 | 2.25 | 0.00060805 | 0 | 2.24 | 0.00072605 | -0.018 |  | LF | Bldg | 2570 | 0.69 | 2250 | 0.608 | 0.996 | 1.19 | -0.008 | 2570 | 0.69 | 2250 | 0.608 | 0.996 | 1.19 | -0.008
LFBldgPGEOfSExIOU | Com-Iltg-dWatt-LF_OSbldg | PGE | OfS | Ex | IOU | 2.5704 | 0.00068909 | 0 | 2.7374 | 0.00083597 | -0.0098776 | 2.25 | 0.00060806 | 0 | 2.3899 | 0.0007376 | -0.008626 |  | LF | Bldg | 2570 | 0.689 | 2250 | 0.608 | 1.06 | 1.21 | -0.0038338 | 2570 | 0.689 | 2250 | 0.608 | 1.06 | 1.21 | -0.00383
LFBldgPGEOfSNewCZ01 | Com-Iltg-dWatt-LF_OSbldg | PGE | OfS | New | CZ01 | 2.25 | 0.000609 | 0 | 2.23 | 0.000711 | -0.0123 | 2.25 | 0.000609 | 0 | 2.23 | 0.000711 | -0.0123 |  | LF | Bldg | 2250 | 0.609 | 2250 | 0.609 | 0.991 | 1.17 | -0.0054667 | 2250 | 0.609 | 2250 | 0.609 | 0.991 | 1.17 | -0.00547
LFBldgPGEOfSNewCZ02 | Com-Iltg-dWatt-LF_OSbldg | PGE | OfS | New | CZ02 | 2.25 | 0.000609 | 0 | 2.37 | 0.000739 | -0.00649 | 2.25 | 0.000609 | 0 | 2.37 | 0.000739 | -0.00649 |  | LF | Bldg | 2250 | 0.609 | 2250 | 0.609 | 1.05 | 1.21 | -0.0028844 | 2250 | 0.609 | 2250 | 0.609 | 1.05 | 1.21 | -0.00288
LFBldgPGEOfSNewCZ03 | Com-Iltg-dWatt-LF_OSbldg | PGE | OfS | New | CZ03 | 2.25 | 0.000609 | 0 | 2.34 | 0.000737 | -0.00721 | 2.25 | 0.000609 | 0 | 2.34 | 0.000737 | -0.00721 |  | LF | Bldg | 2250 | 0.609 | 2250 | 0.609 | 1.04 | 1.21 | -0.0032044 | 2250 | 0.609 | 2250 | 0.609 | 1.04 | 1.21 | -0.0032
LFBldgPGEOfSNewCZ04 | Com-Iltg-dWatt-LF_OSbldg | PGE | OfS | New | CZ04 | 2.25 | 0.000609 | 0 | 2.4 | 0.00075 | -0.00516 | 2.25 | 0.000609 | 0 | 2.4 | 0.00075 | -0.00516 |  | LF | Bldg | 2250 | 0.609 | 2250 | 0.609 | 1.07 | 1.23 | -0.0022933 | 2250 | 0.609 | 2250 | 0.609 | 1.07 | 1.23 | -0.00229
LFBldgPGEOfSNewCZ05 | Com-Iltg-dWatt-LF_OSbldg | PGE | OfS | New | CZ05 | 2.25 | 0.000609 | 0 | 2.35 | 0.000726 | -0.00552 | 2.25 | 0.000609 | 0 | 2.35 | 0.000726 | -0.00552 |  | LF | Bldg | 2250 | 0.609 | 2250 | 0.609 | 1.04 | 1.19 | -0.0024533 | 2250 | 0.609 | 2250 | 0.609 | 1.04 | 1.19 | -0.00245
LFBldgPGEOfSNewCZ11 | Com-Iltg-dWatt-LF_OSbldg | PGE | OfS | New | CZ11 | 2.25 | 0.000609 | 0 | 2.42 | 0.000763 | -0.00739 | 2.25 | 0.000609 | 0 | 2.42 | 0.000763 | -0.00739 |  | LF | Bldg | 2250 | 0.609 | 2250 | 0.609 | 1.08 | 1.25 | -0.0032844 | 2250 | 0.609 | 2250 | 0.609 | 1.08 | 1.25 | -0.00328
LFBldgPGEOfSNewCZ12 | Com-Iltg-dWatt-LF_OSbldg | PGE | OfS | New | CZ12 | 2.25 | 0.000609 | 0 | 2.41 | 0.000756 | -0.00714 | 2.25 | 0.000609 | 0 | 2.41 | 0.000756 | -0.00714 |  | LF | Bldg | 2250 | 0.609 | 2250 | 0.609 | 1.07 | 1.24 | -0.0031733 | 2250 | 0.609 | 2250 | 0.609 | 1.07 | 1.24 | -0.00317
LFBldgPGEOfSNewCZ13 | Com-Iltg-dWatt-LF_OSbldg | PGE | OfS | New | CZ13 | 2.25 | 0.000609 | 0 | 2.43 | 0.000755 | -0.00685 | 2.25 | 0.000609 | 0 | 2.43 | 0.000755 | -0.00685 |  | LF | Bldg | 2250 | 0.609 | 2250 | 0.609 | 1.08 | 1.24 | -0.0030444 | 2250 | 0.609 | 2250 | 0.609 | 1.08 | 1.24 | -0.00304
LFBldgPGEOfSNewCZ16 | Com-Iltg-dWatt-LF_OSbldg | PGE | OfS | New | CZ16 | 2.25 | 0.000609 | 0 | 2.25 | 0.000732 | -0.016 | 2.25 | 0.000609 | 0 | 2.25 | 0.000732 | -0.016 |  | LF | Bldg | 2250 | 0.609 | 2250 | 0.609 | 1 | 1.2 | -0.0071111 | 2250 | 0.609 | 2250 | 0.609 | 1 | 1.2 | -0.00711
LFBldgPGEOfSNewIOU | Com-Iltg-dWatt-LF_OSbldg | PGE | OfS | New | IOU | 2.25 | 0.000609 | 0 | 2.3905 | 0.0007488 | -0.006827 | 2.25 | 0.000609 | 0 | 2.3905 | 0.0007488 | -0.006827 |  | LF | Bldg | 2250 | 0.609 | 2250 | 0.609 | 1.06 | 1.23 | -0.0030342 | 2250 | 0.609 | 2250 | 0.609 | 1.06 | 1.23 | -0.00303
LFBldgPGERFFExCZ01 | Com-Iltg-dWatt-LF_OSbldg | PGE | RFF | Ex | CZ01 | 4.84 | 0.000813 | 0 | 4.68 | 0.000931 | -0.0639 | 4.84 | 0.000813 | 0 | 4.68 | 0.000931 | -0.0639 |  | LF | Bldg | 4840 | 0.813 | 4840 | 0.813 | 0.967 | 1.15 | -0.013202 | 4840 | 0.813 | 4840 | 0.813 | 0.967 | 1.15 | -0.0132
LFBldgPGERFFExCZ02 | Com-Iltg-dWatt-LF_OSbldg | PGE | RFF | Ex | CZ02 | 4.84 | 0.000813 | 0 | 4.99 | 0.000952 | -0.0406 | 4.84 | 0.000813 | 0 | 4.99 | 0.000952 | -0.0406 |  | LF | Bldg | 4840 | 0.813 | 4840 | 0.813 | 1.03 | 1.17 | -0.0083884 | 4840 | 0.813 | 4840 | 0.813 | 1.03 | 1.17 | -0.00839
LFBldgPGERFFExCZ03 | Com-Iltg-dWatt-LF_OSbldg | PGE | RFF | Ex | CZ03 | 4.84 | 0.000813 | 0 | 4.94 | 0.000948 | -0.0431 | 4.84 | 0.000813 | 0 | 4.94 | 0.000948 | -0.0431 |  | LF | Bldg | 4840 | 0.813 | 4840 | 0.813 | 1.02 | 1.17 | -0.008905 | 4840 | 0.813 | 4840 | 0.813 | 1.02 | 1.17 | -0.00891
LFBldgPGERFFExCZ04 | Com-Iltg-dWatt-LF_OSbldg | PGE | RFF | Ex | CZ04 | 4.84 | 0.000813 | 0 | 5.07 | 0.000952 | -0.0338 | 4.84 | 0.000813 | 0 | 5.07 | 0.000952 | -0.0338 |  | LF | Bldg | 4840 | 0.813 | 4840 | 0.813 | 1.05 | 1.17 | -0.0069835 | 4840 | 0.813 | 4840 | 0.813 | 1.05 | 1.17 | -0.00698
LFBldgPGERFFExCZ05 | Com-Iltg-dWatt-LF_OSbldg | PGE | RFF | Ex | CZ05 | 4.84 | 0.000813 | 0 | 4.92 | 0.000937 | -0.0437 | 4.84 | 0.000813 | 0 | 4.92 | 0.000937 | -0.0437 |  | LF | Bldg | 4840 | 0.813 | 4840 | 0.813 | 1.02 | 1.15 | -0.0090289 | 4840 | 0.813 | 4840 | 0.813 | 1.02 | 1.15 | -0.00903
LFBldgPGERFFExCZ11 | Com-Iltg-dWatt-LF_OSbldg | PGE | RFF | Ex | CZ11 | 4.84 | 0.000813 | 0 | 5.1 | 0.000969 | -0.0333 | 4.84 | 0.000813 | 0 | 5.1 | 0.000969 | -0.0333 |  | LF | Bldg | 4840 | 0.813 | 4840 | 0.813 | 1.05 | 1.19 | -0.0068802 | 4840 | 0.813 | 4840 | 0.813 | 1.05 | 1.19 | -0.00688
LFBldgPGERFFExCZ12 | Com-Iltg-dWatt-LF_OSbldg | PGE | RFF | Ex | CZ12 | 4.84 | 0.000813 | 0 | 5.08 | 0.000961 | -0.0347 | 4.84 | 0.000813 | 0 | 5.08 | 0.000961 | -0.0347 |  | LF | Bldg | 4840 | 0.813 | 4840 | 0.813 | 1.05 | 1.18 | -0.0071694 | 4840 | 0.813 | 4840 | 0.813 | 1.05 | 1.18 | -0.00717
LFBldgPGERFFExCZ13 | Com-Iltg-dWatt-LF_OSbldg | PGE | RFF | Ex | CZ13 | 4.84 | 0.000813 | 0 | 5.12 | 0.000957 | -0.0317 | 4.84 | 0.000813 | 0 | 5.12 | 0.000957 | -0.0317 |  | LF | Bldg | 4840 | 0.813 | 4840 | 0.813 | 1.06 | 1.18 | -0.0065496 | 4840 | 0.813 | 4840 | 0.813 | 1.06 | 1.18 | -0.00655
LFBldgPGERFFExCZ16 | Com-Iltg-dWatt-LF_OSbldg | PGE | RFF | Ex | CZ16 | 4.84 | 0.000813 | 0 | 4.73 | 0.000942 | -0.061 | 4.84 | 0.000813 | 0 | 4.73 | 0.000942 | -0.061 |  | LF | Bldg | 4840 | 0.813 | 4840 | 0.813 | 0.977 | 1.16 | -0.012603 | 4840 | 0.813 | 4840 | 0.813 | 0.977 | 1.16 | -0.0126
LFBldgPGERFFExIOU | Com-Iltg-dWatt-LF_OSbldg | PGE | RFF | Ex | IOU | 4.84 | 0.000813 | 0 | 5.0206 | 0.00095358 | -0.038117 | 4.84 | 0.000813 | 0 | 5.0206 | 0.00095358 | -0.038117 |  | LF | Bldg | 4840 | 0.813 | 4840 | 0.813 | 1.04 | 1.17 | -0.0078755 | 4840 | 0.813 | 4840 | 0.813 | 1.04 | 1.17 | -0.00788
LFBldgPGERFFNewCZ01 | Com-Iltg-dWatt-LF_OSbldg | PGE | RFF | New | CZ01 | 4.84 | 0.000813 | 0 | 4.54 | 0.000889 | -0.0682 | 4.84 | 0.000813 | 0 | 4.54 | 0.000889 | -0.0682 |  | LF | Bldg | 4840 | 0.813 | 4840 | 0.813 | 0.938 | 1.09 | -0.014091 | 4840 | 0.813 | 4840 | 0.813 | 0.938 | 1.09 | -0.0141
LFBldgPGERFFNewCZ02 | Com-Iltg-dWatt-LF_OSbldg | PGE | RFF | New | CZ02 | 4.84 | 0.000813 | 0 | 4.9 | 0.000995 | -0.0499 | 4.84 | 0.000813 | 0 | 4.9 | 0.000995 | -0.0499 |  | LF | Bldg | 4840 | 0.813 | 4840 | 0.813 | 1.01 | 1.22 | -0.01031 | 4840 | 0.813 | 4840 | 0.813 | 1.01 | 1.22 | -0.0103
LFBldgPGERFFNewCZ03 | Com-Iltg-dWatt-LF_OSbldg | PGE | RFF | New | CZ03 | 4.84 | 0.000813 | 0 | 4.79 | 0.000963 | -0.0499 | 4.84 | 0.000813 | 0 | 4.79 | 0.000963 | -0.0499 |  | LF | Bldg | 4840 | 0.813 | 4840 | 0.813 | 0.99 | 1.18 | -0.01031 | 4840 | 0.813 | 4840 | 0.813 | 0.99 | 1.18 | -0.0103
LFBldgPGERFFNewCZ04 | Com-Iltg-dWatt-LF_OSbldg | PGE | RFF | New | CZ04 | 4.84 | 0.000813 | 0 | 4.99 | 0.000982 | -0.0407 | 4.84 | 0.000813 | 0 | 4.99 | 0.000982 | -0.0407 |  | LF | Bldg | 4840 | 0.813 | 4840 | 0.813 | 1.03 | 1.21 | -0.0084091 | 4840 | 0.813 | 4840 | 0.813 | 1.03 | 1.21 | -0.00841
LFBldgPGERFFNewCZ05 | Com-Iltg-dWatt-LF_OSbldg | PGE | RFF | New | CZ05 | 4.84 | 0.000813 | 0 | 4.79 | 0.000949 | -0.0439 | 4.84 | 0.000813 | 0 | 4.79 | 0.000949 | -0.0439 |  | LF | Bldg | 4840 | 0.813 | 4840 | 0.813 | 0.99 | 1.17 | -0.0090702 | 4840 | 0.813 | 4840 | 0.813 | 0.99 | 1.17 | -0.00907
LFBldgPGERFFNewCZ11 | Com-Iltg-dWatt-LF_OSbldg | PGE | RFF | New | CZ11 | 4.84 | 0.000813 | 0 | 5.1 | 0.00101 | -0.0401 | 4.84 | 0.000813 | 0 | 5.1 | 0.00101 | -0.0401 |  | LF | Bldg | 4840 | 0.813 | 4840 | 0.813 | 1.05 | 1.24 | -0.0082851 | 4840 | 0.813 | 4840 | 0.813 | 1.05 | 1.24 | -0.00829
LFBldgPGERFFNewCZ12 | Com-Iltg-dWatt-LF_OSbldg | PGE | RFF | New | CZ12 | 4.84 | 0.000813 | 0 | 5.05 | 0.001 | -0.0432 | 4.84 | 0.000813 | 0 | 5.05 | 0.001 | -0.0432 |  | LF | Bldg | 4840 | 0.813 | 4840 | 0.813 | 1.04 | 1.23 | -0.0089256 | 4840 | 0.813 | 4840 | 0.813 | 1.04 | 1.23 | -0.00893
LFBldgPGERFFNewCZ13 | Com-Iltg-dWatt-LF_OSbldg | PGE | RFF | New | CZ13 | 4.84 | 0.000813 | 0 | 5.12 | 0.001 | -0.0382 | 4.84 | 0.000813 | 0 | 5.12 | 0.001 | -0.0382 |  | LF | Bldg | 4840 | 0.813 | 4840 | 0.813 | 1.06 | 1.23 | -0.0078926 | 4840 | 0.813 | 4840 | 0.813 | 1.06 | 1.23 | -0.00789
LFBldgPGERFFNewCZ16 | Com-Iltg-dWatt-LF_OSbldg | PGE | RFF | New | CZ16 | 4.84 | 0.000813 | 0 | 4.71 | 0.000967 | -0.0678 | 4.84 | 0.000813 | 0 | 4.71 | 0.000967 | -0.0678 |  | LF | Bldg | 4840 | 0.813 | 4840 | 0.813 | 0.973 | 1.19 | -0.014008 | 4840 | 0.813 | 4840 | 0.813 | 0.973 | 1.19 | -0.014
LFBldgPGERFFNewIOU | Com-Iltg-dWatt-LF_OSbldg | PGE | RFF | New | IOU | 4.84 | 0.000813 | 0 | 4.9495 | 0.00098356 | -0.045009 | 4.84 | 0.000813 | 0 | 4.9495 | 0.00098356 | -0.045009 |  | LF | Bldg | 4840 | 0.813 | 4840 | 0.813 | 1.02 | 1.21 | -0.0092994 | 4840 | 0.813 | 4840 | 0.813 | 1.02 | 1.21 | -0.0093
LFBldgPGERSDExCZ01 | Com-Iltg-dWatt-LF_OSbldg | PGE | RSD | Ex | CZ01 | 4.83 | 0.0008 | 0 | 4.42 | 0.000922 | -0.0826 | 4.83 | 0.0008 | 0 | 4.42 | 0.000922 | -0.0826 |  | LF | Bldg | 4830 | 0.8 | 4830 | 0.8 | 0.915 | 1.15 | -0.017101 | 4830 | 0.8 | 4830 | 0.8 | 0.915 | 1.15 | -0.0171
LFBldgPGERSDExCZ02 | Com-Iltg-dWatt-LF_OSbldg | PGE | RSD | Ex | CZ02 | 4.83 | 0.0008 | 0 | 4.9 | 0.000939 | -0.0468 | 4.83 | 0.0008 | 0 | 4.9 | 0.000939 | -0.0468 |  | LF | Bldg | 4830 | 0.8 | 4830 | 0.8 | 1.01 | 1.17 | -0.0096894 | 4830 | 0.8 | 4830 | 0.8 | 1.01 | 1.17 | -0.00969
LFBldgPGERSDExCZ03 | Com-Iltg-dWatt-LF_OSbldg | PGE | RSD | Ex | CZ03 | 4.83 | 0.0008 | 0 | 4.82 | 0.000947 | -0.0517 | 4.83 | 0.0008 | 0 | 4.82 | 0.000947 | -0.0517 |  | LF | Bldg | 4830 | 0.8 | 4830 | 0.8 | 0.998 | 1.18 | -0.010704 | 4830 | 0.8 | 4830 | 0.8 | 0.998 | 1.18 | -0.0107
LFBldgPGERSDExCZ04 | Com-Iltg-dWatt-LF_OSbldg | PGE | RSD | Ex | CZ04 | 4.83 | 0.0008 | 0 | 5.01 | 0.000948 | -0.0378 | 4.83 | 0.0008 | 0 | 5.01 | 0.000948 | -0.0378 |  | LF | Bldg | 4830 | 0.8 | 4830 | 0.8 | 1.04 | 1.19 | -0.0078261 | 4830 | 0.8 | 4830 | 0.8 | 1.04 | 1.19 | -0.00783
LFBldgPGERSDExCZ05 | Com-Iltg-dWatt-LF_OSbldg | PGE | RSD | Ex | CZ05 | 4.83 | 0.0008 | 0 | 4.83 | 0.000941 | -0.0497 | 4.83 | 0.0008 | 0 | 4.83 | 0.000941 | -0.0497 |  | LF | Bldg | 4830 | 0.8 | 4830 | 0.8 | 1 | 1.18 | -0.01029 | 4830 | 0.8 | 4830 | 0.8 | 1 | 1.18 | -0.0103
LFBldgPGERSDExCZ11 | Com-Iltg-dWatt-LF_OSbldg | PGE | RSD | Ex | CZ11 | 4.83 | 0.0008 | 0 | 5 | 0.000942 | -0.041 | 4.83 | 0.0008 | 0 | 5 | 0.000942 | -0.041 |  | LF | Bldg | 4830 | 0.8 | 4830 | 0.8 | 1.04 | 1.18 | -0.0084886 | 4830 | 0.8 | 4830 | 0.8 | 1.04 | 1.18 | -0.00849
LFBldgPGERSDExCZ12 | Com-Iltg-dWatt-LF_OSbldg | PGE | RSD | Ex | CZ12 | 4.83 | 0.0008 | 0 | 4.97 | 0.000907 | -0.0421 | 4.83 | 0.0008 | 0 | 4.97 | 0.000907 | -0.0421 |  | LF | Bldg | 4830 | 0.8 | 4830 | 0.8 | 1.03 | 1.13 | -0.0087164 | 4830 | 0.8 | 4830 | 0.8 | 1.03 | 1.13 | -0.00872
LFBldgPGERSDExCZ13 | Com-Iltg-dWatt-LF_OSbldg | PGE | RSD | Ex | CZ13 | 4.83 | 0.0008 | 0 | 5.04 | 0.00095 | -0.038 | 4.83 | 0.0008 | 0 | 5.04 | 0.00095 | -0.038 |  | LF | Bldg | 4830 | 0.8 | 4830 | 0.8 | 1.04 | 1.19 | -0.0078675 | 4830 | 0.8 | 4830 | 0.8 | 1.04 | 1.19 | -0.00787
LFBldgPGERSDExCZ16 | Com-Iltg-dWatt-LF_OSbldg | PGE | RSD | Ex | CZ16 | 4.83 | 0.0008 | 0 | 4.59 | 0.000911 | -0.0671 | 4.83 | 0.0008 | 0 | 4.59 | 0.000911 | -0.0671 |  | LF | Bldg | 4830 | 0.8 | 4830 | 0.8 | 0.95 | 1.14 | -0.013892 | 4830 | 0.8 | 4830 | 0.8 | 0.95 | 1.14 | -0.0139
LFBldgPGERSDExIOU | Com-Iltg-dWatt-LF_OSbldg | PGE | RSD | Ex | IOU | 4.83 | 0.0008 | 0 | 4.9187 | 0.00093724 | -0.045314 | 4.83 | 0.0008 | 0 | 4.9187 | 0.00093724 | -0.045314 |  | LF | Bldg | 4830 | 0.8 | 4830 | 0.8 | 1.02 | 1.17 | -0.0093818 | 4830 | 0.8 | 4830 | 0.8 | 1.02 | 1.17 | -0.00938
LFBldgPGERSDNewCZ01 | Com-Iltg-dWatt-LF_OSbldg | PGE | RSD | New | CZ01 | 4.83 | 0.0008 | 0 | 4.46 | 0.000927 | -0.0396 | 4.83 | 0.0008 | 0 | 4.46 | 0.000927 | -0.0396 |  | LF | Bldg | 4830 | 0.8 | 4830 | 0.8 | 0.923 | 1.16 | -0.0081988 | 4830 | 0.8 | 4830 | 0.8 | 0.923 | 1.16 | -0.0082
LFBldgPGERSDNewCZ02 | Com-Iltg-dWatt-LF_OSbldg | PGE | RSD | New | CZ02 | 4.83 | 0.0008 | 0 | 4.87 | 0.000988 | -0.0531 | 4.83 | 0.0008 | 0 | 4.87 | 0.000988 | -0.0531 |  | LF | Bldg | 4830 | 0.8 | 4830 | 0.8 | 1.01 | 1.23 | -0.010994 | 4830 | 0.8 | 4830 | 0.8 | 1.01 | 1.23 | -0.011
LFBldgPGERSDNewCZ03 | Com-Iltg-dWatt-LF_OSbldg | PGE | RSD | New | CZ03 | 4.83 | 0.0008 | 0 | 4.75 | 0.000974 | -0.0589 | 4.83 | 0.0008 | 0 | 4.75 | 0.000974 | -0.0589 |  | LF | Bldg | 4830 | 0.8 | 4830 | 0.8 | 0.983 | 1.22 | -0.012195 | 4830 | 0.8 | 4830 | 0.8 | 0.983 | 1.22 | -0.0122
LFBldgPGERSDNewCZ04 | Com-Iltg-dWatt-LF_OSbldg | PGE | RSD | New | CZ04 | 4.83 | 0.0008 | 0 | 4.99 | 0.000989 | -0.0429 | 4.83 | 0.0008 | 0 | 4.99 | 0.000989 | -0.0429 |  | LF | Bldg | 4830 | 0.8 | 4830 | 0.8 | 1.03 | 1.24 | -0.008882 | 4830 | 0.8 | 4830 | 0.8 | 1.03 | 1.24 | -0.00888
LFBldgPGERSDNewCZ05 | Com-Iltg-dWatt-LF_OSbldg | PGE | RSD | New | CZ05 | 4.83 | 0.0008 | 0 | 4.75 | 0.00095 | -0.057 | 4.83 | 0.0008 | 0 | 4.75 | 0.00095 | -0.057 |  | LF | Bldg | 4830 | 0.8 | 4830 | 0.8 | 0.983 | 1.19 | -0.011801 | 4830 | 0.8 | 4830 | 0.8 | 0.983 | 1.19 | -0.0118
LFBldgPGERSDNewCZ11 | Com-Iltg-dWatt-LF_OSbldg | PGE | RSD | New | CZ11 | 4.83 | 0.0008 | 0 | 5.03 | 0.00101 | -0.0458 | 4.83 | 0.0008 | 0 | 5.03 | 0.00101 | -0.0458 |  | LF | Bldg | 4830 | 0.8 | 4830 | 0.8 | 1.04 | 1.26 | -0.0094824 | 4830 | 0.8 | 4830 | 0.8 | 1.04 | 1.26 | -0.00948
LFBldgPGERSDNewCZ12 | Com-Iltg-dWatt-LF_OSbldg | PGE | RSD | New | CZ12 | 4.83 | 0.0008 | 0 | 4.99 | 0.000994 | -0.0461 | 4.83 | 0.0008 | 0 | 4.99 | 0.000994 | -0.0461 |  | LF | Bldg | 4830 | 0.8 | 4830 | 0.8 | 1.03 | 1.24 | -0.0095445 | 4830 | 0.8 | 4830 | 0.8 | 1.03 | 1.24 | -0.00954
LFBldgPGERSDNewCZ13 | Com-Iltg-dWatt-LF_OSbldg | PGE | RSD | New | CZ13 | 4.83 | 0.0008 | 0 | 5.06 | 0.00101 | -0.0433 | 4.83 | 0.0008 | 0 | 5.06 | 0.00101 | -0.0433 |  | LF | Bldg | 4830 | 0.8 | 4830 | 0.8 | 1.05 | 1.26 | -0.0089648 | 4830 | 0.8 | 4830 | 0.8 | 1.05 | 1.26 | -0.00896
LFBldgPGERSDNewCZ16 | Com-Iltg-dWatt-LF_OSbldg | PGE | RSD | New | CZ16 | 4.83 | 0.0008 | 0 | 4.58 | 0.000954 | -0.0536 | 4.83 | 0.0008 | 0 | 4.58 | 0.000954 | -0.0536 |  | LF | Bldg | 4830 | 0.8 | 4830 | 0.8 | 0.948 | 1.19 | -0.011097 | 4830 | 0.8 | 4830 | 0.8 | 0.948 | 1.19 | -0.0111
LFBldgPGERSDNewIOU | Com-Iltg-dWatt-LF_OSbldg | PGE | RSD | New | IOU | 4.83 | 0.0008 | 0 | 4.904 | 0.00098796 | -0.049989 | 4.83 | 0.0008 | 0 | 4.904 | 0.00098796 | -0.049989 |  | LF | Bldg | 4830 | 0.8 | 4830 | 0.8 | 1.02 | 1.23 | -0.01035 | 4830 | 0.8 | 4830 | 0.8 | 1.02 | 1.23 | -0.0104
LFBldgPGERt3ExCZ01 | Com-Iltg-dWatt-LF_OSbldg | PGE | Rt3 | Ex | CZ01 | 3.3795 | 0.00075986 | 0 | 3.3136 | 0.00089986 | -0.042895 | 3.37 | 0.00075724 | 0 | 3.31 | 0.00089688 | -0.0428 |  | LF | Bldg | 3380 | 0.76 | 3370 | 0.757 | 0.982 | 1.18 | -0.0127 | 3380 | 0.76 | 3370 | 0.757 | 0.982 | 1.18 | -0.0127
LFBldgPGERt3ExCZ02 | Com-Iltg-dWatt-LF_OSbldg | PGE | Rt3 | Ex | CZ02 | 3.3795 | 0.0007593 | 0 | 3.6095 | 0.00090335 | -0.020695 | 3.37 | 0.00075728 | 0 | 3.6 | 0.00090128 | -0.0206 |  | LF | Bldg | 3380 | 0.759 | 3370 | 0.757 | 1.07 | 1.19 | -0.0061128 | 3380 | 0.759 | 3370 | 0.757 | 1.07 | 1.19 | -0.00611
LFBldgPGERt3ExCZ03 | Com-Iltg-dWatt-LF_OSbldg | PGE | Rt3 | Ex | CZ03 | 3.3795 | 0.00075924 | 0 | 3.63 | 0.00090124 | -0.0188 | 3.37 | 0.00075724 | 0 | 3.6205 | 0.00089924 | -0.0188 |  | LF | Bldg | 3380 | 0.759 | 3370 | 0.757 | 1.07 | 1.19 | -0.0055786 | 3380 | 0.759 | 3370 | 0.757 | 1.07 | 1.19 | -0.00558
LFBldgPGERt3ExCZ04 | Com-Iltg-dWatt-LF_OSbldg | PGE | Rt3 | Ex | CZ04 | 3.3795 | 0.00075932 | 0 | 3.6895 | 0.00090556 | -0.0125 | 3.37 | 0.0007573 | 0 | 3.68 | 0.00090348 | -0.0125 |  | LF | Bldg | 3380 | 0.759 | 3370 | 0.757 | 1.09 | 1.19 | -0.0037092 | 3380 | 0.759 | 3370 | 0.757 | 1.09 | 1.19 | -0.00371
LFBldgPGERt3ExCZ05 | Com-Iltg-dWatt-LF_OSbldg | PGE | Rt3 | Ex | CZ05 | 3.3795 | 0.0007592 | 0 | 3.6297 | 0.0008892 | -0.0151 | 3.37 | 0.0007573 | 0 | 3.6202 | 0.0008873 | -0.0151 |  | LF | Bldg | 3380 | 0.759 | 3370 | 0.757 | 1.07 | 1.17 | -0.0044807 | 3380 | 0.759 | 3370 | 0.757 | 1.07 | 1.17 | -0.00448
LFBldgPGERt3ExCZ11 | Com-Iltg-dWatt-LF_OSbldg | PGE | Rt3 | Ex | CZ11 | 3.3793 | 0.00075921 | 0 | 3.6095 | 0.00090921 | -0.0205 | 3.37 | 0.00075735 | 0 | 3.6002 | 0.00090735 | -0.0205 |  | LF | Bldg | 3380 | 0.759 | 3370 | 0.757 | 1.07 | 1.2 | -0.0060831 | 3380 | 0.759 | 3370 | 0.757 | 1.07 | 1.2 | -0.00608
LFBldgPGERt3ExCZ12 | Com-Iltg-dWatt-LF_OSbldg | PGE | Rt3 | Ex | CZ12 | 3.3794 | 0.00075924 | 0 | 3.6196 | 0.00091424 | -0.019494 | 3.37 | 0.00075736 | 0 | 3.6102 | 0.00091236 | -0.0194 |  | LF | Bldg | 3380 | 0.759 | 3370 | 0.757 | 1.07 | 1.2 | -0.0057567 | 3380 | 0.759 | 3370 | 0.757 | 1.07 | 1.2 | -0.00576
LFBldgPGERt3ExCZ13 | Com-Iltg-dWatt-LF_OSbldg | PGE | Rt3 | Ex | CZ13 | 3.3793 | 0.0007592 | 0 | 3.63 | 0.0009052 | -0.018893 | 3.37 | 0.00075734 | 0 | 3.63 | 0.00090334 | -0.0188 |  | LF | Bldg | 3380 | 0.759 | 3370 | 0.757 | 1.08 | 1.19 | -0.0055786 | 3380 | 0.759 | 3370 | 0.757 | 1.08 | 1.19 | -0.00558
LFBldgPGERt3ExCZ16 | Com-Iltg-dWatt-LF_OSbldg | PGE | Rt3 | Ex | CZ16 | 3.3794 | 0.00076 | 0 | 3.3141 | 0.0008884 | -0.045594 | 3.37 | 0.0007573 | 0 | 3.31 | 0.0008853 | -0.0455 |  | LF | Bldg | 3380 | 0.76 | 3370 | 0.757 | 0.982 | 1.17 | -0.013501 | 3380 | 0.76 | 3370 | 0.757 | 0.982 | 1.17 | -0.0135
LFBldgPGERt3ExIOU | Com-Iltg-dWatt-LF_OSbldg | PGE | Rt3 | Ex | IOU | 3.3795 | 0.00075926 | 0 | 3.6291 | 0.00090568 | -0.018557 | 3.37 | 0.0007573 | 0 | 3.6211 | 0.0009037 | -0.018514 |  | LF | Bldg | 3380 | 0.759 | 3370 | 0.757 | 1.07 | 1.19 | -0.0054938 | 3380 | 0.759 | 3370 | 0.757 | 1.07 | 1.19 | -0.00549
LFBldgPGERt3NewCZ01 | Com-Iltg-dWatt-LF_OSbldg | PGE | Rt3 | New | CZ01 | 3.37 | 0.000758 | 0 | 3.26 | 0.000895 | -0.0488 | 3.37 | 0.000758 | 0 | 3.26 | 0.000895 | -0.0488 |  | LF | Bldg | 3370 | 0.758 | 3370 | 0.758 | 0.967 | 1.18 | -0.014481 | 3370 | 0.758 | 3370 | 0.758 | 0.967 | 1.18 | -0.0145
LFBldgPGERt3NewCZ02 | Com-Iltg-dWatt-LF_OSbldg | PGE | Rt3 | New | CZ02 | 3.37 | 0.000758 | 0 | 3.55 | 0.00093 | -0.0251 | 3.37 | 0.000758 | 0 | 3.55 | 0.00093 | -0.0251 |  | LF | Bldg | 3370 | 0.758 | 3370 | 0.758 | 1.05 | 1.23 | -0.0074481 | 3370 | 0.758 | 3370 | 0.758 | 1.05 | 1.23 | -0.00745
LFBldgPGERt3NewCZ03 | Com-Iltg-dWatt-LF_OSbldg | PGE | Rt3 | New | CZ03 | 3.37 | 0.000758 | 0 | 3.5 | 0.000912 | -0.0238 | 3.37 | 0.000758 | 0 | 3.5 | 0.000912 | -0.0238 |  | LF | Bldg | 3370 | 0.758 | 3370 | 0.758 | 1.04 | 1.2 | -0.0070623 | 3370 | 0.758 | 3370 | 0.758 | 1.04 | 1.2 | -0.00706
LFBldgPGERt3NewCZ04 | Com-Iltg-dWatt-LF_OSbldg | PGE | Rt3 | New | CZ04 | 3.37 | 0.000758 | 0 | 3.62 | 0.000926 | -0.0163 | 3.37 | 0.000758 | 0 | 3.62 | 0.000926 | -0.0163 |  | LF | Bldg | 3370 | 0.758 | 3370 | 0.758 | 1.07 | 1.22 | -0.0048368 | 3370 | 0.758 | 3370 | 0.758 | 1.07 | 1.22 | -0.00484
LFBldgPGERt3NewCZ05 | Com-Iltg-dWatt-LF_OSbldg | PGE | Rt3 | New | CZ05 | 3.37 | 0.000758 | 0 | 3.53 | 0.0009 | -0.019 | 3.37 | 0.000758 | 0 | 3.53 | 0.0009 | -0.019 |  | LF | Bldg | 3370 | 0.758 | 3370 | 0.758 | 1.05 | 1.19 | -0.005638 | 3370 | 0.758 | 3370 | 0.758 | 1.05 | 1.19 | -0.00564
LFBldgPGERt3NewCZ11 | Com-Iltg-dWatt-LF_OSbldg | PGE | Rt3 | New | CZ11 | 3.37 | 0.000758 | 0 | 3.62 | 0.000918 | -0.0212 | 3.37 | 0.000758 | 0 | 3.62 | 0.000918 | -0.0212 |  | LF | Bldg | 3370 | 0.758 | 3370 | 0.758 | 1.07 | 1.21 | -0.0062908 | 3370 | 0.758 | 3370 | 0.758 | 1.07 | 1.21 | -0.00629
LFBldgPGERt3NewCZ12 | Com-Iltg-dWatt-LF_OSbldg | PGE | Rt3 | New | CZ12 | 3.37 | 0.000758 | 0 | 3.63 | 0.000948 | -0.023 | 3.37 | 0.000758 | 0 | 3.63 | 0.000948 | -0.023 |  | LF | Bldg | 3370 | 0.758 | 3370 | 0.758 | 1.08 | 1.25 | -0.0068249 | 3370 | 0.758 | 3370 | 0.758 | 1.08 | 1.25 | -0.00682
LFBldgPGERt3NewCZ13 | Com-Iltg-dWatt-LF_OSbldg | PGE | Rt3 | New | CZ13 | 3.37 | 0.000758 | 0 | 3.66 | 0.000943 | -0.0206 | 3.37 | 0.000758 | 0 | 3.66 | 0.000943 | -0.0206 |  | LF | Bldg | 3370 | 0.758 | 3370 | 0.758 | 1.09 | 1.24 | -0.0061128 | 3370 | 0.758 | 3370 | 0.758 | 1.09 | 1.24 | -0.00611
LFBldgPGERt3NewCZ16 | Com-Iltg-dWatt-LF_OSbldg | PGE | Rt3 | New | CZ16 | 3.37 | 0.000758 | 0 | 3.33 | 0.000905 | -0.0461 | 3.37 | 0.000758 | 0 | 3.33 | 0.000905 | -0.0461 |  | LF | Bldg | 3370 | 0.758 | 3370 | 0.758 | 0.988 | 1.19 | -0.01368 | 3370 | 0.758 | 3370 | 0.758 | 0.988 | 1.19 | -0.0137
LFBldgPGERt3NewIOU | Com-Iltg-dWatt-LF_OSbldg | PGE | Rt3 | New | IOU | 3.37 | 0.000758 | 0 | 3.5884 | 0.00093004 | -0.022119 | 3.37 | 0.000758 | 0 | 3.5884 | 0.00093004 | -0.022119 |  | LF | Bldg | 3370 | 0.758 | 3370 | 0.758 | 1.06 | 1.23 | -0.0065636 | 3370 | 0.758 | 3370 | 0.758 | 1.06 | 1.23 | -0.00656
LFBldgPGERtLExCZ01 | Com-Iltg-dWatt-LF_OSbldg | PGE | RtL | Ex | CZ01 | 4.2695 | 0.00084802 | 0 | 4.1495 | 0.00101 | -0.060195 | 4.26 | 0.00084695 | 0 | 4.14 | 0.00101 | -0.0601 |  | LF | Bldg | 4270 | 0.848 | 4260 | 0.847 | 0.972 | 1.19 | -0.014108 | 4270 | 0.848 | 4260 | 0.847 | 0.972 | 1.19 | -0.0141
LFBldgPGERtLExCZ02 | Com-Iltg-dWatt-LF_OSbldg | PGE | RtL | Ex | CZ02 | 4.2695 | 0.00084804 | 0 | 4.5095 | 0.00101 | -0.0301 | 4.26 | 0.00084695 | 0 | 4.5 | 0.00101 | -0.0301 |  | LF | Bldg | 4270 | 0.848 | 4260 | 0.847 | 1.06 | 1.19 | -0.0070657 | 4270 | 0.848 | 4260 | 0.847 | 1.06 | 1.19 | -0.00707
LFBldgPGERtLExCZ03 | Com-Iltg-dWatt-LF_OSbldg | PGE | RtL | Ex | CZ03 | 4.2695 | 0.00084803 | 0 | 4.5296 | 0.001 | -0.0287 | 4.26 | 0.00084695 | 0 | 4.52 | 0.001 | -0.0287 |  | LF | Bldg | 4270 | 0.848 | 4260 | 0.847 | 1.06 | 1.18 | -0.0067371 | 4270 | 0.848 | 4260 | 0.847 | 1.06 | 1.18 | -0.00674
LFBldgPGERtLExCZ04 | Com-Iltg-dWatt-LF_OSbldg | PGE | RtL | Ex | CZ04 | 4.2695 | 0.00084805 | 0 | 4.6095 | 0.00101 | -0.021 | 4.26 | 0.00084695 | 0 | 4.6 | 0.00101 | -0.021 |  | LF | Bldg | 4270 | 0.848 | 4260 | 0.847 | 1.08 | 1.19 | -0.0049296 | 4270 | 0.848 | 4260 | 0.847 | 1.08 | 1.19 | -0.00493
LFBldgPGERtLExCZ05 | Com-Iltg-dWatt-LF_OSbldg | PGE | RtL | Ex | CZ05 | 4.2695 | 0.00084793 | 0 | 4.5097 | 0.0009899 | -0.028195 | 4.26 | 0.00084698 | 0 | 4.5097 | 0.000988 | -0.0281 |  | LF | Bldg | 4270 | 0.848 | 4260 | 0.847 | 1.06 | 1.17 | -0.0065962 | 4270 | 0.848 | 4260 | 0.847 | 1.06 | 1.17 | -0.0066
LFBldgPGERtLExCZ11 | Com-Iltg-dWatt-LF_OSbldg | PGE | RtL | Ex | CZ11 | 4.2693 | 0.00084791 | 0 | 4.5393 | 0.0010198 | -0.028993 | 4.26 | 0.00084698 | 0 | 4.53 | 0.0010198 | -0.028993 |  | LF | Bldg | 4270 | 0.848 | 4260 | 0.847 | 1.06 | 1.2 | -0.0068059 | 4270 | 0.848 | 4260 | 0.847 | 1.06 | 1.2 | -0.00681
LFBldgPGERtLExCZ12 | Com-Iltg-dWatt-LF_OSbldg | PGE | RtL | Ex | CZ12 | 4.2694 | 0.00084792 | 0 | 4.5396 | 0.00102 | -0.0265 | 4.26 | 0.00084698 | 0 | 4.5396 | 0.00102 | -0.0265 |  | LF | Bldg | 4270 | 0.848 | 4260 | 0.847 | 1.07 | 1.2 | -0.0062207 | 4270 | 0.848 | 4260 | 0.847 | 1.07 | 1.2 | -0.00622
LFBldgPGERtLExCZ13 | Com-Iltg-dWatt-LF_OSbldg | PGE | RtL | Ex | CZ13 | 4.2693 | 0.00084786 | 0 | 4.5793 | 0.00102 | -0.0257 | 4.26 | 0.00084693 | 0 | 4.57 | 0.00102 | -0.0257 |  | LF | Bldg | 4270 | 0.848 | 4260 | 0.847 | 1.07 | 1.2 | -0.0060329 | 4270 | 0.848 | 4260 | 0.847 | 1.07 | 1.2 | -0.00603
LFBldgPGERtLExCZ16 | Com-Iltg-dWatt-LF_OSbldg | PGE | RtL | Ex | CZ16 | 4.2694 | 0.00084789 | 0 | 4.1594 | 0.00097994 | -0.058494 | 4.26 | 0.00084694 | 0 | 4.15 | 0.000979 | -0.0584 |  | LF | Bldg | 4270 | 0.848 | 4260 | 0.847 | 0.974 | 1.16 | -0.013709 | 4270 | 0.848 | 4260 | 0.847 | 0.974 | 1.16 | -0.0137
LFBldgPGERtLExIOU | Com-Iltg-dWatt-LF_OSbldg | PGE | RtL | Ex | IOU | 4.2695 | 0.00084797 | 0 | 4.5437 | 0.0010105 | -0.0272 | 4.26 | 0.00084696 | 0 | 4.5367 | 0.0010104 | -0.027197 |  | LF | Bldg | 4270 | 0.848 | 4260 | 0.847 | 1.06 | 1.19 | -0.0063842 | 4270 | 0.848 | 4260 | 0.847 | 1.06 | 1.19 | -0.00638
LFBldgPGERtLNewCZ01 | Com-Iltg-dWatt-LF_OSbldg | PGE | RtL | New | CZ01 | 4.26 | 0.000846 | 0 | 4.12 | 0.000988 | -0.0652 | 4.26 | 0.000846 | 0 | 4.12 | 0.000988 | -0.0652 |  | LF | Bldg | 4260 | 0.846 | 4260 | 0.846 | 0.967 | 1.17 | -0.015305 | 4260 | 0.846 | 4260 | 0.846 | 0.967 | 1.17 | -0.0153
LFBldgPGERtLNewCZ02 | Com-Iltg-dWatt-LF_OSbldg | PGE | RtL | New | CZ02 | 4.26 | 0.000846 | 0 | 4.48 | 0.00106 | -0.0339 | 4.26 | 0.000846 | 0 | 4.48 | 0.00106 | -0.0339 |  | LF | Bldg | 4260 | 0.846 | 4260 | 0.846 | 1.05 | 1.25 | -0.0079577 | 4260 | 0.846 | 4260 | 0.846 | 1.05 | 1.25 | -0.00796
LFBldgPGERtLNewCZ03 | Com-Iltg-dWatt-LF_OSbldg | PGE | RtL | New | CZ03 | 4.26 | 0.000846 | 0 | 4.41 | 0.00102 | -0.0319 | 4.26 | 0.000846 | 0 | 4.41 | 0.00102 | -0.0319 |  | LF | Bldg | 4260 | 0.846 | 4260 | 0.846 | 1.04 | 1.21 | -0.0074883 | 4260 | 0.846 | 4260 | 0.846 | 1.04 | 1.21 | -0.00749
LFBldgPGERtLNewCZ04 | Com-Iltg-dWatt-LF_OSbldg | PGE | RtL | New | CZ04 | 4.26 | 0.000846 | 0 | 4.57 | 0.00104 | -0.0237 | 4.26 | 0.000846 | 0 | 4.57 | 0.00104 | -0.0237 |  | LF | Bldg | 4260 | 0.846 | 4260 | 0.846 | 1.07 | 1.23 | -0.0055634 | 4260 | 0.846 | 4260 | 0.846 | 1.07 | 1.23 | -0.00556
LFBldgPGERtLNewCZ05 | Com-Iltg-dWatt-LF_OSbldg | PGE | RtL | New | CZ05 | 4.26 | 0.000846 | 0 | 4.41 | 0.001 | -0.0328 | 4.26 | 0.000846 | 0 | 4.41 | 0.001 | -0.0328 |  | LF | Bldg | 4260 | 0.846 | 4260 | 0.846 | 1.04 | 1.18 | -0.0076995 | 4260 | 0.846 | 4260 | 0.846 | 1.04 | 1.18 | -0.0077
LFBldgPGERtLNewCZ11 | Com-Iltg-dWatt-LF_OSbldg | PGE | RtL | New | CZ11 | 4.26 | 0.000846 | 0 | 4.6 | 0.00106 | -0.0307 | 4.26 | 0.000846 | 0 | 4.6 | 0.00106 | -0.0307 |  | LF | Bldg | 4260 | 0.846 | 4260 | 0.846 | 1.08 | 1.25 | -0.0072066 | 4260 | 0.846 | 4260 | 0.846 | 1.08 | 1.25 | -0.00721
LFBldgPGERtLNewCZ12 | Com-Iltg-dWatt-LF_OSbldg | PGE | RtL | New | CZ12 | 4.26 | 0.000846 | 0 | 4.57 | 0.00107 | -0.0301 | 4.26 | 0.000846 | 0 | 4.57 | 0.00107 | -0.0301 |  | LF | Bldg | 4260 | 0.846 | 4260 | 0.846 | 1.07 | 1.26 | -0.0070657 | 4260 | 0.846 | 4260 | 0.846 | 1.07 | 1.26 | -0.00707
LFBldgPGERtLNewCZ13 | Com-Iltg-dWatt-LF_OSbldg | PGE | RtL | New | CZ13 | 4.26 | 0.000846 | 0 | 4.63 | 0.00106 | -0.0286 | 4.26 | 0.000846 | 0 | 4.63 | 0.00106 | -0.0286 |  | LF | Bldg | 4260 | 0.846 | 4260 | 0.846 | 1.09 | 1.25 | -0.0067136 | 4260 | 0.846 | 4260 | 0.846 | 1.09 | 1.25 | -0.00671
LFBldgPGERtLNewCZ16 | Com-Iltg-dWatt-LF_OSbldg | PGE | RtL | New | CZ16 | 4.26 | 0.000846 | 0 | 4.2 | 0.00101 | -0.0618 | 4.26 | 0.000846 | 0 | 4.2 | 0.00101 | -0.0618 |  | LF | Bldg | 4260 | 0.846 | 4260 | 0.846 | 0.986 | 1.19 | -0.014507 | 4260 | 0.846 | 4260 | 0.846 | 0.986 | 1.19 | -0.0145
LFBldgPGERtLNewIOU | Com-Iltg-dWatt-LF_OSbldg | PGE | RtL | New | IOU | 4.26 | 0.000846 | 0 | 4.5272 | 0.0010475 | -0.030209 | 4.26 | 0.000846 | 0 | 4.5272 | 0.0010475 | -0.030209 |  | LF | Bldg | 4260 | 0.846 | 4260 | 0.846 | 1.06 | 1.24 | -0.0070912 | 4260 | 0.846 | 4260 | 0.846 | 1.06 | 1.24 | -0.00709
LFBldgPGERtSExCZ01 | Com-Iltg-dWatt-LF_OSbldg | PGE | RtS | Ex | CZ01 | 3.38 | 0.000875 | 0 | 3.2931 | 0.00101 | -0.040831 | 3.38 | 0.000875 | 0 | 3.2931 | 0.00101 | -0.040831 |  | LF | Bldg | 3380 | 0.875 | 3380 | 0.875 | 0.974 | 1.15 | -0.01208 | 3380 | 0.875 | 3380 | 0.875 | 0.974 | 1.15 | -0.0121
LFBldgPGERtSExCZ02 | Com-Iltg-dWatt-LF_OSbldg | PGE | RtS | Ex | CZ02 | 3.38 | 0.000875 | 0 | 3.57 | 0.00102 | -0.0217 | 3.38 | 0.000875 | 0 | 3.57 | 0.00102 | -0.0217 |  | LF | Bldg | 3380 | 0.875 | 3380 | 0.875 | 1.06 | 1.17 | -0.0064201 | 3380 | 0.875 | 3380 | 0.875 | 1.06 | 1.17 | -0.00642
LFBldgPGERtSExCZ03 | Com-Iltg-dWatt-LF_OSbldg | PGE | RtS | Ex | CZ03 | 3.38 | 0.000875 | 0 | 3.572 | 0.00103 | -0.02012 | 3.38 | 0.000875 | 0 | 3.572 | 0.00103 | -0.02012 |  | LF | Bldg | 3380 | 0.875 | 3380 | 0.875 | 1.06 | 1.18 | -0.0059528 | 3380 | 0.875 | 3380 | 0.875 | 1.06 | 1.18 | -0.00595
LFBldgPGERtSExCZ04 | Com-Iltg-dWatt-LF_OSbldg | PGE | RtS | Ex | CZ04 | 3.38 | 0.000875 | 0 | 3.64 | 0.00104 | -0.0146 | 3.38 | 0.000875 | 0 | 3.64 | 0.00104 | -0.0146 |  | LF | Bldg | 3380 | 0.875 | 3380 | 0.875 | 1.08 | 1.19 | -0.0043195 | 3380 | 0.875 | 3380 | 0.875 | 1.08 | 1.19 | -0.00432
LFBldgPGERtSExCZ05 | Com-Iltg-dWatt-LF_OSbldg | PGE | RtS | Ex | CZ05 | 3.38 | 0.000875 | 0 | 3.5803 | 0.00102 | -0.0167 | 3.38 | 0.000875 | 0 | 3.5803 | 0.00102 | -0.0167 |  | LF | Bldg | 3380 | 0.875 | 3380 | 0.875 | 1.06 | 1.17 | -0.0049408 | 3380 | 0.875 | 3380 | 0.875 | 1.06 | 1.17 | -0.00494
LFBldgPGERtSExCZ11 | Com-Iltg-dWatt-LF_OSbldg | PGE | RtS | Ex | CZ11 | 3.38 | 0.000875 | 0 | 3.59 | 0.00104 | -0.0209 | 3.38 | 0.000875 | 0 | 3.59 | 0.00104 | -0.0209 |  | LF | Bldg | 3380 | 0.875 | 3380 | 0.875 | 1.06 | 1.19 | -0.0061834 | 3380 | 0.875 | 3380 | 0.875 | 1.06 | 1.19 | -0.00618
LFBldgPGERtSExCZ12 | Com-Iltg-dWatt-LF_OSbldg | PGE | RtS | Ex | CZ12 | 3.38 | 0.000875 | 0 | 3.5804 | 0.00104 | -0.021004 | 3.38 | 0.000875 | 0 | 3.5804 | 0.00104 | -0.021004 |  | LF | Bldg | 3380 | 0.875 | 3380 | 0.875 | 1.06 | 1.19 | -0.0062142 | 3380 | 0.875 | 3380 | 0.875 | 1.06 | 1.19 | -0.00621
LFBldgPGERtSExCZ13 | Com-Iltg-dWatt-LF_OSbldg | PGE | RtS | Ex | CZ13 | 3.38 | 0.000875 | 0 | 3.6 | 0.00104 | -0.0196 | 3.38 | 0.000875 | 0 | 3.6 | 0.00104 | -0.0196 |  | LF | Bldg | 3380 | 0.875 | 3380 | 0.875 | 1.07 | 1.19 | -0.0057988 | 3380 | 0.875 | 3380 | 0.875 | 1.07 | 1.19 | -0.0058
LFBldgPGERtSExCZ16 | Com-Iltg-dWatt-LF_OSbldg | PGE | RtS | Ex | CZ16 | 3.38 | 0.000875 | 0 | 3.33 | 0.00102 | -0.0398 | 3.38 | 0.000875 | 0 | 3.33 | 0.00102 | -0.0398 |  | LF | Bldg | 3380 | 0.875 | 3380 | 0.875 | 0.985 | 1.17 | -0.011775 | 3380 | 0.875 | 3380 | 0.875 | 0.985 | 1.17 | -0.0118
LFBldgPGERtSExIOU | Com-Iltg-dWatt-LF_OSbldg | PGE | RtS | Ex | IOU | 3.38 | 0.000875 | 0 | 3.5849 | 0.0010345 | -0.019821 | 3.38 | 0.000875 | 0 | 3.5849 | 0.0010345 | -0.019821 |  | LF | Bldg | 3380 | 0.875 | 3380 | 0.875 | 1.06 | 1.18 | -0.0058643 | 3380 | 0.875 | 3380 | 0.875 | 1.06 | 1.18 | -0.00586
LFBldgPGERtSNewCZ01 | Com-Iltg-dWatt-LF_OSbldg | PGE | RtS | New | CZ01 | 3.38 | 0.000875 | 0 | 3.29 | 0.000996 | -0.0459 | 3.38 | 0.000875 | 0 | 3.29 | 0.000996 | -0.0459 |  | LF | Bldg | 3380 | 0.875 | 3380 | 0.875 | 0.973 | 1.14 | -0.01358 | 3380 | 0.875 | 3380 | 0.875 | 0.973 | 1.14 | -0.0136
LFBldgPGERtSNewCZ02 | Com-Iltg-dWatt-LF_OSbldg | PGE | RtS | New | CZ02 | 3.38 | 0.000875 | 0 | 3.55 | 0.00105 | -0.024 | 3.38 | 0.000875 | 0 | 3.55 | 0.00105 | -0.024 |  | LF | Bldg | 3380 | 0.875 | 3380 | 0.875 | 1.05 | 1.2 | -0.0071006 | 3380 | 0.875 | 3380 | 0.875 | 1.05 | 1.2 | -0.0071
LFBldgPGERtSNewCZ03 | Com-Iltg-dWatt-LF_OSbldg | PGE | RtS | New | CZ03 | 3.38 | 0.000875 | 0 | 3.43 | 0.001 | -0.0221 | 3.38 | 0.000875 | 0 | 3.43 | 0.001 | -0.0221 |  | LF | Bldg | 3380 | 0.875 | 3380 | 0.875 | 1.01 | 1.14 | -0.0065385 | 3380 | 0.875 | 3380 | 0.875 | 1.01 | 1.14 | -0.00654
LFBldgPGERtSNewCZ04 | Com-Iltg-dWatt-LF_OSbldg | PGE | RtS | New | CZ04 | 3.38 | 0.000875 | 0 | 3.6 | 0.00104 | -0.0166 | 3.38 | 0.000875 | 0 | 3.6 | 0.00104 | -0.0166 |  | LF | Bldg | 3380 | 0.875 | 3380 | 0.875 | 1.07 | 1.19 | -0.0049112 | 3380 | 0.875 | 3380 | 0.875 | 1.07 | 1.19 | -0.00491
LFBldgPGERtSNewCZ05 | Com-Iltg-dWatt-LF_OSbldg | PGE | RtS | New | CZ05 | 3.38 | 0.000875 | 0 | 3.51 | 0.00101 | -0.0192 | 3.38 | 0.000875 | 0 | 3.51 | 0.00101 | -0.0192 |  | LF | Bldg | 3380 | 0.875 | 3380 | 0.875 | 1.04 | 1.15 | -0.0056805 | 3380 | 0.875 | 3380 | 0.875 | 1.04 | 1.15 | -0.00568
LFBldgPGERtSNewCZ11 | Com-Iltg-dWatt-LF_OSbldg | PGE | RtS | New | CZ11 | 3.38 | 0.000875 | 0 | 3.64 | 0.00107 | -0.0208 | 3.38 | 0.000875 | 0 | 3.64 | 0.00107 | -0.0208 |  | LF | Bldg | 3380 | 0.875 | 3380 | 0.875 | 1.08 | 1.22 | -0.0061538 | 3380 | 0.875 | 3380 | 0.875 | 1.08 | 1.22 | -0.00615
LFBldgPGERtSNewCZ12 | Com-Iltg-dWatt-LF_OSbldg | PGE | RtS | New | CZ12 | 3.38 | 0.000875 | 0 | 3.61 | 0.00106 | -0.0223 | 3.38 | 0.000875 | 0 | 3.61 | 0.00106 | -0.0223 |  | LF | Bldg | 3380 | 0.875 | 3380 | 0.875 | 1.07 | 1.21 | -0.0065976 | 3380 | 0.875 | 3380 | 0.875 | 1.07 | 1.21 | -0.0066
LFBldgPGERtSNewCZ13 | Com-Iltg-dWatt-LF_OSbldg | PGE | RtS | New | CZ13 | 3.38 | 0.000875 | 0 | 3.63 | 0.00105 | -0.0203 | 3.38 | 0.000875 | 0 | 3.63 | 0.00105 | -0.0203 |  | LF | Bldg | 3380 | 0.875 | 3380 | 0.875 | 1.07 | 1.2 | -0.0060059 | 3380 | 0.875 | 3380 | 0.875 | 1.07 | 1.2 | -0.00601
LFBldgPGERtSNewCZ16 | Com-Iltg-dWatt-LF_OSbldg | PGE | RtS | New | CZ16 | 3.38 | 0.000875 | 0 | 3.34 | 0.00102 | -0.0425 | 3.38 | 0.000875 | 0 | 3.34 | 0.00102 | -0.0425 |  | LF | Bldg | 3380 | 0.875 | 3380 | 0.875 | 0.988 | 1.17 | -0.012574 | 3380 | 0.875 | 3380 | 0.875 | 0.988 | 1.17 | -0.0126
LFBldgPGERtSNewIOU | Com-Iltg-dWatt-LF_OSbldg | PGE | RtS | New | IOU | 3.38 | 0.000875 | 0 | 3.558 | 0.0010383 | -0.021348 | 3.38 | 0.000875 | 0 | 3.558 | 0.0010383 | -0.021348 |  | LF | Bldg | 3380 | 0.875 | 3380 | 0.875 | 1.05 | 1.19 | -0.006316 | 3380 | 0.875 | 3380 | 0.875 | 1.05 | 1.19 | -0.00632
LFBldgPGESCnExCZ01 | Com-Iltg-dWatt-LF_OSbldg | PGE | SCn | Ex | CZ01 | 3.4295 | 0.00070286 | 0 | 2.8966 | 0.00070286 | -0.058332 | 3.39 | 0.000687 | 0 | 2.86 | 0.000687 | -0.0576 |  | LF | Bldg | 3430 | 0.703 | 3390 | 0.687 | 0.844 | 1 | -0.016991 | 3430 | 0.703 | 3390 | 0.687 | 0.844 | 1 | -0.017
LFBldgPGESCnExCZ02 | Com-Iltg-dWatt-LF_OSbldg | PGE | SCn | Ex | CZ02 | 3.4288 | 0.00070268 | 0 | 3.2762 | 0.00088524 | -0.031362 | 3.39 | 0.000687 | 0 | 3.24 | 0.00086526 | -0.031 |  | LF | Bldg | 3430 | 0.703 | 3390 | 0.687 | 0.956 | 1.26 | -0.0091445 | 3430 | 0.703 | 3390 | 0.687 | 0.956 | 1.26 | -0.00914
LFBldgPGESCnExCZ03 | Com-Iltg-dWatt-LF_OSbldg | PGE | SCn | Ex | CZ03 | 3.4353 | 0.00070482 | 0 | 3.1553 | 0.00094425 | -0.034706 | 3.39 | 0.000687 | 0 | 3.1142 | 0.00092042 | -0.0342 |  | LF | Bldg | 3440 | 0.705 | 3390 | 0.687 | 0.919 | 1.34 | -0.010088 | 3440 | 0.705 | 3390 | 0.687 | 0.919 | 1.34 | -0.0101
LFBldgPGESCnExCZ04 | Com-Iltg-dWatt-LF_OSbldg | PGE | SCn | Ex | CZ04 | 3.428 | 0.00070243 | 0 | 3.358 | 0.00088417 | -0.027556 | 3.39 | 0.000687 | 0 | 3.32 | 0.00086424 | -0.0272 |  | LF | Bldg | 3430 | 0.702 | 3390 | 0.687 | 0.979 | 1.26 | -0.0080236 | 3430 | 0.702 | 3390 | 0.687 | 0.979 | 1.26 | -0.00802
LFBldgPGESCnExCZ05 | Com-Iltg-dWatt-LF_OSbldg | PGE | SCn | Ex | CZ05 | 3.4216 | 0.00070037 | 0 | 3.1209 | 0.00084146 | -0.034916 | 3.39 | 0.000687 | 0 | 3.09 | 0.00082508 | -0.0346 |  | LF | Bldg | 3420 | 0.7 | 3390 | 0.687 | 0.912 | 1.2 | -0.010206 | 3420 | 0.7 | 3390 | 0.687 | 0.912 | 1.2 | -0.0102
LFBldgPGESCnExCZ11 | Com-Iltg-dWatt-LF_OSbldg | PGE | SCn | Ex | CZ11 | 3.423 | 0.00070065 | 0 | 3.3505 | 0.0008577 | -0.028715 | 3.39 | 0.000687 | 0 | 3.3115 | 0.00084015 | -0.0284 |  | LF | Bldg | 3420 | 0.701 | 3390 | 0.687 | 0.977 | 1.22 | -0.0083776 | 3420 | 0.701 | 3390 | 0.687 | 0.977 | 1.22 | -0.00838
LFBldgPGESCnExCZ12 | Com-Iltg-dWatt-LF_OSbldg | PGE | SCn | Ex | CZ12 | 3.4222 | 0.00070039 | 0 | 3.3622 | 0.00087039 | -0.028809 | 3.39 | 0.000687 | 0 | 3.33 | 0.00085313 | -0.0285 |  | LF | Bldg | 3420 | 0.7 | 3390 | 0.687 | 0.982 | 1.24 | -0.0084071 | 3420 | 0.7 | 3390 | 0.687 | 0.982 | 1.24 | -0.00841
LFBldgPGESCnExCZ13 | Com-Iltg-dWatt-LF_OSbldg | PGE | SCn | Ex | CZ13 | 3.4172 | 0.00069876 | 0 | 3.3862 | 0.00085148 | -0.025672 | 3.39 | 0.000687 | 0 | 3.35 | 0.000837 | -0.0254 |  | LF | Bldg | 3420 | 0.699 | 3390 | 0.687 | 0.988 | 1.22 | -0.0074926 | 3420 | 0.699 | 3390 | 0.687 | 0.988 | 1.22 | -0.00749
LFBldgPGESCnExCZ16 | Com-Iltg-dWatt-LF_OSbldg | PGE | SCn | Ex | CZ16 | 3.4172 | 0.0006988 | 0 | 3.0372 | 0.00083652 | -0.040363 | 3.39 | 0.000687 | 0 | 3.01 | 0.000822 | -0.04 |  | LF | Bldg | 3420 | 0.699 | 3390 | 0.687 | 0.888 | 1.2 | -0.011799 | 3420 | 0.699 | 3390 | 0.687 | 0.888 | 1.2 | -0.0118
LFBldgPGESCnExIOU | Com-Iltg-dWatt-LF_OSbldg | PGE | SCn | Ex | IOU | 3.4272 | 0.0007021 | 0 | 3.2794 | 0.00089297 | -0.030762 | 3.39 | 0.000687 | 0 | 3.2422 | 0.00087338 | -0.030377 |  | LF | Bldg | 3430 | 0.702 | 3390 | 0.687 | 0.956 | 1.27 | -0.0089608 | 3430 | 0.702 | 3390 | 0.687 | 0.956 | 1.27 | -0.00896
LFBldgPGESCnNewCZ01 | Com-Iltg-dWatt-LF_OSbldg | PGE | SCn | New | CZ01 | 3.39 | 0.000687 | 0 | 2.91 | 0.000687 | -0.0617 | 3.39 | 0.000687 | 0 | 2.91 | 0.000687 | -0.0617 |  | LF | Bldg | 3390 | 0.687 | 3390 | 0.687 | 0.858 | 1 | -0.018201 | 3390 | 0.687 | 3390 | 0.687 | 0.858 | 1 | -0.0182
LFBldgPGESCnNewCZ02 | Com-Iltg-dWatt-LF_OSbldg | PGE | SCn | New | CZ02 | 3.39 | 0.000687 | 0 | 3.23 | 0.000838 | -0.0322 | 3.39 | 0.000687 | 0 | 3.23 | 0.000838 | -0.0322 |  | LF | Bldg | 3390 | 0.687 | 3390 | 0.687 | 0.953 | 1.22 | -0.0094985 | 3390 | 0.687 | 3390 | 0.687 | 0.953 | 1.22 | -0.0095
LFBldgPGESCnNewCZ03 | Com-Iltg-dWatt-LF_OSbldg | PGE | SCn | New | CZ03 | 3.39 | 0.000687 | 0 | 3.13 | 0.000862 | -0.0363 | 3.39 | 0.000687 | 0 | 3.13 | 0.000862 | -0.0363 |  | LF | Bldg | 3390 | 0.687 | 3390 | 0.687 | 0.923 | 1.25 | -0.010708 | 3390 | 0.687 | 3390 | 0.687 | 0.923 | 1.25 | -0.0107
LFBldgPGESCnNewCZ04 | Com-Iltg-dWatt-LF_OSbldg | PGE | SCn | New | CZ04 | 3.39 | 0.000687 | 0 | 3.31 | 0.00083 | -0.0287 | 3.39 | 0.000687 | 0 | 3.31 | 0.00083 | -0.0287 |  | LF | Bldg | 3390 | 0.687 | 3390 | 0.687 | 0.976 | 1.21 | -0.0084661 | 3390 | 0.687 | 3390 | 0.687 | 0.976 | 1.21 | -0.00847
LFBldgPGESCnNewCZ05 | Com-Iltg-dWatt-LF_OSbldg | PGE | SCn | New | CZ05 | 3.39 | 0.000687 | 0 | 3.1 | 0.000824 | -0.0363 | 3.39 | 0.000687 | 0 | 3.1 | 0.000824 | -0.0363 |  | LF | Bldg | 3390 | 0.687 | 3390 | 0.687 | 0.914 | 1.2 | -0.010708 | 3390 | 0.687 | 3390 | 0.687 | 0.914 | 1.2 | -0.0107
LFBldgPGESCnNewCZ11 | Com-Iltg-dWatt-LF_OSbldg | PGE | SCn | New | CZ11 | 3.39 | 0.000687 | 0 | 3.3 | 0.00082 | -0.0294 | 3.39 | 0.000687 | 0 | 3.3 | 0.00082 | -0.0294 |  | LF | Bldg | 3390 | 0.687 | 3390 | 0.687 | 0.973 | 1.19 | -0.0086726 | 3390 | 0.687 | 3390 | 0.687 | 0.973 | 1.19 | -0.00867
LFBldgPGESCnNewCZ12 | Com-Iltg-dWatt-LF_OSbldg | PGE | SCn | New | CZ12 | 3.39 | 0.000687 | 0 | 3.31 | 0.000825 | -0.0297 | 3.39 | 0.000687 | 0 | 3.31 | 0.000825 | -0.0297 |  | LF | Bldg | 3390 | 0.687 | 3390 | 0.687 | 0.976 | 1.2 | -0.0087611 | 3390 | 0.687 | 3390 | 0.687 | 0.976 | 1.2 | -0.00876
LFBldgPGESCnNewCZ13 | Com-Iltg-dWatt-LF_OSbldg | PGE | SCn | New | CZ13 | 3.39 | 0.000687 | 0 | 3.29 | 0.000803 | -0.0257 | 3.39 | 0.000687 | 0 | 3.29 | 0.000803 | -0.0257 |  | LF | Bldg | 3390 | 0.687 | 3390 | 0.687 | 0.971 | 1.17 | -0.0075811 | 3390 | 0.687 | 3390 | 0.687 | 0.971 | 1.17 | -0.00758
LFBldgPGESCnNewCZ16 | Com-Iltg-dWatt-LF_OSbldg | PGE | SCn | New | CZ16 | 3.39 | 0.000687 | 0 | 3 | 0.000797 | -0.042 | 3.39 | 0.000687 | 0 | 3 | 0.000797 | -0.042 |  | LF | Bldg | 3390 | 0.687 | 3390 | 0.687 | 0.885 | 1.16 | -0.012389 | 3390 | 0.687 | 3390 | 0.687 | 0.885 | 1.16 | -0.0124
LFBldgPGESCnNewIOU | Com-Iltg-dWatt-LF_OSbldg | PGE | SCn | New | IOU | 3.39 | 0.000687 | 0 | 3.2518 | 0.00082856 | -0.03086 | 3.39 | 0.000687 | 0 | 3.2518 | 0.00082856 | -0.03086 |  | LF | Bldg | 3390 | 0.687 | 3390 | 0.687 | 0.959 | 1.21 | -0.0091034 | 3390 | 0.687 | 3390 | 0.687 | 0.959 | 1.21 | -0.0091
LFBldgPGESUnExCZ01 | Com-Iltg-dWatt-LF_OSbldg | PGE | SUn | Ex | CZ01 | 3.418 | 0.00069914 | 0 | 3.418 | 0.00069914 | 0 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 |  | LF | Bldg | 3420 | 0.699 | 3390 | 0.687 | 1 | 1 | 0 | 3420 | 0.699 | 3390 | 0.687 | 1 | 1 | 0
LFBldgPGESUnExCZ02 | Com-Iltg-dWatt-LF_OSbldg | PGE | SUn | Ex | CZ02 | 3.4185 | 0.00069934 | 0 | 3.4185 | 0.00069934 | 0 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 |  | LF | Bldg | 3420 | 0.699 | 3390 | 0.687 | 1 | 1 | 0 | 3420 | 0.699 | 3390 | 0.687 | 1 | 1 | 0
LFBldgPGESUnExCZ03 | Com-Iltg-dWatt-LF_OSbldg | PGE | SUn | Ex | CZ03 | 3.4185 | 0.00069935 | 0 | 3.4185 | 0.00069935 | 0 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 |  | LF | Bldg | 3420 | 0.699 | 3390 | 0.687 | 1 | 1 | 0 | 3420 | 0.699 | 3390 | 0.687 | 1 | 1 | 0
LFBldgPGESUnExCZ04 | Com-Iltg-dWatt-LF_OSbldg | PGE | SUn | Ex | CZ04 | 3.4185 | 0.00069935 | 0 | 3.4185 | 0.00069935 | 0 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 |  | LF | Bldg | 3420 | 0.699 | 3390 | 0.687 | 1 | 1 | 0 | 3420 | 0.699 | 3390 | 0.687 | 1 | 1 | 0
LFBldgPGESUnExCZ05 | Com-Iltg-dWatt-LF_OSbldg | PGE | SUn | Ex | CZ05 | 3.4185 | 0.00069935 | 0 | 3.4185 | 0.00069935 | 0 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 |  | LF | Bldg | 3420 | 0.699 | 3390 | 0.687 | 1 | 1 | 0 | 3420 | 0.699 | 3390 | 0.687 | 1 | 1 | 0
LFBldgPGESUnExCZ11 | Com-Iltg-dWatt-LF_OSbldg | PGE | SUn | Ex | CZ11 | 3.4169 | 0.00069867 | 0 | 3.4169 | 0.00069867 | 0 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 |  | LF | Bldg | 3420 | 0.699 | 3390 | 0.687 | 1 | 1 | 0 | 3420 | 0.699 | 3390 | 0.687 | 1 | 1 | 0
LFBldgPGESUnExCZ12 | Com-Iltg-dWatt-LF_OSbldg | PGE | SUn | Ex | CZ12 | 3.4171 | 0.00069874 | 0 | 3.4171 | 0.00069874 | 0 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 |  | LF | Bldg | 3420 | 0.699 | 3390 | 0.687 | 1 | 1 | 0 | 3420 | 0.699 | 3390 | 0.687 | 1 | 1 | 0
LFBldgPGESUnExCZ13 | Com-Iltg-dWatt-LF_OSbldg | PGE | SUn | Ex | CZ13 | 3.4172 | 0.00069876 | 0 | 3.4172 | 0.00069876 | 0 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 |  | LF | Bldg | 3420 | 0.699 | 3390 | 0.687 | 1 | 1 | 0 | 3420 | 0.699 | 3390 | 0.687 | 1 | 1 | 0
LFBldgPGESUnExCZ16 | Com-Iltg-dWatt-LF_OSbldg | PGE | SUn | Ex | CZ16 | 3.4172 | 0.0006988 | 0 | 3.4172 | 0.0006988 | 0 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 |  | LF | Bldg | 3420 | 0.699 | 3390 | 0.687 | 1 | 1 | 0 | 3420 | 0.699 | 3390 | 0.687 | 1 | 1 | 0
LFBldgPGESUnExIOU | Com-Iltg-dWatt-LF_OSbldg | PGE | SUn | Ex | IOU | 3.4179 | 0.00069907 | 0 | 3.4179 | 0.00069907 | 0 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 |  | LF | Bldg | 3420 | 0.699 | 3390 | 0.687 | 1 | 1 | 0 | 3420 | 0.699 | 3390 | 0.687 | 1 | 1 | 0
LFBldgPGESUnNewCZ01 | Com-Iltg-dWatt-LF_OSbldg | PGE | SUn | New | CZ01 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 |  | LF | Bldg | 3390 | 0.687 | 3390 | 0.687 | 1 | 1 | 0 | 3390 | 0.687 | 3390 | 0.687 | 1 | 1 | 0
LFBldgPGESUnNewCZ02 | Com-Iltg-dWatt-LF_OSbldg | PGE | SUn | New | CZ02 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 |  | LF | Bldg | 3390 | 0.687 | 3390 | 0.687 | 1 | 1 | 0 | 3390 | 0.687 | 3390 | 0.687 | 1 | 1 | 0
LFBldgPGESUnNewCZ03 | Com-Iltg-dWatt-LF_OSbldg | PGE | SUn | New | CZ03 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 |  | LF | Bldg | 3390 | 0.687 | 3390 | 0.687 | 1 | 1 | 0 | 3390 | 0.687 | 3390 | 0.687 | 1 | 1 | 0
LFBldgPGESUnNewCZ04 | Com-Iltg-dWatt-LF_OSbldg | PGE | SUn | New | CZ04 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 |  | LF | Bldg | 3390 | 0.687 | 3390 | 0.687 | 1 | 1 | 0 | 3390 | 0.687 | 3390 | 0.687 | 1 | 1 | 0
LFBldgPGESUnNewCZ05 | Com-Iltg-dWatt-LF_OSbldg | PGE | SUn | New | CZ05 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 |  | LF | Bldg | 3390 | 0.687 | 3390 | 0.687 | 1 | 1 | 0 | 3390 | 0.687 | 3390 | 0.687 | 1 | 1 | 0
LFBldgPGESUnNewCZ11 | Com-Iltg-dWatt-LF_OSbldg | PGE | SUn | New | CZ11 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 |  | LF | Bldg | 3390 | 0.687 | 3390 | 0.687 | 1 | 1 | 0 | 3390 | 0.687 | 3390 | 0.687 | 1 | 1 | 0
LFBldgPGESUnNewCZ12 | Com-Iltg-dWatt-LF_OSbldg | PGE | SUn | New | CZ12 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 |  | LF | Bldg | 3390 | 0.687 | 3390 | 0.687 | 1 | 1 | 0 | 3390 | 0.687 | 3390 | 0.687 | 1 | 1 | 0
LFBldgPGESUnNewCZ13 | Com-Iltg-dWatt-LF_OSbldg | PGE | SUn | New | CZ13 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 |  | LF | Bldg | 3390 | 0.687 | 3390 | 0.687 | 1 | 1 | 0 | 3390 | 0.687 | 3390 | 0.687 | 1 | 1 | 0
LFBldgPGESUnNewCZ16 | Com-Iltg-dWatt-LF_OSbldg | PGE | SUn | New | CZ16 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 |  | LF | Bldg | 3390 | 0.687 | 3390 | 0.687 | 1 | 1 | 0 | 3390 | 0.687 | 3390 | 0.687 | 1 | 1 | 0
LFBldgPGESUnNewIOU | Com-Iltg-dWatt-LF_OSbldg | PGE | SUn | New | IOU | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 |  | LF | Bldg | 3390 | 0.687 | 3390 | 0.687 | 1 | 1 | 0 | 3390 | 0.687 | 3390 | 0.687 | 1 | 1 | 0
LFBldgPGEWRfExCZ01 | Com-Iltg-dWatt-LF_OSbldg | PGE | WRf | Ex | CZ01 | 4.7552 | 0.00055521 | 0 | 7.3373 | 0.00076891 | 0 | 4.5402 | 0.000544 | 0 | 7.0102 | 0.00075302 | 0 |  | LF | Bldg | 4760 | 0.555 | 4540 | 0.544 | 1.54 | 1.38 | 0 | 4760 | 0.555 | 4540 | 0.544 | 1.54 | 1.38 | 0
LFBldgPGEWRfExCZ02 | Com-Iltg-dWatt-LF_OSbldg | PGE | WRf | Ex | CZ02 | 4.7574 | 0.00055534 | 0 | 7.5402 | 0.00071913 | 0 | 4.5402 | 0.000544 | 0 | 7.2002 | 0.00070402 | 0 |  | LF | Bldg | 4760 | 0.555 | 4540 | 0.544 | 1.59 | 1.29 | 0 | 4760 | 0.555 | 4540 | 0.544 | 1.59 | 1.29 | 0
LFBldgPGEWRfExCZ03 | Com-Iltg-dWatt-LF_OSbldg | PGE | WRf | Ex | CZ03 | 4.7577 | 0.00055535 | 0 | 7.7603 | 0.00073413 | 0 | 4.5402 | 0.000544 | 0 | 7.4198 | 0.000719 | 0 |  | LF | Bldg | 4760 | 0.555 | 4540 | 0.544 | 1.63 | 1.32 | 0 | 4760 | 0.555 | 4540 | 0.544 | 1.63 | 1.32 | 0
LFBldgPGEWRfExCZ04 | Com-Iltg-dWatt-LF_OSbldg | PGE | WRf | Ex | CZ04 | 4.758 | 0.00055536 | 0 | 7.6905 | 0.0007322 | 0 | 4.5402 | 0.000544 | 0 | 7.3496 | 0.00071705 | 0 |  | LF | Bldg | 4760 | 0.555 | 4540 | 0.544 | 1.62 | 1.32 | 0 | 4760 | 0.555 | 4540 | 0.544 | 1.62 | 1.32 | 0
LFBldgPGEWRfExCZ05 | Com-Iltg-dWatt-LF_OSbldg | PGE | WRf | Ex | CZ05 | 4.8427 | 0.00055996 | 0 | 7.6656 | 0.0007229 | 0 | 4.5405 | 0.000544 | 0 | 7.1962 | 0.000702 | 0 |  | LF | Bldg | 4840 | 0.56 | 4540 | 0.544 | 1.58 | 1.29 | 0 | 4840 | 0.56 | 4540 | 0.544 | 1.58 | 1.29 | 0
LFBldgPGEWRfExCZ11 | Com-Iltg-dWatt-LF_OSbldg | PGE | WRf | Ex | CZ11 | 4.8118 | 0.00055828 | 0 | 7.4346 | 0.00077133 | 0 | 4.541 | 0.000544 | 0 | 7.021 | 0.00075139 | 0 |  | LF | Bldg | 4810 | 0.558 | 4540 | 0.544 | 1.55 | 1.38 | 0 | 4810 | 0.558 | 4540 | 0.544 | 1.55 | 1.38 | 0
LFBldgPGEWRfExCZ12 | Com-Iltg-dWatt-LF_OSbldg | PGE | WRf | Ex | CZ12 | 4.8 | 0.00055764 | 0 | 7.519 | 0.00074031 | 0 | 4.5412 | 0.000544 | 0 | 7.1212 | 0.00072212 | 0 |  | LF | Bldg | 4800 | 0.558 | 4540 | 0.544 | 1.57 | 1.33 | 0 | 4800 | 0.558 | 4540 | 0.544 | 1.57 | 1.33 | 0
LFBldgPGEWRfExCZ13 | Com-Iltg-dWatt-LF_OSbldg | PGE | WRf | Ex | CZ13 | 4.7498 | 0.0005549 | 0 | 7.4187 | 0.00070062 | 0 | 4.5409 | 0.000544 | 0 | 7.1009 | 0.00068609 | 0 |  | LF | Bldg | 4750 | 0.555 | 4540 | 0.544 | 1.56 | 1.26 | 0 | 4750 | 0.555 | 4540 | 0.544 | 1.56 | 1.26 | 0
LFBldgPGEWRfExCZ16 | Com-Iltg-dWatt-LF_OSbldg | PGE | WRf | Ex | CZ16 | 4.7484 | 0.00055482 | 0 | 6.5905 | 0.00076933 | -0.00033552 | 4.541 | 0.000544 | 0 | 6.311 | 0.0007531 | -0.000322 |  | LF | Bldg | 4750 | 0.555 | 4540 | 0.544 | 1.39 | 1.38 | -7.091e-05 | 4750 | 0.555 | 4540 | 0.544 | 1.39 | 1.38 | -7.09e-05
LFBldgPGEWRfExIOU | Com-Iltg-dWatt-LF_OSbldg | PGE | WRf | Ex | IOU | 4.7692 | 0.00055596 | 0 | 7.5835 | 0.00072648 | -1.3091e-07 | 4.5406 | 0.000544 | 0 | 7.2305 | 0.0007105 | -1.2563e-07 |  | LF | Bldg | 4770 | 0.556 | 4540 | 0.544 | 1.59 | 1.31 | -2.7669e-08 | 4770 | 0.556 | 4540 | 0.544 | 1.59 | 1.31 | -2.77e-08
LFBldgPGEWRfNewCZ01 | Com-Iltg-dWatt-LF_OSbldg | PGE | WRf | New | CZ01 | 4.55 | 0.000544 | 0 | 5.77 | 0.000679 | 0 | 4.55 | 0.000544 | 0 | 5.77 | 0.000679 | 0 |  | LF | Bldg | 4550 | 0.544 | 4550 | 0.544 | 1.27 | 1.25 | 0 | 4550 | 0.544 | 4550 | 0.544 | 1.27 | 1.25 | 0
LFBldgPGEWRfNewCZ02 | Com-Iltg-dWatt-LF_OSbldg | PGE | WRf | New | CZ02 | 4.55 | 0.000544 | 0 | 6.22 | 0.000889 | 0 | 4.55 | 0.000544 | 0 | 6.22 | 0.000889 | 0 |  | LF | Bldg | 4550 | 0.544 | 4550 | 0.544 | 1.37 | 1.63 | 0 | 4550 | 0.544 | 4550 | 0.544 | 1.37 | 1.63 | 0
LFBldgPGEWRfNewCZ03 | Com-Iltg-dWatt-LF_OSbldg | PGE | WRf | New | CZ03 | 4.55 | 0.000544 | 0 | 6.01 | 0.00109 | 0 | 4.55 | 0.000544 | 0 | 6.01 | 0.00109 | 0 |  | LF | Bldg | 4550 | 0.544 | 4550 | 0.544 | 1.32 | 2 | 0 | 4550 | 0.544 | 4550 | 0.544 | 1.32 | 2 | 0
LFBldgPGEWRfNewCZ04 | Com-Iltg-dWatt-LF_OSbldg | PGE | WRf | New | CZ04 | 4.55 | 0.000544 | 0 | 6.35 | 0.00109 | 0 | 4.55 | 0.000544 | 0 | 6.35 | 0.00109 | 0 |  | LF | Bldg | 4550 | 0.544 | 4550 | 0.544 | 1.4 | 2 | 0 | 4550 | 0.544 | 4550 | 0.544 | 1.4 | 2 | 0
LFBldgPGEWRfNewCZ05 | Com-Iltg-dWatt-LF_OSbldg | PGE | WRf | New | CZ05 | 4.55 | 0.000544 | 0 | 5.88 | 0.000904 | 0 | 4.55 | 0.000544 | 0 | 5.88 | 0.000904 | 0 |  | LF | Bldg | 4550 | 0.544 | 4550 | 0.544 | 1.29 | 1.66 | 0 | 4550 | 0.544 | 4550 | 0.544 | 1.29 | 1.66 | 0
LFBldgPGEWRfNewCZ11 | Com-Iltg-dWatt-LF_OSbldg | PGE | WRf | New | CZ11 | 4.55 | 0.000544 | 0 | 6.27 | 0.00109 | 0 | 4.55 | 0.000544 | 0 | 6.27 | 0.00109 | 0 |  | LF | Bldg | 4550 | 0.544 | 4550 | 0.544 | 1.38 | 2 | 0 | 4550 | 0.544 | 4550 | 0.544 | 1.38 | 2 | 0
LFBldgPGEWRfNewCZ12 | Com-Iltg-dWatt-LF_OSbldg | PGE | WRf | New | CZ12 | 4.55 | 0.000544 | 0 | 6.32 | 0.000898 | 0 | 4.55 | 0.000544 | 0 | 6.32 | 0.000898 | 0 |  | LF | Bldg | 4550 | 0.544 | 4550 | 0.544 | 1.39 | 1.65 | 0 | 4550 | 0.544 | 4550 | 0.544 | 1.39 | 1.65 | 0
LFBldgPGEWRfNewCZ13 | Com-Iltg-dWatt-LF_OSbldg | PGE | WRf | New | CZ13 | 4.55 | 0.000544 | 0 | 6.38 | 0.000681 | 0 | 4.55 | 0.000544 | 0 | 6.38 | 0.000681 | 0 |  | LF | Bldg | 4550 | 0.544 | 4550 | 0.544 | 1.4 | 1.25 | 0 | 4550 | 0.544 | 4550 | 0.544 | 1.4 | 1.25 | 0
LFBldgPGEWRfNewCZ16 | Com-Iltg-dWatt-LF_OSbldg | PGE | WRf | New | CZ16 | 4.55 | 0.000544 | 0 | 5.73 | 0.00109 | 0 | 4.55 | 0.000544 | 0 | 5.73 | 0.00109 | 0 |  | LF | Bldg | 4550 | 0.544 | 4550 | 0.544 | 1.26 | 2 | 0 | 4550 | 0.544 | 4550 | 0.544 | 1.26 | 2 | 0
LFBldgPGEWRfNewIOU | Com-Iltg-dWatt-LF_OSbldg | PGE | WRf | New | IOU | 4.55 | 0.000544 | 0 | 6.256 | 0.00088589 | 0 | 4.55 | 0.000544 | 0 | 6.256 | 0.00088589 | 0 |  | LF | Bldg | 4550 | 0.544 | 4550 | 0.544 | 1.37 | 1.63 | 0 | 4550 | 0.544 | 4550 | 0.544 | 1.37 | 1.63 | 0
LFBldgSCEAsmExCZ05 | Com-Iltg-dWatt-LF_OSbldg | SCE | Asm | Ex | CZ05 | 2.6096 | 0.00053187 | 0 | 2.749 | 0.00063587 | -0.02689 | 2.5315 | 0.00051912 | 0 | 2.6706 | 0.00062111 | -0.02611 |  | LF | Bldg | 2610 | 0.532 | 2530 | 0.519 | 1.05 | 1.2 | -0.010314 | 2610 | 0.532 | 2530 | 0.519 | 1.05 | 1.2 | -0.0103
LFBldgSCEAsmExCZ06 | Com-Iltg-dWatt-LF_OSbldg | SCE | Asm | Ex | CZ06 | 2.6096 | 0.00053187 | 0 | 2.9294 | 0.00065881 | -0.012998 | 2.5315 | 0.00051911 | 0 | 2.8506 | 0.00064311 | -0.01261 |  | LF | Bldg | 2610 | 0.532 | 2530 | 0.519 | 1.13 | 1.24 | -0.004981 | 2610 | 0.532 | 2530 | 0.519 | 1.13 | 1.24 | -0.00498
LFBldgSCEAsmExCZ08 | Com-Iltg-dWatt-LF_OSbldg | SCE | Asm | Ex | CZ08 | 2.6096 | 0.00053187 | 0 | 2.9489 | 0.00064187 | -0.011198 | 2.5315 | 0.00051911 | 0 | 2.8609 | 0.00062708 | -0.0109 |  | LF | Bldg | 2610 | 0.532 | 2530 | 0.519 | 1.13 | 1.21 | -0.0043057 | 2610 | 0.532 | 2530 | 0.519 | 1.13 | 1.21 | -0.00431
LFBldgSCEAsmExCZ09 | Com-Iltg-dWatt-LF_OSbldg | SCE | Asm | Ex | CZ09 | 2.6096 | 0.00053187 | 0 | 2.9289 | 0.00065882 | -0.013598 | 2.5315 | 0.00051911 | 0 | 2.8409 | 0.00064311 | -0.013206 |  | LF | Bldg | 2610 | 0.532 | 2530 | 0.519 | 1.12 | 1.24 | -0.0052165 | 2610 | 0.532 | 2530 | 0.519 | 1.12 | 1.24 | -0.00522
LFBldgSCEAsmExCZ10 | Com-Iltg-dWatt-LF_OSbldg | SCE | Asm | Ex | CZ10 | 2.6117 | 0.00053211 | 0 | 2.8416 | 0.00063621 | -0.014995 | 2.534 | 0.00051928 | 0 | 2.7627 | 0.00062128 | -0.014527 |  | LF | Bldg | 2610 | 0.532 | 2530 | 0.519 | 1.09 | 1.2 | -0.0057326 | 2610 | 0.532 | 2530 | 0.519 | 1.09 | 1.2 | -0.00573
LFBldgSCEAsmExCZ13 | Com-Iltg-dWatt-LF_OSbldg | SCE | Asm | Ex | CZ13 | 2.6237 | 0.00053411 | 0 | 2.8052 | 0.00064541 | -0.023746 | 2.5341 | 0.00051918 | 0 | 2.7132 | 0.00062794 | -0.023009 |  | LF | Bldg | 2620 | 0.534 | 2530 | 0.519 | 1.07 | 1.21 | -0.0090796 | 2620 | 0.534 | 2530 | 0.519 | 1.07 | 1.21 | -0.00908
LFBldgSCEAsmExCZ14 | Com-Iltg-dWatt-LF_OSbldg | SCE | Asm | Ex | CZ14 | 2.6251 | 0.00053433 | 0 | 2.8141 | 0.00060476 | -0.023725 | 2.5347 | 0.00051921 | 0 | 2.7147 | 0.00058821 | -0.022937 |  | LF | Bldg | 2630 | 0.534 | 2530 | 0.519 | 1.07 | 1.13 | -0.0090491 | 2630 | 0.534 | 2530 | 0.519 | 1.07 | 1.13 | -0.00905
LFBldgSCEAsmExCZ15 | Com-Iltg-dWatt-LF_OSbldg | SCE | Asm | Ex | CZ15 | 2.6016 | 0.00053047 | 0 | 3.0988 | 0.00062919 | -0.0066577 | 2.5328 | 0.00051928 | 0 | 3.0214 | 0.00061628 | -0.0064942 |  | LF | Bldg | 2600 | 0.53 | 2530 | 0.519 | 1.19 | 1.19 | -0.002564 | 2600 | 0.53 | 2530 | 0.519 | 1.19 | 1.19 | -0.00256
LFBldgSCEAsmExCZ16 | Com-Iltg-dWatt-LF_OSbldg | SCE | Asm | Ex | CZ16 | 2.6034 | 0.00053078 | 0 | 2.5634 | 0.00062956 | -0.0367 | 2.5322 | 0.00051922 | 0 | 2.5011 | 0.00061622 | -0.035722 |  | LF | Bldg | 2600 | 0.531 | 2530 | 0.519 | 0.988 | 1.19 | -0.014107 | 2600 | 0.531 | 2530 | 0.519 | 0.988 | 1.19 | -0.0141
LFBldgSCEAsmExIOU | Com-Iltg-dWatt-LF_OSbldg | SCE | Asm | Ex | IOU | 2.6102 | 0.00053194 | 0 | 2.9155 | 0.00064482 | -0.013663 | 2.5322 | 0.00051916 | 0 | 2.8318 | 0.00062969 | -0.013266 |  | LF | Bldg | 2610 | 0.532 | 2530 | 0.519 | 1.12 | 1.21 | -0.005239 | 2610 | 0.532 | 2530 | 0.519 | 1.12 | 1.21 | -0.00524
LFBldgSCEAsmNewCZ05 | Com-Iltg-dWatt-LF_OSbldg | SCE | Asm | New | CZ05 | 2.55 | 0.000521 | 0 | 2.64 | 0.000615 | -0.027 | 2.55 | 0.000521 | 0 | 2.64 | 0.000615 | -0.027 |  | LF | Bldg | 2550 | 0.521 | 2550 | 0.521 | 1.04 | 1.18 | -0.010588 | 2550 | 0.521 | 2550 | 0.521 | 1.04 | 1.18 | -0.0106
LFBldgSCEAsmNewCZ06 | Com-Iltg-dWatt-LF_OSbldg | SCE | Asm | New | CZ06 | 2.55 | 0.000521 | 0 | 2.76 | 0.000635 | -0.0162 | 2.55 | 0.000521 | 0 | 2.76 | 0.000635 | -0.0162 |  | LF | Bldg | 2550 | 0.521 | 2550 | 0.521 | 1.08 | 1.22 | -0.0063529 | 2550 | 0.521 | 2550 | 0.521 | 1.08 | 1.22 | -0.00635
LFBldgSCEAsmNewCZ08 | Com-Iltg-dWatt-LF_OSbldg | SCE | Asm | New | CZ08 | 2.55 | 0.000521 | 0 | 2.79 | 0.000627 | -0.0133 | 2.55 | 0.000521 | 0 | 2.79 | 0.000627 | -0.0133 |  | LF | Bldg | 2550 | 0.521 | 2550 | 0.521 | 1.09 | 1.2 | -0.0052157 | 2550 | 0.521 | 2550 | 0.521 | 1.09 | 1.2 | -0.00522
LFBldgSCEAsmNewCZ09 | Com-Iltg-dWatt-LF_OSbldg | SCE | Asm | New | CZ09 | 2.55 | 0.000521 | 0 | 2.77 | 0.000651 | -0.0151 | 2.55 | 0.000521 | 0 | 2.77 | 0.000651 | -0.0151 |  | LF | Bldg | 2550 | 0.521 | 2550 | 0.521 | 1.09 | 1.25 | -0.0059216 | 2550 | 0.521 | 2550 | 0.521 | 1.09 | 1.25 | -0.00592
LFBldgSCEAsmNewCZ10 | Com-Iltg-dWatt-LF_OSbldg | SCE | Asm | New | CZ10 | 2.55 | 0.000521 | 0 | 2.78 | 0.000641 | -0.0153 | 2.55 | 0.000521 | 0 | 2.78 | 0.000641 | -0.0153 |  | LF | Bldg | 2550 | 0.521 | 2550 | 0.521 | 1.09 | 1.23 | -0.006 | 2550 | 0.521 | 2550 | 0.521 | 1.09 | 1.23 | -0.006
LFBldgSCEAsmNewCZ13 | Com-Iltg-dWatt-LF_OSbldg | SCE | Asm | New | CZ13 | 2.55 | 0.000521 | 0 | 2.72 | 0.000644 | -0.0246 | 2.55 | 0.000521 | 0 | 2.72 | 0.000644 | -0.0246 |  | LF | Bldg | 2550 | 0.521 | 2550 | 0.521 | 1.07 | 1.24 | -0.0096471 | 2550 | 0.521 | 2550 | 0.521 | 1.07 | 1.24 | -0.00965
LFBldgSCEAsmNewCZ14 | Com-Iltg-dWatt-LF_OSbldg | SCE | Asm | New | CZ14 | 2.55 | 0.000521 | 0 | 2.71 | 0.000627 | -0.0244 | 2.55 | 0.000521 | 0 | 2.71 | 0.000627 | -0.0244 |  | LF | Bldg | 2550 | 0.521 | 2550 | 0.521 | 1.06 | 1.2 | -0.0095686 | 2550 | 0.521 | 2550 | 0.521 | 1.06 | 1.2 | -0.00957
LFBldgSCEAsmNewCZ15 | Com-Iltg-dWatt-LF_OSbldg | SCE | Asm | New | CZ15 | 2.55 | 0.000521 | 0 | 2.96 | 0.000639 | -0.00705 | 2.55 | 0.000521 | 0 | 2.96 | 0.000639 | -0.00705 |  | LF | Bldg | 2550 | 0.521 | 2550 | 0.521 | 1.16 | 1.23 | -0.0027647 | 2550 | 0.521 | 2550 | 0.521 | 1.16 | 1.23 | -0.00276
LFBldgSCEAsmNewCZ16 | Com-Iltg-dWatt-LF_OSbldg | SCE | Asm | New | CZ16 | 2.55 | 0.000521 | 0 | 2.53 | 0.000621 | -0.0361 | 2.55 | 0.000521 | 0 | 2.53 | 0.000621 | -0.0361 |  | LF | Bldg | 2550 | 0.521 | 2550 | 0.521 | 0.992 | 1.19 | -0.014157 | 2550 | 0.521 | 2550 | 0.521 | 0.992 | 1.19 | -0.0142
LFBldgSCEAsmNewIOU | Com-Iltg-dWatt-LF_OSbldg | SCE | Asm | New | IOU | 2.55 | 0.000521 | 0 | 2.7849 | 0.00063643 | -0.01542 | 2.55 | 0.000521 | 0 | 2.7849 | 0.00063643 | -0.01542 |  | LF | Bldg | 2550 | 0.521 | 2550 | 0.521 | 1.09 | 1.22 | -0.006047 | 2550 | 0.521 | 2550 | 0.521 | 1.09 | 1.22 | -0.00605
LFBldgSCEComExCZ05 | Com-Iltg-dWatt-LF_OSbldg | SCE | Com | Ex | CZ05 | 3.6217 | 0.00074009 | 0 | 3.8828 | 0.00091389 | -0.029816 | 3.5437 | 0.00072256 | 0 | 3.8008 | 0.00089204 | -0.029249 |  | LF | Bldg | 3620 | 0.74 | 3540 | 0.723 | 1.07 | 1.23 | -0.008254 | 3620 | 0.74 | 3540 | 0.723 | 1.07 | 1.23 | -0.00825
LFBldgSCEComExCZ06 | Com-Iltg-dWatt-LF_OSbldg | SCE | Com | Ex | CZ06 | 3.1817 | 0.00071443 | 0 | 3.5918 | 0.00089149 | -0.012415 | 3.0864 | 0.00068925 | 0 | 3.4849 | 0.0008597 | -0.012041 |  | LF | Bldg | 3180 | 0.714 | 3090 | 0.689 | 1.13 | 1.25 | -0.0039012 | 3180 | 0.714 | 3090 | 0.689 | 1.13 | 1.25 | -0.0039
LFBldgSCEComExCZ08 | Com-Iltg-dWatt-LF_OSbldg | SCE | Com | Ex | CZ08 | 3.211 | 0.00072446 | 0 | 3.6061 | 0.00089998 | -0.011143 | 3.1194 | 0.00069884 | 0 | 3.5005 | 0.00086727 | -0.010803 |  | LF | Bldg | 3210 | 0.724 | 3120 | 0.699 | 1.12 | 1.24 | -0.0034631 | 3210 | 0.724 | 3120 | 0.699 | 1.12 | 1.24 | -0.00346
LFBldgSCEComExCZ09 | Com-Iltg-dWatt-LF_OSbldg | SCE | Com | Ex | CZ09 | 3.1705 | 0.00072031 | 0 | 3.5747 | 0.00091668 | -0.012753 | 3.0716 | 0.00069421 | 0 | 3.4626 | 0.00088267 | -0.012334 |  | LF | Bldg | 3170 | 0.72 | 3070 | 0.694 | 1.13 | 1.27 | -0.0040154 | 3170 | 0.72 | 3070 | 0.694 | 1.13 | 1.27 | -0.00402
LFBldgSCEComExCZ10 | Com-Iltg-dWatt-LF_OSbldg | SCE | Com | Ex | CZ10 | 3.3612 | 0.00073324 | 0 | 3.6636 | 0.00090231 | -0.012882 | 3.2894 | 0.00071286 | 0 | 3.5833 | 0.00087625 | -0.012599 |  | LF | Bldg | 3360 | 0.733 | 3290 | 0.713 | 1.09 | 1.23 | -0.0038303 | 3360 | 0.733 | 3290 | 0.713 | 1.09 | 1.23 | -0.00383
LFBldgSCEComExCZ13 | Com-Iltg-dWatt-LF_OSbldg | SCE | Com | Ex | CZ13 | 3.3158 | 0.00062589 | 0 | 3.7063 | 0.00077601 | -0.019513 | 3.2122 | 0.00060886 | 0 | 3.5897 | 0.00075493 | -0.018938 |  | LF | Bldg | 3320 | 0.626 | 3210 | 0.609 | 1.12 | 1.24 | -0.0058956 | 3320 | 0.626 | 3210 | 0.609 | 1.12 | 1.24 | -0.0059
LFBldgSCEComExCZ14 | Com-Iltg-dWatt-LF_OSbldg | SCE | Com | Ex | CZ14 | 3.2548 | 0.0007326 | 0 | 3.5437 | 0.0009192 | -0.021655 | 3.1684 | 0.00070809 | 0 | 3.4498 | 0.00088846 | -0.021114 |  | LF | Bldg | 3250 | 0.733 | 3170 | 0.708 | 1.09 | 1.25 | -0.0066638 | 3250 | 0.733 | 3170 | 0.708 | 1.09 | 1.25 | -0.00666
LFBldgSCEComExCZ15 | Com-Iltg-dWatt-LF_OSbldg | SCE | Com | Ex | CZ15 | 3.0335 | 0.00066899 | 0 | 3.5732 | 0.00084243 | -0.0053098 | 2.9546 | 0.00064971 | 0 | 3.4811 | 0.00081826 | -0.0051884 |  | LF | Bldg | 3030 | 0.669 | 2950 | 0.65 | 1.18 | 1.26 | -0.0017561 | 3030 | 0.669 | 2950 | 0.65 | 1.18 | 1.26 | -0.00176
LFBldgSCEComExCZ16 | Com-Iltg-dWatt-LF_OSbldg | SCE | Com | Ex | CZ16 | 3.008 | 0.00057597 | 0 | 3.0296 | 0.00069825 | -0.034634 | 2.9123 | 0.00055724 | 0 | 2.9344 | 0.0006757 | -0.033539 |  | LF | Bldg | 3010 | 0.576 | 2910 | 0.557 | 1.01 | 1.21 | -0.011516 | 3010 | 0.576 | 2910 | 0.557 | 1.01 | 1.21 | -0.0115
LFBldgSCEComExIOU | Com-Iltg-dWatt-LF_OSbldg | SCE | Com | Ex | IOU | 3.2218 | 0.00071664 | 0 | 3.599 | 0.00089317 | -0.012782 | 3.1322 | 0.00069264 | 0 | 3.4977 | 0.00086257 | -0.012415 |  | LF | Bldg | 3220 | 0.717 | 3130 | 0.693 | 1.12 | 1.25 | -0.0039637 | 3220 | 0.717 | 3130 | 0.693 | 1.12 | 1.25 | -0.00396
LFBldgSCEComNewCZ05 | Com-Iltg-dWatt-LF_OSbldg | SCE | Com | New | CZ05 | 3.6516 | 0.00074391 | 0 | 3.79 | 0.00090677 | -0.030515 | 3.6516 | 0.00074391 | 0 | 3.79 | 0.00090677 | -0.030515 |  | LF | Bldg | 3650 | 0.744 | 3650 | 0.744 | 1.04 | 1.22 | -0.0083568 | 3650 | 0.744 | 3650 | 0.744 | 1.04 | 1.22 | -0.00836
LFBldgSCEComNewCZ06 | Com-Iltg-dWatt-LF_OSbldg | SCE | Com | New | CZ06 | 3.2652 | 0.00071071 | 0 | 3.5858 | 0.00087308 | -0.012022 | 3.2652 | 0.00071071 | 0 | 3.5858 | 0.00087308 | -0.012022 |  | LF | Bldg | 3270 | 0.711 | 3270 | 0.711 | 1.1 | 1.23 | -0.0036818 | 3270 | 0.711 | 3270 | 0.711 | 1.1 | 1.23 | -0.00368
LFBldgSCEComNewCZ08 | Com-Iltg-dWatt-LF_OSbldg | SCE | Com | New | CZ08 | 3.2793 | 0.00071505 | 0 | 3.5962 | 0.00087924 | -0.010379 | 3.2793 | 0.00071505 | 0 | 3.5962 | 0.00087924 | -0.010379 |  | LF | Bldg | 3280 | 0.715 | 3280 | 0.715 | 1.1 | 1.23 | -0.003165 | 3280 | 0.715 | 3280 | 0.715 | 1.1 | 1.23 | -0.00317
LFBldgSCEComNewCZ09 | Com-Iltg-dWatt-LF_OSbldg | SCE | Com | New | CZ09 | 3.2111 | 0.00070645 | 0 | 3.5498 | 0.00090153 | -0.011344 | 3.2111 | 0.00070645 | 0 | 3.5498 | 0.00090153 | -0.011344 |  | LF | Bldg | 3210 | 0.706 | 3210 | 0.706 | 1.11 | 1.28 | -0.0035327 | 3210 | 0.706 | 3210 | 0.706 | 1.11 | 1.28 | -0.00353
LFBldgSCEComNewCZ10 | Com-Iltg-dWatt-LF_OSbldg | SCE | Com | New | CZ10 | 3.3502 | 0.00071568 | 0 | 3.5994 | 0.00088366 | -0.011555 | 3.3502 | 0.00071568 | 0 | 3.5994 | 0.00088366 | -0.011555 |  | LF | Bldg | 3350 | 0.716 | 3350 | 0.716 | 1.07 | 1.23 | -0.003449 | 3350 | 0.716 | 3350 | 0.716 | 1.07 | 1.23 | -0.00345
LFBldgSCEComNewCZ13 | Com-Iltg-dWatt-LF_OSbldg | SCE | Com | New | CZ13 | 3.3328 | 0.00063649 | 0 | 3.7157 | 0.00080127 | -0.018337 | 3.3328 | 0.00063649 | 0 | 3.7157 | 0.00080127 | -0.018337 |  | LF | Bldg | 3330 | 0.636 | 3330 | 0.636 | 1.11 | 1.26 | -0.0055019 | 3330 | 0.636 | 3330 | 0.636 | 1.11 | 1.26 | -0.0055
LFBldgSCEComNewCZ14 | Com-Iltg-dWatt-LF_OSbldg | SCE | Com | New | CZ14 | 3.2697 | 0.00071808 | 0 | 3.578 | 0.00092741 | -0.021163 | 3.2697 | 0.00071808 | 0 | 3.578 | 0.00092741 | -0.021163 |  | LF | Bldg | 3270 | 0.718 | 3270 | 0.718 | 1.09 | 1.29 | -0.0064726 | 3270 | 0.718 | 3270 | 0.718 | 1.09 | 1.29 | -0.00647
LFBldgSCEComNewCZ15 | Com-Iltg-dWatt-LF_OSbldg | SCE | Com | New | CZ15 | 3.0104 | 0.00066681 | 0 | 3.5392 | 0.00087185 | -0.0042452 | 3.0104 | 0.00066681 | 0 | 3.5392 | 0.00087185 | -0.0042452 |  | LF | Bldg | 3010 | 0.667 | 3010 | 0.667 | 1.18 | 1.31 | -0.0014102 | 3010 | 0.667 | 3010 | 0.667 | 1.18 | 1.31 | -0.00141
LFBldgSCEComNewCZ16 | Com-Iltg-dWatt-LF_OSbldg | SCE | Com | New | CZ16 | 3.0074 | 0.00059764 | 0 | 3.0287 | 0.00073184 | -0.032011 | 3.0074 | 0.00059764 | 0 | 3.0287 | 0.00073184 | -0.032011 |  | LF | Bldg | 3010 | 0.598 | 3010 | 0.598 | 1.01 | 1.22 | -0.010644 | 3010 | 0.598 | 3010 | 0.598 | 1.01 | 1.22 | -0.0106
LFBldgSCEComNewIOU | Com-Iltg-dWatt-LF_OSbldg | SCE | Com | New | IOU | 3.2759 | 0.00070582 | 0 | 3.5773 | 0.00087798 | -0.012039 | 3.2759 | 0.00070582 | 0 | 3.5773 | 0.00087798 | -0.012039 |  | LF | Bldg | 3280 | 0.706 | 3280 | 0.706 | 1.09 | 1.24 | -0.0036748 | 3280 | 0.706 | 3280 | 0.706 | 1.09 | 1.24 | -0.00367
LFBldgSCEECCExCZ05 | Com-Iltg-dWatt-LF_OSbldg | SCE | ECC | Ex | CZ05 | 2.4125 | 0.00080138 | 0 | 2.6316 | 0.00098829 | -0.028011 | 2.27 | 0.00071585 | 0 | 2.4795 | 0.0008828 | -0.026395 |  | LF | Bldg | 2410 | 0.801 | 2270 | 0.716 | 1.09 | 1.23 | -0.011628 | 2410 | 0.801 | 2270 | 0.716 | 1.09 | 1.23 | -0.0116
LFBldgSCEECCExCZ06 | Com-Iltg-dWatt-LF_OSbldg | SCE | ECC | Ex | CZ06 | 2.4127 | 0.00080149 | 0 | 2.7917 | 0.0010244 | -0.013556 | 2.27 | 0.00071585 | 0 | 2.63 | 0.00091881 | -0.0127 |  | LF | Bldg | 2410 | 0.801 | 2270 | 0.716 | 1.16 | 1.28 | -0.0055947 | 2410 | 0.801 | 2270 | 0.716 | 1.16 | 1.28 | -0.00559
LFBldgSCEECCExCZ08 | Com-Iltg-dWatt-LF_OSbldg | SCE | ECC | Ex | CZ08 | 2.4129 | 0.00080157 | 0 | 2.8214 | 0.0010242 | -0.012262 | 2.27 | 0.00071586 | 0 | 2.65 | 0.00091281 | -0.0115 |  | LF | Bldg | 2410 | 0.802 | 2270 | 0.716 | 1.17 | 1.28 | -0.0050661 | 2410 | 0.802 | 2270 | 0.716 | 1.17 | 1.28 | -0.00507
LFBldgSCEECCExCZ09 | Com-Iltg-dWatt-LF_OSbldg | SCE | ECC | Ex | CZ09 | 2.4118 | 0.00080089 | 0 | 2.8001 | 0.0010434 | -0.01405 | 2.27 | 0.00071584 | 0 | 2.63 | 0.00093378 | -0.0132 |  | LF | Bldg | 2410 | 0.801 | 2270 | 0.716 | 1.16 | 1.3 | -0.005815 | 2410 | 0.801 | 2270 | 0.716 | 1.16 | 1.3 | -0.00582
LFBldgSCEECCExCZ10 | Com-Iltg-dWatt-LF_OSbldg | SCE | ECC | Ex | CZ10 | 2.4056 | 0.00079704 | 0 | 2.7627 | 0.0010283 | -0.013413 | 2.27 | 0.00071571 | 0 | 2.609 | 0.00092261 | -0.01269 |  | LF | Bldg | 2410 | 0.797 | 2270 | 0.716 | 1.15 | 1.29 | -0.0055905 | 2410 | 0.797 | 2270 | 0.716 | 1.15 | 1.29 | -0.00559
LFBldgSCEECCExCZ13 | Com-Iltg-dWatt-LF_OSbldg | SCE | ECC | Ex | CZ13 | 2.4016 | 0.00048012 | 0 | 2.7091 | 0.00061915 | -0.02064 | 2.27 | 0.00043275 | 0 | 2.56 | 0.00055775 | -0.0195 |  | LF | Bldg | 2400 | 0.48 | 2270 | 0.433 | 1.13 | 1.29 | -0.0085903 | 2400 | 0.48 | 2270 | 0.433 | 1.13 | 1.29 | -0.00859
LFBldgSCEECCExCZ14 | Com-Iltg-dWatt-LF_OSbldg | SCE | ECC | Ex | CZ14 | 2.4063 | 0.00079748 | 0 | 2.7044 | 0.0010194 | -0.021672 | 2.27 | 0.00071573 | 0 | 2.5591 | 0.00091763 | -0.0204 |  | LF | Bldg | 2410 | 0.797 | 2270 | 0.716 | 1.13 | 1.28 | -0.0089868 | 2410 | 0.797 | 2270 | 0.716 | 1.13 | 1.28 | -0.00899
LFBldgSCEECCExCZ15 | Com-Iltg-dWatt-LF_OSbldg | SCE | ECC | Ex | CZ15 | 2.4056 | 0.00079704 | 0 | 2.9727 | 0.0010187 | -0.0059734 | 2.27 | 0.00071571 | 0 | 2.81 | 0.00091662 | -0.005639 |  | LF | Bldg | 2410 | 0.797 | 2270 | 0.716 | 1.24 | 1.28 | -0.0024842 | 2410 | 0.797 | 2270 | 0.716 | 1.24 | 1.28 | -0.00248
LFBldgSCEECCExCZ16 | Com-Iltg-dWatt-LF_OSbldg | SCE | ECC | Ex | CZ16 | 2.4054 | 0.00048155 | 0 | 2.5144 | 0.00059929 | -0.040447 | 2.27 | 0.00043281 | 0 | 2.379 | 0.0005388 | -0.03819 |  | LF | Bldg | 2410 | 0.482 | 2270 | 0.433 | 1.05 | 1.24 | -0.016824 | 2410 | 0.482 | 2270 | 0.433 | 1.05 | 1.24 | -0.0168
LFBldgSCEECCExIOU | Com-Iltg-dWatt-LF_OSbldg | SCE | ECC | Ex | IOU | 2.4106 | 0.00077005 | 0 | 2.7811 | 0.00098583 | -0.015277 | 2.27 | 0.00068877 | 0 | 2.6186 | 0.00088215 | -0.014365 |  | LF | Bldg | 2410 | 0.77 | 2270 | 0.689 | 1.15 | 1.28 | -0.0063281 | 2410 | 0.77 | 2270 | 0.689 | 1.15 | 1.28 | -0.00633
LFBldgSCEECCNewCZ05 | Com-Iltg-dWatt-LF_OSbldg | SCE | ECC | New | CZ05 | 2.27 | 0.000713 | 0 | 2.45 | 0.000893 | -0.0268 | 2.27 | 0.000713 | 0 | 2.45 | 0.000893 | -0.0268 |  | LF | Bldg | 2270 | 0.713 | 2270 | 0.713 | 1.08 | 1.25 | -0.011806 | 2270 | 0.713 | 2270 | 0.713 | 1.08 | 1.25 | -0.0118
LFBldgSCEECCNewCZ06 | Com-Iltg-dWatt-LF_OSbldg | SCE | ECC | New | CZ06 | 2.27 | 0.000713 | 0 | 2.58 | 0.000908 | -0.0121 | 2.27 | 0.000713 | 0 | 2.58 | 0.000908 | -0.0121 |  | LF | Bldg | 2270 | 0.713 | 2270 | 0.713 | 1.14 | 1.27 | -0.0053304 | 2270 | 0.713 | 2270 | 0.713 | 1.14 | 1.27 | -0.00533
LFBldgSCEECCNewCZ08 | Com-Iltg-dWatt-LF_OSbldg | SCE | ECC | New | CZ08 | 2.27 | 0.000713 | 0 | 2.6 | 0.000914 | -0.00976 | 2.27 | 0.000713 | 0 | 2.6 | 0.000914 | -0.00976 |  | LF | Bldg | 2270 | 0.713 | 2270 | 0.713 | 1.15 | 1.28 | -0.0042996 | 2270 | 0.713 | 2270 | 0.713 | 1.15 | 1.28 | -0.0043
LFBldgSCEECCNewCZ09 | Com-Iltg-dWatt-LF_OSbldg | SCE | ECC | New | CZ09 | 2.27 | 0.000713 | 0 | 2.6 | 0.000939 | -0.0115 | 2.27 | 0.000713 | 0 | 2.6 | 0.000939 | -0.0115 |  | LF | Bldg | 2270 | 0.713 | 2270 | 0.713 | 1.15 | 1.32 | -0.0050661 | 2270 | 0.713 | 2270 | 0.713 | 1.15 | 1.32 | -0.00507
LFBldgSCEECCNewCZ10 | Com-Iltg-dWatt-LF_OSbldg | SCE | ECC | New | CZ10 | 2.27 | 0.000713 | 0 | 2.63 | 0.00095 | -0.0116 | 2.27 | 0.000713 | 0 | 2.63 | 0.00095 | -0.0116 |  | LF | Bldg | 2270 | 0.713 | 2270 | 0.713 | 1.16 | 1.33 | -0.0051101 | 2270 | 0.713 | 2270 | 0.713 | 1.16 | 1.33 | -0.00511
LFBldgSCEECCNewCZ13 | Com-Iltg-dWatt-LF_OSbldg | SCE | ECC | New | CZ13 | 2.27 | 0.000431 | 0 | 2.6 | 0.000596 | -0.0189 | 2.27 | 0.000431 | 0 | 2.6 | 0.000596 | -0.0189 |  | LF | Bldg | 2270 | 0.431 | 2270 | 0.431 | 1.15 | 1.38 | -0.008326 | 2270 | 0.431 | 2270 | 0.431 | 1.15 | 1.38 | -0.00833
LFBldgSCEECCNewCZ14 | Com-Iltg-dWatt-LF_OSbldg | SCE | ECC | New | CZ14 | 2.27 | 0.000713 | 0 | 2.59 | 0.000922 | -0.0199 | 2.27 | 0.000713 | 0 | 2.59 | 0.000922 | -0.0199 |  | LF | Bldg | 2270 | 0.713 | 2270 | 0.713 | 1.14 | 1.29 | -0.0087665 | 2270 | 0.713 | 2270 | 0.713 | 1.14 | 1.29 | -0.00877
LFBldgSCEECCNewCZ15 | Com-Iltg-dWatt-LF_OSbldg | SCE | ECC | New | CZ15 | 2.27 | 0.000713 | 0 | 2.92 | 0.00102 | -0.00422 | 2.27 | 0.000713 | 0 | 2.92 | 0.00102 | -0.00422 |  | LF | Bldg | 2270 | 0.713 | 2270 | 0.713 | 1.29 | 1.43 | -0.001859 | 2270 | 0.713 | 2270 | 0.713 | 1.29 | 1.43 | -0.00186
LFBldgSCEECCNewCZ16 | Com-Iltg-dWatt-LF_OSbldg | SCE | ECC | New | CZ16 | 2.27 | 0.000431 | 0 | 2.4 | 0.000567 | -0.0377 | 2.27 | 0.000431 | 0 | 2.4 | 0.000567 | -0.0377 |  | LF | Bldg | 2270 | 0.431 | 2270 | 0.431 | 1.06 | 1.32 | -0.016608 | 2270 | 0.431 | 2270 | 0.431 | 1.06 | 1.32 | -0.0166
LFBldgSCEECCNewIOU | Com-Iltg-dWatt-LF_OSbldg | SCE | ECC | New | IOU | 2.27 | 0.00066686 | 0 | 2.5942 | 0.00087168 | -0.014651 | 2.27 | 0.00066686 | 0 | 2.5942 | 0.00087168 | -0.014651 |  | LF | Bldg | 2270 | 0.667 | 2270 | 0.667 | 1.14 | 1.31 | -0.0064541 | 2270 | 0.667 | 2270 | 0.667 | 1.14 | 1.31 | -0.00645
LFBldgSCEEPrExCZ05 | Com-Iltg-dWatt-LF_OSbldg | SCE | EPr | Ex | CZ05 | 2.1353 | 0.0006145 | 0 | 2.3348 | 0.00078308 | -0.018858 | 1.95 | 0.00055112 | 0 | 2.13 | 0.00070215 | -0.0172 |  | LF | Bldg | 2140 | 0.615 | 1950 | 0.551 | 1.09 | 1.27 | -0.0088205 | 2140 | 0.615 | 1950 | 0.551 | 1.09 | 1.27 | -0.00882
LFBldgSCEEPrExCZ06 | Com-Iltg-dWatt-LF_OSbldg | SCE | EPr | Ex | CZ06 | 2.1352 | 0.00061448 | 0 | 2.4942 | 0.00079802 | -0.009179 | 1.95 | 0.00055113 | 0 | 2.27 | 0.00071518 | -0.0083797 |  | LF | Bldg | 2140 | 0.614 | 1950 | 0.551 | 1.16 | 1.3 | -0.0042973 | 2140 | 0.614 | 1950 | 0.551 | 1.16 | 1.3 | -0.0043
LFBldgSCEEPrExCZ08 | Com-Iltg-dWatt-LF_OSbldg | SCE | EPr | Ex | CZ08 | 2.1351 | 0.00061445 | 0 | 2.5141 | 0.00080893 | -0.0075324 | 1.95 | 0.00055113 | 0 | 2.2997 | 0.00072515 | -0.0068797 |  | LF | Bldg | 2140 | 0.614 | 1950 | 0.551 | 1.18 | 1.32 | -0.0035281 | 2140 | 0.614 | 1950 | 0.551 | 1.18 | 1.32 | -0.00353
LFBldgSCEEPrExCZ09 | Com-Iltg-dWatt-LF_OSbldg | SCE | EPr | Ex | CZ09 | 2.1348 | 0.00061435 | 0 | 2.4739 | 0.00080879 | -0.0094366 | 1.95 | 0.00055114 | 0 | 2.26 | 0.00072517 | -0.00861 |  | LF | Bldg | 2130 | 0.614 | 1950 | 0.551 | 1.16 | 1.32 | -0.0044154 | 2130 | 0.614 | 1950 | 0.551 | 1.16 | 1.32 | -0.00442
LFBldgSCEEPrExCZ10 | Com-Iltg-dWatt-LF_OSbldg | SCE | EPr | Ex | CZ10 | 2.1285 | 0.00061237 | 0 | 2.3967 | 0.00078827 | -0.010242 | 1.95 | 0.0005513 | 0 | 2.19 | 0.00070936 | -0.00935 |  | LF | Bldg | 2130 | 0.612 | 1950 | 0.551 | 1.12 | 1.29 | -0.0047949 | 2130 | 0.612 | 1950 | 0.551 | 1.12 | 1.29 | -0.00479
LFBldgSCEEPrExCZ13 | Com-Iltg-dWatt-LF_OSbldg | SCE | EPr | Ex | CZ13 | 2.1276 | 1.987e-05 | 0 | 2.3363 | 1.987e-05 | -0.017296 | 1.95 | 1.7906e-05 | 0 | 2.14 | 1.7906e-05 | -0.0158 |  | LF | Bldg | 2130 | 0.0199 | 1950 | 0.0179 | 1.1 | 1 | -0.0081026 | 2130 | 0.0199 | 1950 | 0.0179 | 1.1 | 1 | -0.0081
LFBldgSCEEPrExCZ14 | Com-Iltg-dWatt-LF_OSbldg | SCE | EPr | Ex | CZ14 | 2.13 | 0.00061285 | 0 | 2.329 | 0.0007919 | -0.017121 | 1.95 | 0.00055126 | 0 | 2.13 | 0.00071232 | -0.0157 |  | LF | Bldg | 2130 | 0.613 | 1950 | 0.551 | 1.09 | 1.29 | -0.0080513 | 2130 | 0.613 | 1950 | 0.551 | 1.09 | 1.29 | -0.00805
LFBldgSCEEPrExCZ15 | Com-Iltg-dWatt-LF_OSbldg | SCE | EPr | Ex | CZ15 | 2.1285 | 0.00061236 | 0 | 2.5754 | 0.00078833 | -0.004197 | 1.95 | 0.0005513 | 0 | 2.3594 | 0.00070942 | -0.00384 |  | LF | Bldg | 2130 | 0.612 | 1950 | 0.551 | 1.21 | 1.29 | -0.0019692 | 2130 | 0.612 | 1950 | 0.551 | 1.21 | 1.29 | -0.00197
LFBldgSCEEPrExCZ16 | Com-Iltg-dWatt-LF_OSbldg | SCE | EPr | Ex | CZ16 | 2.1289 | 1.9883e-05 | 0 | 2.0689 | 1.9883e-05 | -0.035312 | 1.95 | 1.7906e-05 | 0 | 1.89 | 1.7906e-05 | -0.0323 |  | LF | Bldg | 2130 | 0.0199 | 1950 | 0.0179 | 0.969 | 1 | -0.016564 | 2130 | 0.0199 | 1950 | 0.0179 | 0.969 | 1 | -0.0166
LFBldgSCEEPrExIOU | Com-Iltg-dWatt-LF_OSbldg | SCE | EPr | Ex | IOU | 2.1329 | 0.00057473 | 0 | 2.4528 | 0.00074948 | -0.010244 | 1.95 | 0.00051605 | 0 | 2.2407 | 0.00067258 | -0.0093576 |  | LF | Bldg | 2130 | 0.575 | 1950 | 0.516 | 1.15 | 1.3 | -0.0047987 | 2130 | 0.575 | 1950 | 0.516 | 1.15 | 1.3 | -0.0048
LFBldgSCEEPrNewCZ05 | Com-Iltg-dWatt-LF_OSbldg | SCE | EPr | New | CZ05 | 1.95 | 0.000556 | 0 | 2.05 | 0.000724 | -0.0168 | 1.95 | 0.000556 | 0 | 2.05 | 0.000724 | -0.0168 |  | LF | Bldg | 1950 | 0.556 | 1950 | 0.556 | 1.05 | 1.3 | -0.0086154 | 1950 | 0.556 | 1950 | 0.556 | 1.05 | 1.3 | -0.00862
LFBldgSCEEPrNewCZ06 | Com-Iltg-dWatt-LF_OSbldg | SCE | EPr | New | CZ06 | 1.95 | 0.000556 | 0 | 2.02 | 0.000528 | -0.00923 | 1.95 | 0.000556 | 0 | 2.02 | 0.000528 | -0.00923 |  | LF | Bldg | 1950 | 0.556 | 1950 | 0.556 | 1.04 | 0.95 | -0.0047333 | 1950 | 0.556 | 1950 | 0.556 | 1.04 | 0.95 | -0.00473
LFBldgSCEEPrNewCZ08 | Com-Iltg-dWatt-LF_OSbldg | SCE | EPr | New | CZ08 | 1.95 | 0.000556 | 0 | 2.2 | 0.000772 | -0.00931 | 1.95 | 0.000556 | 0 | 2.2 | 0.000772 | -0.00931 |  | LF | Bldg | 1950 | 0.556 | 1950 | 0.556 | 1.13 | 1.39 | -0.0047744 | 1950 | 0.556 | 1950 | 0.556 | 1.13 | 1.39 | -0.00477
LFBldgSCEEPrNewCZ09 | Com-Iltg-dWatt-LF_OSbldg | SCE | EPr | New | CZ09 | 1.95 | 0.000556 | 0 | 2.19 | 0.000801 | -0.0107 | 1.95 | 0.000556 | 0 | 2.19 | 0.000801 | -0.0107 |  | LF | Bldg | 1950 | 0.556 | 1950 | 0.556 | 1.12 | 1.44 | -0.0054872 | 1950 | 0.556 | 1950 | 0.556 | 1.12 | 1.44 | -0.00549
LFBldgSCEEPrNewCZ10 | Com-Iltg-dWatt-LF_OSbldg | SCE | EPr | New | CZ10 | 1.95 | 0.000556 | 0 | 2.21 | 0.000814 | -0.0114 | 1.95 | 0.000556 | 0 | 2.21 | 0.000814 | -0.0114 |  | LF | Bldg | 1950 | 0.556 | 1950 | 0.556 | 1.13 | 1.46 | -0.0058462 | 1950 | 0.556 | 1950 | 0.556 | 1.13 | 1.46 | -0.00585
LFBldgSCEEPrNewCZ13 | Com-Iltg-dWatt-LF_OSbldg | SCE | EPr | New | CZ13 | 1.95 | 1.8e-05 | 0 | 2.17 | 1.8e-05 | -0.0187 | 1.95 | 1.8e-05 | 0 | 2.17 | 1.8e-05 | -0.0187 |  | LF | Bldg | 1950 | 0.018 | 1950 | 0.018 | 1.11 | 1 | -0.0095897 | 1950 | 0.018 | 1950 | 0.018 | 1.11 | 1 | -0.00959
LFBldgSCEEPrNewCZ14 | Com-Iltg-dWatt-LF_OSbldg | SCE | EPr | New | CZ14 | 1.95 | 0.000556 | 0 | 2.17 | 0.000798 | -0.0187 | 1.95 | 0.000556 | 0 | 2.17 | 0.000798 | -0.0187 |  | LF | Bldg | 1950 | 0.556 | 1950 | 0.556 | 1.11 | 1.44 | -0.0095897 | 1950 | 0.556 | 1950 | 0.556 | 1.11 | 1.44 | -0.00959
LFBldgSCEEPrNewCZ15 | Com-Iltg-dWatt-LF_OSbldg | SCE | EPr | New | CZ15 | 1.95 | 0.000556 | 0 | 2.4 | 0.000815 | -0.00495 | 1.95 | 0.000556 | 0 | 2.4 | 0.000815 | -0.00495 |  | LF | Bldg | 1950 | 0.556 | 1950 | 0.556 | 1.23 | 1.47 | -0.0025385 | 1950 | 0.556 | 1950 | 0.556 | 1.23 | 1.47 | -0.00254
LFBldgSCEEPrNewCZ16 | Com-Iltg-dWatt-LF_OSbldg | SCE | EPr | New | CZ16 | 1.95 | 1.8e-05 | 0 | 1.92 | 1.8e-05 | -0.0302 | 1.95 | 1.8e-05 | 0 | 1.92 | 1.8e-05 | -0.0302 |  | LF | Bldg | 1950 | 0.018 | 1950 | 0.018 | 0.985 | 1 | -0.015487 | 1950 | 0.018 | 1950 | 0.018 | 0.985 | 1 | -0.0155
LFBldgSCEEPrNewIOU | Com-Iltg-dWatt-LF_OSbldg | SCE | EPr | New | IOU | 1.95 | 0.00049571 | 0 | 2.1711 | 0.00067901 | -0.012245 | 1.95 | 0.00049571 | 0 | 2.1711 | 0.00067901 | -0.012245 |  | LF | Bldg | 1950 | 0.496 | 1950 | 0.496 | 1.11 | 1.37 | -0.0062797 | 1950 | 0.496 | 1950 | 0.496 | 1.11 | 1.37 | -0.00628
LFBldgSCEERCExCZ05 | Com-Iltg-dWatt-LF_OSbldg | SCE | ERC | Ex | CZ05 | 2.4728 | 0.00069968 | 0 | 2.5925 | 0.00090401 | -0.025225 | 2.19 | 0.0006012 | 0 | 2.3 | 0.00077627 | -0.0223 |  | LF | Bldg | 2470 | 0.7 | 2190 | 0.601 | 1.05 | 1.29 | -0.010183 | 2470 | 0.7 | 2190 | 0.601 | 1.05 | 1.29 | -0.0102
LFBldgSCEERCExCZ06 | Com-Iltg-dWatt-LF_OSbldg | SCE | ERC | Ex | CZ06 | 2.4727 | 0.00069964 | 0 | 2.7616 | 0.00088701 | -0.015254 | 2.19 | 0.0006012 | 0 | 2.44 | 0.00076225 | -0.0135 |  | LF | Bldg | 2470 | 0.7 | 2190 | 0.601 | 1.11 | 1.27 | -0.0061644 | 2470 | 0.7 | 2190 | 0.601 | 1.11 | 1.27 | -0.00616
LFBldgSCEERCExCZ08 | Com-Iltg-dWatt-LF_OSbldg | SCE | ERC | Ex | CZ08 | 2.4725 | 0.0006996 | 0 | 2.7615 | 0.0008979 | -0.013459 | 2.19 | 0.00060121 | 0 | 2.44 | 0.00077126 | -0.0119 |  | LF | Bldg | 2470 | 0.7 | 2190 | 0.601 | 1.11 | 1.28 | -0.0054338 | 2470 | 0.7 | 2190 | 0.601 | 1.11 | 1.28 | -0.00543
LFBldgSCEERCExCZ09 | Com-Iltg-dWatt-LF_OSbldg | SCE | ERC | Ex | CZ09 | 2.472 | 0.00069944 | 0 | 2.7609 | 0.00089769 | -0.01505 | 2.19 | 0.00060122 | 0 | 2.44 | 0.00077128 | -0.0133 |  | LF | Bldg | 2470 | 0.699 | 2190 | 0.601 | 1.11 | 1.28 | -0.0060731 | 2470 | 0.699 | 2190 | 0.601 | 1.11 | 1.28 | -0.00607
LFBldgSCEERCExCZ10 | Com-Iltg-dWatt-LF_OSbldg | SCE | ERC | Ex | CZ10 | 2.4624 | 0.00069637 | 0 | 2.74 | 0.00088879 | -0.015291 | 2.19 | 0.00060149 | 0 | 2.43 | 0.00076761 | -0.0136 |  | LF | Bldg | 2460 | 0.696 | 2190 | 0.601 | 1.11 | 1.28 | -0.00621 | 2460 | 0.696 | 2190 | 0.601 | 1.11 | 1.28 | -0.00621
LFBldgSCEERCExCZ13 | Com-Iltg-dWatt-LF_OSbldg | SCE | ERC | Ex | CZ13 | 2.4611 | 1.9824e-05 | 0 | 2.6692 | 1.9824e-05 | -0.021831 | 2.19 | 1.7113e-05 | 0 | 2.37 | 1.7113e-05 | -0.0194 |  | LF | Bldg | 2460 | 0.0198 | 2190 | 0.0171 | 1.08 | 1 | -0.0088584 | 2460 | 0.0198 | 2190 | 0.0171 | 1.08 | 1 | -0.00886
LFBldgSCEERCExCZ14 | Com-Iltg-dWatt-LF_OSbldg | SCE | ERC | Ex | CZ14 | 2.4648 | 0.00069711 | 0 | 2.6932 | 0.00089569 | -0.020474 | 2.19 | 0.00060142 | 0 | 2.39 | 0.00077253 | -0.0182 |  | LF | Bldg | 2460 | 0.697 | 2190 | 0.601 | 1.09 | 1.28 | -0.0083105 | 2460 | 0.697 | 2190 | 0.601 | 1.09 | 1.28 | -0.00831
LFBldgSCEERCExCZ15 | Com-Iltg-dWatt-LF_OSbldg | SCE | ERC | Ex | CZ15 | 2.4624 | 0.00069636 | 0 | 2.9288 | 0.0009106 | -0.0070891 | 2.19 | 0.00060149 | 0 | 2.6 | 0.00078567 | -0.0063 |  | LF | Bldg | 2460 | 0.696 | 2190 | 0.601 | 1.19 | 1.31 | -0.0028767 | 2460 | 0.696 | 2190 | 0.601 | 1.19 | 1.31 | -0.00288
LFBldgSCEERCExCZ16 | Com-Iltg-dWatt-LF_OSbldg | SCE | ERC | Ex | CZ16 | 2.463 | 1.9842e-05 | 0 | 2.463 | 1.9842e-05 | -0.037642 | 2.19 | 1.7112e-05 | 0 | 2.19 | 1.7112e-05 | -0.0335 |  | LF | Bldg | 2460 | 0.0198 | 2190 | 0.0171 | 1 | 1 | -0.015297 | 2460 | 0.0198 | 2190 | 0.0171 | 1 | 1 | -0.0153
LFBldgSCEERCExIOU | Com-Iltg-dWatt-LF_OSbldg | SCE | ERC | Ex | IOU | 2.4691 | 0.00065396 | 0 | 2.7451 | 0.00083634 | -0.01563 | 2.19 | 0.00056281 | 0 | 2.429 | 0.00071956 | -0.013852 |  | LF | Bldg | 2470 | 0.654 | 2190 | 0.563 | 1.11 | 1.28 | -0.0063251 | 2470 | 0.654 | 2190 | 0.563 | 1.11 | 1.28 | -0.00633
LFBldgSCEERCNewCZ05 | Com-Iltg-dWatt-LF_OSbldg | SCE | ERC | New | CZ05 | 2.19 | 0.000609 | 0 | 2.41 | 0.000785 | -0.0216 | 2.19 | 0.000609 | 0 | 2.41 | 0.000785 | -0.0216 |  | LF | Bldg | 2190 | 0.609 | 2190 | 0.609 | 1.1 | 1.29 | -0.009863 | 2190 | 0.609 | 2190 | 0.609 | 1.1 | 1.29 | -0.00986
LFBldgSCEERCNewCZ06 | Com-Iltg-dWatt-LF_OSbldg | SCE | ERC | New | CZ06 | 2.19 | 0.000609 | 0 | 2.53 | 0.000793 | -0.0139 | 2.19 | 0.000609 | 0 | 2.53 | 0.000793 | -0.0139 |  | LF | Bldg | 2190 | 0.609 | 2190 | 0.609 | 1.16 | 1.3 | -0.006347 | 2190 | 0.609 | 2190 | 0.609 | 1.16 | 1.3 | -0.00635
LFBldgSCEERCNewCZ08 | Com-Iltg-dWatt-LF_OSbldg | SCE | ERC | New | CZ08 | 2.19 | 0.000609 | 0 | 2.58 | 0.000811 | -0.0117 | 2.19 | 0.000609 | 0 | 2.58 | 0.000811 | -0.0117 |  | LF | Bldg | 2190 | 0.609 | 2190 | 0.609 | 1.18 | 1.33 | -0.0053425 | 2190 | 0.609 | 2190 | 0.609 | 1.18 | 1.33 | -0.00534
LFBldgSCEERCNewCZ09 | Com-Iltg-dWatt-LF_OSbldg | SCE | ERC | New | CZ09 | 2.19 | 0.000609 | 0 | 2.58 | 0.000834 | -0.0132 | 2.19 | 0.000609 | 0 | 2.58 | 0.000834 | -0.0132 |  | LF | Bldg | 2190 | 0.609 | 2190 | 0.609 | 1.18 | 1.37 | -0.0060274 | 2190 | 0.609 | 2190 | 0.609 | 1.18 | 1.37 | -0.00603
LFBldgSCEERCNewCZ10 | Com-Iltg-dWatt-LF_OSbldg | SCE | ERC | New | CZ10 | 2.19 | 0.000609 | 0 | 2.59 | 0.00085 | -0.0139 | 2.19 | 0.000609 | 0 | 2.59 | 0.00085 | -0.0139 |  | LF | Bldg | 2190 | 0.609 | 2190 | 0.609 | 1.18 | 1.4 | -0.006347 | 2190 | 0.609 | 2190 | 0.609 | 1.18 | 1.4 | -0.00635
LFBldgSCEERCNewCZ13 | Com-Iltg-dWatt-LF_OSbldg | SCE | ERC | New | CZ13 | 2.19 | 1.73e-05 | 0 | 2.56 | 1.73e-05 | -0.0208 | 2.19 | 1.73e-05 | 0 | 2.56 | 1.73e-05 | -0.0208 |  | LF | Bldg | 2190 | 0.0173 | 2190 | 0.0173 | 1.17 | 1 | -0.0094977 | 2190 | 0.0173 | 2190 | 0.0173 | 1.17 | 1 | -0.0095
LFBldgSCEERCNewCZ14 | Com-Iltg-dWatt-LF_OSbldg | SCE | ERC | New | CZ14 | 2.19 | 0.000609 | 0 | 2.55 | 0.000837 | -0.0201 | 2.19 | 0.000609 | 0 | 2.55 | 0.000837 | -0.0201 |  | LF | Bldg | 2190 | 0.609 | 2190 | 0.609 | 1.16 | 1.37 | -0.0091781 | 2190 | 0.609 | 2190 | 0.609 | 1.16 | 1.37 | -0.00918
LFBldgSCEERCNewCZ15 | Com-Iltg-dWatt-LF_OSbldg | SCE | ERC | New | CZ15 | 2.19 | 0.000609 | 0 | 2.82 | 0.000852 | -0.00687 | 2.19 | 0.000609 | 0 | 2.82 | 0.000852 | -0.00687 |  | LF | Bldg | 2190 | 0.609 | 2190 | 0.609 | 1.29 | 1.4 | -0.003137 | 2190 | 0.609 | 2190 | 0.609 | 1.29 | 1.4 | -0.00314
LFBldgSCEERCNewCZ16 | Com-Iltg-dWatt-LF_OSbldg | SCE | ERC | New | CZ16 | 2.19 | 1.73e-05 | 0 | 2.29 | 1.73e-05 | -0.0367 | 2.19 | 1.73e-05 | 0 | 2.29 | 1.73e-05 | -0.0367 |  | LF | Bldg | 2190 | 0.0173 | 2190 | 0.0173 | 1.05 | 1 | -0.016758 | 2190 | 0.0173 | 2190 | 0.0173 | 1.05 | 1 | -0.0168
LFBldgSCEERCNewIOU | Com-Iltg-dWatt-LF_OSbldg | SCE | ERC | New | IOU | 2.19 | 0.00054269 | 0 | 2.5693 | 0.00073877 | -0.01501 | 2.19 | 0.00054269 | 0 | 2.5693 | 0.00073877 | -0.01501 |  | LF | Bldg | 2190 | 0.543 | 2190 | 0.543 | 1.17 | 1.36 | -0.006854 | 2190 | 0.543 | 2190 | 0.543 | 1.17 | 1.36 | -0.00685
LFBldgSCEESeExCZ05 | Com-Iltg-dWatt-LF_OSbldg | SCE | ESe | Ex | CZ05 | 2.2758 | 0.00070758 | 0 | 2.4253 | 0.00088126 | -0.025953 | 2.11 | 0.00064713 | 0 | 2.24 | 0.00080715 | -0.0241 |  | LF | Bldg | 2280 | 0.708 | 2110 | 0.647 | 1.06 | 1.25 | -0.011422 | 2280 | 0.708 | 2110 | 0.647 | 1.06 | 1.25 | -0.0114
LFBldgSCEESeExCZ06 | Com-Iltg-dWatt-LF_OSbldg | SCE | ESe | Ex | CZ06 | 2.2757 | 0.00070755 | 0 | 2.6149 | 0.00091812 | -0.013375 | 2.11 | 0.00064713 | 0 | 2.42 | 0.00084015 | -0.0124 |  | LF | Bldg | 2280 | 0.708 | 2110 | 0.647 | 1.15 | 1.3 | -0.0058768 | 2280 | 0.708 | 2110 | 0.647 | 1.15 | 1.3 | -0.00588
LFBldgSCEESeExCZ08 | Com-Iltg-dWatt-LF_OSbldg | SCE | ESe | Ex | CZ08 | 2.2756 | 0.00070753 | 0 | 2.6348 | 0.00091311 | -0.011677 | 2.11 | 0.00064713 | 0 | 2.44 | 0.00083616 | -0.0108 |  | LF | Bldg | 2280 | 0.708 | 2110 | 0.647 | 1.16 | 1.29 | -0.0051185 | 2280 | 0.708 | 2110 | 0.647 | 1.16 | 1.29 | -0.00512
LFBldgSCEESeExCZ09 | Com-Iltg-dWatt-LF_OSbldg | SCE | ESe | Ex | CZ09 | 2.2753 | 0.00070743 | 0 | 2.6145 | 0.00091896 | -0.013472 | 2.11 | 0.00064714 | 0 | 2.42 | 0.00084117 | -0.0125 |  | LF | Bldg | 2280 | 0.707 | 2110 | 0.647 | 1.15 | 1.3 | -0.0059242 | 2280 | 0.707 | 2110 | 0.647 | 1.15 | 1.3 | -0.00592
LFBldgSCEESeExCZ10 | Com-Iltg-dWatt-LF_OSbldg | SCE | ESe | Ex | CZ10 | 2.2697 | 0.00070555 | 0 | 2.5385 | 0.00089864 | -0.014433 | 2.11 | 0.0006473 | 0 | 2.36 | 0.00082536 | -0.0134 |  | LF | Bldg | 2270 | 0.706 | 2110 | 0.647 | 1.12 | 1.28 | -0.0063507 | 2270 | 0.706 | 2110 | 0.647 | 1.12 | 1.28 | -0.00635
LFBldgSCEESeExCZ13 | Com-Iltg-dWatt-LF_OSbldg | SCE | ESe | Ex | CZ13 | 2.2689 | 1.9896e-05 | 0 | 2.4976 | 1.9896e-05 | -0.022289 | 2.11 | 1.8307e-05 | 0 | 2.32 | 1.8307e-05 | -0.0207 |  | LF | Bldg | 2270 | 0.0199 | 2110 | 0.0183 | 1.1 | 1 | -0.0098104 | 2270 | 0.0199 | 2110 | 0.0183 | 1.1 | 1 | -0.00981
LFBldgSCEESeExCZ14 | Com-Iltg-dWatt-LF_OSbldg | SCE | ESe | Ex | CZ14 | 2.2711 | 0.00070601 | 0 | 2.48 | 0.00087632 | -0.022611 | 2.11 | 0.00064726 | 0 | 2.3 | 0.00080431 | -0.021 |  | LF | Bldg | 2270 | 0.706 | 2110 | 0.647 | 1.09 | 1.24 | -0.0099526 | 2270 | 0.706 | 2110 | 0.647 | 1.09 | 1.24 | -0.00995
LFBldgSCEESeExCZ15 | Com-Iltg-dWatt-LF_OSbldg | SCE | ESe | Ex | CZ15 | 2.2697 | 0.00070554 | 0 | 2.7573 | 0.0008957 | -0.0064603 | 2.11 | 0.0006473 | 0 | 2.56 | 0.00082242 | -0.006 |  | LF | Bldg | 2270 | 0.706 | 2110 | 0.647 | 1.21 | 1.27 | -0.0028436 | 2270 | 0.706 | 2110 | 0.647 | 1.21 | 1.27 | -0.00284
LFBldgSCEESeExCZ16 | Com-Iltg-dWatt-LF_OSbldg | SCE | ESe | Ex | CZ16 | 2.27 | 1.9906e-05 | 0 | 2.22 | 1.9906e-05 | -0.038924 | 2.11 | 1.8306e-05 | 0 | 2.06 | 1.8306e-05 | -0.0361 |  | LF | Bldg | 2270 | 0.0199 | 2110 | 0.0183 | 0.976 | 1 | -0.017109 | 2270 | 0.0199 | 2110 | 0.0183 | 0.976 | 1 | -0.0171
LFBldgSCEESeExIOU | Com-Iltg-dWatt-LF_OSbldg | SCE | ESe | Ex | IOU | 2.2736 | 0.0006617 | 0 | 2.5862 | 0.00085091 | -0.014451 | 2.11 | 0.00060576 | 0 | 2.397 | 0.00077967 | -0.013399 |  | LF | Bldg | 2270 | 0.662 | 2110 | 0.606 | 1.14 | 1.29 | -0.0063503 | 2270 | 0.662 | 2110 | 0.606 | 1.14 | 1.29 | -0.00635
LFBldgSCEESeNewCZ05 | Com-Iltg-dWatt-LF_OSbldg | SCE | ESe | New | CZ05 | 2.11 | 0.000652 | 0 | 2.22 | 0.000832 | -0.0213 | 2.11 | 0.000652 | 0 | 2.22 | 0.000832 | -0.0213 |  | LF | Bldg | 2110 | 0.652 | 2110 | 0.652 | 1.05 | 1.28 | -0.010095 | 2110 | 0.652 | 2110 | 0.652 | 1.05 | 1.28 | -0.0101
LFBldgSCEESeNewCZ06 | Com-Iltg-dWatt-LF_OSbldg | SCE | ESe | New | CZ06 | 2.11 | 0.000652 | 0 | 2.35 | 0.000872 | -0.0157 | 2.11 | 0.000652 | 0 | 2.35 | 0.000872 | -0.0157 |  | LF | Bldg | 2110 | 0.652 | 2110 | 0.652 | 1.11 | 1.34 | -0.0074408 | 2110 | 0.652 | 2110 | 0.652 | 1.11 | 1.34 | -0.00744
LFBldgSCEESeNewCZ08 | Com-Iltg-dWatt-LF_OSbldg | SCE | ESe | New | CZ08 | 2.11 | 0.000652 | 0 | 2.38 | 0.000886 | -0.0119 | 2.11 | 0.000652 | 0 | 2.38 | 0.000886 | -0.0119 |  | LF | Bldg | 2110 | 0.652 | 2110 | 0.652 | 1.13 | 1.36 | -0.0056398 | 2110 | 0.652 | 2110 | 0.652 | 1.13 | 1.36 | -0.00564
LFBldgSCEESeNewCZ09 | Com-Iltg-dWatt-LF_OSbldg | SCE | ESe | New | CZ09 | 2.11 | 0.000652 | 0 | 2.38 | 0.000919 | -0.014 | 2.11 | 0.000652 | 0 | 2.38 | 0.000919 | -0.014 |  | LF | Bldg | 2110 | 0.652 | 2110 | 0.652 | 1.13 | 1.41 | -0.0066351 | 2110 | 0.652 | 2110 | 0.652 | 1.13 | 1.41 | -0.00664
LFBldgSCEESeNewCZ10 | Com-Iltg-dWatt-LF_OSbldg | SCE | ESe | New | CZ10 | 2.11 | 0.000652 | 0 | 2.4 | 0.000932 | -0.0152 | 2.11 | 0.000652 | 0 | 2.4 | 0.000932 | -0.0152 |  | LF | Bldg | 2110 | 0.652 | 2110 | 0.652 | 1.14 | 1.43 | -0.0072038 | 2110 | 0.652 | 2110 | 0.652 | 1.14 | 1.43 | -0.0072
LFBldgSCEESeNewCZ13 | Com-Iltg-dWatt-LF_OSbldg | SCE | ESe | New | CZ13 | 2.11 | 1.84e-05 | 0 | 2.38 | 1.84e-05 | -0.0226 | 2.11 | 1.84e-05 | 0 | 2.38 | 1.84e-05 | -0.0226 |  | LF | Bldg | 2110 | 0.0184 | 2110 | 0.0184 | 1.13 | 1 | -0.010711 | 2110 | 0.0184 | 2110 | 0.0184 | 1.13 | 1 | -0.0107
LFBldgSCEESeNewCZ14 | Com-Iltg-dWatt-LF_OSbldg | SCE | ESe | New | CZ14 | 2.11 | 0.000652 | 0 | 2.36 | 0.00091 | -0.0228 | 2.11 | 0.000652 | 0 | 2.36 | 0.00091 | -0.0228 |  | LF | Bldg | 2110 | 0.652 | 2110 | 0.652 | 1.12 | 1.4 | -0.010806 | 2110 | 0.652 | 2110 | 0.652 | 1.12 | 1.4 | -0.0108
LFBldgSCEESeNewCZ15 | Com-Iltg-dWatt-LF_OSbldg | SCE | ESe | New | CZ15 | 2.11 | 0.000652 | 0 | 2.66 | 0.000925 | -0.00661 | 2.11 | 0.000652 | 0 | 2.66 | 0.000925 | -0.00661 |  | LF | Bldg | 2110 | 0.652 | 2110 | 0.652 | 1.26 | 1.42 | -0.0031327 | 2110 | 0.652 | 2110 | 0.652 | 1.26 | 1.42 | -0.00313
LFBldgSCEESeNewCZ16 | Com-Iltg-dWatt-LF_OSbldg | SCE | ESe | New | CZ16 | 2.11 | 1.84e-05 | 0 | 2.11 | 1.84e-05 | -0.0296 | 2.11 | 1.84e-05 | 0 | 2.11 | 1.84e-05 | -0.0296 |  | LF | Bldg | 2110 | 0.0184 | 2110 | 0.0184 | 1 | 1 | -0.014028 | 2110 | 0.0184 | 2110 | 0.0184 | 1 | 1 | -0.014
LFBldgSCEESeNewIOU | Com-Iltg-dWatt-LF_OSbldg | SCE | ESe | New | IOU | 2.11 | 0.000581 | 0 | 2.3792 | 0.00080925 | -0.015842 | 2.11 | 0.000581 | 0 | 2.3792 | 0.00080925 | -0.015842 |  | LF | Bldg | 2110 | 0.581 | 2110 | 0.581 | 1.13 | 1.39 | -0.0075083 | 2110 | 0.581 | 2110 | 0.581 | 1.13 | 1.39 | -0.00751
LFBldgSCEEUnExCZ05 | Com-Iltg-dWatt-LF_OSbldg | SCE | EUn | Ex | CZ05 | 2.3426 | 0.00071588 | 0 | 2.6116 | 0.00087098 | -0.016345 | 2.2 | 0.00063985 | 0 | 2.45 | 0.0007788 | -0.0153 |  | LF | Bldg | 2340 | 0.716 | 2200 | 0.64 | 1.11 | 1.22 | -0.0069545 | 2340 | 0.716 | 2200 | 0.64 | 1.11 | 1.22 | -0.00695
LFBldgSCEEUnExCZ06 | Com-Iltg-dWatt-LF_OSbldg | SCE | EUn | Ex | CZ06 | 2.3427 | 0.00071597 | 0 | 2.7213 | 0.00090686 | -0.009659 | 2.2 | 0.00063985 | 0 | 2.5595 | 0.00081076 | -0.009069 |  | LF | Bldg | 2340 | 0.716 | 2200 | 0.64 | 1.16 | 1.27 | -0.0041223 | 2340 | 0.716 | 2200 | 0.64 | 1.16 | 1.27 | -0.00412
LFBldgSCEEUnExCZ08 | Com-Iltg-dWatt-LF_OSbldg | SCE | EUn | Ex | CZ08 | 2.3429 | 0.00071609 | 0 | 2.7316 | 0.00090903 | -0.0093606 | 2.2 | 0.0006399 | 0 | 2.5697 | 0.00081284 | -0.0087797 |  | LF | Bldg | 2340 | 0.716 | 2200 | 0.64 | 1.17 | 1.27 | -0.0039908 | 2340 | 0.716 | 2200 | 0.64 | 1.17 | 1.27 | -0.00399
LFBldgSCEEUnExCZ09 | Com-Iltg-dWatt-LF_OSbldg | SCE | EUn | Ex | CZ09 | 2.3418 | 0.00071544 | 0 | 2.7201 | 0.00092307 | -0.01036 | 2.2 | 0.00063984 | 0 | 2.5594 | 0.00082478 | -0.0096794 |  | LF | Bldg | 2340 | 0.715 | 2200 | 0.64 | 1.16 | 1.29 | -0.0043997 | 2340 | 0.715 | 2200 | 0.64 | 1.16 | 1.29 | -0.0044
LFBldgSCEEUnExCZ10 | Com-Iltg-dWatt-LF_OSbldg | SCE | EUn | Ex | CZ10 | 2.3356 | 0.000712 | 0 | 2.6927 | 0.00091169 | -0.0092603 | 2.2 | 0.00063971 | 0 | 2.53 | 0.00081862 | -0.0087181 |  | LF | Bldg | 2340 | 0.712 | 2200 | 0.64 | 1.15 | 1.28 | -0.0039628 | 2340 | 0.712 | 2200 | 0.64 | 1.15 | 1.28 | -0.00396
LFBldgSCEEUnExCZ13 | Com-Iltg-dWatt-LF_OSbldg | SCE | EUn | Ex | CZ13 | 2.3316 | 0.00043273 | 0 | 2.6391 | 0.00054513 | -0.012189 | 2.2 | 0.00038975 | 0 | 2.49 | 0.00049163 | -0.011488 |  | LF | Bldg | 2330 | 0.433 | 2200 | 0.39 | 1.13 | 1.26 | -0.0052217 | 2330 | 0.433 | 2200 | 0.39 | 1.13 | 1.26 | -0.00522
LFBldgSCEEUnExCZ14 | Com-Iltg-dWatt-LF_OSbldg | SCE | EUn | Ex | CZ14 | 2.3363 | 0.0007124 | 0 | 2.6435 | 0.00090629 | -0.013518 | 2.2 | 0.00063973 | 0 | 2.4891 | 0.00081363 | -0.0127 |  | LF | Bldg | 2340 | 0.712 | 2200 | 0.64 | 1.13 | 1.27 | -0.0057727 | 2340 | 0.712 | 2200 | 0.64 | 1.13 | 1.27 | -0.00577
LFBldgSCEEUnExCZ15 | Com-Iltg-dWatt-LF_OSbldg | SCE | EUn | Ex | CZ15 | 2.3356 | 0.000712 | 0 | 2.8117 | 0.00091469 | -0.0049292 | 2.2 | 0.00063971 | 0 | 2.649 | 0.00082161 | -0.00464 |  | LF | Bldg | 2340 | 0.712 | 2200 | 0.64 | 1.2 | 1.28 | -0.0021091 | 2340 | 0.712 | 2200 | 0.64 | 1.2 | 1.28 | -0.00211
LFBldgSCEEUnExCZ16 | Com-Iltg-dWatt-LF_OSbldg | SCE | EUn | Ex | CZ16 | 2.3354 | 0.00043404 | 0 | 2.4735 | 0.00052507 | -0.026625 | 2.2 | 0.00038981 | 0 | 2.329 | 0.00047181 | -0.02509 |  | LF | Bldg | 2340 | 0.434 | 2200 | 0.39 | 1.06 | 1.21 | -0.011405 | 2340 | 0.434 | 2200 | 0.39 | 1.06 | 1.21 | -0.0114
LFBldgSCEEUnExIOU | Com-Iltg-dWatt-LF_OSbldg | SCE | EUn | Ex | IOU | 2.3406 | 0.00068828 | 0 | 2.7019 | 0.00087382 | -0.010854 | 2.2 | 0.00061594 | 0 | 2.5419 | 0.00078217 | -0.010194 |  | LF | Bldg | 2340 | 0.688 | 2200 | 0.616 | 1.16 | 1.27 | -0.0046336 | 2340 | 0.688 | 2200 | 0.616 | 1.16 | 1.27 | -0.00463
LFBldgSCEEUnNewCZ05 | Com-Iltg-dWatt-LF_OSbldg | SCE | EUn | New | CZ05 | 2.2 | 0.000637 | 0 | 2.4 | 0.000792 | -0.0123 | 2.2 | 0.000637 | 0 | 2.4 | 0.000792 | -0.0123 |  | LF | Bldg | 2200 | 0.637 | 2200 | 0.637 | 1.09 | 1.24 | -0.0055909 | 2200 | 0.637 | 2200 | 0.637 | 1.09 | 1.24 | -0.00559
LFBldgSCEEUnNewCZ06 | Com-Iltg-dWatt-LF_OSbldg | SCE | EUn | New | CZ06 | 2.2 | 0.000637 | 0 | 2.54 | 0.000813 | -0.00551 | 2.2 | 0.000637 | 0 | 2.54 | 0.000813 | -0.00551 |  | LF | Bldg | 2200 | 0.637 | 2200 | 0.637 | 1.15 | 1.28 | -0.0025045 | 2200 | 0.637 | 2200 | 0.637 | 1.15 | 1.28 | -0.0025
LFBldgSCEEUnNewCZ08 | Com-Iltg-dWatt-LF_OSbldg | SCE | EUn | New | CZ08 | 2.2 | 0.000637 | 0 | 2.57 | 0.000826 | -0.00492 | 2.2 | 0.000637 | 0 | 2.57 | 0.000826 | -0.00492 |  | LF | Bldg | 2200 | 0.637 | 2200 | 0.637 | 1.17 | 1.3 | -0.0022364 | 2200 | 0.637 | 2200 | 0.637 | 1.17 | 1.3 | -0.00224
LFBldgSCEEUnNewCZ09 | Com-Iltg-dWatt-LF_OSbldg | SCE | EUn | New | CZ09 | 2.2 | 0.000637 | 0 | 2.57 | 0.000852 | -0.00567 | 2.2 | 0.000637 | 0 | 2.57 | 0.000852 | -0.00567 |  | LF | Bldg | 2200 | 0.637 | 2200 | 0.637 | 1.17 | 1.34 | -0.0025773 | 2200 | 0.637 | 2200 | 0.637 | 1.17 | 1.34 | -0.00258
LFBldgSCEEUnNewCZ10 | Com-Iltg-dWatt-LF_OSbldg | SCE | EUn | New | CZ10 | 2.2 | 0.000637 | 0 | 2.58 | 0.000859 | -0.00611 | 2.2 | 0.000637 | 0 | 2.58 | 0.000859 | -0.00611 |  | LF | Bldg | 2200 | 0.637 | 2200 | 0.637 | 1.17 | 1.35 | -0.0027773 | 2200 | 0.637 | 2200 | 0.637 | 1.17 | 1.35 | -0.00278
LFBldgSCEEUnNewCZ13 | Com-Iltg-dWatt-LF_OSbldg | SCE | EUn | New | CZ13 | 2.2 | 0.000388 | 0 | 2.55 | 0.000538 | -0.0107 | 2.2 | 0.000388 | 0 | 2.55 | 0.000538 | -0.0107 |  | LF | Bldg | 2200 | 0.388 | 2200 | 0.388 | 1.16 | 1.39 | -0.0048636 | 2200 | 0.388 | 2200 | 0.388 | 1.16 | 1.39 | -0.00486
LFBldgSCEEUnNewCZ14 | Com-Iltg-dWatt-LF_OSbldg | SCE | EUn | New | CZ14 | 2.2 | 0.000637 | 0 | 2.52 | 0.000827 | -0.0115 | 2.2 | 0.000637 | 0 | 2.52 | 0.000827 | -0.0115 |  | LF | Bldg | 2200 | 0.637 | 2200 | 0.637 | 1.15 | 1.3 | -0.0052273 | 2200 | 0.637 | 2200 | 0.637 | 1.15 | 1.3 | -0.00523
LFBldgSCEEUnNewCZ15 | Com-Iltg-dWatt-LF_OSbldg | SCE | EUn | New | CZ15 | 2.2 | 0.000637 | 0 | 2.74 | 0.000868 | -0.00237 | 2.2 | 0.000637 | 0 | 2.74 | 0.000868 | -0.00237 |  | LF | Bldg | 2200 | 0.637 | 2200 | 0.637 | 1.25 | 1.36 | -0.0010773 | 2200 | 0.637 | 2200 | 0.637 | 1.25 | 1.36 | -0.00108
LFBldgSCEEUnNewCZ16 | Com-Iltg-dWatt-LF_OSbldg | SCE | EUn | New | CZ16 | 2.2 | 0.000388 | 0 | 2.35 | 0.000508 | -0.0239 | 2.2 | 0.000388 | 0 | 2.35 | 0.000508 | -0.0239 |  | LF | Bldg | 2200 | 0.388 | 2200 | 0.388 | 1.07 | 1.31 | -0.010864 | 2200 | 0.388 | 2200 | 0.388 | 1.07 | 1.31 | -0.0109
LFBldgSCEEUnNewIOU | Com-Iltg-dWatt-LF_OSbldg | SCE | EUn | New | IOU | 2.2 | 0.00059626 | 0 | 2.5455 | 0.00078301 | -0.00804 | 2.2 | 0.00059626 | 0 | 2.5455 | 0.00078301 | -0.00804 |  | LF | Bldg | 2200 | 0.596 | 2200 | 0.596 | 1.16 | 1.31 | -0.0036546 | 2200 | 0.596 | 2200 | 0.596 | 1.16 | 1.31 | -0.00365
LFBldgSCEGroExCZ05 | Com-Iltg-dWatt-LF_OSbldg | SCE | Gro | Ex | CZ05 | 4.9137 | 0.0006907 | 0 | 4.7344 | 0.00085293 | -0.083478 | 4.85 | 0.000682 | 0 | 4.68 | 0.00084285 | -0.082485 |  | LF | Bldg | 4910 | 0.691 | 4850 | 0.682 | 0.965 | 1.24 | -0.017007 | 4910 | 0.691 | 4850 | 0.682 | 0.965 | 1.24 | -0.017
LFBldgSCEGroExCZ06 | Com-Iltg-dWatt-LF_OSbldg | SCE | Gro | Ex | CZ06 | 4.9137 | 0.00069069 | 0 | 5.0658 | 0.00086386 | -0.06336 | 4.85 | 0.000682 | 0 | 5.01 | 0.000853 | -0.0626 |  | LF | Bldg | 4910 | 0.691 | 4850 | 0.682 | 1.03 | 1.25 | -0.012907 | 4910 | 0.691 | 4850 | 0.682 | 1.03 | 1.25 | -0.0129
LFBldgSCEGroExCZ08 | Com-Iltg-dWatt-LF_OSbldg | SCE | Gro | Ex | CZ08 | 4.9137 | 0.00069069 | 0 | 5.1758 | 0.00088286 | -0.056952 | 4.85 | 0.000682 | 0 | 5.1185 | 0.000872 | -0.0563 |  | LF | Bldg | 4910 | 0.691 | 4850 | 0.682 | 1.06 | 1.28 | -0.011608 | 4910 | 0.691 | 4850 | 0.682 | 1.06 | 1.28 | -0.0116
LFBldgSCEGroExCZ09 | Com-Iltg-dWatt-LF_OSbldg | SCE | Gro | Ex | CZ09 | 4.9135 | 0.00069067 | 0 | 5.1936 | 0.00089384 | -0.05595 | 4.85 | 0.000682 | 0 | 5.13 | 0.000883 | -0.0553 |  | LF | Bldg | 4910 | 0.691 | 4850 | 0.682 | 1.06 | 1.29 | -0.011402 | 4910 | 0.691 | 4850 | 0.682 | 1.06 | 1.29 | -0.0114
LFBldgSCEGroExCZ10 | Com-Iltg-dWatt-LF_OSbldg | SCE | Gro | Ex | CZ10 | 4.9033 | 0.0006891 | 0 | 5.1733 | 0.00090988 | -0.054425 | 4.85 | 0.000682 | 0 | 5.12 | 0.000901 | -0.053893 |  | LF | Bldg | 4900 | 0.689 | 4850 | 0.682 | 1.06 | 1.32 | -0.011112 | 4900 | 0.689 | 4850 | 0.682 | 1.06 | 1.32 | -0.0111
LFBldgSCEGroExCZ13 | Com-Iltg-dWatt-LF_OSbldg | SCE | Gro | Ex | CZ13 | 4.9041 | 0.00068922 | 0 | 5.1741 | 0.00089602 | -0.055841 | 4.85 | 0.000682 | 0 | 5.12 | 0.000887 | -0.0553 |  | LF | Bldg | 4900 | 0.689 | 4850 | 0.682 | 1.06 | 1.3 | -0.011402 | 4900 | 0.689 | 4850 | 0.682 | 1.06 | 1.3 | -0.0114
LFBldgSCEGroExCZ14 | Com-Iltg-dWatt-LF_OSbldg | SCE | Gro | Ex | CZ14 | 4.9038 | 0.00068917 | 0 | 5.1441 | 0.00092289 | -0.057831 | 4.85 | 0.000682 | 0 | 5.0993 | 0.00091393 | -0.057293 |  | LF | Bldg | 4900 | 0.689 | 4850 | 0.682 | 1.05 | 1.34 | -0.011813 | 4900 | 0.689 | 4850 | 0.682 | 1.05 | 1.34 | -0.0118
LFBldgSCEGroExCZ15 | Com-Iltg-dWatt-LF_OSbldg | SCE | Gro | Ex | CZ15 | 4.9033 | 0.0006891 | 0 | 5.5333 | 0.00090488 | -0.030566 | 4.85 | 0.000682 | 0 | 5.48 | 0.000896 | -0.0303 |  | LF | Bldg | 4900 | 0.689 | 4850 | 0.682 | 1.13 | 1.31 | -0.0062474 | 4900 | 0.689 | 4850 | 0.682 | 1.13 | 1.31 | -0.00625
LFBldgSCEGroExCZ16 | Com-Iltg-dWatt-LF_OSbldg | SCE | Gro | Ex | CZ16 | 4.9038 | 0.00068918 | 0 | 4.7049 | 0.00085707 | -0.077918 | 4.85 | 0.000682 | 0 | 4.66 | 0.000849 | -0.0772 |  | LF | Bldg | 4900 | 0.689 | 4850 | 0.682 | 0.961 | 1.24 | -0.015918 | 4900 | 0.689 | 4850 | 0.682 | 0.961 | 1.24 | -0.0159
LFBldgSCEGroExIOU | Com-Iltg-dWatt-LF_OSbldg | SCE | Gro | Ex | IOU | 4.9101 | 0.00069014 | 0 | 5.1526 | 0.00088877 | -0.057346 | 4.85 | 0.000682 | 0 | 5.0968 | 0.00087861 | -0.056716 |  | LF | Bldg | 4910 | 0.69 | 4850 | 0.682 | 1.05 | 1.29 | -0.011694 | 4910 | 0.69 | 4850 | 0.682 | 1.05 | 1.29 | -0.0117
LFBldgSCEGroNewCZ05 | Com-Iltg-dWatt-LF_OSbldg | SCE | Gro | New | CZ05 | 4.85 | 0.000682 | 0 | 4.83 | 0.000855 | -0.0757 | 4.85 | 0.000682 | 0 | 4.83 | 0.000855 | -0.0757 |  | LF | Bldg | 4850 | 0.682 | 4850 | 0.682 | 0.996 | 1.25 | -0.015608 | 4850 | 0.682 | 4850 | 0.682 | 0.996 | 1.25 | -0.0156
LFBldgSCEGroNewCZ06 | Com-Iltg-dWatt-LF_OSbldg | SCE | Gro | New | CZ06 | 4.85 | 0.000682 | 0 | 5.21 | 0.000856 | -0.0476 | 4.85 | 0.000682 | 0 | 5.21 | 0.000856 | -0.0476 |  | LF | Bldg | 4850 | 0.682 | 4850 | 0.682 | 1.07 | 1.26 | -0.0098144 | 4850 | 0.682 | 4850 | 0.682 | 1.07 | 1.26 | -0.00981
LFBldgSCEGroNewCZ08 | Com-Iltg-dWatt-LF_OSbldg | SCE | Gro | New | CZ08 | 4.85 | 0.000682 | 0 | 5.26 | 0.000877 | -0.042 | 4.85 | 0.000682 | 0 | 5.26 | 0.000877 | -0.042 |  | LF | Bldg | 4850 | 0.682 | 4850 | 0.682 | 1.08 | 1.29 | -0.0086598 | 4850 | 0.682 | 4850 | 0.682 | 1.08 | 1.29 | -0.00866
LFBldgSCEGroNewCZ09 | Com-Iltg-dWatt-LF_OSbldg | SCE | Gro | New | CZ09 | 4.85 | 0.000682 | 0 | 5.25 | 0.000934 | -0.0449 | 4.85 | 0.000682 | 0 | 5.25 | 0.000934 | -0.0449 |  | LF | Bldg | 4850 | 0.682 | 4850 | 0.682 | 1.08 | 1.37 | -0.0092577 | 4850 | 0.682 | 4850 | 0.682 | 1.08 | 1.37 | -0.00926
LFBldgSCEGroNewCZ10 | Com-Iltg-dWatt-LF_OSbldg | SCE | Gro | New | CZ10 | 4.85 | 0.000682 | 0 | 5.29 | 0.000947 | -0.0448 | 4.85 | 0.000682 | 0 | 5.29 | 0.000947 | -0.0448 |  | LF | Bldg | 4850 | 0.682 | 4850 | 0.682 | 1.09 | 1.39 | -0.0092371 | 4850 | 0.682 | 4850 | 0.682 | 1.09 | 1.39 | -0.00924
LFBldgSCEGroNewCZ13 | Com-Iltg-dWatt-LF_OSbldg | SCE | Gro | New | CZ13 | 4.85 | 0.000682 | 0 | 5.29 | 0.000927 | -0.0519 | 4.85 | 0.000682 | 0 | 5.29 | 0.000927 | -0.0519 |  | LF | Bldg | 4850 | 0.682 | 4850 | 0.682 | 1.09 | 1.36 | -0.010701 | 4850 | 0.682 | 4850 | 0.682 | 1.09 | 1.36 | -0.0107
LFBldgSCEGroNewCZ14 | Com-Iltg-dWatt-LF_OSbldg | SCE | Gro | New | CZ14 | 4.85 | 0.000682 | 0 | 5.29 | 0.000942 | -0.0539 | 4.85 | 0.000682 | 0 | 5.29 | 0.000942 | -0.0539 |  | LF | Bldg | 4850 | 0.682 | 4850 | 0.682 | 1.09 | 1.38 | -0.011113 | 4850 | 0.682 | 4850 | 0.682 | 1.09 | 1.38 | -0.0111
LFBldgSCEGroNewCZ15 | Com-Iltg-dWatt-LF_OSbldg | SCE | Gro | New | CZ15 | 4.85 | 0.000682 | 0 | 5.71 | 0.000953 | -0.0248 | 4.85 | 0.000682 | 0 | 5.71 | 0.000953 | -0.0248 |  | LF | Bldg | 4850 | 0.682 | 4850 | 0.682 | 1.18 | 1.4 | -0.0051134 | 4850 | 0.682 | 4850 | 0.682 | 1.18 | 1.4 | -0.00511
LFBldgSCEGroNewCZ16 | Com-Iltg-dWatt-LF_OSbldg | SCE | Gro | New | CZ16 | 4.85 | 0.000682 | 0 | 4.81 | 0.000871 | -0.0718 | 4.85 | 0.000682 | 0 | 4.81 | 0.000871 | -0.0718 |  | LF | Bldg | 4850 | 0.682 | 4850 | 0.682 | 0.992 | 1.28 | -0.014804 | 4850 | 0.682 | 4850 | 0.682 | 0.992 | 1.28 | -0.0148
LFBldgSCEGroNewIOU | Com-Iltg-dWatt-LF_OSbldg | SCE | Gro | New | IOU | 4.85 | 0.000682 | 0 | 5.2699 | 0.00091161 | -0.045469 | 4.85 | 0.000682 | 0 | 5.2699 | 0.00091161 | -0.045469 |  | LF | Bldg | 4850 | 0.682 | 4850 | 0.682 | 1.09 | 1.34 | -0.0093749 | 4850 | 0.682 | 4850 | 0.682 | 1.09 | 1.34 | -0.00937
LFBldgSCEHspExCZ05 | Com-Iltg-dWatt-LF_OSbldg | SCE | Hsp | Ex | CZ05 | 5.2654 | 0.00082839 | 0 | 5.9154 | 0.0010196 | -0.036158 | 5.24 | 0.00082204 | 0 | 5.89 | 0.00101 | -0.036 |  | LF | Bldg | 5270 | 0.828 | 5240 | 0.822 | 1.12 | 1.23 | -0.0068702 | 5270 | 0.828 | 5240 | 0.822 | 1.12 | 1.23 | -0.00687
LFBldgSCEHspExCZ06 | Com-Iltg-dWatt-LF_OSbldg | SCE | Hsp | Ex | CZ06 | 5.2652 | 0.00082835 | 0 | 6.0982 | 0.001043 | -0.026726 | 5.24 | 0.00082204 | 0 | 6.07 | 0.00104 | -0.0266 |  | LF | Bldg | 5270 | 0.828 | 5240 | 0.822 | 1.16 | 1.27 | -0.0050763 | 5270 | 0.828 | 5240 | 0.822 | 1.16 | 1.27 | -0.00508
LFBldgSCEHspExCZ08 | Com-Iltg-dWatt-LF_OSbldg | SCE | Hsp | Ex | CZ08 | 5.2652 | 0.00082834 | 0 | 6.1348 | 0.001043 | -0.026226 | 5.24 | 0.00082204 | 0 | 6.1 | 0.00104 | -0.0261 |  | LF | Bldg | 5270 | 0.828 | 5240 | 0.822 | 1.16 | 1.27 | -0.0049809 | 5270 | 0.828 | 5240 | 0.822 | 1.16 | 1.27 | -0.00498
LFBldgSCEHspExCZ09 | Com-Iltg-dWatt-LF_OSbldg | SCE | Hsp | Ex | CZ09 | 5.2642 | 0.0008281 | 0 | 6.1637 | 0.0010726 | -0.026621 | 5.24 | 0.00082205 | 0 | 6.1326 | 0.00107 | -0.0265 |  | LF | Bldg | 5260 | 0.828 | 5240 | 0.822 | 1.17 | 1.3 | -0.0050573 | 5260 | 0.828 | 5240 | 0.822 | 1.17 | 1.3 | -0.00506
LFBldgSCEHspExCZ10 | Com-Iltg-dWatt-LF_OSbldg | SCE | Hsp | Ex | CZ10 | 5.2595 | 0.00082695 | 0 | 6 | 0.0010597 | -0.028597 | 5.24 | 0.00082208 | 0 | 5.98 | 0.00105 | -0.0285 |  | LF | Bldg | 5260 | 0.827 | 5240 | 0.822 | 1.14 | 1.28 | -0.0054389 | 5260 | 0.827 | 5240 | 0.822 | 1.14 | 1.28 | -0.00544
LFBldgSCEHspExCZ13 | Com-Iltg-dWatt-LF_OSbldg | SCE | Hsp | Ex | CZ13 | 5.2596 | 0.00082696 | 0 | 5.97 | 0.0010593 | -0.032398 | 5.24 | 0.00082206 | 0 | 5.95 | 0.00105 | -0.0323 |  | LF | Bldg | 5260 | 0.827 | 5240 | 0.822 | 1.14 | 1.28 | -0.0061641 | 5260 | 0.827 | 5240 | 0.822 | 1.14 | 1.28 | -0.00616
LFBldgSCEHspExCZ14 | Com-Iltg-dWatt-LF_OSbldg | SCE | Hsp | Ex | CZ14 | 5.2595 | 0.00082695 | 0 | 5.9488 | 0.0010593 | -0.03509 | 5.24 | 0.00082207 | 0 | 5.9205 | 0.00105 | -0.034905 |  | LF | Bldg | 5260 | 0.827 | 5240 | 0.822 | 1.13 | 1.28 | -0.0066612 | 5260 | 0.827 | 5240 | 0.822 | 1.13 | 1.28 | -0.00666
LFBldgSCEHspExCZ15 | Com-Iltg-dWatt-LF_OSbldg | SCE | Hsp | Ex | CZ15 | 5.2584 | 0.00082668 | 0 | 6.2376 | 0.0010692 | -0.022592 | 5.24 | 0.00082208 | 0 | 6.21 | 0.00106 | -0.0225 |  | LF | Bldg | 5260 | 0.827 | 5240 | 0.822 | 1.19 | 1.29 | -0.0042939 | 5260 | 0.827 | 5240 | 0.822 | 1.19 | 1.29 | -0.00429
LFBldgSCEHspExCZ16 | Com-Iltg-dWatt-LF_OSbldg | SCE | Hsp | Ex | CZ16 | 5.2585 | 0.0008267 | 0 | 5.5885 | 0.00102 | -0.047685 | 5.24 | 0.00082208 | 0 | 5.57 | 0.00102 | -0.0475 |  | LF | Bldg | 5260 | 0.827 | 5240 | 0.822 | 1.06 | 1.24 | -0.0090649 | 5260 | 0.827 | 5240 | 0.822 | 1.06 | 1.24 | -0.00906
LFBldgSCEHspExIOU | Com-Iltg-dWatt-LF_OSbldg | SCE | Hsp | Ex | IOU | 5.2635 | 0.00082793 | 0 | 6.0863 | 0.0010508 | -0.027719 | 5.24 | 0.00082205 | 0 | 6.0575 | 0.0010462 | -0.027597 |  | LF | Bldg | 5260 | 0.828 | 5240 | 0.822 | 1.16 | 1.27 | -0.0052666 | 5260 | 0.828 | 5240 | 0.822 | 1.16 | 1.27 | -0.00527
LFBldgSCEHspNewCZ05 | Com-Iltg-dWatt-LF_OSbldg | SCE | Hsp | New | CZ05 | 5.24 | 0.000823 | 0 | 5.56 | 0.00098 | -0.0363 | 5.24 | 0.000823 | 0 | 5.56 | 0.00098 | -0.0363 |  | LF | Bldg | 5240 | 0.823 | 5240 | 0.823 | 1.06 | 1.19 | -0.0069275 | 5240 | 0.823 | 5240 | 0.823 | 1.06 | 1.19 | -0.00693
LFBldgSCEHspNewCZ06 | Com-Iltg-dWatt-LF_OSbldg | SCE | Hsp | New | CZ06 | 5.24 | 0.000823 | 0 | 5.77 | 0.000996 | -0.0284 | 5.24 | 0.000823 | 0 | 5.77 | 0.000996 | -0.0284 |  | LF | Bldg | 5240 | 0.823 | 5240 | 0.823 | 1.1 | 1.21 | -0.0054198 | 5240 | 0.823 | 5240 | 0.823 | 1.1 | 1.21 | -0.00542
LFBldgSCEHspNewCZ08 | Com-Iltg-dWatt-LF_OSbldg | SCE | Hsp | New | CZ08 | 5.24 | 0.000823 | 0 | 5.82 | 0.001 | -0.0265 | 5.24 | 0.000823 | 0 | 5.82 | 0.001 | -0.0265 |  | LF | Bldg | 5240 | 0.823 | 5240 | 0.823 | 1.11 | 1.22 | -0.0050573 | 5240 | 0.823 | 5240 | 0.823 | 1.11 | 1.22 | -0.00506
LFBldgSCEHspNewCZ09 | Com-Iltg-dWatt-LF_OSbldg | SCE | Hsp | New | CZ09 | 5.24 | 0.000823 | 0 | 5.84 | 0.00103 | -0.0266 | 5.24 | 0.000823 | 0 | 5.84 | 0.00103 | -0.0266 |  | LF | Bldg | 5240 | 0.823 | 5240 | 0.823 | 1.11 | 1.25 | -0.0050763 | 5240 | 0.823 | 5240 | 0.823 | 1.11 | 1.25 | -0.00508
LFBldgSCEHspNewCZ10 | Com-Iltg-dWatt-LF_OSbldg | SCE | Hsp | New | CZ10 | 5.24 | 0.000823 | 0 | 5.81 | 0.00104 | -0.0282 | 5.24 | 0.000823 | 0 | 5.81 | 0.00104 | -0.0282 |  | LF | Bldg | 5240 | 0.823 | 5240 | 0.823 | 1.11 | 1.26 | -0.0053817 | 5240 | 0.823 | 5240 | 0.823 | 1.11 | 1.26 | -0.00538
LFBldgSCEHspNewCZ13 | Com-Iltg-dWatt-LF_OSbldg | SCE | Hsp | New | CZ13 | 5.24 | 0.000823 | 0 | 5.79 | 0.00103 | -0.0324 | 5.24 | 0.000823 | 0 | 5.79 | 0.00103 | -0.0324 |  | LF | Bldg | 5240 | 0.823 | 5240 | 0.823 | 1.1 | 1.25 | -0.0061832 | 5240 | 0.823 | 5240 | 0.823 | 1.1 | 1.25 | -0.00618
LFBldgSCEHspNewCZ14 | Com-Iltg-dWatt-LF_OSbldg | SCE | Hsp | New | CZ14 | 5.24 | 0.000823 | 0 | 5.73 | 0.00103 | -0.0358 | 5.24 | 0.000823 | 0 | 5.73 | 0.00103 | -0.0358 |  | LF | Bldg | 5240 | 0.823 | 5240 | 0.823 | 1.09 | 1.25 | -0.0068321 | 5240 | 0.823 | 5240 | 0.823 | 1.09 | 1.25 | -0.00683
LFBldgSCEHspNewCZ15 | Com-Iltg-dWatt-LF_OSbldg | SCE | Hsp | New | CZ15 | 5.24 | 0.000823 | 0 | 6.1 | 0.00105 | -0.0201 | 5.24 | 0.000823 | 0 | 6.1 | 0.00105 | -0.0201 |  | LF | Bldg | 5240 | 0.823 | 5240 | 0.823 | 1.16 | 1.28 | -0.0038359 | 5240 | 0.823 | 5240 | 0.823 | 1.16 | 1.28 | -0.00384
LFBldgSCEHspNewCZ16 | Com-Iltg-dWatt-LF_OSbldg | SCE | Hsp | New | CZ16 | 5.24 | 0.000823 | 0 | 5.35 | 0.00099 | -0.0513 | 5.24 | 0.000823 | 0 | 5.35 | 0.00099 | -0.0513 |  | LF | Bldg | 5240 | 0.823 | 5240 | 0.823 | 1.02 | 1.2 | -0.0097901 | 5240 | 0.823 | 5240 | 0.823 | 1.02 | 1.2 | -0.00979
LFBldgSCEHspNewIOU | Com-Iltg-dWatt-LF_OSbldg | SCE | Hsp | New | IOU | 5.24 | 0.000823 | 0 | 5.8018 | 0.0010177 | -0.028483 | 5.24 | 0.000823 | 0 | 5.8018 | 0.0010177 | -0.028483 |  | LF | Bldg | 5240 | 0.823 | 5240 | 0.823 | 1.11 | 1.24 | -0.0054358 | 5240 | 0.823 | 5240 | 0.823 | 1.11 | 1.24 | -0.00544
LFBldgSCEHtlExCZ05 | Com-Iltg-dWatt-LF_OSbldg | SCE | Htl | Ex | CZ05 | 1.9486 | 0.00024183 | 0 | 1.9086 | 0.00030476 | -0.0068949 | 1.91 | 0.000237 | 0 | 1.8797 | 0.00029897 | -0.0067693 |  | LF | Bldg | 1950 | 0.242 | 1910 | 0.237 | 0.984 | 1.26 | -0.0035441 | 1950 | 0.242 | 1910 | 0.237 | 0.984 | 1.26 | -0.00354
LFBldgSCEHtlExCZ06 | Com-Iltg-dWatt-LF_OSbldg | SCE | Htl | Ex | CZ06 | 1.9484 | 0.0002418 | 0 | 2.1184 | 0.00030573 | -0.0045561 | 1.91 | 0.000237 | 0 | 2.08 | 0.00029996 | -0.0044696 |  | LF | Bldg | 1950 | 0.242 | 1910 | 0.237 | 1.09 | 1.27 | -0.0023401 | 1950 | 0.242 | 1910 | 0.237 | 1.09 | 1.27 | -0.00234
LFBldgSCEHtlExCZ08 | Com-Iltg-dWatt-LF_OSbldg | SCE | Htl | Ex | CZ08 | 1.9485 | 0.00024181 | 0 | 2.1585 | 0.00030877 | -0.0040469 | 1.91 | 0.000237 | 0 | 2.12 | 0.000303 | -0.0039796 |  | LF | Bldg | 1950 | 0.242 | 1910 | 0.237 | 1.11 | 1.28 | -0.0020836 | 1950 | 0.242 | 1910 | 0.237 | 1.11 | 1.28 | -0.00208
LFBldgSCEHtlExCZ09 | Com-Iltg-dWatt-LF_OSbldg | SCE | Htl | Ex | CZ09 | 1.9479 | 0.00024174 | 0 | 2.1379 | 0.00031364 | -0.0041053 | 1.91 | 0.000237 | 0 | 2.1 | 0.000307 | -0.0040295 |  | LF | Bldg | 1950 | 0.242 | 1910 | 0.237 | 1.1 | 1.3 | -0.0021097 | 1950 | 0.242 | 1910 | 0.237 | 1.1 | 1.3 | -0.00211
LFBldgSCEHtlExCZ10 | Com-Iltg-dWatt-LF_OSbldg | SCE | Htl | Ex | CZ10 | 1.9459 | 0.00024148 | 0 | 2.0759 | 0.00031027 | -0.0043707 | 1.91 | 0.000237 | 0 | 2.049 | 0.0003049 | -0.004299 |  | LF | Bldg | 1950 | 0.241 | 1910 | 0.237 | 1.07 | 1.29 | -0.0022508 | 1950 | 0.241 | 1910 | 0.237 | 1.07 | 1.29 | -0.00225
LFBldgSCEHtlExCZ13 | Com-Iltg-dWatt-LF_OSbldg | SCE | Htl | Ex | CZ13 | 1.9469 | 0.00024161 | 0 | 2.0169 | 0.00031046 | -0.0058907 | 1.91 | 0.000237 | 0 | 1.98 | 0.00030492 | -0.0057892 |  | LF | Bldg | 1950 | 0.242 | 1910 | 0.237 | 1.04 | 1.29 | -0.003031 | 1950 | 0.242 | 1910 | 0.237 | 1.04 | 1.29 | -0.00303
LFBldgSCEHtlExCZ14 | Com-Iltg-dWatt-LF_OSbldg | SCE | Htl | Ex | CZ14 | 1.9462 | 0.00024152 | 0 | 1.9962 | 0.00031242 | -0.0059285 | 1.91 | 0.000237 | 0 | 1.96 | 0.000307 | -0.005829 |  | LF | Bldg | 1950 | 0.242 | 1910 | 0.237 | 1.03 | 1.3 | -0.0030519 | 1950 | 0.242 | 1910 | 0.237 | 1.03 | 1.3 | -0.00305
LFBldgSCEHtlExCZ15 | Com-Iltg-dWatt-LF_OSbldg | SCE | Htl | Ex | CZ15 | 1.9459 | 0.00024148 | 0 | 2.2548 | 0.00031327 | -0.0024248 | 1.91 | 0.000237 | 0 | 2.219 | 0.0003079 | -0.002389 |  | LF | Bldg | 1950 | 0.241 | 1910 | 0.237 | 1.16 | 1.3 | -0.0012508 | 1950 | 0.241 | 1910 | 0.237 | 1.16 | 1.3 | -0.00125
LFBldgSCEHtlExCZ16 | Com-Iltg-dWatt-LF_OSbldg | SCE | Htl | Ex | CZ16 | 1.9466 | 0.00024158 | 0 | 1.7375 | 0.0003034 | -0.010183 | 1.91 | 0.000237 | 0 | 1.71 | 0.00029791 | -0.010092 |  | LF | Bldg | 1950 | 0.242 | 1910 | 0.237 | 0.895 | 1.26 | -0.0052835 | 1950 | 0.242 | 1910 | 0.237 | 0.895 | 1.26 | -0.00528
LFBldgSCEHtlExIOU | Com-Iltg-dWatt-LF_OSbldg | SCE | Htl | Ex | IOU | 1.9477 | 0.00024171 | 0 | 2.1282 | 0.00030912 | -0.0043267 | 1.91 | 0.000237 | 0 | 2.0914 | 0.00030331 | -0.0042533 |  | LF | Bldg | 1950 | 0.242 | 1910 | 0.237 | 1.09 | 1.28 | -0.0022268 | 1950 | 0.242 | 1910 | 0.237 | 1.09 | 1.28 | -0.00223
LFBldgSCEHtlNewCZ05 | Com-Iltg-dWatt-LF_OSbldg | SCE | Htl | New | CZ05 | 1.91 | 0.000237 | 0 | 1.77 | 0.000302 | -0.00759 | 1.91 | 0.000237 | 0 | 1.77 | 0.000302 | -0.00759 |  | LF | Bldg | 1910 | 0.237 | 1910 | 0.237 | 0.927 | 1.27 | -0.0039738 | 1910 | 0.237 | 1910 | 0.237 | 0.927 | 1.27 | -0.00397
LFBldgSCEHtlNewCZ06 | Com-Iltg-dWatt-LF_OSbldg | SCE | Htl | New | CZ06 | 1.91 | 0.000237 | 0 | 2.03 | 0.000306 | -0.00423 | 1.91 | 0.000237 | 0 | 2.03 | 0.000306 | -0.00423 |  | LF | Bldg | 1910 | 0.237 | 1910 | 0.237 | 1.06 | 1.29 | -0.0022147 | 1910 | 0.237 | 1910 | 0.237 | 1.06 | 1.29 | -0.00221
LFBldgSCEHtlNewCZ08 | Com-Iltg-dWatt-LF_OSbldg | SCE | Htl | New | CZ08 | 1.91 | 0.000237 | 0 | 2.06 | 0.000309 | -0.00364 | 1.91 | 0.000237 | 0 | 2.06 | 0.000309 | -0.00364 |  | LF | Bldg | 1910 | 0.237 | 1910 | 0.237 | 1.08 | 1.3 | -0.0019058 | 1910 | 0.237 | 1910 | 0.237 | 1.08 | 1.3 | -0.00191
LFBldgSCEHtlNewCZ09 | Com-Iltg-dWatt-LF_OSbldg | SCE | Htl | New | CZ09 | 1.91 | 0.000237 | 0 | 2.05 | 0.000315 | -0.00408 | 1.91 | 0.000237 | 0 | 2.05 | 0.000315 | -0.00408 |  | LF | Bldg | 1910 | 0.237 | 1910 | 0.237 | 1.07 | 1.33 | -0.0021361 | 1910 | 0.237 | 1910 | 0.237 | 1.07 | 1.33 | -0.00214
LFBldgSCEHtlNewCZ10 | Com-Iltg-dWatt-LF_OSbldg | SCE | Htl | New | CZ10 | 1.91 | 0.000237 | 0 | 2.03 | 0.00032 | -0.00471 | 1.91 | 0.000237 | 0 | 2.03 | 0.00032 | -0.00471 |  | LF | Bldg | 1910 | 0.237 | 1910 | 0.237 | 1.06 | 1.35 | -0.002466 | 1910 | 0.237 | 1910 | 0.237 | 1.06 | 1.35 | -0.00247
LFBldgSCEHtlNewCZ13 | Com-Iltg-dWatt-LF_OSbldg | SCE | Htl | New | CZ13 | 1.91 | 0.000237 | 0 | 1.95 | 0.000315 | -0.00626 | 1.91 | 0.000237 | 0 | 1.95 | 0.000315 | -0.00626 |  | LF | Bldg | 1910 | 0.237 | 1910 | 0.237 | 1.02 | 1.33 | -0.0032775 | 1910 | 0.237 | 1910 | 0.237 | 1.02 | 1.33 | -0.00328
LFBldgSCEHtlNewCZ14 | Com-Iltg-dWatt-LF_OSbldg | SCE | Htl | New | CZ14 | 1.91 | 0.000237 | 0 | 1.91 | 0.000318 | -0.00706 | 1.91 | 0.000237 | 0 | 1.91 | 0.000318 | -0.00706 |  | LF | Bldg | 1910 | 0.237 | 1910 | 0.237 | 1 | 1.34 | -0.0036963 | 1910 | 0.237 | 1910 | 0.237 | 1 | 1.34 | -0.0037
LFBldgSCEHtlNewCZ15 | Com-Iltg-dWatt-LF_OSbldg | SCE | Htl | New | CZ15 | 1.91 | 0.000237 | 0 | 2.24 | 0.000323 | -0.00244 | 1.91 | 0.000237 | 0 | 2.24 | 0.000323 | -0.00244 |  | LF | Bldg | 1910 | 0.237 | 1910 | 0.237 | 1.17 | 1.36 | -0.0012775 | 1910 | 0.237 | 1910 | 0.237 | 1.17 | 1.36 | -0.00128
LFBldgSCEHtlNewCZ16 | Com-Iltg-dWatt-LF_OSbldg | SCE | Htl | New | CZ16 | 1.91 | 0.000237 | 0 | 1.65 | 0.000303 | -0.012 | 1.91 | 0.000237 | 0 | 1.65 | 0.000303 | -0.012 |  | LF | Bldg | 1910 | 0.237 | 1910 | 0.237 | 0.864 | 1.28 | -0.0062827 | 1910 | 0.237 | 1910 | 0.237 | 0.864 | 1.28 | -0.00628
LFBldgSCEHtlNewIOU | Com-Iltg-dWatt-LF_OSbldg | SCE | Htl | New | IOU | 1.91 | 0.000237 | 0 | 2.0642 | 0.00031414 | -0.004298 | 1.91 | 0.000237 | 0 | 2.0642 | 0.00031414 | -0.004298 |  | LF | Bldg | 1910 | 0.237 | 1910 | 0.237 | 1.08 | 1.33 | -0.0022503 | 1910 | 0.237 | 1910 | 0.237 | 1.08 | 1.33 | -0.00225
LFBldgSCEMBTExCZ05 | Com-Iltg-dWatt-LF_OSbldg | SCE | MBT | Ex | CZ05 | 3.5237 | 0.00085002 | 0 | 4.0431 | 0.0010689 | -0.0019265 | 3.42 | 0.000834 | 0 | 3.93 | 0.00105 | -0.00187 |  | LF | Bldg | 3520 | 0.85 | 3420 | 0.834 | 1.15 | 1.26 | -0.00054678 | 3520 | 0.85 | 3420 | 0.834 | 1.15 | 1.26 | -0.000547
LFBldgSCEMBTExCZ06 | Com-Iltg-dWatt-LF_OSbldg | SCE | MBT | Ex | CZ06 | 3.5237 | 0.00085003 | 0 | 4.1426 | 0.0010389 | -0.0008804 | 3.42 | 0.000834 | 0 | 4.0294 | 0.00102 | -0.00085589 |  | LF | Bldg | 3520 | 0.85 | 3420 | 0.834 | 1.18 | 1.22 | -0.00025026 | 3520 | 0.85 | 3420 | 0.834 | 1.18 | 1.22 | -0.00025
LFBldgSCEMBTExCZ08 | Com-Iltg-dWatt-LF_OSbldg | SCE | MBT | Ex | CZ08 | 3.5237 | 0.00085003 | 0 | 4.1626 | 0.0010789 | -0.00059192 | 3.42 | 0.000834 | 0 | 4.0494 | 0.00106 | -0.00057494 |  | LF | Bldg | 3520 | 0.85 | 3420 | 0.834 | 1.18 | 1.27 | -0.00016811 | 3520 | 0.85 | 3420 | 0.834 | 1.18 | 1.27 | -0.000168
LFBldgSCEMBTExCZ09 | Com-Iltg-dWatt-LF_OSbldg | SCE | MBT | Ex | CZ09 | 3.5239 | 0.00085006 | 0 | 4.1528 | 0.0010883 | -0.0010683 | 3.42 | 0.000834 | 0 | 4.03 | 0.00106 | -0.00104 |  | LF | Bldg | 3520 | 0.85 | 3420 | 0.834 | 1.18 | 1.27 | -0.00030409 | 3520 | 0.85 | 3420 | 0.834 | 1.18 | 1.27 | -0.000304
LFBldgSCEMBTExCZ10 | Com-Iltg-dWatt-LF_OSbldg | SCE | MBT | Ex | CZ10 | 3.5147 | 0.00084863 | 0 | 4.0119 | 0.0010872 | -0.0011558 | 3.42 | 0.000834 | 0 | 3.9086 | 0.00107 | -0.00113 |  | LF | Bldg | 3510 | 0.849 | 3420 | 0.834 | 1.14 | 1.28 | -0.00033041 | 3510 | 0.849 | 3420 | 0.834 | 1.14 | 1.28 | -0.00033
LFBldgSCEMBTExCZ13 | Com-Iltg-dWatt-LF_OSbldg | SCE | MBT | Ex | CZ13 | 3.5203 | 0.0008495 | 0 | 4.0185 | 0.0010482 | -0.0024829 | 3.42 | 0.000834 | 0 | 3.9091 | 0.00103 | -0.0024191 |  | LF | Bldg | 3520 | 0.85 | 3420 | 0.834 | 1.14 | 1.24 | -0.00070734 | 3520 | 0.85 | 3420 | 0.834 | 1.14 | 1.24 | -0.000707
LFBldgSCEMBTExCZ14 | Com-Iltg-dWatt-LF_OSbldg | SCE | MBT | Ex | CZ14 | 3.5186 | 0.00084924 | 0 | 4.0165 | 0.0010879 | -0.0028307 | 3.42 | 0.000834 | 0 | 3.909 | 0.00107 | -0.002759 |  | LF | Bldg | 3520 | 0.849 | 3420 | 0.834 | 1.14 | 1.28 | -0.00080671 | 3520 | 0.849 | 3420 | 0.834 | 1.14 | 1.28 | -0.000807
LFBldgSCEMBTExCZ15 | Com-Iltg-dWatt-LF_OSbldg | SCE | MBT | Ex | CZ15 | 3.5147 | 0.00084863 | 0 | 4.1719 | 0.0010872 | 0 | 3.42 | 0.000834 | 0 | 4.0686 | 0.00107 | 0 |  | LF | Bldg | 3510 | 0.849 | 3420 | 0.834 | 1.19 | 1.28 | 0 | 3510 | 0.849 | 3420 | 0.834 | 1.19 | 1.28 | 0
LFBldgSCEMBTExCZ16 | Com-Iltg-dWatt-LF_OSbldg | SCE | MBT | Ex | CZ16 | 3.5178 | 0.00084912 | 0 | 3.7767 | 0.0010178 | -0.0096357 | 3.42 | 0.000834 | 0 | 3.67 | 0.001 | -0.0093778 |  | LF | Bldg | 3520 | 0.849 | 3420 | 0.834 | 1.07 | 1.2 | -0.002742 | 3520 | 0.849 | 3420 | 0.834 | 1.07 | 1.2 | -0.00274
LFBldgSCEMBTExIOU | Com-Iltg-dWatt-LF_OSbldg | SCE | MBT | Ex | IOU | 3.5213 | 0.00084966 | 0 | 4.1149 | 0.0010717 | -0.0011156 | 3.42 | 0.000834 | 0 | 4.0029 | 0.0010518 | -0.0010862 |  | LF | Bldg | 3520 | 0.85 | 3420 | 0.834 | 1.17 | 1.26 | -0.00031761 | 3520 | 0.85 | 3420 | 0.834 | 1.17 | 1.26 | -0.000318
LFBldgSCEMBTNewCZ05 | Com-Iltg-dWatt-LF_OSbldg | SCE | MBT | New | CZ05 | 3.42 | 0.000834 | 0 | 3.7 | 0.00104 | -0.00114 | 3.42 | 0.000834 | 0 | 3.7 | 0.00104 | -0.00114 |  | LF | Bldg | 3420 | 0.834 | 3420 | 0.834 | 1.08 | 1.25 | -0.00033333 | 3420 | 0.834 | 3420 | 0.834 | 1.08 | 1.25 | -0.000333
LFBldgSCEMBTNewCZ06 | Com-Iltg-dWatt-LF_OSbldg | SCE | MBT | New | CZ06 | 3.42 | 0.000834 | 0 | 3.84 | 0.00105 | -0.00114 | 3.42 | 0.000834 | 0 | 3.84 | 0.00105 | -0.00114 |  | LF | Bldg | 3420 | 0.834 | 3420 | 0.834 | 1.12 | 1.26 | -0.00033333 | 3420 | 0.834 | 3420 | 0.834 | 1.12 | 1.26 | -0.000333
LFBldgSCEMBTNewCZ08 | Com-Iltg-dWatt-LF_OSbldg | SCE | MBT | New | CZ08 | 3.42 | 0.000834 | 0 | 3.85 | 0.00107 | -0.000913 | 3.42 | 0.000834 | 0 | 3.85 | 0.00107 | -0.000913 |  | LF | Bldg | 3420 | 0.834 | 3420 | 0.834 | 1.13 | 1.28 | -0.00026696 | 3420 | 0.834 | 3420 | 0.834 | 1.13 | 1.28 | -0.000267
LFBldgSCEMBTNewCZ09 | Com-Iltg-dWatt-LF_OSbldg | SCE | MBT | New | CZ09 | 3.42 | 0.000834 | 0 | 3.84 | 0.0011 | -0.00108 | 3.42 | 0.000834 | 0 | 3.84 | 0.0011 | -0.00108 |  | LF | Bldg | 3420 | 0.834 | 3420 | 0.834 | 1.12 | 1.32 | -0.00031579 | 3420 | 0.834 | 3420 | 0.834 | 1.12 | 1.32 | -0.000316
LFBldgSCEMBTNewCZ10 | Com-Iltg-dWatt-LF_OSbldg | SCE | MBT | New | CZ10 | 3.42 | 0.000834 | 0 | 3.86 | 0.00112 | -0.00114 | 3.42 | 0.000834 | 0 | 3.86 | 0.00112 | -0.00114 |  | LF | Bldg | 3420 | 0.834 | 3420 | 0.834 | 1.13 | 1.34 | -0.00033333 | 3420 | 0.834 | 3420 | 0.834 | 1.13 | 1.34 | -0.000333
LFBldgSCEMBTNewCZ13 | Com-Iltg-dWatt-LF_OSbldg | SCE | MBT | New | CZ13 | 3.42 | 0.000834 | 0 | 3.82 | 0.00109 | -0.002 | 3.42 | 0.000834 | 0 | 3.82 | 0.00109 | -0.002 |  | LF | Bldg | 3420 | 0.834 | 3420 | 0.834 | 1.12 | 1.31 | -0.0005848 | 3420 | 0.834 | 3420 | 0.834 | 1.12 | 1.31 | -0.000585
LFBldgSCEMBTNewCZ14 | Com-Iltg-dWatt-LF_OSbldg | SCE | MBT | New | CZ14 | 3.42 | 0.000834 | 0 | 3.82 | 0.0011 | -0.00216 | 3.42 | 0.000834 | 0 | 3.82 | 0.0011 | -0.00216 |  | LF | Bldg | 3420 | 0.834 | 3420 | 0.834 | 1.12 | 1.32 | -0.00063158 | 3420 | 0.834 | 3420 | 0.834 | 1.12 | 1.32 | -0.000632
LFBldgSCEMBTNewCZ15 | Com-Iltg-dWatt-LF_OSbldg | SCE | MBT | New | CZ15 | 3.42 | 0.000834 | 0 | 4.06 | 0.00112 | 0 | 3.42 | 0.000834 | 0 | 4.06 | 0.00112 | 0 |  | LF | Bldg | 3420 | 0.834 | 3420 | 0.834 | 1.19 | 1.34 | 0 | 3420 | 0.834 | 3420 | 0.834 | 1.19 | 1.34 | 0
LFBldgSCEMBTNewCZ16 | Com-Iltg-dWatt-LF_OSbldg | SCE | MBT | New | CZ16 | 3.42 | 0.000834 | 0 | 3.62 | 0.00104 | -0.00687 | 3.42 | 0.000834 | 0 | 3.62 | 0.00104 | -0.00687 |  | LF | Bldg | 3420 | 0.834 | 3420 | 0.834 | 1.06 | 1.25 | -0.0020088 | 3420 | 0.834 | 3420 | 0.834 | 1.06 | 1.25 | -0.00201
LFBldgSCEMBTNewIOU | Com-Iltg-dWatt-LF_OSbldg | SCE | MBT | New | IOU | 3.42 | 0.000834 | 0 | 3.864 | 0.0010918 | -0.0012114 | 3.42 | 0.000834 | 0 | 3.864 | 0.0010918 | -0.0012114 |  | LF | Bldg | 3420 | 0.834 | 3420 | 0.834 | 1.13 | 1.31 | -0.00035422 | 3420 | 0.834 | 3420 | 0.834 | 1.13 | 1.31 | -0.000354
LFBldgSCEMLIExCZ05 | Com-Iltg-dWatt-LF_OSbldg | SCE | MLI | Ex | CZ05 | 3.2194 | 0.00092388 | 0 | 3.3696 | 0.0011294 | -0.017094 | 3.21 | 0.000922 | 0 | 3.3696 | 0.0011294 | -0.017 |  | LF | Bldg | 3220 | 0.924 | 3210 | 0.922 | 1.05 | 1.22 | -0.005296 | 3220 | 0.924 | 3210 | 0.922 | 1.05 | 1.22 | -0.0053
LFBldgSCEMLIExCZ06 | Com-Iltg-dWatt-LF_OSbldg | SCE | MLI | Ex | CZ06 | 3.2194 | 0.00092389 | 0 | 3.5596 | 0.00111 | -0.0058196 | 3.21 | 0.000922 | 0 | 3.5596 | 0.00111 | -0.0058196 |  | LF | Bldg | 3220 | 0.924 | 3210 | 0.922 | 1.11 | 1.2 | -0.001813 | 3220 | 0.924 | 3210 | 0.922 | 1.11 | 1.2 | -0.00181
LFBldgSCEMLIExCZ08 | Com-Iltg-dWatt-LF_OSbldg | SCE | MLI | Ex | CZ08 | 3.2194 | 0.00092389 | 0 | 3.58 | 0.00111 | -0.0047596 | 3.21 | 0.000922 | 0 | 3.58 | 0.00111 | -0.0047596 |  | LF | Bldg | 3220 | 0.924 | 3210 | 0.922 | 1.12 | 1.2 | -0.0014827 | 3220 | 0.924 | 3210 | 0.922 | 1.12 | 1.2 | -0.00148
LFBldgSCEMLIExCZ09 | Com-Iltg-dWatt-LF_OSbldg | SCE | MLI | Ex | CZ09 | 3.2194 | 0.00092389 | 0 | 3.5596 | 0.00113 | -0.0066591 | 3.21 | 0.000922 | 0 | 3.5596 | 0.00113 | -0.0066496 |  | LF | Bldg | 3220 | 0.924 | 3210 | 0.922 | 1.11 | 1.23 | -0.0020715 | 3220 | 0.924 | 3210 | 0.922 | 1.11 | 1.23 | -0.00207
LFBldgSCEMLIExCZ10 | Com-Iltg-dWatt-LF_OSbldg | SCE | MLI | Ex | CZ10 | 3.2186 | 0.00092431 | 0 | 3.4686 | 0.0011229 | -0.0072716 | 3.21 | 0.000922 | 0 | 3.4657 | 0.00112 | -0.0072571 |  | LF | Bldg | 3220 | 0.924 | 3210 | 0.922 | 1.08 | 1.21 | -0.0022608 | 3220 | 0.924 | 3210 | 0.922 | 1.08 | 1.21 | -0.00226
LFBldgSCEMLIExCZ13 | Com-Iltg-dWatt-LF_OSbldg | SCE | MLI | Ex | CZ13 | 3.2191 | 0.00092439 | 0 | 3.4329 | 0.00111 | -0.017429 | 3.21 | 0.000922 | 0 | 3.43 | 0.00111 | -0.0174 |  | LF | Bldg | 3220 | 0.924 | 3210 | 0.922 | 1.07 | 1.2 | -0.0054206 | 3220 | 0.924 | 3210 | 0.922 | 1.07 | 1.2 | -0.00542
LFBldgSCEMLIExCZ14 | Com-Iltg-dWatt-LF_OSbldg | SCE | MLI | Ex | CZ14 | 3.219 | 0.00092434 | 0 | 3.4027 | 0.00112 | -0.0202 | 3.21 | 0.000922 | 0 | 3.4 | 0.00112 | -0.0202 |  | LF | Bldg | 3220 | 0.924 | 3210 | 0.922 | 1.06 | 1.21 | -0.0062928 | 3220 | 0.924 | 3210 | 0.922 | 1.06 | 1.21 | -0.00629
LFBldgSCEMLIExCZ15 | Com-Iltg-dWatt-LF_OSbldg | SCE | MLI | Ex | CZ15 | 3.2186 | 0.00092372 | 0 | 3.71 | 0.00111 | -0.00193 | 3.21 | 0.000922 | 0 | 3.71 | 0.00111 | -0.00193 |  | LF | Bldg | 3220 | 0.924 | 3210 | 0.922 | 1.16 | 1.2 | -0.00060125 | 3220 | 0.924 | 3210 | 0.922 | 1.16 | 1.2 | -0.000601
LFBldgSCEMLIExCZ16 | Com-Iltg-dWatt-LF_OSbldg | SCE | MLI | Ex | CZ16 | 3.2189 | 0.00092378 | 0 | 3.17 | 0.0011 | -0.0392 | 3.21 | 0.000922 | 0 | 3.17 | 0.0011 | -0.0392 |  | LF | Bldg | 3220 | 0.924 | 3210 | 0.922 | 0.988 | 1.19 | -0.012212 | 3220 | 0.924 | 3210 | 0.922 | 0.988 | 1.19 | -0.0122
LFBldgSCEMLIExIOU | Com-Iltg-dWatt-LF_OSbldg | SCE | MLI | Ex | IOU | 3.2192 | 0.00092397 | 0 | 3.5423 | 0.0011154 | -0.0071818 | 3.21 | 0.000922 | 0 | 3.5416 | 0.0011149 | -0.0071771 |  | LF | Bldg | 3220 | 0.924 | 3210 | 0.922 | 1.1 | 1.21 | -0.0022359 | 3220 | 0.924 | 3210 | 0.922 | 1.1 | 1.21 | -0.00224
LFBldgSCEMLINewCZ05 | Com-Iltg-dWatt-LF_OSbldg | SCE | MLI | New | CZ05 | 3.21 | 0.000922 | 0 | 3.23 | 0.0011 | -0.0208 | 3.21 | 0.000922 | 0 | 3.23 | 0.0011 | -0.0208 |  | LF | Bldg | 3210 | 0.922 | 3210 | 0.922 | 1.01 | 1.19 | -0.0064798 | 3210 | 0.922 | 3210 | 0.922 | 1.01 | 1.19 | -0.00648
LFBldgSCEMLINewCZ06 | Com-Iltg-dWatt-LF_OSbldg | SCE | MLI | New | CZ06 | 3.21 | 0.000922 | 0 | 3.45 | 0.00113 | -0.009 | 3.21 | 0.000922 | 0 | 3.45 | 0.00113 | -0.009 |  | LF | Bldg | 3210 | 0.922 | 3210 | 0.922 | 1.07 | 1.23 | -0.0028037 | 3210 | 0.922 | 3210 | 0.922 | 1.07 | 1.23 | -0.0028
LFBldgSCEMLINewCZ08 | Com-Iltg-dWatt-LF_OSbldg | SCE | MLI | New | CZ08 | 3.21 | 0.000922 | 0 | 3.5 | 0.00114 | -0.00701 | 3.21 | 0.000922 | 0 | 3.5 | 0.00114 | -0.00701 |  | LF | Bldg | 3210 | 0.922 | 3210 | 0.922 | 1.09 | 1.24 | -0.0021838 | 3210 | 0.922 | 3210 | 0.922 | 1.09 | 1.24 | -0.00218
LFBldgSCEMLINewCZ09 | Com-Iltg-dWatt-LF_OSbldg | SCE | MLI | New | CZ09 | 3.21 | 0.000922 | 0 | 3.52 | 0.00119 | -0.008 | 3.21 | 0.000922 | 0 | 3.52 | 0.00119 | -0.008 |  | LF | Bldg | 3210 | 0.922 | 3210 | 0.922 | 1.1 | 1.29 | -0.0024922 | 3210 | 0.922 | 3210 | 0.922 | 1.1 | 1.29 | -0.00249
LFBldgSCEMLINewCZ10 | Com-Iltg-dWatt-LF_OSbldg | SCE | MLI | New | CZ10 | 3.21 | 0.000922 | 0 | 3.54 | 0.00121 | -0.00861 | 3.21 | 0.000922 | 0 | 3.54 | 0.00121 | -0.00861 |  | LF | Bldg | 3210 | 0.922 | 3210 | 0.922 | 1.1 | 1.31 | -0.0026822 | 3210 | 0.922 | 3210 | 0.922 | 1.1 | 1.31 | -0.00268
LFBldgSCEMLINewCZ13 | Com-Iltg-dWatt-LF_OSbldg | SCE | MLI | New | CZ13 | 3.21 | 0.000922 | 0 | 3.5 | 0.00119 | -0.0176 | 3.21 | 0.000922 | 0 | 3.5 | 0.00119 | -0.0176 |  | LF | Bldg | 3210 | 0.922 | 3210 | 0.922 | 1.09 | 1.29 | -0.0054829 | 3210 | 0.922 | 3210 | 0.922 | 1.09 | 1.29 | -0.00548
LFBldgSCEMLINewCZ14 | Com-Iltg-dWatt-LF_OSbldg | SCE | MLI | New | CZ14 | 3.21 | 0.000922 | 0 | 3.48 | 0.00119 | -0.0195 | 3.21 | 0.000922 | 0 | 3.48 | 0.00119 | -0.0195 |  | LF | Bldg | 3210 | 0.922 | 3210 | 0.922 | 1.08 | 1.29 | -0.0060748 | 3210 | 0.922 | 3210 | 0.922 | 1.08 | 1.29 | -0.00607
LFBldgSCEMLINewCZ15 | Com-Iltg-dWatt-LF_OSbldg | SCE | MLI | New | CZ15 | 3.21 | 0.000922 | 0 | 3.77 | 0.00123 | -0.00134 | 3.21 | 0.000922 | 0 | 3.77 | 0.00123 | -0.00134 |  | LF | Bldg | 3210 | 0.922 | 3210 | 0.922 | 1.17 | 1.33 | -0.00041745 | 3210 | 0.922 | 3210 | 0.922 | 1.17 | 1.33 | -0.000417
LFBldgSCEMLINewCZ16 | Com-Iltg-dWatt-LF_OSbldg | SCE | MLI | New | CZ16 | 3.21 | 0.000922 | 0 | 3.21 | 0.00111 | -0.0382 | 3.21 | 0.000922 | 0 | 3.21 | 0.00111 | -0.0382 |  | LF | Bldg | 3210 | 0.922 | 3210 | 0.922 | 1 | 1.2 | -0.0119 | 3210 | 0.922 | 3210 | 0.922 | 1 | 1.2 | -0.0119
LFBldgSCEMLINewIOU | Com-Iltg-dWatt-LF_OSbldg | SCE | MLI | New | IOU | 3.21 | 0.000922 | 0 | 3.5258 | 0.0011775 | -0.0091724 | 3.21 | 0.000922 | 0 | 3.5258 | 0.0011775 | -0.0091724 |  | LF | Bldg | 3210 | 0.922 | 3210 | 0.922 | 1.1 | 1.28 | -0.0028575 | 3210 | 0.922 | 3210 | 0.922 | 1.1 | 1.28 | -0.00286
LFBldgSCEMtlExCZ05 | Com-Iltg-dWatt-LF_OSbldg | SCE | Mtl | Ex | CZ05 | 1.5494 | 0.00017193 | 0 | 1.6094 | 0.00021694 | -0.0087965 | 1.5 | 0.000166 | 0 | 1.56 | 0.00021 | -0.0085101 |  | LF | Bldg | 1550 | 0.172 | 1500 | 0.166 | 1.04 | 1.27 | -0.0056734 | 1550 | 0.172 | 1500 | 0.166 | 1.04 | 1.27 | -0.00567
LFBldgSCEMtlExCZ06 | Com-Iltg-dWatt-LF_OSbldg | SCE | Mtl | Ex | CZ06 | 1.5494 | 0.00017192 | 0 | 1.7589 | 0.00021887 | -0.0046078 | 1.5 | 0.000166 | 0 | 1.7 | 0.000211 | -0.0044597 |  | LF | Bldg | 1550 | 0.172 | 1500 | 0.166 | 1.13 | 1.27 | -0.0029732 | 1550 | 0.172 | 1500 | 0.166 | 1.13 | 1.27 | -0.00297
LFBldgSCEMtlExCZ08 | Com-Iltg-dWatt-LF_OSbldg | SCE | Mtl | Ex | CZ08 | 1.5494 | 0.00017192 | 0 | 1.789 | 0.0002209 | -0.0038981 | 1.5 | 0.000166 | 0 | 1.73 | 0.000213 | -0.00377 |  | LF | Bldg | 1550 | 0.172 | 1500 | 0.166 | 1.15 | 1.28 | -0.0025133 | 1550 | 0.172 | 1500 | 0.166 | 1.15 | 1.28 | -0.00251
LFBldgSCEMtlExCZ09 | Com-Iltg-dWatt-LF_OSbldg | SCE | Mtl | Ex | CZ09 | 1.5491 | 0.0001719 | 0 | 1.7786 | 0.00022686 | -0.0042781 | 1.5 | 0.000166 | 0 | 1.72 | 0.000219 | -0.0041405 |  | LF | Bldg | 1550 | 0.172 | 1500 | 0.166 | 1.15 | 1.32 | -0.0027603 | 1550 | 0.172 | 1500 | 0.166 | 1.15 | 1.32 | -0.00276
LFBldgSCEMtlExCZ10 | Com-Iltg-dWatt-LF_OSbldg | SCE | Mtl | Ex | CZ10 | 1.5526 | 0.00017231 | 0 | 1.7416 | 0.00022642 | -0.0048668 | 1.5 | 0.000166 | 0 | 1.68 | 0.000218 | -0.0046984 |  | LF | Bldg | 1550 | 0.172 | 1500 | 0.166 | 1.12 | 1.31 | -0.0031323 | 1550 | 0.172 | 1500 | 0.166 | 1.12 | 1.31 | -0.00313
LFBldgSCEMtlExCZ13 | Com-Iltg-dWatt-LF_OSbldg | SCE | Mtl | Ex | CZ13 | 1.5602 | 0.00017322 | 0 | 1.7002 | 0.00022671 | -0.006812 | 1.5 | 0.000166 | 0 | 1.64 | 0.00021708 | -0.0065472 |  | LF | Bldg | 1560 | 0.173 | 1500 | 0.166 | 1.09 | 1.31 | -0.0043648 | 1560 | 0.173 | 1500 | 0.166 | 1.09 | 1.31 | -0.00436
LFBldgSCEMtlExCZ14 | Com-Iltg-dWatt-LF_OSbldg | SCE | Mtl | Ex | CZ14 | 1.5557 | 0.00017269 | 0 | 1.6878 | 0.00022692 | -0.0065541 | 1.5 | 0.000166 | 0 | 1.63 | 0.000218 | -0.00632 |  | LF | Bldg | 1560 | 0.173 | 1500 | 0.166 | 1.09 | 1.31 | -0.0042133 | 1560 | 0.173 | 1500 | 0.166 | 1.09 | 1.31 | -0.00421
LFBldgSCEMtlExCZ15 | Com-Iltg-dWatt-LF_OSbldg | SCE | Mtl | Ex | CZ15 | 1.5448 | 0.00017138 | 0 | 1.8638 | 0.00022827 | -0.0020127 | 1.5 | 0.000166 | 0 | 1.801 | 0.0002211 | -0.00195 |  | LF | Bldg | 1540 | 0.171 | 1500 | 0.166 | 1.2 | 1.33 | -0.0013 | 1540 | 0.171 | 1500 | 0.166 | 1.2 | 1.33 | -0.0013
LFBldgSCEMtlExCZ16 | Com-Iltg-dWatt-LF_OSbldg | SCE | Mtl | Ex | CZ16 | 1.5458 | 0.00017149 | 0 | 1.4866 | 0.00021632 | -0.011374 | 1.5 | 0.000166 | 0 | 1.4409 | 0.000209 | -0.0111 |  | LF | Bldg | 1550 | 0.171 | 1500 | 0.166 | 0.961 | 1.26 | -0.0074 | 1550 | 0.171 | 1500 | 0.166 | 0.961 | 1.26 | -0.0074
LFBldgSCEMtlExIOU | Com-Iltg-dWatt-LF_OSbldg | SCE | Mtl | Ex | IOU | 1.549 | 0.00017188 | 0 | 1.7695 | 0.00022253 | -0.0043845 | 1.5 | 0.000166 | 0 | 1.7105 | 0.0002147 | -0.0042448 |  | LF | Bldg | 1550 | 0.172 | 1500 | 0.166 | 1.14 | 1.29 | -0.0028299 | 1550 | 0.172 | 1500 | 0.166 | 1.14 | 1.29 | -0.00283
LFBldgSCEMtlNewCZ05 | Com-Iltg-dWatt-LF_OSbldg | SCE | Mtl | New | CZ05 | 1.5 | 0.000166 | 0 | 1.49 | 0.000211 | -0.0117 | 1.5 | 0.000166 | 0 | 1.49 | 0.000211 | -0.0117 |  | LF | Bldg | 1500 | 0.166 | 1500 | 0.166 | 0.993 | 1.27 | -0.0078 | 1500 | 0.166 | 1500 | 0.166 | 0.993 | 1.27 | -0.0078
LFBldgSCEMtlNewCZ06 | Com-Iltg-dWatt-LF_OSbldg | SCE | Mtl | New | CZ06 | 1.5 | 0.000166 | 0 | 1.66 | 0.000215 | -0.00641 | 1.5 | 0.000166 | 0 | 1.66 | 0.000215 | -0.00641 |  | LF | Bldg | 1500 | 0.166 | 1500 | 0.166 | 1.11 | 1.3 | -0.0042733 | 1500 | 0.166 | 1500 | 0.166 | 1.11 | 1.3 | -0.00427
LFBldgSCEMtlNewCZ08 | Com-Iltg-dWatt-LF_OSbldg | SCE | Mtl | New | CZ08 | 1.5 | 0.000166 | 0 | 1.7 | 0.000219 | -0.00532 | 1.5 | 0.000166 | 0 | 1.7 | 0.000219 | -0.00532 |  | LF | Bldg | 1500 | 0.166 | 1500 | 0.166 | 1.13 | 1.32 | -0.0035467 | 1500 | 0.166 | 1500 | 0.166 | 1.13 | 1.32 | -0.00355
LFBldgSCEMtlNewCZ09 | Com-Iltg-dWatt-LF_OSbldg | SCE | Mtl | New | CZ09 | 1.5 | 0.000166 | 0 | 1.69 | 0.000222 | -0.0053 | 1.5 | 0.000166 | 0 | 1.69 | 0.000222 | -0.0053 |  | LF | Bldg | 1500 | 0.166 | 1500 | 0.166 | 1.13 | 1.34 | -0.0035333 | 1500 | 0.166 | 1500 | 0.166 | 1.13 | 1.34 | -0.00353
LFBldgSCEMtlNewCZ10 | Com-Iltg-dWatt-LF_OSbldg | SCE | Mtl | New | CZ10 | 1.5 | 0.000166 | 0 | 1.66 | 0.000223 | -0.00649 | 1.5 | 0.000166 | 0 | 1.66 | 0.000223 | -0.00649 |  | LF | Bldg | 1500 | 0.166 | 1500 | 0.166 | 1.11 | 1.34 | -0.0043267 | 1500 | 0.166 | 1500 | 0.166 | 1.11 | 1.34 | -0.00433
LFBldgSCEMtlNewCZ13 | Com-Iltg-dWatt-LF_OSbldg | SCE | Mtl | New | CZ13 | 1.5 | 0.000166 | 0 | 1.6 | 0.00022 | -0.00823 | 1.5 | 0.000166 | 0 | 1.6 | 0.00022 | -0.00823 |  | LF | Bldg | 1500 | 0.166 | 1500 | 0.166 | 1.07 | 1.33 | -0.0054867 | 1500 | 0.166 | 1500 | 0.166 | 1.07 | 1.33 | -0.00549
LFBldgSCEMtlNewCZ14 | Com-Iltg-dWatt-LF_OSbldg | SCE | Mtl | New | CZ14 | 1.5 | 0.000166 | 0 | 1.58 | 0.000222 | -0.00846 | 1.5 | 0.000166 | 0 | 1.58 | 0.000222 | -0.00846 |  | LF | Bldg | 1500 | 0.166 | 1500 | 0.166 | 1.05 | 1.34 | -0.00564 | 1500 | 0.166 | 1500 | 0.166 | 1.05 | 1.34 | -0.00564
LFBldgSCEMtlNewCZ15 | Com-Iltg-dWatt-LF_OSbldg | SCE | Mtl | New | CZ15 | 1.5 | 0.000166 | 0 | 1.8 | 0.000227 | -0.00305 | 1.5 | 0.000166 | 0 | 1.8 | 0.000227 | -0.00305 |  | LF | Bldg | 1500 | 0.166 | 1500 | 0.166 | 1.2 | 1.37 | -0.0020333 | 1500 | 0.166 | 1500 | 0.166 | 1.2 | 1.37 | -0.00203
LFBldgSCEMtlNewCZ16 | Com-Iltg-dWatt-LF_OSbldg | SCE | Mtl | New | CZ16 | 1.5 | 0.000166 | 0 | 1.39 | 0.000211 | -0.0132 | 1.5 | 0.000166 | 0 | 1.39 | 0.000211 | -0.0132 |  | LF | Bldg | 1500 | 0.166 | 1500 | 0.166 | 0.927 | 1.27 | -0.0088 | 1500 | 0.166 | 1500 | 0.166 | 0.927 | 1.27 | -0.0088
LFBldgSCEMtlNewIOU | Com-Iltg-dWatt-LF_OSbldg | SCE | Mtl | New | IOU | 1.5 | 0.000166 | 0 | 1.6871 | 0.00022072 | -0.0057246 | 1.5 | 0.000166 | 0 | 1.6871 | 0.00022072 | -0.0057246 |  | LF | Bldg | 1500 | 0.166 | 1500 | 0.166 | 1.12 | 1.33 | -0.0038164 | 1500 | 0.166 | 1500 | 0.166 | 1.12 | 1.33 | -0.00382
LFBldgSCENrsExCZ05 | Com-Iltg-dWatt-LF_OSbldg | SCE | Nrs | Ex | CZ05 | 4.1632 | 0.00067659 | 0 | 4.2244 | 0.00083773 | -0.065751 | 4.0804 | 0.00066404 | 0 | 4.1504 | 0.00082204 | -0.064504 |  | LF | Bldg | 4160 | 0.677 | 4080 | 0.664 | 1.02 | 1.24 | -0.015808 | 4160 | 0.677 | 4080 | 0.664 | 1.02 | 1.24 | -0.0158
LFBldgSCENrsExCZ06 | Com-Iltg-dWatt-LF_OSbldg | SCE | Nrs | Ex | CZ06 | 4.1631 | 0.00067657 | 0 | 4.5135 | 0.00088279 | -0.043639 | 4.0804 | 0.00066404 | 0 | 4.4292 | 0.00086616 | -0.042892 |  | LF | Bldg | 4160 | 0.677 | 4080 | 0.664 | 1.09 | 1.3 | -0.010512 | 4160 | 0.677 | 4080 | 0.664 | 1.09 | 1.3 | -0.0105
LFBldgSCENrsExCZ08 | Com-Iltg-dWatt-LF_OSbldg | SCE | Nrs | Ex | CZ08 | 4.1631 | 0.00067657 | 0 | 4.5547 | 0.00087978 | -0.042431 | 4.0804 | 0.00066404 | 0 | 4.4792 | 0.00086404 | -0.041692 |  | LF | Bldg | 4160 | 0.677 | 4080 | 0.664 | 1.1 | 1.3 | -0.010218 | 4160 | 0.677 | 4080 | 0.664 | 1.1 | 1.3 | -0.0102
LFBldgSCENrsExCZ09 | Com-Iltg-dWatt-LF_OSbldg | SCE | Nrs | Ex | CZ09 | 4.1625 | 0.00067647 | 0 | 4.5733 | 0.00091161 | -0.043233 | 4.0805 | 0.00066405 | 0 | 4.4905 | 0.00089505 | -0.042491 |  | LF | Bldg | 4160 | 0.676 | 4080 | 0.664 | 1.1 | 1.35 | -0.010413 | 4160 | 0.676 | 4080 | 0.664 | 1.1 | 1.35 | -0.0104
LFBldgSCENrsExCZ10 | Com-Iltg-dWatt-LF_OSbldg | SCE | Nrs | Ex | CZ10 | 4.1541 | 0.00067509 | 0 | 4.5041 | 0.00090976 | -0.043141 | 4.0805 | 0.00066405 | 0 | 4.4305 | 0.00089505 | -0.042497 |  | LF | Bldg | 4150 | 0.675 | 4080 | 0.664 | 1.09 | 1.35 | -0.010415 | 4150 | 0.675 | 4080 | 0.664 | 1.09 | 1.35 | -0.0104
LFBldgSCENrsExCZ13 | Com-Iltg-dWatt-LF_OSbldg | SCE | Nrs | Ex | CZ13 | 4.1552 | 0.00067526 | 0 | 4.4552 | 0.000898 | -0.050246 | 4.0804 | 0.00066404 | 0 | 4.3898 | 0.00088304 | -0.049404 |  | LF | Bldg | 4160 | 0.675 | 4080 | 0.664 | 1.08 | 1.33 | -0.012108 | 4160 | 0.675 | 4080 | 0.664 | 1.08 | 1.33 | -0.0121
LFBldgSCENrsExCZ14 | Com-Iltg-dWatt-LF_OSbldg | SCE | Nrs | Ex | CZ14 | 4.1547 | 0.00067517 | 0 | 4.4739 | 0.00089493 | -0.051439 | 4.0805 | 0.00066405 | 0 | 4.3998 | 0.0008801 | -0.050605 |  | LF | Bldg | 4150 | 0.675 | 4080 | 0.664 | 1.08 | 1.33 | -0.012402 | 4150 | 0.675 | 4080 | 0.664 | 1.08 | 1.33 | -0.0124
LFBldgSCENrsExCZ15 | Com-Iltg-dWatt-LF_OSbldg | SCE | Nrs | Ex | CZ15 | 4.1543 | 0.00067511 | 0 | 4.8235 | 0.00091579 | -0.026068 | 4.0808 | 0.00066408 | 0 | 4.75 | 0.00090016 | -0.0257 |  | LF | Bldg | 4150 | 0.675 | 4080 | 0.664 | 1.16 | 1.36 | -0.0062978 | 4150 | 0.675 | 4080 | 0.664 | 1.16 | 1.36 | -0.0063
LFBldgSCENrsExCZ16 | Com-Iltg-dWatt-LF_OSbldg | SCE | Nrs | Ex | CZ16 | 4.1547 | 0.00067517 | 0 | 4.1147 | 0.00085694 | -0.074309 | 4.0808 | 0.00066408 | 0 | 4.05 | 0.00084215 | -0.073108 |  | LF | Bldg | 4150 | 0.675 | 4080 | 0.664 | 0.992 | 1.27 | -0.017915 | 4150 | 0.675 | 4080 | 0.664 | 0.992 | 1.27 | -0.0179
LFBldgSCENrsExIOU | Com-Iltg-dWatt-LF_OSbldg | SCE | Nrs | Ex | IOU | 4.1607 | 0.00067617 | 0 | 4.5266 | 0.00089077 | -0.044032 | 4.0805 | 0.00066405 | 0 | 4.4485 | 0.0008749 | -0.043292 |  | LF | Bldg | 4160 | 0.676 | 4080 | 0.664 | 1.09 | 1.32 | -0.01061 | 4160 | 0.676 | 4080 | 0.664 | 1.09 | 1.32 | -0.0106
LFBldgSCENrsNewCZ05 | Com-Iltg-dWatt-LF_OSbldg | SCE | Nrs | New | CZ05 | 4.09 | 0.000665 | 0 | 3.97 | 0.000812 | -0.0736 | 4.09 | 0.000665 | 0 | 3.97 | 0.000812 | -0.0736 |  | LF | Bldg | 4090 | 0.665 | 4090 | 0.665 | 0.971 | 1.22 | -0.017995 | 4090 | 0.665 | 4090 | 0.665 | 0.971 | 1.22 | -0.018
LFBldgSCENrsNewCZ06 | Com-Iltg-dWatt-LF_OSbldg | SCE | Nrs | New | CZ06 | 4.09 | 0.000665 | 0 | 4.22 | 0.000852 | -0.047 | 4.09 | 0.000665 | 0 | 4.22 | 0.000852 | -0.047 |  | LF | Bldg | 4090 | 0.665 | 4090 | 0.665 | 1.03 | 1.28 | -0.011491 | 4090 | 0.665 | 4090 | 0.665 | 1.03 | 1.28 | -0.0115
LFBldgSCENrsNewCZ08 | Com-Iltg-dWatt-LF_OSbldg | SCE | Nrs | New | CZ08 | 4.09 | 0.000665 | 0 | 4.31 | 0.000857 | -0.0442 | 4.09 | 0.000665 | 0 | 4.31 | 0.000857 | -0.0442 |  | LF | Bldg | 4090 | 0.665 | 4090 | 0.665 | 1.05 | 1.29 | -0.010807 | 4090 | 0.665 | 4090 | 0.665 | 1.05 | 1.29 | -0.0108
LFBldgSCENrsNewCZ09 | Com-Iltg-dWatt-LF_OSbldg | SCE | Nrs | New | CZ09 | 4.09 | 0.000665 | 0 | 4.34 | 0.00089 | -0.045 | 4.09 | 0.000665 | 0 | 4.34 | 0.00089 | -0.045 |  | LF | Bldg | 4090 | 0.665 | 4090 | 0.665 | 1.06 | 1.34 | -0.011002 | 4090 | 0.665 | 4090 | 0.665 | 1.06 | 1.34 | -0.011
LFBldgSCENrsNewCZ10 | Com-Iltg-dWatt-LF_OSbldg | SCE | Nrs | New | CZ10 | 4.09 | 0.000665 | 0 | 4.36 | 0.000892 | -0.0417 | 4.09 | 0.000665 | 0 | 4.36 | 0.000892 | -0.0417 |  | LF | Bldg | 4090 | 0.665 | 4090 | 0.665 | 1.07 | 1.34 | -0.010196 | 4090 | 0.665 | 4090 | 0.665 | 1.07 | 1.34 | -0.0102
LFBldgSCENrsNewCZ13 | Com-Iltg-dWatt-LF_OSbldg | SCE | Nrs | New | CZ13 | 4.09 | 0.000665 | 0 | 4.32 | 0.000884 | -0.0536 | 4.09 | 0.000665 | 0 | 4.32 | 0.000884 | -0.0536 |  | LF | Bldg | 4090 | 0.665 | 4090 | 0.665 | 1.06 | 1.33 | -0.013105 | 4090 | 0.665 | 4090 | 0.665 | 1.06 | 1.33 | -0.0131
LFBldgSCENrsNewCZ14 | Com-Iltg-dWatt-LF_OSbldg | SCE | Nrs | New | CZ14 | 4.09 | 0.000665 | 0 | 4.32 | 0.000865 | -0.0552 | 4.09 | 0.000665 | 0 | 4.32 | 0.000865 | -0.0552 |  | LF | Bldg | 4090 | 0.665 | 4090 | 0.665 | 1.06 | 1.3 | -0.013496 | 4090 | 0.665 | 4090 | 0.665 | 1.06 | 1.3 | -0.0135
LFBldgSCENrsNewCZ15 | Com-Iltg-dWatt-LF_OSbldg | SCE | Nrs | New | CZ15 | 4.09 | 0.000665 | 0 | 4.7 | 0.000887 | -0.0254 | 4.09 | 0.000665 | 0 | 4.7 | 0.000887 | -0.0254 |  | LF | Bldg | 4090 | 0.665 | 4090 | 0.665 | 1.15 | 1.33 | -0.0062103 | 4090 | 0.665 | 4090 | 0.665 | 1.15 | 1.33 | -0.00621
LFBldgSCENrsNewCZ16 | Com-Iltg-dWatt-LF_OSbldg | SCE | Nrs | New | CZ16 | 4.09 | 0.000665 | 0 | 3.99 | 0.000835 | -0.0793 | 4.09 | 0.000665 | 0 | 3.99 | 0.000835 | -0.0793 |  | LF | Bldg | 4090 | 0.665 | 4090 | 0.665 | 0.976 | 1.26 | -0.019389 | 4090 | 0.665 | 4090 | 0.665 | 0.976 | 1.26 | -0.0194
LFBldgSCENrsNewIOU | Com-Iltg-dWatt-LF_OSbldg | SCE | Nrs | New | IOU | 4.09 | 0.000665 | 0 | 4.3143 | 0.00087097 | -0.045575 | 4.09 | 0.000665 | 0 | 4.3143 | 0.00087097 | -0.045575 |  | LF | Bldg | 4090 | 0.665 | 4090 | 0.665 | 1.05 | 1.31 | -0.011143 | 4090 | 0.665 | 4090 | 0.665 | 1.05 | 1.31 | -0.0111
LFBldgSCEOfLExCZ05 | Com-Iltg-dWatt-LF_OSbldg | SCE | OfL | Ex | CZ05 | 2.6496 | 0.00071234 | 0 | 2.9709 | 0.00090996 | -0.018273 | 2.49 | 0.00067298 | 0 | 2.79 | 0.00085986 | -0.0172 |  | LF | Bldg | 2650 | 0.712 | 2490 | 0.673 | 1.12 | 1.28 | -0.0069076 | 2650 | 0.712 | 2490 | 0.673 | 1.12 | 1.28 | -0.00691
LFBldgSCEOfLExCZ06 | Com-Iltg-dWatt-LF_OSbldg | SCE | OfL | Ex | CZ06 | 2.6487 | 0.00071212 | 0 | 3.0996 | 0.00093673 | -0.011841 | 2.49 | 0.00067297 | 0 | 2.9189 | 0.00088497 | -0.0111 |  | LF | Bldg | 2650 | 0.712 | 2490 | 0.673 | 1.17 | 1.32 | -0.0044578 | 2650 | 0.712 | 2490 | 0.673 | 1.17 | 1.32 | -0.00446
LFBldgSCEOfLExCZ08 | Com-Iltg-dWatt-LF_OSbldg | SCE | OfL | Ex | CZ08 | 2.6485 | 0.00071207 | 0 | 3.1194 | 0.00094575 | -0.01174 | 2.49 | 0.00067297 | 0 | 2.93 | 0.00089397 | -0.011 |  | LF | Bldg | 2650 | 0.712 | 2490 | 0.673 | 1.18 | 1.33 | -0.0044177 | 2650 | 0.712 | 2490 | 0.673 | 1.18 | 1.33 | -0.00442
LFBldgSCEOfLExCZ09 | Com-Iltg-dWatt-LF_OSbldg | SCE | OfL | Ex | CZ09 | 2.6452 | 0.00071125 | 0 | 3.0963 | 0.00095985 | -0.01372 | 2.49 | 0.00067296 | 0 | 2.9196 | 0.00090892 | -0.0129 |  | LF | Bldg | 2650 | 0.711 | 2490 | 0.673 | 1.17 | 1.35 | -0.0051807 | 2650 | 0.711 | 2490 | 0.673 | 1.17 | 1.35 | -0.00518
LFBldgSCEOfLExCZ10 | Com-Iltg-dWatt-LF_OSbldg | SCE | OfL | Ex | CZ10 | 2.6265 | 0.00070664 | 0 | 3.0647 | 0.00094347 | -0.011137 | 2.49 | 0.00067297 | 0 | 2.91 | 0.00089888 | -0.0105 |  | LF | Bldg | 2630 | 0.707 | 2490 | 0.673 | 1.17 | 1.34 | -0.0042169 | 2630 | 0.707 | 2490 | 0.673 | 1.17 | 1.34 | -0.00422
LFBldgSCEOfLExCZ13 | Com-Iltg-dWatt-LF_OSbldg | SCE | OfL | Ex | CZ13 | 2.6288 | 0.00070722 | 0 | 3.0466 | 0.00092733 | -0.015833 | 2.49 | 0.00067297 | 0 | 2.88 | 0.0008829 | -0.015 |  | LF | Bldg | 2630 | 0.707 | 2490 | 0.673 | 1.16 | 1.31 | -0.0060241 | 2630 | 0.707 | 2490 | 0.673 | 1.16 | 1.31 | -0.00602
LFBldgSCEOfLExCZ14 | Com-Iltg-dWatt-LF_OSbldg | SCE | OfL | Ex | CZ14 | 2.6293 | 0.00070735 | 0 | 3.0377 | 0.00094543 | -0.014543 | 2.49 | 0.00067298 | 0 | 2.8798 | 0.0008999 | -0.0138 |  | LF | Bldg | 2630 | 0.707 | 2490 | 0.673 | 1.16 | 1.34 | -0.0055422 | 2630 | 0.707 | 2490 | 0.673 | 1.16 | 1.34 | -0.00554
LFBldgSCEOfLExCZ15 | Com-Iltg-dWatt-LF_OSbldg | SCE | OfL | Ex | CZ15 | 2.6265 | 0.00070658 | 0 | 3.2229 | 0.0009415 | -0.0069631 | 2.49 | 0.00067291 | 0 | 3.0591 | 0.00089782 | -0.0066082 |  | LF | Bldg | 2630 | 0.707 | 2490 | 0.673 | 1.23 | 1.33 | -0.0026539 | 2630 | 0.707 | 2490 | 0.673 | 1.23 | 1.33 | -0.00265
LFBldgSCEOfLExCZ16 | Com-Iltg-dWatt-LF_OSbldg | SCE | OfL | Ex | CZ16 | 2.6296 | 0.00070736 | 0 | 2.8282 | 0.00090067 | -0.026589 | 2.49 | 0.00067293 | 0 | 2.6793 | 0.00085693 | -0.025193 |  | LF | Bldg | 2630 | 0.707 | 2490 | 0.673 | 1.08 | 1.27 | -0.010118 | 2630 | 0.707 | 2490 | 0.673 | 1.08 | 1.27 | -0.0101
LFBldgSCEOfLExIOU | Com-Iltg-dWatt-LF_OSbldg | SCE | OfL | Ex | IOU | 2.6449 | 0.00071118 | 0 | 3.1014 | 0.00094518 | -0.012276 | 2.49 | 0.00067297 | 0 | 2.9218 | 0.0008946 | -0.011528 |  | LF | Bldg | 2640 | 0.711 | 2490 | 0.673 | 1.17 | 1.33 | -0.0046298 | 2640 | 0.711 | 2490 | 0.673 | 1.17 | 1.33 | -0.00463
LFBldgSCEOfLNewCZ05 | Com-Iltg-dWatt-LF_OSbldg | SCE | OfL | New | CZ05 | 2.49 | 0.000672 | 0 | 2.79 | 0.000837 | -0.00774 | 2.49 | 0.000672 | 0 | 2.79 | 0.000837 | -0.00774 |  | LF | Bldg | 2490 | 0.672 | 2490 | 0.672 | 1.12 | 1.25 | -0.0031084 | 2490 | 0.672 | 2490 | 0.672 | 1.12 | 1.25 | -0.00311
LFBldgSCEOfLNewCZ06 | Com-Iltg-dWatt-LF_OSbldg | SCE | OfL | New | CZ06 | 2.49 | 0.000672 | 0 | 2.9 | 0.000852 | -0.00458 | 2.49 | 0.000672 | 0 | 2.9 | 0.000852 | -0.00458 |  | LF | Bldg | 2490 | 0.672 | 2490 | 0.672 | 1.16 | 1.27 | -0.0018394 | 2490 | 0.672 | 2490 | 0.672 | 1.16 | 1.27 | -0.00184
LFBldgSCEOfLNewCZ08 | Com-Iltg-dWatt-LF_OSbldg | SCE | OfL | New | CZ08 | 2.49 | 0.000672 | 0 | 2.91 | 0.000862 | -0.00418 | 2.49 | 0.000672 | 0 | 2.91 | 0.000862 | -0.00418 |  | LF | Bldg | 2490 | 0.672 | 2490 | 0.672 | 1.17 | 1.28 | -0.0016787 | 2490 | 0.672 | 2490 | 0.672 | 1.17 | 1.28 | -0.00168
LFBldgSCEOfLNewCZ09 | Com-Iltg-dWatt-LF_OSbldg | SCE | OfL | New | CZ09 | 2.49 | 0.000672 | 0 | 2.91 | 0.000884 | -0.00597 | 2.49 | 0.000672 | 0 | 2.91 | 0.000884 | -0.00597 |  | LF | Bldg | 2490 | 0.672 | 2490 | 0.672 | 1.17 | 1.32 | -0.0023976 | 2490 | 0.672 | 2490 | 0.672 | 1.17 | 1.32 | -0.0024
LFBldgSCEOfLNewCZ10 | Com-Iltg-dWatt-LF_OSbldg | SCE | OfL | New | CZ10 | 2.49 | 0.000672 | 0 | 2.93 | 0.000888 | -0.0047 | 2.49 | 0.000672 | 0 | 2.93 | 0.000888 | -0.0047 |  | LF | Bldg | 2490 | 0.672 | 2490 | 0.672 | 1.18 | 1.32 | -0.0018876 | 2490 | 0.672 | 2490 | 0.672 | 1.18 | 1.32 | -0.00189
LFBldgSCEOfLNewCZ13 | Com-Iltg-dWatt-LF_OSbldg | SCE | OfL | New | CZ13 | 2.49 | 0.000672 | 0 | 2.87 | 0.000872 | -0.00744 | 2.49 | 0.000672 | 0 | 2.87 | 0.000872 | -0.00744 |  | LF | Bldg | 2490 | 0.672 | 2490 | 0.672 | 1.15 | 1.3 | -0.002988 | 2490 | 0.672 | 2490 | 0.672 | 1.15 | 1.3 | -0.00299
LFBldgSCEOfLNewCZ14 | Com-Iltg-dWatt-LF_OSbldg | SCE | OfL | New | CZ14 | 2.49 | 0.000672 | 0 | 2.89 | 0.000891 | -0.0057 | 2.49 | 0.000672 | 0 | 2.89 | 0.000891 | -0.0057 |  | LF | Bldg | 2490 | 0.672 | 2490 | 0.672 | 1.16 | 1.33 | -0.0022892 | 2490 | 0.672 | 2490 | 0.672 | 1.16 | 1.33 | -0.00229
LFBldgSCEOfLNewCZ15 | Com-Iltg-dWatt-LF_OSbldg | SCE | OfL | New | CZ15 | 2.49 | 0.000672 | 0 | 3.05 | 0.000887 | -0.00261 | 2.49 | 0.000672 | 0 | 3.05 | 0.000887 | -0.00261 |  | LF | Bldg | 2490 | 0.672 | 2490 | 0.672 | 1.22 | 1.32 | -0.0010482 | 2490 | 0.672 | 2490 | 0.672 | 1.22 | 1.32 | -0.00105
LFBldgSCEOfLNewCZ16 | Com-Iltg-dWatt-LF_OSbldg | SCE | OfL | New | CZ16 | 2.49 | 0.000672 | 0 | 2.71 | 0.000848 | -0.0171 | 2.49 | 0.000672 | 0 | 2.71 | 0.000848 | -0.0171 |  | LF | Bldg | 2490 | 0.672 | 2490 | 0.672 | 1.09 | 1.26 | -0.0068675 | 2490 | 0.672 | 2490 | 0.672 | 1.09 | 1.26 | -0.00687
LFBldgSCEOfLNewIOU | Com-Iltg-dWatt-LF_OSbldg | SCE | OfL | New | IOU | 2.49 | 0.000672 | 0 | 2.9147 | 0.00087235 | -0.0050049 | 2.49 | 0.000672 | 0 | 2.9147 | 0.00087235 | -0.0050049 |  | LF | Bldg | 2490 | 0.672 | 2490 | 0.672 | 1.17 | 1.3 | -0.00201 | 2490 | 0.672 | 2490 | 0.672 | 1.17 | 1.3 | -0.00201
LFBldgSCEOfSExCZ05 | Com-Iltg-dWatt-LF_OSbldg | SCE | OfS | Ex | CZ05 | 2.6675 | 0.00071296 | 0 | 2.9335 | 0.00089185 | -0.0083285 | 2.25 | 0.00060805 | 0 | 2.47 | 0.00076038 | -0.0070138 |  | LF | Bldg | 2670 | 0.713 | 2250 | 0.608 | 1.1 | 1.25 | -0.0031173 | 2670 | 0.713 | 2250 | 0.608 | 1.1 | 1.25 | -0.00312
LFBldgSCEOfSExCZ06 | Com-Iltg-dWatt-LF_OSbldg | SCE | OfS | Ex | CZ06 | 2.6668 | 0.00071278 | 0 | 3.0677 | 0.00090279 | -0.004056 | 2.25 | 0.00060805 | 0 | 2.5833 | 0.00077005 | -0.00342 |  | LF | Bldg | 2670 | 0.713 | 2250 | 0.608 | 1.15 | 1.27 | -0.00152 | 2670 | 0.713 | 2250 | 0.608 | 1.15 | 1.27 | -0.00152
LFBldgSCEOfSExCZ08 | Com-Iltg-dWatt-LF_OSbldg | SCE | OfS | Ex | CZ08 | 2.6666 | 0.00071275 | 0 | 3.087 | 0.0009097 | -0.0037671 | 2.25 | 0.00060805 | 0 | 2.6 | 0.00077605 | -0.0031706 |  | LF | Bldg | 2670 | 0.713 | 2250 | 0.608 | 1.16 | 1.28 | -0.0014091 | 2670 | 0.713 | 2250 | 0.608 | 1.16 | 1.28 | -0.00141
LFBldgSCEOfSExCZ09 | Com-Iltg-dWatt-LF_OSbldg | SCE | OfS | Ex | CZ09 | 2.6638 | 0.00071205 | 0 | 3.0643 | 0.00091934 | -0.0045635 | 2.25 | 0.00060805 | 0 | 2.59 | 0.00078337 | -0.0038432 |  | LF | Bldg | 2660 | 0.712 | 2250 | 0.608 | 1.15 | 1.29 | -0.0017081 | 2660 | 0.712 | 2250 | 0.608 | 1.15 | 1.29 | -0.00171
LFBldgSCEOfSExCZ10 | Com-Iltg-dWatt-LF_OSbldg | SCE | OfS | Ex | CZ10 | 2.5807 | 0.00069159 | 0 | 2.9287 | 0.00088284 | -0.0041049 | 2.25 | 0.00060809 | 0 | 2.55 | 0.00077609 | -0.0035715 |  | LF | Bldg | 2580 | 0.692 | 2250 | 0.608 | 1.13 | 1.28 | -0.0015873 | 2580 | 0.692 | 2250 | 0.608 | 1.13 | 1.28 | -0.00159
LFBldgSCEOfSExCZ13 | Com-Iltg-dWatt-LF_OSbldg | SCE | OfS | Ex | CZ13 | 2.5838 | 0.00069238 | 0 | 2.8726 | 0.00087793 | -0.0099639 | 2.25 | 0.00060806 | 0 | 2.5 | 0.00077106 | -0.0086516 |  | LF | Bldg | 2580 | 0.692 | 2250 | 0.608 | 1.11 | 1.27 | -0.0038451 | 2580 | 0.692 | 2250 | 0.608 | 1.11 | 1.27 | -0.00385
LFBldgSCEOfSExCZ14 | Com-Iltg-dWatt-LF_OSbldg | SCE | OfS | Ex | CZ14 | 2.5815 | 0.00069181 | 0 | 2.88 | 0.00089425 | -0.0076539 | 2.25 | 0.00060808 | 0 | 2.5008 | 0.00078521 | -0.0066521 |  | LF | Bldg | 2580 | 0.692 | 2250 | 0.608 | 1.11 | 1.29 | -0.0029565 | 2580 | 0.692 | 2250 | 0.608 | 1.11 | 1.29 | -0.00296
LFBldgSCEOfSExCZ15 | Com-Iltg-dWatt-LF_OSbldg | SCE | OfS | Ex | CZ15 | 2.5604 | 0.0006866 | 0 | 3.0934 | 0.0008746 | -0.0012452 | 2.25 | 0.00060809 | 0 | 2.71 | 0.00077417 | -0.00109 |  | LF | Bldg | 2560 | 0.687 | 2250 | 0.608 | 1.2 | 1.27 | -0.00048444 | 2560 | 0.687 | 2250 | 0.608 | 1.2 | 1.27 | -0.000484
LFBldgSCEOfSExCZ16 | Com-Iltg-dWatt-LF_OSbldg | SCE | OfS | Ex | CZ16 | 2.5659 | 0.00068798 | 0 | 2.5859 | 0.00085449 | -0.018723 | 2.25 | 0.00060807 | 0 | 2.27 | 0.00075507 | -0.0164 |  | LF | Bldg | 2570 | 0.688 | 2250 | 0.608 | 1.01 | 1.24 | -0.0072889 | 2570 | 0.688 | 2250 | 0.608 | 1.01 | 1.24 | -0.00729
LFBldgSCEOfSExIOU | Com-Iltg-dWatt-LF_OSbldg | SCE | OfS | Ex | IOU | 2.6342 | 0.00070478 | 0 | 3.0217 | 0.00089902 | -0.0045475 | 2.25 | 0.00060806 | 0 | 2.5771 | 0.00077529 | -0.0038855 |  | LF | Bldg | 2630 | 0.705 | 2250 | 0.608 | 1.15 | 1.28 | -0.0017269 | 2630 | 0.705 | 2250 | 0.608 | 1.15 | 1.28 | -0.00173
LFBldgSCEOfSNewCZ05 | Com-Iltg-dWatt-LF_OSbldg | SCE | OfS | New | CZ05 | 2.25 | 0.000609 | 0 | 2.38 | 0.000752 | -0.00574 | 2.25 | 0.000609 | 0 | 2.38 | 0.000752 | -0.00574 |  | LF | Bldg | 2250 | 0.609 | 2250 | 0.609 | 1.06 | 1.23 | -0.0025511 | 2250 | 0.609 | 2250 | 0.609 | 1.06 | 1.23 | -0.00255
LFBldgSCEOfSNewCZ06 | Com-Iltg-dWatt-LF_OSbldg | SCE | OfS | New | CZ06 | 2.25 | 0.000609 | 0 | 2.51 | 0.000759 | -0.0023 | 2.25 | 0.000609 | 0 | 2.51 | 0.000759 | -0.0023 |  | LF | Bldg | 2250 | 0.609 | 2250 | 0.609 | 1.12 | 1.25 | -0.0010222 | 2250 | 0.609 | 2250 | 0.609 | 1.12 | 1.25 | -0.00102
LFBldgSCEOfSNewCZ08 | Com-Iltg-dWatt-LF_OSbldg | SCE | OfS | New | CZ08 | 2.25 | 0.000609 | 0 | 2.53 | 0.000771 | -0.00207 | 2.25 | 0.000609 | 0 | 2.53 | 0.000771 | -0.00207 |  | LF | Bldg | 2250 | 0.609 | 2250 | 0.609 | 1.12 | 1.27 | -0.00092 | 2250 | 0.609 | 2250 | 0.609 | 1.12 | 1.27 | -0.00092
LFBldgSCEOfSNewCZ09 | Com-Iltg-dWatt-LF_OSbldg | SCE | OfS | New | CZ09 | 2.25 | 0.000609 | 0 | 2.52 | 0.00079 | -0.00227 | 2.25 | 0.000609 | 0 | 2.52 | 0.00079 | -0.00227 |  | LF | Bldg | 2250 | 0.609 | 2250 | 0.609 | 1.12 | 1.3 | -0.0010089 | 2250 | 0.609 | 2250 | 0.609 | 1.12 | 1.3 | -0.00101
LFBldgSCEOfSNewCZ10 | Com-Iltg-dWatt-LF_OSbldg | SCE | OfS | New | CZ10 | 2.25 | 0.000609 | 0 | 2.55 | 0.000799 | -0.00164 | 2.25 | 0.000609 | 0 | 2.55 | 0.000799 | -0.00164 |  | LF | Bldg | 2250 | 0.609 | 2250 | 0.609 | 1.13 | 1.31 | -0.00072889 | 2250 | 0.609 | 2250 | 0.609 | 1.13 | 1.31 | -0.000729
LFBldgSCEOfSNewCZ13 | Com-Iltg-dWatt-LF_OSbldg | SCE | OfS | New | CZ13 | 2.25 | 0.000609 | 0 | 2.48 | 0.000787 | -0.00642 | 2.25 | 0.000609 | 0 | 2.48 | 0.000787 | -0.00642 |  | LF | Bldg | 2250 | 0.609 | 2250 | 0.609 | 1.1 | 1.29 | -0.0028533 | 2250 | 0.609 | 2250 | 0.609 | 1.1 | 1.29 | -0.00285
LFBldgSCEOfSNewCZ14 | Com-Iltg-dWatt-LF_OSbldg | SCE | OfS | New | CZ14 | 2.25 | 0.000609 | 0 | 2.49 | 0.000798 | -0.00514 | 2.25 | 0.000609 | 0 | 2.49 | 0.000798 | -0.00514 |  | LF | Bldg | 2250 | 0.609 | 2250 | 0.609 | 1.11 | 1.31 | -0.0022844 | 2250 | 0.609 | 2250 | 0.609 | 1.11 | 1.31 | -0.00228
LFBldgSCEOfSNewCZ15 | Com-Iltg-dWatt-LF_OSbldg | SCE | OfS | New | CZ15 | 2.25 | 0.000609 | 0 | 2.67 | 0.000807 | -0.000148 | 2.25 | 0.000609 | 0 | 2.67 | 0.000807 | -0.000148 |  | LF | Bldg | 2250 | 0.609 | 2250 | 0.609 | 1.19 | 1.33 | -6.5778e-05 | 2250 | 0.609 | 2250 | 0.609 | 1.19 | 1.33 | -6.58e-05
LFBldgSCEOfSNewCZ16 | Com-Iltg-dWatt-LF_OSbldg | SCE | OfS | New | CZ16 | 2.25 | 0.000609 | 0 | 2.27 | 0.000759 | -0.0148 | 2.25 | 0.000609 | 0 | 2.27 | 0.000759 | -0.0148 |  | LF | Bldg | 2250 | 0.609 | 2250 | 0.609 | 1.01 | 1.25 | -0.0065778 | 2250 | 0.609 | 2250 | 0.609 | 1.01 | 1.25 | -0.00658
LFBldgSCEOfSNewIOU | Com-Iltg-dWatt-LF_OSbldg | SCE | OfS | New | IOU | 2.25 | 0.000609 | 0 | 2.533 | 0.00078326 | -0.0024078 | 2.25 | 0.000609 | 0 | 2.533 | 0.00078326 | -0.0024078 |  | LF | Bldg | 2250 | 0.609 | 2250 | 0.609 | 1.13 | 1.29 | -0.0010702 | 2250 | 0.609 | 2250 | 0.609 | 1.13 | 1.29 | -0.00107
LFBldgSCERFFExCZ05 | Com-Iltg-dWatt-LF_OSbldg | SCE | RFF | Ex | CZ05 | 4.8436 | 0.00081371 | 0 | 5.0336 | 0.00097471 | -0.049936 | 4.8436 | 0.00081371 | 0 | 5.0336 | 0.00097471 | -0.049936 |  | LF | Bldg | 4840 | 0.814 | 4840 | 0.814 | 1.04 | 1.2 | -0.01031 | 4840 | 0.814 | 4840 | 0.814 | 1.04 | 1.2 | -0.0103
LFBldgSCERFFExCZ06 | Com-Iltg-dWatt-LF_OSbldg | SCE | RFF | Ex | CZ06 | 4.8436 | 0.00081371 | 0 | 5.2971 | 0.00099507 | -0.027236 | 4.8436 | 0.00081371 | 0 | 5.2971 | 0.00099507 | -0.027236 |  | LF | Bldg | 4840 | 0.814 | 4840 | 0.814 | 1.09 | 1.22 | -0.0056231 | 4840 | 0.814 | 4840 | 0.814 | 1.09 | 1.22 | -0.00562
LFBldgSCERFFExCZ08 | Com-Iltg-dWatt-LF_OSbldg | SCE | RFF | Ex | CZ08 | 4.8436 | 0.00081371 | 0 | 5.3536 | 0.00098707 | -0.024136 | 4.8436 | 0.00081371 | 0 | 5.3536 | 0.00098707 | -0.024136 |  | LF | Bldg | 4840 | 0.814 | 4840 | 0.814 | 1.11 | 1.21 | -0.004983 | 4840 | 0.814 | 4840 | 0.814 | 1.11 | 1.21 | -0.00498
LFBldgSCERFFExCZ09 | Com-Iltg-dWatt-LF_OSbldg | SCE | RFF | Ex | CZ09 | 4.8436 | 0.00081372 | 0 | 5.3636 | 0.00101 | -0.025 | 4.8436 | 0.00081372 | 0 | 5.3636 | 0.00101 | -0.025 |  | LF | Bldg | 4840 | 0.814 | 4840 | 0.814 | 1.11 | 1.24 | -0.0051614 | 4840 | 0.814 | 4840 | 0.814 | 1.11 | 1.24 | -0.00516
LFBldgSCERFFExCZ10 | Com-Iltg-dWatt-LF_OSbldg | SCE | RFF | Ex | CZ10 | 4.8419 | 0.00081338 | 0 | 5.2519 | 0.00099138 | -0.0278 | 4.8419 | 0.00081338 | 0 | 5.2519 | 0.00099138 | -0.0278 |  | LF | Bldg | 4840 | 0.813 | 4840 | 0.813 | 1.08 | 1.22 | -0.0057416 | 4840 | 0.813 | 4840 | 0.813 | 1.08 | 1.22 | -0.00574
LFBldgSCERFFExCZ13 | Com-Iltg-dWatt-LF_OSbldg | SCE | RFF | Ex | CZ13 | 4.8411 | 0.00081322 | 0 | 5.2411 | 0.00099822 | -0.0372 | 4.8411 | 0.00081322 | 0 | 5.2411 | 0.00099822 | -0.0372 |  | LF | Bldg | 4840 | 0.813 | 4840 | 0.813 | 1.08 | 1.23 | -0.0076842 | 4840 | 0.813 | 4840 | 0.813 | 1.08 | 1.23 | -0.00768
LFBldgSCERFFExCZ14 | Com-Iltg-dWatt-LF_OSbldg | SCE | RFF | Ex | CZ14 | 4.8417 | 0.00081333 | 0 | 5.2017 | 0.00101 | -0.0392 | 4.8417 | 0.00081333 | 0 | 5.2017 | 0.00101 | -0.0392 |  | LF | Bldg | 4840 | 0.813 | 4840 | 0.813 | 1.07 | 1.24 | -0.0080964 | 4840 | 0.813 | 4840 | 0.813 | 1.07 | 1.24 | -0.0081
LFBldgSCERFFExCZ15 | Com-Iltg-dWatt-LF_OSbldg | SCE | RFF | Ex | CZ15 | 4.84 | 0.000813 | 0 | 5.59 | 0.001 | -0.0128 | 4.84 | 0.000813 | 0 | 5.59 | 0.001 | -0.0128 |  | LF | Bldg | 4840 | 0.813 | 4840 | 0.813 | 1.15 | 1.23 | -0.0026446 | 4840 | 0.813 | 4840 | 0.813 | 1.15 | 1.23 | -0.00264
LFBldgSCERFFExCZ16 | Com-Iltg-dWatt-LF_OSbldg | SCE | RFF | Ex | CZ16 | 4.84 | 0.000813 | 0 | 4.84 | 0.000974 | -0.0711 | 4.84 | 0.000813 | 0 | 4.84 | 0.000974 | -0.0711 |  | LF | Bldg | 4840 | 0.813 | 4840 | 0.813 | 1 | 1.2 | -0.01469 | 4840 | 0.813 | 4840 | 0.813 | 1 | 1.2 | -0.0147
LFBldgSCERFFExIOU | Com-Iltg-dWatt-LF_OSbldg | SCE | RFF | Ex | IOU | 4.8428 | 0.00081357 | 0 | 5.3097 | 0.00099485 | -0.027211 | 4.8428 | 0.00081357 | 0 | 5.3097 | 0.00099485 | -0.027211 |  | LF | Bldg | 4840 | 0.814 | 4840 | 0.814 | 1.1 | 1.22 | -0.0056189 | 4840 | 0.814 | 4840 | 0.814 | 1.1 | 1.22 | -0.00562
LFBldgSCERFFNewCZ05 | Com-Iltg-dWatt-LF_OSbldg | SCE | RFF | New | CZ05 | 4.85 | 0.000815 | 0 | 4.99 | 0.000994 | -0.049 | 4.85 | 0.000815 | 0 | 4.99 | 0.000994 | -0.049 |  | LF | Bldg | 4850 | 0.815 | 4850 | 0.815 | 1.03 | 1.22 | -0.010103 | 4850 | 0.815 | 4850 | 0.815 | 1.03 | 1.22 | -0.0101
LFBldgSCERFFNewCZ06 | Com-Iltg-dWatt-LF_OSbldg | SCE | RFF | New | CZ06 | 4.85 | 0.000815 | 0 | 5.24 | 0.00102 | -0.0266 | 4.85 | 0.000815 | 0 | 5.24 | 0.00102 | -0.0266 |  | LF | Bldg | 4850 | 0.815 | 4850 | 0.815 | 1.08 | 1.25 | -0.0054845 | 4850 | 0.815 | 4850 | 0.815 | 1.08 | 1.25 | -0.00548
LFBldgSCERFFNewCZ08 | Com-Iltg-dWatt-LF_OSbldg | SCE | RFF | New | CZ08 | 4.85 | 0.000815 | 0 | 5.32 | 0.00103 | -0.0289 | 4.85 | 0.000815 | 0 | 5.32 | 0.00103 | -0.0289 |  | LF | Bldg | 4850 | 0.815 | 4850 | 0.815 | 1.1 | 1.26 | -0.0059588 | 4850 | 0.815 | 4850 | 0.815 | 1.1 | 1.26 | -0.00596
LFBldgSCERFFNewCZ09 | Com-Iltg-dWatt-LF_OSbldg | SCE | RFF | New | CZ09 | 4.85 | 0.000815 | 0 | 5.35 | 0.00106 | -0.0311 | 4.85 | 0.000815 | 0 | 5.35 | 0.00106 | -0.0311 |  | LF | Bldg | 4850 | 0.815 | 4850 | 0.815 | 1.1 | 1.3 | -0.0064124 | 4850 | 0.815 | 4850 | 0.815 | 1.1 | 1.3 | -0.00641
LFBldgSCERFFNewCZ10 | Com-Iltg-dWatt-LF_OSbldg | SCE | RFF | New | CZ10 | 4.84 | 0.000813 | 0 | 5.37 | 0.00107 | -0.0319 | 4.84 | 0.000813 | 0 | 5.37 | 0.00107 | -0.0319 |  | LF | Bldg | 4840 | 0.813 | 4840 | 0.813 | 1.11 | 1.32 | -0.0065909 | 4840 | 0.813 | 4840 | 0.813 | 1.11 | 1.32 | -0.00659
LFBldgSCERFFNewCZ13 | Com-Iltg-dWatt-LF_OSbldg | SCE | RFF | New | CZ13 | 4.84 | 0.000813 | 0 | 5.35 | 0.00106 | -0.0429 | 4.84 | 0.000813 | 0 | 5.35 | 0.00106 | -0.0429 |  | LF | Bldg | 4840 | 0.813 | 4840 | 0.813 | 1.11 | 1.3 | -0.0088636 | 4840 | 0.813 | 4840 | 0.813 | 1.11 | 1.3 | -0.00886
LFBldgSCERFFNewCZ14 | Com-Iltg-dWatt-LF_OSbldg | SCE | RFF | New | CZ14 | 4.84 | 0.000813 | 0 | 5.34 | 0.00107 | -0.0452 | 4.84 | 0.000813 | 0 | 5.34 | 0.00107 | -0.0452 |  | LF | Bldg | 4840 | 0.813 | 4840 | 0.813 | 1.1 | 1.32 | -0.0093388 | 4840 | 0.813 | 4840 | 0.813 | 1.1 | 1.32 | -0.00934
LFBldgSCERFFNewCZ15 | Com-Iltg-dWatt-LF_OSbldg | SCE | RFF | New | CZ15 | 4.84 | 0.000813 | 0 | 5.75 | 0.00109 | -0.0157 | 4.84 | 0.000813 | 0 | 5.75 | 0.00109 | -0.0157 |  | LF | Bldg | 4840 | 0.813 | 4840 | 0.813 | 1.19 | 1.34 | -0.0032438 | 4840 | 0.813 | 4840 | 0.813 | 1.19 | 1.34 | -0.00324
LFBldgSCERFFNewCZ16 | Com-Iltg-dWatt-LF_OSbldg | SCE | RFF | New | CZ16 | 4.84 | 0.000813 | 0 | 4.91 | 0.00102 | -0.0765 | 4.84 | 0.000813 | 0 | 4.91 | 0.00102 | -0.0765 |  | LF | Bldg | 4840 | 0.813 | 4840 | 0.813 | 1.01 | 1.25 | -0.015806 | 4840 | 0.813 | 4840 | 0.813 | 1.01 | 1.25 | -0.0158
LFBldgSCERFFNewIOU | Com-Iltg-dWatt-LF_OSbldg | SCE | RFF | New | IOU | 4.8457 | 0.00081415 | 0 | 5.3362 | 0.0010483 | -0.030963 | 4.8457 | 0.00081415 | 0 | 5.3362 | 0.0010483 | -0.030963 |  | LF | Bldg | 4850 | 0.814 | 4850 | 0.814 | 1.1 | 1.29 | -0.0063898 | 4850 | 0.814 | 4850 | 0.814 | 1.1 | 1.29 | -0.00639
LFBldgSCERSDExCZ05 | Com-Iltg-dWatt-LF_OSbldg | SCE | RSD | Ex | CZ05 | 4.8302 | 0.00080005 | 0 | 5.0002 | 0.00098505 | -0.057002 | 4.8302 | 0.00080005 | 0 | 5.0002 | 0.00098505 | -0.057002 |  | LF | Bldg | 4830 | 0.8 | 4830 | 0.8 | 1.04 | 1.23 | -0.011801 | 4830 | 0.8 | 4830 | 0.8 | 1.04 | 1.23 | -0.0118
LFBldgSCERSDExCZ06 | Com-Iltg-dWatt-LF_OSbldg | SCE | RSD | Ex | CZ06 | 4.8302 | 0.00080005 | 0 | 5.3502 | 0.00099405 | -0.0296 | 4.8302 | 0.00080005 | 0 | 5.3502 | 0.00099405 | -0.0296 |  | LF | Bldg | 4830 | 0.8 | 4830 | 0.8 | 1.11 | 1.24 | -0.006128 | 4830 | 0.8 | 4830 | 0.8 | 1.11 | 1.24 | -0.00613
LFBldgSCERSDExCZ08 | Com-Iltg-dWatt-LF_OSbldg | SCE | RSD | Ex | CZ08 | 4.8302 | 0.00080005 | 0 | 5.3902 | 0.00096405 | -0.024402 | 4.8302 | 0.00080005 | 0 | 5.3902 | 0.00096405 | -0.024402 |  | LF | Bldg | 4830 | 0.8 | 4830 | 0.8 | 1.12 | 1.2 | -0.005052 | 4830 | 0.8 | 4830 | 0.8 | 1.12 | 1.2 | -0.00505
LFBldgSCERSDExCZ09 | Com-Iltg-dWatt-LF_OSbldg | SCE | RSD | Ex | CZ09 | 4.8302 | 0.00080004 | 0 | 5.3702 | 0.00097107 | -0.027602 | 4.8302 | 0.00080004 | 0 | 5.3702 | 0.00097107 | -0.027602 |  | LF | Bldg | 4830 | 0.8 | 4830 | 0.8 | 1.11 | 1.21 | -0.0057145 | 4830 | 0.8 | 4830 | 0.8 | 1.11 | 1.21 | -0.00571
LFBldgSCERSDExCZ10 | Com-Iltg-dWatt-LF_OSbldg | SCE | RSD | Ex | CZ10 | 4.8317 | 0.00080034 | 0 | 5.2917 | 0.00092251 | -0.029 | 4.8317 | 0.00080034 | 0 | 5.2917 | 0.00092251 | -0.029 |  | LF | Bldg | 4830 | 0.8 | 4830 | 0.8 | 1.1 | 1.15 | -0.006002 | 4830 | 0.8 | 4830 | 0.8 | 1.1 | 1.15 | -0.006
LFBldgSCERSDExCZ13 | Com-Iltg-dWatt-LF_OSbldg | SCE | RSD | Ex | CZ13 | 4.8321 | 0.00080043 | 0 | 5.2221 | 0.00099643 | -0.044221 | 4.8321 | 0.00080043 | 0 | 5.2221 | 0.00099643 | -0.044221 |  | LF | Bldg | 4830 | 0.8 | 4830 | 0.8 | 1.08 | 1.24 | -0.0091515 | 4830 | 0.8 | 4830 | 0.8 | 1.08 | 1.24 | -0.00915
LFBldgSCERSDExCZ14 | Com-Iltg-dWatt-LF_OSbldg | SCE | RSD | Ex | CZ14 | 4.8316 | 0.00080033 | 0 | 5.1716 | 0.00092633 | -0.047217 | 4.8316 | 0.00080033 | 0 | 5.1716 | 0.00092633 | -0.047217 |  | LF | Bldg | 4830 | 0.8 | 4830 | 0.8 | 1.07 | 1.16 | -0.0097723 | 4830 | 0.8 | 4830 | 0.8 | 1.07 | 1.16 | -0.00977
LFBldgSCERSDExCZ15 | Com-Iltg-dWatt-LF_OSbldg | SCE | RSD | Ex | CZ15 | 4.83 | 0.0008 | 0 | 5.66 | 0.00101 | -0.0116 | 4.83 | 0.0008 | 0 | 5.66 | 0.00101 | -0.0116 |  | LF | Bldg | 4830 | 0.8 | 4830 | 0.8 | 1.17 | 1.26 | -0.0024017 | 4830 | 0.8 | 4830 | 0.8 | 1.17 | 1.26 | -0.0024
LFBldgSCERSDExCZ16 | Com-Iltg-dWatt-LF_OSbldg | SCE | RSD | Ex | CZ16 | 4.83 | 0.0008 | 0 | 4.79 | 0.000946 | -0.0778 | 4.83 | 0.0008 | 0 | 4.79 | 0.000946 | -0.0778 |  | LF | Bldg | 4830 | 0.8 | 4830 | 0.8 | 0.992 | 1.18 | -0.016108 | 4830 | 0.8 | 4830 | 0.8 | 0.992 | 1.18 | -0.0161
LFBldgSCERSDExIOU | Com-Iltg-dWatt-LF_OSbldg | SCE | RSD | Ex | IOU | 4.8307 | 0.00080013 | 0 | 5.3419 | 0.00096309 | -0.029084 | 4.8307 | 0.00080013 | 0 | 5.3419 | 0.00096309 | -0.029084 |  | LF | Bldg | 4830 | 0.8 | 4830 | 0.8 | 1.11 | 1.2 | -0.0060208 | 4830 | 0.8 | 4830 | 0.8 | 1.11 | 1.2 | -0.00602
LFBldgSCERSDNewCZ05 | Com-Iltg-dWatt-LF_OSbldg | SCE | RSD | New | CZ05 | 4.83 | 0.0008 | 0 | 4.95 | 0.000998 | -0.0642 | 4.83 | 0.0008 | 0 | 4.95 | 0.000998 | -0.0642 |  | LF | Bldg | 4830 | 0.8 | 4830 | 0.8 | 1.02 | 1.25 | -0.013292 | 4830 | 0.8 | 4830 | 0.8 | 1.02 | 1.25 | -0.0133
LFBldgSCERSDNewCZ06 | Com-Iltg-dWatt-LF_OSbldg | SCE | RSD | New | CZ06 | 4.83 | 0.0008 | 0 | 5.27 | 0.00101 | -0.0357 | 4.83 | 0.0008 | 0 | 5.27 | 0.00101 | -0.0357 |  | LF | Bldg | 4830 | 0.8 | 4830 | 0.8 | 1.09 | 1.26 | -0.0073913 | 4830 | 0.8 | 4830 | 0.8 | 1.09 | 1.26 | -0.00739
LFBldgSCERSDNewCZ08 | Com-Iltg-dWatt-LF_OSbldg | SCE | RSD | New | CZ08 | 4.83 | 0.0008 | 0 | 5.34 | 0.00102 | -0.0293 | 4.83 | 0.0008 | 0 | 5.34 | 0.00102 | -0.0293 |  | LF | Bldg | 4830 | 0.8 | 4830 | 0.8 | 1.11 | 1.27 | -0.0060663 | 4830 | 0.8 | 4830 | 0.8 | 1.11 | 1.27 | -0.00607
LFBldgSCERSDNewCZ09 | Com-Iltg-dWatt-LF_OSbldg | SCE | RSD | New | CZ09 | 4.83 | 0.0008 | 0 | 5.37 | 0.00106 | -0.0312 | 4.83 | 0.0008 | 0 | 5.37 | 0.00106 | -0.0312 |  | LF | Bldg | 4830 | 0.8 | 4830 | 0.8 | 1.11 | 1.33 | -0.0064596 | 4830 | 0.8 | 4830 | 0.8 | 1.11 | 1.33 | -0.00646
LFBldgSCERSDNewCZ10 | Com-Iltg-dWatt-LF_OSbldg | SCE | RSD | New | CZ10 | 4.83 | 0.0008 | 0 | 5.39 | 0.00106 | -0.0319 | 4.83 | 0.0008 | 0 | 5.39 | 0.00106 | -0.0319 |  | LF | Bldg | 4830 | 0.8 | 4830 | 0.8 | 1.12 | 1.33 | -0.0066046 | 4830 | 0.8 | 4830 | 0.8 | 1.12 | 1.33 | -0.0066
LFBldgSCERSDNewCZ13 | Com-Iltg-dWatt-LF_OSbldg | SCE | RSD | New | CZ13 | 4.83 | 0.0008 | 0 | 5.31 | 0.00108 | -0.0493 | 4.83 | 0.0008 | 0 | 5.31 | 0.00108 | -0.0493 |  | LF | Bldg | 4830 | 0.8 | 4830 | 0.8 | 1.1 | 1.35 | -0.010207 | 4830 | 0.8 | 4830 | 0.8 | 1.1 | 1.35 | -0.0102
LFBldgSCERSDNewCZ14 | Com-Iltg-dWatt-LF_OSbldg | SCE | RSD | New | CZ14 | 4.83 | 0.0008 | 0 | 5.28 | 0.00106 | -0.0512 | 4.83 | 0.0008 | 0 | 5.28 | 0.00106 | -0.0512 |  | LF | Bldg | 4830 | 0.8 | 4830 | 0.8 | 1.09 | 1.33 | -0.0106 | 4830 | 0.8 | 4830 | 0.8 | 1.09 | 1.33 | -0.0106
LFBldgSCERSDNewCZ15 | Com-Iltg-dWatt-LF_OSbldg | SCE | RSD | New | CZ15 | 4.83 | 0.0008 | 0 | 5.8 | 0.0011 | -0.0143 | 4.83 | 0.0008 | 0 | 5.8 | 0.0011 | -0.0143 |  | LF | Bldg | 4830 | 0.8 | 4830 | 0.8 | 1.2 | 1.38 | -0.0029607 | 4830 | 0.8 | 4830 | 0.8 | 1.2 | 1.38 | -0.00296
LFBldgSCERSDNewCZ16 | Com-Iltg-dWatt-LF_OSbldg | SCE | RSD | New | CZ16 | 4.83 | 0.0008 | 0 | 4.84 | 0.001 | -0.0609 | 4.83 | 0.0008 | 0 | 4.84 | 0.001 | -0.0609 |  | LF | Bldg | 4830 | 0.8 | 4830 | 0.8 | 1 | 1.25 | -0.012609 | 4830 | 0.8 | 4830 | 0.8 | 1 | 1.25 | -0.0126
LFBldgSCERSDNewIOU | Com-Iltg-dWatt-LF_OSbldg | SCE | RSD | New | IOU | 4.83 | 0.0008 | 0 | 5.3525 | 0.001041 | -0.033094 | 4.83 | 0.0008 | 0 | 5.3525 | 0.001041 | -0.033094 |  | LF | Bldg | 4830 | 0.8 | 4830 | 0.8 | 1.11 | 1.3 | -0.0068517 | 4830 | 0.8 | 4830 | 0.8 | 1.11 | 1.3 | -0.00685
LFBldgSCERt3ExCZ05 | Com-Iltg-dWatt-LF_OSbldg | SCE | Rt3 | Ex | CZ05 | 3.3794 | 0.0007592 | 0 | 3.6994 | 0.00092145 | -0.0141 | 3.37 | 0.00075732 | 0 | 3.69 | 0.00091958 | -0.0141 |  | LF | Bldg | 3380 | 0.759 | 3370 | 0.757 | 1.09 | 1.21 | -0.004184 | 3380 | 0.759 | 3370 | 0.757 | 1.09 | 1.21 | -0.00418
LFBldgSCERt3ExCZ06 | Com-Iltg-dWatt-LF_OSbldg | SCE | Rt3 | Ex | CZ06 | 3.3794 | 0.0007592 | 0 | 3.9294 | 0.0009322 | -0.00337 | 3.37 | 0.00075732 | 0 | 3.92 | 0.00093033 | -0.00337 |  | LF | Bldg | 3380 | 0.759 | 3370 | 0.757 | 1.16 | 1.23 | -0.001 | 3380 | 0.759 | 3370 | 0.757 | 1.16 | 1.23 | -0.001
LFBldgSCERt3ExCZ08 | Com-Iltg-dWatt-LF_OSbldg | SCE | Rt3 | Ex | CZ08 | 3.3793 | 0.0007592 | 0 | 3.9298 | 0.0009232 | -0.0030398 | 3.37 | 0.00075733 | 0 | 3.9204 | 0.00092133 | -0.0030398 |  | LF | Bldg | 3380 | 0.759 | 3370 | 0.757 | 1.16 | 1.22 | -0.00090201 | 3380 | 0.759 | 3370 | 0.757 | 1.16 | 1.22 | -0.000902
LFBldgSCERt3ExCZ09 | Com-Iltg-dWatt-LF_OSbldg | SCE | Rt3 | Ex | CZ09 | 3.3793 | 0.0007592 | 0 | 3.8898 | 0.0009362 | -0.0047293 | 3.37 | 0.00075733 | 0 | 3.8804 | 0.00093433 | -0.00472 |  | LF | Bldg | 3380 | 0.759 | 3370 | 0.757 | 1.15 | 1.23 | -0.0014006 | 3380 | 0.759 | 3370 | 0.757 | 1.15 | 1.23 | -0.0014
LFBldgSCERt3ExCZ10 | Com-Iltg-dWatt-LF_OSbldg | SCE | Rt3 | Ex | CZ10 | 3.3788 | 0.00075995 | 0 | 3.8022 | 0.00092495 | -0.0054022 | 3.37 | 0.00075752 | 0 | 3.79 | 0.00092218 | -0.00539 |  | LF | Bldg | 3380 | 0.76 | 3370 | 0.758 | 1.12 | 1.22 | -0.0015994 | 3380 | 0.76 | 3370 | 0.758 | 1.12 | 1.22 | -0.0016
LFBldgSCERt3ExCZ13 | Com-Iltg-dWatt-LF_OSbldg | SCE | Rt3 | Ex | CZ13 | 3.379 | 0.00075971 | 0 | 3.7122 | 0.00093893 | -0.0179 | 3.37 | 0.00075747 | 0 | 3.71 | 0.00093647 | -0.0179 |  | LF | Bldg | 3380 | 0.76 | 3370 | 0.757 | 1.1 | 1.24 | -0.0053116 | 3380 | 0.76 | 3370 | 0.757 | 1.1 | 1.24 | -0.00531
LFBldgSCERt3ExCZ14 | Com-Iltg-dWatt-LF_OSbldg | SCE | Rt3 | Ex | CZ14 | 3.379 | 0.0007599 | 0 | 3.669 | 0.00093557 | -0.018932 | 3.37 | 0.00075745 | 0 | 3.66 | 0.00093245 | -0.0189 |  | LF | Bldg | 3380 | 0.76 | 3370 | 0.757 | 1.09 | 1.23 | -0.0056083 | 3380 | 0.76 | 3370 | 0.757 | 1.09 | 1.23 | -0.00561
LFBldgSCERt3ExCZ15 | Com-Iltg-dWatt-LF_OSbldg | SCE | Rt3 | Ex | CZ15 | 3.3788 | 0.00075928 | 0 | 3.9388 | 0.00094528 | -0.00122 | 3.37 | 0.00075752 | 0 | 3.93 | 0.00094352 | -0.00122 |  | LF | Bldg | 3380 | 0.759 | 3370 | 0.758 | 1.17 | 1.25 | -0.00036202 | 3380 | 0.759 | 3370 | 0.758 | 1.17 | 1.25 | -0.000362
LFBldgSCERt3ExCZ16 | Com-Iltg-dWatt-LF_OSbldg | SCE | Rt3 | Ex | CZ16 | 3.379 | 0.00075926 | 0 | 3.329 | 0.00091426 | -0.04249 | 3.37 | 0.00075747 | 0 | 3.32 | 0.00091247 | -0.0424 |  | LF | Bldg | 3380 | 0.759 | 3370 | 0.757 | 0.985 | 1.2 | -0.012582 | 3380 | 0.759 | 3370 | 0.757 | 0.985 | 1.2 | -0.0126
LFBldgSCERt3ExIOU | Com-Iltg-dWatt-LF_OSbldg | SCE | Rt3 | Ex | IOU | 3.3792 | 0.00075941 | 0 | 3.8738 | 0.00092925 | -0.0052647 | 3.37 | 0.00075738 | 0 | 3.8641 | 0.00092712 | -0.0052586 |  | LF | Bldg | 3380 | 0.759 | 3370 | 0.757 | 1.15 | 1.22 | -0.0015604 | 3380 | 0.759 | 3370 | 0.757 | 1.15 | 1.22 | -0.00156
LFBldgSCERt3NewCZ05 | Com-Iltg-dWatt-LF_OSbldg | SCE | Rt3 | New | CZ05 | 3.37 | 0.000758 | 0 | 3.57 | 0.000931 | -0.0177 | 3.37 | 0.000758 | 0 | 3.57 | 0.000931 | -0.0177 |  | LF | Bldg | 3370 | 0.758 | 3370 | 0.758 | 1.06 | 1.23 | -0.0052522 | 3370 | 0.758 | 3370 | 0.758 | 1.06 | 1.23 | -0.00525
LFBldgSCERt3NewCZ06 | Com-Iltg-dWatt-LF_OSbldg | SCE | Rt3 | New | CZ06 | 3.37 | 0.000758 | 0 | 3.81 | 0.000939 | -0.00445 | 3.37 | 0.000758 | 0 | 3.81 | 0.000939 | -0.00445 |  | LF | Bldg | 3370 | 0.758 | 3370 | 0.758 | 1.13 | 1.24 | -0.0013205 | 3370 | 0.758 | 3370 | 0.758 | 1.13 | 1.24 | -0.00132
LFBldgSCERt3NewCZ08 | Com-Iltg-dWatt-LF_OSbldg | SCE | Rt3 | New | CZ08 | 3.37 | 0.000758 | 0 | 3.85 | 0.000947 | -0.00374 | 3.37 | 0.000758 | 0 | 3.85 | 0.000947 | -0.00374 |  | LF | Bldg | 3370 | 0.758 | 3370 | 0.758 | 1.14 | 1.25 | -0.0011098 | 3370 | 0.758 | 3370 | 0.758 | 1.14 | 1.25 | -0.00111
LFBldgSCERt3NewCZ09 | Com-Iltg-dWatt-LF_OSbldg | SCE | Rt3 | New | CZ09 | 3.37 | 0.000758 | 0 | 3.77 | 0.000908 | -0.00589 | 3.37 | 0.000758 | 0 | 3.77 | 0.000908 | -0.00589 |  | LF | Bldg | 3370 | 0.758 | 3370 | 0.758 | 1.12 | 1.2 | -0.0017478 | 3370 | 0.758 | 3370 | 0.758 | 1.12 | 1.2 | -0.00175
LFBldgSCERt3NewCZ10 | Com-Iltg-dWatt-LF_OSbldg | SCE | Rt3 | New | CZ10 | 3.37 | 0.000758 | 0 | 3.8 | 0.000941 | -0.00687 | 3.37 | 0.000758 | 0 | 3.8 | 0.000941 | -0.00687 |  | LF | Bldg | 3370 | 0.758 | 3370 | 0.758 | 1.13 | 1.24 | -0.0020386 | 3370 | 0.758 | 3370 | 0.758 | 1.13 | 1.24 | -0.00204
LFBldgSCERt3NewCZ13 | Com-Iltg-dWatt-LF_OSbldg | SCE | Rt3 | New | CZ13 | 3.37 | 0.000758 | 0 | 3.74 | 0.000984 | -0.0194 | 3.37 | 0.000758 | 0 | 3.74 | 0.000984 | -0.0194 |  | LF | Bldg | 3370 | 0.758 | 3370 | 0.758 | 1.11 | 1.3 | -0.0057567 | 3370 | 0.758 | 3370 | 0.758 | 1.11 | 1.3 | -0.00576
LFBldgSCERt3NewCZ14 | Com-Iltg-dWatt-LF_OSbldg | SCE | Rt3 | New | CZ14 | 3.37 | 0.000758 | 0 | 3.74 | 0.000979 | -0.0199 | 3.37 | 0.000758 | 0 | 3.74 | 0.000979 | -0.0199 |  | LF | Bldg | 3370 | 0.758 | 3370 | 0.758 | 1.11 | 1.29 | -0.005905 | 3370 | 0.758 | 3370 | 0.758 | 1.11 | 1.29 | -0.00591
LFBldgSCERt3NewCZ15 | Com-Iltg-dWatt-LF_OSbldg | SCE | Rt3 | New | CZ15 | 3.37 | 0.000758 | 0 | 3.8 | 0.000894 | -0.000721 | 3.37 | 0.000758 | 0 | 3.8 | 0.000894 | -0.000721 |  | LF | Bldg | 3370 | 0.758 | 3370 | 0.758 | 1.13 | 1.18 | -0.00021395 | 3370 | 0.758 | 3370 | 0.758 | 1.13 | 1.18 | -0.000214
LFBldgSCERt3NewCZ16 | Com-Iltg-dWatt-LF_OSbldg | SCE | Rt3 | New | CZ16 | 3.37 | 0.000758 | 0 | 3.36 | 0.000938 | -0.0431 | 3.37 | 0.000758 | 0 | 3.36 | 0.000938 | -0.0431 |  | LF | Bldg | 3370 | 0.758 | 3370 | 0.758 | 0.997 | 1.24 | -0.012789 | 3370 | 0.758 | 3370 | 0.758 | 0.997 | 1.24 | -0.0128
LFBldgSCERt3NewIOU | Com-Iltg-dWatt-LF_OSbldg | SCE | Rt3 | New | IOU | 3.37 | 0.000758 | 0 | 3.7984 | 0.00093923 | -0.0068778 | 3.37 | 0.000758 | 0 | 3.7984 | 0.00093923 | -0.0068778 |  | LF | Bldg | 3370 | 0.758 | 3370 | 0.758 | 1.13 | 1.24 | -0.0020409 | 3370 | 0.758 | 3370 | 0.758 | 1.13 | 1.24 | -0.00204
LFBldgSCERtLExCZ05 | Com-Iltg-dWatt-LF_OSbldg | SCE | RtL | Ex | CZ05 | 4.2694 | 0.00084791 | 0 | 4.5994 | 0.00103 | -0.0254 | 4.26 | 0.00084694 | 0 | 4.59 | 0.00103 | -0.0254 |  | LF | Bldg | 4270 | 0.848 | 4260 | 0.847 | 1.08 | 1.22 | -0.0059624 | 4270 | 0.848 | 4260 | 0.847 | 1.08 | 1.22 | -0.00596
LFBldgSCERtLExCZ06 | Com-Iltg-dWatt-LF_OSbldg | SCE | RtL | Ex | CZ06 | 4.2694 | 0.00084791 | 0 | 4.89 | 0.0010404 | -0.0098998 | 4.26 | 0.00084694 | 0 | 4.8896 | 0.00104 | -0.0098896 |  | LF | Bldg | 4270 | 0.848 | 4260 | 0.847 | 1.15 | 1.23 | -0.0023215 | 4270 | 0.848 | 4260 | 0.847 | 1.15 | 1.23 | -0.00232
LFBldgSCERtLExCZ08 | Com-Iltg-dWatt-LF_OSbldg | SCE | RtL | Ex | CZ08 | 4.2694 | 0.00084791 | 0 | 4.9093 | 0.0010494 | -0.0085794 | 4.26 | 0.00084694 | 0 | 4.8996 | 0.0010404 | -0.0085696 |  | LF | Bldg | 4270 | 0.848 | 4260 | 0.847 | 1.15 | 1.23 | -0.0020116 | 4270 | 0.848 | 4260 | 0.847 | 1.15 | 1.23 | -0.00201
LFBldgSCERtLExCZ09 | Com-Iltg-dWatt-LF_OSbldg | SCE | RtL | Ex | CZ09 | 4.2693 | 0.00084791 | 0 | 4.8593 | 0.00107 | -0.0102 | 4.26 | 0.00084693 | 0 | 4.85 | 0.00107 | -0.0102 |  | LF | Bldg | 4270 | 0.848 | 4260 | 0.847 | 1.14 | 1.26 | -0.0023944 | 4270 | 0.848 | 4260 | 0.847 | 1.14 | 1.26 | -0.00239
LFBldgSCERtLExCZ10 | Com-Iltg-dWatt-LF_OSbldg | SCE | RtL | Ex | CZ10 | 4.2688 | 0.00084791 | 0 | 4.7688 | 0.0010588 | -0.0114 | 4.26 | 0.00084688 | 0 | 4.76 | 0.0010515 | -0.0114 |  | LF | Bldg | 4270 | 0.848 | 4260 | 0.847 | 1.12 | 1.24 | -0.0026761 | 4270 | 0.848 | 4260 | 0.847 | 1.12 | 1.24 | -0.00268
LFBldgSCERtLExCZ13 | Com-Iltg-dWatt-LF_OSbldg | SCE | RtL | Ex | CZ13 | 4.269 | 0.00084811 | 0 | 4.68 | 0.00106 | -0.02349 | 4.26 | 0.0008469 | 0 | 4.6769 | 0.00106 | -0.023459 |  | LF | Bldg | 4270 | 0.848 | 4260 | 0.847 | 1.1 | 1.25 | -0.0055067 | 4270 | 0.848 | 4260 | 0.847 | 1.1 | 1.25 | -0.00551
LFBldgSCERtLExCZ14 | Com-Iltg-dWatt-LF_OSbldg | SCE | RtL | Ex | CZ14 | 4.269 | 0.00084803 | 0 | 4.639 | 0.00107 | -0.02409 | 4.26 | 0.0008469 | 0 | 4.6367 | 0.00107 | -0.024 |  | LF | Bldg | 4270 | 0.848 | 4260 | 0.847 | 1.09 | 1.26 | -0.0056338 | 4270 | 0.848 | 4260 | 0.847 | 1.09 | 1.26 | -0.00563
LFBldgSCERtLExCZ15 | Com-Iltg-dWatt-LF_OSbldg | SCE | RtL | Ex | CZ15 | 4.2688 | 0.00084776 | 0 | 4.99 | 0.00107 | -0.0039988 | 4.26 | 0.00084688 | 0 | 4.99 | 0.00107 | -0.0039988 |  | LF | Bldg | 4270 | 0.848 | 4260 | 0.847 | 1.17 | 1.26 | -0.00093869 | 4270 | 0.848 | 4260 | 0.847 | 1.17 | 1.26 | -0.000939
LFBldgSCERtLExCZ16 | Com-Iltg-dWatt-LF_OSbldg | SCE | RtL | Ex | CZ16 | 4.269 | 0.00084779 | 0 | 4.19 | 0.00102 | -0.0546 | 4.26 | 0.0008469 | 0 | 4.19 | 0.00102 | -0.0546 |  | LF | Bldg | 4270 | 0.848 | 4260 | 0.847 | 0.984 | 1.2 | -0.012817 | 4270 | 0.848 | 4260 | 0.847 | 0.984 | 1.2 | -0.0128
LFBldgSCERtLExIOU | Com-Iltg-dWatt-LF_OSbldg | SCE | RtL | Ex | IOU | 4.2692 | 0.00084792 | 0 | 4.8445 | 0.0010537 | -0.011118 | 4.26 | 0.00084692 | 0 | 4.8382 | 0.0010496 | -0.011109 |  | LF | Bldg | 4270 | 0.848 | 4260 | 0.847 | 1.14 | 1.24 | -0.0026077 | 4270 | 0.848 | 4260 | 0.847 | 1.14 | 1.24 | -0.00261
LFBldgSCERtLNewCZ05 | Com-Iltg-dWatt-LF_OSbldg | SCE | RtL | New | CZ05 | 4.26 | 0.000846 | 0 | 4.47 | 0.00104 | -0.0299 | 4.26 | 0.000846 | 0 | 4.47 | 0.00104 | -0.0299 |  | LF | Bldg | 4260 | 0.846 | 4260 | 0.846 | 1.05 | 1.23 | -0.0070188 | 4260 | 0.846 | 4260 | 0.846 | 1.05 | 1.23 | -0.00702
LFBldgSCERtLNewCZ06 | Com-Iltg-dWatt-LF_OSbldg | SCE | RtL | New | CZ06 | 4.26 | 0.000846 | 0 | 4.72 | 0.00106 | -0.0135 | 4.26 | 0.000846 | 0 | 4.72 | 0.00106 | -0.0135 |  | LF | Bldg | 4260 | 0.846 | 4260 | 0.846 | 1.11 | 1.25 | -0.003169 | 4260 | 0.846 | 4260 | 0.846 | 1.11 | 1.25 | -0.00317
LFBldgSCERtLNewCZ08 | Com-Iltg-dWatt-LF_OSbldg | SCE | RtL | New | CZ08 | 4.26 | 0.000846 | 0 | 4.79 | 0.00108 | -0.0115 | 4.26 | 0.000846 | 0 | 4.79 | 0.00108 | -0.0115 |  | LF | Bldg | 4260 | 0.846 | 4260 | 0.846 | 1.12 | 1.28 | -0.0026995 | 4260 | 0.846 | 4260 | 0.846 | 1.12 | 1.28 | -0.0027
LFBldgSCERtLNewCZ09 | Com-Iltg-dWatt-LF_OSbldg | SCE | RtL | New | CZ09 | 4.26 | 0.000846 | 0 | 4.8 | 0.00112 | -0.0115 | 4.26 | 0.000846 | 0 | 4.8 | 0.00112 | -0.0115 |  | LF | Bldg | 4260 | 0.846 | 4260 | 0.846 | 1.13 | 1.32 | -0.0026995 | 4260 | 0.846 | 4260 | 0.846 | 1.13 | 1.32 | -0.0027
LFBldgSCERtLNewCZ10 | Com-Iltg-dWatt-LF_OSbldg | SCE | RtL | New | CZ10 | 4.26 | 0.000846 | 0 | 4.82 | 0.00112 | -0.0133 | 4.26 | 0.000846 | 0 | 4.82 | 0.00112 | -0.0133 |  | LF | Bldg | 4260 | 0.846 | 4260 | 0.846 | 1.13 | 1.32 | -0.0031221 | 4260 | 0.846 | 4260 | 0.846 | 1.13 | 1.32 | -0.00312
LFBldgSCERtLNewCZ13 | Com-Iltg-dWatt-LF_OSbldg | SCE | RtL | New | CZ13 | 4.26 | 0.000846 | 0 | 4.72 | 0.00111 | -0.0262 | 4.26 | 0.000846 | 0 | 4.72 | 0.00111 | -0.0262 |  | LF | Bldg | 4260 | 0.846 | 4260 | 0.846 | 1.11 | 1.31 | -0.0061502 | 4260 | 0.846 | 4260 | 0.846 | 1.11 | 1.31 | -0.00615
LFBldgSCERtLNewCZ14 | Com-Iltg-dWatt-LF_OSbldg | SCE | RtL | New | CZ14 | 4.26 | 0.000846 | 0 | 4.71 | 0.00111 | -0.0266 | 4.26 | 0.000846 | 0 | 4.71 | 0.00111 | -0.0266 |  | LF | Bldg | 4260 | 0.846 | 4260 | 0.846 | 1.11 | 1.31 | -0.0062441 | 4260 | 0.846 | 4260 | 0.846 | 1.11 | 1.31 | -0.00624
LFBldgSCERtLNewCZ15 | Com-Iltg-dWatt-LF_OSbldg | SCE | RtL | New | CZ15 | 4.26 | 0.000846 | 0 | 5.11 | 0.00113 | -0.00403 | 4.26 | 0.000846 | 0 | 5.11 | 0.00113 | -0.00403 |  | LF | Bldg | 4260 | 0.846 | 4260 | 0.846 | 1.2 | 1.34 | -0.00094601 | 4260 | 0.846 | 4260 | 0.846 | 1.2 | 1.34 | -0.000946
LFBldgSCERtLNewCZ16 | Com-Iltg-dWatt-LF_OSbldg | SCE | RtL | New | CZ16 | 4.26 | 0.000846 | 0 | 4.24 | 0.00105 | -0.0576 | 4.26 | 0.000846 | 0 | 4.24 | 0.00105 | -0.0576 |  | LF | Bldg | 4260 | 0.846 | 4260 | 0.846 | 0.995 | 1.24 | -0.013521 | 4260 | 0.846 | 4260 | 0.846 | 0.995 | 1.24 | -0.0135
LFBldgSCERtLNewIOU | Com-Iltg-dWatt-LF_OSbldg | SCE | RtL | New | IOU | 4.26 | 0.000846 | 0 | 4.7887 | 0.0010985 | -0.013987 | 4.26 | 0.000846 | 0 | 4.7887 | 0.0010985 | -0.013987 |  | LF | Bldg | 4260 | 0.846 | 4260 | 0.846 | 1.12 | 1.3 | -0.0032833 | 4260 | 0.846 | 4260 | 0.846 | 1.12 | 1.3 | -0.00328
LFBldgSCERtSExCZ05 | Com-Iltg-dWatt-LF_OSbldg | SCE | RtS | Ex | CZ05 | 3.38 | 0.000875 | 0 | 3.6302 | 0.00106 | -0.0156 | 3.38 | 0.000875 | 0 | 3.6302 | 0.00106 | -0.0156 |  | LF | Bldg | 3380 | 0.875 | 3380 | 0.875 | 1.07 | 1.21 | -0.0046154 | 3380 | 0.875 | 3380 | 0.875 | 1.07 | 1.21 | -0.00462
LFBldgSCERtSExCZ06 | Com-Iltg-dWatt-LF_OSbldg | SCE | RtS | Ex | CZ06 | 3.38 | 0.000875 | 0 | 3.8402 | 0.00107 | -0.0051302 | 3.38 | 0.000875 | 0 | 3.8402 | 0.00107 | -0.0051302 |  | LF | Bldg | 3380 | 0.875 | 3380 | 0.875 | 1.14 | 1.22 | -0.0015178 | 3380 | 0.875 | 3380 | 0.875 | 1.14 | 1.22 | -0.00152
LFBldgSCERtSExCZ08 | Com-Iltg-dWatt-LF_OSbldg | SCE | RtS | Ex | CZ08 | 3.38 | 0.000875 | 0 | 3.87 | 0.00107 | -0.0043502 | 3.38 | 0.000875 | 0 | 3.87 | 0.00107 | -0.0043502 |  | LF | Bldg | 3380 | 0.875 | 3380 | 0.875 | 1.14 | 1.22 | -0.001287 | 3380 | 0.875 | 3380 | 0.875 | 1.14 | 1.22 | -0.00129
LFBldgSCERtSExCZ09 | Com-Iltg-dWatt-LF_OSbldg | SCE | RtS | Ex | CZ09 | 3.38 | 0.000875 | 0 | 3.8315 | 0.00109 | -0.0058415 | 3.38 | 0.000875 | 0 | 3.8315 | 0.00109 | -0.0058415 |  | LF | Bldg | 3380 | 0.875 | 3380 | 0.875 | 1.13 | 1.25 | -0.0017283 | 3380 | 0.875 | 3380 | 0.875 | 1.13 | 1.25 | -0.00173
LFBldgSCERtSExCZ10 | Com-Iltg-dWatt-LF_OSbldg | SCE | RtS | Ex | CZ10 | 3.38 | 0.000875 | 0 | 3.7617 | 0.00107 | -0.0065517 | 3.38 | 0.000875 | 0 | 3.7617 | 0.00107 | -0.0065517 |  | LF | Bldg | 3380 | 0.875 | 3380 | 0.875 | 1.11 | 1.22 | -0.0019384 | 3380 | 0.875 | 3380 | 0.875 | 1.11 | 1.22 | -0.00194
LFBldgSCERtSExCZ13 | Com-Iltg-dWatt-LF_OSbldg | SCE | RtS | Ex | CZ13 | 3.38 | 0.000875 | 0 | 3.69 | 0.00108 | -0.0185 | 3.38 | 0.000875 | 0 | 3.69 | 0.00108 | -0.0185 |  | LF | Bldg | 3380 | 0.875 | 3380 | 0.875 | 1.09 | 1.23 | -0.0054734 | 3380 | 0.875 | 3380 | 0.875 | 1.09 | 1.23 | -0.00547
LFBldgSCERtSExCZ14 | Com-Iltg-dWatt-LF_OSbldg | SCE | RtS | Ex | CZ14 | 3.38 | 0.000875 | 0 | 3.68 | 0.00107 | -0.0162 | 3.38 | 0.000875 | 0 | 3.68 | 0.00107 | -0.0162 |  | LF | Bldg | 3380 | 0.875 | 3380 | 0.875 | 1.09 | 1.22 | -0.0047929 | 3380 | 0.875 | 3380 | 0.875 | 1.09 | 1.22 | -0.00479
LFBldgSCERtSExCZ15 | Com-Iltg-dWatt-LF_OSbldg | SCE | RtS | Ex | CZ15 | 3.38 | 0.000875 | 0 | 3.96 | 0.00108 | -0.0014 | 3.38 | 0.000875 | 0 | 3.96 | 0.00108 | -0.0014 |  | LF | Bldg | 3380 | 0.875 | 3380 | 0.875 | 1.17 | 1.23 | -0.0004142 | 3380 | 0.875 | 3380 | 0.875 | 1.17 | 1.23 | -0.000414
LFBldgSCERtSExCZ16 | Com-Iltg-dWatt-LF_OSbldg | SCE | RtS | Ex | CZ16 | 3.38 | 0.000875 | 0 | 3.3507 | 0.00105 | -0.0375 | 3.38 | 0.000875 | 0 | 3.3507 | 0.00105 | -0.0375 |  | LF | Bldg | 3380 | 0.875 | 3380 | 0.875 | 0.991 | 1.2 | -0.011095 | 3380 | 0.875 | 3380 | 0.875 | 0.991 | 1.2 | -0.0111
LFBldgSCERtSExIOU | Com-Iltg-dWatt-LF_OSbldg | SCE | RtS | Ex | IOU | 3.38 | 0.000875 | 0 | 3.8182 | 0.0010734 | -0.0063515 | 3.38 | 0.000875 | 0 | 3.8182 | 0.0010734 | -0.0063515 |  | LF | Bldg | 3380 | 0.875 | 3380 | 0.875 | 1.13 | 1.23 | -0.0018792 | 3380 | 0.875 | 3380 | 0.875 | 1.13 | 1.23 | -0.00188
LFBldgSCERtSNewCZ05 | Com-Iltg-dWatt-LF_OSbldg | SCE | RtS | New | CZ05 | 3.38 | 0.000875 | 0 | 3.54 | 0.00104 | -0.0178 | 3.38 | 0.000875 | 0 | 3.54 | 0.00104 | -0.0178 |  | LF | Bldg | 3380 | 0.875 | 3380 | 0.875 | 1.05 | 1.19 | -0.0052663 | 3380 | 0.875 | 3380 | 0.875 | 1.05 | 1.19 | -0.00527
LFBldgSCERtSNewCZ06 | Com-Iltg-dWatt-LF_OSbldg | SCE | RtS | New | CZ06 | 3.38 | 0.000875 | 0 | 3.74 | 0.00106 | -0.00678 | 3.38 | 0.000875 | 0 | 3.74 | 0.00106 | -0.00678 |  | LF | Bldg | 3380 | 0.875 | 3380 | 0.875 | 1.11 | 1.21 | -0.0020059 | 3380 | 0.875 | 3380 | 0.875 | 1.11 | 1.21 | -0.00201
LFBldgSCERtSNewCZ08 | Com-Iltg-dWatt-LF_OSbldg | SCE | RtS | New | CZ08 | 3.38 | 0.000875 | 0 | 3.78 | 0.00107 | -0.0057 | 3.38 | 0.000875 | 0 | 3.78 | 0.00107 | -0.0057 |  | LF | Bldg | 3380 | 0.875 | 3380 | 0.875 | 1.12 | 1.22 | -0.0016864 | 3380 | 0.875 | 3380 | 0.875 | 1.12 | 1.22 | -0.00169
LFBldgSCERtSNewCZ09 | Com-Iltg-dWatt-LF_OSbldg | SCE | RtS | New | CZ09 | 3.38 | 0.000875 | 0 | 3.78 | 0.0011 | -0.00692 | 3.38 | 0.000875 | 0 | 3.78 | 0.0011 | -0.00692 |  | LF | Bldg | 3380 | 0.875 | 3380 | 0.875 | 1.12 | 1.26 | -0.0020473 | 3380 | 0.875 | 3380 | 0.875 | 1.12 | 1.26 | -0.00205
LFBldgSCERtSNewCZ10 | Com-Iltg-dWatt-LF_OSbldg | SCE | RtS | New | CZ10 | 3.38 | 0.000875 | 0 | 3.81 | 0.00112 | -0.00709 | 3.38 | 0.000875 | 0 | 3.81 | 0.00112 | -0.00709 |  | LF | Bldg | 3380 | 0.875 | 3380 | 0.875 | 1.13 | 1.28 | -0.0020976 | 3380 | 0.875 | 3380 | 0.875 | 1.13 | 1.28 | -0.0021
LFBldgSCERtSNewCZ13 | Com-Iltg-dWatt-LF_OSbldg | SCE | RtS | New | CZ13 | 3.38 | 0.000875 | 0 | 3.7 | 0.00109 | -0.0189 | 3.38 | 0.000875 | 0 | 3.7 | 0.00109 | -0.0189 |  | LF | Bldg | 3380 | 0.875 | 3380 | 0.875 | 1.09 | 1.25 | -0.0055917 | 3380 | 0.875 | 3380 | 0.875 | 1.09 | 1.25 | -0.00559
LFBldgSCERtSNewCZ14 | Com-Iltg-dWatt-LF_OSbldg | SCE | RtS | New | CZ14 | 3.38 | 0.000875 | 0 | 3.72 | 0.00109 | -0.0171 | 3.38 | 0.000875 | 0 | 3.72 | 0.00109 | -0.0171 |  | LF | Bldg | 3380 | 0.875 | 3380 | 0.875 | 1.1 | 1.25 | -0.0050592 | 3380 | 0.875 | 3380 | 0.875 | 1.1 | 1.25 | -0.00506
LFBldgSCERtSNewCZ15 | Com-Iltg-dWatt-LF_OSbldg | SCE | RtS | New | CZ15 | 3.38 | 0.000875 | 0 | 3.98 | 0.00112 | -0.00126 | 3.38 | 0.000875 | 0 | 3.98 | 0.00112 | -0.00126 |  | LF | Bldg | 3380 | 0.875 | 3380 | 0.875 | 1.18 | 1.28 | -0.00037278 | 3380 | 0.875 | 3380 | 0.875 | 1.18 | 1.28 | -0.000373
LFBldgSCERtSNewCZ16 | Com-Iltg-dWatt-LF_OSbldg | SCE | RtS | New | CZ16 | 3.38 | 0.000875 | 0 | 3.36 | 0.00105 | -0.0398 | 3.38 | 0.000875 | 0 | 3.36 | 0.00105 | -0.0398 |  | LF | Bldg | 3380 | 0.875 | 3380 | 0.875 | 0.994 | 1.2 | -0.011775 | 3380 | 0.875 | 3380 | 0.875 | 0.994 | 1.2 | -0.0118
LFBldgSCERtSNewIOU | Com-Iltg-dWatt-LF_OSbldg | SCE | RtS | New | IOU | 3.38 | 0.000875 | 0 | 3.78 | 0.0010917 | -0.0077691 | 3.38 | 0.000875 | 0 | 3.78 | 0.0010917 | -0.0077691 |  | LF | Bldg | 3380 | 0.875 | 3380 | 0.875 | 1.12 | 1.25 | -0.0022986 | 3380 | 0.875 | 3380 | 0.875 | 1.12 | 1.25 | -0.0023
LFBldgSCEs_AgrExCZ05 | Com-Iltg-dWatt-LF_OSbldg | SCE | s_Agr | Ex | CZ05 | 3.156 | 0.00089473 | 0 | 3.3332 | 0.0010964 | -0.015486 | 3.018 | 0.0008592 | 0 | 3.182 | 0.0010482 | -0.015004 |  | LF | Bldg | 3160 | 0.895 | 3020 | 0.859 | 1.05 | 1.22 | -0.0049715 | 3160 | 0.895 | 3020 | 0.859 | 1.05 | 1.22 | -0.00497
LFBldgSCEs_AgrExCZ06 | Com-Iltg-dWatt-LF_OSbldg | SCE | s_Agr | Ex | CZ06 | 3.156 | 0.00089473 | 0 | 3.5149 | 0.0010832 | -0.0055456 | 3.018 | 0.0008592 | 0 | 3.358 | 0.001042 | -0.005332 |  | LF | Bldg | 3160 | 0.895 | 3020 | 0.859 | 1.11 | 1.21 | -0.0017667 | 3160 | 0.895 | 3020 | 0.859 | 1.11 | 1.21 | -0.00177
LFBldgSCEs_AgrExCZ08 | Com-Iltg-dWatt-LF_OSbldg | SCE | s_Agr | Ex | CZ08 | 3.156 | 0.00089474 | 0 | 3.5428 | 0.0010846 | -0.0046344 | 3.018 | 0.0008592 | 0 | 3.384 | 0.0010432 | -0.004434 |  | LF | Bldg | 3160 | 0.895 | 3020 | 0.859 | 1.12 | 1.21 | -0.0014692 | 3160 | 0.895 | 3020 | 0.859 | 1.12 | 1.21 | -0.00147
LFBldgSCEs_AgrExCZ09 | Com-Iltg-dWatt-LF_OSbldg | SCE | s_Agr | Ex | CZ09 | 3.1561 | 0.00089476 | 0 | 3.515 | 0.0011111 | -0.0063279 | 3.018 | 0.0008592 | 0 | 3.358 | 0.0010608 | -0.006082 |  | LF | Bldg | 3160 | 0.895 | 3020 | 0.859 | 1.11 | 1.23 | -0.0020152 | 3160 | 0.895 | 3020 | 0.859 | 1.11 | 1.23 | -0.00202
LFBldgSCEs_AgrExCZ10 | Com-Iltg-dWatt-LF_OSbldg | SCE | s_Agr | Ex | CZ10 | 3.1509 | 0.00089336 | 0 | 3.4273 | 0.0010981 | -0.0067357 | 3.018 | 0.0008592 | 0 | 3.278 | 0.0010512 | -0.006516 |  | LF | Bldg | 3150 | 0.893 | 3020 | 0.859 | 1.09 | 1.22 | -0.002159 | 3150 | 0.893 | 3020 | 0.859 | 1.09 | 1.22 | -0.00216
LFBldgSCEs_AgrExCZ13 | Com-Iltg-dWatt-LF_OSbldg | SCE | s_Agr | Ex | CZ13 | 3.1552 | 0.00089451 | 0 | 3.3944 | 0.0010833 | -0.016222 | 3.018 | 0.0008592 | 0 | 3.244 | 0.0010422 | -0.015652 |  | LF | Bldg | 3160 | 0.895 | 3020 | 0.859 | 1.07 | 1.21 | -0.0051862 | 3160 | 0.895 | 3020 | 0.859 | 1.07 | 1.21 | -0.00519
LFBldgSCEs_AgrExCZ14 | Com-Iltg-dWatt-LF_OSbldg | SCE | s_Agr | Ex | CZ14 | 3.1522 | 0.00089374 | 0 | 3.369 | 0.0010945 | -0.017868 | 3.018 | 0.0008592 | 0 | 3.22 | 0.0010532 | -0.017492 |  | LF | Bldg | 3150 | 0.894 | 3020 | 0.859 | 1.07 | 1.23 | -0.0057959 | 3150 | 0.894 | 3020 | 0.859 | 1.07 | 1.23 | -0.0058
LFBldgSCEs_AgrExCZ15 | Com-Iltg-dWatt-LF_OSbldg | SCE | s_Agr | Ex | CZ15 | 3.1509 | 0.00089336 | 0 | 3.6604 | 0.0010899 | -0.001831 | 3.018 | 0.0008592 | 0 | 3.502 | 0.001043 | -0.001762 |  | LF | Bldg | 3150 | 0.893 | 3020 | 0.859 | 1.16 | 1.21 | -0.00058383 | 3150 | 0.893 | 3020 | 0.859 | 1.16 | 1.21 | -0.000584
LFBldgSCEs_AgrExCZ16 | Com-Iltg-dWatt-LF_OSbldg | SCE | s_Agr | Ex | CZ16 | 3.1533 | 0.00089401 | 0 | 3.1173 | 0.0010708 | -0.035659 | 3.018 | 0.0008592 | 0 | 2.982 | 0.001031 | -0.03464 |  | LF | Bldg | 3150 | 0.894 | 3020 | 0.859 | 0.988 | 1.2 | -0.011478 | 3150 | 0.894 | 3020 | 0.859 | 0.988 | 1.2 | -0.0115
LFBldgSCEs_AgrExIOU | Com-Iltg-dWatt-LF_OSbldg | SCE | s_Agr | Ex | IOU | 3.1545 | 0.00089433 | 0 | 3.4998 | 0.0010908 | -0.0067554 | 3.018 | 0.0008592 | 0 | 3.3447 | 0.0010469 | -0.0065132 |  | LF | Bldg | 3150 | 0.894 | 3020 | 0.859 | 1.11 | 1.22 | -0.0021581 | 3150 | 0.894 | 3020 | 0.859 | 1.11 | 1.22 | -0.00216
LFBldgSCEs_CliExCZ05 | Com-Iltg-dWatt-LF_OSbldg | SCE | s_Cli | Ex | CZ05 | 3.5633 | 0.00072883 | 0 | 3.7413 | 0.00090754 | -0.037883 | 3.165 | 0.000636 | 0 | 3.31 | 0.0007915 | -0.03576 |  | LF | Bldg | 3560 | 0.729 | 3160 | 0.636 | 1.05 | 1.24 | -0.011299 | 3560 | 0.729 | 3160 | 0.636 | 1.05 | 1.24 | -0.0113
LFBldgSCEs_CliExCZ06 | Com-Iltg-dWatt-LF_OSbldg | SCE | s_Cli | Ex | CZ06 | 3.5631 | 0.00072882 | 0 | 3.96 | 0.00093642 | -0.024374 | 3.165 | 0.000636 | 0 | 3.505 | 0.0008185 | -0.02311 |  | LF | Bldg | 3560 | 0.729 | 3160 | 0.636 | 1.11 | 1.29 | -0.0073017 | 3560 | 0.729 | 3160 | 0.636 | 1.11 | 1.29 | -0.0073
LFBldgSCEs_CliExCZ08 | Com-Iltg-dWatt-LF_OSbldg | SCE | s_Cli | Ex | CZ08 | 3.5631 | 0.00072881 | 0 | 3.9947 | 0.00093838 | -0.023568 | 3.165 | 0.000636 | 0 | 3.535 | 0.00082 | -0.022385 |  | LF | Bldg | 3560 | 0.729 | 3160 | 0.636 | 1.12 | 1.29 | -0.0070727 | 3560 | 0.729 | 3160 | 0.636 | 1.12 | 1.29 | -0.00707
LFBldgSCEs_CliExCZ09 | Com-Iltg-dWatt-LF_OSbldg | SCE | s_Cli | Ex | CZ09 | 3.5625 | 0.00072873 | 0 | 3.9895 | 0.00096156 | -0.024442 | 3.165 | 0.000636 | 0 | 3.54 | 0.0008395 | -0.023125 |  | LF | Bldg | 3560 | 0.729 | 3160 | 0.636 | 1.12 | 1.32 | -0.0073065 | 3560 | 0.729 | 3160 | 0.636 | 1.12 | 1.32 | -0.00731
LFBldgSCEs_CliExCZ10 | Com-Iltg-dWatt-LF_OSbldg | SCE | s_Cli | Ex | CZ10 | 3.5489 | 0.00072554 | 0 | 3.9196 | 0.00095017 | -0.024223 | 3.165 | 0.000636 | 0 | 3.49 | 0.0008355 | -0.02299 |  | LF | Bldg | 3550 | 0.726 | 3160 | 0.636 | 1.1 | 1.31 | -0.0072638 | 3550 | 0.726 | 3160 | 0.636 | 1.1 | 1.31 | -0.00726
LFBldgSCEs_CliExCZ13 | Com-Iltg-dWatt-LF_OSbldg | SCE | s_Cli | Ex | CZ13 | 3.5599 | 0.00072819 | 0 | 3.8726 | 0.00094458 | -0.031114 | 3.165 | 0.000636 | 0 | 3.44 | 0.000827 | -0.02903 |  | LF | Bldg | 3560 | 0.728 | 3160 | 0.636 | 1.09 | 1.3 | -0.0091722 | 3560 | 0.728 | 3160 | 0.636 | 1.09 | 1.3 | -0.00917
LFBldgSCEs_CliExCZ14 | Com-Iltg-dWatt-LF_OSbldg | SCE | s_Cli | Ex | CZ14 | 3.5522 | 0.00072632 | 0 | 3.8783 | 0.00095097 | -0.03045 | 3.165 | 0.000636 | 0 | 3.445 | 0.000833 | -0.02863 |  | LF | Bldg | 3550 | 0.726 | 3160 | 0.636 | 1.09 | 1.31 | -0.0090458 | 3550 | 0.726 | 3160 | 0.636 | 1.09 | 1.31 | -0.00905
LFBldgSCEs_CliExCZ15 | Com-Iltg-dWatt-LF_OSbldg | SCE | s_Cli | Ex | CZ15 | 3.5489 | 0.00072554 | 0 | 4.1866 | 0.00095263 | -0.01396 | 3.165 | 0.000636 | 0 | 3.725 | 0.0008375 | -0.013345 |  | LF | Bldg | 3550 | 0.726 | 3160 | 0.636 | 1.18 | 1.32 | -0.0042164 | 3550 | 0.726 | 3160 | 0.636 | 1.18 | 1.32 | -0.00422
LFBldgSCEs_CliExCZ16 | Com-Iltg-dWatt-LF_OSbldg | SCE | s_Cli | Ex | CZ16 | 3.5549 | 0.000727 | 0 | 3.5449 | 0.00091228 | -0.048317 | 3.165 | 0.000636 | 0 | 3.155 | 0.000799 | -0.0447 |  | LF | Bldg | 3550 | 0.727 | 3160 | 0.636 | 0.997 | 1.26 | -0.014123 | 3550 | 0.727 | 3160 | 0.636 | 0.997 | 1.26 | -0.0141
LFBldgSCEs_CliExIOU | Com-Iltg-dWatt-LF_OSbldg | SCE | s_Cli | Ex | IOU | 3.5589 | 0.00072785 | 0 | 3.9583 | 0.00094296 | -0.024865 | 3.165 | 0.000636 | 0 | 3.5103 | 0.00082526 | -0.023547 |  | LF | Bldg | 3560 | 0.728 | 3160 | 0.636 | 1.11 | 1.3 | -0.0074399 | 3560 | 0.728 | 3160 | 0.636 | 1.11 | 1.3 | -0.00744
LFBldgSCEs_FStExCZ05 | Com-Iltg-dWatt-LF_OSbldg | SCE | s_FSt | Ex | CZ05 | 4.1666 | 0.00078601 | 0 | 4.2069 | 0.00096038 | -0.049891 | 4.115 | 0.0007785 | 0 | 4.16 | 0.000951 | -0.049 |  | LF | Bldg | 4170 | 0.786 | 4110 | 0.778 | 1.01 | 1.22 | -0.011908 | 4170 | 0.786 | 4110 | 0.778 | 1.01 | 1.22 | -0.0119
LFBldgSCEs_FStExCZ06 | Com-Iltg-dWatt-LF_OSbldg | SCE | s_FSt | Ex | CZ06 | 4.1666 | 0.000786 | 0 | 4.4816 | 0.00097088 | -0.034527 | 4.115 | 0.0007785 | 0 | 4.43 | 0.0009615 | -0.03387 |  | LF | Bldg | 4170 | 0.786 | 4110 | 0.778 | 1.08 | 1.24 | -0.0082309 | 4170 | 0.786 | 4110 | 0.778 | 1.08 | 1.24 | -0.00823
LFBldgSCEs_FStExCZ08 | Com-Iltg-dWatt-LF_OSbldg | SCE | s_FSt | Ex | CZ08 | 4.1666 | 0.000786 | 0 | 4.5463 | 0.00098038 | -0.030893 | 4.115 | 0.0007785 | 0 | 4.49 | 0.000971 | -0.03033 |  | LF | Bldg | 4170 | 0.786 | 4110 | 0.778 | 1.09 | 1.25 | -0.0073706 | 4170 | 0.786 | 4110 | 0.778 | 1.09 | 1.25 | -0.00737
LFBldgSCEs_FStExCZ09 | Com-Iltg-dWatt-LF_OSbldg | SCE | s_FSt | Ex | CZ09 | 4.1665 | 0.00078599 | 0 | 4.5365 | 0.00099586 | -0.031137 | 4.115 | 0.0007785 | 0 | 4.485 | 0.0009865 | -0.030575 |  | LF | Bldg | 4170 | 0.786 | 4110 | 0.778 | 1.09 | 1.27 | -0.0074301 | 4170 | 0.786 | 4110 | 0.778 | 1.09 | 1.27 | -0.00743
LFBldgSCEs_FStExCZ10 | Com-Iltg-dWatt-LF_OSbldg | SCE | s_FSt | Ex | CZ10 | 4.1638 | 0.0007856 | 0 | 4.4938 | 0.00099482 | -0.030757 | 4.115 | 0.0007785 | 0 | 4.445 | 0.0009855 | -0.03018 |  | LF | Bldg | 4160 | 0.786 | 4110 | 0.778 | 1.08 | 1.27 | -0.0073341 | 4160 | 0.786 | 4110 | 0.778 | 1.08 | 1.27 | -0.00733
LFBldgSCEs_FStExCZ13 | Com-Iltg-dWatt-LF_OSbldg | SCE | s_FSt | Ex | CZ13 | 4.1646 | 0.00078572 | 0 | 4.4546 | 0.00099252 | -0.037441 | 4.115 | 0.0007785 | 0 | 4.405 | 0.0009835 | -0.0369 |  | LF | Bldg | 4160 | 0.786 | 4110 | 0.778 | 1.07 | 1.26 | -0.0089672 | 4160 | 0.786 | 4110 | 0.778 | 1.07 | 1.26 | -0.00897
LFBldgSCEs_FStExCZ14 | Com-Iltg-dWatt-LF_OSbldg | SCE | s_FSt | Ex | CZ14 | 4.1643 | 0.00078567 | 0 | 4.4388 | 0.0010014 | -0.037333 | 4.115 | 0.0007785 | 0 | 4.385 | 0.0009915 | -0.03675 |  | LF | Bldg | 4160 | 0.786 | 4110 | 0.778 | 1.07 | 1.27 | -0.0089307 | 4160 | 0.786 | 4110 | 0.778 | 1.07 | 1.27 | -0.00893
LFBldgSCEs_FStExCZ15 | Com-Iltg-dWatt-LF_OSbldg | SCE | s_FSt | Ex | CZ15 | 4.1638 | 0.0007856 | 0 | 4.7733 | 0.00099682 | -0.016166 | 4.115 | 0.0007785 | 0 | 4.72 | 0.0009875 | -0.015855 |  | LF | Bldg | 4160 | 0.786 | 4110 | 0.778 | 1.15 | 1.27 | -0.003853 | 4160 | 0.786 | 4110 | 0.778 | 1.15 | 1.27 | -0.00385
LFBldgSCEs_FStExCZ16 | Com-Iltg-dWatt-LF_OSbldg | SCE | s_FSt | Ex | CZ16 | 4.1643 | 0.00078568 | 0 | 4.0549 | 0.00095797 | -0.058107 | 4.115 | 0.0007785 | 0 | 4.01 | 0.000949 | -0.0573 |  | LF | Bldg | 4160 | 0.786 | 4110 | 0.778 | 0.974 | 1.22 | -0.013925 | 4160 | 0.786 | 4110 | 0.778 | 0.974 | 1.22 | -0.0139
LFBldgSCEs_FStExIOU | Com-Iltg-dWatt-LF_OSbldg | SCE | s_FSt | Ex | IOU | 4.1657 | 0.00078587 | 0 | 4.5111 | 0.00098531 | -0.032111 | 4.115 | 0.0007785 | 0 | 4.4587 | 0.00097594 | -0.031527 |  | LF | Bldg | 4170 | 0.786 | 4110 | 0.778 | 1.08 | 1.25 | -0.0076614 | 4170 | 0.786 | 4110 | 0.778 | 1.08 | 1.25 | -0.00766
LFBldgSCEs_IndExCZ05 | Com-Iltg-dWatt-LF_OSbldg | SCE | s_Ind | Ex | CZ05 | 3.4187 | 0.00089591 | 0 | 3.7628 | 0.0011086 | -0.009534 | 3.315 | 0.000878 | 0 | 3.645 | 0.001085 | -0.009435 |  | LF | Bldg | 3420 | 0.896 | 3320 | 0.878 | 1.1 | 1.24 | -0.0028462 | 3420 | 0.896 | 3320 | 0.878 | 1.1 | 1.24 | -0.00285
LFBldgSCEs_IndExCZ06 | Com-Iltg-dWatt-LF_OSbldg | SCE | s_Ind | Ex | CZ06 | 3.4187 | 0.00089591 | 0 | 3.9079 | 0.0010839 | -0.0033669 | 3.315 | 0.000878 | 0 | 3.79 | 0.001065 | -0.0033325 |  | LF | Bldg | 3420 | 0.896 | 3320 | 0.878 | 1.14 | 1.21 | -0.0010053 | 3420 | 0.896 | 3320 | 0.878 | 1.14 | 1.21 | -0.00101
LFBldgSCEs_IndExCZ08 | Com-Iltg-dWatt-LF_OSbldg | SCE | s_Ind | Ex | CZ08 | 3.4187 | 0.00089592 | 0 | 3.9326 | 0.0011039 | -0.0026884 | 3.315 | 0.000878 | 0 | 3.81 | 0.001085 | -0.0026625 |  | LF | Bldg | 3420 | 0.896 | 3320 | 0.878 | 1.15 | 1.24 | -0.00080317 | 3420 | 0.896 | 3320 | 0.878 | 1.15 | 1.24 | -0.000803
LFBldgSCEs_IndExCZ09 | Com-Iltg-dWatt-LF_OSbldg | SCE | s_Ind | Ex | CZ09 | 3.4189 | 0.00089595 | 0 | 3.9128 | 0.0011233 | -0.0038825 | 3.315 | 0.000878 | 0 | 3.79 | 0.001095 | -0.00384 |  | LF | Bldg | 3420 | 0.896 | 3320 | 0.878 | 1.14 | 1.25 | -0.0011584 | 3420 | 0.896 | 3320 | 0.878 | 1.14 | 1.25 | -0.00116
LFBldgSCEs_IndExCZ10 | Com-Iltg-dWatt-LF_OSbldg | SCE | s_Ind | Ex | CZ10 | 3.4097 | 0.00089435 | 0 | 3.7926 | 0.0011165 | -0.004233 | 3.315 | 0.000878 | 0 | 3.685 | 0.001095 | -0.00419 |  | LF | Bldg | 3410 | 0.894 | 3320 | 0.878 | 1.11 | 1.25 | -0.001264 | 3410 | 0.894 | 3320 | 0.878 | 1.11 | 1.25 | -0.00126
LFBldgSCEs_IndExCZ13 | Com-Iltg-dWatt-LF_OSbldg | SCE | s_Ind | Ex | CZ13 | 3.4153 | 0.00089532 | 0 | 3.779 | 0.0010882 | -0.010019 | 3.315 | 0.000878 | 0 | 3.665 | 0.00107 | -0.009905 |  | LF | Bldg | 3420 | 0.895 | 3320 | 0.878 | 1.11 | 1.22 | -0.0029879 | 3420 | 0.895 | 3320 | 0.878 | 1.11 | 1.22 | -0.00299
LFBldgSCEs_IndExCZ14 | Com-Iltg-dWatt-LF_OSbldg | SCE | s_Ind | Ex | CZ14 | 3.4136 | 0.00089503 | 0 | 3.7671 | 0.0011129 | -0.011551 | 3.315 | 0.000878 | 0 | 3.655 | 0.001095 | -0.011475 |  | LF | Bldg | 3410 | 0.895 | 3320 | 0.878 | 1.1 | 1.25 | -0.0034615 | 3410 | 0.895 | 3320 | 0.878 | 1.1 | 1.25 | -0.00346
LFBldgSCEs_IndExCZ15 | Com-Iltg-dWatt-LF_OSbldg | SCE | s_Ind | Ex | CZ15 | 3.4097 | 0.00089435 | 0 | 3.9969 | 0.0011115 | -0.0009693 | 3.315 | 0.000878 | 0 | 3.885 | 0.00109 | -0.000965 |  | LF | Bldg | 3410 | 0.894 | 3320 | 0.878 | 1.17 | 1.24 | -0.0002911 | 3410 | 0.894 | 3320 | 0.878 | 1.17 | 1.24 | -0.000291
LFBldgSCEs_IndExCZ16 | Com-Iltg-dWatt-LF_OSbldg | SCE | s_Ind | Ex | CZ16 | 3.4128 | 0.0008949 | 0 | 3.5173 | 0.0010678 | -0.024587 | 3.315 | 0.000878 | 0 | 3.415 | 0.00105 | -0.024285 |  | LF | Bldg | 3410 | 0.895 | 3320 | 0.878 | 1.03 | 1.2 | -0.0073258 | 3410 | 0.895 | 3320 | 0.878 | 1.03 | 1.2 | -0.00733
LFBldgSCEs_IndExIOU | Com-Iltg-dWatt-LF_OSbldg | SCE | s_Ind | Ex | IOU | 3.4163 | 0.0008955 | 0 | 3.8857 | 0.0011041 | -0.0041693 | 3.315 | 0.000878 | 0 | 3.7682 | 0.0010833 | -0.0041273 |  | LF | Bldg | 3420 | 0.896 | 3320 | 0.878 | 1.14 | 1.23 | -0.001245 | 3420 | 0.896 | 3320 | 0.878 | 1.14 | 1.23 | -0.00125
LFBldgSCEs_MiCExCZ05 | Com-Iltg-dWatt-LF_OSbldg | SCE | s_MiC | Ex | CZ05 | 3.7074 | 0.00081586 | 0 | 3.9461 | 0.0010037 | -0.027251 | 3.49 | 0.00076167 | 0 | 3.7067 | 0.000936 | -0.026573 |  | LF | Bldg | 3710 | 0.816 | 3490 | 0.762 | 1.06 | 1.23 | -0.0076141 | 3710 | 0.816 | 3490 | 0.762 | 1.06 | 1.23 | -0.00761
LFBldgSCEs_MiCExCZ06 | Com-Iltg-dWatt-LF_OSbldg | SCE | s_MiC | Ex | CZ06 | 3.7074 | 0.00081586 | 0 | 4.1823 | 0.001014 | -0.013051 | 3.49 | 0.00076167 | 0 | 3.9333 | 0.00094533 | -0.01272 |  | LF | Bldg | 3710 | 0.816 | 3490 | 0.762 | 1.13 | 1.24 | -0.0036447 | 3710 | 0.816 | 3490 | 0.762 | 1.13 | 1.24 | -0.00364
LFBldgSCEs_MiCExCZ08 | Com-Iltg-dWatt-LF_OSbldg | SCE | s_MiC | Ex | CZ08 | 3.7074 | 0.00081586 | 0 | 4.2087 | 0.0010063 | -0.010986 | 3.49 | 0.00076167 | 0 | 3.9567 | 0.00093733 | -0.010677 |  | LF | Bldg | 3710 | 0.816 | 3490 | 0.762 | 1.13 | 1.23 | -0.0030592 | 3710 | 0.816 | 3490 | 0.762 | 1.13 | 1.23 | -0.00306
LFBldgSCEs_MiCExCZ09 | Com-Iltg-dWatt-LF_OSbldg | SCE | s_MiC | Ex | CZ09 | 3.7075 | 0.00081589 | 0 | 4.1857 | 0.0010206 | -0.012839 | 3.49 | 0.00076167 | 0 | 3.9367 | 0.00094933 | -0.012467 |  | LF | Bldg | 3710 | 0.816 | 3490 | 0.762 | 1.13 | 1.25 | -0.0035721 | 3710 | 0.816 | 3490 | 0.762 | 1.13 | 1.25 | -0.00357
LFBldgSCEs_MiCExCZ10 | Com-Iltg-dWatt-LF_OSbldg | SCE | s_MiC | Ex | CZ10 | 3.7 | 0.00081401 | 0 | 4.1107 | 0.00099031 | -0.013378 | 3.49 | 0.00076167 | 0 | 3.8733 | 0.00092367 | -0.013047 |  | LF | Bldg | 3700 | 0.814 | 3490 | 0.762 | 1.11 | 1.21 | -0.0037383 | 3700 | 0.814 | 3490 | 0.762 | 1.11 | 1.21 | -0.00374
LFBldgSCEs_MiCExCZ13 | Com-Iltg-dWatt-LF_OSbldg | SCE | s_MiC | Ex | CZ13 | 3.7065 | 0.00081565 | 0 | 4.0452 | 0.0010181 | -0.024649 | 3.49 | 0.00076167 | 0 | 3.8067 | 0.00094967 | -0.02382 |  | LF | Bldg | 3710 | 0.816 | 3490 | 0.762 | 1.09 | 1.25 | -0.0068252 | 3710 | 0.816 | 3490 | 0.762 | 1.09 | 1.25 | -0.00683
LFBldgSCEs_MiCExCZ14 | Com-Iltg-dWatt-LF_OSbldg | SCE | s_MiC | Ex | CZ14 | 3.7018 | 0.00081446 | 0 | 4.023 | 0.00099675 | -0.024046 | 3.49 | 0.00076167 | 0 | 3.7867 | 0.000928 | -0.02342 |  | LF | Bldg | 3700 | 0.814 | 3490 | 0.762 | 1.09 | 1.22 | -0.0067106 | 3700 | 0.814 | 3490 | 0.762 | 1.09 | 1.22 | -0.00671
LFBldgSCEs_MiCExCZ15 | Com-Iltg-dWatt-LF_OSbldg | SCE | s_MiC | Ex | CZ15 | 3.7 | 0.00081401 | 0 | 4.3659 | 0.0010216 | -0.0048035 | 3.49 | 0.00076167 | 0 | 4.1133 | 0.000955 | -0.0047 |  | LF | Bldg | 3700 | 0.814 | 3490 | 0.762 | 1.18 | 1.25 | -0.0013467 | 3700 | 0.814 | 3490 | 0.762 | 1.18 | 1.25 | -0.00135
LFBldgSCEs_MiCExCZ16 | Com-Iltg-dWatt-LF_OSbldg | SCE | s_MiC | Ex | CZ16 | 3.7037 | 0.00081494 | 0 | 3.6904 | 0.00098394 | -0.045513 | 3.49 | 0.00076167 | 0 | 3.4767 | 0.00091767 | -0.043933 |  | LF | Bldg | 3700 | 0.815 | 3490 | 0.762 | 0.996 | 1.2 | -0.012588 | 3700 | 0.815 | 3490 | 0.762 | 0.996 | 1.2 | -0.0126
LFBldgSCEs_MiCExIOU | Com-Iltg-dWatt-LF_OSbldg | SCE | s_MiC | Ex | IOU | 3.7052 | 0.00081531 | 0 | 4.164 | 0.0010065 | -0.013501 | 3.49 | 0.00076167 | 0 | 3.9178 | 0.00093799 | -0.013128 |  | LF | Bldg | 3710 | 0.815 | 3490 | 0.762 | 1.12 | 1.23 | -0.0037617 | 3710 | 0.815 | 3490 | 0.762 | 1.12 | 1.23 | -0.00376
LFBldgSCEs_TCUExCZ05 | Com-Iltg-dWatt-LF_OSbldg | SCE | s_TCU | Ex | CZ05 | 3.1633 | 0.00077292 | 0 | 3.2645 | 0.0009312 | -0.016331 | 2.946 | 0.0007154 | 0 | 3.028 | 0.000859 | -0.015364 |  | LF | Bldg | 3160 | 0.773 | 2950 | 0.715 | 1.03 | 1.2 | -0.0052152 | 3160 | 0.773 | 2950 | 0.715 | 1.03 | 1.2 | -0.00522
LFBldgSCEs_TCUExCZ06 | Com-Iltg-dWatt-LF_OSbldg | SCE | s_TCU | Ex | CZ06 | 3.1631 | 0.00077287 | 0 | 3.4337 | 0.00094179 | -0.0083561 | 2.946 | 0.0007154 | 0 | 3.188 | 0.0008704 | -0.007806 |  | LF | Bldg | 3160 | 0.773 | 2950 | 0.715 | 1.08 | 1.22 | -0.0026497 | 3160 | 0.773 | 2950 | 0.715 | 1.08 | 1.22 | -0.00265
LFBldgSCEs_TCUExCZ08 | Com-Iltg-dWatt-LF_OSbldg | SCE | s_TCU | Ex | CZ08 | 3.1631 | 0.00077287 | 0 | 3.4595 | 0.00094457 | -0.0075219 | 2.946 | 0.0007154 | 0 | 3.21 | 0.0008728 | -0.007004 |  | LF | Bldg | 3160 | 0.773 | 2950 | 0.715 | 1.09 | 1.22 | -0.0023775 | 3160 | 0.773 | 2950 | 0.715 | 1.09 | 1.22 | -0.00238
LFBldgSCEs_TCUExCZ09 | Com-Iltg-dWatt-LF_OSbldg | SCE | s_TCU | Ex | CZ09 | 3.1621 | 0.00077261 | 0 | 3.4427 | 0.00096003 | -0.0090695 | 2.946 | 0.0007154 | 0 | 3.198 | 0.0008848 | -0.008478 |  | LF | Bldg | 3160 | 0.773 | 2950 | 0.715 | 1.09 | 1.24 | -0.0028778 | 3160 | 0.773 | 2950 | 0.715 | 1.09 | 1.24 | -0.00288
LFBldgSCEs_TCUExCZ10 | Com-Iltg-dWatt-LF_OSbldg | SCE | s_TCU | Ex | CZ10 | 3.1508 | 0.00076931 | 0 | 3.3963 | 0.00094576 | -0.008751 | 2.946 | 0.0007154 | 0 | 3.166 | 0.0008764 | -0.008246 |  | LF | Bldg | 3150 | 0.769 | 2950 | 0.715 | 1.07 | 1.23 | -0.002799 | 3150 | 0.769 | 2950 | 0.715 | 1.07 | 1.23 | -0.0028
LFBldgSCEs_TCUExCZ13 | Com-Iltg-dWatt-LF_OSbldg | SCE | s_TCU | Ex | CZ13 | 3.1572 | 0.0007711 | 0 | 3.3656 | 0.00093708 | -0.014446 | 2.946 | 0.0007154 | 0 | 3.132 | 0.000868 | -0.013512 |  | LF | Bldg | 3160 | 0.771 | 2950 | 0.715 | 1.06 | 1.21 | -0.0045866 | 3160 | 0.771 | 2950 | 0.715 | 1.06 | 1.21 | -0.00459
LFBldgSCEs_TCUExCZ14 | Com-Iltg-dWatt-LF_OSbldg | SCE | s_TCU | Ex | CZ14 | 3.154 | 0.00077022 | 0 | 3.3501 | 0.00094566 | -0.014745 | 2.946 | 0.0007154 | 0 | 3.12 | 0.000876 | -0.013972 |  | LF | Bldg | 3150 | 0.77 | 2950 | 0.715 | 1.06 | 1.22 | -0.0047427 | 3150 | 0.77 | 2950 | 0.715 | 1.06 | 1.22 | -0.00474
LFBldgSCEs_TCUExCZ15 | Com-Iltg-dWatt-LF_OSbldg | SCE | s_TCU | Ex | CZ15 | 3.1508 | 0.00076931 | 0 | 3.5669 | 0.00094156 | -0.0037513 | 2.946 | 0.0007154 | 0 | 3.324 | 0.0008722 | -0.003518 |  | LF | Bldg | 3150 | 0.769 | 2950 | 0.715 | 1.13 | 1.22 | -0.0011942 | 3150 | 0.769 | 2950 | 0.715 | 1.13 | 1.22 | -0.00119
LFBldgSCEs_TCUExCZ16 | Com-Iltg-dWatt-LF_OSbldg | SCE | s_TCU | Ex | CZ16 | 3.1545 | 0.00077028 | 0 | 3.1306 | 0.00091927 | -0.026168 | 2.946 | 0.0007154 | 0 | 2.92 | 0.0008526 | -0.02448 |  | LF | Bldg | 3150 | 0.77 | 2950 | 0.715 | 0.991 | 1.19 | -0.0083096 | 3150 | 0.77 | 2950 | 0.715 | 0.991 | 1.19 | -0.00831
LFBldgSCEs_TCUExIOU | Com-Iltg-dWatt-LF_OSbldg | SCE | s_TCU | Ex | IOU | 3.1597 | 0.00077184 | 0 | 3.4331 | 0.0009458 | -0.0087553 | 2.946 | 0.0007154 | 0 | 3.1906 | 0.00087436 | -0.0081885 |  | LF | Bldg | 3160 | 0.772 | 2950 | 0.715 | 1.08 | 1.22 | -0.0027795 | 3160 | 0.772 | 2950 | 0.715 | 1.08 | 1.22 | -0.00278
LFBldgSCESCnExCZ05 | Com-Iltg-dWatt-LF_OSbldg | SCE | SCn | Ex | CZ05 | 3.4183 | 0.00069925 | 0 | 3.1583 | 0.00088402 | -0.035883 | 3.39 | 0.000687 | 0 | 3.13 | 0.000868 | -0.0356 |  | LF | Bldg | 3420 | 0.699 | 3390 | 0.687 | 0.923 | 1.26 | -0.010501 | 3420 | 0.699 | 3390 | 0.687 | 0.923 | 1.26 | -0.0105
LFBldgSCESCnExCZ06 | Com-Iltg-dWatt-LF_OSbldg | SCE | SCn | Ex | CZ06 | 3.4183 | 0.00069924 | 0 | 3.5281 | 0.00091599 | -0.018888 | 3.39 | 0.000687 | 0 | 3.4904 | 0.00089904 | -0.0187 |  | LF | Bldg | 3420 | 0.699 | 3390 | 0.687 | 1.03 | 1.31 | -0.0055162 | 3420 | 0.699 | 3390 | 0.687 | 1.03 | 1.31 | -0.00552
LFBldgSCESCnExCZ08 | Com-Iltg-dWatt-LF_OSbldg | SCE | SCn | Ex | CZ08 | 3.4183 | 0.00069925 | 0 | 3.5877 | 0.00091302 | -0.016289 | 3.39 | 0.000687 | 0 | 3.55 | 0.000897 | -0.0161 |  | LF | Bldg | 3420 | 0.699 | 3390 | 0.687 | 1.05 | 1.31 | -0.0047493 | 3420 | 0.699 | 3390 | 0.687 | 1.05 | 1.31 | -0.00475
LFBldgSCESCnExCZ09 | Com-Iltg-dWatt-LF_OSbldg | SCE | SCn | Ex | CZ09 | 3.4296 | 0.0007029 | 0 | 3.5789 | 0.00093472 | -0.019245 | 3.39 | 0.000687 | 0 | 3.5329 | 0.00091329 | -0.019 |  | LF | Bldg | 3430 | 0.703 | 3390 | 0.687 | 1.04 | 1.33 | -0.0056047 | 3430 | 0.703 | 3390 | 0.687 | 1.04 | 1.33 | -0.0056
LFBldgSCESCnExCZ10 | Com-Iltg-dWatt-LF_OSbldg | SCE | SCn | Ex | CZ10 | 3.4249 | 0.00070096 | 0 | 3.5602 | 0.00091925 | -0.020115 | 3.39 | 0.000687 | 0 | 3.52 | 0.000901 | -0.0199 |  | LF | Bldg | 3420 | 0.701 | 3390 | 0.687 | 1.04 | 1.31 | -0.0058702 | 3420 | 0.701 | 3390 | 0.687 | 1.04 | 1.31 | -0.00587
LFBldgSCESCnExCZ13 | Com-Iltg-dWatt-LF_OSbldg | SCE | SCn | Ex | CZ13 | 3.4248 | 0.0007011 | 0 | 3.4948 | 0.00090744 | -0.02674 | 3.39 | 0.000687 | 0 | 3.46 | 0.00088923 | -0.0265 |  | LF | Bldg | 3420 | 0.701 | 3390 | 0.687 | 1.02 | 1.29 | -0.0078171 | 3420 | 0.701 | 3390 | 0.687 | 1.02 | 1.29 | -0.00782
LFBldgSCESCnExCZ14 | Com-Iltg-dWatt-LF_OSbldg | SCE | SCn | Ex | CZ14 | 3.415 | 0.00069785 | 0 | 3.4634 | 0.00090219 | -0.02935 | 3.39 | 0.000687 | 0 | 3.43 | 0.000888 | -0.0291 |  | LF | Bldg | 3420 | 0.698 | 3390 | 0.687 | 1.01 | 1.29 | -0.0085841 | 3420 | 0.698 | 3390 | 0.687 | 1.01 | 1.29 | -0.00858
LFBldgSCESCnExCZ15 | Com-Iltg-dWatt-LF_OSbldg | SCE | SCn | Ex | CZ15 | 3.4141 | 0.00069744 | 0 | 3.7921 | 0.00090565 | -0.0080242 | 3.39 | 0.000687 | 0 | 3.76 | 0.000892 | -0.00796 |  | LF | Bldg | 3410 | 0.697 | 3390 | 0.687 | 1.11 | 1.3 | -0.0023481 | 3410 | 0.697 | 3390 | 0.687 | 1.11 | 1.3 | -0.00235
LFBldgSCESCnExCZ16 | Com-Iltg-dWatt-LF_OSbldg | SCE | SCn | Ex | CZ16 | 3.4194 | 0.00069918 | 0 | 3.1194 | 0.0008788 | -0.042087 | 3.39 | 0.000687 | 0 | 3.0913 | 0.00086313 | -0.0417 |  | LF | Bldg | 3420 | 0.699 | 3390 | 0.687 | 0.912 | 1.26 | -0.012301 | 3420 | 0.699 | 3390 | 0.687 | 0.912 | 1.26 | -0.0123
LFBldgSCESCnExIOU | Com-Iltg-dWatt-LF_OSbldg | SCE | SCn | Ex | IOU | 3.4217 | 0.00070019 | 0 | 3.5658 | 0.00091728 | -0.018561 | 3.39 | 0.000687 | 0 | 3.5266 | 0.00089984 | -0.018356 |  | LF | Bldg | 3420 | 0.7 | 3390 | 0.687 | 1.04 | 1.31 | -0.0054148 | 3420 | 0.7 | 3390 | 0.687 | 1.04 | 1.31 | -0.00541
LFBldgSCESCnNewCZ05 | Com-Iltg-dWatt-LF_OSbldg | SCE | SCn | New | CZ05 | 3.39 | 0.000687 | 0 | 3.15 | 0.000866 | -0.0376 | 3.39 | 0.000687 | 0 | 3.15 | 0.000866 | -0.0376 |  | LF | Bldg | 3390 | 0.687 | 3390 | 0.687 | 0.929 | 1.26 | -0.011091 | 3390 | 0.687 | 3390 | 0.687 | 0.929 | 1.26 | -0.0111
LFBldgSCESCnNewCZ06 | Com-Iltg-dWatt-LF_OSbldg | SCE | SCn | New | CZ06 | 3.39 | 0.000687 | 0 | 3.39 | 0.00083 | -0.02 | 3.39 | 0.000687 | 0 | 3.39 | 0.00083 | -0.02 |  | LF | Bldg | 3390 | 0.687 | 3390 | 0.687 | 1 | 1.21 | -0.0058997 | 3390 | 0.687 | 3390 | 0.687 | 1 | 1.21 | -0.0059
LFBldgSCESCnNewCZ08 | Com-Iltg-dWatt-LF_OSbldg | SCE | SCn | New | CZ08 | 3.39 | 0.000687 | 0 | 3.47 | 0.000843 | -0.0174 | 3.39 | 0.000687 | 0 | 3.47 | 0.000843 | -0.0174 |  | LF | Bldg | 3390 | 0.687 | 3390 | 0.687 | 1.02 | 1.23 | -0.0051327 | 3390 | 0.687 | 3390 | 0.687 | 1.02 | 1.23 | -0.00513
LFBldgSCESCnNewCZ09 | Com-Iltg-dWatt-LF_OSbldg | SCE | SCn | New | CZ09 | 3.39 | 0.000687 | 0 | 3.47 | 0.000872 | -0.0187 | 3.39 | 0.000687 | 0 | 3.47 | 0.000872 | -0.0187 |  | LF | Bldg | 3390 | 0.687 | 3390 | 0.687 | 1.02 | 1.27 | -0.0055162 | 3390 | 0.687 | 3390 | 0.687 | 1.02 | 1.27 | -0.00552
LFBldgSCESCnNewCZ10 | Com-Iltg-dWatt-LF_OSbldg | SCE | SCn | New | CZ10 | 3.39 | 0.000687 | 0 | 3.48 | 0.000864 | -0.0203 | 3.39 | 0.000687 | 0 | 3.48 | 0.000864 | -0.0203 |  | LF | Bldg | 3390 | 0.687 | 3390 | 0.687 | 1.03 | 1.26 | -0.0059882 | 3390 | 0.687 | 3390 | 0.687 | 1.03 | 1.26 | -0.00599
LFBldgSCESCnNewCZ13 | Com-Iltg-dWatt-LF_OSbldg | SCE | SCn | New | CZ13 | 3.39 | 0.000687 | 0 | 3.38 | 0.00084 | -0.0266 | 3.39 | 0.000687 | 0 | 3.38 | 0.00084 | -0.0266 |  | LF | Bldg | 3390 | 0.687 | 3390 | 0.687 | 0.997 | 1.22 | -0.0078466 | 3390 | 0.687 | 3390 | 0.687 | 0.997 | 1.22 | -0.00785
LFBldgSCESCnNewCZ14 | Com-Iltg-dWatt-LF_OSbldg | SCE | SCn | New | CZ14 | 3.39 | 0.000687 | 0 | 3.42 | 0.000861 | -0.0298 | 3.39 | 0.000687 | 0 | 3.42 | 0.000861 | -0.0298 |  | LF | Bldg | 3390 | 0.687 | 3390 | 0.687 | 1.01 | 1.25 | -0.0087906 | 3390 | 0.687 | 3390 | 0.687 | 1.01 | 1.25 | -0.00879
LFBldgSCESCnNewCZ15 | Com-Iltg-dWatt-LF_OSbldg | SCE | SCn | New | CZ15 | 3.39 | 0.000687 | 0 | 3.7 | 0.000868 | -0.00637 | 3.39 | 0.000687 | 0 | 3.7 | 0.000868 | -0.00637 |  | LF | Bldg | 3390 | 0.687 | 3390 | 0.687 | 1.09 | 1.26 | -0.0018791 | 3390 | 0.687 | 3390 | 0.687 | 1.09 | 1.26 | -0.00188
LFBldgSCESCnNewCZ16 | Com-Iltg-dWatt-LF_OSbldg | SCE | SCn | New | CZ16 | 3.39 | 0.000687 | 0 | 3.07 | 0.000831 | -0.0434 | 3.39 | 0.000687 | 0 | 3.07 | 0.000831 | -0.0434 |  | LF | Bldg | 3390 | 0.687 | 3390 | 0.687 | 0.906 | 1.21 | -0.012802 | 3390 | 0.687 | 3390 | 0.687 | 0.906 | 1.21 | -0.0128
LFBldgSCESCnNewIOU | Com-Iltg-dWatt-LF_OSbldg | SCE | SCn | New | IOU | 3.39 | 0.000687 | 0 | 3.4666 | 0.00085731 | -0.019978 | 3.39 | 0.000687 | 0 | 3.4666 | 0.00085731 | -0.019978 |  | LF | Bldg | 3390 | 0.687 | 3390 | 0.687 | 1.02 | 1.25 | -0.0058932 | 3390 | 0.687 | 3390 | 0.687 | 1.02 | 1.25 | -0.00589
LFBldgSCESUnExCZ05 | Com-Iltg-dWatt-LF_OSbldg | SCE | SUn | Ex | CZ05 | 3.4198 | 0.00069974 | 0 | 3.4198 | 0.00069974 | 0 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 |  | LF | Bldg | 3420 | 0.7 | 3390 | 0.687 | 1 | 1 | 0 | 3420 | 0.7 | 3390 | 0.687 | 1 | 1 | 0
LFBldgSCESUnExCZ06 | Com-Iltg-dWatt-LF_OSbldg | SCE | SUn | Ex | CZ06 | 3.4198 | 0.00069975 | 0 | 3.4198 | 0.00069975 | 0 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 |  | LF | Bldg | 3420 | 0.7 | 3390 | 0.687 | 1 | 1 | 0 | 3420 | 0.7 | 3390 | 0.687 | 1 | 1 | 0
LFBldgSCESUnExCZ08 | Com-Iltg-dWatt-LF_OSbldg | SCE | SUn | Ex | CZ08 | 3.4198 | 0.00069975 | 0 | 3.4198 | 0.00069975 | 0 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 |  | LF | Bldg | 3420 | 0.7 | 3390 | 0.687 | 1 | 1 | 0 | 3420 | 0.7 | 3390 | 0.687 | 1 | 1 | 0
LFBldgSCESUnExCZ09 | Com-Iltg-dWatt-LF_OSbldg | SCE | SUn | Ex | CZ09 | 3.4327 | 0.00070393 | 0 | 3.4327 | 0.00070393 | 0 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 |  | LF | Bldg | 3430 | 0.704 | 3390 | 0.687 | 1 | 1 | 0 | 3430 | 0.704 | 3390 | 0.687 | 1 | 1 | 0
LFBldgSCESUnExCZ10 | Com-Iltg-dWatt-LF_OSbldg | SCE | SUn | Ex | CZ10 | 3.4163 | 0.00069817 | 0 | 3.4163 | 0.00069817 | 0 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 |  | LF | Bldg | 3420 | 0.698 | 3390 | 0.687 | 1 | 1 | 0 | 3420 | 0.698 | 3390 | 0.687 | 1 | 1 | 0
LFBldgSCESUnExCZ13 | Com-Iltg-dWatt-LF_OSbldg | SCE | SUn | Ex | CZ13 | 3.4208 | 0.0006998 | 0 | 3.4208 | 0.0006998 | 0 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 |  | LF | Bldg | 3420 | 0.7 | 3390 | 0.687 | 1 | 1 | 0 | 3420 | 0.7 | 3390 | 0.687 | 1 | 1 | 0
LFBldgSCESUnExCZ14 | Com-Iltg-dWatt-LF_OSbldg | SCE | SUn | Ex | CZ14 | 3.415 | 0.00069785 | 0 | 3.415 | 0.00069785 | 0 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 |  | LF | Bldg | 3420 | 0.698 | 3390 | 0.687 | 1 | 1 | 0 | 3420 | 0.698 | 3390 | 0.687 | 1 | 1 | 0
LFBldgSCESUnExCZ15 | Com-Iltg-dWatt-LF_OSbldg | SCE | SUn | Ex | CZ15 | 3.4141 | 0.00069744 | 0 | 3.4141 | 0.00069744 | 0 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 |  | LF | Bldg | 3410 | 0.697 | 3390 | 0.687 | 1 | 1 | 0 | 3410 | 0.697 | 3390 | 0.687 | 1 | 1 | 0
LFBldgSCESUnExCZ16 | Com-Iltg-dWatt-LF_OSbldg | SCE | SUn | Ex | CZ16 | 3.422 | 0.00070003 | 0 | 3.422 | 0.00070003 | 0 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 |  | LF | Bldg | 3420 | 0.7 | 3390 | 0.687 | 1 | 1 | 0 | 3420 | 0.7 | 3390 | 0.687 | 1 | 1 | 0
LFBldgSCESUnExIOU | Com-Iltg-dWatt-LF_OSbldg | SCE | SUn | Ex | IOU | 3.42 | 0.00069965 | 0 | 3.42 | 0.00069965 | 0 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 |  | LF | Bldg | 3420 | 0.7 | 3390 | 0.687 | 1 | 1 | 0 | 3420 | 0.7 | 3390 | 0.687 | 1 | 1 | 0
LFBldgSCESUnNewCZ05 | Com-Iltg-dWatt-LF_OSbldg | SCE | SUn | New | CZ05 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 |  | LF | Bldg | 3390 | 0.687 | 3390 | 0.687 | 1 | 1 | 0 | 3390 | 0.687 | 3390 | 0.687 | 1 | 1 | 0
LFBldgSCESUnNewCZ06 | Com-Iltg-dWatt-LF_OSbldg | SCE | SUn | New | CZ06 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 |  | LF | Bldg | 3390 | 0.687 | 3390 | 0.687 | 1 | 1 | 0 | 3390 | 0.687 | 3390 | 0.687 | 1 | 1 | 0
LFBldgSCESUnNewCZ08 | Com-Iltg-dWatt-LF_OSbldg | SCE | SUn | New | CZ08 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 |  | LF | Bldg | 3390 | 0.687 | 3390 | 0.687 | 1 | 1 | 0 | 3390 | 0.687 | 3390 | 0.687 | 1 | 1 | 0
LFBldgSCESUnNewCZ09 | Com-Iltg-dWatt-LF_OSbldg | SCE | SUn | New | CZ09 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 |  | LF | Bldg | 3390 | 0.687 | 3390 | 0.687 | 1 | 1 | 0 | 3390 | 0.687 | 3390 | 0.687 | 1 | 1 | 0
LFBldgSCESUnNewCZ10 | Com-Iltg-dWatt-LF_OSbldg | SCE | SUn | New | CZ10 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 |  | LF | Bldg | 3390 | 0.687 | 3390 | 0.687 | 1 | 1 | 0 | 3390 | 0.687 | 3390 | 0.687 | 1 | 1 | 0
LFBldgSCESUnNewCZ13 | Com-Iltg-dWatt-LF_OSbldg | SCE | SUn | New | CZ13 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 |  | LF | Bldg | 3390 | 0.687 | 3390 | 0.687 | 1 | 1 | 0 | 3390 | 0.687 | 3390 | 0.687 | 1 | 1 | 0
LFBldgSCESUnNewCZ14 | Com-Iltg-dWatt-LF_OSbldg | SCE | SUn | New | CZ14 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 |  | LF | Bldg | 3390 | 0.687 | 3390 | 0.687 | 1 | 1 | 0 | 3390 | 0.687 | 3390 | 0.687 | 1 | 1 | 0
LFBldgSCESUnNewCZ15 | Com-Iltg-dWatt-LF_OSbldg | SCE | SUn | New | CZ15 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 |  | LF | Bldg | 3390 | 0.687 | 3390 | 0.687 | 1 | 1 | 0 | 3390 | 0.687 | 3390 | 0.687 | 1 | 1 | 0
LFBldgSCESUnNewCZ16 | Com-Iltg-dWatt-LF_OSbldg | SCE | SUn | New | CZ16 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 |  | LF | Bldg | 3390 | 0.687 | 3390 | 0.687 | 1 | 1 | 0 | 3390 | 0.687 | 3390 | 0.687 | 1 | 1 | 0
LFBldgSCESUnNewIOU | Com-Iltg-dWatt-LF_OSbldg | SCE | SUn | New | IOU | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 |  | LF | Bldg | 3390 | 0.687 | 3390 | 0.687 | 1 | 1 | 0 | 3390 | 0.687 | 3390 | 0.687 | 1 | 1 | 0
LFBldgSCEWRfExCZ06 | Com-Iltg-dWatt-LF_OSbldg | SCE | WRf | Ex | CZ06 | 4.771 | 0.00055605 | 0 | 7.5316 | 0.00069707 | 0 | 4.5407 | 0.000544 | 0 | 7.1707 | 0.000682 | 0 |  | LF | Bldg | 4770 | 0.556 | 4540 | 0.544 | 1.58 | 1.25 | 0 | 4770 | 0.556 | 4540 | 0.544 | 1.58 | 1.25 | 0
LFBldgSCEWRfExCZ08 | Com-Iltg-dWatt-LF_OSbldg | SCE | WRf | Ex | CZ08 | 4.7711 | 0.00055606 | 0 | 7.6218 | 0.00069808 | 0 | 4.5407 | 0.000544 | 0 | 7.26 | 0.000683 | 0 |  | LF | Bldg | 4770 | 0.556 | 4540 | 0.544 | 1.6 | 1.26 | 0 | 4770 | 0.556 | 4540 | 0.544 | 1.6 | 1.26 | 0
LFBldgSCEWRfExCZ09 | Com-Iltg-dWatt-LF_OSbldg | SCE | WRf | Ex | CZ09 | 4.7532 | 0.0005551 | 0 | 7.5435 | 0.00071187 | 0 | 4.5405 | 0.000544 | 0 | 7.2105 | 0.00069707 | 0 |  | LF | Bldg | 4750 | 0.555 | 4540 | 0.544 | 1.59 | 1.28 | 0 | 4750 | 0.555 | 4540 | 0.544 | 1.59 | 1.28 | 0
LFBldgSCEWRfExCZ10 | Com-Iltg-dWatt-LF_OSbldg | SCE | WRf | Ex | CZ10 | 4.7496 | 0.0005549 | 0 | 7.5086 | 0.00070163 | 0 | 4.5406 | 0.000544 | 0 | 7.1906 | 0.00068709 | 0 |  | LF | Bldg | 4750 | 0.555 | 4540 | 0.544 | 1.58 | 1.26 | 0 | 4750 | 0.555 | 4540 | 0.544 | 1.58 | 1.26 | 0
LFBldgSCEWRfExCZ13 | Com-Iltg-dWatt-LF_OSbldg | SCE | WRf | Ex | CZ13 | 4.7393 | 0.00055435 | 0 | 7.3527 | 0.00069893 | 0 | 4.5409 | 0.000544 | 0 | 7.0509 | 0.00068514 | 0 |  | LF | Bldg | 4740 | 0.554 | 4540 | 0.544 | 1.55 | 1.26 | 0 | 4740 | 0.554 | 4540 | 0.544 | 1.55 | 1.26 | 0
LFBldgSCEWRfExCZ14 | Com-Iltg-dWatt-LF_OSbldg | SCE | WRf | Ex | CZ14 | 4.7499 | 0.00055492 | 0 | 7.229 | 0.00069665 | 0 | 4.5406 | 0.000544 | 0 | 6.9197 | 0.000683 | 0 |  | LF | Bldg | 4750 | 0.555 | 4540 | 0.544 | 1.52 | 1.26 | 0 | 4750 | 0.555 | 4540 | 0.544 | 1.52 | 1.26 | 0
LFBldgSCEWRfExCZ15 | Com-Iltg-dWatt-LF_OSbldg | SCE | WRf | Ex | CZ15 | 4.7498 | 0.0005549 | 0 | 7.737 | 0.00070162 | 0 | 4.5409 | 0.000544 | 0 | 7.4009 | 0.00068709 | 0 |  | LF | Bldg | 4750 | 0.555 | 4540 | 0.544 | 1.63 | 1.26 | 0 | 4750 | 0.555 | 4540 | 0.544 | 1.63 | 1.26 | 0
LFBldgSCEWRfExCZ16 | Com-Iltg-dWatt-LF_OSbldg | SCE | WRf | Ex | CZ16 | 4.7917 | 0.00055718 | 0 | 6.6306 | 0.00079368 | -0.00016392 | 4.5414 | 0.000544 | 0 | 6.2877 | 0.000775 | -0.00015513 |  | LF | Bldg | 4790 | 0.557 | 4540 | 0.544 | 1.38 | 1.42 | -3.416e-05 | 4790 | 0.557 | 4540 | 0.544 | 1.38 | 1.42 | -3.42e-05
LFBldgSCEWRfExIOU | Com-Iltg-dWatt-LF_OSbldg | SCE | WRf | Ex | IOU | 4.7604 | 0.00055549 | 0 | 7.5286 | 0.00070024 | -5.2655e-07 | 4.5407 | 0.000544 | 0 | 7.1872 | 0.00068548 | -4.9832e-07 |  | LF | Bldg | 4760 | 0.555 | 4540 | 0.544 | 1.58 | 1.26 | -1.0975e-07 | 4760 | 0.555 | 4540 | 0.544 | 1.58 | 1.26 | -1.1e-07
LFBldgSCEWRfNewCZ05 | Com-Iltg-dWatt-LF_OSbldg | SCE | WRf | New | CZ05 | 4.55 | 0.000544 | 0 | 5.88 | 0.000904 | 0 | 4.55 | 0.000544 | 0 | 5.88 | 0.000904 | 0 |  | LF | Bldg | 4550 | 0.544 | 4550 | 0.544 | 1.29 | 1.66 | 0 | 4550 | 0.544 | 4550 | 0.544 | 1.29 | 1.66 | 0
LFBldgSCEWRfNewCZ06 | Com-Iltg-dWatt-LF_OSbldg | SCE | WRf | New | CZ06 | 4.55 | 0.000544 | 0 | 6.55 | 0.000671 | 0 | 4.55 | 0.000544 | 0 | 6.55 | 0.000671 | 0 |  | LF | Bldg | 4550 | 0.544 | 4550 | 0.544 | 1.44 | 1.23 | 0 | 4550 | 0.544 | 4550 | 0.544 | 1.44 | 1.23 | 0
LFBldgSCEWRfNewCZ08 | Com-Iltg-dWatt-LF_OSbldg | SCE | WRf | New | CZ08 | 4.55 | 0.000544 | 0 | 6.48 | 0.000673 | 0 | 4.55 | 0.000544 | 0 | 6.48 | 0.000673 | 0 |  | LF | Bldg | 4550 | 0.544 | 4550 | 0.544 | 1.42 | 1.24 | 0 | 4550 | 0.544 | 4550 | 0.544 | 1.42 | 1.24 | 0
LFBldgSCEWRfNewCZ09 | Com-Iltg-dWatt-LF_OSbldg | SCE | WRf | New | CZ09 | 4.55 | 0.000544 | 0 | 6.42 | 0.000695 | 0 | 4.55 | 0.000544 | 0 | 6.42 | 0.000695 | 0 |  | LF | Bldg | 4550 | 0.544 | 4550 | 0.544 | 1.41 | 1.28 | 0 | 4550 | 0.544 | 4550 | 0.544 | 1.41 | 1.28 | 0
LFBldgSCEWRfNewCZ10 | Com-Iltg-dWatt-LF_OSbldg | SCE | WRf | New | CZ10 | 4.55 | 0.000544 | 0 | 6.39 | 0.000681 | 0 | 4.55 | 0.000544 | 0 | 6.39 | 0.000681 | 0 |  | LF | Bldg | 4550 | 0.544 | 4550 | 0.544 | 1.4 | 1.25 | 0 | 4550 | 0.544 | 4550 | 0.544 | 1.4 | 1.25 | 0
LFBldgSCEWRfNewCZ13 | Com-Iltg-dWatt-LF_OSbldg | SCE | WRf | New | CZ13 | 4.55 | 0.000544 | 0 | 6.38 | 0.000681 | 0 | 4.55 | 0.000544 | 0 | 6.38 | 0.000681 | 0 |  | LF | Bldg | 4550 | 0.544 | 4550 | 0.544 | 1.4 | 1.25 | 0 | 4550 | 0.544 | 4550 | 0.544 | 1.4 | 1.25 | 0
LFBldgSCEWRfNewCZ14 | Com-Iltg-dWatt-LF_OSbldg | SCE | WRf | New | CZ14 | 4.55 | 0.000544 | 0 | 6.26 | 0.000675 | 0 | 4.55 | 0.000544 | 0 | 6.26 | 0.000675 | 0 |  | LF | Bldg | 4550 | 0.544 | 4550 | 0.544 | 1.38 | 1.24 | 0 | 4550 | 0.544 | 4550 | 0.544 | 1.38 | 1.24 | 0
LFBldgSCEWRfNewCZ15 | Com-Iltg-dWatt-LF_OSbldg | SCE | WRf | New | CZ15 | 4.55 | 0.000544 | 0 | 6.69 | 0.00068 | 0 | 4.55 | 0.000544 | 0 | 6.69 | 0.00068 | 0 |  | LF | Bldg | 4550 | 0.544 | 4550 | 0.544 | 1.47 | 1.25 | 0 | 4550 | 0.544 | 4550 | 0.544 | 1.47 | 1.25 | 0
LFBldgSCEWRfNewCZ16 | Com-Iltg-dWatt-LF_OSbldg | SCE | WRf | New | CZ16 | 4.55 | 0.000544 | 0 | 5.73 | 0.00109 | 0 | 4.55 | 0.000544 | 0 | 5.73 | 0.00109 | 0 |  | LF | Bldg | 4550 | 0.544 | 4550 | 0.544 | 1.26 | 2 | 0 | 4550 | 0.544 | 4550 | 0.544 | 1.26 | 2 | 0
LFBldgSCEWRfNewIOU | Com-Iltg-dWatt-LF_OSbldg | SCE | WRf | New | IOU | 4.55 | 0.000544 | 0 | 6.4425 | 0.00068042 | 0 | 4.55 | 0.000544 | 0 | 6.4425 | 0.00068042 | 0 |  | LF | Bldg | 4550 | 0.544 | 4550 | 0.544 | 1.42 | 1.25 | 0 | 4550 | 0.544 | 4550 | 0.544 | 1.42 | 1.25 | 0
LFBldgSDGAsmExCZ06 | Com-Iltg-dWatt-LF_OSbldg | SDG | Asm | Ex | CZ06 | 2.6128 | 0.00053234 | 0 | 2.8729 | 0.00065647 | -0.014605 | 2.5329 | 0.00051918 | 0 | 2.792 | 0.00064108 | -0.0142 |  | LF | Bldg | 2610 | 0.532 | 2530 | 0.519 | 1.1 | 1.23 | -0.0056062 | 2610 | 0.532 | 2530 | 0.519 | 1.1 | 1.23 | -0.00561
LFBldgSDGAsmExCZ07 | Com-Iltg-dWatt-LF_OSbldg | SDG | Asm | Ex | CZ07 | 2.6128 | 0.00053234 | 0 | 2.8829 | 0.00065547 | -0.013514 | 2.5329 | 0.00051918 | 0 | 2.802 | 0.00063928 | -0.013109 |  | LF | Bldg | 2610 | 0.532 | 2530 | 0.519 | 1.11 | 1.23 | -0.0051756 | 2610 | 0.532 | 2530 | 0.519 | 1.11 | 1.23 | -0.00518
LFBldgSDGAsmExCZ08 | Com-Iltg-dWatt-LF_OSbldg | SDG | Asm | Ex | CZ08 | 2.6128 | 0.00053234 | 0 | 2.9029 | 0.00063747 | -0.012314 | 2.5329 | 0.00051918 | 0 | 2.8129 | 0.00062219 | -0.012 |  | LF | Bldg | 2610 | 0.532 | 2530 | 0.519 | 1.11 | 1.2 | -0.0047377 | 2610 | 0.532 | 2530 | 0.519 | 1.11 | 1.2 | -0.00474
LFBldgSDGAsmExCZ10 | Com-Iltg-dWatt-LF_OSbldg | SDG | Asm | Ex | CZ10 | 2.6044 | 0.00053098 | 0 | 2.8635 | 0.0006428 | -0.015663 | 2.5319 | 0.00051918 | 0 | 2.7909 | 0.00062919 | -0.0153 |  | LF | Bldg | 2600 | 0.531 | 2530 | 0.519 | 1.1 | 1.21 | -0.006043 | 2600 | 0.531 | 2530 | 0.519 | 1.1 | 1.21 | -0.00604
LFBldgSDGAsmExCZ14 | Com-Iltg-dWatt-LF_OSbldg | SDG | Asm | Ex | CZ14 | 2.6212 | 0.00053371 | 0 | 2.8024 | 0.00060483 | -0.025312 | 2.534 | 0.00051918 | 0 | 2.713 | 0.00058897 | -0.02453 |  | LF | Bldg | 2620 | 0.534 | 2530 | 0.519 | 1.07 | 1.13 | -0.0096806 | 2620 | 0.534 | 2530 | 0.519 | 1.07 | 1.13 | -0.00968
LFBldgSDGAsmExCZ15 | Com-Iltg-dWatt-LF_OSbldg | SDG | Asm | Ex | CZ15 | 2.6213 | 0.00053372 | 0 | 3.1745 | 0.00063895 | -0.0069984 | 2.534 | 0.00051918 | 0 | 3.074 | 0.00062197 | -0.0067749 |  | LF | Bldg | 2620 | 0.534 | 2530 | 0.519 | 1.21 | 1.2 | -0.0026736 | 2620 | 0.534 | 2530 | 0.519 | 1.21 | 1.2 | -0.00267
LFBldgSDGAsmExIOU | Com-Iltg-dWatt-LF_OSbldg | SDG | Asm | Ex | IOU | 2.6104 | 0.00053195 | 0 | 2.8773 | 0.00065077 | -0.01427 | 2.5326 | 0.00051918 | 0 | 2.7985 | 0.0006354 | -0.013876 |  | LF | Bldg | 2610 | 0.532 | 2530 | 0.519 | 1.1 | 1.22 | -0.0054791 | 2610 | 0.532 | 2530 | 0.519 | 1.1 | 1.22 | -0.00548
LFBldgSDGAsmNewCZ06 | Com-Iltg-dWatt-LF_OSbldg | SDG | Asm | New | CZ06 | 2.55 | 0.000521 | 0 | 2.77 | 0.000639 | -0.0174 | 2.55 | 0.000521 | 0 | 2.77 | 0.000639 | -0.0174 |  | LF | Bldg | 2550 | 0.521 | 2550 | 0.521 | 1.09 | 1.23 | -0.0068235 | 2550 | 0.521 | 2550 | 0.521 | 1.09 | 1.23 | -0.00682
LFBldgSDGAsmNewCZ07 | Com-Iltg-dWatt-LF_OSbldg | SDG | Asm | New | CZ07 | 2.55 | 0.000521 | 0 | 2.78 | 0.000639 | -0.0159 | 2.55 | 0.000521 | 0 | 2.78 | 0.000639 | -0.0159 |  | LF | Bldg | 2550 | 0.521 | 2550 | 0.521 | 1.09 | 1.23 | -0.0062353 | 2550 | 0.521 | 2550 | 0.521 | 1.09 | 1.23 | -0.00624
LFBldgSDGAsmNewCZ08 | Com-Iltg-dWatt-LF_OSbldg | SDG | Asm | New | CZ08 | 2.55 | 0.000521 | 0 | 2.8 | 0.00063 | -0.0143 | 2.55 | 0.000521 | 0 | 2.8 | 0.00063 | -0.0143 |  | LF | Bldg | 2550 | 0.521 | 2550 | 0.521 | 1.1 | 1.21 | -0.0056078 | 2550 | 0.521 | 2550 | 0.521 | 1.1 | 1.21 | -0.00561
LFBldgSDGAsmNewCZ10 | Com-Iltg-dWatt-LF_OSbldg | SDG | Asm | New | CZ10 | 2.55 | 0.000521 | 0 | 2.78 | 0.000646 | -0.0164 | 2.55 | 0.000521 | 0 | 2.78 | 0.000646 | -0.0164 |  | LF | Bldg | 2550 | 0.521 | 2550 | 0.521 | 1.09 | 1.24 | -0.0064314 | 2550 | 0.521 | 2550 | 0.521 | 1.09 | 1.24 | -0.00643
LFBldgSDGAsmNewCZ14 | Com-Iltg-dWatt-LF_OSbldg | SDG | Asm | New | CZ14 | 2.55 | 0.000521 | 0 | 2.72 | 0.00063 | -0.0263 | 2.55 | 0.000521 | 0 | 2.72 | 0.00063 | -0.0263 |  | LF | Bldg | 2550 | 0.521 | 2550 | 0.521 | 1.07 | 1.21 | -0.010314 | 2550 | 0.521 | 2550 | 0.521 | 1.07 | 1.21 | -0.0103
LFBldgSDGAsmNewCZ15 | Com-Iltg-dWatt-LF_OSbldg | SDG | Asm | New | CZ15 | 2.55 | 0.000521 | 0 | 2.97 | 0.000643 | -0.00761 | 2.55 | 0.000521 | 0 | 2.97 | 0.000643 | -0.00761 |  | LF | Bldg | 2550 | 0.521 | 2550 | 0.521 | 1.16 | 1.23 | -0.0029843 | 2550 | 0.521 | 2550 | 0.521 | 1.16 | 1.23 | -0.00298
LFBldgSDGAsmNewIOU | Com-Iltg-dWatt-LF_OSbldg | SDG | Asm | New | IOU | 2.55 | 0.000521 | 0 | 2.7801 | 0.00064087 | -0.016142 | 2.55 | 0.000521 | 0 | 2.7801 | 0.00064087 | -0.016142 |  | LF | Bldg | 2550 | 0.521 | 2550 | 0.521 | 1.09 | 1.23 | -0.0063302 | 2550 | 0.521 | 2550 | 0.521 | 1.09 | 1.23 | -0.00633
LFBldgSDGComExCZ06 | Com-Iltg-dWatt-LF_OSbldg | SDG | Com | Ex | CZ06 | 3.2132 | 0.00068352 | 0 | 3.5364 | 0.00084238 | -0.014439 | 3.1248 | 0.00066063 | 0 | 3.4382 | 0.00081365 | -0.014093 |  | LF | Bldg | 3210 | 0.684 | 3120 | 0.661 | 1.1 | 1.23 | -0.0045102 | 3210 | 0.684 | 3120 | 0.661 | 1.1 | 1.23 | -0.00451
LFBldgSDGComExCZ07 | Com-Iltg-dWatt-LF_OSbldg | SDG | Com | Ex | CZ07 | 3.1144 | 0.00069497 | 0 | 3.4625 | 0.00085233 | -0.010273 | 3.0152 | 0.00066786 | 0 | 3.3488 | 0.0008189 | -0.010038 |  | LF | Bldg | 3110 | 0.695 | 3020 | 0.668 | 1.11 | 1.23 | -0.0033293 | 3110 | 0.695 | 3020 | 0.668 | 1.11 | 1.23 | -0.00333
LFBldgSDGComExCZ08 | Com-Iltg-dWatt-LF_OSbldg | SDG | Com | Ex | CZ08 | 3.3558 | 0.00075176 | 0 | 3.7756 | 0.00093166 | -0.011277 | 3.2707 | 0.00072799 | 0 | 3.678 | 0.00090188 | -0.011003 |  | LF | Bldg | 3360 | 0.752 | 3270 | 0.728 | 1.12 | 1.24 | -0.0033641 | 3360 | 0.752 | 3270 | 0.728 | 1.12 | 1.24 | -0.00336
LFBldgSDGComExCZ10 | Com-Iltg-dWatt-LF_OSbldg | SDG | Com | Ex | CZ10 | 3.2026 | 0.00072494 | 0 | 3.5497 | 0.00090662 | -0.012585 | 3.1112 | 0.00069879 | 0 | 3.4462 | 0.00087301 | -0.012257 |  | LF | Bldg | 3200 | 0.725 | 3110 | 0.699 | 1.11 | 1.25 | -0.0039396 | 3200 | 0.725 | 3110 | 0.699 | 1.11 | 1.25 | -0.00394
LFBldgSDGComExCZ14 | Com-Iltg-dWatt-LF_OSbldg | SDG | Com | Ex | CZ14 | 2.8003 | 0.00065595 | 0 | 3.0515 | 0.00082134 | -0.015886 | 2.6874 | 0.00062474 | 0 | 2.9277 | 0.00078151 | -0.015294 |  | LF | Bldg | 2800 | 0.656 | 2690 | 0.625 | 1.09 | 1.25 | -0.005691 | 2800 | 0.656 | 2690 | 0.625 | 1.09 | 1.25 | -0.00569
LFBldgSDGComExCZ15 | Com-Iltg-dWatt-LF_OSbldg | SDG | Com | Ex | CZ15 | 2.5351 | 0.00052396 | 0 | 2.984 | 0.00066119 | -0.0039406 | 2.4485 | 0.00050356 | 0 | 2.8821 | 0.00063491 | -0.0038141 |  | LF | Bldg | 2540 | 0.524 | 2450 | 0.504 | 1.18 | 1.26 | -0.0015577 | 2540 | 0.524 | 2450 | 0.504 | 1.18 | 1.26 | -0.00156
LFBldgSDGComExIOU | Com-Iltg-dWatt-LF_OSbldg | SDG | Com | Ex | IOU | 3.1422 | 0.00070264 | 0 | 3.4911 | 0.00086632 | -0.01098 | 3.0455 | 0.00067598 | 0 | 3.3807 | 0.00083308 | -0.010717 |  | LF | Bldg | 3140 | 0.703 | 3050 | 0.676 | 1.11 | 1.23 | -0.0035191 | 3140 | 0.703 | 3050 | 0.676 | 1.11 | 1.23 | -0.00352
LFBldgSDGComNewCZ06 | Com-Iltg-dWatt-LF_OSbldg | SDG | Com | New | CZ06 | 3.1361 | 0.00064274 | 0 | 3.416 | 0.0007894 | -0.013569 | 3.1361 | 0.00064274 | 0 | 3.416 | 0.0007894 | -0.013569 |  | LF | Bldg | 3140 | 0.643 | 3140 | 0.643 | 1.09 | 1.23 | -0.0043267 | 3140 | 0.643 | 3140 | 0.643 | 1.09 | 1.23 | -0.00433
LFBldgSDGComNewCZ07 | Com-Iltg-dWatt-LF_OSbldg | SDG | Com | New | CZ07 | 3.0098 | 0.00065263 | 0 | 3.2848 | 0.00079339 | -0.0091744 | 3.0098 | 0.00065263 | 0 | 3.2848 | 0.00079339 | -0.0091744 |  | LF | Bldg | 3010 | 0.653 | 3010 | 0.653 | 1.09 | 1.22 | -0.0030482 | 3010 | 0.653 | 3010 | 0.653 | 1.09 | 1.22 | -0.00305
LFBldgSDGComNewCZ08 | Com-Iltg-dWatt-LF_OSbldg | SDG | Com | New | CZ08 | 3.359 | 0.00074215 | 0 | 3.7343 | 0.00092943 | -0.010811 | 3.359 | 0.00074215 | 0 | 3.7343 | 0.00092943 | -0.010811 |  | LF | Bldg | 3360 | 0.742 | 3360 | 0.742 | 1.11 | 1.25 | -0.0032185 | 3360 | 0.742 | 3360 | 0.742 | 1.11 | 1.25 | -0.00322
LFBldgSDGComNewCZ10 | Com-Iltg-dWatt-LF_OSbldg | SDG | Com | New | CZ10 | 3.1819 | 0.0007032 | 0 | 3.5129 | 0.00090544 | -0.011907 | 3.1819 | 0.0007032 | 0 | 3.5129 | 0.00090544 | -0.011907 |  | LF | Bldg | 3180 | 0.703 | 3180 | 0.703 | 1.1 | 1.29 | -0.0037421 | 3180 | 0.703 | 3180 | 0.703 | 1.1 | 1.29 | -0.00374
LFBldgSDGComNewCZ14 | Com-Iltg-dWatt-LF_OSbldg | SDG | Com | New | CZ14 | 2.7224 | 0.00060725 | 0 | 2.9606 | 0.00078631 | -0.015268 | 2.7224 | 0.00060725 | 0 | 2.9606 | 0.00078631 | -0.015268 |  | LF | Bldg | 2720 | 0.607 | 2720 | 0.607 | 1.09 | 1.29 | -0.0056083 | 2720 | 0.607 | 2720 | 0.607 | 1.09 | 1.29 | -0.00561
LFBldgSDGComNewCZ15 | Com-Iltg-dWatt-LF_OSbldg | SDG | Com | New | CZ15 | 2.378 | 0.00045699 | 0 | 2.788 | 0.0006008 | -0.0035731 | 2.378 | 0.00045699 | 0 | 2.788 | 0.0006008 | -0.0035731 |  | LF | Bldg | 2380 | 0.457 | 2380 | 0.457 | 1.17 | 1.31 | -0.0015025 | 2380 | 0.457 | 2380 | 0.457 | 1.17 | 1.31 | -0.0015
LFBldgSDGComNewIOU | Com-Iltg-dWatt-LF_OSbldg | SDG | Com | New | IOU | 3.0603 | 0.00066576 | 0 | 3.3514 | 0.00082246 | -0.010014 | 3.0603 | 0.00066576 | 0 | 3.3514 | 0.00082246 | -0.010014 |  | LF | Bldg | 3060 | 0.666 | 3060 | 0.666 | 1.1 | 1.24 | -0.0032723 | 3060 | 0.666 | 3060 | 0.666 | 1.1 | 1.24 | -0.00327
LFBldgSDGECCExCZ06 | Com-Iltg-dWatt-LF_OSbldg | SDG | ECC | Ex | CZ06 | 2.4105 | 0.00080011 | 0 | 2.7292 | 0.0010128 | -0.013943 | 2.27 | 0.00071581 | 0 | 2.57 | 0.00090975 | -0.0131 |  | LF | Bldg | 2410 | 0.8 | 2270 | 0.716 | 1.13 | 1.27 | -0.0057709 | 2410 | 0.8 | 2270 | 0.716 | 1.13 | 1.27 | -0.00577
LFBldgSDGECCExCZ07 | Com-Iltg-dWatt-LF_OSbldg | SDG | ECC | Ex | CZ07 | 2.4106 | 0.00080018 | 0 | 2.7487 | 0.0010127 | -0.01165 | 2.27 | 0.00071581 | 0 | 2.5894 | 0.00090675 | -0.010994 |  | LF | Bldg | 2410 | 0.8 | 2270 | 0.716 | 1.14 | 1.27 | -0.004843 | 2410 | 0.8 | 2270 | 0.716 | 1.14 | 1.27 | -0.00484
LFBldgSDGECCExCZ08 | Com-Iltg-dWatt-LF_OSbldg | SDG | ECC | Ex | CZ08 | 2.4107 | 0.00080022 | 0 | 2.7594 | 0.0010126 | -0.01265 | 2.27 | 0.00071581 | 0 | 2.6 | 0.00090475 | -0.0119 |  | LF | Bldg | 2410 | 0.8 | 2270 | 0.716 | 1.15 | 1.26 | -0.0052423 | 2410 | 0.8 | 2270 | 0.716 | 1.15 | 1.26 | -0.00524
LFBldgSDGECCExCZ10 | Com-Iltg-dWatt-LF_OSbldg | SDG | ECC | Ex | CZ10 | 2.4106 | 0.00080018 | 0 | 2.7487 | 0.0010324 | -0.015037 | 2.27 | 0.00071581 | 0 | 2.5894 | 0.00092275 | -0.0141 |  | LF | Bldg | 2410 | 0.8 | 2270 | 0.716 | 1.14 | 1.29 | -0.0062115 | 2410 | 0.8 | 2270 | 0.716 | 1.14 | 1.29 | -0.00621
LFBldgSDGECCExCZ14 | Com-Iltg-dWatt-LF_OSbldg | SDG | ECC | Ex | CZ14 | 2.4105 | 0.00080011 | 0 | 2.6892 | 0.0010225 | -0.022611 | 2.27 | 0.00071581 | 0 | 2.5394 | 0.00091475 | -0.0213 |  | LF | Bldg | 2410 | 0.8 | 2270 | 0.716 | 1.12 | 1.28 | -0.0093833 | 2410 | 0.8 | 2270 | 0.716 | 1.12 | 1.28 | -0.00938
LFBldgSDGECCExIOU | Com-Iltg-dWatt-LF_OSbldg | SDG | ECC | Ex | IOU | 2.4106 | 0.00080018 | 0 | 2.7484 | 0.0010174 | -0.012524 | 2.27 | 0.00071581 | 0 | 2.5891 | 0.00091055 | -0.011796 |  | LF | Bldg | 2410 | 0.8 | 2270 | 0.716 | 1.14 | 1.27 | -0.0051966 | 2410 | 0.8 | 2270 | 0.716 | 1.14 | 1.27 | -0.0052
LFBldgSDGECCNewCZ06 | Com-Iltg-dWatt-LF_OSbldg | SDG | ECC | New | CZ06 | 2.27 | 0.000713 | 0 | 2.58 | 0.0009 | -0.0123 | 2.27 | 0.000713 | 0 | 2.58 | 0.0009 | -0.0123 |  | LF | Bldg | 2270 | 0.713 | 2270 | 0.713 | 1.14 | 1.26 | -0.0054185 | 2270 | 0.713 | 2270 | 0.713 | 1.14 | 1.26 | -0.00542
LFBldgSDGECCNewCZ07 | Com-Iltg-dWatt-LF_OSbldg | SDG | ECC | New | CZ07 | 2.27 | 0.000713 | 0 | 2.57 | 0.000901 | -0.01 | 2.27 | 0.000713 | 0 | 2.57 | 0.000901 | -0.01 |  | LF | Bldg | 2270 | 0.713 | 2270 | 0.713 | 1.13 | 1.26 | -0.0044053 | 2270 | 0.713 | 2270 | 0.713 | 1.13 | 1.26 | -0.00441
LFBldgSDGECCNewCZ08 | Com-Iltg-dWatt-LF_OSbldg | SDG | ECC | New | CZ08 | 2.27 | 0.000713 | 0 | 2.61 | 0.000903 | -0.0102 | 2.27 | 0.000713 | 0 | 2.61 | 0.000903 | -0.0102 |  | LF | Bldg | 2270 | 0.713 | 2270 | 0.713 | 1.15 | 1.27 | -0.0044934 | 2270 | 0.713 | 2270 | 0.713 | 1.15 | 1.27 | -0.00449
LFBldgSDGECCNewCZ10 | Com-Iltg-dWatt-LF_OSbldg | SDG | ECC | New | CZ10 | 2.27 | 0.000713 | 0 | 2.63 | 0.000934 | -0.0119 | 2.27 | 0.000713 | 0 | 2.63 | 0.000934 | -0.0119 |  | LF | Bldg | 2270 | 0.713 | 2270 | 0.713 | 1.16 | 1.31 | -0.0052423 | 2270 | 0.713 | 2270 | 0.713 | 1.16 | 1.31 | -0.00524
LFBldgSDGECCNewCZ14 | Com-Iltg-dWatt-LF_OSbldg | SDG | ECC | New | CZ14 | 2.27 | 0.000713 | 0 | 2.6 | 0.000906 | -0.0197 | 2.27 | 0.000713 | 0 | 2.6 | 0.000906 | -0.0197 |  | LF | Bldg | 2270 | 0.713 | 2270 | 0.713 | 1.15 | 1.27 | -0.0086784 | 2270 | 0.713 | 2270 | 0.713 | 1.15 | 1.27 | -0.00868
LFBldgSDGECCNewCZ15 | Com-Iltg-dWatt-LF_OSbldg | SDG | ECC | New | CZ15 | 2.27 | 0.000713 | 0 | 2.88 | 0.000983 | -0.00436 | 2.27 | 0.000713 | 0 | 2.88 | 0.000983 | -0.00436 |  | LF | Bldg | 2270 | 0.713 | 2270 | 0.713 | 1.27 | 1.38 | -0.0019207 | 2270 | 0.713 | 2270 | 0.713 | 1.27 | 1.38 | -0.00192
LFBldgSDGECCNewIOU | Com-Iltg-dWatt-LF_OSbldg | SDG | ECC | New | IOU | 2.27 | 0.000713 | 0 | 2.5847 | 0.00090879 | -0.010511 | 2.27 | 0.000713 | 0 | 2.5847 | 0.00090879 | -0.010511 |  | LF | Bldg | 2270 | 0.713 | 2270 | 0.713 | 1.14 | 1.27 | -0.0046303 | 2270 | 0.713 | 2270 | 0.713 | 1.14 | 1.27 | -0.00463
LFBldgSDGEPrExCZ06 | Com-Iltg-dWatt-LF_OSbldg | SDG | EPr | Ex | CZ06 | 2.1332 | 0.00061386 | 0 | 2.4322 | 0.00078726 | -0.0094697 | 1.95 | 0.00055118 | 0 | 2.22 | 0.00070721 | -0.00865 |  | LF | Bldg | 2130 | 0.614 | 1950 | 0.551 | 1.14 | 1.28 | -0.0044359 | 2130 | 0.614 | 1950 | 0.551 | 1.14 | 1.28 | -0.00444
LFBldgSDGEPrExCZ07 | Com-Iltg-dWatt-LF_OSbldg | SDG | EPr | Ex | CZ07 | 2.1333 | 0.00061387 | 0 | 2.4222 | 0.00079523 | -0.0084727 | 1.95 | 0.00055118 | 0 | 2.2197 | 0.00071325 | -0.0077397 |  | LF | Bldg | 2130 | 0.614 | 1950 | 0.551 | 1.14 | 1.29 | -0.0039691 | 2130 | 0.614 | 1950 | 0.551 | 1.14 | 1.29 | -0.00397
LFBldgSDGEPrExCZ08 | Com-Iltg-dWatt-LF_OSbldg | SDG | EPr | Ex | CZ08 | 2.1333 | 0.00061388 | 0 | 2.4522 | 0.00079524 | -0.0078549 | 1.95 | 0.00055118 | 0 | 2.24 | 0.00071421 | -0.00717 |  | LF | Bldg | 2130 | 0.614 | 1950 | 0.551 | 1.15 | 1.3 | -0.0036769 | 2130 | 0.614 | 1950 | 0.551 | 1.15 | 1.3 | -0.00368
LFBldgSDGEPrExCZ10 | Com-Iltg-dWatt-LF_OSbldg | SDG | EPr | Ex | CZ10 | 2.1333 | 0.00061387 | 0 | 2.4322 | 0.00079123 | -0.010067 | 1.95 | 0.00055118 | 0 | 2.22 | 0.00071021 | -0.0091796 |  | LF | Bldg | 2130 | 0.614 | 1950 | 0.551 | 1.14 | 1.29 | -0.0047075 | 2130 | 0.614 | 1950 | 0.551 | 1.14 | 1.29 | -0.00471
LFBldgSDGEPrExCZ14 | Com-Iltg-dWatt-LF_OSbldg | SDG | EPr | Ex | CZ14 | 2.1332 | 0.00061384 | 0 | 2.3324 | 0.00079219 | -0.017142 | 1.95 | 0.00055118 | 0 | 2.13 | 0.00071122 | -0.0156 |  | LF | Bldg | 2130 | 0.614 | 1950 | 0.551 | 1.09 | 1.29 | -0.008 | 2130 | 0.614 | 1950 | 0.551 | 1.09 | 1.29 | -0.008
LFBldgSDGEPrExCZ15 | Com-Iltg-dWatt-LF_OSbldg | SDG | EPr | Ex | CZ15 | 2.1335 | 0.00061395 | 0 | 2.6118 | 0.00079233 | -0.0041174 | 1.95 | 0.00055117 | 0 | 2.38 | 0.00071121 | -0.00376 |  | LF | Bldg | 2130 | 0.614 | 1950 | 0.551 | 1.22 | 1.29 | -0.0019282 | 2130 | 0.614 | 1950 | 0.551 | 1.22 | 1.29 | -0.00193
LFBldgSDGEPrExIOU | Com-Iltg-dWatt-LF_OSbldg | SDG | EPr | Ex | IOU | 2.1333 | 0.00061387 | 0 | 2.4272 | 0.00079351 | -0.0090733 | 1.95 | 0.00055118 | 0 | 2.2205 | 0.000712 | -0.0082821 |  | LF | Bldg | 2130 | 0.614 | 1950 | 0.551 | 1.14 | 1.29 | -0.0042472 | 2130 | 0.614 | 1950 | 0.551 | 1.14 | 1.29 | -0.00425
LFBldgSDGEPrNewCZ06 | Com-Iltg-dWatt-LF_OSbldg | SDG | EPr | New | CZ06 | 1.95 | 0.000556 | 0 | 2.02 | 0.000527 | -0.00933 | 1.95 | 0.000556 | 0 | 2.02 | 0.000527 | -0.00933 |  | LF | Bldg | 1950 | 0.556 | 1950 | 0.556 | 1.04 | 0.948 | -0.0047846 | 1950 | 0.556 | 1950 | 0.556 | 1.04 | 0.948 | -0.00478
LFBldgSDGEPrNewCZ07 | Com-Iltg-dWatt-LF_OSbldg | SDG | EPr | New | CZ07 | 1.95 | 0.000556 | 0 | 2.13 | 0.000743 | -0.00999 | 1.95 | 0.000556 | 0 | 2.13 | 0.000743 | -0.00999 |  | LF | Bldg | 1950 | 0.556 | 1950 | 0.556 | 1.09 | 1.34 | -0.0051231 | 1950 | 0.556 | 1950 | 0.556 | 1.09 | 1.34 | -0.00512
LFBldgSDGEPrNewCZ08 | Com-Iltg-dWatt-LF_OSbldg | SDG | EPr | New | CZ08 | 1.95 | 0.000556 | 0 | 2.19 | 0.000766 | -0.0094 | 1.95 | 0.000556 | 0 | 2.19 | 0.000766 | -0.0094 |  | LF | Bldg | 1950 | 0.556 | 1950 | 0.556 | 1.12 | 1.38 | -0.0048205 | 1950 | 0.556 | 1950 | 0.556 | 1.12 | 1.38 | -0.00482
LFBldgSDGEPrNewCZ10 | Com-Iltg-dWatt-LF_OSbldg | SDG | EPr | New | CZ10 | 1.95 | 0.000556 | 0 | 2.2 | 0.000807 | -0.0116 | 1.95 | 0.000556 | 0 | 2.2 | 0.000807 | -0.0116 |  | LF | Bldg | 1950 | 0.556 | 1950 | 0.556 | 1.13 | 1.45 | -0.0059487 | 1950 | 0.556 | 1950 | 0.556 | 1.13 | 1.45 | -0.00595
LFBldgSDGEPrNewCZ14 | Com-Iltg-dWatt-LF_OSbldg | SDG | EPr | New | CZ14 | 1.95 | 0.000556 | 0 | 2.16 | 0.000792 | -0.0189 | 1.95 | 0.000556 | 0 | 2.16 | 0.000792 | -0.0189 |  | LF | Bldg | 1950 | 0.556 | 1950 | 0.556 | 1.11 | 1.42 | -0.0096923 | 1950 | 0.556 | 1950 | 0.556 | 1.11 | 1.42 | -0.00969
LFBldgSDGEPrNewCZ15 | Com-Iltg-dWatt-LF_OSbldg | SDG | EPr | New | CZ15 | 1.95 | 0.000556 | 0 | 2.39 | 0.000807 | -0.00498 | 1.95 | 0.000556 | 0 | 2.39 | 0.000807 | -0.00498 |  | LF | Bldg | 1950 | 0.556 | 1950 | 0.556 | 1.23 | 1.45 | -0.0025538 | 1950 | 0.556 | 1950 | 0.556 | 1.23 | 1.45 | -0.00255
LFBldgSDGEPrNewIOU | Com-Iltg-dWatt-LF_OSbldg | SDG | EPr | New | IOU | 1.95 | 0.000556 | 0 | 2.1516 | 0.00075515 | -0.010518 | 1.95 | 0.000556 | 0 | 2.1516 | 0.00075515 | -0.010518 |  | LF | Bldg | 1950 | 0.556 | 1950 | 0.556 | 1.1 | 1.36 | -0.0053938 | 1950 | 0.556 | 1950 | 0.556 | 1.1 | 1.36 | -0.00539
LFBldgSDGERCExCZ06 | Com-Iltg-dWatt-LF_OSbldg | SDG | ERC | Ex | CZ06 | 2.4697 | 0.00069869 | 0 | 2.7483 | 0.00087783 | -0.015136 | 2.19 | 0.00060129 | 0 | 2.43 | 0.00075536 | -0.0134 |  | LF | Bldg | 2470 | 0.699 | 2190 | 0.601 | 1.11 | 1.26 | -0.0061187 | 2470 | 0.699 | 2190 | 0.601 | 1.11 | 1.26 | -0.00612
LFBldgSDGERCExCZ07 | Com-Iltg-dWatt-LF_OSbldg | SDG | ERC | Ex | CZ07 | 2.4697 | 0.0006987 | 0 | 2.7883 | 0.00089378 | -0.012547 | 2.19 | 0.00060128 | 0 | 2.47 | 0.00076839 | -0.0111 |  | LF | Bldg | 2470 | 0.699 | 2190 | 0.601 | 1.13 | 1.28 | -0.0050685 | 2470 | 0.699 | 2190 | 0.601 | 1.13 | 1.28 | -0.00507
LFBldgSDGERCExCZ08 | Com-Iltg-dWatt-LF_OSbldg | SDG | ERC | Ex | CZ08 | 2.4697 | 0.00069871 | 0 | 2.7483 | 0.00088779 | -0.013243 | 2.19 | 0.00060128 | 0 | 2.43 | 0.00076335 | -0.0117 |  | LF | Bldg | 2470 | 0.699 | 2190 | 0.601 | 1.11 | 1.27 | -0.0053425 | 2470 | 0.699 | 2190 | 0.601 | 1.11 | 1.27 | -0.00534
LFBldgSDGERCExCZ10 | Com-Iltg-dWatt-LF_OSbldg | SDG | ERC | Ex | CZ10 | 2.4697 | 0.0006987 | 0 | 2.7387 | 0.00088982 | -0.015636 | 2.19 | 0.00060128 | 0 | 2.43 | 0.00076539 | -0.0139 |  | LF | Bldg | 2470 | 0.699 | 2190 | 0.601 | 1.11 | 1.27 | -0.006347 | 2470 | 0.699 | 2190 | 0.601 | 1.11 | 1.27 | -0.00635
LFBldgSDGERCExCZ14 | Com-Iltg-dWatt-LF_OSbldg | SDG | ERC | Ex | CZ14 | 2.4695 | 0.00069865 | 0 | 2.6985 | 0.00089471 | -0.02071 | 2.19 | 0.00060129 | 0 | 2.39 | 0.00077036 | -0.0183 |  | LF | Bldg | 2470 | 0.699 | 2190 | 0.601 | 1.09 | 1.28 | -0.0083562 | 2470 | 0.699 | 2190 | 0.601 | 1.09 | 1.28 | -0.00836
LFBldgSDGERCExCZ15 | Com-Iltg-dWatt-LF_OSbldg | SDG | ERC | Ex | CZ15 | 2.4701 | 0.00069882 | 0 | 2.9284 | 0.00091186 | -0.0072903 | 2.19 | 0.00060127 | 0 | 2.6 | 0.00078438 | -0.00645 |  | LF | Bldg | 2470 | 0.699 | 2190 | 0.601 | 1.19 | 1.3 | -0.0029452 | 2470 | 0.699 | 2190 | 0.601 | 1.19 | 1.3 | -0.00295
LFBldgSDGERCExIOU | Com-Iltg-dWatt-LF_OSbldg | SDG | ERC | Ex | IOU | 2.4697 | 0.0006987 | 0 | 2.7675 | 0.00089143 | -0.013778 | 2.19 | 0.00060128 | 0 | 2.4524 | 0.00076656 | -0.01221 |  | LF | Bldg | 2470 | 0.699 | 2190 | 0.601 | 1.12 | 1.27 | -0.0055754 | 2470 | 0.699 | 2190 | 0.601 | 1.12 | 1.27 | -0.00558
LFBldgSDGERCNewCZ06 | Com-Iltg-dWatt-LF_OSbldg | SDG | ERC | New | CZ06 | 2.19 | 0.000609 | 0 | 2.53 | 0.000788 | -0.014 | 2.19 | 0.000609 | 0 | 2.53 | 0.000788 | -0.014 |  | LF | Bldg | 2190 | 0.609 | 2190 | 0.609 | 1.16 | 1.29 | -0.0063927 | 2190 | 0.609 | 2190 | 0.609 | 1.16 | 1.29 | -0.00639
LFBldgSDGERCNewCZ07 | Com-Iltg-dWatt-LF_OSbldg | SDG | ERC | New | CZ07 | 2.19 | 0.000609 | 0 | 2.53 | 0.000793 | -0.011 | 2.19 | 0.000609 | 0 | 2.53 | 0.000793 | -0.011 |  | LF | Bldg | 2190 | 0.609 | 2190 | 0.609 | 1.16 | 1.3 | -0.0050228 | 2190 | 0.609 | 2190 | 0.609 | 1.16 | 1.3 | -0.00502
LFBldgSDGERCNewCZ08 | Com-Iltg-dWatt-LF_OSbldg | SDG | ERC | New | CZ08 | 2.19 | 0.000609 | 0 | 2.57 | 0.000806 | -0.0118 | 2.19 | 0.000609 | 0 | 2.57 | 0.000806 | -0.0118 |  | LF | Bldg | 2190 | 0.609 | 2190 | 0.609 | 1.17 | 1.32 | -0.0053881 | 2190 | 0.609 | 2190 | 0.609 | 1.17 | 1.32 | -0.00539
LFBldgSDGERCNewCZ10 | Com-Iltg-dWatt-LF_OSbldg | SDG | ERC | New | CZ10 | 2.19 | 0.000609 | 0 | 2.58 | 0.000843 | -0.014 | 2.19 | 0.000609 | 0 | 2.58 | 0.000843 | -0.014 |  | LF | Bldg | 2190 | 0.609 | 2190 | 0.609 | 1.18 | 1.38 | -0.0063927 | 2190 | 0.609 | 2190 | 0.609 | 1.18 | 1.38 | -0.00639
LFBldgSDGERCNewCZ14 | Com-Iltg-dWatt-LF_OSbldg | SDG | ERC | New | CZ14 | 2.19 | 0.000609 | 0 | 2.54 | 0.00083 | -0.0204 | 2.19 | 0.000609 | 0 | 2.54 | 0.00083 | -0.0204 |  | LF | Bldg | 2190 | 0.609 | 2190 | 0.609 | 1.16 | 1.36 | -0.0093151 | 2190 | 0.609 | 2190 | 0.609 | 1.16 | 1.36 | -0.00932
LFBldgSDGERCNewCZ15 | Com-Iltg-dWatt-LF_OSbldg | SDG | ERC | New | CZ15 | 2.19 | 0.000609 | 0 | 2.8 | 0.000845 | -0.00695 | 2.19 | 0.000609 | 0 | 2.8 | 0.000845 | -0.00695 |  | LF | Bldg | 2190 | 0.609 | 2190 | 0.609 | 1.28 | 1.39 | -0.0031735 | 2190 | 0.609 | 2190 | 0.609 | 1.28 | 1.39 | -0.00317
LFBldgSDGERCNewIOU | Com-Iltg-dWatt-LF_OSbldg | SDG | ERC | New | IOU | 2.19 | 0.000609 | 0 | 2.5492 | 0.00081021 | -0.012242 | 2.19 | 0.000609 | 0 | 2.5492 | 0.00081021 | -0.012242 |  | LF | Bldg | 2190 | 0.609 | 2190 | 0.609 | 1.16 | 1.33 | -0.0055902 | 2190 | 0.609 | 2190 | 0.609 | 1.16 | 1.33 | -0.00559
LFBldgSDGESeExCZ06 | Com-Iltg-dWatt-LF_OSbldg | SDG | ESe | Ex | CZ06 | 2.274 | 0.00070697 | 0 | 2.5532 | 0.0009024 | -0.012864 | 2.11 | 0.00064718 | 0 | 2.37 | 0.00082621 | -0.0119 |  | LF | Bldg | 2270 | 0.707 | 2110 | 0.647 | 1.12 | 1.28 | -0.0056398 | 2270 | 0.707 | 2110 | 0.647 | 1.12 | 1.28 | -0.00564
LFBldgSDGESeExCZ07 | Com-Iltg-dWatt-LF_OSbldg | SDG | ESe | Ex | CZ07 | 2.274 | 0.00070698 | 0 | 2.5529 | 0.00088845 | -0.011268 | 2.11 | 0.00064718 | 0 | 2.3696 | 0.00081321 | -0.0104 |  | LF | Bldg | 2270 | 0.707 | 2110 | 0.647 | 1.12 | 1.26 | -0.0049289 | 2270 | 0.707 | 2110 | 0.647 | 1.12 | 1.26 | -0.00493
LFBldgSDGESeExCZ08 | Com-Iltg-dWatt-LF_OSbldg | SDG | ESe | Ex | CZ08 | 2.274 | 0.00070698 | 0 | 2.5829 | 0.00089749 | -0.010972 | 2.11 | 0.00064718 | 0 | 2.39 | 0.00082225 | -0.0102 |  | LF | Bldg | 2270 | 0.707 | 2110 | 0.647 | 1.13 | 1.27 | -0.0048341 | 2270 | 0.707 | 2110 | 0.647 | 1.13 | 1.27 | -0.00483
LFBldgSDGESeExCZ10 | Com-Iltg-dWatt-LF_OSbldg | SDG | ESe | Ex | CZ10 | 2.274 | 0.00070698 | 0 | 2.5729 | 0.00089645 | -0.013764 | 2.11 | 0.00064718 | 0 | 2.38 | 0.00082121 | -0.0128 |  | LF | Bldg | 2270 | 0.707 | 2110 | 0.647 | 1.13 | 1.27 | -0.0060664 | 2270 | 0.707 | 2110 | 0.647 | 1.13 | 1.27 | -0.00607
LFBldgSDGESeExCZ14 | Com-Iltg-dWatt-LF_OSbldg | SDG | ESe | Ex | CZ14 | 2.2739 | 0.00070695 | 0 | 2.4832 | 0.00087048 | -0.022139 | 2.11 | 0.00064718 | 0 | 2.3 | 0.00079722 | -0.0205 |  | LF | Bldg | 2270 | 0.707 | 2110 | 0.647 | 1.09 | 1.23 | -0.0097156 | 2270 | 0.707 | 2110 | 0.647 | 1.09 | 1.23 | -0.00972
LFBldgSDGESeExCZ15 | Com-Iltg-dWatt-LF_OSbldg | SDG | ESe | Ex | CZ15 | 2.2742 | 0.00070705 | 0 | 2.7828 | 0.00089554 | -0.0060643 | 2.11 | 0.00064717 | 0 | 2.58 | 0.00082021 | -0.00562 |  | LF | Bldg | 2270 | 0.707 | 2110 | 0.647 | 1.22 | 1.27 | -0.0026635 | 2270 | 0.707 | 2110 | 0.647 | 1.22 | 1.27 | -0.00266
LFBldgSDGESeExIOU | Com-Iltg-dWatt-LF_OSbldg | SDG | ESe | Ex | IOU | 2.274 | 0.00070698 | 0 | 2.561 | 0.00089209 | -0.012227 | 2.11 | 0.00064718 | 0 | 2.374 | 0.00081682 | -0.011322 |  | LF | Bldg | 2270 | 0.707 | 2110 | 0.647 | 1.13 | 1.26 | -0.005366 | 2270 | 0.707 | 2110 | 0.647 | 1.13 | 1.26 | -0.00537
LFBldgSDGESeNewCZ06 | Com-Iltg-dWatt-LF_OSbldg | SDG | ESe | New | CZ06 | 2.11 | 0.000652 | 0 | 2.33 | 0.000862 | -0.0157 | 2.11 | 0.000652 | 0 | 2.33 | 0.000862 | -0.0157 |  | LF | Bldg | 2110 | 0.652 | 2110 | 0.652 | 1.1 | 1.32 | -0.0074408 | 2110 | 0.652 | 2110 | 0.652 | 1.1 | 1.32 | -0.00744
LFBldgSDGESeNewCZ07 | Com-Iltg-dWatt-LF_OSbldg | SDG | ESe | New | CZ07 | 2.11 | 0.000652 | 0 | 2.31 | 0.000844 | -0.0123 | 2.11 | 0.000652 | 0 | 2.31 | 0.000844 | -0.0123 |  | LF | Bldg | 2110 | 0.652 | 2110 | 0.652 | 1.09 | 1.29 | -0.0058294 | 2110 | 0.652 | 2110 | 0.652 | 1.09 | 1.29 | -0.00583
LFBldgSDGESeNewCZ08 | Com-Iltg-dWatt-LF_OSbldg | SDG | ESe | New | CZ08 | 2.11 | 0.000652 | 0 | 2.36 | 0.000876 | -0.0119 | 2.11 | 0.000652 | 0 | 2.36 | 0.000876 | -0.0119 |  | LF | Bldg | 2110 | 0.652 | 2110 | 0.652 | 1.12 | 1.34 | -0.0056398 | 2110 | 0.652 | 2110 | 0.652 | 1.12 | 1.34 | -0.00564
LFBldgSDGESeNewCZ10 | Com-Iltg-dWatt-LF_OSbldg | SDG | ESe | New | CZ10 | 2.11 | 0.000652 | 0 | 2.38 | 0.000921 | -0.0154 | 2.11 | 0.000652 | 0 | 2.38 | 0.000921 | -0.0154 |  | LF | Bldg | 2110 | 0.652 | 2110 | 0.652 | 1.13 | 1.41 | -0.0072986 | 2110 | 0.652 | 2110 | 0.652 | 1.13 | 1.41 | -0.0073
LFBldgSDGESeNewCZ14 | Com-Iltg-dWatt-LF_OSbldg | SDG | ESe | New | CZ14 | 2.11 | 0.000652 | 0 | 2.35 | 0.0009 | -0.023 | 2.11 | 0.000652 | 0 | 2.35 | 0.0009 | -0.023 |  | LF | Bldg | 2110 | 0.652 | 2110 | 0.652 | 1.11 | 1.38 | -0.0109 | 2110 | 0.652 | 2110 | 0.652 | 1.11 | 1.38 | -0.0109
LFBldgSDGESeNewCZ15 | Com-Iltg-dWatt-LF_OSbldg | SDG | ESe | New | CZ15 | 2.11 | 0.000652 | 0 | 2.63 | 0.000915 | -0.00661 | 2.11 | 0.000652 | 0 | 2.63 | 0.000915 | -0.00661 |  | LF | Bldg | 2110 | 0.652 | 2110 | 0.652 | 1.25 | 1.4 | -0.0031327 | 2110 | 0.652 | 2110 | 0.652 | 1.25 | 1.4 | -0.00313
LFBldgSDGESeNewIOU | Com-Iltg-dWatt-LF_OSbldg | SDG | ESe | New | IOU | 2.11 | 0.000652 | 0 | 2.3376 | 0.00087238 | -0.013537 | 2.11 | 0.000652 | 0 | 2.3376 | 0.00087238 | -0.013537 |  | LF | Bldg | 2110 | 0.652 | 2110 | 0.652 | 1.11 | 1.34 | -0.0064155 | 2110 | 0.652 | 2110 | 0.652 | 1.11 | 1.34 | -0.00642
LFBldgSDGEUnExCZ06 | Com-Iltg-dWatt-LF_OSbldg | SDG | EUn | Ex | CZ06 | 2.3405 | 0.00071475 | 0 | 2.6792 | 0.00090235 | -0.0099608 | 2.2 | 0.00063981 | 0 | 2.52 | 0.00080775 | -0.0093987 |  | LF | Bldg | 2340 | 0.715 | 2200 | 0.64 | 1.15 | 1.26 | -0.0042721 | 2340 | 0.715 | 2200 | 0.64 | 1.15 | 1.26 | -0.00427
LFBldgSDGEUnExCZ07 | Com-Iltg-dWatt-LF_OSbldg | SDG | EUn | Ex | CZ07 | 2.3406 | 0.0007148 | 0 | 2.6694 | 0.00089449 | -0.0086737 | 2.2 | 0.00063981 | 0 | 2.51 | 0.00080075 | -0.0081394 |  | LF | Bldg | 2340 | 0.715 | 2200 | 0.64 | 1.14 | 1.25 | -0.0036997 | 2340 | 0.715 | 2200 | 0.64 | 1.14 | 1.25 | -0.0037
LFBldgSDGEUnExCZ08 | Com-Iltg-dWatt-LF_OSbldg | SDG | EUn | Ex | CZ08 | 2.3407 | 0.00071484 | 0 | 2.6988 | 0.00090541 | -0.0096102 | 2.2 | 0.00063981 | 0 | 2.53 | 0.00080975 | -0.0090194 |  | LF | Bldg | 2340 | 0.715 | 2200 | 0.64 | 1.15 | 1.27 | -0.0040997 | 2340 | 0.715 | 2200 | 0.64 | 1.15 | 1.27 | -0.0041
LFBldgSDGEUnExCZ10 | Com-Iltg-dWatt-LF_OSbldg | SDG | EUn | Ex | CZ10 | 2.3406 | 0.0007148 | 0 | 2.6887 | 0.00092024 | -0.01115 | 2.2 | 0.00063981 | 0 | 2.5294 | 0.00082275 | -0.0104 |  | LF | Bldg | 2340 | 0.715 | 2200 | 0.64 | 1.15 | 1.29 | -0.0047273 | 2340 | 0.715 | 2200 | 0.64 | 1.15 | 1.29 | -0.00473
LFBldgSDGEUnExCZ14 | Com-Iltg-dWatt-LF_OSbldg | SDG | EUn | Ex | CZ14 | 2.3405 | 0.00071475 | 0 | 2.6586 | 0.00091129 | -0.014937 | 2.2 | 0.00063981 | 0 | 2.49 | 0.00081575 | -0.014094 |  | LF | Bldg | 2340 | 0.715 | 2200 | 0.64 | 1.13 | 1.27 | -0.0064062 | 2340 | 0.715 | 2200 | 0.64 | 1.13 | 1.27 | -0.00641
LFBldgSDGEUnExIOU | Com-Iltg-dWatt-LF_OSbldg | SDG | EUn | Ex | IOU | 2.3406 | 0.0007148 | 0 | 2.6742 | 0.00090077 | -0.0093032 | 2.2 | 0.00063981 | 0 | 2.5147 | 0.00080611 | -0.0087159 |  | LF | Bldg | 2340 | 0.715 | 2200 | 0.64 | 1.14 | 1.26 | -0.0039618 | 2340 | 0.715 | 2200 | 0.64 | 1.14 | 1.26 | -0.00396
LFBldgSDGEUnNewCZ06 | Com-Iltg-dWatt-LF_OSbldg | SDG | EUn | New | CZ06 | 2.2 | 0.000637 | 0 | 2.55 | 0.000805 | -0.0062 | 2.2 | 0.000637 | 0 | 2.55 | 0.000805 | -0.0062 |  | LF | Bldg | 2200 | 0.637 | 2200 | 0.637 | 1.16 | 1.26 | -0.0028182 | 2200 | 0.637 | 2200 | 0.637 | 1.16 | 1.26 | -0.00282
LFBldgSDGEUnNewCZ07 | Com-Iltg-dWatt-LF_OSbldg | SDG | EUn | New | CZ07 | 2.2 | 0.000637 | 0 | 2.53 | 0.000798 | -0.00508 | 2.2 | 0.000637 | 0 | 2.53 | 0.000798 | -0.00508 |  | LF | Bldg | 2200 | 0.637 | 2200 | 0.637 | 1.15 | 1.25 | -0.0023091 | 2200 | 0.637 | 2200 | 0.637 | 1.15 | 1.25 | -0.00231
LFBldgSDGEUnNewCZ08 | Com-Iltg-dWatt-LF_OSbldg | SDG | EUn | New | CZ08 | 2.2 | 0.000637 | 0 | 2.57 | 0.000814 | -0.00556 | 2.2 | 0.000637 | 0 | 2.57 | 0.000814 | -0.00556 |  | LF | Bldg | 2200 | 0.637 | 2200 | 0.637 | 1.17 | 1.28 | -0.0025273 | 2200 | 0.637 | 2200 | 0.637 | 1.17 | 1.28 | -0.00253
LFBldgSDGEUnNewCZ10 | Com-Iltg-dWatt-LF_OSbldg | SDG | EUn | New | CZ10 | 2.2 | 0.000637 | 0 | 2.59 | 0.000842 | -0.00659 | 2.2 | 0.000637 | 0 | 2.59 | 0.000842 | -0.00659 |  | LF | Bldg | 2200 | 0.637 | 2200 | 0.637 | 1.18 | 1.32 | -0.0029955 | 2200 | 0.637 | 2200 | 0.637 | 1.18 | 1.32 | -0.003
LFBldgSDGEUnNewCZ14 | Com-Iltg-dWatt-LF_OSbldg | SDG | EUn | New | CZ14 | 2.2 | 0.000637 | 0 | 2.54 | 0.000812 | -0.0121 | 2.2 | 0.000637 | 0 | 2.54 | 0.000812 | -0.0121 |  | LF | Bldg | 2200 | 0.637 | 2200 | 0.637 | 1.15 | 1.27 | -0.0055 | 2200 | 0.637 | 2200 | 0.637 | 1.15 | 1.27 | -0.0055
LFBldgSDGEUnNewCZ15 | Com-Iltg-dWatt-LF_OSbldg | SDG | EUn | New | CZ15 | 2.2 | 0.000637 | 0 | 2.71 | 0.000847 | -0.00259 | 2.2 | 0.000637 | 0 | 2.71 | 0.000847 | -0.00259 |  | LF | Bldg | 2200 | 0.637 | 2200 | 0.637 | 1.23 | 1.33 | -0.0011773 | 2200 | 0.637 | 2200 | 0.637 | 1.23 | 1.33 | -0.00118
LFBldgSDGEUnNewIOU | Com-Iltg-dWatt-LF_OSbldg | SDG | EUn | New | IOU | 2.2 | 0.000637 | 0 | 2.5446 | 0.00080859 | -0.0054814 | 2.2 | 0.000637 | 0 | 2.5446 | 0.00080859 | -0.0054814 |  | LF | Bldg | 2200 | 0.637 | 2200 | 0.637 | 1.16 | 1.27 | -0.0024916 | 2200 | 0.637 | 2200 | 0.637 | 1.16 | 1.27 | -0.00249
LFBldgSDGGroExCZ06 | Com-Iltg-dWatt-LF_OSbldg | SDG | Gro | Ex | CZ06 | 4.9252 | 0.00069256 | 0 | 4.9757 | 0.00085121 | -0.062524 | 4.85 | 0.000682 | 0 | 4.9057 | 0.00083851 | -0.0616 |  | LF | Bldg | 4930 | 0.693 | 4850 | 0.682 | 1.01 | 1.23 | -0.012701 | 4930 | 0.693 | 4850 | 0.682 | 1.01 | 1.23 | -0.0127
LFBldgSDGGroExCZ07 | Com-Iltg-dWatt-LF_OSbldg | SDG | Gro | Ex | CZ07 | 4.9049 | 0.00068933 | 0 | 4.8858 | 0.00082624 | -0.066141 | 4.85 | 0.000682 | 0 | 4.84 | 0.000818 | -0.0655 |  | LF | Bldg | 4900 | 0.689 | 4850 | 0.682 | 0.998 | 1.2 | -0.013505 | 4900 | 0.689 | 4850 | 0.682 | 0.998 | 1.2 | -0.0135
LFBldgSDGGroExCZ08 | Com-Iltg-dWatt-LF_OSbldg | SDG | Gro | Ex | CZ08 | 4.9131 | 0.00069064 | 0 | 5.075 | 0.00086979 | -0.056448 | 4.85 | 0.000682 | 0 | 5.0178 | 0.000859 | -0.0558 |  | LF | Bldg | 4910 | 0.691 | 4850 | 0.682 | 1.03 | 1.26 | -0.011505 | 4910 | 0.691 | 4850 | 0.682 | 1.03 | 1.26 | -0.0115
LFBldgSDGGroExCZ10 | Com-Iltg-dWatt-LF_OSbldg | SDG | Gro | Ex | CZ10 | 4.9131 | 0.00069064 | 0 | 5.1451 | 0.00090596 | -0.053548 | 4.85 | 0.000682 | 0 | 5.0878 | 0.000895 | -0.0529 |  | LF | Bldg | 4910 | 0.691 | 4850 | 0.682 | 1.05 | 1.31 | -0.010907 | 4910 | 0.691 | 4850 | 0.682 | 1.05 | 1.31 | -0.0109
LFBldgSDGGroExCZ14 | Com-Iltg-dWatt-LF_OSbldg | SDG | Gro | Ex | CZ14 | 4.9132 | 0.00069064 | 0 | 5.1132 | 0.00091697 | -0.056448 | 4.85 | 0.000682 | 0 | 5.05 | 0.000906 | -0.0558 |  | LF | Bldg | 4910 | 0.691 | 4850 | 0.682 | 1.04 | 1.33 | -0.011505 | 4910 | 0.691 | 4850 | 0.682 | 1.04 | 1.33 | -0.0115
LFBldgSDGGroExCZ15 | Com-Iltg-dWatt-LF_OSbldg | SDG | Gro | Ex | CZ15 | 4.9131 | 0.00069064 | 0 | 5.5148 | 0.00090074 | -0.030118 | 4.85 | 0.000682 | 0 | 5.45 | 0.00088978 | -0.029778 |  | LF | Bldg | 4910 | 0.691 | 4850 | 0.682 | 1.12 | 1.3 | -0.0061398 | 4910 | 0.691 | 4850 | 0.682 | 1.12 | 1.3 | -0.00614
LFBldgSDGGroExIOU | Com-Iltg-dWatt-LF_OSbldg | SDG | Gro | Ex | IOU | 4.9086 | 0.00068991 | 0 | 4.9675 | 0.00085081 | -0.062201 | 4.85 | 0.000682 | 0 | 4.9169 | 0.00084149 | -0.061542 |  | LF | Bldg | 4910 | 0.69 | 4850 | 0.682 | 1.01 | 1.23 | -0.012689 | 4910 | 0.69 | 4850 | 0.682 | 1.01 | 1.23 | -0.0127
LFBldgSDGGroNewCZ06 | Com-Iltg-dWatt-LF_OSbldg | SDG | Gro | New | CZ06 | 4.85 | 0.000682 | 0 | 5.17 | 0.00085 | -0.0457 | 4.85 | 0.000682 | 0 | 5.17 | 0.00085 | -0.0457 |  | LF | Bldg | 4850 | 0.682 | 4850 | 0.682 | 1.07 | 1.25 | -0.0094227 | 4850 | 0.682 | 4850 | 0.682 | 1.07 | 1.25 | -0.00942
LFBldgSDGGroNewCZ07 | Com-Iltg-dWatt-LF_OSbldg | SDG | Gro | New | CZ07 | 4.85 | 0.000682 | 0 | 5.13 | 0.000829 | -0.0457 | 4.85 | 0.000682 | 0 | 5.13 | 0.000829 | -0.0457 |  | LF | Bldg | 4850 | 0.682 | 4850 | 0.682 | 1.06 | 1.22 | -0.0094227 | 4850 | 0.682 | 4850 | 0.682 | 1.06 | 1.22 | -0.00942
LFBldgSDGGroNewCZ08 | Com-Iltg-dWatt-LF_OSbldg | SDG | Gro | New | CZ08 | 4.85 | 0.000682 | 0 | 5.22 | 0.000871 | -0.0403 | 4.85 | 0.000682 | 0 | 5.22 | 0.000871 | -0.0403 |  | LF | Bldg | 4850 | 0.682 | 4850 | 0.682 | 1.08 | 1.28 | -0.0083093 | 4850 | 0.682 | 4850 | 0.682 | 1.08 | 1.28 | -0.00831
LFBldgSDGGroNewCZ10 | Com-Iltg-dWatt-LF_OSbldg | SDG | Gro | New | CZ10 | 4.85 | 0.000682 | 0 | 5.25 | 0.000939 | -0.043 | 4.85 | 0.000682 | 0 | 5.25 | 0.000939 | -0.043 |  | LF | Bldg | 4850 | 0.682 | 4850 | 0.682 | 1.08 | 1.38 | -0.008866 | 4850 | 0.682 | 4850 | 0.682 | 1.08 | 1.38 | -0.00887
LFBldgSDGGroNewCZ14 | Com-Iltg-dWatt-LF_OSbldg | SDG | Gro | New | CZ14 | 4.85 | 0.000682 | 0 | 5.24 | 0.000933 | -0.0514 | 4.85 | 0.000682 | 0 | 5.24 | 0.000933 | -0.0514 |  | LF | Bldg | 4850 | 0.682 | 4850 | 0.682 | 1.08 | 1.37 | -0.010598 | 4850 | 0.682 | 4850 | 0.682 | 1.08 | 1.37 | -0.0106
LFBldgSDGGroNewCZ15 | Com-Iltg-dWatt-LF_OSbldg | SDG | Gro | New | CZ15 | 4.85 | 0.000682 | 0 | 5.67 | 0.000943 | -0.0237 | 4.85 | 0.000682 | 0 | 5.67 | 0.000943 | -0.0237 |  | LF | Bldg | 4850 | 0.682 | 4850 | 0.682 | 1.17 | 1.38 | -0.0048866 | 4850 | 0.682 | 4850 | 0.682 | 1.17 | 1.38 | -0.00489
LFBldgSDGGroNewIOU | Com-Iltg-dWatt-LF_OSbldg | SDG | Gro | New | IOU | 4.85 | 0.000682 | 0 | 5.1681 | 0.00086159 | -0.044833 | 4.85 | 0.000682 | 0 | 5.1681 | 0.00086159 | -0.044833 |  | LF | Bldg | 4850 | 0.682 | 4850 | 0.682 | 1.07 | 1.26 | -0.0092439 | 4850 | 0.682 | 4850 | 0.682 | 1.07 | 1.26 | -0.00924
LFBldgSDGHspExCZ06 | Com-Iltg-dWatt-LF_OSbldg | SDG | Hsp | Ex | CZ06 | 5.2607 | 0.00082721 | 0 | 6.0303 | 0.0010307 | -0.027103 | 5.24 | 0.00082204 | 0 | 6.0007 | 0.00103 | -0.027 |  | LF | Bldg | 5260 | 0.827 | 5240 | 0.822 | 1.15 | 1.25 | -0.0051527 | 5260 | 0.827 | 5240 | 0.822 | 1.15 | 1.25 | -0.00515
LFBldgSDGHspExCZ07 | Com-Iltg-dWatt-LF_OSbldg | SDG | Hsp | Ex | CZ07 | 5.2592 | 0.00082684 | 0 | 6.0288 | 0.00102 | -0.024796 | 5.24 | 0.00082204 | 0 | 6 | 0.00102 | -0.0247 |  | LF | Bldg | 5260 | 0.827 | 5240 | 0.822 | 1.15 | 1.24 | -0.0047137 | 5260 | 0.827 | 5240 | 0.822 | 1.15 | 1.24 | -0.00471
LFBldgSDGHspExCZ08 | Com-Iltg-dWatt-LF_OSbldg | SDG | Hsp | Ex | CZ08 | 5.2616 | 0.00082744 | 0 | 6.0612 | 0.0010312 | -0.026708 | 5.24 | 0.00082204 | 0 | 6.0312 | 0.00103 | -0.0266 |  | LF | Bldg | 5260 | 0.827 | 5240 | 0.822 | 1.15 | 1.25 | -0.0050763 | 5260 | 0.827 | 5240 | 0.822 | 1.15 | 1.25 | -0.00508
LFBldgSDGHspExCZ10 | Com-Iltg-dWatt-LF_OSbldg | SDG | Hsp | Ex | CZ10 | 5.2616 | 0.00082744 | 0 | 6.0612 | 0.0010608 | -0.028808 | 5.24 | 0.00082204 | 0 | 6.0312 | 0.00105 | -0.0287 |  | LF | Bldg | 5260 | 0.827 | 5240 | 0.822 | 1.15 | 1.28 | -0.0054771 | 5260 | 0.827 | 5240 | 0.822 | 1.15 | 1.28 | -0.00548
LFBldgSDGHspExCZ14 | Com-Iltg-dWatt-LF_OSbldg | SDG | Hsp | Ex | CZ14 | 5.2613 | 0.00082736 | 0 | 5.9624 | 0.0010512 | -0.035318 | 5.24 | 0.00082205 | 0 | 5.94 | 0.00105 | -0.0352 |  | LF | Bldg | 5260 | 0.827 | 5240 | 0.822 | 1.13 | 1.28 | -0.0067176 | 5260 | 0.827 | 5240 | 0.822 | 1.13 | 1.28 | -0.00672
LFBldgSDGHspExIOU | Com-Iltg-dWatt-LF_OSbldg | SDG | Hsp | Ex | IOU | 5.2597 | 0.00082696 | 0 | 6.0348 | 0.0010265 | -0.025507 | 5.24 | 0.00082204 | 0 | 6.0058 | 0.0010249 | -0.025409 |  | LF | Bldg | 5260 | 0.827 | 5240 | 0.822 | 1.15 | 1.25 | -0.004849 | 5260 | 0.827 | 5240 | 0.822 | 1.15 | 1.25 | -0.00485
LFBldgSDGHspNewCZ06 | Com-Iltg-dWatt-LF_OSbldg | SDG | Hsp | New | CZ06 | 5.24 | 0.000823 | 0 | 5.77 | 0.00099 | -0.0281 | 5.24 | 0.000823 | 0 | 5.77 | 0.00099 | -0.0281 |  | LF | Bldg | 5240 | 0.823 | 5240 | 0.823 | 1.1 | 1.2 | -0.0053626 | 5240 | 0.823 | 5240 | 0.823 | 1.1 | 1.2 | -0.00536
LFBldgSDGHspNewCZ07 | Com-Iltg-dWatt-LF_OSbldg | SDG | Hsp | New | CZ07 | 5.24 | 0.000823 | 0 | 5.79 | 0.000981 | -0.0233 | 5.24 | 0.000823 | 0 | 5.79 | 0.000981 | -0.0233 |  | LF | Bldg | 5240 | 0.823 | 5240 | 0.823 | 1.1 | 1.19 | -0.0044466 | 5240 | 0.823 | 5240 | 0.823 | 1.1 | 1.19 | -0.00445
LFBldgSDGHspNewCZ08 | Com-Iltg-dWatt-LF_OSbldg | SDG | Hsp | New | CZ08 | 5.24 | 0.000823 | 0 | 5.82 | 0.000993 | -0.0264 | 5.24 | 0.000823 | 0 | 5.82 | 0.000993 | -0.0264 |  | LF | Bldg | 5240 | 0.823 | 5240 | 0.823 | 1.11 | 1.21 | -0.0050382 | 5240 | 0.823 | 5240 | 0.823 | 1.11 | 1.21 | -0.00504
LFBldgSDGHspNewCZ10 | Com-Iltg-dWatt-LF_OSbldg | SDG | Hsp | New | CZ10 | 5.24 | 0.000823 | 0 | 5.81 | 0.00103 | -0.0282 | 5.24 | 0.000823 | 0 | 5.81 | 0.00103 | -0.0282 |  | LF | Bldg | 5240 | 0.823 | 5240 | 0.823 | 1.11 | 1.25 | -0.0053817 | 5240 | 0.823 | 5240 | 0.823 | 1.11 | 1.25 | -0.00538
LFBldgSDGHspNewCZ14 | Com-Iltg-dWatt-LF_OSbldg | SDG | Hsp | New | CZ14 | 5.24 | 0.000823 | 0 | 5.73 | 0.00102 | -0.0358 | 5.24 | 0.000823 | 0 | 5.73 | 0.00102 | -0.0358 |  | LF | Bldg | 5240 | 0.823 | 5240 | 0.823 | 1.09 | 1.24 | -0.0068321 | 5240 | 0.823 | 5240 | 0.823 | 1.09 | 1.24 | -0.00683
LFBldgSDGHspNewCZ15 | Com-Iltg-dWatt-LF_OSbldg | SDG | Hsp | New | CZ15 | 5.24 | 0.000823 | 0 | 6.08 | 0.00104 | -0.0201 | 5.24 | 0.000823 | 0 | 6.08 | 0.00104 | -0.0201 |  | LF | Bldg | 5240 | 0.823 | 5240 | 0.823 | 1.16 | 1.26 | -0.0038359 | 5240 | 0.823 | 5240 | 0.823 | 1.16 | 1.26 | -0.00384
LFBldgSDGHspNewIOU | Com-Iltg-dWatt-LF_OSbldg | SDG | Hsp | New | IOU | 5.24 | 0.000823 | 0 | 5.7936 | 0.00098866 | -0.024252 | 5.24 | 0.000823 | 0 | 5.7936 | 0.00098866 | -0.024252 |  | LF | Bldg | 5240 | 0.823 | 5240 | 0.823 | 1.11 | 1.2 | -0.0046282 | 5240 | 0.823 | 5240 | 0.823 | 1.11 | 1.2 | -0.00463
LFBldgSDGHtlExCZ06 | Com-Iltg-dWatt-LF_OSbldg | SDG | Htl | Ex | CZ06 | 1.9522 | 0.00024254 | 0 | 2.0919 | 0.00030362 | -0.0048766 | 1.91 | 0.000237 | 0 | 2.0497 | 0.00029697 | -0.0047768 |  | LF | Bldg | 1950 | 0.243 | 1910 | 0.237 | 1.07 | 1.25 | -0.002501 | 1950 | 0.243 | 1910 | 0.237 | 1.07 | 1.25 | -0.0025
LFBldgSDGHtlExCZ07 | Com-Iltg-dWatt-LF_OSbldg | SDG | Htl | Ex | CZ07 | 1.9459 | 0.00024148 | 0 | 2.1348 | 0.00030028 | -0.0039217 | 1.91 | 0.000237 | 0 | 2.099 | 0.0002949 | -0.003859 |  | LF | Bldg | 1950 | 0.241 | 1910 | 0.237 | 1.1 | 1.24 | -0.0020204 | 1950 | 0.241 | 1910 | 0.237 | 1.1 | 1.24 | -0.00202
LFBldgSDGHtlExCZ08 | Com-Iltg-dWatt-LF_OSbldg | SDG | Htl | Ex | CZ08 | 1.9479 | 0.00024183 | 0 | 2.1186 | 0.00030479 | -0.0043162 | 1.91 | 0.000237 | 0 | 2.08 | 0.000299 | -0.004239 |  | LF | Bldg | 1950 | 0.242 | 1910 | 0.237 | 1.09 | 1.26 | -0.0022194 | 1950 | 0.242 | 1910 | 0.237 | 1.09 | 1.26 | -0.00222
LFBldgSDGHtlExCZ10 | Com-Iltg-dWatt-LF_OSbldg | SDG | Htl | Ex | CZ10 | 1.9479 | 0.00024183 | 0 | 2.0879 | 0.00030869 | -0.0048252 | 1.91 | 0.000237 | 0 | 2.05 | 0.0003029 | -0.004739 |  | LF | Bldg | 1950 | 0.242 | 1910 | 0.237 | 1.07 | 1.28 | -0.0024811 | 1950 | 0.242 | 1910 | 0.237 | 1.07 | 1.28 | -0.00248
LFBldgSDGHtlExCZ14 | Com-Iltg-dWatt-LF_OSbldg | SDG | Htl | Ex | CZ14 | 1.9479 | 0.00024183 | 0 | 1.9886 | 0.00031069 | -0.0064824 | 1.91 | 0.000237 | 0 | 1.959 | 0.00030483 | -0.0063672 |  | LF | Bldg | 1950 | 0.242 | 1910 | 0.237 | 1.03 | 1.29 | -0.0033336 | 1950 | 0.242 | 1910 | 0.237 | 1.03 | 1.29 | -0.00333
LFBldgSDGHtlExCZ15 | Com-Iltg-dWatt-LF_OSbldg | SDG | Htl | Ex | CZ15 | 1.9479 | 0.00024183 | 0 | 2.2569 | 0.00031176 | -0.0027865 | 1.91 | 0.000237 | 0 | 2.2183 | 0.0003059 | -0.00273 |  | LF | Bldg | 1950 | 0.242 | 1910 | 0.237 | 1.16 | 1.29 | -0.0014293 | 1950 | 0.242 | 1910 | 0.237 | 1.16 | 1.29 | -0.00143
LFBldgSDGHtlExIOU | Com-Iltg-dWatt-LF_OSbldg | SDG | Htl | Ex | IOU | 1.9464 | 0.00024158 | 0 | 2.1283 | 0.00030147 | -0.0040654 | 1.91 | 0.000237 | 0 | 2.0919 | 0.00029598 | -0.0039982 |  | LF | Bldg | 1950 | 0.242 | 1910 | 0.237 | 1.1 | 1.25 | -0.0020933 | 1950 | 0.242 | 1910 | 0.237 | 1.1 | 1.25 | -0.00209
LFBldgSDGHtlNewCZ06 | Com-Iltg-dWatt-LF_OSbldg | SDG | Htl | New | CZ06 | 1.91 | 0.000237 | 0 | 2.03 | 0.000304 | -0.00462 | 1.91 | 0.000237 | 0 | 2.03 | 0.000304 | -0.00462 |  | LF | Bldg | 1910 | 0.237 | 1910 | 0.237 | 1.06 | 1.28 | -0.0024188 | 1910 | 0.237 | 1910 | 0.237 | 1.06 | 1.28 | -0.00242
LFBldgSDGHtlNewCZ07 | Com-Iltg-dWatt-LF_OSbldg | SDG | Htl | New | CZ07 | 1.91 | 0.000237 | 0 | 2.07 | 0.000299 | -0.00307 | 1.91 | 0.000237 | 0 | 2.07 | 0.000299 | -0.00307 |  | LF | Bldg | 1910 | 0.237 | 1910 | 0.237 | 1.08 | 1.26 | -0.0016073 | 1910 | 0.237 | 1910 | 0.237 | 1.08 | 1.26 | -0.00161
LFBldgSDGHtlNewCZ08 | Com-Iltg-dWatt-LF_OSbldg | SDG | Htl | New | CZ08 | 1.91 | 0.000237 | 0 | 2.06 | 0.000307 | -0.00395 | 1.91 | 0.000237 | 0 | 2.06 | 0.000307 | -0.00395 |  | LF | Bldg | 1910 | 0.237 | 1910 | 0.237 | 1.08 | 1.3 | -0.0020681 | 1910 | 0.237 | 1910 | 0.237 | 1.08 | 1.3 | -0.00207
LFBldgSDGHtlNewCZ10 | Com-Iltg-dWatt-LF_OSbldg | SDG | Htl | New | CZ10 | 1.91 | 0.000237 | 0 | 2.03 | 0.000317 | -0.00509 | 1.91 | 0.000237 | 0 | 2.03 | 0.000317 | -0.00509 |  | LF | Bldg | 1910 | 0.237 | 1910 | 0.237 | 1.06 | 1.34 | -0.0026649 | 1910 | 0.237 | 1910 | 0.237 | 1.06 | 1.34 | -0.00266
LFBldgSDGHtlNewCZ14 | Com-Iltg-dWatt-LF_OSbldg | SDG | Htl | New | CZ14 | 1.91 | 0.000237 | 0 | 1.92 | 0.000315 | -0.00755 | 1.91 | 0.000237 | 0 | 1.92 | 0.000315 | -0.00755 |  | LF | Bldg | 1910 | 0.237 | 1910 | 0.237 | 1.01 | 1.33 | -0.0039529 | 1910 | 0.237 | 1910 | 0.237 | 1.01 | 1.33 | -0.00395
LFBldgSDGHtlNewCZ15 | Com-Iltg-dWatt-LF_OSbldg | SDG | Htl | New | CZ15 | 1.91 | 0.000237 | 0 | 2.23 | 0.00032 | -0.00269 | 1.91 | 0.000237 | 0 | 2.23 | 0.00032 | -0.00269 |  | LF | Bldg | 1910 | 0.237 | 1910 | 0.237 | 1.17 | 1.35 | -0.0014084 | 1910 | 0.237 | 1910 | 0.237 | 1.17 | 1.35 | -0.00141
LFBldgSDGHtlNewIOU | Com-Iltg-dWatt-LF_OSbldg | SDG | Htl | New | IOU | 1.91 | 0.000237 | 0 | 2.0647 | 0.00030136 | -0.0033761 | 1.91 | 0.000237 | 0 | 2.0647 | 0.00030136 | -0.0033761 |  | LF | Bldg | 1910 | 0.237 | 1910 | 0.237 | 1.08 | 1.27 | -0.0017676 | 1910 | 0.237 | 1910 | 0.237 | 1.08 | 1.27 | -0.00177
LFBldgSDGMBTExCZ06 | Com-Iltg-dWatt-LF_OSbldg | SDG | MBT | Ex | CZ06 | 3.5198 | 0.00084943 | 0 | 4.098 | 0.0010281 | -0.00092832 | 3.42 | 0.000834 | 0 | 3.98 | 0.00101 | -0.00090381 |  | LF | Bldg | 3520 | 0.849 | 3420 | 0.834 | 1.16 | 1.21 | -0.00026427 | 3520 | 0.849 | 3420 | 0.834 | 1.16 | 1.21 | -0.000264
LFBldgSDGMBTExCZ07 | Com-Iltg-dWatt-LF_OSbldg | SDG | MBT | Ex | CZ07 | 3.5198 | 0.00084943 | 0 | 4.1089 | 0.0010182 | -0.00018144 | 3.42 | 0.000834 | 0 | 4 | 0.001 | -0.000176 |  | LF | Bldg | 3520 | 0.849 | 3420 | 0.834 | 1.17 | 1.2 | -5.1462e-05 | 3520 | 0.849 | 3420 | 0.834 | 1.17 | 1.2 | -5.15e-05
LFBldgSDGMBTExCZ08 | Com-Iltg-dWatt-LF_OSbldg | SDG | MBT | Ex | CZ08 | 3.5198 | 0.00084943 | 0 | 4.098 | 0.0010782 | -0.00059124 | 3.42 | 0.000834 | 0 | 3.9891 | 0.00106 | -0.00057491 |  | LF | Bldg | 3520 | 0.849 | 3420 | 0.834 | 1.17 | 1.27 | -0.0001681 | 3520 | 0.849 | 3420 | 0.834 | 1.17 | 1.27 | -0.000168
LFBldgSDGMBTExCZ10 | Com-Iltg-dWatt-LF_OSbldg | SDG | MBT | Ex | CZ10 | 3.5198 | 0.00084943 | 0 | 4.078 | 0.0010982 | -0.0012063 | 3.42 | 0.000834 | 0 | 3.9691 | 0.00108 | -0.00117 |  | LF | Bldg | 3520 | 0.849 | 3420 | 0.834 | 1.16 | 1.29 | -0.00034211 | 3520 | 0.849 | 3420 | 0.834 | 1.16 | 1.29 | -0.000342
LFBldgSDGMBTExCZ14 | Com-Iltg-dWatt-LF_OSbldg | SDG | MBT | Ex | CZ14 | 3.5198 | 0.00084943 | 0 | 4.018 | 0.0010972 | -0.0029017 | 3.42 | 0.000834 | 0 | 3.9091 | 0.00107 | -0.00282 |  | LF | Bldg | 3520 | 0.849 | 3420 | 0.834 | 1.14 | 1.28 | -0.00082456 | 3520 | 0.849 | 3420 | 0.834 | 1.14 | 1.28 | -0.000825
LFBldgSDGMBTExCZ15 | Com-Iltg-dWatt-LF_OSbldg | SDG | MBT | Ex | CZ15 | 3.5198 | 0.00084943 | 0 | 4.248 | 0.0011072 | 0 | 3.42 | 0.000834 | 0 | 4.13 | 0.00108 | 0 |  | LF | Bldg | 3520 | 0.849 | 3420 | 0.834 | 1.21 | 1.29 | 0 | 3520 | 0.849 | 3420 | 0.834 | 1.21 | 1.29 | 0
LFBldgSDGMBTExIOU | Com-Iltg-dWatt-LF_OSbldg | SDG | MBT | Ex | IOU | 3.5198 | 0.00084943 | 0 | 4.0985 | 0.001045 | -0.00055021 | 3.42 | 0.000834 | 0 | 3.9893 | 0.0010267 | -0.00053386 |  | LF | Bldg | 3520 | 0.849 | 3420 | 0.834 | 1.17 | 1.23 | -0.0001561 | 3520 | 0.849 | 3420 | 0.834 | 1.17 | 1.23 | -0.000156
LFBldgSDGMBTNewCZ06 | Com-Iltg-dWatt-LF_OSbldg | SDG | MBT | New | CZ06 | 3.42 | 0.000834 | 0 | 3.86 | 0.00105 | -0.00118 | 3.42 | 0.000834 | 0 | 3.86 | 0.00105 | -0.00118 |  | LF | Bldg | 3420 | 0.834 | 3420 | 0.834 | 1.13 | 1.26 | -0.00034503 | 3420 | 0.834 | 3420 | 0.834 | 1.13 | 1.26 | -0.000345
LFBldgSDGMBTNewCZ07 | Com-Iltg-dWatt-LF_OSbldg | SDG | MBT | New | CZ07 | 3.42 | 0.000834 | 0 | 3.84 | 0.00104 | 0 | 3.42 | 0.000834 | 0 | 3.84 | 0.00104 | 0 |  | LF | Bldg | 3420 | 0.834 | 3420 | 0.834 | 1.12 | 1.25 | 0 | 3420 | 0.834 | 3420 | 0.834 | 1.12 | 1.25 | 0
LFBldgSDGMBTNewCZ08 | Com-Iltg-dWatt-LF_OSbldg | SDG | MBT | New | CZ08 | 3.42 | 0.000834 | 0 | 3.87 | 0.00108 | -0.000943 | 3.42 | 0.000834 | 0 | 3.87 | 0.00108 | -0.000943 |  | LF | Bldg | 3420 | 0.834 | 3420 | 0.834 | 1.13 | 1.29 | -0.00027573 | 3420 | 0.834 | 3420 | 0.834 | 1.13 | 1.29 | -0.000276
LFBldgSDGMBTNewCZ10 | Com-Iltg-dWatt-LF_OSbldg | SDG | MBT | New | CZ10 | 3.42 | 0.000834 | 0 | 3.88 | 0.00113 | -0.00118 | 3.42 | 0.000834 | 0 | 3.88 | 0.00113 | -0.00118 |  | LF | Bldg | 3420 | 0.834 | 3420 | 0.834 | 1.13 | 1.35 | -0.00034503 | 3420 | 0.834 | 3420 | 0.834 | 1.13 | 1.35 | -0.000345
LFBldgSDGMBTNewCZ14 | Com-Iltg-dWatt-LF_OSbldg | SDG | MBT | New | CZ14 | 3.42 | 0.000834 | 0 | 3.83 | 0.00111 | -0.00224 | 3.42 | 0.000834 | 0 | 3.83 | 0.00111 | -0.00224 |  | LF | Bldg | 3420 | 0.834 | 3420 | 0.834 | 1.12 | 1.33 | -0.00065497 | 3420 | 0.834 | 3420 | 0.834 | 1.12 | 1.33 | -0.000655
LFBldgSDGMBTNewCZ15 | Com-Iltg-dWatt-LF_OSbldg | SDG | MBT | New | CZ15 | 3.42 | 0.000834 | 0 | 4.08 | 0.00113 | 0 | 3.42 | 0.000834 | 0 | 4.08 | 0.00113 | 0 |  | LF | Bldg | 3420 | 0.834 | 3420 | 0.834 | 1.19 | 1.35 | 0 | 3420 | 0.834 | 3420 | 0.834 | 1.19 | 1.35 | 0
LFBldgSDGMBTNewIOU | Com-Iltg-dWatt-LF_OSbldg | SDG | MBT | New | IOU | 3.42 | 0.000834 | 0 | 3.854 | 0.0010694 | -0.00043669 | 3.42 | 0.000834 | 0 | 3.854 | 0.0010694 | -0.00043669 |  | LF | Bldg | 3420 | 0.834 | 3420 | 0.834 | 1.13 | 1.28 | -0.00012769 | 3420 | 0.834 | 3420 | 0.834 | 1.13 | 1.28 | -0.000128
LFBldgSDGMLIExCZ06 | Com-Iltg-dWatt-LF_OSbldg | SDG | MLI | Ex | CZ06 | 3.2191 | 0.00092382 | 0 | 3.4791 | 0.0011091 | -0.0067591 | 3.21 | 0.000922 | 0 | 3.47 | 0.0011 | -0.00675 |  | LF | Bldg | 3220 | 0.924 | 3210 | 0.922 | 1.08 | 1.19 | -0.0021028 | 3220 | 0.924 | 3210 | 0.922 | 1.08 | 1.19 | -0.0021
LFBldgSDGMLIExCZ07 | Com-Iltg-dWatt-LF_OSbldg | SDG | MLI | Ex | CZ07 | 3.2191 | 0.00092382 | 0 | 3.47 | 0.0011 | -0.0033791 | 3.21 | 0.000922 | 0 | 3.47 | 0.0011 | -0.0033791 |  | LF | Bldg | 3220 | 0.924 | 3210 | 0.922 | 1.08 | 1.19 | -0.0010527 | 3220 | 0.924 | 3210 | 0.922 | 1.08 | 1.19 | -0.00105
LFBldgSDGMLIExCZ08 | Com-Iltg-dWatt-LF_OSbldg | SDG | MLI | Ex | CZ08 | 3.2191 | 0.00092382 | 0 | 3.51 | 0.0011091 | -0.00553 | 3.21 | 0.000922 | 0 | 3.51 | 0.0011 | -0.00553 |  | LF | Bldg | 3220 | 0.924 | 3210 | 0.922 | 1.09 | 1.19 | -0.0017227 | 3220 | 0.924 | 3210 | 0.922 | 1.09 | 1.19 | -0.00172
LFBldgSDGMLIExCZ10 | Com-Iltg-dWatt-LF_OSbldg | SDG | MLI | Ex | CZ10 | 3.2191 | 0.00092382 | 0 | 3.5 | 0.0011391 | -0.00762 | 3.21 | 0.000922 | 0 | 3.5 | 0.00113 | -0.00762 |  | LF | Bldg | 3220 | 0.924 | 3210 | 0.922 | 1.09 | 1.23 | -0.0023738 | 3220 | 0.924 | 3210 | 0.922 | 1.09 | 1.23 | -0.00237
LFBldgSDGMLIExCZ14 | Com-Iltg-dWatt-LF_OSbldg | SDG | MLI | Ex | CZ14 | 3.2191 | 0.00092382 | 0 | 3.4 | 0.00112 | -0.0216 | 3.21 | 0.000922 | 0 | 3.4 | 0.00112 | -0.0216 |  | LF | Bldg | 3220 | 0.924 | 3210 | 0.922 | 1.06 | 1.21 | -0.006729 | 3220 | 0.924 | 3210 | 0.922 | 1.06 | 1.21 | -0.00673
LFBldgSDGMLIExCZ15 | Com-Iltg-dWatt-LF_OSbldg | SDG | MLI | Ex | CZ15 | 3.2191 | 0.00092382 | 0 | 3.76 | 0.00112 | -0.00207 | 3.21 | 0.000922 | 0 | 3.76 | 0.00112 | -0.00207 |  | LF | Bldg | 3220 | 0.924 | 3210 | 0.922 | 1.17 | 1.21 | -0.00064486 | 3220 | 0.924 | 3210 | 0.922 | 1.17 | 1.21 | -0.000645
LFBldgSDGMLIExIOU | Com-Iltg-dWatt-LF_OSbldg | SDG | MLI | Ex | IOU | 3.2191 | 0.00092382 | 0 | 3.4804 | 0.0011126 | -0.004988 | 3.21 | 0.000922 | 0 | 3.4801 | 0.0011094 | -0.0049877 |  | LF | Bldg | 3220 | 0.924 | 3210 | 0.922 | 1.08 | 1.2 | -0.0015538 | 3220 | 0.924 | 3210 | 0.922 | 1.08 | 1.2 | -0.00155
LFBldgSDGMLINewCZ06 | Com-Iltg-dWatt-LF_OSbldg | SDG | MLI | New | CZ06 | 3.21 | 0.000922 | 0 | 3.46 | 0.00113 | -0.00967 | 3.21 | 0.000922 | 0 | 3.46 | 0.00113 | -0.00967 |  | LF | Bldg | 3210 | 0.922 | 3210 | 0.922 | 1.08 | 1.23 | -0.0030125 | 3210 | 0.922 | 3210 | 0.922 | 1.08 | 1.23 | -0.00301
LFBldgSDGMLINewCZ07 | Com-Iltg-dWatt-LF_OSbldg | SDG | MLI | New | CZ07 | 3.21 | 0.000922 | 0 | 3.41 | 0.0011 | -0.00495 | 3.21 | 0.000922 | 0 | 3.41 | 0.0011 | -0.00495 |  | LF | Bldg | 3210 | 0.922 | 3210 | 0.922 | 1.06 | 1.19 | -0.0015421 | 3210 | 0.922 | 3210 | 0.922 | 1.06 | 1.19 | -0.00154
LFBldgSDGMLINewCZ08 | Com-Iltg-dWatt-LF_OSbldg | SDG | MLI | New | CZ08 | 3.21 | 0.000922 | 0 | 3.51 | 0.00115 | -0.00752 | 3.21 | 0.000922 | 0 | 3.51 | 0.00115 | -0.00752 |  | LF | Bldg | 3210 | 0.922 | 3210 | 0.922 | 1.09 | 1.25 | -0.0023427 | 3210 | 0.922 | 3210 | 0.922 | 1.09 | 1.25 | -0.00234
LFBldgSDGMLINewCZ10 | Com-Iltg-dWatt-LF_OSbldg | SDG | MLI | New | CZ10 | 3.21 | 0.000922 | 0 | 3.55 | 0.00122 | -0.00926 | 3.21 | 0.000922 | 0 | 3.55 | 0.00122 | -0.00926 |  | LF | Bldg | 3210 | 0.922 | 3210 | 0.922 | 1.11 | 1.32 | -0.0028847 | 3210 | 0.922 | 3210 | 0.922 | 1.11 | 1.32 | -0.00288
LFBldgSDGMLINewCZ14 | Com-Iltg-dWatt-LF_OSbldg | SDG | MLI | New | CZ14 | 3.21 | 0.000922 | 0 | 3.49 | 0.0012 | -0.0209 | 3.21 | 0.000922 | 0 | 3.49 | 0.0012 | -0.0209 |  | LF | Bldg | 3210 | 0.922 | 3210 | 0.922 | 1.09 | 1.3 | -0.0065109 | 3210 | 0.922 | 3210 | 0.922 | 1.09 | 1.3 | -0.00651
LFBldgSDGMLINewCZ15 | Com-Iltg-dWatt-LF_OSbldg | SDG | MLI | New | CZ15 | 3.21 | 0.000922 | 0 | 3.8 | 0.00124 | -0.00143 | 3.21 | 0.000922 | 0 | 3.8 | 0.00124 | -0.00143 |  | LF | Bldg | 3210 | 0.922 | 3210 | 0.922 | 1.18 | 1.34 | -0.00044548 | 3210 | 0.922 | 3210 | 0.922 | 1.18 | 1.34 | -0.000445
LFBldgSDGMLINewIOU | Com-Iltg-dWatt-LF_OSbldg | SDG | MLI | New | IOU | 3.21 | 0.000922 | 0 | 3.4581 | 0.0011398 | -0.0066039 | 3.21 | 0.000922 | 0 | 3.4581 | 0.0011398 | -0.0066039 |  | LF | Bldg | 3210 | 0.922 | 3210 | 0.922 | 1.08 | 1.24 | -0.0020573 | 3210 | 0.922 | 3210 | 0.922 | 1.08 | 1.24 | -0.00206
LFBldgSDGMtlExCZ06 | Com-Iltg-dWatt-LF_OSbldg | SDG | Mtl | Ex | CZ06 | 1.5448 | 0.00017138 | 0 | 1.7248 | 0.00021528 | -0.0049834 | 1.5 | 0.000166 | 0 | 1.68 | 0.000209 | -0.00484 |  | LF | Bldg | 1540 | 0.171 | 1500 | 0.166 | 1.12 | 1.26 | -0.0032267 | 1540 | 0.171 | 1500 | 0.166 | 1.12 | 1.26 | -0.00323
LFBldgSDGMtlExCZ07 | Com-Iltg-dWatt-LF_OSbldg | SDG | Mtl | Ex | CZ07 | 1.5448 | 0.00017138 | 0 | 1.7738 | 0.00021428 | -0.0036476 | 1.5 | 0.000166 | 0 | 1.72 | 0.000208 | -0.00354 |  | LF | Bldg | 1540 | 0.171 | 1500 | 0.166 | 1.15 | 1.25 | -0.00236 | 1540 | 0.171 | 1500 | 0.166 | 1.15 | 1.25 | -0.00236
LFBldgSDGMtlExCZ08 | Com-Iltg-dWatt-LF_OSbldg | SDG | Mtl | Ex | CZ08 | 1.5448 | 0.00017138 | 0 | 1.7538 | 0.00021817 | -0.0041955 | 1.5 | 0.000166 | 0 | 1.7 | 0.000211 | -0.00407 |  | LF | Bldg | 1540 | 0.171 | 1500 | 0.166 | 1.13 | 1.27 | -0.0027133 | 1540 | 0.171 | 1500 | 0.166 | 1.13 | 1.27 | -0.00271
LFBldgSDGMtlExCZ10 | Com-Iltg-dWatt-LF_OSbldg | SDG | Mtl | Ex | CZ10 | 1.5448 | 0.00017138 | 0 | 1.7338 | 0.00022428 | -0.0049234 | 1.5 | 0.000166 | 0 | 1.68 | 0.0002171 | -0.00478 |  | LF | Bldg | 1540 | 0.171 | 1500 | 0.166 | 1.12 | 1.31 | -0.0031867 | 1540 | 0.171 | 1500 | 0.166 | 1.12 | 1.31 | -0.00319
LFBldgSDGMtlExCZ14 | Com-Iltg-dWatt-LF_OSbldg | SDG | Mtl | Ex | CZ14 | 1.5448 | 0.00017138 | 0 | 1.6738 | 0.00022417 | -0.0067572 | 1.5 | 0.000166 | 0 | 1.62 | 0.000217 | -0.00656 |  | LF | Bldg | 1540 | 0.171 | 1500 | 0.166 | 1.08 | 1.31 | -0.0043733 | 1540 | 0.171 | 1500 | 0.166 | 1.08 | 1.31 | -0.00437
LFBldgSDGMtlExCZ15 | Com-Iltg-dWatt-LF_OSbldg | SDG | Mtl | Ex | CZ15 | 1.5448 | 0.00017138 | 0 | 1.8538 | 0.00022817 | -0.0020727 | 1.5 | 0.000166 | 0 | 1.8 | 0.000221 | -0.00201 |  | LF | Bldg | 1540 | 0.171 | 1500 | 0.166 | 1.2 | 1.33 | -0.00134 | 1540 | 0.171 | 1500 | 0.166 | 1.2 | 1.33 | -0.00134
LFBldgSDGMtlExIOU | Com-Iltg-dWatt-LF_OSbldg | SDG | Mtl | Ex | IOU | 1.5448 | 0.00017138 | 0 | 1.7676 | 0.00021553 | -0.0038454 | 1.5 | 0.000166 | 0 | 1.7142 | 0.00020915 | -0.0037323 |  | LF | Bldg | 1540 | 0.171 | 1500 | 0.166 | 1.14 | 1.26 | -0.0024882 | 1540 | 0.171 | 1500 | 0.166 | 1.14 | 1.26 | -0.00249
LFBldgSDGMtlNewCZ06 | Com-Iltg-dWatt-LF_OSbldg | SDG | Mtl | New | CZ06 | 1.5 | 0.000166 | 0 | 1.66 | 0.000214 | -0.00659 | 1.5 | 0.000166 | 0 | 1.66 | 0.000214 | -0.00659 |  | LF | Bldg | 1500 | 0.166 | 1500 | 0.166 | 1.11 | 1.29 | -0.0043933 | 1500 | 0.166 | 1500 | 0.166 | 1.11 | 1.29 | -0.00439
LFBldgSDGMtlNewCZ07 | Com-Iltg-dWatt-LF_OSbldg | SDG | Mtl | New | CZ07 | 1.5 | 0.000166 | 0 | 1.69 | 0.000209 | -0.00473 | 1.5 | 0.000166 | 0 | 1.69 | 0.000209 | -0.00473 |  | LF | Bldg | 1500 | 0.166 | 1500 | 0.166 | 1.13 | 1.26 | -0.0031533 | 1500 | 0.166 | 1500 | 0.166 | 1.13 | 1.26 | -0.00315
LFBldgSDGMtlNewCZ08 | Com-Iltg-dWatt-LF_OSbldg | SDG | Mtl | New | CZ08 | 1.5 | 0.000166 | 0 | 1.69 | 0.000217 | -0.00545 | 1.5 | 0.000166 | 0 | 1.69 | 0.000217 | -0.00545 |  | LF | Bldg | 1500 | 0.166 | 1500 | 0.166 | 1.13 | 1.31 | -0.0036333 | 1500 | 0.166 | 1500 | 0.166 | 1.13 | 1.31 | -0.00363
LFBldgSDGMtlNewCZ10 | Com-Iltg-dWatt-LF_OSbldg | SDG | Mtl | New | CZ10 | 1.5 | 0.000166 | 0 | 1.65 | 0.000222 | -0.0067 | 1.5 | 0.000166 | 0 | 1.65 | 0.000222 | -0.0067 |  | LF | Bldg | 1500 | 0.166 | 1500 | 0.166 | 1.1 | 1.34 | -0.0044667 | 1500 | 0.166 | 1500 | 0.166 | 1.1 | 1.34 | -0.00447
LFBldgSDGMtlNewCZ14 | Com-Iltg-dWatt-LF_OSbldg | SDG | Mtl | New | CZ14 | 1.5 | 0.000166 | 0 | 1.58 | 0.000221 | -0.00873 | 1.5 | 0.000166 | 0 | 1.58 | 0.000221 | -0.00873 |  | LF | Bldg | 1500 | 0.166 | 1500 | 0.166 | 1.05 | 1.33 | -0.00582 | 1500 | 0.166 | 1500 | 0.166 | 1.05 | 1.33 | -0.00582
LFBldgSDGMtlNewCZ15 | Com-Iltg-dWatt-LF_OSbldg | SDG | Mtl | New | CZ15 | 1.5 | 0.000166 | 0 | 1.79 | 0.000225 | -0.00314 | 1.5 | 0.000166 | 0 | 1.79 | 0.000225 | -0.00314 |  | LF | Bldg | 1500 | 0.166 | 1500 | 0.166 | 1.19 | 1.36 | -0.0020933 | 1500 | 0.166 | 1500 | 0.166 | 1.19 | 1.36 | -0.00209
LFBldgSDGMtlNewIOU | Com-Iltg-dWatt-LF_OSbldg | SDG | Mtl | New | IOU | 1.5 | 0.000166 | 0 | 1.6849 | 0.00021079 | -0.0050274 | 1.5 | 0.000166 | 0 | 1.6849 | 0.00021079 | -0.0050274 |  | LF | Bldg | 1500 | 0.166 | 1500 | 0.166 | 1.12 | 1.27 | -0.0033516 | 1500 | 0.166 | 1500 | 0.166 | 1.12 | 1.27 | -0.00335
LFBldgSDGNrsExCZ06 | Com-Iltg-dWatt-LF_OSbldg | SDG | Nrs | Ex | CZ06 | 4.1572 | 0.00067556 | 0 | 4.4672 | 0.00087944 | -0.042772 | 4.0804 | 0.00066404 | 0 | 4.3904 | 0.00086408 | -0.0421 |  | LF | Bldg | 4160 | 0.676 | 4080 | 0.664 | 1.08 | 1.3 | -0.010318 | 4160 | 0.676 | 4080 | 0.664 | 1.08 | 1.3 | -0.0103
LFBldgSDGNrsExCZ07 | Com-Iltg-dWatt-LF_OSbldg | SDG | Nrs | Ex | CZ07 | 4.1572 | 0.00067556 | 0 | 4.4472 | 0.0008664 | -0.039072 | 4.0804 | 0.00066404 | 0 | 4.3704 | 0.00085104 | -0.0384 |  | LF | Bldg | 4160 | 0.676 | 4080 | 0.664 | 1.07 | 1.28 | -0.0094108 | 4160 | 0.676 | 4080 | 0.664 | 1.07 | 1.28 | -0.00941
LFBldgSDGNrsExCZ08 | Com-Iltg-dWatt-LF_OSbldg | SDG | Nrs | Ex | CZ08 | 4.1572 | 0.00067556 | 0 | 4.5172 | 0.00087644 | -0.041476 | 4.0804 | 0.00066404 | 0 | 4.4404 | 0.00086204 | -0.040804 |  | LF | Bldg | 4160 | 0.676 | 4080 | 0.664 | 1.09 | 1.3 | -0.01 | 4160 | 0.676 | 4080 | 0.664 | 1.09 | 1.3 | -0.01
LFBldgSDGNrsExCZ10 | Com-Iltg-dWatt-LF_OSbldg | SDG | Nrs | Ex | CZ10 | 4.1572 | 0.00067556 | 0 | 4.5372 | 0.0009124 | -0.044072 | 4.0804 | 0.00066404 | 0 | 4.4604 | 0.00089608 | -0.043304 |  | LF | Bldg | 4160 | 0.676 | 4080 | 0.664 | 1.09 | 1.35 | -0.010613 | 4160 | 0.676 | 4080 | 0.664 | 1.09 | 1.35 | -0.0106
LFBldgSDGNrsExCZ14 | Com-Iltg-dWatt-LF_OSbldg | SDG | Nrs | Ex | CZ14 | 4.1564 | 0.00067543 | 0 | 4.4763 | 0.00089522 | -0.051458 | 4.0805 | 0.00066405 | 0 | 4.41 | 0.00088005 | -0.050605 |  | LF | Bldg | 4160 | 0.675 | 4080 | 0.664 | 1.08 | 1.33 | -0.012402 | 4160 | 0.675 | 4080 | 0.664 | 1.08 | 1.33 | -0.0124
LFBldgSDGNrsExIOU | Com-Iltg-dWatt-LF_OSbldg | SDG | Nrs | Ex | IOU | 4.1572 | 0.00067556 | 0 | 4.4634 | 0.00087364 | -0.039979 | 4.0804 | 0.00066404 | 0 | 4.3867 | 0.00085819 | -0.039293 |  | LF | Bldg | 4160 | 0.676 | 4080 | 0.664 | 1.08 | 1.29 | -0.0096297 | 4160 | 0.676 | 4080 | 0.664 | 1.08 | 1.29 | -0.00963
LFBldgSDGNrsNewCZ06 | Com-Iltg-dWatt-LF_OSbldg | SDG | Nrs | New | CZ06 | 4.09 | 0.000665 | 0 | 4.23 | 0.00085 | -0.0474 | 4.09 | 0.000665 | 0 | 4.23 | 0.00085 | -0.0474 |  | LF | Bldg | 4090 | 0.665 | 4090 | 0.665 | 1.03 | 1.28 | -0.011589 | 4090 | 0.665 | 4090 | 0.665 | 1.03 | 1.28 | -0.0116
LFBldgSDGNrsNewCZ07 | Com-Iltg-dWatt-LF_OSbldg | SDG | Nrs | New | CZ07 | 4.09 | 0.000665 | 0 | 4.19 | 0.000854 | -0.045 | 4.09 | 0.000665 | 0 | 4.19 | 0.000854 | -0.045 |  | LF | Bldg | 4090 | 0.665 | 4090 | 0.665 | 1.02 | 1.28 | -0.011002 | 4090 | 0.665 | 4090 | 0.665 | 1.02 | 1.28 | -0.011
LFBldgSDGNrsNewCZ08 | Com-Iltg-dWatt-LF_OSbldg | SDG | Nrs | New | CZ08 | 4.09 | 0.000665 | 0 | 4.31 | 0.000856 | -0.0446 | 4.09 | 0.000665 | 0 | 4.31 | 0.000856 | -0.0446 |  | LF | Bldg | 4090 | 0.665 | 4090 | 0.665 | 1.05 | 1.29 | -0.010905 | 4090 | 0.665 | 4090 | 0.665 | 1.05 | 1.29 | -0.0109
LFBldgSDGNrsNewCZ10 | Com-Iltg-dWatt-LF_OSbldg | SDG | Nrs | New | CZ10 | 4.09 | 0.000665 | 0 | 4.36 | 0.000892 | -0.0421 | 4.09 | 0.000665 | 0 | 4.36 | 0.000892 | -0.0421 |  | LF | Bldg | 4090 | 0.665 | 4090 | 0.665 | 1.07 | 1.34 | -0.010293 | 4090 | 0.665 | 4090 | 0.665 | 1.07 | 1.34 | -0.0103
LFBldgSDGNrsNewCZ14 | Com-Iltg-dWatt-LF_OSbldg | SDG | Nrs | New | CZ14 | 4.09 | 0.000665 | 0 | 4.32 | 0.000862 | -0.0556 | 4.09 | 0.000665 | 0 | 4.32 | 0.000862 | -0.0556 |  | LF | Bldg | 4090 | 0.665 | 4090 | 0.665 | 1.06 | 1.3 | -0.013594 | 4090 | 0.665 | 4090 | 0.665 | 1.06 | 1.3 | -0.0136
LFBldgSDGNrsNewCZ15 | Com-Iltg-dWatt-LF_OSbldg | SDG | Nrs | New | CZ15 | 4.09 | 0.000665 | 0 | 4.69 | 0.000885 | -0.0257 | 4.09 | 0.000665 | 0 | 4.69 | 0.000885 | -0.0257 |  | LF | Bldg | 4090 | 0.665 | 4090 | 0.665 | 1.15 | 1.33 | -0.0062836 | 4090 | 0.665 | 4090 | 0.665 | 1.15 | 1.33 | -0.00628
LFBldgSDGNrsNewIOU | Com-Iltg-dWatt-LF_OSbldg | SDG | Nrs | New | IOU | 4.09 | 0.000665 | 0 | 4.2203 | 0.00085933 | -0.044641 | 4.09 | 0.000665 | 0 | 4.2203 | 0.00085933 | -0.044641 |  | LF | Bldg | 4090 | 0.665 | 4090 | 0.665 | 1.03 | 1.29 | -0.010915 | 4090 | 0.665 | 4090 | 0.665 | 1.03 | 1.29 | -0.0109
LFBldgSDGOfLExCZ06 | Com-Iltg-dWatt-LF_OSbldg | SDG | OfL | Ex | CZ06 | 2.6319 | 0.00070795 | 0 | 3.0603 | 0.00090041 | -0.0060011 | 2.49 | 0.00067295 | 0 | 2.8995 | 0.00085595 | -0.0056795 |  | LF | Bldg | 2630 | 0.708 | 2490 | 0.673 | 1.16 | 1.27 | -0.0022809 | 2630 | 0.708 | 2490 | 0.673 | 1.16 | 1.27 | -0.00228
LFBldgSDGOfLExCZ07 | Com-Iltg-dWatt-LF_OSbldg | SDG | OfL | Ex | CZ07 | 2.6319 | 0.00070795 | 0 | 3.0503 | 0.00089141 | -0.0053138 | 2.49 | 0.00067295 | 0 | 2.88 | 0.00084789 | -0.0050395 |  | LF | Bldg | 2630 | 0.708 | 2490 | 0.673 | 1.16 | 1.26 | -0.0020239 | 2630 | 0.708 | 2490 | 0.673 | 1.16 | 1.26 | -0.00202
LFBldgSDGOfLExCZ08 | Com-Iltg-dWatt-LF_OSbldg | SDG | OfL | Ex | CZ08 | 2.6319 | 0.00070795 | 0 | 3.0703 | 0.00090935 | -0.0059811 | 2.49 | 0.00067295 | 0 | 2.9 | 0.00086489 | -0.0056595 |  | LF | Bldg | 2630 | 0.708 | 2490 | 0.673 | 1.16 | 1.29 | -0.0022729 | 2630 | 0.708 | 2490 | 0.673 | 1.16 | 1.29 | -0.00227
LFBldgSDGOfLExCZ10 | Com-Iltg-dWatt-LF_OSbldg | SDG | OfL | Ex | CZ10 | 2.6319 | 0.00070795 | 0 | 3.0603 | 0.00092235 | -0.0070279 | 2.49 | 0.00067295 | 0 | 2.89 | 0.00087695 | -0.0066589 |  | LF | Bldg | 2630 | 0.708 | 2490 | 0.673 | 1.16 | 1.3 | -0.0026743 | 2630 | 0.708 | 2490 | 0.673 | 1.16 | 1.3 | -0.00267
LFBldgSDGOfLExCZ14 | Com-Iltg-dWatt-LF_OSbldg | SDG | OfL | Ex | CZ14 | 2.6319 | 0.00070795 | 0 | 3.0208 | 0.00091736 | -0.0087925 | 2.49 | 0.00067295 | 0 | 2.86 | 0.00087289 | -0.0083289 |  | LF | Bldg | 2630 | 0.708 | 2490 | 0.673 | 1.15 | 1.3 | -0.0033449 | 2630 | 0.708 | 2490 | 0.673 | 1.15 | 1.3 | -0.00334
LFBldgSDGOfLExCZ15 | Com-Iltg-dWatt-LF_OSbldg | SDG | OfL | Ex | CZ15 | 2.6319 | 0.00070794 | 0 | 3.2102 | 0.00092728 | -0.0040775 | 2.49 | 0.00067295 | 0 | 3.04 | 0.00088189 | -0.00386 |  | LF | Bldg | 2630 | 0.708 | 2490 | 0.673 | 1.22 | 1.31 | -0.0015502 | 2630 | 0.708 | 2490 | 0.673 | 1.22 | 1.31 | -0.00155
LFBldgSDGOfLExIOU | Com-Iltg-dWatt-LF_OSbldg | SDG | OfL | Ex | IOU | 2.6319 | 0.00070795 | 0 | 3.0527 | 0.00089749 | -0.0056525 | 2.49 | 0.00067295 | 0 | 2.8827 | 0.0008536 | -0.0053591 |  | LF | Bldg | 2630 | 0.708 | 2490 | 0.673 | 1.16 | 1.27 | -0.0021522 | 2630 | 0.708 | 2490 | 0.673 | 1.16 | 1.27 | -0.00215
LFBldgSDGOfLNewCZ06 | Com-Iltg-dWatt-LF_OSbldg | SDG | OfL | New | CZ06 | 2.49 | 0.000672 | 0 | 2.9 | 0.000846 | -0.00333 | 2.49 | 0.000672 | 0 | 2.9 | 0.000846 | -0.00333 |  | LF | Bldg | 2490 | 0.672 | 2490 | 0.672 | 1.16 | 1.26 | -0.0013373 | 2490 | 0.672 | 2490 | 0.672 | 1.16 | 1.26 | -0.00134
LFBldgSDGOfLNewCZ07 | Com-Iltg-dWatt-LF_OSbldg | SDG | OfL | New | CZ07 | 2.49 | 0.000672 | 0 | 2.88 | 0.000833 | -0.0023 | 2.49 | 0.000672 | 0 | 2.88 | 0.000833 | -0.0023 |  | LF | Bldg | 2490 | 0.672 | 2490 | 0.672 | 1.16 | 1.24 | -0.00092369 | 2490 | 0.672 | 2490 | 0.672 | 1.16 | 1.24 | -0.000924
LFBldgSDGOfLNewCZ08 | Com-Iltg-dWatt-LF_OSbldg | SDG | OfL | New | CZ08 | 2.49 | 0.000672 | 0 | 2.91 | 0.000857 | -0.00296 | 2.49 | 0.000672 | 0 | 2.91 | 0.000857 | -0.00296 |  | LF | Bldg | 2490 | 0.672 | 2490 | 0.672 | 1.17 | 1.28 | -0.0011888 | 2490 | 0.672 | 2490 | 0.672 | 1.17 | 1.28 | -0.00119
LFBldgSDGOfLNewCZ10 | Com-Iltg-dWatt-LF_OSbldg | SDG | OfL | New | CZ10 | 2.49 | 0.000672 | 0 | 2.92 | 0.000882 | -0.00328 | 2.49 | 0.000672 | 0 | 2.92 | 0.000882 | -0.00328 |  | LF | Bldg | 2490 | 0.672 | 2490 | 0.672 | 1.17 | 1.31 | -0.0013173 | 2490 | 0.672 | 2490 | 0.672 | 1.17 | 1.31 | -0.00132
LFBldgSDGOfLNewCZ14 | Com-Iltg-dWatt-LF_OSbldg | SDG | OfL | New | CZ14 | 2.49 | 0.000672 | 0 | 2.88 | 0.000889 | -0.0048 | 2.49 | 0.000672 | 0 | 2.88 | 0.000889 | -0.0048 |  | LF | Bldg | 2490 | 0.672 | 2490 | 0.672 | 1.16 | 1.32 | -0.0019277 | 2490 | 0.672 | 2490 | 0.672 | 1.16 | 1.32 | -0.00193
LFBldgSDGOfLNewCZ15 | Com-Iltg-dWatt-LF_OSbldg | SDG | OfL | New | CZ15 | 2.49 | 0.000672 | 0 | 3.04 | 0.000883 | -0.0017 | 2.49 | 0.000672 | 0 | 3.04 | 0.000883 | -0.0017 |  | LF | Bldg | 2490 | 0.672 | 2490 | 0.672 | 1.22 | 1.31 | -0.00068273 | 2490 | 0.672 | 2490 | 0.672 | 1.22 | 1.31 | -0.000683
LFBldgSDGOfLNewIOU | Com-Iltg-dWatt-LF_OSbldg | SDG | OfL | New | IOU | 2.49 | 0.000672 | 0 | 2.8882 | 0.00084257 | -0.0025154 | 2.49 | 0.000672 | 0 | 2.8882 | 0.00084257 | -0.0025154 |  | LF | Bldg | 2490 | 0.672 | 2490 | 0.672 | 1.16 | 1.25 | -0.0010102 | 2490 | 0.672 | 2490 | 0.672 | 1.16 | 1.25 | -0.00101
LFBldgSDGOfSExCZ06 | Com-Iltg-dWatt-LF_OSbldg | SDG | OfS | Ex | CZ06 | 2.574 | 0.00069001 | 0 | 2.9717 | 0.00086398 | -0.0019978 | 2.25 | 0.00060805 | 0 | 2.5905 | 0.00076105 | -0.0017405 |  | LF | Bldg | 2570 | 0.69 | 2250 | 0.608 | 1.15 | 1.25 | -0.00077354 | 2570 | 0.69 | 2250 | 0.608 | 1.15 | 1.25 | -0.000774
LFBldgSDGOfSExCZ07 | Com-Iltg-dWatt-LF_OSbldg | SDG | OfS | Ex | CZ07 | 2.5741 | 0.00069002 | 0 | 2.9817 | 0.00085608 | -0.00056949 | 2.25 | 0.00060805 | 0 | 2.6005 | 0.00075409 | -0.00049705 |  | LF | Bldg | 2570 | 0.69 | 2250 | 0.608 | 1.16 | 1.24 | -0.00022091 | 2570 | 0.69 | 2250 | 0.608 | 1.16 | 1.24 | -0.000221
LFBldgSDGOfSExCZ08 | Com-Iltg-dWatt-LF_OSbldg | SDG | OfS | Ex | CZ08 | 2.5741 | 0.00069003 | 0 | 2.9918 | 0.000869 | -0.0017192 | 2.25 | 0.00060805 | 0 | 2.6105 | 0.00076605 | -0.0015 |  | LF | Bldg | 2570 | 0.69 | 2250 | 0.608 | 1.16 | 1.26 | -0.00066667 | 2570 | 0.69 | 2250 | 0.608 | 1.16 | 1.26 | -0.000667
LFBldgSDGOfSExCZ10 | Com-Iltg-dWatt-LF_OSbldg | SDG | OfS | Ex | CZ10 | 2.5741 | 0.00069002 | 0 | 2.9817 | 0.00087394 | -0.0026036 | 2.25 | 0.00060805 | 0 | 2.6005 | 0.00077005 | -0.00227 |  | LF | Bldg | 2570 | 0.69 | 2250 | 0.608 | 1.16 | 1.27 | -0.0010089 | 2570 | 0.69 | 2250 | 0.608 | 1.16 | 1.27 | -0.00101
LFBldgSDGOfSExCZ14 | Com-Iltg-dWatt-LF_OSbldg | SDG | OfS | Ex | CZ14 | 2.5739 | 0.00068998 | 0 | 2.9116 | 0.00088384 | -0.0064493 | 2.25 | 0.00060805 | 0 | 2.54 | 0.00077905 | -0.0056205 |  | LF | Bldg | 2570 | 0.69 | 2250 | 0.608 | 1.13 | 1.28 | -0.002498 | 2570 | 0.69 | 2250 | 0.608 | 1.13 | 1.28 | -0.0025
LFBldgSDGOfSExCZ15 | Com-Iltg-dWatt-LF_OSbldg | SDG | OfS | Ex | CZ15 | 2.5744 | 0.00069009 | 0 | 3.1607 | 0.00087204 | -0.00053374 | 2.25 | 0.00060805 | 0 | 2.76 | 0.00076805 | -0.00046505 |  | LF | Bldg | 2570 | 0.69 | 2250 | 0.608 | 1.23 | 1.26 | -0.00020669 | 2570 | 0.69 | 2250 | 0.608 | 1.23 | 1.26 | -0.000207
LFBldgSDGOfSExIOU | Com-Iltg-dWatt-LF_OSbldg | SDG | OfS | Ex | IOU | 2.5741 | 0.00069002 | 0 | 2.9817 | 0.00085975 | -0.0010012 | 2.25 | 0.00060805 | 0 | 2.6004 | 0.00075738 | -0.00087335 |  | LF | Bldg | 2570 | 0.69 | 2250 | 0.608 | 1.16 | 1.25 | -0.00038815 | 2570 | 0.69 | 2250 | 0.608 | 1.16 | 1.25 | -0.000388
LFBldgSDGOfSNewCZ06 | Com-Iltg-dWatt-LF_OSbldg | SDG | OfS | New | CZ06 | 2.25 | 0.000609 | 0 | 2.5 | 0.000751 | -0.00178 | 2.25 | 0.000609 | 0 | 2.5 | 0.000751 | -0.00178 |  | LF | Bldg | 2250 | 0.609 | 2250 | 0.609 | 1.11 | 1.23 | -0.00079111 | 2250 | 0.609 | 2250 | 0.609 | 1.11 | 1.23 | -0.000791
LFBldgSDGOfSNewCZ07 | Com-Iltg-dWatt-LF_OSbldg | SDG | OfS | New | CZ07 | 2.25 | 0.000609 | 0 | 2.48 | 0.000742 | -0.000408 | 2.25 | 0.000609 | 0 | 2.48 | 0.000742 | -0.000408 |  | LF | Bldg | 2250 | 0.609 | 2250 | 0.609 | 1.1 | 1.22 | -0.00018133 | 2250 | 0.609 | 2250 | 0.609 | 1.1 | 1.22 | -0.000181
LFBldgSDGOfSNewCZ08 | Com-Iltg-dWatt-LF_OSbldg | SDG | OfS | New | CZ08 | 2.25 | 0.000609 | 0 | 2.51 | 0.000762 | -0.00153 | 2.25 | 0.000609 | 0 | 2.51 | 0.000762 | -0.00153 |  | LF | Bldg | 2250 | 0.609 | 2250 | 0.609 | 1.12 | 1.25 | -0.00068 | 2250 | 0.609 | 2250 | 0.609 | 1.12 | 1.25 | -0.00068
LFBldgSDGOfSNewCZ10 | Com-Iltg-dWatt-LF_OSbldg | SDG | OfS | New | CZ10 | 2.25 | 0.000609 | 0 | 2.54 | 0.000787 | -0.00121 | 2.25 | 0.000609 | 0 | 2.54 | 0.000787 | -0.00121 |  | LF | Bldg | 2250 | 0.609 | 2250 | 0.609 | 1.13 | 1.29 | -0.00053778 | 2250 | 0.609 | 2250 | 0.609 | 1.13 | 1.29 | -0.000538
LFBldgSDGOfSNewCZ14 | Com-Iltg-dWatt-LF_OSbldg | SDG | OfS | New | CZ14 | 2.25 | 0.000609 | 0 | 2.48 | 0.000787 | -0.00468 | 2.25 | 0.000609 | 0 | 2.48 | 0.000787 | -0.00468 |  | LF | Bldg | 2250 | 0.609 | 2250 | 0.609 | 1.1 | 1.29 | -0.00208 | 2250 | 0.609 | 2250 | 0.609 | 1.1 | 1.29 | -0.00208
LFBldgSDGOfSNewCZ15 | Com-Iltg-dWatt-LF_OSbldg | SDG | OfS | New | CZ15 | 2.25 | 0.000609 | 0 | 2.65 | 0.000796 | 0 | 2.25 | 0.000609 | 0 | 2.65 | 0.000796 | 0 |  | LF | Bldg | 2250 | 0.609 | 2250 | 0.609 | 1.18 | 1.31 | 0 | 2250 | 0.609 | 2250 | 0.609 | 1.18 | 1.31 | 0
LFBldgSDGOfSNewIOU | Com-Iltg-dWatt-LF_OSbldg | SDG | OfS | New | IOU | 2.25 | 0.000609 | 0 | 2.4917 | 0.00075067 | -0.00061719 | 2.25 | 0.000609 | 0 | 2.4917 | 0.00075067 | -0.00061719 |  | LF | Bldg | 2250 | 0.609 | 2250 | 0.609 | 1.11 | 1.23 | -0.00027431 | 2250 | 0.609 | 2250 | 0.609 | 1.11 | 1.23 | -0.000274
LFBldgSDGRFFExCZ06 | Com-Iltg-dWatt-LF_OSbldg | SDG | RFF | Ex | CZ06 | 4.84 | 0.000813 | 0 | 5.4 | 0.001 | -0.0278 | 4.84 | 0.000813 | 0 | 5.4 | 0.001 | -0.0278 |  | LF | Bldg | 4840 | 0.813 | 4840 | 0.813 | 1.12 | 1.23 | -0.0057438 | 4840 | 0.813 | 4840 | 0.813 | 1.12 | 1.23 | -0.00574
LFBldgSDGRFFExCZ07 | Com-Iltg-dWatt-LF_OSbldg | SDG | RFF | Ex | CZ07 | 4.84 | 0.000813 | 0 | 5.41 | 0.000998 | -0.0254 | 4.84 | 0.000813 | 0 | 5.41 | 0.000998 | -0.0254 |  | LF | Bldg | 4840 | 0.813 | 4840 | 0.813 | 1.12 | 1.23 | -0.0052479 | 4840 | 0.813 | 4840 | 0.813 | 1.12 | 1.23 | -0.00525
LFBldgSDGRFFExCZ08 | Com-Iltg-dWatt-LF_OSbldg | SDG | RFF | Ex | CZ08 | 4.84 | 0.000813 | 0 | 5.44 | 0.000995 | -0.0247 | 4.84 | 0.000813 | 0 | 5.44 | 0.000995 | -0.0247 |  | LF | Bldg | 4840 | 0.813 | 4840 | 0.813 | 1.12 | 1.22 | -0.0051033 | 4840 | 0.813 | 4840 | 0.813 | 1.12 | 1.22 | -0.0051
LFBldgSDGRFFExCZ10 | Com-Iltg-dWatt-LF_OSbldg | SDG | RFF | Ex | CZ10 | 4.84 | 0.000813 | 0 | 5.44 | 0.00101 | -0.0273 | 4.84 | 0.000813 | 0 | 5.44 | 0.00101 | -0.0273 |  | LF | Bldg | 4840 | 0.813 | 4840 | 0.813 | 1.12 | 1.24 | -0.0056405 | 4840 | 0.813 | 4840 | 0.813 | 1.12 | 1.24 | -0.00564
LFBldgSDGRFFExCZ14 | Com-Iltg-dWatt-LF_OSbldg | SDG | RFF | Ex | CZ14 | 4.84 | 0.000813 | 0 | 5.33 | 0.00103 | -0.0388 | 4.84 | 0.000813 | 0 | 5.33 | 0.00103 | -0.0388 |  | LF | Bldg | 4840 | 0.813 | 4840 | 0.813 | 1.1 | 1.27 | -0.0080165 | 4840 | 0.813 | 4840 | 0.813 | 1.1 | 1.27 | -0.00802
LFBldgSDGRFFExCZ15 | Com-Iltg-dWatt-LF_OSbldg | SDG | RFF | Ex | CZ15 | 4.84 | 0.000813 | 0 | 5.77 | 0.00102 | -0.0125 | 4.84 | 0.000813 | 0 | 5.77 | 0.00102 | -0.0125 |  | LF | Bldg | 4840 | 0.813 | 4840 | 0.813 | 1.19 | 1.25 | -0.0025826 | 4840 | 0.813 | 4840 | 0.813 | 1.19 | 1.25 | -0.00258
LFBldgSDGRFFExIOU | Com-Iltg-dWatt-LF_OSbldg | SDG | RFF | Ex | IOU | 4.84 | 0.000813 | 0 | 5.4172 | 0.0010007 | -0.025921 | 4.84 | 0.000813 | 0 | 5.4172 | 0.0010007 | -0.025921 |  | LF | Bldg | 4840 | 0.813 | 4840 | 0.813 | 1.12 | 1.23 | -0.0053555 | 4840 | 0.813 | 4840 | 0.813 | 1.12 | 1.23 | -0.00536
LFBldgSDGRFFNewCZ06 | Com-Iltg-dWatt-LF_OSbldg | SDG | RFF | New | CZ06 | 4.84 | 0.000813 | 0 | 5.22 | 0.00102 | -0.0276 | 4.84 | 0.000813 | 0 | 5.22 | 0.00102 | -0.0276 |  | LF | Bldg | 4840 | 0.813 | 4840 | 0.813 | 1.08 | 1.25 | -0.0057025 | 4840 | 0.813 | 4840 | 0.813 | 1.08 | 1.25 | -0.0057
LFBldgSDGRFFNewCZ07 | Com-Iltg-dWatt-LF_OSbldg | SDG | RFF | New | CZ07 | 4.84 | 0.000813 | 0 | 5.19 | 0.00101 | -0.0315 | 4.84 | 0.000813 | 0 | 5.19 | 0.00101 | -0.0315 |  | LF | Bldg | 4840 | 0.813 | 4840 | 0.813 | 1.07 | 1.24 | -0.0065083 | 4840 | 0.813 | 4840 | 0.813 | 1.07 | 1.24 | -0.00651
LFBldgSDGRFFNewCZ08 | Com-Iltg-dWatt-LF_OSbldg | SDG | RFF | New | CZ08 | 4.84 | 0.000813 | 0 | 5.3 | 0.00103 | -0.0299 | 4.84 | 0.000813 | 0 | 5.3 | 0.00103 | -0.0299 |  | LF | Bldg | 4840 | 0.813 | 4840 | 0.813 | 1.1 | 1.27 | -0.0061777 | 4840 | 0.813 | 4840 | 0.813 | 1.1 | 1.27 | -0.00618
LFBldgSDGRFFNewCZ10 | Com-Iltg-dWatt-LF_OSbldg | SDG | RFF | New | CZ10 | 4.84 | 0.000813 | 0 | 5.36 | 0.00107 | -0.0331 | 4.84 | 0.000813 | 0 | 5.36 | 0.00107 | -0.0331 |  | LF | Bldg | 4840 | 0.813 | 4840 | 0.813 | 1.11 | 1.32 | -0.0068388 | 4840 | 0.813 | 4840 | 0.813 | 1.11 | 1.32 | -0.00684
LFBldgSDGRFFNewCZ14 | Com-Iltg-dWatt-LF_OSbldg | SDG | RFF | New | CZ14 | 4.84 | 0.000813 | 0 | 5.33 | 0.00108 | -0.0469 | 4.84 | 0.000813 | 0 | 5.33 | 0.00108 | -0.0469 |  | LF | Bldg | 4840 | 0.813 | 4840 | 0.813 | 1.1 | 1.33 | -0.0096901 | 4840 | 0.813 | 4840 | 0.813 | 1.1 | 1.33 | -0.00969
LFBldgSDGRFFNewCZ15 | Com-Iltg-dWatt-LF_OSbldg | SDG | RFF | New | CZ15 | 4.84 | 0.000813 | 0 | 5.75 | 0.00109 | -0.0163 | 4.84 | 0.000813 | 0 | 5.75 | 0.00109 | -0.0163 |  | LF | Bldg | 4840 | 0.813 | 4840 | 0.813 | 1.19 | 1.34 | -0.0033678 | 4840 | 0.813 | 4840 | 0.813 | 1.19 | 1.34 | -0.00337
LFBldgSDGRFFNewIOU | Com-Iltg-dWatt-LF_OSbldg | SDG | RFF | New | IOU | 4.84 | 0.000813 | 0 | 5.2329 | 0.0010245 | -0.03164 | 4.84 | 0.000813 | 0 | 5.2329 | 0.0010245 | -0.03164 |  | LF | Bldg | 4840 | 0.813 | 4840 | 0.813 | 1.08 | 1.26 | -0.0065371 | 4840 | 0.813 | 4840 | 0.813 | 1.08 | 1.26 | -0.00654
LFBldgSDGRSDExCZ06 | Com-Iltg-dWatt-LF_OSbldg | SDG | RSD | Ex | CZ06 | 4.83 | 0.0008 | 0 | 5.42 | 0.001 | -0.0305 | 4.83 | 0.0008 | 0 | 5.42 | 0.001 | -0.0305 |  | LF | Bldg | 4830 | 0.8 | 4830 | 0.8 | 1.12 | 1.25 | -0.0063147 | 4830 | 0.8 | 4830 | 0.8 | 1.12 | 1.25 | -0.00631
LFBldgSDGRSDExCZ07 | Com-Iltg-dWatt-LF_OSbldg | SDG | RSD | Ex | CZ07 | 4.83 | 0.0008 | 0 | 5.42 | 0.00102 | -0.028 | 4.83 | 0.0008 | 0 | 5.42 | 0.00102 | -0.028 |  | LF | Bldg | 4830 | 0.8 | 4830 | 0.8 | 1.12 | 1.27 | -0.0057971 | 4830 | 0.8 | 4830 | 0.8 | 1.12 | 1.27 | -0.0058
LFBldgSDGRSDExCZ08 | Com-Iltg-dWatt-LF_OSbldg | SDG | RSD | Ex | CZ08 | 4.83 | 0.0008 | 0 | 5.46 | 0.00097 | -0.0253 | 4.83 | 0.0008 | 0 | 5.46 | 0.00097 | -0.0253 |  | LF | Bldg | 4830 | 0.8 | 4830 | 0.8 | 1.13 | 1.21 | -0.0052381 | 4830 | 0.8 | 4830 | 0.8 | 1.13 | 1.21 | -0.00524
LFBldgSDGRSDExCZ10 | Com-Iltg-dWatt-LF_OSbldg | SDG | RSD | Ex | CZ10 | 4.83 | 0.0008 | 0 | 5.42 | 0.000923 | -0.0298 | 4.83 | 0.0008 | 0 | 5.42 | 0.000923 | -0.0298 |  | LF | Bldg | 4830 | 0.8 | 4830 | 0.8 | 1.12 | 1.15 | -0.0061698 | 4830 | 0.8 | 4830 | 0.8 | 1.12 | 1.15 | -0.00617
LFBldgSDGRSDExCZ14 | Com-Iltg-dWatt-LF_OSbldg | SDG | RSD | Ex | CZ14 | 4.83 | 0.0008 | 0 | 5.24 | 0.000922 | -0.0488 | 4.83 | 0.0008 | 0 | 5.24 | 0.000922 | -0.0488 |  | LF | Bldg | 4830 | 0.8 | 4830 | 0.8 | 1.08 | 1.15 | -0.010104 | 4830 | 0.8 | 4830 | 0.8 | 1.08 | 1.15 | -0.0101
LFBldgSDGRSDExCZ15 | Com-Iltg-dWatt-LF_OSbldg | SDG | RSD | Ex | CZ15 | 4.83 | 0.0008 | 0 | 5.84 | 0.00103 | -0.0114 | 4.83 | 0.0008 | 0 | 5.84 | 0.00103 | -0.0114 |  | LF | Bldg | 4830 | 0.8 | 4830 | 0.8 | 1.21 | 1.29 | -0.0023602 | 4830 | 0.8 | 4830 | 0.8 | 1.21 | 1.29 | -0.00236
LFBldgSDGRSDExIOU | Com-Iltg-dWatt-LF_OSbldg | SDG | RSD | Ex | IOU | 4.83 | 0.0008 | 0 | 5.4213 | 0.00099606 | -0.028454 | 4.83 | 0.0008 | 0 | 5.4213 | 0.00099606 | -0.028454 |  | LF | Bldg | 4830 | 0.8 | 4830 | 0.8 | 1.12 | 1.25 | -0.005891 | 4830 | 0.8 | 4830 | 0.8 | 1.12 | 1.25 | -0.00589
LFBldgSDGRSDNewCZ06 | Com-Iltg-dWatt-LF_OSbldg | SDG | RSD | New | CZ06 | 4.83 | 0.0008 | 0 | 5.27 | 0.00101 | -0.0371 | 4.83 | 0.0008 | 0 | 5.27 | 0.00101 | -0.0371 |  | LF | Bldg | 4830 | 0.8 | 4830 | 0.8 | 1.09 | 1.26 | -0.0076812 | 4830 | 0.8 | 4830 | 0.8 | 1.09 | 1.26 | -0.00768
LFBldgSDGRSDNewCZ07 | Com-Iltg-dWatt-LF_OSbldg | SDG | RSD | New | CZ07 | 4.83 | 0.0008 | 0 | 5.24 | 0.00103 | -0.0352 | 4.83 | 0.0008 | 0 | 5.24 | 0.00103 | -0.0352 |  | LF | Bldg | 4830 | 0.8 | 4830 | 0.8 | 1.08 | 1.29 | -0.0072878 | 4830 | 0.8 | 4830 | 0.8 | 1.08 | 1.29 | -0.00729
LFBldgSDGRSDNewCZ08 | Com-Iltg-dWatt-LF_OSbldg | SDG | RSD | New | CZ08 | 4.83 | 0.0008 | 0 | 5.33 | 0.00102 | -0.0304 | 4.83 | 0.0008 | 0 | 5.33 | 0.00102 | -0.0304 |  | LF | Bldg | 4830 | 0.8 | 4830 | 0.8 | 1.1 | 1.27 | -0.006294 | 4830 | 0.8 | 4830 | 0.8 | 1.1 | 1.27 | -0.00629
LFBldgSDGRSDNewCZ10 | Com-Iltg-dWatt-LF_OSbldg | SDG | RSD | New | CZ10 | 4.83 | 0.0008 | 0 | 5.39 | 0.00107 | -0.033 | 4.83 | 0.0008 | 0 | 5.39 | 0.00107 | -0.033 |  | LF | Bldg | 4830 | 0.8 | 4830 | 0.8 | 1.12 | 1.34 | -0.0068323 | 4830 | 0.8 | 4830 | 0.8 | 1.12 | 1.34 | -0.00683
LFBldgSDGRSDNewCZ14 | Com-Iltg-dWatt-LF_OSbldg | SDG | RSD | New | CZ14 | 4.83 | 0.0008 | 0 | 5.26 | 0.00106 | -0.0531 | 4.83 | 0.0008 | 0 | 5.26 | 0.00106 | -0.0531 |  | LF | Bldg | 4830 | 0.8 | 4830 | 0.8 | 1.09 | 1.33 | -0.010994 | 4830 | 0.8 | 4830 | 0.8 | 1.09 | 1.33 | -0.011
LFBldgSDGRSDNewCZ15 | Com-Iltg-dWatt-LF_OSbldg | SDG | RSD | New | CZ15 | 4.83 | 0.0008 | 0 | 5.81 | 0.0011 | -0.0148 | 4.83 | 0.0008 | 0 | 5.81 | 0.0011 | -0.0148 |  | LF | Bldg | 4830 | 0.8 | 4830 | 0.8 | 1.2 | 1.38 | -0.0030642 | 4830 | 0.8 | 4830 | 0.8 | 1.2 | 1.38 | -0.00306
LFBldgSDGRSDNewIOU | Com-Iltg-dWatt-LF_OSbldg | SDG | RSD | New | IOU | 4.83 | 0.0008 | 0 | 5.2777 | 0.0010377 | -0.034673 | 4.83 | 0.0008 | 0 | 5.2777 | 0.0010377 | -0.034673 |  | LF | Bldg | 4830 | 0.8 | 4830 | 0.8 | 1.09 | 1.3 | -0.0071787 | 4830 | 0.8 | 4830 | 0.8 | 1.09 | 1.3 | -0.00718
LFBldgSDGRt3ExCZ06 | Com-Iltg-dWatt-LF_OSbldg | SDG | Rt3 | Ex | CZ06 | 3.3793 | 0.00075924 | 0 | 3.87 | 0.00092723 | -0.0032193 | 3.37 | 0.00075738 | 0 | 3.87 | 0.00092538 | -0.00321 |  | LF | Bldg | 3380 | 0.759 | 3370 | 0.757 | 1.15 | 1.22 | -0.00095252 | 3380 | 0.759 | 3370 | 0.757 | 1.15 | 1.22 | -0.000953
LFBldgSDGRt3ExCZ07 | Com-Iltg-dWatt-LF_OSbldg | SDG | Rt3 | Ex | CZ07 | 3.3793 | 0.00075924 | 0 | 3.8893 | 0.00091324 | -0.00139 | 3.37 | 0.00075738 | 0 | 3.88 | 0.00091138 | -0.00139 |  | LF | Bldg | 3380 | 0.759 | 3370 | 0.757 | 1.15 | 1.2 | -0.00041246 | 3380 | 0.759 | 3370 | 0.757 | 1.15 | 1.2 | -0.000412
LFBldgSDGRt3ExCZ08 | Com-Iltg-dWatt-LF_OSbldg | SDG | Rt3 | Ex | CZ08 | 3.3793 | 0.00075924 | 0 | 3.8893 | 0.00091823 | -0.00288 | 3.37 | 0.00075738 | 0 | 3.88 | 0.00091638 | -0.00288 |  | LF | Bldg | 3380 | 0.759 | 3370 | 0.757 | 1.15 | 1.21 | -0.0008546 | 3380 | 0.759 | 3370 | 0.757 | 1.15 | 1.21 | -0.000855
LFBldgSDGRt3ExCZ10 | Com-Iltg-dWatt-LF_OSbldg | SDG | Rt3 | Ex | CZ10 | 3.3793 | 0.00075924 | 0 | 3.8493 | 0.00093116 | -0.0052593 | 3.37 | 0.00075738 | 0 | 3.84 | 0.00092869 | -0.0052593 |  | LF | Bldg | 3380 | 0.759 | 3370 | 0.757 | 1.14 | 1.23 | -0.0015606 | 3380 | 0.759 | 3370 | 0.757 | 1.14 | 1.23 | -0.00156
LFBldgSDGRt3ExCZ14 | Com-Iltg-dWatt-LF_OSbldg | SDG | Rt3 | Ex | CZ14 | 3.3793 | 0.00075924 | 0 | 3.6793 | 0.00093716 | -0.0192 | 3.37 | 0.00075738 | 0 | 3.67 | 0.00093469 | -0.0192 |  | LF | Bldg | 3380 | 0.759 | 3370 | 0.757 | 1.09 | 1.23 | -0.0056973 | 3380 | 0.759 | 3370 | 0.757 | 1.09 | 1.23 | -0.0057
LFBldgSDGRt3ExCZ15 | Com-Iltg-dWatt-LF_OSbldg | SDG | Rt3 | Ex | CZ15 | 3.3793 | 0.00075923 | 0 | 3.9792 | 0.00095054 | -0.00124 | 3.37 | 0.00075738 | 0 | 3.97 | 0.00094838 | -0.00124 |  | LF | Bldg | 3380 | 0.759 | 3370 | 0.757 | 1.18 | 1.25 | -0.00036795 | 3380 | 0.759 | 3370 | 0.757 | 1.18 | 1.25 | -0.000368
LFBldgSDGRt3ExIOU | Com-Iltg-dWatt-LF_OSbldg | SDG | Rt3 | Ex | IOU | 3.3793 | 0.00075924 | 0 | 3.8786 | 0.00091844 | -0.0025077 | 3.37 | 0.00075738 | 0 | 3.8697 | 0.00091644 | -0.0025074 |  | LF | Bldg | 3380 | 0.759 | 3370 | 0.757 | 1.15 | 1.21 | -0.00074404 | 3380 | 0.759 | 3370 | 0.757 | 1.15 | 1.21 | -0.000744
LFBldgSDGRt3NewCZ06 | Com-Iltg-dWatt-LF_OSbldg | SDG | Rt3 | New | CZ06 | 3.37 | 0.000758 | 0 | 3.8 | 0.000938 | -0.00455 | 3.37 | 0.000758 | 0 | 3.8 | 0.000938 | -0.00455 |  | LF | Bldg | 3370 | 0.758 | 3370 | 0.758 | 1.13 | 1.24 | -0.0013501 | 3370 | 0.758 | 3370 | 0.758 | 1.13 | 1.24 | -0.00135
LFBldgSDGRt3NewCZ07 | Com-Iltg-dWatt-LF_OSbldg | SDG | Rt3 | New | CZ07 | 3.37 | 0.000758 | 0 | 3.79 | 0.00092 | -0.00176 | 3.37 | 0.000758 | 0 | 3.79 | 0.00092 | -0.00176 |  | LF | Bldg | 3370 | 0.758 | 3370 | 0.758 | 1.12 | 1.21 | -0.00052226 | 3370 | 0.758 | 3370 | 0.758 | 1.12 | 1.21 | -0.000522
LFBldgSDGRt3NewCZ08 | Com-Iltg-dWatt-LF_OSbldg | SDG | Rt3 | New | CZ08 | 3.37 | 0.000758 | 0 | 3.84 | 0.000945 | -0.00381 | 3.37 | 0.000758 | 0 | 3.84 | 0.000945 | -0.00381 |  | LF | Bldg | 3370 | 0.758 | 3370 | 0.758 | 1.14 | 1.25 | -0.0011306 | 3370 | 0.758 | 3370 | 0.758 | 1.14 | 1.25 | -0.00113
LFBldgSDGRt3NewCZ10 | Com-Iltg-dWatt-LF_OSbldg | SDG | Rt3 | New | CZ10 | 3.37 | 0.000758 | 0 | 3.79 | 0.000938 | -0.00701 | 3.37 | 0.000758 | 0 | 3.79 | 0.000938 | -0.00701 |  | LF | Bldg | 3370 | 0.758 | 3370 | 0.758 | 1.12 | 1.24 | -0.0020801 | 3370 | 0.758 | 3370 | 0.758 | 1.12 | 1.24 | -0.00208
LFBldgSDGRt3NewCZ14 | Com-Iltg-dWatt-LF_OSbldg | SDG | Rt3 | New | CZ14 | 3.37 | 0.000758 | 0 | 3.74 | 0.000978 | -0.0205 | 3.37 | 0.000758 | 0 | 3.74 | 0.000978 | -0.0205 |  | LF | Bldg | 3370 | 0.758 | 3370 | 0.758 | 1.11 | 1.29 | -0.0060831 | 3370 | 0.758 | 3370 | 0.758 | 1.11 | 1.29 | -0.00608
LFBldgSDGRt3NewCZ15 | Com-Iltg-dWatt-LF_OSbldg | SDG | Rt3 | New | CZ15 | 3.37 | 0.000758 | 0 | 3.79 | 0.000891 | -0.000704 | 3.37 | 0.000758 | 0 | 3.79 | 0.000891 | -0.000704 |  | LF | Bldg | 3370 | 0.758 | 3370 | 0.758 | 1.12 | 1.18 | -0.0002089 | 3370 | 0.758 | 3370 | 0.758 | 1.12 | 1.18 | -0.000209
LFBldgSDGRt3NewIOU | Com-Iltg-dWatt-LF_OSbldg | SDG | Rt3 | New | IOU | 3.37 | 0.000758 | 0 | 3.7933 | 0.00092658 | -0.0032832 | 3.37 | 0.000758 | 0 | 3.7933 | 0.00092658 | -0.0032832 |  | LF | Bldg | 3370 | 0.758 | 3370 | 0.758 | 1.13 | 1.22 | -0.00097425 | 3370 | 0.758 | 3370 | 0.758 | 1.13 | 1.22 | -0.000974
LFBldgSDGRtLExCZ06 | Com-Iltg-dWatt-LF_OSbldg | SDG | RtL | Ex | CZ06 | 4.2693 | 0.00084786 | 0 | 4.8393 | 0.00104 | -0.010193 | 4.26 | 0.00084693 | 0 | 4.83 | 0.00104 | -0.0101 |  | LF | Bldg | 4270 | 0.848 | 4260 | 0.847 | 1.13 | 1.23 | -0.0023709 | 4270 | 0.848 | 4260 | 0.847 | 1.13 | 1.23 | -0.00237
LFBldgSDGRtLExCZ07 | Com-Iltg-dWatt-LF_OSbldg | SDG | RtL | Ex | CZ07 | 4.2693 | 0.00084786 | 0 | 4.8693 | 0.00104 | -0.0074293 | 4.26 | 0.00084693 | 0 | 4.86 | 0.00104 | -0.00742 |  | LF | Bldg | 4270 | 0.848 | 4260 | 0.847 | 1.14 | 1.23 | -0.0017418 | 4270 | 0.848 | 4260 | 0.847 | 1.14 | 1.23 | -0.00174
LFBldgSDGRtLExCZ08 | Com-Iltg-dWatt-LF_OSbldg | SDG | RtL | Ex | CZ08 | 4.2693 | 0.00084786 | 0 | 4.8593 | 0.00104 | -0.0087893 | 4.26 | 0.00084693 | 0 | 4.85 | 0.00104 | -0.00878 |  | LF | Bldg | 4270 | 0.848 | 4260 | 0.847 | 1.14 | 1.23 | -0.002061 | 4270 | 0.848 | 4260 | 0.847 | 1.14 | 1.23 | -0.00206
LFBldgSDGRtLExCZ10 | Com-Iltg-dWatt-LF_OSbldg | SDG | RtL | Ex | CZ10 | 4.2693 | 0.00084786 | 0 | 4.8193 | 0.00106 | -0.0117 | 4.26 | 0.00084693 | 0 | 4.81 | 0.00106 | -0.0117 |  | LF | Bldg | 4270 | 0.848 | 4260 | 0.847 | 1.13 | 1.25 | -0.0027465 | 4270 | 0.848 | 4260 | 0.847 | 1.13 | 1.25 | -0.00275
LFBldgSDGRtLExCZ14 | Com-Iltg-dWatt-LF_OSbldg | SDG | RtL | Ex | CZ14 | 4.2693 | 0.00084803 | 0 | 4.65 | 0.00107 | -0.0247 | 4.26 | 0.00084693 | 0 | 4.6482 | 0.00107 | -0.0247 |  | LF | Bldg | 4270 | 0.848 | 4260 | 0.847 | 1.09 | 1.26 | -0.0057981 | 4270 | 0.848 | 4260 | 0.847 | 1.09 | 1.26 | -0.0058
LFBldgSDGRtLExCZ15 | Com-Iltg-dWatt-LF_OSbldg | SDG | RtL | Ex | CZ15 | 4.2692 | 0.00084785 | 0 | 5.0392 | 0.00108 | -0.00415 | 4.26 | 0.00084693 | 0 | 5.03 | 0.00108 | -0.00415 |  | LF | Bldg | 4270 | 0.848 | 4260 | 0.847 | 1.18 | 1.28 | -0.00097418 | 4270 | 0.848 | 4260 | 0.847 | 1.18 | 1.28 | -0.000974
LFBldgSDGRtLExIOU | Com-Iltg-dWatt-LF_OSbldg | SDG | RtL | Ex | IOU | 4.2693 | 0.00084786 | 0 | 4.8552 | 0.0010449 | -0.0086678 | 4.26 | 0.00084693 | 0 | 4.846 | 0.0010449 | -0.008658 |  | LF | Bldg | 4270 | 0.848 | 4260 | 0.847 | 1.14 | 1.23 | -0.0020324 | 4270 | 0.848 | 4260 | 0.847 | 1.14 | 1.23 | -0.00203
LFBldgSDGRtLNewCZ06 | Com-Iltg-dWatt-LF_OSbldg | SDG | RtL | New | CZ06 | 4.26 | 0.000846 | 0 | 4.72 | 0.00106 | -0.0139 | 4.26 | 0.000846 | 0 | 4.72 | 0.00106 | -0.0139 |  | LF | Bldg | 4260 | 0.846 | 4260 | 0.846 | 1.11 | 1.25 | -0.0032629 | 4260 | 0.846 | 4260 | 0.846 | 1.11 | 1.25 | -0.00326
LFBldgSDGRtLNewCZ07 | Com-Iltg-dWatt-LF_OSbldg | SDG | RtL | New | CZ07 | 4.26 | 0.000846 | 0 | 4.68 | 0.00102 | -0.0101 | 4.26 | 0.000846 | 0 | 4.68 | 0.00102 | -0.0101 |  | LF | Bldg | 4260 | 0.846 | 4260 | 0.846 | 1.1 | 1.21 | -0.0023709 | 4260 | 0.846 | 4260 | 0.846 | 1.1 | 1.21 | -0.00237
LFBldgSDGRtLNewCZ08 | Com-Iltg-dWatt-LF_OSbldg | SDG | RtL | New | CZ08 | 4.26 | 0.000846 | 0 | 4.78 | 0.00108 | -0.0119 | 4.26 | 0.000846 | 0 | 4.78 | 0.00108 | -0.0119 |  | LF | Bldg | 4260 | 0.846 | 4260 | 0.846 | 1.12 | 1.28 | -0.0027934 | 4260 | 0.846 | 4260 | 0.846 | 1.12 | 1.28 | -0.00279
LFBldgSDGRtLNewCZ10 | Com-Iltg-dWatt-LF_OSbldg | SDG | RtL | New | CZ10 | 4.26 | 0.000846 | 0 | 4.82 | 0.00112 | -0.0137 | 4.26 | 0.000846 | 0 | 4.82 | 0.00112 | -0.0137 |  | LF | Bldg | 4260 | 0.846 | 4260 | 0.846 | 1.13 | 1.32 | -0.003216 | 4260 | 0.846 | 4260 | 0.846 | 1.13 | 1.32 | -0.00322
LFBldgSDGRtLNewCZ14 | Com-Iltg-dWatt-LF_OSbldg | SDG | RtL | New | CZ14 | 4.26 | 0.000846 | 0 | 4.71 | 0.00111 | -0.0275 | 4.26 | 0.000846 | 0 | 4.71 | 0.00111 | -0.0275 |  | LF | Bldg | 4260 | 0.846 | 4260 | 0.846 | 1.11 | 1.31 | -0.0064554 | 4260 | 0.846 | 4260 | 0.846 | 1.11 | 1.31 | -0.00646
LFBldgSDGRtLNewCZ15 | Com-Iltg-dWatt-LF_OSbldg | SDG | RtL | New | CZ15 | 4.26 | 0.000846 | 0 | 5.1 | 0.00113 | -0.00413 | 4.26 | 0.000846 | 0 | 5.1 | 0.00113 | -0.00413 |  | LF | Bldg | 4260 | 0.846 | 4260 | 0.846 | 1.2 | 1.34 | -0.00096948 | 4260 | 0.846 | 4260 | 0.846 | 1.2 | 1.34 | -0.000969
LFBldgSDGRtLNewIOU | Com-Iltg-dWatt-LF_OSbldg | SDG | RtL | New | IOU | 4.26 | 0.000846 | 0 | 4.7219 | 0.0010496 | -0.011235 | 4.26 | 0.000846 | 0 | 4.7219 | 0.0010496 | -0.011235 |  | LF | Bldg | 4260 | 0.846 | 4260 | 0.846 | 1.11 | 1.24 | -0.0026373 | 4260 | 0.846 | 4260 | 0.846 | 1.11 | 1.24 | -0.00264
LFBldgSDGRtSExCZ06 | Com-Iltg-dWatt-LF_OSbldg | SDG | RtS | Ex | CZ06 | 3.38 | 0.000875 | 0 | 3.8 | 0.00107 | -0.0053 | 3.38 | 0.000875 | 0 | 3.8 | 0.00107 | -0.0053 |  | LF | Bldg | 3380 | 0.875 | 3380 | 0.875 | 1.12 | 1.22 | -0.001568 | 3380 | 0.875 | 3380 | 0.875 | 1.12 | 1.22 | -0.00157
LFBldgSDGRtSExCZ07 | Com-Iltg-dWatt-LF_OSbldg | SDG | RtS | Ex | CZ07 | 3.38 | 0.000875 | 0 | 3.81 | 0.00105 | -0.00315 | 3.38 | 0.000875 | 0 | 3.81 | 0.00105 | -0.00315 |  | LF | Bldg | 3380 | 0.875 | 3380 | 0.875 | 1.13 | 1.2 | -0.00093195 | 3380 | 0.875 | 3380 | 0.875 | 1.13 | 1.2 | -0.000932
LFBldgSDGRtSExCZ08 | Com-Iltg-dWatt-LF_OSbldg | SDG | RtS | Ex | CZ08 | 3.38 | 0.000875 | 0 | 3.83 | 0.00107 | -0.00449 | 3.38 | 0.000875 | 0 | 3.83 | 0.00107 | -0.00449 |  | LF | Bldg | 3380 | 0.875 | 3380 | 0.875 | 1.13 | 1.22 | -0.0013284 | 3380 | 0.875 | 3380 | 0.875 | 1.13 | 1.22 | -0.00133
LFBldgSDGRtSExCZ10 | Com-Iltg-dWatt-LF_OSbldg | SDG | RtS | Ex | CZ10 | 3.38 | 0.000875 | 0 | 3.81 | 0.00108 | -0.00661 | 3.38 | 0.000875 | 0 | 3.81 | 0.00108 | -0.00661 |  | LF | Bldg | 3380 | 0.875 | 3380 | 0.875 | 1.13 | 1.23 | -0.0019556 | 3380 | 0.875 | 3380 | 0.875 | 1.13 | 1.23 | -0.00196
LFBldgSDGRtSExCZ14 | Com-Iltg-dWatt-LF_OSbldg | SDG | RtS | Ex | CZ14 | 3.38 | 0.000875 | 0 | 3.69 | 0.00107 | -0.0166 | 3.38 | 0.000875 | 0 | 3.69 | 0.00107 | -0.0166 |  | LF | Bldg | 3380 | 0.875 | 3380 | 0.875 | 1.09 | 1.22 | -0.0049112 | 3380 | 0.875 | 3380 | 0.875 | 1.09 | 1.22 | -0.00491
LFBldgSDGRtSExCZ15 | Com-Iltg-dWatt-LF_OSbldg | SDG | RtS | Ex | CZ15 | 3.38 | 0.000875 | 0 | 4 | 0.00109 | -0.00142 | 3.38 | 0.000875 | 0 | 4 | 0.00109 | -0.00142 |  | LF | Bldg | 3380 | 0.875 | 3380 | 0.875 | 1.18 | 1.25 | -0.00042012 | 3380 | 0.875 | 3380 | 0.875 | 1.18 | 1.25 | -0.00042
LFBldgSDGRtSExIOU | Com-Iltg-dWatt-LF_OSbldg | SDG | RtS | Ex | IOU | 3.38 | 0.000875 | 0 | 3.8108 | 0.0010593 | -0.0041647 | 3.38 | 0.000875 | 0 | 3.8108 | 0.0010593 | -0.0041647 |  | LF | Bldg | 3380 | 0.875 | 3380 | 0.875 | 1.13 | 1.21 | -0.0012321 | 3380 | 0.875 | 3380 | 0.875 | 1.13 | 1.21 | -0.00123
LFBldgSDGRtSNewCZ06 | Com-Iltg-dWatt-LF_OSbldg | SDG | RtS | New | CZ06 | 3.38 | 0.000875 | 0 | 3.74 | 0.00106 | -0.00699 | 3.38 | 0.000875 | 0 | 3.74 | 0.00106 | -0.00699 |  | LF | Bldg | 3380 | 0.875 | 3380 | 0.875 | 1.11 | 1.21 | -0.002068 | 3380 | 0.875 | 3380 | 0.875 | 1.11 | 1.21 | -0.00207
LFBldgSDGRtSNewCZ07 | Com-Iltg-dWatt-LF_OSbldg | SDG | RtS | New | CZ07 | 3.38 | 0.000875 | 0 | 3.71 | 0.00105 | -0.00412 | 3.38 | 0.000875 | 0 | 3.71 | 0.00105 | -0.00412 |  | LF | Bldg | 3380 | 0.875 | 3380 | 0.875 | 1.1 | 1.2 | -0.0012189 | 3380 | 0.875 | 3380 | 0.875 | 1.1 | 1.2 | -0.00122
LFBldgSDGRtSNewCZ08 | Com-Iltg-dWatt-LF_OSbldg | SDG | RtS | New | CZ08 | 3.38 | 0.000875 | 0 | 3.77 | 0.00107 | -0.00584 | 3.38 | 0.000875 | 0 | 3.77 | 0.00107 | -0.00584 |  | LF | Bldg | 3380 | 0.875 | 3380 | 0.875 | 1.12 | 1.22 | -0.0017278 | 3380 | 0.875 | 3380 | 0.875 | 1.12 | 1.22 | -0.00173
LFBldgSDGRtSNewCZ10 | Com-Iltg-dWatt-LF_OSbldg | SDG | RtS | New | CZ10 | 3.38 | 0.000875 | 0 | 3.81 | 0.00111 | -0.00729 | 3.38 | 0.000875 | 0 | 3.81 | 0.00111 | -0.00729 |  | LF | Bldg | 3380 | 0.875 | 3380 | 0.875 | 1.13 | 1.27 | -0.0021568 | 3380 | 0.875 | 3380 | 0.875 | 1.13 | 1.27 | -0.00216
LFBldgSDGRtSNewCZ14 | Com-Iltg-dWatt-LF_OSbldg | SDG | RtS | New | CZ14 | 3.38 | 0.000875 | 0 | 3.72 | 0.00109 | -0.0177 | 3.38 | 0.000875 | 0 | 3.72 | 0.00109 | -0.0177 |  | LF | Bldg | 3380 | 0.875 | 3380 | 0.875 | 1.1 | 1.25 | -0.0052367 | 3380 | 0.875 | 3380 | 0.875 | 1.1 | 1.25 | -0.00524
LFBldgSDGRtSNewCZ15 | Com-Iltg-dWatt-LF_OSbldg | SDG | RtS | New | CZ15 | 3.38 | 0.000875 | 0 | 3.98 | 0.00112 | -0.00125 | 3.38 | 0.000875 | 0 | 3.98 | 0.00112 | -0.00125 |  | LF | Bldg | 3380 | 0.875 | 3380 | 0.875 | 1.18 | 1.28 | -0.00036982 | 3380 | 0.875 | 3380 | 0.875 | 1.18 | 1.28 | -0.00037
LFBldgSDGRtSNewIOU | Com-Iltg-dWatt-LF_OSbldg | SDG | RtS | New | IOU | 3.38 | 0.000875 | 0 | 3.7393 | 0.0010663 | -0.0051104 | 3.38 | 0.000875 | 0 | 3.7393 | 0.0010663 | -0.0051104 |  | LF | Bldg | 3380 | 0.875 | 3380 | 0.875 | 1.11 | 1.22 | -0.001512 | 3380 | 0.875 | 3380 | 0.875 | 1.11 | 1.22 | -0.00151
LFBldgSDGSCnExCZ06 | Com-Iltg-dWatt-LF_OSbldg | SDG | SCn | Ex | CZ06 | 3.418 | 0.00069914 | 0 | 3.5073 | 0.0009078 | -0.018987 | 3.39 | 0.000687 | 0 | 3.47 | 0.000891 | -0.0188 |  | LF | Bldg | 3420 | 0.699 | 3390 | 0.687 | 1.02 | 1.3 | -0.0055457 | 3420 | 0.699 | 3390 | 0.687 | 1.02 | 1.3 | -0.00555
LFBldgSDGSCnExCZ07 | Com-Iltg-dWatt-LF_OSbldg | SDG | SCn | Ex | CZ07 | 3.418 | 0.00069914 | 0 | 3.4473 | 0.0009138 | -0.015587 | 3.39 | 0.000687 | 0 | 3.41 | 0.000897 | -0.0154 |  | LF | Bldg | 3420 | 0.699 | 3390 | 0.687 | 1.01 | 1.31 | -0.0045428 | 3420 | 0.699 | 3390 | 0.687 | 1.01 | 1.31 | -0.00454
LFBldgSDGSCnExCZ08 | Com-Iltg-dWatt-LF_OSbldg | SDG | SCn | Ex | CZ08 | 3.418 | 0.00069913 | 0 | 3.5573 | 0.00090587 | -0.016193 | 3.39 | 0.000687 | 0 | 3.52 | 0.00089 | -0.0161 |  | LF | Bldg | 3420 | 0.699 | 3390 | 0.687 | 1.04 | 1.3 | -0.0047493 | 3420 | 0.699 | 3390 | 0.687 | 1.04 | 1.3 | -0.00475
LFBldgSDGSCnExCZ10 | Com-Iltg-dWatt-LF_OSbldg | SDG | SCn | Ex | CZ10 | 3.418 | 0.00069914 | 0 | 3.5673 | 0.00091781 | -0.019987 | 3.39 | 0.000687 | 0 | 3.53 | 0.000901 | -0.0198 |  | LF | Bldg | 3420 | 0.699 | 3390 | 0.687 | 1.04 | 1.31 | -0.0058407 | 3420 | 0.699 | 3390 | 0.687 | 1.04 | 1.31 | -0.00584
LFBldgSDGSCnExCZ14 | Com-Iltg-dWatt-LF_OSbldg | SDG | SCn | Ex | CZ14 | 3.418 | 0.00069914 | 0 | 3.458 | 0.00090187 | -0.02928 | 3.39 | 0.000687 | 0 | 3.43 | 0.000886 | -0.029 |  | LF | Bldg | 3420 | 0.699 | 3390 | 0.687 | 1.01 | 1.29 | -0.0085546 | 3420 | 0.699 | 3390 | 0.687 | 1.01 | 1.29 | -0.00855
LFBldgSDGSCnExCZ15 | Com-Iltg-dWatt-LF_OSbldg | SDG | SCn | Ex | CZ15 | 3.418 | 0.00069914 | 0 | 3.8174 | 0.00090188 | -0.0085447 | 3.39 | 0.000687 | 0 | 3.78 | 0.000886 | -0.00847 |  | LF | Bldg | 3420 | 0.699 | 3390 | 0.687 | 1.12 | 1.29 | -0.0024985 | 3420 | 0.699 | 3390 | 0.687 | 1.12 | 1.29 | -0.0025
LFBldgSDGSCnExIOU | Com-Iltg-dWatt-LF_OSbldg | SDG | SCn | Ex | IOU | 3.418 | 0.00069914 | 0 | 3.487 | 0.00091468 | -0.017029 | 3.39 | 0.000687 | 0 | 3.4497 | 0.00089789 | -0.016844 |  | LF | Bldg | 3420 | 0.699 | 3390 | 0.687 | 1.02 | 1.31 | -0.0049686 | 3420 | 0.699 | 3390 | 0.687 | 1.02 | 1.31 | -0.00497
LFBldgSDGSCnNewCZ06 | Com-Iltg-dWatt-LF_OSbldg | SDG | SCn | New | CZ06 | 3.39 | 0.000687 | 0 | 3.38 | 0.000827 | -0.0201 | 3.39 | 0.000687 | 0 | 3.38 | 0.000827 | -0.0201 |  | LF | Bldg | 3390 | 0.687 | 3390 | 0.687 | 0.997 | 1.2 | -0.0059292 | 3390 | 0.687 | 3390 | 0.687 | 0.997 | 1.2 | -0.00593
LFBldgSDGSCnNewCZ07 | Com-Iltg-dWatt-LF_OSbldg | SDG | SCn | New | CZ07 | 3.39 | 0.000687 | 0 | 3.38 | 0.000845 | -0.0168 | 3.39 | 0.000687 | 0 | 3.38 | 0.000845 | -0.0168 |  | LF | Bldg | 3390 | 0.687 | 3390 | 0.687 | 0.997 | 1.23 | -0.0049558 | 3390 | 0.687 | 3390 | 0.687 | 0.997 | 1.23 | -0.00496
LFBldgSDGSCnNewCZ08 | Com-Iltg-dWatt-LF_OSbldg | SDG | SCn | New | CZ08 | 3.39 | 0.000687 | 0 | 3.46 | 0.000839 | -0.0176 | 3.39 | 0.000687 | 0 | 3.46 | 0.000839 | -0.0176 |  | LF | Bldg | 3390 | 0.687 | 3390 | 0.687 | 1.02 | 1.22 | -0.0051917 | 3390 | 0.687 | 3390 | 0.687 | 1.02 | 1.22 | -0.00519
LFBldgSDGSCnNewCZ10 | Com-Iltg-dWatt-LF_OSbldg | SDG | SCn | New | CZ10 | 3.39 | 0.000687 | 0 | 3.47 | 0.00086 | -0.0205 | 3.39 | 0.000687 | 0 | 3.47 | 0.00086 | -0.0205 |  | LF | Bldg | 3390 | 0.687 | 3390 | 0.687 | 1.02 | 1.25 | -0.0060472 | 3390 | 0.687 | 3390 | 0.687 | 1.02 | 1.25 | -0.00605
LFBldgSDGSCnNewCZ14 | Com-Iltg-dWatt-LF_OSbldg | SDG | SCn | New | CZ14 | 3.39 | 0.000687 | 0 | 3.4 | 0.000857 | -0.03 | 3.39 | 0.000687 | 0 | 3.4 | 0.000857 | -0.03 |  | LF | Bldg | 3390 | 0.687 | 3390 | 0.687 | 1 | 1.25 | -0.0088496 | 3390 | 0.687 | 3390 | 0.687 | 1 | 1.25 | -0.00885
LFBldgSDGSCnNewCZ15 | Com-Iltg-dWatt-LF_OSbldg | SDG | SCn | New | CZ15 | 3.39 | 0.000687 | 0 | 3.69 | 0.000864 | -0.0064 | 3.39 | 0.000687 | 0 | 3.69 | 0.000864 | -0.0064 |  | LF | Bldg | 3390 | 0.687 | 3390 | 0.687 | 1.09 | 1.26 | -0.0018879 | 3390 | 0.687 | 3390 | 0.687 | 1.09 | 1.26 | -0.00189
LFBldgSDGSCnNewIOU | Com-Iltg-dWatt-LF_OSbldg | SDG | SCn | New | IOU | 3.39 | 0.000687 | 0 | 3.4087 | 0.00084901 | -0.018027 | 3.39 | 0.000687 | 0 | 3.4087 | 0.00084901 | -0.018027 |  | LF | Bldg | 3390 | 0.687 | 3390 | 0.687 | 1.01 | 1.24 | -0.0053178 | 3390 | 0.687 | 3390 | 0.687 | 1.01 | 1.24 | -0.00532
LFBldgSDGSUnExCZ06 | Com-Iltg-dWatt-LF_OSbldg | SDG | SUn | Ex | CZ06 | 3.418 | 0.00069914 | 0 | 3.418 | 0.00069914 | 0 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 |  | LF | Bldg | 3420 | 0.699 | 3390 | 0.687 | 1 | 1 | 0 | 3420 | 0.699 | 3390 | 0.687 | 1 | 1 | 0
LFBldgSDGSUnExCZ07 | Com-Iltg-dWatt-LF_OSbldg | SDG | SUn | Ex | CZ07 | 3.418 | 0.00069914 | 0 | 3.418 | 0.00069914 | 0 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 |  | LF | Bldg | 3420 | 0.699 | 3390 | 0.687 | 1 | 1 | 0 | 3420 | 0.699 | 3390 | 0.687 | 1 | 1 | 0
LFBldgSDGSUnExCZ08 | Com-Iltg-dWatt-LF_OSbldg | SDG | SUn | Ex | CZ08 | 3.418 | 0.00069913 | 0 | 3.418 | 0.00069913 | 0 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 |  | LF | Bldg | 3420 | 0.699 | 3390 | 0.687 | 1 | 1 | 0 | 3420 | 0.699 | 3390 | 0.687 | 1 | 1 | 0
LFBldgSDGSUnExCZ10 | Com-Iltg-dWatt-LF_OSbldg | SDG | SUn | Ex | CZ10 | 3.418 | 0.00069914 | 0 | 3.418 | 0.00069914 | 0 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 |  | LF | Bldg | 3420 | 0.699 | 3390 | 0.687 | 1 | 1 | 0 | 3420 | 0.699 | 3390 | 0.687 | 1 | 1 | 0
LFBldgSDGSUnExCZ14 | Com-Iltg-dWatt-LF_OSbldg | SDG | SUn | Ex | CZ14 | 3.418 | 0.00069914 | 0 | 3.418 | 0.00069914 | 0 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 |  | LF | Bldg | 3420 | 0.699 | 3390 | 0.687 | 1 | 1 | 0 | 3420 | 0.699 | 3390 | 0.687 | 1 | 1 | 0
LFBldgSDGSUnExCZ15 | Com-Iltg-dWatt-LF_OSbldg | SDG | SUn | Ex | CZ15 | 3.418 | 0.00069914 | 0 | 3.418 | 0.00069914 | 0 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 |  | LF | Bldg | 3420 | 0.699 | 3390 | 0.687 | 1 | 1 | 0 | 3420 | 0.699 | 3390 | 0.687 | 1 | 1 | 0
LFBldgSDGSUnExIOU | Com-Iltg-dWatt-LF_OSbldg | SDG | SUn | Ex | IOU | 3.418 | 0.00069914 | 0 | 3.418 | 0.00069914 | 0 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 |  | LF | Bldg | 3420 | 0.699 | 3390 | 0.687 | 1 | 1 | 0 | 3420 | 0.699 | 3390 | 0.687 | 1 | 1 | 0
LFBldgSDGSUnNewCZ06 | Com-Iltg-dWatt-LF_OSbldg | SDG | SUn | New | CZ06 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 |  | LF | Bldg | 3390 | 0.687 | 3390 | 0.687 | 1 | 1 | 0 | 3390 | 0.687 | 3390 | 0.687 | 1 | 1 | 0
LFBldgSDGSUnNewCZ07 | Com-Iltg-dWatt-LF_OSbldg | SDG | SUn | New | CZ07 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 |  | LF | Bldg | 3390 | 0.687 | 3390 | 0.687 | 1 | 1 | 0 | 3390 | 0.687 | 3390 | 0.687 | 1 | 1 | 0
LFBldgSDGSUnNewCZ08 | Com-Iltg-dWatt-LF_OSbldg | SDG | SUn | New | CZ08 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 |  | LF | Bldg | 3390 | 0.687 | 3390 | 0.687 | 1 | 1 | 0 | 3390 | 0.687 | 3390 | 0.687 | 1 | 1 | 0
LFBldgSDGSUnNewCZ10 | Com-Iltg-dWatt-LF_OSbldg | SDG | SUn | New | CZ10 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 |  | LF | Bldg | 3390 | 0.687 | 3390 | 0.687 | 1 | 1 | 0 | 3390 | 0.687 | 3390 | 0.687 | 1 | 1 | 0
LFBldgSDGSUnNewCZ14 | Com-Iltg-dWatt-LF_OSbldg | SDG | SUn | New | CZ14 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 |  | LF | Bldg | 3390 | 0.687 | 3390 | 0.687 | 1 | 1 | 0 | 3390 | 0.687 | 3390 | 0.687 | 1 | 1 | 0
LFBldgSDGSUnNewCZ15 | Com-Iltg-dWatt-LF_OSbldg | SDG | SUn | New | CZ15 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 |  | LF | Bldg | 3390 | 0.687 | 3390 | 0.687 | 1 | 1 | 0 | 3390 | 0.687 | 3390 | 0.687 | 1 | 1 | 0
LFBldgSDGSUnNewIOU | Com-Iltg-dWatt-LF_OSbldg | SDG | SUn | New | IOU | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 | 3.39 | 0.000687 | 0 |  | LF | Bldg | 3390 | 0.687 | 3390 | 0.687 | 1 | 1 | 0 | 3390 | 0.687 | 3390 | 0.687 | 1 | 1 | 0
LFBldgSDGWRfExCZ06 | Com-Iltg-dWatt-LF_OSbldg | SDG | WRf | Ex | CZ06 | 4.7517 | 0.000555 | 0 | 7.6208 | 0.00069575 | 0 | 4.5408 | 0.000544 | 0 | 7.3 | 0.00068108 | 0 |  | LF | Bldg | 4750 | 0.555 | 4540 | 0.544 | 1.61 | 1.25 | 0 | 4750 | 0.555 | 4540 | 0.544 | 1.61 | 1.25 | 0
LFBldgSDGWRfExCZ07 | Com-Iltg-dWatt-LF_OSbldg | SDG | WRf | Ex | CZ07 | 4.7522 | 0.00055503 | 0 | 7.6716 | 0.00069578 | 0 | 4.5408 | 0.000544 | 0 | 7.3408 | 0.00068108 | 0 |  | LF | Bldg | 4750 | 0.555 | 4540 | 0.544 | 1.62 | 1.25 | 0 | 4750 | 0.555 | 4540 | 0.544 | 1.62 | 1.25 | 0
LFBldgSDGWRfExCZ10 | Com-Iltg-dWatt-LF_OSbldg | SDG | WRf | Ex | CZ10 | 4.7521 | 0.00055503 | 0 | 7.5324 | 0.00070178 | 0 | 4.5408 | 0.000544 | 0 | 7.2108 | 0.00068708 | 0 |  | LF | Bldg | 4750 | 0.555 | 4540 | 0.544 | 1.59 | 1.26 | 0 | 4750 | 0.555 | 4540 | 0.544 | 1.59 | 1.26 | 0
LFBldgSDGWRfExIOU | Com-Iltg-dWatt-LF_OSbldg | SDG | WRf | Ex | IOU | 4.7522 | 0.00055503 | 0 | 7.6406 | 0.0006971 | 0 | 4.5408 | 0.000544 | 0 | 7.3119 | 0.0006824 | 0 |  | LF | Bldg | 4750 | 0.555 | 4540 | 0.544 | 1.61 | 1.25 | 0 | 4750 | 0.555 | 4540 | 0.544 | 1.61 | 1.25 | 0
LFBldgSDGWRfNewCZ06 | Com-Iltg-dWatt-LF_OSbldg | SDG | WRf | New | CZ06 | 4.55 | 0.000544 | 0 | 6.55 | 0.000671 | 0 | 4.55 | 0.000544 | 0 | 6.55 | 0.000671 | 0 |  | LF | Bldg | 4550 | 0.544 | 4550 | 0.544 | 1.44 | 1.23 | 0 | 4550 | 0.544 | 4550 | 0.544 | 1.44 | 1.23 | 0
LFBldgSDGWRfNewCZ07 | Com-Iltg-dWatt-LF_OSbldg | SDG | WRf | New | CZ07 | 4.55 | 0.000544 | 0 | 6.5 | 0.000671 | 0 | 4.55 | 0.000544 | 0 | 6.5 | 0.000671 | 0 |  | LF | Bldg | 4550 | 0.544 | 4550 | 0.544 | 1.43 | 1.23 | 0 | 4550 | 0.544 | 4550 | 0.544 | 1.43 | 1.23 | 0
LFBldgSDGWRfNewCZ08 | Com-Iltg-dWatt-LF_OSbldg | SDG | WRf | New | CZ08 | 4.55 | 0.000544 | 0 | 6.48 | 0.000673 | 0 | 4.55 | 0.000544 | 0 | 6.48 | 0.000673 | 0 |  | LF | Bldg | 4550 | 0.544 | 4550 | 0.544 | 1.42 | 1.24 | 0 | 4550 | 0.544 | 4550 | 0.544 | 1.42 | 1.24 | 0
LFBldgSDGWRfNewCZ10 | Com-Iltg-dWatt-LF_OSbldg | SDG | WRf | New | CZ10 | 4.55 | 0.000544 | 0 | 6.39 | 0.000681 | 0 | 4.55 | 0.000544 | 0 | 6.39 | 0.000681 | 0 |  | LF | Bldg | 4550 | 0.544 | 4550 | 0.544 | 1.4 | 1.25 | 0 | 4550 | 0.544 | 4550 | 0.544 | 1.4 | 1.25 | 0
LFBldgSDGWRfNewCZ14 | Com-Iltg-dWatt-LF_OSbldg | SDG | WRf | New | CZ14 | 4.55 | 0.000544 | 0 | 6.26 | 0.000675 | 0 | 4.55 | 0.000544 | 0 | 6.26 | 0.000675 | 0 |  | LF | Bldg | 4550 | 0.544 | 4550 | 0.544 | 1.38 | 1.24 | 0 | 4550 | 0.544 | 4550 | 0.544 | 1.38 | 1.24 | 0
LFBldgSDGWRfNewCZ15 | Com-Iltg-dWatt-LF_OSbldg | SDG | WRf | New | CZ15 | 4.55 | 0.000544 | 0 | 6.69 | 0.00068 | 0 | 4.55 | 0.000544 | 0 | 6.69 | 0.00068 | 0 |  | LF | Bldg | 4550 | 0.544 | 4550 | 0.544 | 1.47 | 1.25 | 0 | 4550 | 0.544 | 4550 | 0.544 | 1.47 | 1.25 | 0
LFBldgSDGWRfNewIOU | Com-Iltg-dWatt-LF_OSbldg | SDG | WRf | New | IOU | 4.55 | 0.000544 | 0 | 6.4764 | 0.00067319 | 0 | 4.55 | 0.000544 | 0 | 6.4764 | 0.00067319 | 0 |  | LF | Bldg | 4550 | 0.544 | 4550 | 0.544 | 1.42 | 1.24 | 0 | 4550 | 0.544 | 4550 | 0.544 | 1.42 | 1.24 | 0
LFNonePGEAsmExCZ01 | Com-Iltg-dWatt-LF_OSnone | PGE | Asm | Ex | CZ01 | 2.6115 | 0.000532 | 0 | 2.4815 | 0.000608 | -0.05013 | 2.6115 | 0.000532 | 0 | 2.4815 | 0.000608 | -0.05013 |  | LF | None | 2610 | 0.532 | 2610 | 0.532 | 0.95 | 1.14 | -0.019196 | 2610 | 0.532 | 2610 | 0.532 | 0.95 | 1.14 | -0.0192
LFNonePGEAsmExCZ02 | Com-Iltg-dWatt-LF_OSnone | PGE | Asm | Ex | CZ02 | 2.6103 | 0.000532 | 0 | 2.7003 | 0.00062 | -0.028203 | 2.6103 | 0.000532 | 0 | 2.7003 | 0.00062 | -0.028203 |  | LF | None | 2610 | 0.532 | 2610 | 0.532 | 1.03 | 1.17 | -0.010805 | 2610 | 0.532 | 2610 | 0.532 | 1.03 | 1.17 | -0.0108
LFNonePGEAsmExCZ03 | Com-Iltg-dWatt-LF_OSnone | PGE | Asm | Ex | CZ03 | 2.6102 | 0.000532 | 0 | 2.6702 | 0.000621 | -0.031102 | 2.6102 | 0.000532 | 0 | 2.6702 | 0.000621 | -0.031102 |  | LF | None | 2610 | 0.532 | 2610 | 0.532 | 1.02 | 1.17 | -0.011916 | 2610 | 0.532 | 2610 | 0.532 | 1.02 | 1.17 | -0.0119
LFNonePGEAsmExCZ04 | Com-Iltg-dWatt-LF_OSnone | PGE | Asm | Ex | CZ04 | 2.6103 | 0.000532 | 0 | 2.7403 | 0.000619 | -0.023203 | 2.6103 | 0.000532 | 0 | 2.7403 | 0.000619 | -0.023203 |  | LF | None | 2610 | 0.532 | 2610 | 0.532 | 1.05 | 1.16 | -0.008889 | 2610 | 0.532 | 2610 | 0.532 | 1.05 | 1.16 | -0.00889
LFNonePGEAsmExCZ05 | Com-Iltg-dWatt-LF_OSnone | PGE | Asm | Ex | CZ05 | 2.61 | 0.000532 | 0 | 2.69 | 0.00061 | -0.0279 | 2.61 | 0.000532 | 0 | 2.69 | 0.00061 | -0.0279 |  | LF | None | 2610 | 0.532 | 2610 | 0.532 | 1.03 | 1.15 | -0.01069 | 2610 | 0.532 | 2610 | 0.532 | 1.03 | 1.15 | -0.0107
LFNonePGEAsmExCZ11 | Com-Iltg-dWatt-LF_OSnone | PGE | Asm | Ex | CZ11 | 2.61 | 0.000532 | 0 | 2.74 | 0.000619 | -0.0244 | 2.61 | 0.000532 | 0 | 2.74 | 0.000619 | -0.0244 |  | LF | None | 2610 | 0.532 | 2610 | 0.532 | 1.05 | 1.16 | -0.0093487 | 2610 | 0.532 | 2610 | 0.532 | 1.05 | 1.16 | -0.00935
LFNonePGEAsmExCZ12 | Com-Iltg-dWatt-LF_OSnone | PGE | Asm | Ex | CZ12 | 2.6127 | 0.000532 | 0 | 2.7227 | 0.000624 | -0.025827 | 2.6127 | 0.000532 | 0 | 2.7227 | 0.000624 | -0.025827 |  | LF | None | 2610 | 0.532 | 2610 | 0.532 | 1.04 | 1.17 | -0.0098852 | 2610 | 0.532 | 2610 | 0.532 | 1.04 | 1.17 | -0.00989
LFNonePGEAsmExCZ13 | Com-Iltg-dWatt-LF_OSnone | PGE | Asm | Ex | CZ13 | 2.6126 | 0.000532 | 0 | 2.7426 | 0.000618 | -0.023726 | 2.6126 | 0.000532 | 0 | 2.7426 | 0.000618 | -0.023726 |  | LF | None | 2610 | 0.532 | 2610 | 0.532 | 1.05 | 1.16 | -0.0090814 | 2610 | 0.532 | 2610 | 0.532 | 1.05 | 1.16 | -0.00908
LFNonePGEAsmExCZ16 | Com-Iltg-dWatt-LF_OSnone | PGE | Asm | Ex | CZ16 | 2.6124 | 0.000532 | 0 | 2.5524 | 0.00061 | -0.037347 | 2.6124 | 0.000532 | 0 | 2.5524 | 0.00061 | -0.037347 |  | LF | None | 2610 | 0.532 | 2610 | 0.532 | 0.977 | 1.15 | -0.014296 | 2610 | 0.532 | 2610 | 0.532 | 0.977 | 1.15 | -0.0143
LFNonePGEAsmExIOU | Com-Iltg-dWatt-LF_OSnone | PGE | Asm | Ex | IOU | 2.611 | 0.000532 | 0 | 2.7053 | 0.00062023 | -0.027341 | 2.611 | 0.000532 | 0 | 2.7053 | 0.00062023 | -0.027341 |  | LF | None | 2610 | 0.532 | 2610 | 0.532 | 1.04 | 1.17 | -0.010471 | 2610 | 0.532 | 2610 | 0.532 | 1.04 | 1.17 | -0.0105
LFNonePGEAsmNewCZ01 | Com-Iltg-dWatt-LF_OSnone | PGE | Asm | New | CZ01 | 2.61 | 0.000532 | 0 | 2.49 | 0.000612 | -0.0496 | 2.61 | 0.000532 | 0 | 2.49 | 0.000612 | -0.0496 |  | LF | None | 2610 | 0.532 | 2610 | 0.532 | 0.954 | 1.15 | -0.019004 | 2610 | 0.532 | 2610 | 0.532 | 0.954 | 1.15 | -0.019
LFNonePGEAsmNewCZ02 | Com-Iltg-dWatt-LF_OSnone | PGE | Asm | New | CZ02 | 2.61 | 0.000532 | 0 | 2.66 | 0.000624 | -0.0308 | 2.61 | 0.000532 | 0 | 2.66 | 0.000624 | -0.0308 |  | LF | None | 2610 | 0.532 | 2610 | 0.532 | 1.02 | 1.17 | -0.011801 | 2610 | 0.532 | 2610 | 0.532 | 1.02 | 1.17 | -0.0118
LFNonePGEAsmNewCZ03 | Com-Iltg-dWatt-LF_OSnone | PGE | Asm | New | CZ03 | 2.61 | 0.000532 | 0 | 2.64 | 0.000614 | -0.0326 | 2.61 | 0.000532 | 0 | 2.64 | 0.000614 | -0.0326 |  | LF | None | 2610 | 0.532 | 2610 | 0.532 | 1.01 | 1.15 | -0.01249 | 2610 | 0.532 | 2610 | 0.532 | 1.01 | 1.15 | -0.0125
LFNonePGEAsmNewCZ04 | Com-Iltg-dWatt-LF_OSnone | PGE | Asm | New | CZ04 | 2.61 | 0.000532 | 0 | 2.7 | 0.00062 | -0.0255 | 2.61 | 0.000532 | 0 | 2.7 | 0.00062 | -0.0255 |  | LF | None | 2610 | 0.532 | 2610 | 0.532 | 1.03 | 1.17 | -0.0097701 | 2610 | 0.532 | 2610 | 0.532 | 1.03 | 1.17 | -0.00977
LFNonePGEAsmNewCZ05 | Com-Iltg-dWatt-LF_OSnone | PGE | Asm | New | CZ05 | 2.61 | 0.000532 | 0 | 2.66 | 0.000607 | -0.0284 | 2.61 | 0.000532 | 0 | 2.66 | 0.000607 | -0.0284 |  | LF | None | 2610 | 0.532 | 2610 | 0.532 | 1.02 | 1.14 | -0.010881 | 2610 | 0.532 | 2610 | 0.532 | 1.02 | 1.14 | -0.0109
LFNonePGEAsmNewCZ11 | Com-Iltg-dWatt-LF_OSnone | PGE | Asm | New | CZ11 | 2.61 | 0.000532 | 0 | 2.72 | 0.000631 | -0.0264 | 2.61 | 0.000532 | 0 | 2.72 | 0.000631 | -0.0264 |  | LF | None | 2610 | 0.532 | 2610 | 0.532 | 1.04 | 1.19 | -0.010115 | 2610 | 0.532 | 2610 | 0.532 | 1.04 | 1.19 | -0.0101
LFNonePGEAsmNewCZ12 | Com-Iltg-dWatt-LF_OSnone | PGE | Asm | New | CZ12 | 2.61 | 0.000532 | 0 | 2.71 | 0.00063 | -0.0282 | 2.61 | 0.000532 | 0 | 2.71 | 0.00063 | -0.0282 |  | LF | None | 2610 | 0.532 | 2610 | 0.532 | 1.04 | 1.18 | -0.010805 | 2610 | 0.532 | 2610 | 0.532 | 1.04 | 1.18 | -0.0108
LFNonePGEAsmNewCZ13 | Com-Iltg-dWatt-LF_OSnone | PGE | Asm | New | CZ13 | 2.61 | 0.000532 | 0 | 2.73 | 0.00063 | -0.0256 | 2.61 | 0.000532 | 0 | 2.73 | 0.00063 | -0.0256 |  | LF | None | 2610 | 0.532 | 2610 | 0.532 | 1.05 | 1.18 | -0.0098084 | 2610 | 0.532 | 2610 | 0.532 | 1.05 | 1.18 | -0.00981
LFNonePGEAsmNewCZ16 | Com-Iltg-dWatt-LF_OSnone | PGE | Asm | New | CZ16 | 2.61 | 0.000532 | 0 | 2.56 | 0.000611 | -0.0376 | 2.61 | 0.000532 | 0 | 2.56 | 0.000611 | -0.0376 |  | LF | None | 2610 | 0.532 | 2610 | 0.532 | 0.981 | 1.15 | -0.014406 | 2610 | 0.532 | 2610 | 0.532 | 0.981 | 1.15 | -0.0144
LFNonePGEAsmNewIOU | Com-Iltg-dWatt-LF_OSnone | PGE | Asm | New | IOU | 2.61 | 0.000532 | 0 | 2.6879 | 0.00062324 | -0.028635 | 2.61 | 0.000532 | 0 | 2.6879 | 0.00062324 | -0.028635 |  | LF | None | 2610 | 0.532 | 2610 | 0.532 | 1.03 | 1.17 | -0.010971 | 2610 | 0.532 | 2610 | 0.532 | 1.03 | 1.17 | -0.011
LFNonePGEComExCZ01 | Com-Iltg-dWatt-LF_OSnone | PGE | Com | Ex | CZ01 | 3.126 | 0.00070525 | 0 | 3.0675 | 0.00081674 | -0.038454 | 3.126 | 0.00070525 | 0 | 3.0675 | 0.00081674 | -0.038454 |  | LF | None | 3130 | 0.705 | 3130 | 0.705 | 0.981 | 1.16 | -0.012301 | 3130 | 0.705 | 3130 | 0.705 | 0.981 | 1.16 | -0.0123
LFNonePGEComExCZ02 | Com-Iltg-dWatt-LF_OSnone | PGE | Com | Ex | CZ02 | 3.2425 | 0.00063394 | 0 | 3.3896 | 0.00076697 | -0.024469 | 3.2425 | 0.00063394 | 0 | 3.3896 | 0.00076697 | -0.024469 |  | LF | None | 3240 | 0.634 | 3240 | 0.634 | 1.05 | 1.21 | -0.0075464 | 3240 | 0.634 | 3240 | 0.634 | 1.05 | 1.21 | -0.00755
LFNonePGEComExCZ03 | Com-Iltg-dWatt-LF_OSnone | PGE | Com | Ex | CZ03 | 3.1 | 0.00064467 | 0 | 3.2661 | 0.0007808 | -0.021769 | 3.1 | 0.00064467 | 0 | 3.2661 | 0.0007808 | -0.021769 |  | LF | None | 3100 | 0.645 | 3100 | 0.645 | 1.05 | 1.21 | -0.0070223 | 3100 | 0.645 | 3100 | 0.645 | 1.05 | 1.21 | -0.00702
LFNonePGEComExCZ04 | Com-Iltg-dWatt-LF_OSnone | PGE | Com | Ex | CZ04 | 3.106 | 0.00071453 | 0 | 3.3241 | 0.00087419 | -0.017621 | 3.106 | 0.00071453 | 0 | 3.3241 | 0.00087419 | -0.017621 |  | LF | None | 3110 | 0.715 | 3110 | 0.715 | 1.07 | 1.22 | -0.0056732 | 3110 | 0.715 | 3110 | 0.715 | 1.07 | 1.22 | -0.00567
LFNonePGEComExCZ05 | Com-Iltg-dWatt-LF_OSnone | PGE | Com | Ex | CZ05 | 3.0454 | 0.0006791 | 0 | 3.2079 | 0.00081091 | -0.022294 | 3.0454 | 0.0006791 | 0 | 3.2079 | 0.00081091 | -0.022294 |  | LF | None | 3050 | 0.679 | 3050 | 0.679 | 1.05 | 1.19 | -0.0073207 | 3050 | 0.679 | 3050 | 0.679 | 1.05 | 1.19 | -0.00732
LFNonePGEComExCZ11 | Com-Iltg-dWatt-LF_OSnone | PGE | Com | Ex | CZ11 | 3.2665 | 0.00062697 | 0 | 3.4695 | 0.00075706 | -0.022145 | 3.2665 | 0.00062697 | 0 | 3.4695 | 0.00075706 | -0.022145 |  | LF | None | 3270 | 0.627 | 3270 | 0.627 | 1.06 | 1.21 | -0.0067795 | 3270 | 0.627 | 3270 | 0.627 | 1.06 | 1.21 | -0.00678
LFNonePGEComExCZ12 | Com-Iltg-dWatt-LF_OSnone | PGE | Com | Ex | CZ12 | 3.2633 | 0.00065088 | 0 | 3.4619 | 0.00078699 | -0.021466 | 3.2633 | 0.00065088 | 0 | 3.4619 | 0.00078699 | -0.021466 |  | LF | None | 3260 | 0.651 | 3260 | 0.651 | 1.06 | 1.21 | -0.0065778 | 3260 | 0.651 | 3260 | 0.651 | 1.06 | 1.21 | -0.00658
LFNonePGEComExCZ13 | Com-Iltg-dWatt-LF_OSnone | PGE | Com | Ex | CZ13 | 3.2849 | 0.00063263 | 0 | 3.5541 | 0.00076167 | -0.019713 | 3.2849 | 0.00063263 | 0 | 3.5541 | 0.00076167 | -0.019713 |  | LF | None | 3280 | 0.633 | 3280 | 0.633 | 1.08 | 1.2 | -0.0060012 | 3280 | 0.633 | 3280 | 0.633 | 1.08 | 1.2 | -0.006
LFNonePGEComExCZ16 | Com-Iltg-dWatt-LF_OSnone | PGE | Com | Ex | CZ16 | 3.1175 | 0.00059164 | 0 | 3.0398 | 0.00069056 | -0.033501 | 3.1175 | 0.00059164 | 0 | 3.0398 | 0.00069056 | -0.033501 |  | LF | None | 3120 | 0.592 | 3120 | 0.592 | 0.975 | 1.17 | -0.010746 | 3120 | 0.592 | 3120 | 0.592 | 0.975 | 1.17 | -0.0107
LFNonePGEComExIOU | Com-Iltg-dWatt-LF_OSnone | PGE | Com | Ex | IOU | 3.1747 | 0.00065466 | 0 | 3.3656 | 0.0007924 | -0.021246 | 3.1747 | 0.00065466 | 0 | 3.3656 | 0.0007924 | -0.021246 |  | LF | None | 3170 | 0.655 | 3170 | 0.655 | 1.06 | 1.21 | -0.0066921 | 3170 | 0.655 | 3170 | 0.655 | 1.06 | 1.21 | -0.00669
LFNonePGEComNewCZ05 | Com-Iltg-dWatt-LF_OSnone | PGE | Com | New | CZ05 | 2.9992 | 0.00066276 | 0 | 3.1043 | 0.0007934 | -0.021334 | 2.9992 | 0.00066276 | 0 | 3.1043 | 0.0007934 | -0.021334 |  | LF | None | 3000 | 0.663 | 3000 | 0.663 | 1.04 | 1.2 | -0.0071132 | 3000 | 0.663 | 3000 | 0.663 | 1.04 | 1.2 | -0.00711
LFNonePGEComNewCZ11 | Com-Iltg-dWatt-LF_OSnone | PGE | Com | New | CZ11 | 3.2934 | 0.00063976 | 0 | 3.4991 | 0.00078408 | -0.020892 | 3.2934 | 0.00063976 | 0 | 3.4991 | 0.00078408 | -0.020892 |  | LF | None | 3290 | 0.64 | 3290 | 0.64 | 1.06 | 1.23 | -0.0063435 | 3290 | 0.64 | 3290 | 0.64 | 1.06 | 1.23 | -0.00634
LFNonePGEComNewCZ12 | Com-Iltg-dWatt-LF_OSnone | PGE | Com | New | CZ12 | 3.2763 | 0.00065882 | 0 | 3.48 | 0.00080541 | -0.01995 | 3.2763 | 0.00065882 | 0 | 3.48 | 0.00080541 | -0.01995 |  | LF | None | 3280 | 0.659 | 3280 | 0.659 | 1.06 | 1.22 | -0.006089 | 3280 | 0.659 | 3280 | 0.659 | 1.06 | 1.22 | -0.00609
LFNonePGEComNewCZ13 | Com-Iltg-dWatt-LF_OSnone | PGE | Com | New | CZ13 | 3.3297 | 0.00064948 | 0 | 3.5911 | 0.00078671 | -0.01883 | 3.3297 | 0.00064948 | 0 | 3.5911 | 0.00078671 | -0.01883 |  | LF | None | 3330 | 0.649 | 3330 | 0.649 | 1.08 | 1.21 | -0.0056551 | 3330 | 0.649 | 3330 | 0.649 | 1.08 | 1.21 | -0.00566
LFNonePGEComNewCZ16 | Com-Iltg-dWatt-LF_OSnone | PGE | Com | New | CZ16 | 3.1295 | 0.00059683 | 0 | 3.0531 | 0.00069714 | -0.031213 | 3.1295 | 0.00059683 | 0 | 3.0531 | 0.00069714 | -0.031213 |  | LF | None | 3130 | 0.597 | 3130 | 0.597 | 0.976 | 1.17 | -0.0099739 | 3130 | 0.597 | 3130 | 0.597 | 0.976 | 1.17 | -0.00997
LFNonePGEComNewIOU | Com-Iltg-dWatt-LF_OSnone | PGE | Com | New | IOU | 3.218 | 0.00066641 | 0 | 3.3981 | 0.00080935 | -0.019841 | 3.218 | 0.00066641 | 0 | 3.3981 | 0.00080935 | -0.019841 |  | LF | None | 3220 | 0.666 | 3220 | 0.666 | 1.06 | 1.21 | -0.0061657 | 3220 | 0.666 | 3220 | 0.666 | 1.06 | 1.21 | -0.00617
LFNonePGEECCExCZ01 | Com-Iltg-dWatt-LF_OSnone | PGE | ECC | Ex | CZ01 | 2.42 | 0.000806 | 0 | 2.49 | 0.000972 | -0.0487 | 2.42 | 0.000806 | 0 | 2.49 | 0.000972 | -0.0487 |  | LF | None | 2420 | 0.806 | 2420 | 0.806 | 1.03 | 1.21 | -0.020124 | 2420 | 0.806 | 2420 | 0.806 | 1.03 | 1.21 | -0.0201
LFNonePGEECCExCZ02 | Com-Iltg-dWatt-LF_OSnone | PGE | ECC | Ex | CZ02 | 2.42 | 0.000487 | 0 | 2.65 | 0.000635 | -0.0293 | 2.42 | 0.000487 | 0 | 2.65 | 0.000635 | -0.0293 |  | LF | None | 2420 | 0.487 | 2420 | 0.487 | 1.1 | 1.3 | -0.012107 | 2420 | 0.487 | 2420 | 0.487 | 1.1 | 1.3 | -0.0121
LFNonePGEECCExCZ03 | Com-Iltg-dWatt-LF_OSnone | PGE | ECC | Ex | CZ03 | 2.42 | 0.000487 | 0 | 2.62 | 0.000604 | -0.0305 | 2.42 | 0.000487 | 0 | 2.62 | 0.000604 | -0.0305 |  | LF | None | 2420 | 0.487 | 2420 | 0.487 | 1.08 | 1.24 | -0.012603 | 2420 | 0.487 | 2420 | 0.487 | 1.08 | 1.24 | -0.0126
LFNonePGEECCExCZ04 | Com-Iltg-dWatt-LF_OSnone | PGE | ECC | Ex | CZ04 | 2.42 | 0.000806 | 0 | 2.69 | 0.00104 | -0.0231 | 2.42 | 0.000806 | 0 | 2.69 | 0.00104 | -0.0231 |  | LF | None | 2420 | 0.806 | 2420 | 0.806 | 1.11 | 1.29 | -0.0095455 | 2420 | 0.806 | 2420 | 0.806 | 1.11 | 1.29 | -0.00955
LFNonePGEECCExCZ05 | Com-Iltg-dWatt-LF_OSnone | PGE | ECC | Ex | CZ05 | 2.42 | 0.000806 | 0 | 2.62 | 0.000983 | -0.0293 | 2.42 | 0.000806 | 0 | 2.62 | 0.000983 | -0.0293 |  | LF | None | 2420 | 0.806 | 2420 | 0.806 | 1.08 | 1.22 | -0.012107 | 2420 | 0.806 | 2420 | 0.806 | 1.08 | 1.22 | -0.0121
LFNonePGEECCExCZ11 | Com-Iltg-dWatt-LF_OSnone | PGE | ECC | Ex | CZ11 | 2.42 | 0.000487 | 0 | 2.72 | 0.000606 | -0.0264 | 2.42 | 0.000487 | 0 | 2.72 | 0.000606 | -0.0264 |  | LF | None | 2420 | 0.487 | 2420 | 0.487 | 1.12 | 1.24 | -0.010909 | 2420 | 0.487 | 2420 | 0.487 | 1.12 | 1.24 | -0.0109
LFNonePGEECCExCZ12 | Com-Iltg-dWatt-LF_OSnone | PGE | ECC | Ex | CZ12 | 2.42 | 0.000487 | 0 | 2.69 | 0.000627 | -0.0262 | 2.42 | 0.000487 | 0 | 2.69 | 0.000627 | -0.0262 |  | LF | None | 2420 | 0.487 | 2420 | 0.487 | 1.11 | 1.29 | -0.010826 | 2420 | 0.487 | 2420 | 0.487 | 1.11 | 1.29 | -0.0108
LFNonePGEECCExCZ13 | Com-Iltg-dWatt-LF_OSnone | PGE | ECC | Ex | CZ13 | 2.42 | 0.000487 | 0 | 2.74 | 0.000633 | -0.0232 | 2.42 | 0.000487 | 0 | 2.74 | 0.000633 | -0.0232 |  | LF | None | 2420 | 0.487 | 2420 | 0.487 | 1.13 | 1.3 | -0.0095868 | 2420 | 0.487 | 2420 | 0.487 | 1.13 | 1.3 | -0.00959
LFNonePGEECCExCZ16 | Com-Iltg-dWatt-LF_OSnone | PGE | ECC | Ex | CZ16 | 2.42 | 0.000487 | 0 | 2.56 | 0.000596 | -0.0426 | 2.42 | 0.000487 | 0 | 2.56 | 0.000596 | -0.0426 |  | LF | None | 2420 | 0.487 | 2420 | 0.487 | 1.06 | 1.22 | -0.017603 | 2420 | 0.487 | 2420 | 0.487 | 1.06 | 1.22 | -0.0176
LFNonePGEECCExIOU | Com-Iltg-dWatt-LF_OSnone | PGE | ECC | Ex | IOU | 2.42 | 0.00054783 | 0 | 2.6593 | 0.00069061 | -0.028277 | 2.42 | 0.00054783 | 0 | 2.6593 | 0.00069061 | -0.028277 |  | LF | None | 2420 | 0.548 | 2420 | 0.548 | 1.1 | 1.26 | -0.011685 | 2420 | 0.548 | 2420 | 0.548 | 1.1 | 1.26 | -0.0117
LFNonePGEECCNewCZ01 | Com-Iltg-dWatt-LF_OSnone | PGE | ECC | New | CZ01 | 2.42 | 0.000806 | 0 | 2.5 | 0.000945 | -0.0468 | 2.42 | 0.000806 | 0 | 2.5 | 0.000945 | -0.0468 |  | LF | None | 2420 | 0.806 | 2420 | 0.806 | 1.03 | 1.17 | -0.019339 | 2420 | 0.806 | 2420 | 0.806 | 1.03 | 1.17 | -0.0193
LFNonePGEECCNewCZ02 | Com-Iltg-dWatt-LF_OSnone | PGE | ECC | New | CZ02 | 2.42 | 0.000487 | 0 | 2.65 | 0.000652 | -0.0271 | 2.42 | 0.000487 | 0 | 2.65 | 0.000652 | -0.0271 |  | LF | None | 2420 | 0.487 | 2420 | 0.487 | 1.1 | 1.34 | -0.011198 | 2420 | 0.487 | 2420 | 0.487 | 1.1 | 1.34 | -0.0112
LFNonePGEECCNewCZ03 | Com-Iltg-dWatt-LF_OSnone | PGE | ECC | New | CZ03 | 2.42 | 0.000487 | 0 | 2.6 | 0.000631 | -0.0286 | 2.42 | 0.000487 | 0 | 2.6 | 0.000631 | -0.0286 |  | LF | None | 2420 | 0.487 | 2420 | 0.487 | 1.07 | 1.3 | -0.011818 | 2420 | 0.487 | 2420 | 0.487 | 1.07 | 1.3 | -0.0118
LFNonePGEECCNewCZ04 | Com-Iltg-dWatt-LF_OSnone | PGE | ECC | New | CZ04 | 2.42 | 0.000806 | 0 | 2.69 | 0.00101 | -0.0212 | 2.42 | 0.000806 | 0 | 2.69 | 0.00101 | -0.0212 |  | LF | None | 2420 | 0.806 | 2420 | 0.806 | 1.11 | 1.25 | -0.0087603 | 2420 | 0.806 | 2420 | 0.806 | 1.11 | 1.25 | -0.00876
LFNonePGEECCNewCZ05 | Com-Iltg-dWatt-LF_OSnone | PGE | ECC | New | CZ05 | 2.42 | 0.000806 | 0 | 2.62 | 0.00098 | -0.0279 | 2.42 | 0.000806 | 0 | 2.62 | 0.00098 | -0.0279 |  | LF | None | 2420 | 0.806 | 2420 | 0.806 | 1.08 | 1.22 | -0.011529 | 2420 | 0.806 | 2420 | 0.806 | 1.08 | 1.22 | -0.0115
LFNonePGEECCNewCZ11 | Com-Iltg-dWatt-LF_OSnone | PGE | ECC | New | CZ11 | 2.42 | 0.000487 | 0 | 2.73 | 0.00064 | -0.0229 | 2.42 | 0.000487 | 0 | 2.73 | 0.00064 | -0.0229 |  | LF | None | 2420 | 0.487 | 2420 | 0.487 | 1.13 | 1.31 | -0.0094628 | 2420 | 0.487 | 2420 | 0.487 | 1.13 | 1.31 | -0.00946
LFNonePGEECCNewCZ12 | Com-Iltg-dWatt-LF_OSnone | PGE | ECC | New | CZ12 | 2.42 | 0.000487 | 0 | 2.71 | 0.000653 | -0.0232 | 2.42 | 0.000487 | 0 | 2.71 | 0.000653 | -0.0232 |  | LF | None | 2420 | 0.487 | 2420 | 0.487 | 1.12 | 1.34 | -0.0095868 | 2420 | 0.487 | 2420 | 0.487 | 1.12 | 1.34 | -0.00959
LFNonePGEECCNewCZ13 | Com-Iltg-dWatt-LF_OSnone | PGE | ECC | New | CZ13 | 2.42 | 0.000487 | 0 | 2.75 | 0.000646 | -0.0202 | 2.42 | 0.000487 | 0 | 2.75 | 0.000646 | -0.0202 |  | LF | None | 2420 | 0.487 | 2420 | 0.487 | 1.14 | 1.33 | -0.0083471 | 2420 | 0.487 | 2420 | 0.487 | 1.14 | 1.33 | -0.00835
LFNonePGEECCNewCZ16 | Com-Iltg-dWatt-LF_OSnone | PGE | ECC | New | CZ16 | 2.42 | 0.000487 | 0 | 2.57 | 0.000619 | -0.0395 | 2.42 | 0.000487 | 0 | 2.57 | 0.000619 | -0.0395 |  | LF | None | 2420 | 0.487 | 2420 | 0.487 | 1.06 | 1.27 | -0.016322 | 2420 | 0.487 | 2420 | 0.487 | 1.06 | 1.27 | -0.0163
LFNonePGEECCNewIOU | Com-Iltg-dWatt-LF_OSnone | PGE | ECC | New | IOU | 2.42 | 0.00054821 | 0 | 2.671 | 0.00070908 | -0.025039 | 2.42 | 0.00054821 | 0 | 2.671 | 0.00070908 | -0.025039 |  | LF | None | 2420 | 0.548 | 2420 | 0.548 | 1.1 | 1.29 | -0.010347 | 2420 | 0.548 | 2420 | 0.548 | 1.1 | 1.29 | -0.0103
LFNonePGEEPrExCZ01 | Com-Iltg-dWatt-LF_OSnone | PGE | EPr | Ex | CZ01 | 2.14 | 0.000616 | 0 | 2.12 | 0.000736 | -0.0387 | 2.14 | 0.000616 | 0 | 2.12 | 0.000736 | -0.0387 |  | LF | None | 2140 | 0.616 | 2140 | 0.616 | 0.991 | 1.19 | -0.018084 | 2140 | 0.616 | 2140 | 0.616 | 0.991 | 1.19 | -0.0181
LFNonePGEEPrExCZ02 | Com-Iltg-dWatt-LF_OSnone | PGE | EPr | Ex | CZ02 | 2.14 | 2e-05 | 0 | 2.26 | 2e-05 | -0.0227 | 2.14 | 2e-05 | 0 | 2.26 | 2e-05 | -0.0227 |  | LF | None | 2140 | 0.02 | 2140 | 0.02 | 1.06 | 1 | -0.010607 | 2140 | 0.02 | 2140 | 0.02 | 1.06 | 1 | -0.0106
LFNonePGEEPrExCZ03 | Com-Iltg-dWatt-LF_OSnone | PGE | EPr | Ex | CZ03 | 2.14 | 2e-05 | 0 | 2.28 | 2e-05 | -0.022 | 2.14 | 2e-05 | 0 | 2.28 | 2e-05 | -0.022 |  | LF | None | 2140 | 0.02 | 2140 | 0.02 | 1.07 | 1 | -0.01028 | 2140 | 0.02 | 2140 | 0.02 | 1.07 | 1 | -0.0103
LFNonePGEEPrExCZ04 | Com-Iltg-dWatt-LF_OSnone | PGE | EPr | Ex | CZ04 | 2.14 | 0.000616 | 0 | 2.32 | 0.00076 | -0.0173 | 2.14 | 0.000616 | 0 | 2.32 | 0.00076 | -0.0173 |  | LF | None | 2140 | 0.616 | 2140 | 0.616 | 1.08 | 1.23 | -0.0080841 | 2140 | 0.616 | 2140 | 0.616 | 1.08 | 1.23 | -0.00808
LFNonePGEEPrExCZ05 | Com-Iltg-dWatt-LF_OSnone | PGE | EPr | Ex | CZ05 | 2.14 | 0.000616 | 0 | 2.28 | 0.000744 | -0.0207 | 2.14 | 0.000616 | 0 | 2.28 | 0.000744 | -0.0207 |  | LF | None | 2140 | 0.616 | 2140 | 0.616 | 1.07 | 1.21 | -0.0096729 | 2140 | 0.616 | 2140 | 0.616 | 1.07 | 1.21 | -0.00967
LFNonePGEEPrExCZ11 | Com-Iltg-dWatt-LF_OSnone | PGE | EPr | Ex | CZ11 | 2.14 | 2e-05 | 0 | 2.28 | 2e-05 | -0.0209 | 2.14 | 2e-05 | 0 | 2.28 | 2e-05 | -0.0209 |  | LF | None | 2140 | 0.02 | 2140 | 0.02 | 1.07 | 1 | -0.0097664 | 2140 | 0.02 | 2140 | 0.02 | 1.07 | 1 | -0.00977
LFNonePGEEPrExCZ12 | Com-Iltg-dWatt-LF_OSnone | PGE | EPr | Ex | CZ12 | 2.14 | 2e-05 | 0 | 2.28 | 2e-05 | -0.0216 | 2.14 | 2e-05 | 0 | 2.28 | 2e-05 | -0.0216 |  | LF | None | 2140 | 0.02 | 2140 | 0.02 | 1.07 | 1 | -0.010093 | 2140 | 0.02 | 2140 | 0.02 | 1.07 | 1 | -0.0101
LFNonePGEEPrExCZ13 | Com-Iltg-dWatt-LF_OSnone | PGE | EPr | Ex | CZ13 | 2.14 | 2e-05 | 0 | 2.3 | 2e-05 | -0.0187 | 2.14 | 2e-05 | 0 | 2.3 | 2e-05 | -0.0187 |  | LF | None | 2140 | 0.02 | 2140 | 0.02 | 1.07 | 1 | -0.0087383 | 2140 | 0.02 | 2140 | 0.02 | 1.07 | 1 | -0.00874
LFNonePGEEPrExCZ16 | Com-Iltg-dWatt-LF_OSnone | PGE | EPr | Ex | CZ16 | 2.14 | 2e-05 | 0 | 2.08 | 2e-05 | -0.0383 | 2.14 | 2e-05 | 0 | 2.08 | 2e-05 | -0.0383 |  | LF | None | 2140 | 0.02 | 2140 | 0.02 | 0.972 | 1 | -0.017897 | 2140 | 0.02 | 2140 | 0.02 | 0.972 | 1 | -0.0179
LFNonePGEEPrExIOU | Com-Iltg-dWatt-LF_OSnone | PGE | EPr | Ex | IOU | 2.14 | 0.00012487 | 0 | 2.2842 | 0.00014965 | -0.020951 | 2.14 | 0.00012487 | 0 | 2.2842 | 0.00014965 | -0.020951 |  | LF | None | 2140 | 0.125 | 2140 | 0.125 | 1.07 | 1.2 | -0.0097902 | 2140 | 0.125 | 2140 | 0.125 | 1.07 | 1.2 | -0.00979
LFNonePGEEPrNewCZ01 | Com-Iltg-dWatt-LF_OSnone | PGE | EPr | New | CZ01 | 2.14 | 0.000616 | 0 | 2.12 | 0.000717 | -0.0422 | 2.14 | 0.000616 | 0 | 2.12 | 0.000717 | -0.0422 |  | LF | None | 2140 | 0.616 | 2140 | 0.616 | 0.991 | 1.16 | -0.01972 | 2140 | 0.616 | 2140 | 0.616 | 0.991 | 1.16 | -0.0197
LFNonePGEEPrNewCZ02 | Com-Iltg-dWatt-LF_OSnone | PGE | EPr | New | CZ02 | 2.14 | 2e-05 | 0 | 2.25 | 2e-05 | -0.0274 | 2.14 | 2e-05 | 0 | 2.25 | 2e-05 | -0.0274 |  | LF | None | 2140 | 0.02 | 2140 | 0.02 | 1.05 | 1 | -0.012804 | 2140 | 0.02 | 2140 | 0.02 | 1.05 | 1 | -0.0128
LFNonePGEEPrNewCZ03 | Com-Iltg-dWatt-LF_OSnone | PGE | EPr | New | CZ03 | 2.14 | 2e-05 | 0 | 2.23 | 2e-05 | -0.0231 | 2.14 | 2e-05 | 0 | 2.23 | 2e-05 | -0.0231 |  | LF | None | 2140 | 0.02 | 2140 | 0.02 | 1.04 | 1 | -0.010794 | 2140 | 0.02 | 2140 | 0.02 | 1.04 | 1 | -0.0108
LFNonePGEEPrNewCZ04 | Com-Iltg-dWatt-LF_OSnone | PGE | EPr | New | CZ04 | 2.14 | 0.000616 | 0 | 2.3 | 0.000814 | -0.0207 | 2.14 | 0.000616 | 0 | 2.3 | 0.000814 | -0.0207 |  | LF | None | 2140 | 0.616 | 2140 | 0.616 | 1.07 | 1.32 | -0.0096729 | 2140 | 0.616 | 2140 | 0.616 | 1.07 | 1.32 | -0.00967
LFNonePGEEPrNewCZ05 | Com-Iltg-dWatt-LF_OSnone | PGE | EPr | New | CZ05 | 2.14 | 0.000616 | 0 | 2.24 | 0.000769 | -0.0201 | 2.14 | 0.000616 | 0 | 2.24 | 0.000769 | -0.0201 |  | LF | None | 2140 | 0.616 | 2140 | 0.616 | 1.05 | 1.25 | -0.0093925 | 2140 | 0.616 | 2140 | 0.616 | 1.05 | 1.25 | -0.00939
LFNonePGEEPrNewCZ11 | Com-Iltg-dWatt-LF_OSnone | PGE | EPr | New | CZ11 | 2.14 | 2e-05 | 0 | 2.33 | 2e-05 | -0.0244 | 2.14 | 2e-05 | 0 | 2.33 | 2e-05 | -0.0244 |  | LF | None | 2140 | 0.02 | 2140 | 0.02 | 1.09 | 1 | -0.011402 | 2140 | 0.02 | 2140 | 0.02 | 1.09 | 1 | -0.0114
LFNonePGEEPrNewCZ12 | Com-Iltg-dWatt-LF_OSnone | PGE | EPr | New | CZ12 | 2.14 | 2e-05 | 0 | 2.3 | 2e-05 | -0.0248 | 2.14 | 2e-05 | 0 | 2.3 | 2e-05 | -0.0248 |  | LF | None | 2140 | 0.02 | 2140 | 0.02 | 1.07 | 1 | -0.011589 | 2140 | 0.02 | 2140 | 0.02 | 1.07 | 1 | -0.0116
LFNonePGEEPrNewCZ13 | Com-Iltg-dWatt-LF_OSnone | PGE | EPr | New | CZ13 | 2.14 | 2e-05 | 0 | 2.34 | 2e-05 | -0.0223 | 2.14 | 2e-05 | 0 | 2.34 | 2e-05 | -0.0223 |  | LF | None | 2140 | 0.02 | 2140 | 0.02 | 1.09 | 1 | -0.010421 | 2140 | 0.02 | 2140 | 0.02 | 1.09 | 1 | -0.0104
LFNonePGEEPrNewCZ16 | Com-Iltg-dWatt-LF_OSnone | PGE | EPr | New | CZ16 | 2.14 | 2e-05 | 0 | 2.13 | 2e-05 | -0.0357 | 2.14 | 2e-05 | 0 | 2.13 | 2e-05 | -0.0357 |  | LF | None | 2140 | 0.02 | 2140 | 0.02 | 0.995 | 1 | -0.016682 | 2140 | 0.02 | 2140 | 0.02 | 0.995 | 1 | -0.0167
LFNonePGEEPrNewIOU | Com-Iltg-dWatt-LF_OSnone | PGE | EPr | New | IOU | 2.14 | 0.00010406 | 0 | 2.2923 | 0.00013034 | -0.023808 | 2.14 | 0.00010406 | 0 | 2.2923 | 0.00013034 | -0.023808 |  | LF | None | 2140 | 0.104 | 2140 | 0.104 | 1.07 | 1.25 | -0.011125 | 2140 | 0.104 | 2140 | 0.104 | 1.07 | 1.25 | -0.0111
LFNonePGEERCExCZ01 | Com-Iltg-dWatt-LF_OSnone | PGE | ERC | Ex | CZ01 | 2.48 | 0.000702 | 0 | 2.4 | 0.000833 | -0.0429 | 2.48 | 0.000702 | 0 | 2.4 | 0.000833 | -0.0429 |  | LF | None | 2480 | 0.702 | 2480 | 0.702 | 0.968 | 1.19 | -0.017298 | 2480 | 0.702 | 2480 | 0.702 | 0.968 | 1.19 | -0.0173
LFNonePGEERCExCZ02 | Com-Iltg-dWatt-LF_OSnone | PGE | ERC | Ex | CZ02 | 2.48 | 2e-05 | 0 | 2.53 | 2e-05 | -0.0303 | 2.48 | 2e-05 | 0 | 2.53 | 2e-05 | -0.0303 |  | LF | None | 2480 | 0.02 | 2480 | 0.02 | 1.02 | 1 | -0.012218 | 2480 | 0.02 | 2480 | 0.02 | 1.02 | 1 | -0.0122
LFNonePGEERCExCZ03 | Com-Iltg-dWatt-LF_OSnone | PGE | ERC | Ex | CZ03 | 2.48 | 2e-05 | 0 | 2.49 | 2e-05 | -0.028 | 2.48 | 2e-05 | 0 | 2.49 | 2e-05 | -0.028 |  | LF | None | 2480 | 0.02 | 2480 | 0.02 | 1 | 1 | -0.01129 | 2480 | 0.02 | 2480 | 0.02 | 1 | 1 | -0.0113
LFNonePGEERCExCZ04 | Com-Iltg-dWatt-LF_OSnone | PGE | ERC | Ex | CZ04 | 2.48 | 0.000702 | 0 | 2.59 | 0.000851 | -0.0236 | 2.48 | 0.000702 | 0 | 2.59 | 0.000851 | -0.0236 |  | LF | None | 2480 | 0.702 | 2480 | 0.702 | 1.04 | 1.21 | -0.0095161 | 2480 | 0.702 | 2480 | 0.702 | 1.04 | 1.21 | -0.00952
LFNonePGEERCExCZ05 | Com-Iltg-dWatt-LF_OSnone | PGE | ERC | Ex | CZ05 | 2.48 | 0.000702 | 0 | 2.53 | 0.000858 | -0.0275 | 2.48 | 0.000702 | 0 | 2.53 | 0.000858 | -0.0275 |  | LF | None | 2480 | 0.702 | 2480 | 0.702 | 1.02 | 1.22 | -0.011089 | 2480 | 0.702 | 2480 | 0.702 | 1.02 | 1.22 | -0.0111
LFNonePGEERCExCZ11 | Com-Iltg-dWatt-LF_OSnone | PGE | ERC | Ex | CZ11 | 2.48 | 2e-05 | 0 | 2.58 | 2e-05 | -0.0255 | 2.48 | 2e-05 | 0 | 2.58 | 2e-05 | -0.0255 |  | LF | None | 2480 | 0.02 | 2480 | 0.02 | 1.04 | 1 | -0.010282 | 2480 | 0.02 | 2480 | 0.02 | 1.04 | 1 | -0.0103
LFNonePGEERCExCZ12 | Com-Iltg-dWatt-LF_OSnone | PGE | ERC | Ex | CZ12 | 2.48 | 2e-05 | 0 | 2.58 | 2e-05 | -0.027 | 2.48 | 2e-05 | 0 | 2.58 | 2e-05 | -0.027 |  | LF | None | 2480 | 0.02 | 2480 | 0.02 | 1.04 | 1 | -0.010887 | 2480 | 0.02 | 2480 | 0.02 | 1.04 | 1 | -0.0109
LFNonePGEERCExCZ13 | Com-Iltg-dWatt-LF_OSnone | PGE | ERC | Ex | CZ13 | 2.48 | 2e-05 | 0 | 2.62 | 2e-05 | -0.0241 | 2.48 | 2e-05 | 0 | 2.62 | 2e-05 | -0.0241 |  | LF | None | 2480 | 0.02 | 2480 | 0.02 | 1.06 | 1 | -0.0097177 | 2480 | 0.02 | 2480 | 0.02 | 1.06 | 1 | -0.00972
LFNonePGEERCExCZ16 | Com-Iltg-dWatt-LF_OSnone | PGE | ERC | Ex | CZ16 | 2.48 | 2e-05 | 0 | 2.46 | 2e-05 | -0.0412 | 2.48 | 2e-05 | 0 | 2.46 | 2e-05 | -0.0412 |  | LF | None | 2480 | 0.02 | 2480 | 0.02 | 0.992 | 1 | -0.016613 | 2480 | 0.02 | 2480 | 0.02 | 0.992 | 1 | -0.0166
LFNonePGEERCExIOU | Com-Iltg-dWatt-LF_OSnone | PGE | ERC | Ex | IOU | 2.48 | 0.00014001 | 0 | 2.5547 | 0.00016618 | -0.026761 | 2.48 | 0.00014001 | 0 | 2.5547 | 0.00016618 | -0.026761 |  | LF | None | 2480 | 0.14 | 2480 | 0.14 | 1.03 | 1.19 | -0.010791 | 2480 | 0.14 | 2480 | 0.14 | 1.03 | 1.19 | -0.0108
LFNonePGEERCNewCZ01 | Com-Iltg-dWatt-LF_OSnone | PGE | ERC | New | CZ01 | 2.48 | 0.000702 | 0 | 2.58 | 0.000839 | -0.0479 | 2.48 | 0.000702 | 0 | 2.58 | 0.000839 | -0.0479 |  | LF | None | 2480 | 0.702 | 2480 | 0.702 | 1.04 | 1.2 | -0.019315 | 2480 | 0.702 | 2480 | 0.702 | 1.04 | 1.2 | -0.0193
LFNonePGEERCNewCZ02 | Com-Iltg-dWatt-LF_OSnone | PGE | ERC | New | CZ02 | 2.48 | 2e-05 | 0 | 2.71 | 2e-05 | -0.0312 | 2.48 | 2e-05 | 0 | 2.71 | 2e-05 | -0.0312 |  | LF | None | 2480 | 0.02 | 2480 | 0.02 | 1.09 | 1 | -0.012581 | 2480 | 0.02 | 2480 | 0.02 | 1.09 | 1 | -0.0126
LFNonePGEERCNewCZ03 | Com-Iltg-dWatt-LF_OSnone | PGE | ERC | New | CZ03 | 2.48 | 2e-05 | 0 | 2.71 | 2e-05 | -0.028 | 2.48 | 2e-05 | 0 | 2.71 | 2e-05 | -0.028 |  | LF | None | 2480 | 0.02 | 2480 | 0.02 | 1.09 | 1 | -0.01129 | 2480 | 0.02 | 2480 | 0.02 | 1.09 | 1 | -0.0113
LFNonePGEERCNewCZ04 | Com-Iltg-dWatt-LF_OSnone | PGE | ERC | New | CZ04 | 2.48 | 0.000702 | 0 | 2.77 | 0.000896 | -0.0241 | 2.48 | 0.000702 | 0 | 2.77 | 0.000896 | -0.0241 |  | LF | None | 2480 | 0.702 | 2480 | 0.702 | 1.12 | 1.28 | -0.0097177 | 2480 | 0.702 | 2480 | 0.702 | 1.12 | 1.28 | -0.00972
LFNonePGEERCNewCZ05 | Com-Iltg-dWatt-LF_OSnone | PGE | ERC | New | CZ05 | 2.48 | 0.000702 | 0 | 2.69 | 0.000869 | -0.0265 | 2.48 | 0.000702 | 0 | 2.69 | 0.000869 | -0.0265 |  | LF | None | 2480 | 0.702 | 2480 | 0.702 | 1.08 | 1.24 | -0.010685 | 2480 | 0.702 | 2480 | 0.702 | 1.08 | 1.24 | -0.0107
LFNonePGEERCNewCZ11 | Com-Iltg-dWatt-LF_OSnone | PGE | ERC | New | CZ11 | 2.48 | 2e-05 | 0 | 2.8 | 2e-05 | -0.028 | 2.48 | 2e-05 | 0 | 2.8 | 2e-05 | -0.028 |  | LF | None | 2480 | 0.02 | 2480 | 0.02 | 1.13 | 1 | -0.01129 | 2480 | 0.02 | 2480 | 0.02 | 1.13 | 1 | -0.0113
LFNonePGEERCNewCZ12 | Com-Iltg-dWatt-LF_OSnone | PGE | ERC | New | CZ12 | 2.48 | 2e-05 | 0 | 2.77 | 2e-05 | -0.0288 | 2.48 | 2e-05 | 0 | 2.77 | 2e-05 | -0.0288 |  | LF | None | 2480 | 0.02 | 2480 | 0.02 | 1.12 | 1 | -0.011613 | 2480 | 0.02 | 2480 | 0.02 | 1.12 | 1 | -0.0116
LFNonePGEERCNewCZ13 | Com-Iltg-dWatt-LF_OSnone | PGE | ERC | New | CZ13 | 2.48 | 2e-05 | 0 | 2.82 | 2e-05 | -0.0255 | 2.48 | 2e-05 | 0 | 2.82 | 2e-05 | -0.0255 |  | LF | None | 2480 | 0.02 | 2480 | 0.02 | 1.14 | 1 | -0.010282 | 2480 | 0.02 | 2480 | 0.02 | 1.14 | 1 | -0.0103
LFNonePGEERCNewCZ16 | Com-Iltg-dWatt-LF_OSnone | PGE | ERC | New | CZ16 | 2.48 | 2e-05 | 0 | 2.59 | 2e-05 | -0.0451 | 2.48 | 2e-05 | 0 | 2.59 | 2e-05 | -0.0451 |  | LF | None | 2480 | 0.02 | 2480 | 0.02 | 1.04 | 1 | -0.018185 | 2480 | 0.02 | 2480 | 0.02 | 1.04 | 1 | -0.0182
LFNonePGEERCNewIOU | Com-Iltg-dWatt-LF_OSnone | PGE | ERC | New | IOU | 2.48 | 0.00011619 | 0 | 2.7652 | 0.00014258 | -0.027785 | 2.48 | 0.00011619 | 0 | 2.7652 | 0.00014258 | -0.027785 |  | LF | None | 2480 | 0.116 | 2480 | 0.116 | 1.11 | 1.23 | -0.011204 | 2480 | 0.116 | 2480 | 0.116 | 1.11 | 1.23 | -0.0112
LFNonePGEESeExCZ01 | Com-Iltg-dWatt-LF_OSnone | PGE | ESe | Ex | CZ01 | 2.28 | 0.000709 | 0 | 2.22 | 0.000842 | -0.0482 | 2.28 | 0.000709 | 0 | 2.22 | 0.000842 | -0.0482 |  | LF | None | 2280 | 0.709 | 2280 | 0.709 | 0.974 | 1.19 | -0.02114 | 2280 | 0.709 | 2280 | 0.709 | 0.974 | 1.19 | -0.0211
LFNonePGEESeExCZ02 | Com-Iltg-dWatt-LF_OSnone | PGE | ESe | Ex | CZ02 | 2.28 | 2e-05 | 0 | 2.38 | 2e-05 | -0.0297 | 2.28 | 2e-05 | 0 | 2.38 | 2e-05 | -0.0297 |  | LF | None | 2280 | 0.02 | 2280 | 0.02 | 1.04 | 1 | -0.013026 | 2280 | 0.02 | 2280 | 0.02 | 1.04 | 1 | -0.013
LFNonePGEESeExCZ03 | Com-Iltg-dWatt-LF_OSnone | PGE | ESe | Ex | CZ03 | 2.28 | 2e-05 | 0 | 2.38 | 2e-05 | -0.0306 | 2.28 | 2e-05 | 0 | 2.38 | 2e-05 | -0.0306 |  | LF | None | 2280 | 0.02 | 2280 | 0.02 | 1.04 | 1 | -0.013421 | 2280 | 0.02 | 2280 | 0.02 | 1.04 | 1 | -0.0134
LFNonePGEESeExCZ04 | Com-Iltg-dWatt-LF_OSnone | PGE | ESe | Ex | CZ04 | 2.28 | 0.000709 | 0 | 2.44 | 0.000866 | -0.0233 | 2.28 | 0.000709 | 0 | 2.44 | 0.000866 | -0.0233 |  | LF | None | 2280 | 0.709 | 2280 | 0.709 | 1.07 | 1.22 | -0.010219 | 2280 | 0.709 | 2280 | 0.709 | 1.07 | 1.22 | -0.0102
LFNonePGEESeExCZ05 | Com-Iltg-dWatt-LF_OSnone | PGE | ESe | Ex | CZ05 | 2.28 | 0.000709 | 0 | 2.39 | 0.000844 | -0.0281 | 2.28 | 0.000709 | 0 | 2.39 | 0.000844 | -0.0281 |  | LF | None | 2280 | 0.709 | 2280 | 0.709 | 1.05 | 1.19 | -0.012325 | 2280 | 0.709 | 2280 | 0.709 | 1.05 | 1.19 | -0.0123
LFNonePGEESeExCZ11 | Com-Iltg-dWatt-LF_OSnone | PGE | ESe | Ex | CZ11 | 2.28 | 2e-05 | 0 | 2.43 | 2e-05 | -0.0263 | 2.28 | 2e-05 | 0 | 2.43 | 2e-05 | -0.0263 |  | LF | None | 2280 | 0.02 | 2280 | 0.02 | 1.07 | 1 | -0.011535 | 2280 | 0.02 | 2280 | 0.02 | 1.07 | 1 | -0.0115
LFNonePGEESeExCZ12 | Com-Iltg-dWatt-LF_OSnone | PGE | ESe | Ex | CZ12 | 2.28 | 2e-05 | 0 | 2.42 | 2e-05 | -0.0272 | 2.28 | 2e-05 | 0 | 2.42 | 2e-05 | -0.0272 |  | LF | None | 2280 | 0.02 | 2280 | 0.02 | 1.06 | 1 | -0.01193 | 2280 | 0.02 | 2280 | 0.02 | 1.06 | 1 | -0.0119
LFNonePGEESeExCZ13 | Com-Iltg-dWatt-LF_OSnone | PGE | ESe | Ex | CZ13 | 2.28 | 2e-05 | 0 | 2.46 | 2e-05 | -0.0238 | 2.28 | 2e-05 | 0 | 2.46 | 2e-05 | -0.0238 |  | LF | None | 2280 | 0.02 | 2280 | 0.02 | 1.08 | 1 | -0.010439 | 2280 | 0.02 | 2280 | 0.02 | 1.08 | 1 | -0.0104
LFNonePGEESeExCZ16 | Com-Iltg-dWatt-LF_OSnone | PGE | ESe | Ex | CZ16 | 2.28 | 2e-05 | 0 | 2.24 | 2e-05 | -0.0416 | 2.28 | 2e-05 | 0 | 2.24 | 2e-05 | -0.0416 |  | LF | None | 2280 | 0.02 | 2280 | 0.02 | 0.982 | 1 | -0.018246 | 2280 | 0.02 | 2280 | 0.02 | 0.982 | 1 | -0.0182
LFNonePGEESeExIOU | Com-Iltg-dWatt-LF_OSnone | PGE | ESe | Ex | IOU | 2.28 | 0.00014124 | 0 | 2.4115 | 0.00016818 | -0.027532 | 2.28 | 0.00014124 | 0 | 2.4115 | 0.00016818 | -0.027532 |  | LF | None | 2280 | 0.141 | 2280 | 0.141 | 1.06 | 1.19 | -0.012075 | 2280 | 0.141 | 2280 | 0.141 | 1.06 | 1.19 | -0.0121
LFNonePGEESeNewCZ01 | Com-Iltg-dWatt-LF_OSnone | PGE | ESe | New | CZ01 | 2.28 | 0.000709 | 0 | 2.27 | 0.000822 | -0.0354 | 2.28 | 0.000709 | 0 | 2.27 | 0.000822 | -0.0354 |  | LF | None | 2280 | 0.709 | 2280 | 0.709 | 0.996 | 1.16 | -0.015526 | 2280 | 0.709 | 2280 | 0.709 | 0.996 | 1.16 | -0.0155
LFNonePGEESeNewCZ02 | Com-Iltg-dWatt-LF_OSnone | PGE | ESe | New | CZ02 | 2.28 | 2e-05 | 0 | 2.42 | 2e-05 | -0.0333 | 2.28 | 2e-05 | 0 | 2.42 | 2e-05 | -0.0333 |  | LF | None | 2280 | 0.02 | 2280 | 0.02 | 1.06 | 1 | -0.014605 | 2280 | 0.02 | 2280 | 0.02 | 1.06 | 1 | -0.0146
LFNonePGEESeNewCZ03 | Com-Iltg-dWatt-LF_OSnone | PGE | ESe | New | CZ03 | 2.28 | 2e-05 | 0 | 2.39 | 2e-05 | -0.0311 | 2.28 | 2e-05 | 0 | 2.39 | 2e-05 | -0.0311 |  | LF | None | 2280 | 0.02 | 2280 | 0.02 | 1.05 | 1 | -0.01364 | 2280 | 0.02 | 2280 | 0.02 | 1.05 | 1 | -0.0136
LFNonePGEESeNewCZ04 | Com-Iltg-dWatt-LF_OSnone | PGE | ESe | New | CZ04 | 2.28 | 0.000709 | 0 | 2.46 | 0.00093 | -0.0263 | 2.28 | 0.000709 | 0 | 2.46 | 0.00093 | -0.0263 |  | LF | None | 2280 | 0.709 | 2280 | 0.709 | 1.08 | 1.31 | -0.011535 | 2280 | 0.709 | 2280 | 0.709 | 1.08 | 1.31 | -0.0115
LFNonePGEESeNewCZ05 | Com-Iltg-dWatt-LF_OSnone | PGE | ESe | New | CZ05 | 2.28 | 0.000709 | 0 | 2.39 | 0.000871 | -0.0251 | 2.28 | 0.000709 | 0 | 2.39 | 0.000871 | -0.0251 |  | LF | None | 2280 | 0.709 | 2280 | 0.709 | 1.05 | 1.23 | -0.011009 | 2280 | 0.709 | 2280 | 0.709 | 1.05 | 1.23 | -0.011
LFNonePGEESeNewCZ11 | Com-Iltg-dWatt-LF_OSnone | PGE | ESe | New | CZ11 | 2.28 | 2e-05 | 0 | 2.5 | 2e-05 | -0.0285 | 2.28 | 2e-05 | 0 | 2.5 | 2e-05 | -0.0285 |  | LF | None | 2280 | 0.02 | 2280 | 0.02 | 1.1 | 1 | -0.0125 | 2280 | 0.02 | 2280 | 0.02 | 1.1 | 1 | -0.0125
LFNonePGEESeNewCZ12 | Com-Iltg-dWatt-LF_OSnone | PGE | ESe | New | CZ12 | 2.28 | 2e-05 | 0 | 2.47 | 2e-05 | -0.0297 | 2.28 | 2e-05 | 0 | 2.47 | 2e-05 | -0.0297 |  | LF | None | 2280 | 0.02 | 2280 | 0.02 | 1.08 | 1 | -0.013026 | 2280 | 0.02 | 2280 | 0.02 | 1.08 | 1 | -0.013
LFNonePGEESeNewCZ13 | Com-Iltg-dWatt-LF_OSnone | PGE | ESe | New | CZ13 | 2.28 | 2e-05 | 0 | 2.53 | 2e-05 | -0.0263 | 2.28 | 2e-05 | 0 | 2.53 | 2e-05 | -0.0263 |  | LF | None | 2280 | 0.02 | 2280 | 0.02 | 1.11 | 1 | -0.011535 | 2280 | 0.02 | 2280 | 0.02 | 1.11 | 1 | -0.0115
LFNonePGEESeNewCZ16 | Com-Iltg-dWatt-LF_OSnone | PGE | ESe | New | CZ16 | 2.28 | 2e-05 | 0 | 2.29 | 2e-05 | -0.0343 | 2.28 | 2e-05 | 0 | 2.29 | 2e-05 | -0.0343 |  | LF | None | 2280 | 0.02 | 2280 | 0.02 | 1 | 1 | -0.015044 | 2280 | 0.02 | 2280 | 0.02 | 1 | 1 | -0.015
LFNonePGEESeNewIOU | Com-Iltg-dWatt-LF_OSnone | PGE | ESe | New | IOU | 2.28 | 0.00011718 | 0 | 2.4634 | 0.00014637 | -0.028898 | 2.28 | 0.00011718 | 0 | 2.4634 | 0.00014637 | -0.028898 |  | LF | None | 2280 | 0.117 | 2280 | 0.117 | 1.08 | 1.25 | -0.012675 | 2280 | 0.117 | 2280 | 0.117 | 1.08 | 1.25 | -0.0127
LFNonePGEEUnExCZ01 | Com-Iltg-dWatt-LF_OSnone | PGE | EUn | Ex | CZ01 | 2.35 | 0.00072 | 0 | 2.49 | 0.000878 | -0.0247 | 2.35 | 0.00072 | 0 | 2.49 | 0.000878 | -0.0247 |  | LF | None | 2350 | 0.72 | 2350 | 0.72 | 1.06 | 1.22 | -0.010511 | 2350 | 0.72 | 2350 | 0.72 | 1.06 | 1.22 | -0.0105
LFNonePGEEUnExCZ02 | Com-Iltg-dWatt-LF_OSnone | PGE | EUn | Ex | CZ02 | 2.35 | 0.000439 | 0 | 2.6 | 0.00054 | -0.018 | 2.35 | 0.000439 | 0 | 2.6 | 0.00054 | -0.018 |  | LF | None | 2350 | 0.439 | 2350 | 0.439 | 1.11 | 1.23 | -0.0076596 | 2350 | 0.439 | 2350 | 0.439 | 1.11 | 1.23 | -0.00766
LFNonePGEEUnExCZ03 | Com-Iltg-dWatt-LF_OSnone | PGE | EUn | Ex | CZ03 | 2.35 | 0.000439 | 0 | 2.59 | 0.000522 | -0.0176 | 2.35 | 0.000439 | 0 | 2.59 | 0.000522 | -0.0176 |  | LF | None | 2350 | 0.439 | 2350 | 0.439 | 1.1 | 1.19 | -0.0074894 | 2350 | 0.439 | 2350 | 0.439 | 1.1 | 1.19 | -0.00749
LFNonePGEEUnExCZ04 | Com-Iltg-dWatt-LF_OSnone | PGE | EUn | Ex | CZ04 | 2.35 | 0.00072 | 0 | 2.63 | 0.000922 | -0.0141 | 2.35 | 0.00072 | 0 | 2.63 | 0.000922 | -0.0141 |  | LF | None | 2350 | 0.72 | 2350 | 0.72 | 1.12 | 1.28 | -0.006 | 2350 | 0.72 | 2350 | 0.72 | 1.12 | 1.28 | -0.006
LFNonePGEEUnExCZ05 | Com-Iltg-dWatt-LF_OSnone | PGE | EUn | Ex | CZ05 | 2.35 | 0.00072 | 0 | 2.58 | 0.000874 | -0.0168 | 2.35 | 0.00072 | 0 | 2.58 | 0.000874 | -0.0168 |  | LF | None | 2350 | 0.72 | 2350 | 0.72 | 1.1 | 1.21 | -0.0071489 | 2350 | 0.72 | 2350 | 0.72 | 1.1 | 1.21 | -0.00715
LFNonePGEEUnExCZ11 | Com-Iltg-dWatt-LF_OSnone | PGE | EUn | Ex | CZ11 | 2.35 | 0.000439 | 0 | 2.64 | 0.000547 | -0.0161 | 2.35 | 0.000439 | 0 | 2.64 | 0.000547 | -0.0161 |  | LF | None | 2350 | 0.439 | 2350 | 0.439 | 1.12 | 1.25 | -0.0068511 | 2350 | 0.439 | 2350 | 0.439 | 1.12 | 1.25 | -0.00685
LFNonePGEEUnExCZ12 | Com-Iltg-dWatt-LF_OSnone | PGE | EUn | Ex | CZ12 | 2.35 | 0.000439 | 0 | 2.63 | 0.000543 | -0.0162 | 2.35 | 0.000439 | 0 | 2.63 | 0.000543 | -0.0162 |  | LF | None | 2350 | 0.439 | 2350 | 0.439 | 1.12 | 1.24 | -0.0068936 | 2350 | 0.439 | 2350 | 0.439 | 1.12 | 1.24 | -0.00689
LFNonePGEEUnExCZ13 | Com-Iltg-dWatt-LF_OSnone | PGE | EUn | Ex | CZ13 | 2.35 | 0.000439 | 0 | 2.66 | 0.000556 | -0.0142 | 2.35 | 0.000439 | 0 | 2.66 | 0.000556 | -0.0142 |  | LF | None | 2350 | 0.439 | 2350 | 0.439 | 1.13 | 1.27 | -0.0060426 | 2350 | 0.439 | 2350 | 0.439 | 1.13 | 1.27 | -0.00604
LFNonePGEEUnExCZ16 | Com-Iltg-dWatt-LF_OSnone | PGE | EUn | Ex | CZ16 | 2.35 | 0.000439 | 0 | 2.51 | 0.000527 | -0.0256 | 2.35 | 0.000439 | 0 | 2.51 | 0.000527 | -0.0256 |  | LF | None | 2350 | 0.439 | 2350 | 0.439 | 1.07 | 1.2 | -0.010894 | 2350 | 0.439 | 2350 | 0.439 | 1.07 | 1.2 | -0.0109
LFNonePGEEUnExIOU | Com-Iltg-dWatt-LF_OSnone | PGE | EUn | Ex | IOU | 2.35 | 0.00049258 | 0 | 2.6099 | 0.00060464 | -0.016696 | 2.35 | 0.00049258 | 0 | 2.6099 | 0.00060464 | -0.016696 |  | LF | None | 2350 | 0.493 | 2350 | 0.493 | 1.11 | 1.23 | -0.0071048 | 2350 | 0.493 | 2350 | 0.493 | 1.11 | 1.23 | -0.0071
LFNonePGEEUnNewCZ01 | Com-Iltg-dWatt-LF_OSnone | PGE | EUn | New | CZ01 | 2.35 | 0.00072 | 0 | 2.48 | 0.000849 | -0.0193 | 2.35 | 0.00072 | 0 | 2.48 | 0.000849 | -0.0193 |  | LF | None | 2350 | 0.72 | 2350 | 0.72 | 1.06 | 1.18 | -0.0082128 | 2350 | 0.72 | 2350 | 0.72 | 1.06 | 1.18 | -0.00821
LFNonePGEEUnNewCZ02 | Com-Iltg-dWatt-LF_OSnone | PGE | EUn | New | CZ02 | 2.35 | 0.000439 | 0 | 2.63 | 0.000576 | -0.0139 | 2.35 | 0.000439 | 0 | 2.63 | 0.000576 | -0.0139 |  | LF | None | 2350 | 0.439 | 2350 | 0.439 | 1.12 | 1.31 | -0.0059149 | 2350 | 0.439 | 2350 | 0.439 | 1.12 | 1.31 | -0.00591
LFNonePGEEUnNewCZ03 | Com-Iltg-dWatt-LF_OSnone | PGE | EUn | New | CZ03 | 2.35 | 0.000439 | 0 | 2.57 | 0.000558 | -0.0132 | 2.35 | 0.000439 | 0 | 2.57 | 0.000558 | -0.0132 |  | LF | None | 2350 | 0.439 | 2350 | 0.439 | 1.09 | 1.27 | -0.005617 | 2350 | 0.439 | 2350 | 0.439 | 1.09 | 1.27 | -0.00562
LFNonePGEEUnNewCZ04 | Com-Iltg-dWatt-LF_OSnone | PGE | EUn | New | CZ04 | 2.35 | 0.00072 | 0 | 2.65 | 0.000908 | -0.0111 | 2.35 | 0.00072 | 0 | 2.65 | 0.000908 | -0.0111 |  | LF | None | 2350 | 0.72 | 2350 | 0.72 | 1.13 | 1.26 | -0.0047234 | 2350 | 0.72 | 2350 | 0.72 | 1.13 | 1.26 | -0.00472
LFNonePGEEUnNewCZ05 | Com-Iltg-dWatt-LF_OSnone | PGE | EUn | New | CZ05 | 2.35 | 0.00072 | 0 | 2.57 | 0.00087 | -0.0128 | 2.35 | 0.00072 | 0 | 2.57 | 0.00087 | -0.0128 |  | LF | None | 2350 | 0.72 | 2350 | 0.72 | 1.09 | 1.21 | -0.0054468 | 2350 | 0.72 | 2350 | 0.72 | 1.09 | 1.21 | -0.00545
LFNonePGEEUnNewCZ11 | Com-Iltg-dWatt-LF_OSnone | PGE | EUn | New | CZ11 | 2.35 | 0.000439 | 0 | 2.69 | 0.000577 | -0.0126 | 2.35 | 0.000439 | 0 | 2.69 | 0.000577 | -0.0126 |  | LF | None | 2350 | 0.439 | 2350 | 0.439 | 1.14 | 1.31 | -0.0053617 | 2350 | 0.439 | 2350 | 0.439 | 1.14 | 1.31 | -0.00536
LFNonePGEEUnNewCZ12 | Com-Iltg-dWatt-LF_OSnone | PGE | EUn | New | CZ12 | 2.35 | 0.000439 | 0 | 2.68 | 0.000577 | -0.0117 | 2.35 | 0.000439 | 0 | 2.68 | 0.000577 | -0.0117 |  | LF | None | 2350 | 0.439 | 2350 | 0.439 | 1.14 | 1.31 | -0.0049787 | 2350 | 0.439 | 2350 | 0.439 | 1.14 | 1.31 | -0.00498
LFNonePGEEUnNewCZ13 | Com-Iltg-dWatt-LF_OSnone | PGE | EUn | New | CZ13 | 2.35 | 0.000439 | 0 | 2.71 | 0.000576 | -0.0112 | 2.35 | 0.000439 | 0 | 2.71 | 0.000576 | -0.0112 |  | LF | None | 2350 | 0.439 | 2350 | 0.439 | 1.15 | 1.31 | -0.004766 | 2350 | 0.439 | 2350 | 0.439 | 1.15 | 1.31 | -0.00477
LFNonePGEEUnNewCZ16 | Com-Iltg-dWatt-LF_OSnone | PGE | EUn | New | CZ16 | 2.35 | 0.000439 | 0 | 2.53 | 0.000553 | -0.0225 | 2.35 | 0.000439 | 0 | 2.53 | 0.000553 | -0.0225 |  | LF | None | 2350 | 0.439 | 2350 | 0.439 | 1.08 | 1.26 | -0.0095745 | 2350 | 0.439 | 2350 | 0.439 | 1.08 | 1.26 | -0.00957
LFNonePGEEUnNewIOU | Com-Iltg-dWatt-LF_OSnone | PGE | EUn | New | IOU | 2.35 | 0.00049292 | 0 | 2.6365 | 0.000631 | -0.012478 | 2.35 | 0.00049292 | 0 | 2.6365 | 0.000631 | -0.012478 |  | LF | None | 2350 | 0.493 | 2350 | 0.493 | 1.12 | 1.28 | -0.00531 | 2350 | 0.493 | 2350 | 0.493 | 1.12 | 1.28 | -0.00531
LFNonePGEGroExCZ01 | Com-Iltg-dWatt-LF_OSnone | PGE | Gro | Ex | CZ01 | 4.91 | 0.00069 | 0 | 3.92 | 0.000685 | -0.0883 | 4.91 | 0.00069 | 0 | 3.92 | 0.000685 | -0.0883 |  | LF | None | 4910 | 0.69 | 4910 | 0.69 | 0.798 | 0.993 | -0.017984 | 4910 | 0.69 | 4910 | 0.69 | 0.798 | 0.993 | -0.018
LFNonePGEGroExCZ02 | Com-Iltg-dWatt-LF_OSnone | PGE | Gro | Ex | CZ02 | 4.91 | 0.00069 | 0 | 4.48 | 0.000893 | -0.0652 | 4.91 | 0.00069 | 0 | 4.48 | 0.000893 | -0.0652 |  | LF | None | 4910 | 0.69 | 4910 | 0.69 | 0.912 | 1.29 | -0.013279 | 4910 | 0.69 | 4910 | 0.69 | 0.912 | 1.29 | -0.0133
LFNonePGEGroExCZ03 | Com-Iltg-dWatt-LF_OSnone | PGE | Gro | Ex | CZ03 | 4.91 | 0.00069 | 0 | 4.28 | 0.000855 | -0.0746 | 4.91 | 0.00069 | 0 | 4.28 | 0.000855 | -0.0746 |  | LF | None | 4910 | 0.69 | 4910 | 0.69 | 0.872 | 1.24 | -0.015193 | 4910 | 0.69 | 4910 | 0.69 | 0.872 | 1.24 | -0.0152
LFNonePGEGroExCZ04 | Com-Iltg-dWatt-LF_OSnone | PGE | Gro | Ex | CZ04 | 4.91 | 0.00069 | 0 | 4.59 | 0.00088 | -0.0618 | 4.91 | 0.00069 | 0 | 4.59 | 0.00088 | -0.0618 |  | LF | None | 4910 | 0.69 | 4910 | 0.69 | 0.935 | 1.28 | -0.012587 | 4910 | 0.69 | 4910 | 0.69 | 0.935 | 1.28 | -0.0126
LFNonePGEGroExCZ05 | Com-Iltg-dWatt-LF_OSnone | PGE | Gro | Ex | CZ05 | 4.91 | 0.00069 | 0 | 4.25 | 0.000842 | -0.0746 | 4.91 | 0.00069 | 0 | 4.25 | 0.000842 | -0.0746 |  | LF | None | 4910 | 0.69 | 4910 | 0.69 | 0.866 | 1.22 | -0.015193 | 4910 | 0.69 | 4910 | 0.69 | 0.866 | 1.22 | -0.0152
LFNonePGEGroExCZ11 | Com-Iltg-dWatt-LF_OSnone | PGE | Gro | Ex | CZ11 | 4.91 | 0.00069 | 0 | 4.83 | 0.000909 | -0.053 | 4.91 | 0.00069 | 0 | 4.83 | 0.000909 | -0.053 |  | LF | None | 4910 | 0.69 | 4910 | 0.69 | 0.984 | 1.32 | -0.010794 | 4910 | 0.69 | 4910 | 0.69 | 0.984 | 1.32 | -0.0108
LFNonePGEGroExCZ12 | Com-Iltg-dWatt-LF_OSnone | PGE | Gro | Ex | CZ12 | 4.91 | 0.00069 | 0 | 4.73 | 0.000891 | -0.0574 | 4.91 | 0.00069 | 0 | 4.73 | 0.000891 | -0.0574 |  | LF | None | 4910 | 0.69 | 4910 | 0.69 | 0.963 | 1.29 | -0.01169 | 4910 | 0.69 | 4910 | 0.69 | 0.963 | 1.29 | -0.0117
LFNonePGEGroExCZ13 | Com-Iltg-dWatt-LF_OSnone | PGE | Gro | Ex | CZ13 | 4.91 | 0.00069 | 0 | 4.89 | 0.000891 | -0.05 | 4.91 | 0.00069 | 0 | 4.89 | 0.000891 | -0.05 |  | LF | None | 4910 | 0.69 | 4910 | 0.69 | 0.996 | 1.29 | -0.010183 | 4910 | 0.69 | 4910 | 0.69 | 0.996 | 1.29 | -0.0102
LFNonePGEGroExCZ16 | Com-Iltg-dWatt-LF_OSnone | PGE | Gro | Ex | CZ16 | 4.91 | 0.00069 | 0 | 4.29 | 0.000857 | -0.0697 | 4.91 | 0.00069 | 0 | 4.29 | 0.000857 | -0.0697 |  | LF | None | 4910 | 0.69 | 4910 | 0.69 | 0.874 | 1.24 | -0.014196 | 4910 | 0.69 | 4910 | 0.69 | 0.874 | 1.24 | -0.0142
LFNonePGEGroExIOU | Com-Iltg-dWatt-LF_OSnone | PGE | Gro | Ex | IOU | 4.91 | 0.00069 | 0 | 4.5734 | 0.00087706 | -0.062789 | 4.91 | 0.00069 | 0 | 4.5734 | 0.00087706 | -0.062789 |  | LF | None | 4910 | 0.69 | 4910 | 0.69 | 0.931 | 1.27 | -0.012788 | 4910 | 0.69 | 4910 | 0.69 | 0.931 | 1.27 | -0.0128
LFNonePGEGroNewCZ01 | Com-Iltg-dWatt-LF_OSnone | PGE | Gro | New | CZ01 | 4.91 | 0.00069 | 0 | 4.1 | 0.000782 | -0.0908 | 4.91 | 0.00069 | 0 | 4.1 | 0.000782 | -0.0908 |  | LF | None | 4910 | 0.69 | 4910 | 0.69 | 0.835 | 1.13 | -0.018493 | 4910 | 0.69 | 4910 | 0.69 | 0.835 | 1.13 | -0.0185
LFNonePGEGroNewCZ02 | Com-Iltg-dWatt-LF_OSnone | PGE | Gro | New | CZ02 | 4.91 | 0.00069 | 0 | 4.71 | 0.000925 | -0.0633 | 4.91 | 0.00069 | 0 | 4.71 | 0.000925 | -0.0633 |  | LF | None | 4910 | 0.69 | 4910 | 0.69 | 0.959 | 1.34 | -0.012892 | 4910 | 0.69 | 4910 | 0.69 | 0.959 | 1.34 | -0.0129
LFNonePGEGroNewCZ03 | Com-Iltg-dWatt-LF_OSnone | PGE | Gro | New | CZ03 | 4.91 | 0.00069 | 0 | 4.49 | 0.000874 | -0.0706 | 4.91 | 0.00069 | 0 | 4.49 | 0.000874 | -0.0706 |  | LF | None | 4910 | 0.69 | 4910 | 0.69 | 0.914 | 1.27 | -0.014379 | 4910 | 0.69 | 4910 | 0.69 | 0.914 | 1.27 | -0.0144
LFNonePGEGroNewCZ04 | Com-Iltg-dWatt-LF_OSnone | PGE | Gro | New | CZ04 | 4.91 | 0.00069 | 0 | 4.86 | 0.0009 | -0.0564 | 4.91 | 0.00069 | 0 | 4.86 | 0.0009 | -0.0564 |  | LF | None | 4910 | 0.69 | 4910 | 0.69 | 0.99 | 1.3 | -0.011487 | 4910 | 0.69 | 4910 | 0.69 | 0.99 | 1.3 | -0.0115
LFNonePGEGroNewCZ05 | Com-Iltg-dWatt-LF_OSnone | PGE | Gro | New | CZ05 | 4.91 | 0.00069 | 0 | 4.47 | 0.000854 | -0.0702 | 4.91 | 0.00069 | 0 | 4.47 | 0.000854 | -0.0702 |  | LF | None | 4910 | 0.69 | 4910 | 0.69 | 0.91 | 1.24 | -0.014297 | 4910 | 0.69 | 4910 | 0.69 | 0.91 | 1.24 | -0.0143
LFNonePGEGroNewCZ11 | Com-Iltg-dWatt-LF_OSnone | PGE | Gro | New | CZ11 | 4.91 | 0.00069 | 0 | 5.03 | 0.000947 | -0.0505 | 4.91 | 0.00069 | 0 | 5.03 | 0.000947 | -0.0505 |  | LF | None | 4910 | 0.69 | 4910 | 0.69 | 1.02 | 1.37 | -0.010285 | 4910 | 0.69 | 4910 | 0.69 | 1.02 | 1.37 | -0.0103
LFNonePGEGroNewCZ12 | Com-Iltg-dWatt-LF_OSnone | PGE | Gro | New | CZ12 | 4.91 | 0.00069 | 0 | 4.94 | 0.000933 | -0.0545 | 4.91 | 0.00069 | 0 | 4.94 | 0.000933 | -0.0545 |  | LF | None | 4910 | 0.69 | 4910 | 0.69 | 1.01 | 1.35 | -0.0111 | 4910 | 0.69 | 4910 | 0.69 | 1.01 | 1.35 | -0.0111
LFNonePGEGroNewCZ13 | Com-Iltg-dWatt-LF_OSnone | PGE | Gro | New | CZ13 | 4.91 | 0.00069 | 0 | 5.09 | 0.000929 | -0.0478 | 4.91 | 0.00069 | 0 | 5.09 | 0.000929 | -0.0478 |  | LF | None | 4910 | 0.69 | 4910 | 0.69 | 1.04 | 1.35 | -0.0097352 | 4910 | 0.69 | 4910 | 0.69 | 1.04 | 1.35 | -0.00974
LFNonePGEGroNewCZ16 | Com-Iltg-dWatt-LF_OSnone | PGE | Gro | New | CZ16 | 4.91 | 0.00069 | 0 | 4.49 | 0.000872 | -0.0662 | 4.91 | 0.00069 | 0 | 4.49 | 0.000872 | -0.0662 |  | LF | None | 4910 | 0.69 | 4910 | 0.69 | 0.914 | 1.26 | -0.013483 | 4910 | 0.69 | 4910 | 0.69 | 0.914 | 1.26 | -0.0135
LFNonePGEGroNewIOU | Com-Iltg-dWatt-LF_OSnone | PGE | Gro | New | IOU | 4.91 | 0.00069 | 0 | 4.8363 | 0.00091285 | -0.057755 | 4.91 | 0.00069 | 0 | 4.8363 | 0.00091285 | -0.057755 |  | LF | None | 4910 | 0.69 | 4910 | 0.69 | 0.985 | 1.32 | -0.011763 | 4910 | 0.69 | 4910 | 0.69 | 0.985 | 1.32 | -0.0118
LFNonePGEHspExCZ01 | Com-Iltg-dWatt-LF_OSnone | PGE | Hsp | Ex | CZ01 | 5.26 | 0.000827 | 0 | 5.65 | 0.000962 | -0.045 | 5.26 | 0.000827 | 0 | 5.65 | 0.000962 | -0.045 |  | LF | None | 5260 | 0.827 | 5260 | 0.827 | 1.07 | 1.16 | -0.0085551 | 5260 | 0.827 | 5260 | 0.827 | 1.07 | 1.16 | -0.00856
LFNonePGEHspExCZ02 | Com-Iltg-dWatt-LF_OSnone | PGE | Hsp | Ex | CZ02 | 5.26 | 0.000827 | 0 | 5.8 | 0.00103 | -0.0352 | 5.26 | 0.000827 | 0 | 5.8 | 0.00103 | -0.0352 |  | LF | None | 5260 | 0.827 | 5260 | 0.827 | 1.1 | 1.25 | -0.006692 | 5260 | 0.827 | 5260 | 0.827 | 1.1 | 1.25 | -0.00669
LFNonePGEHspExCZ03 | Com-Iltg-dWatt-LF_OSnone | PGE | Hsp | Ex | CZ03 | 5.26 | 0.000827 | 0 | 5.83 | 0.001 | -0.0332 | 5.26 | 0.000827 | 0 | 5.83 | 0.001 | -0.0332 |  | LF | None | 5260 | 0.827 | 5260 | 0.827 | 1.11 | 1.21 | -0.0063118 | 5260 | 0.827 | 5260 | 0.827 | 1.11 | 1.21 | -0.00631
LFNonePGEHspExCZ04 | Com-Iltg-dWatt-LF_OSnone | PGE | Hsp | Ex | CZ04 | 5.26 | 0.000827 | 0 | 5.83 | 0.00102 | -0.0315 | 5.26 | 0.000827 | 0 | 5.83 | 0.00102 | -0.0315 |  | LF | None | 5260 | 0.827 | 5260 | 0.827 | 1.11 | 1.23 | -0.0059886 | 5260 | 0.827 | 5260 | 0.827 | 1.11 | 1.23 | -0.00599
LFNonePGEHspExCZ05 | Com-Iltg-dWatt-LF_OSnone | PGE | Hsp | Ex | CZ05 | 5.26 | 0.000827 | 0 | 5.74 | 0.000983 | -0.0353 | 5.26 | 0.000827 | 0 | 5.74 | 0.000983 | -0.0353 |  | LF | None | 5260 | 0.827 | 5260 | 0.827 | 1.09 | 1.19 | -0.006711 | 5260 | 0.827 | 5260 | 0.827 | 1.09 | 1.19 | -0.00671
LFNonePGEHspExCZ11 | Com-Iltg-dWatt-LF_OSnone | PGE | Hsp | Ex | CZ11 | 5.26 | 0.000827 | 0 | 5.86 | 0.00103 | -0.0329 | 5.26 | 0.000827 | 0 | 5.86 | 0.00103 | -0.0329 |  | LF | None | 5260 | 0.827 | 5260 | 0.827 | 1.11 | 1.25 | -0.0062548 | 5260 | 0.827 | 5260 | 0.827 | 1.11 | 1.25 | -0.00625
LFNonePGEHspExCZ12 | Com-Iltg-dWatt-LF_OSnone | PGE | Hsp | Ex | CZ12 | 5.26 | 0.000827 | 0 | 5.84 | 0.00103 | -0.032 | 5.26 | 0.000827 | 0 | 5.84 | 0.00103 | -0.032 |  | LF | None | 5260 | 0.827 | 5260 | 0.827 | 1.11 | 1.25 | -0.0060837 | 5260 | 0.827 | 5260 | 0.827 | 1.11 | 1.25 | -0.00608
LFNonePGEHspExCZ13 | Com-Iltg-dWatt-LF_OSnone | PGE | Hsp | Ex | CZ13 | 5.26 | 0.000827 | 0 | 5.89 | 0.00103 | -0.0308 | 5.26 | 0.000827 | 0 | 5.89 | 0.00103 | -0.0308 |  | LF | None | 5260 | 0.827 | 5260 | 0.827 | 1.12 | 1.25 | -0.0058555 | 5260 | 0.827 | 5260 | 0.827 | 1.12 | 1.25 | -0.00586
LFNonePGEHspExCZ16 | Com-Iltg-dWatt-LF_OSnone | PGE | Hsp | Ex | CZ16 | 5.26 | 0.000827 | 0 | 5.56 | 0.000997 | -0.0504 | 5.26 | 0.000827 | 0 | 5.56 | 0.000997 | -0.0504 |  | LF | None | 5260 | 0.827 | 5260 | 0.827 | 1.06 | 1.21 | -0.0095817 | 5260 | 0.827 | 5260 | 0.827 | 1.06 | 1.21 | -0.00958
LFNonePGEHspExIOU | Com-Iltg-dWatt-LF_OSnone | PGE | Hsp | Ex | IOU | 5.26 | 0.000827 | 0 | 5.8364 | 0.0010182 | -0.032732 | 5.26 | 0.000827 | 0 | 5.8364 | 0.0010182 | -0.032732 |  | LF | None | 5260 | 0.827 | 5260 | 0.827 | 1.11 | 1.23 | -0.0062229 | 5260 | 0.827 | 5260 | 0.827 | 1.11 | 1.23 | -0.00622
LFNonePGEHspNewCZ01 | Com-Iltg-dWatt-LF_OSnone | PGE | Hsp | New | CZ01 | 5.26 | 0.000827 | 0 | 5.39 | 0.000932 | -0.0444 | 5.26 | 0.000827 | 0 | 5.39 | 0.000932 | -0.0444 |  | LF | None | 5260 | 0.827 | 5260 | 0.827 | 1.02 | 1.13 | -0.0084411 | 5260 | 0.827 | 5260 | 0.827 | 1.02 | 1.13 | -0.00844
LFNonePGEHspNewCZ02 | Com-Iltg-dWatt-LF_OSnone | PGE | Hsp | New | CZ02 | 5.26 | 0.000827 | 0 | 5.59 | 0.000994 | -0.0365 | 5.26 | 0.000827 | 0 | 5.59 | 0.000994 | -0.0365 |  | LF | None | 5260 | 0.827 | 5260 | 0.827 | 1.06 | 1.2 | -0.0069392 | 5260 | 0.827 | 5260 | 0.827 | 1.06 | 1.2 | -0.00694
LFNonePGEHspNewCZ03 | Com-Iltg-dWatt-LF_OSnone | PGE | Hsp | New | CZ03 | 5.26 | 0.000827 | 0 | 5.57 | 0.000969 | -0.033 | 5.26 | 0.000827 | 0 | 5.57 | 0.000969 | -0.033 |  | LF | None | 5260 | 0.827 | 5260 | 0.827 | 1.06 | 1.17 | -0.0062738 | 5260 | 0.827 | 5260 | 0.827 | 1.06 | 1.17 | -0.00627
LFNonePGEHspNewCZ04 | Com-Iltg-dWatt-LF_OSnone | PGE | Hsp | New | CZ04 | 5.26 | 0.000827 | 0 | 5.63 | 0.000985 | -0.0327 | 5.26 | 0.000827 | 0 | 5.63 | 0.000985 | -0.0327 |  | LF | None | 5260 | 0.827 | 5260 | 0.827 | 1.07 | 1.19 | -0.0062167 | 5260 | 0.827 | 5260 | 0.827 | 1.07 | 1.19 | -0.00622
LFNonePGEHspNewCZ05 | Com-Iltg-dWatt-LF_OSnone | PGE | Hsp | New | CZ05 | 5.26 | 0.000827 | 0 | 5.54 | 0.000958 | -0.0363 | 5.26 | 0.000827 | 0 | 5.54 | 0.000958 | -0.0363 |  | LF | None | 5260 | 0.827 | 5260 | 0.827 | 1.05 | 1.16 | -0.0069011 | 5260 | 0.827 | 5260 | 0.827 | 1.05 | 1.16 | -0.0069
LFNonePGEHspNewCZ11 | Com-Iltg-dWatt-LF_OSnone | PGE | Hsp | New | CZ11 | 5.26 | 0.000827 | 0 | 5.71 | 0.000998 | -0.0334 | 5.26 | 0.000827 | 0 | 5.71 | 0.000998 | -0.0334 |  | LF | None | 5260 | 0.827 | 5260 | 0.827 | 1.09 | 1.21 | -0.0063498 | 5260 | 0.827 | 5260 | 0.827 | 1.09 | 1.21 | -0.00635
LFNonePGEHspNewCZ12 | Com-Iltg-dWatt-LF_OSnone | PGE | Hsp | New | CZ12 | 5.26 | 0.000827 | 0 | 5.66 | 0.001 | -0.0329 | 5.26 | 0.000827 | 0 | 5.66 | 0.001 | -0.0329 |  | LF | None | 5260 | 0.827 | 5260 | 0.827 | 1.08 | 1.21 | -0.0062548 | 5260 | 0.827 | 5260 | 0.827 | 1.08 | 1.21 | -0.00625
LFNonePGEHspNewCZ13 | Com-Iltg-dWatt-LF_OSnone | PGE | Hsp | New | CZ13 | 5.26 | 0.000827 | 0 | 5.73 | 0.000998 | -0.0318 | 5.26 | 0.000827 | 0 | 5.73 | 0.000998 | -0.0318 |  | LF | None | 5260 | 0.827 | 5260 | 0.827 | 1.09 | 1.21 | -0.0060456 | 5260 | 0.827 | 5260 | 0.827 | 1.09 | 1.21 | -0.00605
LFNonePGEHspNewCZ16 | Com-Iltg-dWatt-LF_OSnone | PGE | Hsp | New | CZ16 | 5.26 | 0.000827 | 0 | 5.36 | 0.000966 | -0.0536 | 5.26 | 0.000827 | 0 | 5.36 | 0.000966 | -0.0536 |  | LF | None | 5260 | 0.827 | 5260 | 0.827 | 1.02 | 1.17 | -0.01019 | 5260 | 0.827 | 5260 | 0.827 | 1.02 | 1.17 | -0.0102
LFNonePGEHspNewIOU | Com-Iltg-dWatt-LF_OSnone | PGE | Hsp | New | IOU | 5.26 | 0.000827 | 0 | 5.6398 | 0.00098805 | -0.033286 | 5.26 | 0.000827 | 0 | 5.6398 | 0.00098805 | -0.033286 |  | LF | None | 5260 | 0.827 | 5260 | 0.827 | 1.07 | 1.19 | -0.0063282 | 5260 | 0.827 | 5260 | 0.827 | 1.07 | 1.19 | -0.00633
LFNonePGEHtlExCZ01 | Com-Iltg-dWatt-LF_OSnone | PGE | Htl | Ex | CZ01 | 1.95 | 0.000242 | 0 | 1.71 | 0.000294 | -0.012 | 1.95 | 0.000242 | 0 | 1.71 | 0.000294 | -0.012 |  | LF | None | 1950 | 0.242 | 1950 | 0.242 | 0.877 | 1.21 | -0.0061538 | 1950 | 0.242 | 1950 | 0.242 | 0.877 | 1.21 | -0.00615
LFNonePGEHtlExCZ02 | Com-Iltg-dWatt-LF_OSnone | PGE | Htl | Ex | CZ02 | 1.95 | 0.000242 | 0 | 1.89 | 0.000301 | -0.00859 | 1.95 | 0.000242 | 0 | 1.89 | 0.000301 | -0.00859 |  | LF | None | 1950 | 0.242 | 1950 | 0.242 | 0.969 | 1.24 | -0.0044051 | 1950 | 0.242 | 1950 | 0.242 | 0.969 | 1.24 | -0.00441
LFNonePGEHtlExCZ03 | Com-Iltg-dWatt-LF_OSnone | PGE | Htl | Ex | CZ03 | 1.95 | 0.000242 | 0 | 1.91 | 0.000298 | -0.00842 | 1.95 | 0.000242 | 0 | 1.91 | 0.000298 | -0.00842 |  | LF | None | 1950 | 0.242 | 1950 | 0.242 | 0.979 | 1.23 | -0.0043179 | 1950 | 0.242 | 1950 | 0.242 | 0.979 | 1.23 | -0.00432
LFNonePGEHtlExCZ04 | Com-Iltg-dWatt-LF_OSnone | PGE | Htl | Ex | CZ04 | 1.95 | 0.000242 | 0 | 1.97 | 0.0003 | -0.00697 | 1.95 | 0.000242 | 0 | 1.97 | 0.0003 | -0.00697 |  | LF | None | 1950 | 0.242 | 1950 | 0.242 | 1.01 | 1.24 | -0.0035744 | 1950 | 0.242 | 1950 | 0.242 | 1.01 | 1.24 | -0.00357
LFNonePGEHtlExCZ05 | Com-Iltg-dWatt-LF_OSnone | PGE | Htl | Ex | CZ05 | 1.95 | 0.000242 | 0 | 1.89 | 0.000295 | -0.00857 | 1.95 | 0.000242 | 0 | 1.89 | 0.000295 | -0.00857 |  | LF | None | 1950 | 0.242 | 1950 | 0.242 | 0.969 | 1.22 | -0.0043949 | 1950 | 0.242 | 1950 | 0.242 | 0.969 | 1.22 | -0.00439
LFNonePGEHtlExCZ11 | Com-Iltg-dWatt-LF_OSnone | PGE | Htl | Ex | CZ11 | 1.95 | 0.000242 | 0 | 1.98 | 0.000306 | -0.0073 | 1.95 | 0.000242 | 0 | 1.98 | 0.000306 | -0.0073 |  | LF | None | 1950 | 0.242 | 1950 | 0.242 | 1.02 | 1.26 | -0.0037436 | 1950 | 0.242 | 1950 | 0.242 | 1.02 | 1.26 | -0.00374
LFNonePGEHtlExCZ12 | Com-Iltg-dWatt-LF_OSnone | PGE | Htl | Ex | CZ12 | 1.95 | 0.000242 | 0 | 1.95 | 0.000305 | -0.00758 | 1.95 | 0.000242 | 0 | 1.95 | 0.000305 | -0.00758 |  | LF | None | 1950 | 0.242 | 1950 | 0.242 | 1 | 1.26 | -0.0038872 | 1950 | 0.242 | 1950 | 0.242 | 1 | 1.26 | -0.00389
LFNonePGEHtlExCZ13 | Com-Iltg-dWatt-LF_OSnone | PGE | Htl | Ex | CZ13 | 1.95 | 0.000242 | 0 | 2.01 | 0.000303 | -0.0068 | 1.95 | 0.000242 | 0 | 2.01 | 0.000303 | -0.0068 |  | LF | None | 1950 | 0.242 | 1950 | 0.242 | 1.03 | 1.25 | -0.0034872 | 1950 | 0.242 | 1950 | 0.242 | 1.03 | 1.25 | -0.00349
LFNonePGEHtlExCZ16 | Com-Iltg-dWatt-LF_OSnone | PGE | Htl | Ex | CZ16 | 1.95 | 0.000242 | 0 | 1.75 | 0.000295 | -0.0126 | 1.95 | 0.000242 | 0 | 1.75 | 0.000295 | -0.0126 |  | LF | None | 1950 | 0.242 | 1950 | 0.242 | 0.897 | 1.22 | -0.0064615 | 1950 | 0.242 | 1950 | 0.242 | 0.897 | 1.22 | -0.00646
LFNonePGEHtlExIOU | Com-Iltg-dWatt-LF_OSnone | PGE | Htl | Ex | IOU | 1.95 | 0.000242 | 0 | 1.9269 | 0.00029985 | -0.0080613 | 1.95 | 0.000242 | 0 | 1.9269 | 0.00029985 | -0.0080613 |  | LF | None | 1950 | 0.242 | 1950 | 0.242 | 0.988 | 1.24 | -0.004134 | 1950 | 0.242 | 1950 | 0.242 | 0.988 | 1.24 | -0.00413
LFNonePGEHtlNewCZ01 | Com-Iltg-dWatt-LF_OSnone | PGE | Htl | New | CZ01 | 1.95 | 0.000242 | 0 | 1.63 | 0.000288 | -0.015 | 1.95 | 0.000242 | 0 | 1.63 | 0.000288 | -0.015 |  | LF | None | 1950 | 0.242 | 1950 | 0.242 | 0.836 | 1.19 | -0.0076923 | 1950 | 0.242 | 1950 | 0.242 | 0.836 | 1.19 | -0.00769
LFNonePGEHtlNewCZ02 | Com-Iltg-dWatt-LF_OSnone | PGE | Htl | New | CZ02 | 1.95 | 0.000242 | 0 | 1.85 | 0.000309 | -0.0108 | 1.95 | 0.000242 | 0 | 1.85 | 0.000309 | -0.0108 |  | LF | None | 1950 | 0.242 | 1950 | 0.242 | 0.949 | 1.28 | -0.0055385 | 1950 | 0.242 | 1950 | 0.242 | 0.949 | 1.28 | -0.00554
LFNonePGEHtlNewCZ03 | Com-Iltg-dWatt-LF_OSnone | PGE | Htl | New | CZ03 | 1.95 | 0.000242 | 0 | 1.84 | 0.000299 | -0.0102 | 1.95 | 0.000242 | 0 | 1.84 | 0.000299 | -0.0102 |  | LF | None | 1950 | 0.242 | 1950 | 0.242 | 0.944 | 1.24 | -0.0052308 | 1950 | 0.242 | 1950 | 0.242 | 0.944 | 1.24 | -0.00523
LFNonePGEHtlNewCZ04 | Com-Iltg-dWatt-LF_OSnone | PGE | Htl | New | CZ04 | 1.95 | 0.000242 | 0 | 1.93 | 0.000305 | -0.00877 | 1.95 | 0.000242 | 0 | 1.93 | 0.000305 | -0.00877 |  | LF | None | 1950 | 0.242 | 1950 | 0.242 | 0.99 | 1.26 | -0.0044974 | 1950 | 0.242 | 1950 | 0.242 | 0.99 | 1.26 | -0.0045
LFNonePGEHtlNewCZ05 | Com-Iltg-dWatt-LF_OSnone | PGE | Htl | New | CZ05 | 1.95 | 0.000242 | 0 | 1.83 | 0.000297 | -0.0105 | 1.95 | 0.000242 | 0 | 1.83 | 0.000297 | -0.0105 |  | LF | None | 1950 | 0.242 | 1950 | 0.242 | 0.938 | 1.23 | -0.0053846 | 1950 | 0.242 | 1950 | 0.242 | 0.938 | 1.23 | -0.00538
LFNonePGEHtlNewCZ11 | Com-Iltg-dWatt-LF_OSnone | PGE | Htl | New | CZ11 | 1.95 | 0.000242 | 0 | 1.96 | 0.000311 | -0.00939 | 1.95 | 0.000242 | 0 | 1.96 | 0.000311 | -0.00939 |  | LF | None | 1950 | 0.242 | 1950 | 0.242 | 1.01 | 1.29 | -0.0048154 | 1950 | 0.242 | 1950 | 0.242 | 1.01 | 1.29 | -0.00482
LFNonePGEHtlNewCZ12 | Com-Iltg-dWatt-LF_OSnone | PGE | Htl | New | CZ12 | 1.95 | 0.000242 | 0 | 1.93 | 0.00031 | -0.00941 | 1.95 | 0.000242 | 0 | 1.93 | 0.00031 | -0.00941 |  | LF | None | 1950 | 0.242 | 1950 | 0.242 | 0.99 | 1.28 | -0.0048256 | 1950 | 0.242 | 1950 | 0.242 | 0.99 | 1.28 | -0.00483
LFNonePGEHtlNewCZ13 | Com-Iltg-dWatt-LF_OSnone | PGE | Htl | New | CZ13 | 1.95 | 0.000242 | 0 | 1.98 | 0.000307 | -0.00859 | 1.95 | 0.000242 | 0 | 1.98 | 0.000307 | -0.00859 |  | LF | None | 1950 | 0.242 | 1950 | 0.242 | 1.02 | 1.27 | -0.0044051 | 1950 | 0.242 | 1950 | 0.242 | 1.02 | 1.27 | -0.00441
LFNonePGEHtlNewCZ16 | Com-Iltg-dWatt-LF_OSnone | PGE | Htl | New | CZ16 | 1.95 | 0.000242 | 0 | 1.72 | 0.000297 | -0.0158 | 1.95 | 0.000242 | 0 | 1.72 | 0.000297 | -0.0158 |  | LF | None | 1950 | 0.242 | 1950 | 0.242 | 0.882 | 1.23 | -0.0081026 | 1950 | 0.242 | 1950 | 0.242 | 0.882 | 1.23 | -0.0081
LFNonePGEHtlNewIOU | Com-Iltg-dWatt-LF_OSnone | PGE | Htl | New | IOU | 1.95 | 0.000242 | 0 | 1.8909 | 0.00030434 | -0.0098311 | 1.95 | 0.000242 | 0 | 1.8909 | 0.00030434 | -0.0098311 |  | LF | None | 1950 | 0.242 | 1950 | 0.242 | 0.97 | 1.26 | -0.0050416 | 1950 | 0.242 | 1950 | 0.242 | 0.97 | 1.26 | -0.00504
LFNonePGEMBTExCZ01 | Com-Iltg-dWatt-LF_OSnone | PGE | MBT | Ex | CZ01 | 3.53 | 0.000851 | 0 | 3.81 | 0.00102 | -0.00441 | 3.53 | 0.000851 | 0 | 3.81 | 0.00102 | -0.00441 |  | LF | None | 3530 | 0.851 | 3530 | 0.851 | 1.08 | 1.2 | -0.0012493 | 3530 | 0.851 | 3530 | 0.851 | 1.08 | 1.2 | -0.00125
LFNonePGEMBTExCZ02 | Com-Iltg-dWatt-LF_OSnone | PGE | MBT | Ex | CZ02 | 3.53 | 0.000851 | 0 | 3.92 | 0.00101 | -0.00221 | 3.53 | 0.000851 | 0 | 3.92 | 0.00101 | -0.00221 |  | LF | None | 3530 | 0.851 | 3530 | 0.851 | 1.11 | 1.19 | -0.00062606 | 3530 | 0.851 | 3530 | 0.851 | 1.11 | 1.19 | -0.000626
LFNonePGEMBTExCZ03 | Com-Iltg-dWatt-LF_OSnone | PGE | MBT | Ex | CZ03 | 3.53 | 0.000851 | 0 | 3.95 | 0.00101 | -0.00193 | 3.53 | 0.000851 | 0 | 3.95 | 0.00101 | -0.00193 |  | LF | None | 3530 | 0.851 | 3530 | 0.851 | 1.12 | 1.19 | -0.00054674 | 3530 | 0.851 | 3530 | 0.851 | 1.12 | 1.19 | -0.000547
LFNonePGEMBTExCZ04 | Com-Iltg-dWatt-LF_OSnone | PGE | MBT | Ex | CZ04 | 3.53 | 0.000851 | 0 | 3.95 | 0.00103 | -0.00149 | 3.53 | 0.000851 | 0 | 3.95 | 0.00103 | -0.00149 |  | LF | None | 3530 | 0.851 | 3530 | 0.851 | 1.12 | 1.21 | -0.0004221 | 3530 | 0.851 | 3530 | 0.851 | 1.12 | 1.21 | -0.000422
LFNonePGEMBTExCZ05 | Com-Iltg-dWatt-LF_OSnone | PGE | MBT | Ex | CZ05 | 3.53 | 0.000851 | 0 | 3.92 | 0.00102 | -0.00146 | 3.53 | 0.000851 | 0 | 3.92 | 0.00102 | -0.00146 |  | LF | None | 3530 | 0.851 | 3530 | 0.851 | 1.11 | 1.2 | -0.0004136 | 3530 | 0.851 | 3530 | 0.851 | 1.11 | 1.2 | -0.000414
LFNonePGEMBTExCZ11 | Com-Iltg-dWatt-LF_OSnone | PGE | MBT | Ex | CZ11 | 3.53 | 0.000851 | 0 | 3.94 | 0.00103 | -0.00232 | 3.53 | 0.000851 | 0 | 3.94 | 0.00103 | -0.00232 |  | LF | None | 3530 | 0.851 | 3530 | 0.851 | 1.12 | 1.21 | -0.00065722 | 3530 | 0.851 | 3530 | 0.851 | 1.12 | 1.21 | -0.000657
LFNonePGEMBTExCZ12 | Com-Iltg-dWatt-LF_OSnone | PGE | MBT | Ex | CZ12 | 3.53 | 0.000851 | 0 | 3.93 | 0.00101 | -0.00232 | 3.53 | 0.000851 | 0 | 3.93 | 0.00101 | -0.00232 |  | LF | None | 3530 | 0.851 | 3530 | 0.851 | 1.11 | 1.19 | -0.00065722 | 3530 | 0.851 | 3530 | 0.851 | 1.11 | 1.19 | -0.000657
LFNonePGEMBTExCZ13 | Com-Iltg-dWatt-LF_OSnone | PGE | MBT | Ex | CZ13 | 3.53 | 0.000851 | 0 | 3.95 | 0.00101 | -0.00208 | 3.53 | 0.000851 | 0 | 3.95 | 0.00101 | -0.00208 |  | LF | None | 3530 | 0.851 | 3530 | 0.851 | 1.12 | 1.19 | -0.00058924 | 3530 | 0.851 | 3530 | 0.851 | 1.12 | 1.19 | -0.000589
LFNonePGEMBTExCZ16 | Com-Iltg-dWatt-LF_OSnone | PGE | MBT | Ex | CZ16 | 3.53 | 0.000851 | 0 | 3.77 | 0.000989 | -0.00988 | 3.53 | 0.000851 | 0 | 3.77 | 0.000989 | -0.00988 |  | LF | None | 3530 | 0.851 | 3530 | 0.851 | 1.07 | 1.16 | -0.0027989 | 3530 | 0.851 | 3530 | 0.851 | 1.07 | 1.16 | -0.0028
LFNonePGEMBTExIOU | Com-Iltg-dWatt-LF_OSnone | PGE | MBT | Ex | IOU | 3.53 | 0.000851 | 0 | 3.94 | 0.0010147 | -0.0020744 | 3.53 | 0.000851 | 0 | 3.94 | 0.0010147 | -0.0020744 |  | LF | None | 3530 | 0.851 | 3530 | 0.851 | 1.12 | 1.19 | -0.00058765 | 3530 | 0.851 | 3530 | 0.851 | 1.12 | 1.19 | -0.000588
LFNonePGEMBTNewCZ01 | Com-Iltg-dWatt-LF_OSnone | PGE | MBT | New | CZ01 | 3.53 | 0.000851 | 0 | 3.62 | 0.000976 | -0.00381 | 3.53 | 0.000851 | 0 | 3.62 | 0.000976 | -0.00381 |  | LF | None | 3530 | 0.851 | 3530 | 0.851 | 1.03 | 1.15 | -0.0010793 | 3530 | 0.851 | 3530 | 0.851 | 1.03 | 1.15 | -0.00108
LFNonePGEMBTNewCZ02 | Com-Iltg-dWatt-LF_OSnone | PGE | MBT | New | CZ02 | 3.53 | 0.000851 | 0 | 3.77 | 0.00105 | -0.00192 | 3.53 | 0.000851 | 0 | 3.77 | 0.00105 | -0.00192 |  | LF | None | 3530 | 0.851 | 3530 | 0.851 | 1.07 | 1.23 | -0.00054391 | 3530 | 0.851 | 3530 | 0.851 | 1.07 | 1.23 | -0.000544
LFNonePGEMBTNewCZ03 | Com-Iltg-dWatt-LF_OSnone | PGE | MBT | New | CZ03 | 3.53 | 0.000851 | 0 | 3.74 | 0.00102 | -0.00179 | 3.53 | 0.000851 | 0 | 3.74 | 0.00102 | -0.00179 |  | LF | None | 3530 | 0.851 | 3530 | 0.851 | 1.06 | 1.2 | -0.00050708 | 3530 | 0.851 | 3530 | 0.851 | 1.06 | 1.2 | -0.000507
LFNonePGEMBTNewCZ04 | Com-Iltg-dWatt-LF_OSnone | PGE | MBT | New | CZ04 | 3.53 | 0.000851 | 0 | 3.81 | 0.00105 | -0.00143 | 3.53 | 0.000851 | 0 | 3.81 | 0.00105 | -0.00143 |  | LF | None | 3530 | 0.851 | 3530 | 0.851 | 1.08 | 1.23 | -0.0004051 | 3530 | 0.851 | 3530 | 0.851 | 1.08 | 1.23 | -0.000405
LFNonePGEMBTNewCZ05 | Com-Iltg-dWatt-LF_OSnone | PGE | MBT | New | CZ05 | 3.53 | 0.000851 | 0 | 3.76 | 0.00101 | -0.000914 | 3.53 | 0.000851 | 0 | 3.76 | 0.00101 | -0.000914 | 0.97095 | LF | None | 3530 | 0.851 | 3530 | 0.851 | 1.07 | 1.19 | -0.00025892 | 3530 | 0.851 | 3530 | 0.851 | 1.07 | 1.19 | -0.000259
LFNonePGEMBTNewCZ11 | Com-Iltg-dWatt-LF_OSnone | PGE | MBT | New | CZ11 | 3.53 | 0.000851 | 0 | 3.85 | 0.00106 | -0.00166 | 3.53 | 0.000851 | 0 | 3.85 | 0.00106 | -0.00166 |  | LF | None | 3530 | 0.851 | 3530 | 0.851 | 1.09 | 1.25 | -0.00047025 | 3530 | 0.851 | 3530 | 0.851 | 1.09 | 1.25 | -0.00047
LFNonePGEMBTNewCZ12 | Com-Iltg-dWatt-LF_OSnone | PGE | MBT | New | CZ12 | 3.53 | 0.000851 | 0 | 3.82 | 0.00106 | -0.00172 | 3.53 | 0.000851 | 0 | 3.82 | 0.00106 | -0.00172 | 76 | LF | None | 3530 | 0.851 | 3530 | 0.851 | 1.08 | 1.25 | -0.00048725 | 3530 | 0.851 | 3530 | 0.851 | 1.08 | 1.25 | -0.000487
LFNonePGEMBTNewCZ13 | Com-Iltg-dWatt-LF_OSnone | PGE | MBT | New | CZ13 | 3.53 | 0.000851 | 0 | 3.86 | 0.00105 | -0.00159 | 3.53 | 0.000851 | 0 | 3.86 | 0.00105 | -0.00159 | 2540 | LF | None | 3530 | 0.851 | 3530 | 0.851 | 1.09 | 1.23 | -0.00045042 | 3530 | 0.851 | 3530 | 0.851 | 1.09 | 1.23 | -0.00045
LFNonePGEMBTNewCZ16 | Com-Iltg-dWatt-LF_OSnone | PGE | MBT | New | CZ16 | 3.53 | 0.000851 | 0 | 3.7 | 0.00102 | -0.00674 | 3.53 | 0.000851 | 0 | 3.7 | 0.00102 | -0.00674 | 2616 | LF | None | 3530 | 0.851 | 3530 | 0.851 | 1.05 | 1.2 | -0.0019093 | 3530 | 0.851 | 3530 | 0.851 | 1.05 | 1.2 | -0.00191
LFNonePGEMBTNewIOU | Com-Iltg-dWatt-LF_OSnone | PGE | MBT | New | IOU | 3.53 | 0.000851 | 0 | 3.8009 | 0.0010441 | -0.0017389 | 3.53 | 0.000851 | 0 | 3.8009 | 0.0010441 | -0.0017389 | 2.616 | LF | None | 3530 | 0.851 | 3530 | 0.851 | 1.08 | 1.23 | -0.00049261 | 3530 | 0.851 | 3530 | 0.851 | 1.08 | 1.23 | -0.000493
LFNonePGEMLIExCZ01 | Com-Iltg-dWatt-LF_OSnone | PGE | MLI | Ex | CZ01 | 3.22 | 0.000924 | 0 | 3.11 | 0.00107 | -0.0389 | 3.22 | 0.000924 | 0 | 3.11 | 0.00107 | -0.0389 | 0 | LF | None | 3220 | 0.924 | 3220 | 0.924 | 0.966 | 1.16 | -0.012081 | 3220 | 0.924 | 3220 | 0.924 | 0.966 | 1.16 | -0.0121
LFNonePGEMLIExCZ02 | Com-Iltg-dWatt-LF_OSnone | PGE | MLI | Ex | CZ02 | 3.22 | 0.000924 | 0 | 3.34 | 0.00108 | -0.0199 | 3.22 | 0.000924 | 0 | 3.34 | 0.00108 | -0.0199 | 1 | LF | None | 3220 | 0.924 | 3220 | 0.924 | 1.04 | 1.17 | -0.0061801 | 3220 | 0.924 | 3220 | 0.924 | 1.04 | 1.17 | -0.00618
LFNonePGEMLIExCZ03 | Com-Iltg-dWatt-LF_OSnone | PGE | MLI | Ex | CZ03 | 3.22 | 0.000924 | 0 | 3.33 | 0.00108 | -0.0187 | 3.22 | 0.000924 | 0 | 3.33 | 0.00108 | -0.0187 | 1 | LF | None | 3220 | 0.924 | 3220 | 0.924 | 1.03 | 1.17 | -0.0058075 | 3220 | 0.924 | 3220 | 0.924 | 1.03 | 1.17 | -0.00581
LFNonePGEMLIExCZ04 | Com-Iltg-dWatt-LF_OSnone | PGE | MLI | Ex | CZ04 | 3.22 | 0.000924 | 0 | 3.37 | 0.00108 | -0.0151 | 3.22 | 0.000924 | 0 | 3.37 | 0.00108 | -0.0151 | 1 | LF | None | 3220 | 0.924 | 3220 | 0.924 | 1.05 | 1.17 | -0.0046894 | 3220 | 0.924 | 3220 | 0.924 | 1.05 | 1.17 | -0.00469
LFNonePGEMLIExCZ05 | Com-Iltg-dWatt-LF_OSnone | PGE | MLI | Ex | CZ05 | 3.22 | 0.000924 | 0 | 3.32 | 0.00108 | -0.0173 | 3.22 | 0.000924 | 0 | 3.32 | 0.00108 | -0.0173 | 3530 | LF | None | 3220 | 0.924 | 3220 | 0.924 | 1.03 | 1.17 | -0.0053727 | 3220 | 0.924 | 3220 | 0.924 | 1.03 | 1.17 | -0.00537
LFNonePGEMLIExCZ11 | Com-Iltg-dWatt-LF_OSnone | PGE | MLI | Ex | CZ11 | 3.22 | 0.000924 | 0 | 3.36 | 0.00108 | -0.0199 | 3.22 | 0.000924 | 0 | 3.36 | 0.00108 | -0.0199 |  | LF | None | 3220 | 0.924 | 3220 | 0.924 | 1.04 | 1.17 | -0.0061801 | 3220 | 0.924 | 3220 | 0.924 | 1.04 | 1.17 | -0.00618
LFNonePGEMLIExCZ12 | Com-Iltg-dWatt-LF_OSnone | PGE | MLI | Ex | CZ12 | 3.22 | 0.000924 | 0 | 3.35 | 0.00109 | -0.0196 | 3.22 | 0.000924 | 0 | 3.35 | 0.00109 | -0.0196 | 3530 | LF | None | 3220 | 0.924 | 3220 | 0.924 | 1.04 | 1.18 | -0.006087 | 3220 | 0.924 | 3220 | 0.924 | 1.04 | 1.18 | -0.00609
LFNonePGEMLIExCZ13 | Com-Iltg-dWatt-LF_OSnone | PGE | MLI | Ex | CZ13 | 3.22 | 0.000924 | 0 | 3.39 | 0.00107 | -0.0175 | 3.22 | 0.000924 | 0 | 3.39 | 0.00107 | -0.0175 |  | LF | None | 3220 | 0.924 | 3220 | 0.924 | 1.05 | 1.16 | -0.0054348 | 3220 | 0.924 | 3220 | 0.924 | 1.05 | 1.16 | -0.00543
LFNonePGEMLIExCZ16 | Com-Iltg-dWatt-LF_OSnone | PGE | MLI | Ex | CZ16 | 3.22 | 0.000924 | 0 | 3.16 | 0.00106 | -0.0396 | 3.22 | 0.000924 | 0 | 3.16 | 0.00106 | -0.0396 |  | LF | None | 3220 | 0.924 | 3220 | 0.924 | 0.981 | 1.15 | -0.012298 | 3220 | 0.924 | 3220 | 0.924 | 0.981 | 1.15 | -0.0123
LFNonePGEMLIExIOU | Com-Iltg-dWatt-LF_OSnone | PGE | MLI | Ex | IOU | 3.22 | 0.000924 | 0 | 3.3471 | 0.0010804 | -0.018546 | 3.22 | 0.000924 | 0 | 3.3471 | 0.0010804 | -0.018546 |  | LF | None | 3220 | 0.924 | 3220 | 0.924 | 1.04 | 1.17 | -0.0057595 | 3220 | 0.924 | 3220 | 0.924 | 1.04 | 1.17 | -0.00576
LFNonePGEMLINewCZ01 | Com-Iltg-dWatt-LF_OSnone | PGE | MLI | New | CZ01 | 3.22 | 0.000924 | 0 | 3.07 | 0.000998 | -0.0425 | 3.22 | 0.000924 | 0 | 3.07 | 0.000998 | -0.0425 |  | LF | None | 3220 | 0.924 | 3220 | 0.924 | 0.953 | 1.08 | -0.013199 | 3220 | 0.924 | 3220 | 0.924 | 0.953 | 1.08 | -0.0132
LFNonePGEMLINewCZ02 | Com-Iltg-dWatt-LF_OSnone | PGE | MLI | New | CZ02 | 3.22 | 0.000924 | 0 | 3.3 | 0.00111 | -0.0231 | 3.22 | 0.000924 | 0 | 3.3 | 0.00111 | -0.0231 |  | LF | None | 3220 | 0.924 | 3220 | 0.924 | 1.02 | 1.2 | -0.0071739 | 3220 | 0.924 | 3220 | 0.924 | 1.02 | 1.2 | -0.00717
LFNonePGEMLINewCZ03 | Com-Iltg-dWatt-LF_OSnone | PGE | MLI | New | CZ03 | 3.22 | 0.000924 | 0 | 3.22 | 0.00107 | -0.0215 | 3.22 | 0.000924 | 0 | 3.22 | 0.00107 | -0.0215 |  | LF | None | 3220 | 0.924 | 3220 | 0.924 | 1 | 1.16 | -0.006677 | 3220 | 0.924 | 3220 | 0.924 | 1 | 1.16 | -0.00668
LFNonePGEMLINewCZ04 | Com-Iltg-dWatt-LF_OSnone | PGE | MLI | New | CZ04 | 3.22 | 0.000924 | 0 | 3.34 | 0.00109 | -0.0176 | 3.22 | 0.000924 | 0 | 3.34 | 0.00109 | -0.0176 |  | LF | None | 3220 | 0.924 | 3220 | 0.924 | 1.04 | 1.18 | -0.0054658 | 3220 | 0.924 | 3220 | 0.924 | 1.04 | 1.18 | -0.00547
LFNonePGEMLINewCZ05 | Com-Iltg-dWatt-LF_OSnone | PGE | MLI | New | CZ05 | 3.22 | 0.000924 | 0 | 3.22 | 0.00106 | -0.0211 | 3.22 | 0.000924 | 0 | 3.22 | 0.00106 | -0.0211 |  | LF | None | 3220 | 0.924 | 3220 | 0.924 | 1 | 1.15 | -0.0065528 | 3220 | 0.924 | 3220 | 0.924 | 1 | 1.15 | -0.00655
LFNonePGEMLINewCZ11 | Com-Iltg-dWatt-LF_OSnone | PGE | MLI | New | CZ11 | 3.22 | 0.000924 | 0 | 3.42 | 0.00114 | -0.0191 | 3.22 | 0.000924 | 0 | 3.42 | 0.00114 | -0.0191 |  | LF | None | 3220 | 0.924 | 3220 | 0.924 | 1.06 | 1.23 | -0.0059317 | 3220 | 0.924 | 3220 | 0.924 | 1.06 | 1.23 | -0.00593
LFNonePGEMLINewCZ12 | Com-Iltg-dWatt-LF_OSnone | PGE | MLI | New | CZ12 | 3.22 | 0.000924 | 0 | 3.38 | 0.00114 | -0.0216 | 3.22 | 0.000924 | 0 | 3.38 | 0.00114 | -0.0216 |  | LF | None | 3220 | 0.924 | 3220 | 0.924 | 1.05 | 1.23 | -0.0067081 | 3220 | 0.924 | 3220 | 0.924 | 1.05 | 1.23 | -0.00671
LFNonePGEMLINewCZ13 | Com-Iltg-dWatt-LF_OSnone | PGE | MLI | New | CZ13 | 3.22 | 0.000924 | 0 | 3.44 | 0.00114 | -0.0178 | 3.22 | 0.000924 | 0 | 3.44 | 0.00114 | -0.0178 |  | LF | None | 3220 | 0.924 | 3220 | 0.924 | 1.07 | 1.23 | -0.005528 | 3220 | 0.924 | 3220 | 0.924 | 1.07 | 1.23 | -0.00553
LFNonePGEMLINewCZ16 | Com-Iltg-dWatt-LF_OSnone | PGE | MLI | New | CZ16 | 3.22 | 0.000924 | 0 | 3.2 | 0.00107 | -0.0389 | 3.22 | 0.000924 | 0 | 3.2 | 0.00107 | -0.0389 |  | LF | None | 3220 | 0.924 | 3220 | 0.924 | 0.994 | 1.16 | -0.012081 | 3220 | 0.924 | 3220 | 0.924 | 0.994 | 1.16 | -0.0121
LFNonePGEMLINewIOU | Com-Iltg-dWatt-LF_OSnone | PGE | MLI | New | IOU | 3.22 | 0.000924 | 0 | 3.3352 | 0.0011089 | -0.020505 | 3.22 | 0.000924 | 0 | 3.3352 | 0.0011089 | -0.020505 |  | LF | None | 3220 | 0.924 | 3220 | 0.924 | 1.04 | 1.2 | -0.0063682 | 3220 | 0.924 | 3220 | 0.924 | 1.04 | 1.2 | -0.00637
LFNonePGEMtlExCZ01 | Com-Iltg-dWatt-LF_OSnone | PGE | Mtl | Ex | CZ01 | 1.55 | 0.000172 | 0 | 1.48 | 0.000205 | -0.0154 | 1.55 | 0.000172 | 0 | 1.48 | 0.000205 | -0.0154 |  | LF | None | 1550 | 0.172 | 1550 | 0.172 | 0.955 | 1.19 | -0.0099355 | 1550 | 0.172 | 1550 | 0.172 | 0.955 | 1.19 | -0.00994
LFNonePGEMtlExCZ02 | Com-Iltg-dWatt-LF_OSnone | PGE | Mtl | Ex | CZ02 | 1.55 | 0.000172 | 0 | 1.58 | 0.000213 | -0.0102 | 1.55 | 0.000172 | 0 | 1.58 | 0.000213 | -0.0102 |  | LF | None | 1550 | 0.172 | 1550 | 0.172 | 1.02 | 1.24 | -0.0065806 | 1550 | 0.172 | 1550 | 0.172 | 1.02 | 1.24 | -0.00658
LFNonePGEMtlExCZ03 | Com-Iltg-dWatt-LF_OSnone | PGE | Mtl | Ex | CZ03 | 1.55 | 0.000172 | 0 | 1.6 | 0.000208 | -0.00993 | 1.55 | 0.000172 | 0 | 1.6 | 0.000208 | -0.00993 |  | LF | None | 1550 | 0.172 | 1550 | 0.172 | 1.03 | 1.21 | -0.0064065 | 1550 | 0.172 | 1550 | 0.172 | 1.03 | 1.21 | -0.00641
LFNonePGEMtlExCZ04 | Com-Iltg-dWatt-LF_OSnone | PGE | Mtl | Ex | CZ04 | 1.55 | 0.000172 | 0 | 1.63 | 0.000211 | -0.00829 | 1.55 | 0.000172 | 0 | 1.63 | 0.000211 | -0.00829 |  | LF | None | 1550 | 0.172 | 1550 | 0.172 | 1.05 | 1.23 | -0.0053484 | 1550 | 0.172 | 1550 | 0.172 | 1.05 | 1.23 | -0.00535
LFNonePGEMtlExCZ05 | Com-Iltg-dWatt-LF_OSnone | PGE | Mtl | Ex | CZ05 | 1.55 | 0.000172 | 0 | 1.58 | 0.000207 | -0.0106 | 1.55 | 0.000172 | 0 | 1.58 | 0.000207 | -0.0106 |  | LF | None | 1550 | 0.172 | 1550 | 0.172 | 1.02 | 1.2 | -0.0068387 | 1550 | 0.172 | 1550 | 0.172 | 1.02 | 1.2 | -0.00684
LFNonePGEMtlExCZ11 | Com-Iltg-dWatt-LF_OSnone | PGE | Mtl | Ex | CZ11 | 1.55 | 0.000172 | 0 | 1.64 | 0.000215 | -0.00858 | 1.55 | 0.000172 | 0 | 1.64 | 0.000215 | -0.00858 |  | LF | None | 1550 | 0.172 | 1550 | 0.172 | 1.06 | 1.25 | -0.0055355 | 1550 | 0.172 | 1550 | 0.172 | 1.06 | 1.25 | -0.00554
LFNonePGEMtlExCZ12 | Com-Iltg-dWatt-LF_OSnone | PGE | Mtl | Ex | CZ12 | 1.55 | 0.000172 | 0 | 1.62 | 0.000214 | -0.00903 | 1.55 | 0.000172 | 0 | 1.62 | 0.000214 | -0.00903 |  | LF | None | 1550 | 0.172 | 1550 | 0.172 | 1.05 | 1.24 | -0.0058258 | 1550 | 0.172 | 1550 | 0.172 | 1.05 | 1.24 | -0.00583
LFNonePGEMtlExCZ13 | Com-Iltg-dWatt-LF_OSnone | PGE | Mtl | Ex | CZ13 | 1.55 | 0.000172 | 0 | 1.66 | 0.000214 | -0.00801 | 1.55 | 0.000172 | 0 | 1.66 | 0.000214 | -0.00801 |  | LF | None | 1550 | 0.172 | 1550 | 0.172 | 1.07 | 1.24 | -0.0051677 | 1550 | 0.172 | 1550 | 0.172 | 1.07 | 1.24 | -0.00517
LFNonePGEMtlExCZ16 | Com-Iltg-dWatt-LF_OSnone | PGE | Mtl | Ex | CZ16 | 1.55 | 0.000172 | 0 | 1.48 | 0.000207 | -0.0134 | 1.55 | 0.000172 | 0 | 1.48 | 0.000207 | -0.0134 |  | LF | None | 1550 | 0.172 | 1550 | 0.172 | 0.955 | 1.2 | -0.0086452 | 1550 | 0.172 | 1550 | 0.172 | 0.955 | 1.2 | -0.00865
LFNonePGEMtlExIOU | Com-Iltg-dWatt-LF_OSnone | PGE | Mtl | Ex | IOU | 1.55 | 0.000172 | 0 | 1.6073 | 0.00021022 | -0.0095567 | 1.55 | 0.000172 | 0 | 1.6073 | 0.00021022 | -0.0095567 |  | LF | None | 1550 | 0.172 | 1550 | 0.172 | 1.04 | 1.22 | -0.0061656 | 1550 | 0.172 | 1550 | 0.172 | 1.04 | 1.22 | -0.00617
LFNonePGEMtlNewCZ01 | Com-Iltg-dWatt-LF_OSnone | PGE | Mtl | New | CZ01 | 1.55 | 0.000172 | 0 | 1.4 | 0.000205 | -0.02 | 1.55 | 0.000172 | 0 | 1.4 | 0.000205 | -0.02 |  | LF | None | 1550 | 0.172 | 1550 | 0.172 | 0.903 | 1.19 | -0.012903 | 1550 | 0.172 | 1550 | 0.172 | 0.903 | 1.19 | -0.0129
LFNonePGEMtlNewCZ02 | Com-Iltg-dWatt-LF_OSnone | PGE | Mtl | New | CZ02 | 1.55 | 0.000172 | 0 | 1.54 | 0.000217 | -0.0135 | 1.55 | 0.000172 | 0 | 1.54 | 0.000217 | -0.0135 |  | LF | None | 1550 | 0.172 | 1550 | 0.172 | 0.994 | 1.26 | -0.0087097 | 1550 | 0.172 | 1550 | 0.172 | 0.994 | 1.26 | -0.00871
LFNonePGEMtlNewCZ03 | Com-Iltg-dWatt-LF_OSnone | PGE | Mtl | New | CZ03 | 1.55 | 0.000172 | 0 | 1.56 | 0.000211 | -0.0129 | 1.55 | 0.000172 | 0 | 1.56 | 0.000211 | -0.0129 |  | LF | None | 1550 | 0.172 | 1550 | 0.172 | 1.01 | 1.23 | -0.0083226 | 1550 | 0.172 | 1550 | 0.172 | 1.01 | 1.23 | -0.00832
LFNonePGEMtlNewCZ04 | Com-Iltg-dWatt-LF_OSnone | PGE | Mtl | New | CZ04 | 1.55 | 0.000172 | 0 | 1.6 | 0.000215 | -0.0109 | 1.55 | 0.000172 | 0 | 1.6 | 0.000215 | -0.0109 |  | LF | None | 1550 | 0.172 | 1550 | 0.172 | 1.03 | 1.25 | -0.0070323 | 1550 | 0.172 | 1550 | 0.172 | 1.03 | 1.25 | -0.00703
LFNonePGEMtlNewCZ05 | Com-Iltg-dWatt-LF_OSnone | PGE | Mtl | New | CZ05 | 1.55 | 0.000172 | 0 | 1.52 | 0.000209 | -0.0146 | 1.55 | 0.000172 | 0 | 1.52 | 0.000209 | -0.0146 |  | LF | None | 1550 | 0.172 | 1550 | 0.172 | 0.981 | 1.22 | -0.0094194 | 1550 | 0.172 | 1550 | 0.172 | 0.981 | 1.22 | -0.00942
LFNonePGEMtlNewCZ11 | Com-Iltg-dWatt-LF_OSnone | PGE | Mtl | New | CZ11 | 1.55 | 0.000172 | 0 | 1.61 | 0.000217 | -0.0108 | 1.55 | 0.000172 | 0 | 1.61 | 0.000217 | -0.0108 |  | LF | None | 1550 | 0.172 | 1550 | 0.172 | 1.04 | 1.26 | -0.0069677 | 1550 | 0.172 | 1550 | 0.172 | 1.04 | 1.26 | -0.00697
LFNonePGEMtlNewCZ12 | Com-Iltg-dWatt-LF_OSnone | PGE | Mtl | New | CZ12 | 1.55 | 0.000172 | 0 | 1.6 | 0.000217 | -0.0112 | 1.55 | 0.000172 | 0 | 1.6 | 0.000217 | -0.0112 |  | LF | None | 1550 | 0.172 | 1550 | 0.172 | 1.03 | 1.26 | -0.0072258 | 1550 | 0.172 | 1550 | 0.172 | 1.03 | 1.26 | -0.00723
LFNonePGEMtlNewCZ13 | Com-Iltg-dWatt-LF_OSnone | PGE | Mtl | New | CZ13 | 1.55 | 0.000172 | 0 | 1.63 | 0.000216 | -0.0102 | 1.55 | 0.000172 | 0 | 1.63 | 0.000216 | -0.0102 |  | LF | None | 1550 | 0.172 | 1550 | 0.172 | 1.05 | 1.26 | -0.0065806 | 1550 | 0.172 | 1550 | 0.172 | 1.05 | 1.26 | -0.00658
LFNonePGEMtlNewCZ16 | Com-Iltg-dWatt-LF_OSnone | PGE | Mtl | New | CZ16 | 1.55 | 0.000172 | 0 | 1.44 | 0.000209 | -0.0158 | 1.55 | 0.000172 | 0 | 1.44 | 0.000209 | -0.0158 |  | LF | None | 1550 | 0.172 | 1550 | 0.172 | 0.929 | 1.22 | -0.010194 | 1550 | 0.172 | 1550 | 0.172 | 0.929 | 1.22 | -0.0102
LFNonePGEMtlNewIOU | Com-Iltg-dWatt-LF_OSnone | PGE | Mtl | New | IOU | 1.55 | 0.000172 | 0 | 1.5759 | 0.00021404 | -0.012139 | 1.55 | 0.000172 | 0 | 1.5759 | 0.00021404 | -0.012139 |  | LF | None | 1550 | 0.172 | 1550 | 0.172 | 1.02 | 1.24 | -0.0078318 | 1550 | 0.172 | 1550 | 0.172 | 1.02 | 1.24 | -0.00783
LFNonePGENrsExCZ01 | Com-Iltg-dWatt-LF_OSnone | PGE | Nrs | Ex | CZ01 | 4.16 | 0.000676 | 0 | 4.04 | 0.000771 | -0.091 | 4.16 | 0.000676 | 0 | 4.04 | 0.000771 | -0.091 |  | LF | None | 4160 | 0.676 | 4160 | 0.676 | 0.971 | 1.14 | -0.021875 | 4160 | 0.676 | 4160 | 0.676 | 0.971 | 1.14 | -0.0219
LFNonePGENrsExCZ02 | Com-Iltg-dWatt-LF_OSnone | PGE | Nrs | Ex | CZ02 | 4.16 | 0.000676 | 0 | 4.28 | 0.000855 | -0.0657 | 4.16 | 0.000676 | 0 | 4.28 | 0.000855 | -0.0657 |  | LF | None | 4160 | 0.676 | 4160 | 0.676 | 1.03 | 1.26 | -0.015793 | 4160 | 0.676 | 4160 | 0.676 | 1.03 | 1.26 | -0.0158
LFNonePGENrsExCZ03 | Com-Iltg-dWatt-LF_OSnone | PGE | Nrs | Ex | CZ03 | 4.16 | 0.000676 | 0 | 4.23 | 0.000823 | -0.0673 | 4.16 | 0.000676 | 0 | 4.23 | 0.000823 | -0.0673 |  | LF | None | 4160 | 0.676 | 4160 | 0.676 | 1.02 | 1.22 | -0.016178 | 4160 | 0.676 | 4160 | 0.676 | 1.02 | 1.22 | -0.0162
LFNonePGENrsExCZ04 | Com-Iltg-dWatt-LF_OSnone | PGE | Nrs | Ex | CZ04 | 4.16 | 0.000676 | 0 | 4.35 | 0.000843 | -0.0565 | 4.16 | 0.000676 | 0 | 4.35 | 0.000843 | -0.0565 |  | LF | None | 4160 | 0.676 | 4160 | 0.676 | 1.05 | 1.25 | -0.013582 | 4160 | 0.676 | 4160 | 0.676 | 1.05 | 1.25 | -0.0136
LFNonePGENrsExCZ05 | Com-Iltg-dWatt-LF_OSnone | PGE | Nrs | Ex | CZ05 | 4.16 | 0.000676 | 0 | 4.2 | 0.000799 | -0.0682 | 4.16 | 0.000676 | 0 | 4.2 | 0.000799 | -0.0682 |  | LF | None | 4160 | 0.676 | 4160 | 0.676 | 1.01 | 1.18 | -0.016394 | 4160 | 0.676 | 4160 | 0.676 | 1.01 | 1.18 | -0.0164
LFNonePGENrsExCZ11 | Com-Iltg-dWatt-LF_OSnone | PGE | Nrs | Ex | CZ11 | 4.16 | 0.000676 | 0 | 4.41 | 0.000863 | -0.0544 | 4.16 | 0.000676 | 0 | 4.41 | 0.000863 | -0.0544 |  | LF | None | 4160 | 0.676 | 4160 | 0.676 | 1.06 | 1.28 | -0.013077 | 4160 | 0.676 | 4160 | 0.676 | 1.06 | 1.28 | -0.0131
LFNonePGENrsExCZ12 | Com-Iltg-dWatt-LF_OSnone | PGE | Nrs | Ex | CZ12 | 4.16 | 0.000676 | 0 | 4.37 | 0.000863 | -0.0574 | 4.16 | 0.000676 | 0 | 4.37 | 0.000863 | -0.0574 |  | LF | None | 4160 | 0.676 | 4160 | 0.676 | 1.05 | 1.28 | -0.013798 | 4160 | 0.676 | 4160 | 0.676 | 1.05 | 1.28 | -0.0138
LFNonePGENrsExCZ13 | Com-Iltg-dWatt-LF_OSnone | PGE | Nrs | Ex | CZ13 | 4.16 | 0.000676 | 0 | 4.43 | 0.000862 | -0.0524 | 4.16 | 0.000676 | 0 | 4.43 | 0.000862 | -0.0524 |  | LF | None | 4160 | 0.676 | 4160 | 0.676 | 1.06 | 1.28 | -0.012596 | 4160 | 0.676 | 4160 | 0.676 | 1.06 | 1.28 | -0.0126
LFNonePGENrsExCZ16 | Com-Iltg-dWatt-LF_OSnone | PGE | Nrs | Ex | CZ16 | 4.16 | 0.000676 | 0 | 4.15 | 0.000818 | -0.0785 | 4.16 | 0.000676 | 0 | 4.15 | 0.000818 | -0.0785 |  | LF | None | 4160 | 0.676 | 4160 | 0.676 | 0.998 | 1.21 | -0.01887 | 4160 | 0.676 | 4160 | 0.676 | 0.998 | 1.21 | -0.0189
LFNonePGENrsExIOU | Com-Iltg-dWatt-LF_OSnone | PGE | Nrs | Ex | IOU | 4.16 | 0.000676 | 0 | 4.3231 | 0.00084544 | -0.060577 | 4.16 | 0.000676 | 0 | 4.3231 | 0.00084544 | -0.060577 |  | LF | None | 4160 | 0.676 | 4160 | 0.676 | 1.04 | 1.25 | -0.014562 | 4160 | 0.676 | 4160 | 0.676 | 1.04 | 1.25 | -0.0146
LFNonePGENrsNewCZ01 | Com-Iltg-dWatt-LF_OSnone | PGE | Nrs | New | CZ01 | 4.16 | 0.000676 | 0 | 3.9 | 0.000735 | -0.102 | 4.16 | 0.000676 | 0 | 3.9 | 0.000735 | -0.102 |  | LF | None | 4160 | 0.676 | 4160 | 0.676 | 0.938 | 1.09 | -0.024519 | 4160 | 0.676 | 4160 | 0.676 | 0.938 | 1.09 | -0.0245
LFNonePGENrsNewCZ02 | Com-Iltg-dWatt-LF_OSnone | PGE | Nrs | New | CZ02 | 4.16 | 0.000676 | 0 | 4.16 | 0.000863 | -0.0727 | 4.16 | 0.000676 | 0 | 4.16 | 0.000863 | -0.0727 |  | LF | None | 4160 | 0.676 | 4160 | 0.676 | 1 | 1.28 | -0.017476 | 4160 | 0.676 | 4160 | 0.676 | 1 | 1.28 | -0.0175
LFNonePGENrsNewCZ03 | Com-Iltg-dWatt-LF_OSnone | PGE | Nrs | New | CZ03 | 4.16 | 0.000676 | 0 | 4.05 | 0.000836 | -0.0761 | 4.16 | 0.000676 | 0 | 4.05 | 0.000836 | -0.0761 |  | LF | None | 4160 | 0.676 | 4160 | 0.676 | 0.974 | 1.24 | -0.018293 | 4160 | 0.676 | 4160 | 0.676 | 0.974 | 1.24 | -0.0183
LFNonePGENrsNewCZ04 | Com-Iltg-dWatt-LF_OSnone | PGE | Nrs | New | CZ04 | 4.16 | 0.000676 | 0 | 4.23 | 0.000852 | -0.0623 | 4.16 | 0.000676 | 0 | 4.23 | 0.000852 | -0.0623 |  | LF | None | 4160 | 0.676 | 4160 | 0.676 | 1.02 | 1.26 | -0.014976 | 4160 | 0.676 | 4160 | 0.676 | 1.02 | 1.26 | -0.015
LFNonePGENrsNewCZ05 | Com-Iltg-dWatt-LF_OSnone | PGE | Nrs | New | CZ05 | 4.16 | 0.000676 | 0 | 4.06 | 0.000802 | -0.0765 | 4.16 | 0.000676 | 0 | 4.06 | 0.000802 | -0.0765 |  | LF | None | 4160 | 0.676 | 4160 | 0.676 | 0.976 | 1.19 | -0.018389 | 4160 | 0.676 | 4160 | 0.676 | 0.976 | 1.19 | -0.0184
LFNonePGENrsNewCZ11 | Com-Iltg-dWatt-LF_OSnone | PGE | Nrs | New | CZ11 | 4.16 | 0.000676 | 0 | 4.33 | 0.000861 | -0.0578 | 4.16 | 0.000676 | 0 | 4.33 | 0.000861 | -0.0578 |  | LF | None | 4160 | 0.676 | 4160 | 0.676 | 1.04 | 1.27 | -0.013894 | 4160 | 0.676 | 4160 | 0.676 | 1.04 | 1.27 | -0.0139
LFNonePGENrsNewCZ12 | Com-Iltg-dWatt-LF_OSnone | PGE | Nrs | New | CZ12 | 4.16 | 0.000676 | 0 | 4.28 | 0.000867 | -0.0611 | 4.16 | 0.000676 | 0 | 4.28 | 0.000867 | -0.0611 |  | LF | None | 4160 | 0.676 | 4160 | 0.676 | 1.03 | 1.28 | -0.014688 | 4160 | 0.676 | 4160 | 0.676 | 1.03 | 1.28 | -0.0147
LFNonePGENrsNewCZ13 | Com-Iltg-dWatt-LF_OSnone | PGE | Nrs | New | CZ13 | 4.16 | 0.000676 | 0 | 4.36 | 0.000865 | -0.0553 | 4.16 | 0.000676 | 0 | 4.36 | 0.000865 | -0.0553 |  | LF | None | 4160 | 0.676 | 4160 | 0.676 | 1.05 | 1.28 | -0.013293 | 4160 | 0.676 | 4160 | 0.676 | 1.05 | 1.28 | -0.0133
LFNonePGENrsNewCZ16 | Com-Iltg-dWatt-LF_OSnone | PGE | Nrs | New | CZ16 | 4.16 | 0.000676 | 0 | 4.07 | 0.000823 | -0.0831 | 4.16 | 0.000676 | 0 | 4.07 | 0.000823 | -0.0831 |  | LF | None | 4160 | 0.676 | 4160 | 0.676 | 0.978 | 1.22 | -0.019976 | 4160 | 0.676 | 4160 | 0.676 | 0.978 | 1.22 | -0.02
LFNonePGENrsNewIOU | Com-Iltg-dWatt-LF_OSnone | PGE | Nrs | New | IOU | 4.16 | 0.000676 | 0 | 4.2185 | 0.00085388 | -0.065273 | 4.16 | 0.000676 | 0 | 4.2185 | 0.00085388 | -0.065273 |  | LF | None | 4160 | 0.676 | 4160 | 0.676 | 1.01 | 1.26 | -0.015691 | 4160 | 0.676 | 4160 | 0.676 | 1.01 | 1.26 | -0.0157
LFNonePGEOfLExCZ01 | Com-Iltg-dWatt-LF_OSnone | PGE | OfL | Ex | CZ01 | 2.64 | 0.00071 | 0 | 2.84 | 0.00088 | -0.0247 | 2.64 | 0.00071 | 0 | 2.84 | 0.00088 | -0.0247 |  | LF | None | 2640 | 0.71 | 2640 | 0.71 | 1.08 | 1.24 | -0.0093561 | 2640 | 0.71 | 2640 | 0.71 | 1.08 | 1.24 | -0.00936
LFNonePGEOfLExCZ02 | Com-Iltg-dWatt-LF_OSnone | PGE | OfL | Ex | CZ02 | 2.64 | 0.00071 | 0 | 2.93 | 0.000936 | -0.0181 | 2.64 | 0.00071 | 0 | 2.93 | 0.000936 | -0.0181 |  | LF | None | 2640 | 0.71 | 2640 | 0.71 | 1.11 | 1.32 | -0.0068561 | 2640 | 0.71 | 2640 | 0.71 | 1.11 | 1.32 | -0.00686
LFNonePGEOfLExCZ03 | Com-Iltg-dWatt-LF_OSnone | PGE | OfL | Ex | CZ03 | 2.64 | 0.00071 | 0 | 2.92 | 0.000907 | -0.0168 | 2.64 | 0.00071 | 0 | 2.92 | 0.000907 | -0.0168 |  | LF | None | 2640 | 0.71 | 2640 | 0.71 | 1.11 | 1.28 | -0.0063636 | 2640 | 0.71 | 2640 | 0.71 | 1.11 | 1.28 | -0.00636
LFNonePGEOfLExCZ04 | Com-Iltg-dWatt-LF_OSnone | PGE | OfL | Ex | CZ04 | 2.64 | 0.00071 | 0 | 2.96 | 0.000934 | -0.0152 | 2.64 | 0.00071 | 0 | 2.96 | 0.000934 | -0.0152 |  | LF | None | 2640 | 0.71 | 2640 | 0.71 | 1.12 | 1.32 | -0.0057576 | 2640 | 0.71 | 2640 | 0.71 | 1.12 | 1.32 | -0.00576
LFNonePGEOfLExCZ05 | Com-Iltg-dWatt-LF_OSnone | PGE | OfL | Ex | CZ05 | 2.64 | 0.00071 | 0 | 2.91 | 0.000892 | -0.0163 | 2.64 | 0.00071 | 0 | 2.91 | 0.000892 | -0.0163 |  | LF | None | 2640 | 0.71 | 2640 | 0.71 | 1.1 | 1.26 | -0.0061742 | 2640 | 0.71 | 2640 | 0.71 | 1.1 | 1.26 | -0.00617
LFNonePGEOfLExCZ11 | Com-Iltg-dWatt-LF_OSnone | PGE | OfL | Ex | CZ11 | 2.64 | 0.00071 | 0 | 2.99 | 0.000944 | -0.0173 | 2.64 | 0.00071 | 0 | 2.99 | 0.000944 | -0.0173 |  | LF | None | 2640 | 0.71 | 2640 | 0.71 | 1.13 | 1.33 | -0.006553 | 2640 | 0.71 | 2640 | 0.71 | 1.13 | 1.33 | -0.00655
LFNonePGEOfLExCZ12 | Com-Iltg-dWatt-LF_OSnone | PGE | OfL | Ex | CZ12 | 2.64 | 0.00071 | 0 | 2.96 | 0.000929 | -0.0168 | 2.64 | 0.00071 | 0 | 2.96 | 0.000929 | -0.0168 |  | LF | None | 2640 | 0.71 | 2640 | 0.71 | 1.12 | 1.31 | -0.0063636 | 2640 | 0.71 | 2640 | 0.71 | 1.12 | 1.31 | -0.00636
LFNonePGEOfLExCZ13 | Com-Iltg-dWatt-LF_OSnone | PGE | OfL | Ex | CZ13 | 2.64 | 0.00071 | 0 | 3.02 | 0.000943 | -0.0157 | 2.64 | 0.00071 | 0 | 3.02 | 0.000943 | -0.0157 |  | LF | None | 2640 | 0.71 | 2640 | 0.71 | 1.14 | 1.33 | -0.005947 | 2640 | 0.71 | 2640 | 0.71 | 1.14 | 1.33 | -0.00595
LFNonePGEOfLExCZ16 | Com-Iltg-dWatt-LF_OSnone | PGE | OfL | Ex | CZ16 | 2.64 | 0.00071 | 0 | 2.8 | 0.000899 | -0.0296 | 2.64 | 0.00071 | 0 | 2.8 | 0.000899 | -0.0296 |  | LF | None | 2640 | 0.71 | 2640 | 0.71 | 1.06 | 1.27 | -0.011212 | 2640 | 0.71 | 2640 | 0.71 | 1.06 | 1.27 | -0.0112
LFNonePGEOfLExIOU | Com-Iltg-dWatt-LF_OSnone | PGE | OfL | Ex | IOU | 2.64 | 0.00071 | 0 | 2.9414 | 0.00091975 | -0.016521 | 2.64 | 0.00071 | 0 | 2.9414 | 0.00091975 | -0.016521 |  | LF | None | 2640 | 0.71 | 2640 | 0.71 | 1.11 | 1.3 | -0.006258 | 2640 | 0.71 | 2640 | 0.71 | 1.11 | 1.3 | -0.00626
LFNonePGEOfLNewCZ01 | Com-Iltg-dWatt-LF_OSnone | PGE | OfL | New | CZ01 | 2.64 | 0.00071 | 0 | 2.84 | 0.000855 | -0.0122 | 2.64 | 0.00071 | 0 | 2.84 | 0.000855 | -0.0122 |  | LF | None | 2640 | 0.71 | 2640 | 0.71 | 1.08 | 1.2 | -0.0046212 | 2640 | 0.71 | 2640 | 0.71 | 1.08 | 1.2 | -0.00462
LFNonePGEOfLNewCZ02 | Com-Iltg-dWatt-LF_OSnone | PGE | OfL | New | CZ02 | 2.64 | 0.00071 | 0 | 2.96 | 0.000887 | -0.00882 | 2.64 | 0.00071 | 0 | 2.96 | 0.000887 | -0.00882 |  | LF | None | 2640 | 0.71 | 2640 | 0.71 | 1.12 | 1.25 | -0.0033409 | 2640 | 0.71 | 2640 | 0.71 | 1.12 | 1.25 | -0.00334
LFNonePGEOfLNewCZ03 | Com-Iltg-dWatt-LF_OSnone | PGE | OfL | New | CZ03 | 2.64 | 0.00071 | 0 | 2.94 | 0.000873 | -0.00787 | 2.64 | 0.00071 | 0 | 2.94 | 0.000873 | -0.00787 |  | LF | None | 2640 | 0.71 | 2640 | 0.71 | 1.11 | 1.23 | -0.0029811 | 2640 | 0.71 | 2640 | 0.71 | 1.11 | 1.23 | -0.00298
LFNonePGEOfLNewCZ04 | Com-Iltg-dWatt-LF_OSnone | PGE | OfL | New | CZ04 | 2.64 | 0.00071 | 0 | 2.99 | 0.000885 | -0.00732 | 2.64 | 0.00071 | 0 | 2.99 | 0.000885 | -0.00732 |  | LF | None | 2640 | 0.71 | 2640 | 0.71 | 1.13 | 1.25 | -0.0027727 | 2640 | 0.71 | 2640 | 0.71 | 1.13 | 1.25 | -0.00277
LFNonePGEOfLNewCZ05 | Com-Iltg-dWatt-LF_OSnone | PGE | OfL | New | CZ05 | 2.64 | 0.00071 | 0 | 2.93 | 0.000863 | -0.00806 | 2.64 | 0.00071 | 0 | 2.93 | 0.000863 | -0.00806 |  | LF | None | 2640 | 0.71 | 2640 | 0.71 | 1.11 | 1.22 | -0.003053 | 2640 | 0.71 | 2640 | 0.71 | 1.11 | 1.22 | -0.00305
LFNonePGEOfLNewCZ11 | Com-Iltg-dWatt-LF_OSnone | PGE | OfL | New | CZ11 | 2.64 | 0.00071 | 0 | 3.01 | 0.0009 | -0.00716 | 2.64 | 0.00071 | 0 | 3.01 | 0.0009 | -0.00716 |  | LF | None | 2640 | 0.71 | 2640 | 0.71 | 1.14 | 1.27 | -0.0027121 | 2640 | 0.71 | 2640 | 0.71 | 1.14 | 1.27 | -0.00271
LFNonePGEOfLNewCZ12 | Com-Iltg-dWatt-LF_OSnone | PGE | OfL | New | CZ12 | 2.64 | 0.00071 | 0 | 2.98 | 0.000893 | -0.0084 | 2.64 | 0.00071 | 0 | 2.98 | 0.000893 | -0.0084 |  | LF | None | 2640 | 0.71 | 2640 | 0.71 | 1.13 | 1.26 | -0.0031818 | 2640 | 0.71 | 2640 | 0.71 | 1.13 | 1.26 | -0.00318
LFNonePGEOfLNewCZ13 | Com-Iltg-dWatt-LF_OSnone | PGE | OfL | New | CZ13 | 2.64 | 0.00071 | 0 | 3.01 | 0.000893 | -0.00787 | 2.64 | 0.00071 | 0 | 3.01 | 0.000893 | -0.00787 |  | LF | None | 2640 | 0.71 | 2640 | 0.71 | 1.14 | 1.26 | -0.0029811 | 2640 | 0.71 | 2640 | 0.71 | 1.14 | 1.26 | -0.00298
LFNonePGEOfLNewCZ16 | Com-Iltg-dWatt-LF_OSnone | PGE | OfL | New | CZ16 | 2.64 | 0.00071 | 0 | 2.86 | 0.000875 | -0.0183 | 2.64 | 0.00071 | 0 | 2.86 | 0.000875 | -0.0183 |  | LF | None | 2640 | 0.71 | 2640 | 0.71 | 1.08 | 1.23 | -0.0069318 | 2640 | 0.71 | 2640 | 0.71 | 1.08 | 1.23 | -0.00693
LFNonePGEOfLNewIOU | Com-Iltg-dWatt-LF_OSnone | PGE | OfL | New | IOU | 2.64 | 0.00071 | 0 | 2.9673 | 0.00088259 | -0.0079196 | 2.64 | 0.00071 | 0 | 2.9673 | 0.00088259 | -0.0079196 |  | LF | None | 2640 | 0.71 | 2640 | 0.71 | 1.12 | 1.24 | -0.0029998 | 2640 | 0.71 | 2640 | 0.71 | 1.12 | 1.24 | -0.003
LFNonePGEOfSExCZ01 | Com-Iltg-dWatt-LF_OSnone | PGE | OfS | Ex | CZ01 | 2.59 | 0.000694 | 0 | 2.61 | 0.000816 | -0.0167 | 2.59 | 0.000694 | 0 | 2.61 | 0.000816 | -0.0167 |  | LF | None | 2590 | 0.694 | 2590 | 0.694 | 1.01 | 1.18 | -0.0064479 | 2590 | 0.694 | 2590 | 0.694 | 1.01 | 1.18 | -0.00645
LFNonePGEOfSExCZ02 | Com-Iltg-dWatt-LF_OSnone | PGE | OfS | Ex | CZ02 | 2.59 | 0.000694 | 0 | 2.73 | 0.000843 | -0.0108 | 2.59 | 0.000694 | 0 | 2.73 | 0.000843 | -0.0108 |  | LF | None | 2590 | 0.694 | 2590 | 0.694 | 1.05 | 1.21 | -0.0041699 | 2590 | 0.694 | 2590 | 0.694 | 1.05 | 1.21 | -0.00417
LFNonePGEOfSExCZ03 | Com-Iltg-dWatt-LF_OSnone | PGE | OfS | Ex | CZ03 | 2.59 | 0.000694 | 0 | 2.73 | 0.00084 | -0.00926 | 2.59 | 0.000694 | 0 | 2.73 | 0.00084 | -0.00926 |  | LF | None | 2590 | 0.694 | 2590 | 0.694 | 1.05 | 1.21 | -0.0035753 | 2590 | 0.694 | 2590 | 0.694 | 1.05 | 1.21 | -0.00358
LFNonePGEOfSExCZ04 | Com-Iltg-dWatt-LF_OSnone | PGE | OfS | Ex | CZ04 | 2.59 | 0.000694 | 0 | 2.78 | 0.000847 | -0.00737 | 2.59 | 0.000694 | 0 | 2.78 | 0.000847 | -0.00737 |  | LF | None | 2590 | 0.694 | 2590 | 0.694 | 1.07 | 1.22 | -0.0028456 | 2590 | 0.694 | 2590 | 0.694 | 1.07 | 1.22 | -0.00285
LFNonePGEOfSExCZ05 | Com-Iltg-dWatt-LF_OSnone | PGE | OfS | Ex | CZ05 | 2.59 | 0.000694 | 0 | 2.74 | 0.000827 | -0.00755 | 2.59 | 0.000694 | 0 | 2.74 | 0.000827 | -0.00755 |  | LF | None | 2590 | 0.694 | 2590 | 0.694 | 1.06 | 1.19 | -0.0029151 | 2590 | 0.694 | 2590 | 0.694 | 1.06 | 1.19 | -0.00292
LFNonePGEOfSExCZ11 | Com-Iltg-dWatt-LF_OSnone | PGE | OfS | Ex | CZ11 | 2.59 | 0.000694 | 0 | 2.78 | 0.000847 | -0.0114 | 2.59 | 0.000694 | 0 | 2.78 | 0.000847 | -0.0114 |  | LF | None | 2590 | 0.694 | 2590 | 0.694 | 1.07 | 1.22 | -0.0044015 | 2590 | 0.694 | 2590 | 0.694 | 1.07 | 1.22 | -0.0044
LFNonePGEOfSExCZ12 | Com-Iltg-dWatt-LF_OSnone | PGE | OfS | Ex | CZ12 | 2.59 | 0.000694 | 0 | 2.76 | 0.000845 | -0.0111 | 2.59 | 0.000694 | 0 | 2.76 | 0.000845 | -0.0111 |  | LF | None | 2590 | 0.694 | 2590 | 0.694 | 1.07 | 1.22 | -0.0042857 | 2590 | 0.694 | 2590 | 0.694 | 1.07 | 1.22 | -0.00429
LFNonePGEOfSExCZ13 | Com-Iltg-dWatt-LF_OSnone | PGE | OfS | Ex | CZ13 | 2.59 | 0.000694 | 0 | 2.79 | 0.000838 | -0.0104 | 2.59 | 0.000694 | 0 | 2.79 | 0.000838 | -0.0104 |  | LF | None | 2590 | 0.694 | 2590 | 0.694 | 1.08 | 1.21 | -0.0040154 | 2590 | 0.694 | 2590 | 0.694 | 1.08 | 1.21 | -0.00402
LFNonePGEOfSExCZ16 | Com-Iltg-dWatt-LF_OSnone | PGE | OfS | Ex | CZ16 | 2.59 | 0.000694 | 0 | 2.58 | 0.000829 | -0.0208 | 2.59 | 0.000694 | 0 | 2.58 | 0.000829 | -0.0208 |  | LF | None | 2590 | 0.694 | 2590 | 0.694 | 0.996 | 1.19 | -0.0080309 | 2590 | 0.694 | 2590 | 0.694 | 0.996 | 1.19 | -0.00803
LFNonePGEOfSExIOU | Com-Iltg-dWatt-LF_OSnone | PGE | OfS | Ex | IOU | 2.59 | 0.000694 | 0 | 2.7585 | 0.00084192 | -0.0099532 | 2.59 | 0.000694 | 0 | 2.7585 | 0.00084192 | -0.0099532 |  | LF | None | 2590 | 0.694 | 2590 | 0.694 | 1.07 | 1.21 | -0.0038429 | 2590 | 0.694 | 2590 | 0.694 | 1.07 | 1.21 | -0.00384
LFNonePGEOfSNewCZ01 | Com-Iltg-dWatt-LF_OSnone | PGE | OfS | New | CZ01 | 2.59 | 0.000694 | 0 | 2.57 | 0.00081 | -0.0141 | 2.59 | 0.000694 | 0 | 2.57 | 0.00081 | -0.0141 |  | LF | None | 2590 | 0.694 | 2590 | 0.694 | 0.992 | 1.17 | -0.005444 | 2590 | 0.694 | 2590 | 0.694 | 0.992 | 1.17 | -0.00544
LFNonePGEOfSNewCZ02 | Com-Iltg-dWatt-LF_OSnone | PGE | OfS | New | CZ02 | 2.59 | 0.000694 | 0 | 2.73 | 0.000842 | -0.00747 | 2.59 | 0.000694 | 0 | 2.73 | 0.000842 | -0.00747 |  | LF | None | 2590 | 0.694 | 2590 | 0.694 | 1.05 | 1.21 | -0.0028842 | 2590 | 0.694 | 2590 | 0.694 | 1.05 | 1.21 | -0.00288
LFNonePGEOfSNewCZ03 | Com-Iltg-dWatt-LF_OSnone | PGE | OfS | New | CZ03 | 2.59 | 0.000694 | 0 | 2.69 | 0.00084 | -0.0083 | 2.59 | 0.000694 | 0 | 2.69 | 0.00084 | -0.0083 |  | LF | None | 2590 | 0.694 | 2590 | 0.694 | 1.04 | 1.21 | -0.0032046 | 2590 | 0.694 | 2590 | 0.694 | 1.04 | 1.21 | -0.0032
LFNonePGEOfSNewCZ04 | Com-Iltg-dWatt-LF_OSnone | PGE | OfS | New | CZ04 | 2.59 | 0.000694 | 0 | 2.77 | 0.000855 | -0.00594 | 2.59 | 0.000694 | 0 | 2.77 | 0.000855 | -0.00594 |  | LF | None | 2590 | 0.694 | 2590 | 0.694 | 1.07 | 1.23 | -0.0022934 | 2590 | 0.694 | 2590 | 0.694 | 1.07 | 1.23 | -0.00229
LFNonePGEOfSNewCZ05 | Com-Iltg-dWatt-LF_OSnone | PGE | OfS | New | CZ05 | 2.59 | 0.000694 | 0 | 2.71 | 0.000827 | -0.00636 | 2.59 | 0.000694 | 0 | 2.71 | 0.000827 | -0.00636 |  | LF | None | 2590 | 0.694 | 2590 | 0.694 | 1.05 | 1.19 | -0.0024556 | 2590 | 0.694 | 2590 | 0.694 | 1.05 | 1.19 | -0.00246
LFNonePGEOfSNewCZ11 | Com-Iltg-dWatt-LF_OSnone | PGE | OfS | New | CZ11 | 2.59 | 0.000694 | 0 | 2.79 | 0.00087 | -0.00851 | 2.59 | 0.000694 | 0 | 2.79 | 0.00087 | -0.00851 |  | LF | None | 2590 | 0.694 | 2590 | 0.694 | 1.08 | 1.25 | -0.0032857 | 2590 | 0.694 | 2590 | 0.694 | 1.08 | 1.25 | -0.00329
LFNonePGEOfSNewCZ12 | Com-Iltg-dWatt-LF_OSnone | PGE | OfS | New | CZ12 | 2.59 | 0.000694 | 0 | 2.77 | 0.000861 | -0.00822 | 2.59 | 0.000694 | 0 | 2.77 | 0.000861 | -0.00822 |  | LF | None | 2590 | 0.694 | 2590 | 0.694 | 1.07 | 1.24 | -0.0031737 | 2590 | 0.694 | 2590 | 0.694 | 1.07 | 1.24 | -0.00317
LFNonePGEOfSNewCZ13 | Com-Iltg-dWatt-LF_OSnone | PGE | OfS | New | CZ13 | 2.59 | 0.000694 | 0 | 2.8 | 0.000861 | -0.00789 | 2.59 | 0.000694 | 0 | 2.8 | 0.000861 | -0.00789 |  | LF | None | 2590 | 0.694 | 2590 | 0.694 | 1.08 | 1.24 | -0.0030463 | 2590 | 0.694 | 2590 | 0.694 | 1.08 | 1.24 | -0.00305
LFNonePGEOfSNewCZ16 | Com-Iltg-dWatt-LF_OSnone | PGE | OfS | New | CZ16 | 2.59 | 0.000694 | 0 | 2.59 | 0.000835 | -0.0185 | 2.59 | 0.000694 | 0 | 2.59 | 0.000835 | -0.0185 |  | LF | None | 2590 | 0.694 | 2590 | 0.694 | 1 | 1.2 | -0.0071429 | 2590 | 0.694 | 2590 | 0.694 | 1 | 1.2 | -0.00714
LFNonePGEOfSNewIOU | Com-Iltg-dWatt-LF_OSnone | PGE | OfS | New | IOU | 2.59 | 0.000694 | 0 | 2.7523 | 0.00085343 | -0.0078601 | 2.59 | 0.000694 | 0 | 2.7523 | 0.00085343 | -0.0078601 |  | LF | None | 2590 | 0.694 | 2590 | 0.694 | 1.06 | 1.23 | -0.0030348 | 2590 | 0.694 | 2590 | 0.694 | 1.06 | 1.23 | -0.00303
LFNonePGERFFExCZ01 | Com-Iltg-dWatt-LF_OSnone | PGE | RFF | Ex | CZ01 | 4.84 | 0.000813 | 0 | 4.68 | 0.000931 | -0.0639 | 4.84 | 0.000813 | 0 | 4.68 | 0.000931 | -0.0639 |  | LF | None | 4840 | 0.813 | 4840 | 0.813 | 0.967 | 1.15 | -0.013202 | 4840 | 0.813 | 4840 | 0.813 | 0.967 | 1.15 | -0.0132
LFNonePGERFFExCZ02 | Com-Iltg-dWatt-LF_OSnone | PGE | RFF | Ex | CZ02 | 4.84 | 0.000813 | 0 | 4.99 | 0.000952 | -0.0406 | 4.84 | 0.000813 | 0 | 4.99 | 0.000952 | -0.0406 |  | LF | None | 4840 | 0.813 | 4840 | 0.813 | 1.03 | 1.17 | -0.0083884 | 4840 | 0.813 | 4840 | 0.813 | 1.03 | 1.17 | -0.00839
LFNonePGERFFExCZ03 | Com-Iltg-dWatt-LF_OSnone | PGE | RFF | Ex | CZ03 | 4.84 | 0.000813 | 0 | 4.94 | 0.000948 | -0.0431 | 4.84 | 0.000813 | 0 | 4.94 | 0.000948 | -0.0431 |  | LF | None | 4840 | 0.813 | 4840 | 0.813 | 1.02 | 1.17 | -0.008905 | 4840 | 0.813 | 4840 | 0.813 | 1.02 | 1.17 | -0.00891
LFNonePGERFFExCZ04 | Com-Iltg-dWatt-LF_OSnone | PGE | RFF | Ex | CZ04 | 4.84 | 0.000813 | 0 | 5.07 | 0.000952 | -0.0338 | 4.84 | 0.000813 | 0 | 5.07 | 0.000952 | -0.0338 |  | LF | None | 4840 | 0.813 | 4840 | 0.813 | 1.05 | 1.17 | -0.0069835 | 4840 | 0.813 | 4840 | 0.813 | 1.05 | 1.17 | -0.00698
LFNonePGERFFExCZ05 | Com-Iltg-dWatt-LF_OSnone | PGE | RFF | Ex | CZ05 | 4.84 | 0.000813 | 0 | 4.92 | 0.000937 | -0.0437 | 4.84 | 0.000813 | 0 | 4.92 | 0.000937 | -0.0437 |  | LF | None | 4840 | 0.813 | 4840 | 0.813 | 1.02 | 1.15 | -0.0090289 | 4840 | 0.813 | 4840 | 0.813 | 1.02 | 1.15 | -0.00903
LFNonePGERFFExCZ11 | Com-Iltg-dWatt-LF_OSnone | PGE | RFF | Ex | CZ11 | 4.84 | 0.000813 | 0 | 5.1 | 0.000969 | -0.0333 | 4.84 | 0.000813 | 0 | 5.1 | 0.000969 | -0.0333 |  | LF | None | 4840 | 0.813 | 4840 | 0.813 | 1.05 | 1.19 | -0.0068802 | 4840 | 0.813 | 4840 | 0.813 | 1.05 | 1.19 | -0.00688
LFNonePGERFFExCZ12 | Com-Iltg-dWatt-LF_OSnone | PGE | RFF | Ex | CZ12 | 4.84 | 0.000813 | 0 | 5.08 | 0.000961 | -0.0347 | 4.84 | 0.000813 | 0 | 5.08 | 0.000961 | -0.0347 |  | LF | None | 4840 | 0.813 | 4840 | 0.813 | 1.05 | 1.18 | -0.0071694 | 4840 | 0.813 | 4840 | 0.813 | 1.05 | 1.18 | -0.00717
LFNonePGERFFExCZ13 | Com-Iltg-dWatt-LF_OSnone | PGE | RFF | Ex | CZ13 | 4.84 | 0.000813 | 0 | 5.12 | 0.000957 | -0.0317 | 4.84 | 0.000813 | 0 | 5.12 | 0.000957 | -0.0317 |  | LF | None | 4840 | 0.813 | 4840 | 0.813 | 1.06 | 1.18 | -0.0065496 | 4840 | 0.813 | 4840 | 0.813 | 1.06 | 1.18 | -0.00655
LFNonePGERFFExCZ16 | Com-Iltg-dWatt-LF_OSnone | PGE | RFF | Ex | CZ16 | 4.84 | 0.000813 | 0 | 4.73 | 0.000942 | -0.061 | 4.84 | 0.000813 | 0 | 4.73 | 0.000942 | -0.061 |  | LF | None | 4840 | 0.813 | 4840 | 0.813 | 0.977 | 1.16 | -0.012603 | 4840 | 0.813 | 4840 | 0.813 | 0.977 | 1.16 | -0.0126
LFNonePGERFFExIOU | Com-Iltg-dWatt-LF_OSnone | PGE | RFF | Ex | IOU | 4.84 | 0.000813 | 0 | 5.0206 | 0.00095358 | -0.038117 | 4.84 | 0.000813 | 0 | 5.0206 | 0.00095358 | -0.038117 |  | LF | None | 4840 | 0.813 | 4840 | 0.813 | 1.04 | 1.17 | -0.0078755 | 4840 | 0.813 | 4840 | 0.813 | 1.04 | 1.17 | -0.00788
LFNonePGERFFNewCZ01 | Com-Iltg-dWatt-LF_OSnone | PGE | RFF | New | CZ01 | 4.84 | 0.000813 | 0 | 4.54 | 0.000889 | -0.0682 | 4.84 | 0.000813 | 0 | 4.54 | 0.000889 | -0.0682 |  | LF | None | 4840 | 0.813 | 4840 | 0.813 | 0.938 | 1.09 | -0.014091 | 4840 | 0.813 | 4840 | 0.813 | 0.938 | 1.09 | -0.0141
LFNonePGERFFNewCZ02 | Com-Iltg-dWatt-LF_OSnone | PGE | RFF | New | CZ02 | 4.84 | 0.000813 | 0 | 4.9 | 0.000995 | -0.0499 | 4.84 | 0.000813 | 0 | 4.9 | 0.000995 | -0.0499 |  | LF | None | 4840 | 0.813 | 4840 | 0.813 | 1.01 | 1.22 | -0.01031 | 4840 | 0.813 | 4840 | 0.813 | 1.01 | 1.22 | -0.0103
LFNonePGERFFNewCZ03 | Com-Iltg-dWatt-LF_OSnone | PGE | RFF | New | CZ03 | 4.84 | 0.000813 | 0 | 4.79 | 0.000963 | -0.0499 | 4.84 | 0.000813 | 0 | 4.79 | 0.000963 | -0.0499 |  | LF | None | 4840 | 0.813 | 4840 | 0.813 | 0.99 | 1.18 | -0.01031 | 4840 | 0.813 | 4840 | 0.813 | 0.99 | 1.18 | -0.0103
LFNonePGERFFNewCZ04 | Com-Iltg-dWatt-LF_OSnone | PGE | RFF | New | CZ04 | 4.84 | 0.000813 | 0 | 4.99 | 0.000982 | -0.0407 | 4.84 | 0.000813 | 0 | 4.99 | 0.000982 | -0.0407 |  | LF | None | 4840 | 0.813 | 4840 | 0.813 | 1.03 | 1.21 | -0.0084091 | 4840 | 0.813 | 4840 | 0.813 | 1.03 | 1.21 | -0.00841
LFNonePGERFFNewCZ05 | Com-Iltg-dWatt-LF_OSnone | PGE | RFF | New | CZ05 | 4.84 | 0.000813 | 0 | 4.79 | 0.000949 | -0.0439 | 4.84 | 0.000813 | 0 | 4.79 | 0.000949 | -0.0439 |  | LF | None | 4840 | 0.813 | 4840 | 0.813 | 0.99 | 1.17 | -0.0090702 | 4840 | 0.813 | 4840 | 0.813 | 0.99 | 1.17 | -0.00907
LFNonePGERFFNewCZ11 | Com-Iltg-dWatt-LF_OSnone | PGE | RFF | New | CZ11 | 4.84 | 0.000813 | 0 | 5.1 | 0.00101 | -0.0401 | 4.84 | 0.000813 | 0 | 5.1 | 0.00101 | -0.0401 |  | LF | None | 4840 | 0.813 | 4840 | 0.813 | 1.05 | 1.24 | -0.0082851 | 4840 | 0.813 | 4840 | 0.813 | 1.05 | 1.24 | -0.00829
LFNonePGERFFNewCZ12 | Com-Iltg-dWatt-LF_OSnone | PGE | RFF | New | CZ12 | 4.84 | 0.000813 | 0 | 5.05 | 0.001 | -0.0432 | 4.84 | 0.000813 | 0 | 5.05 | 0.001 | -0.0432 |  | LF | None | 4840 | 0.813 | 4840 | 0.813 | 1.04 | 1.23 | -0.0089256 | 4840 | 0.813 | 4840 | 0.813 | 1.04 | 1.23 | -0.00893
LFNonePGERFFNewCZ13 | Com-Iltg-dWatt-LF_OSnone | PGE | RFF | New | CZ13 | 4.84 | 0.000813 | 0 | 5.12 | 0.001 | -0.0382 | 4.84 | 0.000813 | 0 | 5.12 | 0.001 | -0.0382 |  | LF | None | 4840 | 0.813 | 4840 | 0.813 | 1.06 | 1.23 | -0.0078926 | 4840 | 0.813 | 4840 | 0.813 | 1.06 | 1.23 | -0.00789
LFNonePGERFFNewCZ16 | Com-Iltg-dWatt-LF_OSnone | PGE | RFF | New | CZ16 | 4.84 | 0.000813 | 0 | 4.71 | 0.000967 | -0.0678 | 4.84 | 0.000813 | 0 | 4.71 | 0.000967 | -0.0678 |  | LF | None | 4840 | 0.813 | 4840 | 0.813 | 0.973 | 1.19 | -0.014008 | 4840 | 0.813 | 4840 | 0.813 | 0.973 | 1.19 | -0.014
LFNonePGERFFNewIOU | Com-Iltg-dWatt-LF_OSnone | PGE | RFF | New | IOU | 4.84 | 0.000813 | 0 | 4.9495 | 0.00098356 | -0.045009 | 4.84 | 0.000813 | 0 | 4.9495 | 0.00098356 | -0.045009 |  | LF | None | 4840 | 0.813 | 4840 | 0.813 | 1.02 | 1.21 | -0.0092994 | 4840 | 0.813 | 4840 | 0.813 | 1.02 | 1.21 | -0.0093
LFNonePGERSDExCZ01 | Com-Iltg-dWatt-LF_OSnone | PGE | RSD | Ex | CZ01 | 4.83 | 0.0008 | 0 | 4.42 | 0.000922 | -0.0826 | 4.83 | 0.0008 | 0 | 4.42 | 0.000922 | -0.0826 |  | LF | None | 4830 | 0.8 | 4830 | 0.8 | 0.915 | 1.15 | -0.017101 | 4830 | 0.8 | 4830 | 0.8 | 0.915 | 1.15 | -0.0171
LFNonePGERSDExCZ02 | Com-Iltg-dWatt-LF_OSnone | PGE | RSD | Ex | CZ02 | 4.83 | 0.0008 | 0 | 4.9 | 0.000939 | -0.0468 | 4.83 | 0.0008 | 0 | 4.9 | 0.000939 | -0.0468 |  | LF | None | 4830 | 0.8 | 4830 | 0.8 | 1.01 | 1.17 | -0.0096894 | 4830 | 0.8 | 4830 | 0.8 | 1.01 | 1.17 | -0.00969
LFNonePGERSDExCZ03 | Com-Iltg-dWatt-LF_OSnone | PGE | RSD | Ex | CZ03 | 4.83 | 0.0008 | 0 | 4.82 | 0.000947 | -0.0517 | 4.83 | 0.0008 | 0 | 4.82 | 0.000947 | -0.0517 |  | LF | None | 4830 | 0.8 | 4830 | 0.8 | 0.998 | 1.18 | -0.010704 | 4830 | 0.8 | 4830 | 0.8 | 0.998 | 1.18 | -0.0107
LFNonePGERSDExCZ04 | Com-Iltg-dWatt-LF_OSnone | PGE | RSD | Ex | CZ04 | 4.83 | 0.0008 | 0 | 5.01 | 0.000948 | -0.0378 | 4.83 | 0.0008 | 0 | 5.01 | 0.000948 | -0.0378 |  | LF | None | 4830 | 0.8 | 4830 | 0.8 | 1.04 | 1.19 | -0.0078261 | 4830 | 0.8 | 4830 | 0.8 | 1.04 | 1.19 | -0.00783
LFNonePGERSDExCZ05 | Com-Iltg-dWatt-LF_OSnone | PGE | RSD | Ex | CZ05 | 4.83 | 0.0008 | 0 | 4.83 | 0.000941 | -0.0497 | 4.83 | 0.0008 | 0 | 4.83 | 0.000941 | -0.0497 |  | LF | None | 4830 | 0.8 | 4830 | 0.8 | 1 | 1.18 | -0.01029 | 4830 | 0.8 | 4830 | 0.8 | 1 | 1.18 | -0.0103
LFNonePGERSDExCZ11 | Com-Iltg-dWatt-LF_OSnone | PGE | RSD | Ex | CZ11 | 4.83 | 0.0008 | 0 | 5 | 0.000942 | -0.041 | 4.83 | 0.0008 | 0 | 5 | 0.000942 | -0.041 |  | LF | None | 4830 | 0.8 | 4830 | 0.8 | 1.04 | 1.18 | -0.0084886 | 4830 | 0.8 | 4830 | 0.8 | 1.04 | 1.18 | -0.00849
LFNonePGERSDExCZ12 | Com-Iltg-dWatt-LF_OSnone | PGE | RSD | Ex | CZ12 | 4.83 | 0.0008 | 0 | 4.97 | 0.000907 | -0.0421 | 4.83 | 0.0008 | 0 | 4.97 | 0.000907 | -0.0421 |  | LF | None | 4830 | 0.8 | 4830 | 0.8 | 1.03 | 1.13 | -0.0087164 | 4830 | 0.8 | 4830 | 0.8 | 1.03 | 1.13 | -0.00872
LFNonePGERSDExCZ13 | Com-Iltg-dWatt-LF_OSnone | PGE | RSD | Ex | CZ13 | 4.83 | 0.0008 | 0 | 5.04 | 0.00095 | -0.038 | 4.83 | 0.0008 | 0 | 5.04 | 0.00095 | -0.038 |  | LF | None | 4830 | 0.8 | 4830 | 0.8 | 1.04 | 1.19 | -0.0078675 | 4830 | 0.8 | 4830 | 0.8 | 1.04 | 1.19 | -0.00787
LFNonePGERSDExCZ16 | Com-Iltg-dWatt-LF_OSnone | PGE | RSD | Ex | CZ16 | 4.83 | 0.0008 | 0 | 4.59 | 0.000911 | -0.0671 | 4.83 | 0.0008 | 0 | 4.59 | 0.000911 | -0.0671 |  | LF | None | 4830 | 0.8 | 4830 | 0.8 | 0.95 | 1.14 | -0.013892 | 4830 | 0.8 | 4830 | 0.8 | 0.95 | 1.14 | -0.0139
LFNonePGERSDExIOU | Com-Iltg-dWatt-LF_OSnone | PGE | RSD | Ex | IOU | 4.83 | 0.0008 | 0 | 4.9187 | 0.00093724 | -0.045314 | 4.83 | 0.0008 | 0 | 4.9187 | 0.00093724 | -0.045314 |  | LF | None | 4830 | 0.8 | 4830 | 0.8 | 1.02 | 1.17 | -0.0093818 | 4830 | 0.8 | 4830 | 0.8 | 1.02 | 1.17 | -0.00938
LFNonePGERSDNewCZ01 | Com-Iltg-dWatt-LF_OSnone | PGE | RSD | New | CZ01 | 4.83 | 0.0008 | 0 | 4.46 | 0.000927 | -0.0396 | 4.83 | 0.0008 | 0 | 4.46 | 0.000927 | -0.0396 |  | LF | None | 4830 | 0.8 | 4830 | 0.8 | 0.923 | 1.16 | -0.0081988 | 4830 | 0.8 | 4830 | 0.8 | 0.923 | 1.16 | -0.0082
LFNonePGERSDNewCZ02 | Com-Iltg-dWatt-LF_OSnone | PGE | RSD | New | CZ02 | 4.83 | 0.0008 | 0 | 4.87 | 0.000988 | -0.0531 | 4.83 | 0.0008 | 0 | 4.87 | 0.000988 | -0.0531 |  | LF | None | 4830 | 0.8 | 4830 | 0.8 | 1.01 | 1.23 | -0.010994 | 4830 | 0.8 | 4830 | 0.8 | 1.01 | 1.23 | -0.011
LFNonePGERSDNewCZ03 | Com-Iltg-dWatt-LF_OSnone | PGE | RSD | New | CZ03 | 4.83 | 0.0008 | 0 | 4.75 | 0.000974 | -0.0589 | 4.83 | 0.0008 | 0 | 4.75 | 0.000974 | -0.0589 |  | LF | None | 4830 | 0.8 | 4830 | 0.8 | 0.983 | 1.22 | -0.012195 | 4830 | 0.8 | 4830 | 0.8 | 0.983 | 1.22 | -0.0122
LFNonePGERSDNewCZ04 | Com-Iltg-dWatt-LF_OSnone | PGE | RSD | New | CZ04 | 4.83 | 0.0008 | 0 | 4.99 | 0.000989 | -0.0429 | 4.83 | 0.0008 | 0 | 4.99 | 0.000989 | -0.0429 |  | LF | None | 4830 | 0.8 | 4830 | 0.8 | 1.03 | 1.24 | -0.008882 | 4830 | 0.8 | 4830 | 0.8 | 1.03 | 1.24 | -0.00888
LFNonePGERSDNewCZ05 | Com-Iltg-dWatt-LF_OSnone | PGE | RSD | New | CZ05 | 4.83 | 0.0008 | 0 | 4.75 | 0.00095 | -0.057 | 4.83 | 0.0008 | 0 | 4.75 | 0.00095 | -0.057 |  | LF | None | 4830 | 0.8 | 4830 | 0.8 | 0.983 | 1.19 | -0.011801 | 4830 | 0.8 | 4830 | 0.8 | 0.983 | 1.19 | -0.0118
LFNonePGERSDNewCZ11 | Com-Iltg-dWatt-LF_OSnone | PGE | RSD | New | CZ11 | 4.83 | 0.0008 | 0 | 5.03 | 0.00101 | -0.0458 | 4.83 | 0.0008 | 0 | 5.03 | 0.00101 | -0.0458 |  | LF | None | 4830 | 0.8 | 4830 | 0.8 | 1.04 | 1.26 | -0.0094824 | 4830 | 0.8 | 4830 | 0.8 | 1.04 | 1.26 | -0.00948
LFNonePGERSDNewCZ12 | Com-Iltg-dWatt-LF_OSnone | PGE | RSD | New | CZ12 | 4.83 | 0.0008 | 0 | 4.99 | 0.000994 | -0.0461 | 4.83 | 0.0008 | 0 | 4.99 | 0.000994 | -0.0461 |  | LF | None | 4830 | 0.8 | 4830 | 0.8 | 1.03 | 1.24 | -0.0095445 | 4830 | 0.8 | 4830 | 0.8 | 1.03 | 1.24 | -0.00954
LFNonePGERSDNewCZ13 | Com-Iltg-dWatt-LF_OSnone | PGE | RSD | New | CZ13 | 4.83 | 0.0008 | 0 | 5.06 | 0.00101 | -0.0433 | 4.83 | 0.0008 | 0 | 5.06 | 0.00101 | -0.0433 |  | LF | None | 4830 | 0.8 | 4830 | 0.8 | 1.05 | 1.26 | -0.0089648 | 4830 | 0.8 | 4830 | 0.8 | 1.05 | 1.26 | -0.00896
LFNonePGERSDNewCZ16 | Com-Iltg-dWatt-LF_OSnone | PGE | RSD | New | CZ16 | 4.83 | 0.0008 | 0 | 4.58 | 0.000954 | -0.0536 | 4.83 | 0.0008 | 0 | 4.58 | 0.000954 | -0.0536 |  | LF | None | 4830 | 0.8 | 4830 | 0.8 | 0.948 | 1.19 | -0.011097 | 4830 | 0.8 | 4830 | 0.8 | 0.948 | 1.19 | -0.0111
LFNonePGERSDNewIOU | Com-Iltg-dWatt-LF_OSnone | PGE | RSD | New | IOU | 4.83 | 0.0008 | 0 | 4.904 | 0.00098796 | -0.049989 | 4.83 | 0.0008 | 0 | 4.904 | 0.00098796 | -0.049989 |  | LF | None | 4830 | 0.8 | 4830 | 0.8 | 1.02 | 1.23 | -0.01035 | 4830 | 0.8 | 4830 | 0.8 | 1.02 | 1.23 | -0.0104
LFNonePGERt3ExCZ01 | Com-Iltg-dWatt-LF_OSnone | PGE | Rt3 | Ex | CZ01 | 3.38 | 0.00075924 | 0 | 3.31 | 0.00089924 | -0.0429 | 3.38 | 0.00075924 | 0 | 3.31 | 0.00089924 | -0.0429 |  | LF | None | 3380 | 0.759 | 3380 | 0.759 | 0.979 | 1.18 | -0.012692 | 3380 | 0.759 | 3380 | 0.759 | 0.979 | 1.18 | -0.0127
LFNonePGERt3ExCZ02 | Com-Iltg-dWatt-LF_OSnone | PGE | Rt3 | Ex | CZ02 | 3.38 | 0.00075928 | 0 | 3.61 | 0.00090328 | -0.0207 | 3.38 | 0.00075928 | 0 | 3.61 | 0.00090328 | -0.0207 |  | LF | None | 3380 | 0.759 | 3380 | 0.759 | 1.07 | 1.19 | -0.0061243 | 3380 | 0.759 | 3380 | 0.759 | 1.07 | 1.19 | -0.00612
LFNonePGERt3ExCZ03 | Com-Iltg-dWatt-LF_OSnone | PGE | Rt3 | Ex | CZ03 | 3.38 | 0.00075924 | 0 | 3.63 | 0.00090124 | -0.0188 | 3.38 | 0.00075924 | 0 | 3.63 | 0.00090124 | -0.0188 |  | LF | None | 3380 | 0.759 | 3380 | 0.759 | 1.07 | 1.19 | -0.0055621 | 3380 | 0.759 | 3380 | 0.759 | 1.07 | 1.19 | -0.00556
LFNonePGERt3ExCZ04 | Com-Iltg-dWatt-LF_OSnone | PGE | Rt3 | Ex | CZ04 | 3.38 | 0.0007593 | 0 | 3.69 | 0.00090559 | -0.0125 | 3.38 | 0.0007593 | 0 | 3.69 | 0.00090559 | -0.0125 |  | LF | None | 3380 | 0.759 | 3380 | 0.759 | 1.09 | 1.19 | -0.0036982 | 3380 | 0.759 | 3380 | 0.759 | 1.09 | 1.19 | -0.0037
LFNonePGERt3ExCZ05 | Com-Iltg-dWatt-LF_OSnone | PGE | Rt3 | Ex | CZ05 | 3.38 | 0.0007593 | 0 | 3.63 | 0.0008893 | -0.0151 | 3.38 | 0.0007593 | 0 | 3.63 | 0.0008893 | -0.0151 |  | LF | None | 3380 | 0.759 | 3380 | 0.759 | 1.07 | 1.17 | -0.0044675 | 3380 | 0.759 | 3380 | 0.759 | 1.07 | 1.17 | -0.00447
LFNonePGERt3ExCZ11 | Com-Iltg-dWatt-LF_OSnone | PGE | Rt3 | Ex | CZ11 | 3.38 | 0.00075935 | 0 | 3.61 | 0.00090935 | -0.0205 | 3.38 | 0.00075935 | 0 | 3.61 | 0.00090935 | -0.0205 |  | LF | None | 3380 | 0.759 | 3380 | 0.759 | 1.07 | 1.2 | -0.0060651 | 3380 | 0.759 | 3380 | 0.759 | 1.07 | 1.2 | -0.00607
LFNonePGERt3ExCZ12 | Com-Iltg-dWatt-LF_OSnone | PGE | Rt3 | Ex | CZ12 | 3.38 | 0.00075936 | 0 | 3.62 | 0.00091436 | -0.0195 | 3.38 | 0.00075936 | 0 | 3.62 | 0.00091436 | -0.0195 |  | LF | None | 3380 | 0.759 | 3380 | 0.759 | 1.07 | 1.2 | -0.0057692 | 3380 | 0.759 | 3380 | 0.759 | 1.07 | 1.2 | -0.00577
LFNonePGERt3ExCZ13 | Com-Iltg-dWatt-LF_OSnone | PGE | Rt3 | Ex | CZ13 | 3.38 | 0.00075934 | 0 | 3.63 | 0.00090534 | -0.0189 | 3.38 | 0.00075934 | 0 | 3.63 | 0.00090534 | -0.0189 |  | LF | None | 3380 | 0.759 | 3380 | 0.759 | 1.07 | 1.19 | -0.0055917 | 3380 | 0.759 | 3380 | 0.759 | 1.07 | 1.19 | -0.00559
LFNonePGERt3ExCZ16 | Com-Iltg-dWatt-LF_OSnone | PGE | Rt3 | Ex | CZ16 | 3.38 | 0.0007593 | 0 | 3.31 | 0.0008873 | -0.0456 | 3.38 | 0.0007593 | 0 | 3.31 | 0.0008873 | -0.0456 |  | LF | None | 3380 | 0.759 | 3380 | 0.759 | 0.979 | 1.17 | -0.013491 | 3380 | 0.759 | 3380 | 0.759 | 0.979 | 1.17 | -0.0135
LFNonePGERt3ExIOU | Com-Iltg-dWatt-LF_OSnone | PGE | Rt3 | Ex | IOU | 3.38 | 0.0007593 | 0 | 3.6293 | 0.00090572 | -0.01856 | 3.38 | 0.0007593 | 0 | 3.6293 | 0.00090572 | -0.01856 |  | LF | None | 3380 | 0.759 | 3380 | 0.759 | 1.07 | 1.19 | -0.0054911 | 3380 | 0.759 | 3380 | 0.759 | 1.07 | 1.19 | -0.00549
LFNonePGERt3NewCZ01 | Com-Iltg-dWatt-LF_OSnone | PGE | Rt3 | New | CZ01 | 3.38 | 0.00076 | 0 | 3.26 | 0.000898 | -0.0489 | 3.38 | 0.00076 | 0 | 3.26 | 0.000898 | -0.0489 |  | LF | None | 3380 | 0.76 | 3380 | 0.76 | 0.964 | 1.18 | -0.014467 | 3380 | 0.76 | 3380 | 0.76 | 0.964 | 1.18 | -0.0145
LFNonePGERt3NewCZ02 | Com-Iltg-dWatt-LF_OSnone | PGE | Rt3 | New | CZ02 | 3.38 | 0.00076 | 0 | 3.56 | 0.000933 | -0.0251 | 3.38 | 0.00076 | 0 | 3.56 | 0.000933 | -0.0251 |  | LF | None | 3380 | 0.76 | 3380 | 0.76 | 1.05 | 1.23 | -0.007426 | 3380 | 0.76 | 3380 | 0.76 | 1.05 | 1.23 | -0.00743
LFNonePGERt3NewCZ03 | Com-Iltg-dWatt-LF_OSnone | PGE | Rt3 | New | CZ03 | 3.38 | 0.00076 | 0 | 3.5 | 0.000914 | -0.0239 | 3.38 | 0.00076 | 0 | 3.5 | 0.000914 | -0.0239 |  | LF | None | 3380 | 0.76 | 3380 | 0.76 | 1.04 | 1.2 | -0.007071 | 3380 | 0.76 | 3380 | 0.76 | 1.04 | 1.2 | -0.00707
LFNonePGERt3NewCZ04 | Com-Iltg-dWatt-LF_OSnone | PGE | Rt3 | New | CZ04 | 3.38 | 0.00076 | 0 | 3.63 | 0.000929 | -0.0164 | 3.38 | 0.00076 | 0 | 3.63 | 0.000929 | -0.0164 |  | LF | None | 3380 | 0.76 | 3380 | 0.76 | 1.07 | 1.22 | -0.0048521 | 3380 | 0.76 | 3380 | 0.76 | 1.07 | 1.22 | -0.00485
LFNonePGERt3NewCZ05 | Com-Iltg-dWatt-LF_OSnone | PGE | Rt3 | New | CZ05 | 3.38 | 0.00076 | 0 | 3.53 | 0.000902 | -0.0191 | 3.38 | 0.00076 | 0 | 3.53 | 0.000902 | -0.0191 |  | LF | None | 3380 | 0.76 | 3380 | 0.76 | 1.04 | 1.19 | -0.0056509 | 3380 | 0.76 | 3380 | 0.76 | 1.04 | 1.19 | -0.00565
LFNonePGERt3NewCZ11 | Com-Iltg-dWatt-LF_OSnone | PGE | Rt3 | New | CZ11 | 3.38 | 0.00076 | 0 | 3.63 | 0.00092 | -0.0213 | 3.38 | 0.00076 | 0 | 3.63 | 0.00092 | -0.0213 |  | LF | None | 3380 | 0.76 | 3380 | 0.76 | 1.07 | 1.21 | -0.0063018 | 3380 | 0.76 | 3380 | 0.76 | 1.07 | 1.21 | -0.0063
LFNonePGERt3NewCZ12 | Com-Iltg-dWatt-LF_OSnone | PGE | Rt3 | New | CZ12 | 3.38 | 0.00076 | 0 | 3.63 | 0.00095 | -0.0231 | 3.38 | 0.00076 | 0 | 3.63 | 0.00095 | -0.0231 |  | LF | None | 3380 | 0.76 | 3380 | 0.76 | 1.07 | 1.25 | -0.0068343 | 3380 | 0.76 | 3380 | 0.76 | 1.07 | 1.25 | -0.00683
LFNonePGERt3NewCZ13 | Com-Iltg-dWatt-LF_OSnone | PGE | Rt3 | New | CZ13 | 3.38 | 0.00076 | 0 | 3.67 | 0.000945 | -0.0207 | 3.38 | 0.00076 | 0 | 3.67 | 0.000945 | -0.0207 |  | LF | None | 3380 | 0.76 | 3380 | 0.76 | 1.09 | 1.24 | -0.0061243 | 3380 | 0.76 | 3380 | 0.76 | 1.09 | 1.24 | -0.00612
LFNonePGERt3NewCZ16 | Com-Iltg-dWatt-LF_OSnone | PGE | Rt3 | New | CZ16 | 3.38 | 0.00076 | 0 | 3.34 | 0.000907 | -0.0462 | 3.38 | 0.00076 | 0 | 3.34 | 0.000907 | -0.0462 |  | LF | None | 3380 | 0.76 | 3380 | 0.76 | 0.988 | 1.19 | -0.013669 | 3380 | 0.76 | 3380 | 0.76 | 0.988 | 1.19 | -0.0137
LFNonePGERt3NewIOU | Com-Iltg-dWatt-LF_OSnone | PGE | Rt3 | New | IOU | 3.38 | 0.00076 | 0 | 3.5928 | 0.00093224 | -0.022213 | 3.38 | 0.00076 | 0 | 3.5928 | 0.00093224 | -0.022213 |  | LF | None | 3380 | 0.76 | 3380 | 0.76 | 1.06 | 1.23 | -0.006572 | 3380 | 0.76 | 3380 | 0.76 | 1.06 | 1.23 | -0.00657
LFNonePGERtLExCZ01 | Com-Iltg-dWatt-LF_OSnone | PGE | RtL | Ex | CZ01 | 4.27 | 0.000848 | 0 | 4.15 | 0.00101 | -0.0602 | 4.27 | 0.000848 | 0 | 4.15 | 0.00101 | -0.0602 |  | LF | None | 4270 | 0.848 | 4270 | 0.848 | 0.972 | 1.19 | -0.014098 | 4270 | 0.848 | 4270 | 0.848 | 0.972 | 1.19 | -0.0141
LFNonePGERtLExCZ02 | Com-Iltg-dWatt-LF_OSnone | PGE | RtL | Ex | CZ02 | 4.27 | 0.000848 | 0 | 4.51 | 0.00101 | -0.0301 | 4.27 | 0.000848 | 0 | 4.51 | 0.00101 | -0.0301 |  | LF | None | 4270 | 0.848 | 4270 | 0.848 | 1.06 | 1.19 | -0.0070492 | 4270 | 0.848 | 4270 | 0.848 | 1.06 | 1.19 | -0.00705
LFNonePGERtLExCZ03 | Com-Iltg-dWatt-LF_OSnone | PGE | RtL | Ex | CZ03 | 4.27 | 0.000848 | 0 | 4.53 | 0.001 | -0.0287 | 4.27 | 0.000848 | 0 | 4.53 | 0.001 | -0.0287 |  | LF | None | 4270 | 0.848 | 4270 | 0.848 | 1.06 | 1.18 | -0.0067213 | 4270 | 0.848 | 4270 | 0.848 | 1.06 | 1.18 | -0.00672
LFNonePGERtLExCZ04 | Com-Iltg-dWatt-LF_OSnone | PGE | RtL | Ex | CZ04 | 4.27 | 0.000848 | 0 | 4.61 | 0.00101 | -0.021 | 4.27 | 0.000848 | 0 | 4.61 | 0.00101 | -0.021 |  | LF | None | 4270 | 0.848 | 4270 | 0.848 | 1.08 | 1.19 | -0.004918 | 4270 | 0.848 | 4270 | 0.848 | 1.08 | 1.19 | -0.00492
LFNonePGERtLExCZ05 | Com-Iltg-dWatt-LF_OSnone | PGE | RtL | Ex | CZ05 | 4.27 | 0.000848 | 0 | 4.51 | 0.00099 | -0.0282 | 4.27 | 0.000848 | 0 | 4.51 | 0.00099 | -0.0282 |  | LF | None | 4270 | 0.848 | 4270 | 0.848 | 1.06 | 1.17 | -0.0066042 | 4270 | 0.848 | 4270 | 0.848 | 1.06 | 1.17 | -0.0066
LFNonePGERtLExCZ11 | Com-Iltg-dWatt-LF_OSnone | PGE | RtL | Ex | CZ11 | 4.27 | 0.000848 | 0 | 4.54 | 0.00102 | -0.029 | 4.27 | 0.000848 | 0 | 4.54 | 0.00102 | -0.029 |  | LF | None | 4270 | 0.848 | 4270 | 0.848 | 1.06 | 1.2 | -0.0067916 | 4270 | 0.848 | 4270 | 0.848 | 1.06 | 1.2 | -0.00679
LFNonePGERtLExCZ12 | Com-Iltg-dWatt-LF_OSnone | PGE | RtL | Ex | CZ12 | 4.27 | 0.000848 | 0 | 4.54 | 0.00102 | -0.0265 | 4.27 | 0.000848 | 0 | 4.54 | 0.00102 | -0.0265 |  | LF | None | 4270 | 0.848 | 4270 | 0.848 | 1.06 | 1.2 | -0.0062061 | 4270 | 0.848 | 4270 | 0.848 | 1.06 | 1.2 | -0.00621
LFNonePGERtLExCZ13 | Com-Iltg-dWatt-LF_OSnone | PGE | RtL | Ex | CZ13 | 4.27 | 0.000848 | 0 | 4.58 | 0.00102 | -0.0257 | 4.27 | 0.000848 | 0 | 4.58 | 0.00102 | -0.0257 |  | LF | None | 4270 | 0.848 | 4270 | 0.848 | 1.07 | 1.2 | -0.0060187 | 4270 | 0.848 | 4270 | 0.848 | 1.07 | 1.2 | -0.00602
LFNonePGERtLExCZ16 | Com-Iltg-dWatt-LF_OSnone | PGE | RtL | Ex | CZ16 | 4.27 | 0.000848 | 0 | 4.16 | 0.00098 | -0.0585 | 4.27 | 0.000848 | 0 | 4.16 | 0.00098 | -0.0585 |  | LF | None | 4270 | 0.848 | 4270 | 0.848 | 0.974 | 1.16 | -0.0137 | 4270 | 0.848 | 4270 | 0.848 | 0.974 | 1.16 | -0.0137
LFNonePGERtLExIOU | Com-Iltg-dWatt-LF_OSnone | PGE | RtL | Ex | IOU | 4.27 | 0.000848 | 0 | 4.5442 | 0.0010105 | -0.027201 | 4.27 | 0.000848 | 0 | 4.5442 | 0.0010105 | -0.027201 |  | LF | None | 4270 | 0.848 | 4270 | 0.848 | 1.06 | 1.19 | -0.0063703 | 4270 | 0.848 | 4270 | 0.848 | 1.06 | 1.19 | -0.00637
LFNonePGERtLNewCZ01 | Com-Iltg-dWatt-LF_OSnone | PGE | RtL | New | CZ01 | 4.27 | 0.000848 | 0 | 4.13 | 0.00099 | -0.0653 | 4.27 | 0.000848 | 0 | 4.13 | 0.00099 | -0.0653 |  | LF | None | 4270 | 0.848 | 4270 | 0.848 | 0.967 | 1.17 | -0.015293 | 4270 | 0.848 | 4270 | 0.848 | 0.967 | 1.17 | -0.0153
LFNonePGERtLNewCZ02 | Com-Iltg-dWatt-LF_OSnone | PGE | RtL | New | CZ02 | 4.27 | 0.000848 | 0 | 4.48 | 0.00106 | -0.0339 | 4.27 | 0.000848 | 0 | 4.48 | 0.00106 | -0.0339 |  | LF | None | 4270 | 0.848 | 4270 | 0.848 | 1.05 | 1.25 | -0.0079391 | 4270 | 0.848 | 4270 | 0.848 | 1.05 | 1.25 | -0.00794
LFNonePGERtLNewCZ03 | Com-Iltg-dWatt-LF_OSnone | PGE | RtL | New | CZ03 | 4.27 | 0.000848 | 0 | 4.41 | 0.00103 | -0.0319 | 4.27 | 0.000848 | 0 | 4.41 | 0.00103 | -0.0319 |  | LF | None | 4270 | 0.848 | 4270 | 0.848 | 1.03 | 1.21 | -0.0074707 | 4270 | 0.848 | 4270 | 0.848 | 1.03 | 1.21 | -0.00747
LFNonePGERtLNewCZ04 | Com-Iltg-dWatt-LF_OSnone | PGE | RtL | New | CZ04 | 4.27 | 0.000848 | 0 | 4.57 | 0.00104 | -0.0238 | 4.27 | 0.000848 | 0 | 4.57 | 0.00104 | -0.0238 |  | LF | None | 4270 | 0.848 | 4270 | 0.848 | 1.07 | 1.23 | -0.0055738 | 4270 | 0.848 | 4270 | 0.848 | 1.07 | 1.23 | -0.00557
LFNonePGERtLNewCZ05 | Com-Iltg-dWatt-LF_OSnone | PGE | RtL | New | CZ05 | 4.27 | 0.000848 | 0 | 4.42 | 0.001 | -0.0329 | 4.27 | 0.000848 | 0 | 4.42 | 0.001 | -0.0329 |  | LF | None | 4270 | 0.848 | 4270 | 0.848 | 1.04 | 1.18 | -0.0077049 | 4270 | 0.848 | 4270 | 0.848 | 1.04 | 1.18 | -0.0077
LFNonePGERtLNewCZ11 | Com-Iltg-dWatt-LF_OSnone | PGE | RtL | New | CZ11 | 4.27 | 0.000848 | 0 | 4.61 | 0.00106 | -0.0307 | 4.27 | 0.000848 | 0 | 4.61 | 0.00106 | -0.0307 |  | LF | None | 4270 | 0.848 | 4270 | 0.848 | 1.08 | 1.25 | -0.0071897 | 4270 | 0.848 | 4270 | 0.848 | 1.08 | 1.25 | -0.00719
LFNonePGERtLNewCZ12 | Com-Iltg-dWatt-LF_OSnone | PGE | RtL | New | CZ12 | 4.27 | 0.000848 | 0 | 4.58 | 0.00107 | -0.0301 | 4.27 | 0.000848 | 0 | 4.58 | 0.00107 | -0.0301 |  | LF | None | 4270 | 0.848 | 4270 | 0.848 | 1.07 | 1.26 | -0.0070492 | 4270 | 0.848 | 4270 | 0.848 | 1.07 | 1.26 | -0.00705
LFNonePGERtLNewCZ13 | Com-Iltg-dWatt-LF_OSnone | PGE | RtL | New | CZ13 | 4.27 | 0.000848 | 0 | 4.63 | 0.00106 | -0.0286 | 4.27 | 0.000848 | 0 | 4.63 | 0.00106 | -0.0286 |  | LF | None | 4270 | 0.848 | 4270 | 0.848 | 1.08 | 1.25 | -0.0066979 | 4270 | 0.848 | 4270 | 0.848 | 1.08 | 1.25 | -0.0067
LFNonePGERtLNewCZ16 | Com-Iltg-dWatt-LF_OSnone | PGE | RtL | New | CZ16 | 4.27 | 0.000848 | 0 | 4.21 | 0.00102 | -0.0619 | 4.27 | 0.000848 | 0 | 4.21 | 0.00102 | -0.0619 |  | LF | None | 4270 | 0.848 | 4270 | 0.848 | 0.986 | 1.2 | -0.014496 | 4270 | 0.848 | 4270 | 0.848 | 0.986 | 1.2 | -0.0145
LFNonePGERtLNewIOU | Com-Iltg-dWatt-LF_OSnone | PGE | RtL | New | IOU | 4.27 | 0.000848 | 0 | 4.5309 | 0.0010502 | -0.030225 | 4.27 | 0.000848 | 0 | 4.5309 | 0.0010502 | -0.030225 |  | LF | None | 4270 | 0.848 | 4270 | 0.848 | 1.06 | 1.24 | -0.0070784 | 4270 | 0.848 | 4270 | 0.848 | 1.06 | 1.24 | -0.00708
LFNonePGERtSExCZ01 | Com-Iltg-dWatt-LF_OSnone | PGE | RtS | Ex | CZ01 | 3.38 | 0.000875 | 0 | 3.29 | 0.00101 | -0.0408 | 3.38 | 0.000875 | 0 | 3.29 | 0.00101 | -0.0408 |  | LF | None | 3380 | 0.875 | 3380 | 0.875 | 0.973 | 1.15 | -0.012071 | 3380 | 0.875 | 3380 | 0.875 | 0.973 | 1.15 | -0.0121
LFNonePGERtSExCZ02 | Com-Iltg-dWatt-LF_OSnone | PGE | RtS | Ex | CZ02 | 3.38 | 0.000875 | 0 | 3.57 | 0.00102 | -0.0217 | 3.38 | 0.000875 | 0 | 3.57 | 0.00102 | -0.0217 |  | LF | None | 3380 | 0.875 | 3380 | 0.875 | 1.06 | 1.17 | -0.0064201 | 3380 | 0.875 | 3380 | 0.875 | 1.06 | 1.17 | -0.00642
LFNonePGERtSExCZ03 | Com-Iltg-dWatt-LF_OSnone | PGE | RtS | Ex | CZ03 | 3.38 | 0.000875 | 0 | 3.57 | 0.00103 | -0.0201 | 3.38 | 0.000875 | 0 | 3.57 | 0.00103 | -0.0201 |  | LF | None | 3380 | 0.875 | 3380 | 0.875 | 1.06 | 1.18 | -0.0059467 | 3380 | 0.875 | 3380 | 0.875 | 1.06 | 1.18 | -0.00595
LFNonePGERtSExCZ04 | Com-Iltg-dWatt-LF_OSnone | PGE | RtS | Ex | CZ04 | 3.38 | 0.000875 | 0 | 3.64 | 0.00104 | -0.0146 | 3.38 | 0.000875 | 0 | 3.64 | 0.00104 | -0.0146 |  | LF | None | 3380 | 0.875 | 3380 | 0.875 | 1.08 | 1.19 | -0.0043195 | 3380 | 0.875 | 3380 | 0.875 | 1.08 | 1.19 | -0.00432
LFNonePGERtSExCZ05 | Com-Iltg-dWatt-LF_OSnone | PGE | RtS | Ex | CZ05 | 3.38 | 0.000875 | 0 | 3.58 | 0.00102 | -0.0167 | 3.38 | 0.000875 | 0 | 3.58 | 0.00102 | -0.0167 |  | LF | None | 3380 | 0.875 | 3380 | 0.875 | 1.06 | 1.17 | -0.0049408 | 3380 | 0.875 | 3380 | 0.875 | 1.06 | 1.17 | -0.00494
LFNonePGERtSExCZ11 | Com-Iltg-dWatt-LF_OSnone | PGE | RtS | Ex | CZ11 | 3.38 | 0.000875 | 0 | 3.59 | 0.00104 | -0.0209 | 3.38 | 0.000875 | 0 | 3.59 | 0.00104 | -0.0209 |  | LF | None | 3380 | 0.875 | 3380 | 0.875 | 1.06 | 1.19 | -0.0061834 | 3380 | 0.875 | 3380 | 0.875 | 1.06 | 1.19 | -0.00618
LFNonePGERtSExCZ12 | Com-Iltg-dWatt-LF_OSnone | PGE | RtS | Ex | CZ12 | 3.38 | 0.000875 | 0 | 3.58 | 0.00104 | -0.021 | 3.38 | 0.000875 | 0 | 3.58 | 0.00104 | -0.021 |  | LF | None | 3380 | 0.875 | 3380 | 0.875 | 1.06 | 1.19 | -0.006213 | 3380 | 0.875 | 3380 | 0.875 | 1.06 | 1.19 | -0.00621
LFNonePGERtSExCZ13 | Com-Iltg-dWatt-LF_OSnone | PGE | RtS | Ex | CZ13 | 3.38 | 0.000875 | 0 | 3.6 | 0.00104 | -0.0196 | 3.38 | 0.000875 | 0 | 3.6 | 0.00104 | -0.0196 |  | LF | None | 3380 | 0.875 | 3380 | 0.875 | 1.07 | 1.19 | -0.0057988 | 3380 | 0.875 | 3380 | 0.875 | 1.07 | 1.19 | -0.0058
LFNonePGERtSExCZ16 | Com-Iltg-dWatt-LF_OSnone | PGE | RtS | Ex | CZ16 | 3.38 | 0.000875 | 0 | 3.33 | 0.00102 | -0.0398 | 3.38 | 0.000875 | 0 | 3.33 | 0.00102 | -0.0398 |  | LF | None | 3380 | 0.875 | 3380 | 0.875 | 0.985 | 1.17 | -0.011775 | 3380 | 0.875 | 3380 | 0.875 | 0.985 | 1.17 | -0.0118
LFNonePGERtSExIOU | Com-Iltg-dWatt-LF_OSnone | PGE | RtS | Ex | IOU | 3.38 | 0.000875 | 0 | 3.5841 | 0.0010345 | -0.019814 | 3.38 | 0.000875 | 0 | 3.5841 | 0.0010345 | -0.019814 |  | LF | None | 3380 | 0.875 | 3380 | 0.875 | 1.06 | 1.18 | -0.005862 | 3380 | 0.875 | 3380 | 0.875 | 1.06 | 1.18 | -0.00586
LFNonePGERtSNewCZ01 | Com-Iltg-dWatt-LF_OSnone | PGE | RtS | New | CZ01 | 3.38 | 0.000875 | 0 | 3.29 | 0.000996 | -0.0459 | 3.38 | 0.000875 | 0 | 3.29 | 0.000996 | -0.0459 |  | LF | None | 3380 | 0.875 | 3380 | 0.875 | 0.973 | 1.14 | -0.01358 | 3380 | 0.875 | 3380 | 0.875 | 0.973 | 1.14 | -0.0136
LFNonePGERtSNewCZ02 | Com-Iltg-dWatt-LF_OSnone | PGE | RtS | New | CZ02 | 3.38 | 0.000875 | 0 | 3.55 | 0.00105 | -0.024 | 3.38 | 0.000875 | 0 | 3.55 | 0.00105 | -0.024 |  | LF | None | 3380 | 0.875 | 3380 | 0.875 | 1.05 | 1.2 | -0.0071006 | 3380 | 0.875 | 3380 | 0.875 | 1.05 | 1.2 | -0.0071
LFNonePGERtSNewCZ03 | Com-Iltg-dWatt-LF_OSnone | PGE | RtS | New | CZ03 | 3.38 | 0.000875 | 0 | 3.43 | 0.001 | -0.0221 | 3.38 | 0.000875 | 0 | 3.43 | 0.001 | -0.0221 |  | LF | None | 3380 | 0.875 | 3380 | 0.875 | 1.01 | 1.14 | -0.0065385 | 3380 | 0.875 | 3380 | 0.875 | 1.01 | 1.14 | -0.00654
LFNonePGERtSNewCZ04 | Com-Iltg-dWatt-LF_OSnone | PGE | RtS | New | CZ04 | 3.38 | 0.000875 | 0 | 3.6 | 0.00104 | -0.0166 | 3.38 | 0.000875 | 0 | 3.6 | 0.00104 | -0.0166 |  | LF | None | 3380 | 0.875 | 3380 | 0.875 | 1.07 | 1.19 | -0.0049112 | 3380 | 0.875 | 3380 | 0.875 | 1.07 | 1.19 | -0.00491
LFNonePGERtSNewCZ05 | Com-Iltg-dWatt-LF_OSnone | PGE | RtS | New | CZ05 | 3.38 | 0.000875 | 0 | 3.51 | 0.00101 | -0.0192 | 3.38 | 0.000875 | 0 | 3.51 | 0.00101 | -0.0192 |  | LF | None | 3380 | 0.875 | 3380 | 0.875 | 1.04 | 1.15 | -0.0056805 | 3380 | 0.875 | 3380 | 0.875 | 1.04 | 1.15 | -0.00568
LFNonePGERtSNewCZ11 | Com-Iltg-dWatt-LF_OSnone | PGE | RtS | New | CZ11 | 3.38 | 0.000875 | 0 | 3.64 | 0.00107 | -0.0208 | 3.38 | 0.000875 | 0 | 3.64 | 0.00107 | -0.0208 |  | LF | None | 3380 | 0.875 | 3380 | 0.875 | 1.08 | 1.22 | -0.0061538 | 3380 | 0.875 | 3380 | 0.875 | 1.08 | 1.22 | -0.00615
LFNonePGERtSNewCZ12 | Com-Iltg-dWatt-LF_OSnone | PGE | RtS | New | CZ12 | 3.38 | 0.000875 | 0 | 3.61 | 0.00106 | -0.0223 | 3.38 | 0.000875 | 0 | 3.61 | 0.00106 | -0.0223 |  | LF | None | 3380 | 0.875 | 3380 | 0.875 | 1.07 | 1.21 | -0.0065976 | 3380 | 0.875 | 3380 | 0.875 | 1.07 | 1.21 | -0.0066
LFNonePGERtSNewCZ13 | Com-Iltg-dWatt-LF_OSnone | PGE | RtS | New | CZ13 | 3.38 | 0.000875 | 0 | 3.63 | 0.00105 | -0.0203 | 3.38 | 0.000875 | 0 | 3.63 | 0.00105 | -0.0203 |  | LF | None | 3380 | 0.875 | 3380 | 0.875 | 1.07 | 1.2 | -0.0060059 | 3380 | 0.875 | 3380 | 0.875 | 1.07 | 1.2 | -0.00601
LFNonePGERtSNewCZ16 | Com-Iltg-dWatt-LF_OSnone | PGE | RtS | New | CZ16 | 3.38 | 0.000875 | 0 | 3.34 | 0.00102 | -0.0425 | 3.38 | 0.000875 | 0 | 3.34 | 0.00102 | -0.0425 |  | LF | None | 3380 | 0.875 | 3380 | 0.875 | 0.988 | 1.17 | -0.012574 | 3380 | 0.875 | 3380 | 0.875 | 0.988 | 1.17 | -0.0126
LFNonePGERtSNewIOU | Com-Iltg-dWatt-LF_OSnone | PGE | RtS | New | IOU | 3.38 | 0.000875 | 0 | 3.558 | 0.0010383 | -0.021348 | 3.38 | 0.000875 | 0 | 3.558 | 0.0010383 | -0.021348 |  | LF | None | 3380 | 0.875 | 3380 | 0.875 | 1.05 | 1.19 | -0.006316 | 3380 | 0.875 | 3380 | 0.875 | 1.05 | 1.19 | -0.00632
LFNonePGESCnExCZ01 | Com-Iltg-dWatt-LF_OSnone | PGE | SCn | Ex | CZ01 | 3.42 | 0.0007 | 0 | 2.89 | 0.0007 | -0.0582 | 3.42 | 0.0007 | 0 | 2.89 | 0.0007 | -0.0582 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 0.845 | 1 | -0.017018 | 3420 | 0.7 | 3420 | 0.7 | 0.845 | 1 | -0.017
LFNonePGESCnExCZ02 | Com-Iltg-dWatt-LF_OSnone | PGE | SCn | Ex | CZ02 | 3.42 | 0.0007 | 0 | 3.27 | 0.000882 | -0.0313 | 3.42 | 0.0007 | 0 | 3.27 | 0.000882 | -0.0313 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 0.956 | 1.26 | -0.009152 | 3420 | 0.7 | 3420 | 0.7 | 0.956 | 1.26 | -0.00915
LFNonePGESCnExCZ03 | Com-Iltg-dWatt-LF_OSnone | PGE | SCn | Ex | CZ03 | 3.42 | 0.0007 | 0 | 3.14 | 0.000938 | -0.0346 | 3.42 | 0.0007 | 0 | 3.14 | 0.000938 | -0.0346 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 0.918 | 1.34 | -0.010117 | 3420 | 0.7 | 3420 | 0.7 | 0.918 | 1.34 | -0.0101
LFNonePGESCnExCZ04 | Com-Iltg-dWatt-LF_OSnone | PGE | SCn | Ex | CZ04 | 3.42 | 0.0007 | 0 | 3.35 | 0.000881 | -0.0275 | 3.42 | 0.0007 | 0 | 3.35 | 0.000881 | -0.0275 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 0.98 | 1.26 | -0.0080409 | 3420 | 0.7 | 3420 | 0.7 | 0.98 | 1.26 | -0.00804
LFNonePGESCnExCZ05 | Com-Iltg-dWatt-LF_OSnone | PGE | SCn | Ex | CZ05 | 3.42 | 0.0007 | 0 | 3.12 | 0.000841 | -0.0349 | 3.42 | 0.0007 | 0 | 3.12 | 0.000841 | -0.0349 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 0.912 | 1.2 | -0.010205 | 3420 | 0.7 | 3420 | 0.7 | 0.912 | 1.2 | -0.0102
LFNonePGESCnExCZ11 | Com-Iltg-dWatt-LF_OSnone | PGE | SCn | Ex | CZ11 | 3.42 | 0.0007 | 0 | 3.35 | 0.000857 | -0.0287 | 3.42 | 0.0007 | 0 | 3.35 | 0.000857 | -0.0287 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 0.98 | 1.22 | -0.0083918 | 3420 | 0.7 | 3420 | 0.7 | 0.98 | 1.22 | -0.00839
LFNonePGESCnExCZ12 | Com-Iltg-dWatt-LF_OSnone | PGE | SCn | Ex | CZ12 | 3.42 | 0.0007 | 0 | 3.36 | 0.00087 | -0.0288 | 3.42 | 0.0007 | 0 | 3.36 | 0.00087 | -0.0288 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 0.982 | 1.24 | -0.0084211 | 3420 | 0.7 | 3420 | 0.7 | 0.982 | 1.24 | -0.00842
LFNonePGESCnExCZ13 | Com-Iltg-dWatt-LF_OSnone | PGE | SCn | Ex | CZ13 | 3.42 | 0.0007 | 0 | 3.39 | 0.000853 | -0.0257 | 3.42 | 0.0007 | 0 | 3.39 | 0.000853 | -0.0257 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 0.991 | 1.22 | -0.0075146 | 3420 | 0.7 | 3420 | 0.7 | 0.991 | 1.22 | -0.00751
LFNonePGESCnExCZ16 | Com-Iltg-dWatt-LF_OSnone | PGE | SCn | Ex | CZ16 | 3.42 | 0.0007 | 0 | 3.04 | 0.000838 | -0.0404 | 3.42 | 0.0007 | 0 | 3.04 | 0.000838 | -0.0404 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 0.889 | 1.2 | -0.011813 | 3420 | 0.7 | 3420 | 0.7 | 0.889 | 1.2 | -0.0118
LFNonePGESCnExIOU | Com-Iltg-dWatt-LF_OSnone | PGE | SCn | Ex | IOU | 3.42 | 0.0007 | 0 | 3.2727 | 0.0008903 | -0.030715 | 3.42 | 0.0007 | 0 | 3.2727 | 0.0008903 | -0.030715 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 0.957 | 1.27 | -0.0089809 | 3420 | 0.7 | 3420 | 0.7 | 0.957 | 1.27 | -0.00898
LFNonePGESCnNewCZ01 | Com-Iltg-dWatt-LF_OSnone | PGE | SCn | New | CZ01 | 3.42 | 0.0007 | 0 | 2.93 | 0.0007 | -0.0623 | 3.42 | 0.0007 | 0 | 2.93 | 0.0007 | -0.0623 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 0.857 | 1 | -0.018216 | 3420 | 0.7 | 3420 | 0.7 | 0.857 | 1 | -0.0182
LFNonePGESCnNewCZ02 | Com-Iltg-dWatt-LF_OSnone | PGE | SCn | New | CZ02 | 3.42 | 0.0007 | 0 | 3.26 | 0.000854 | -0.0325 | 3.42 | 0.0007 | 0 | 3.26 | 0.000854 | -0.0325 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 0.953 | 1.22 | -0.0095029 | 3420 | 0.7 | 3420 | 0.7 | 0.953 | 1.22 | -0.0095
LFNonePGESCnNewCZ03 | Com-Iltg-dWatt-LF_OSnone | PGE | SCn | New | CZ03 | 3.42 | 0.0007 | 0 | 3.16 | 0.000878 | -0.0366 | 3.42 | 0.0007 | 0 | 3.16 | 0.000878 | -0.0366 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 0.924 | 1.25 | -0.010702 | 3420 | 0.7 | 3420 | 0.7 | 0.924 | 1.25 | -0.0107
LFNonePGESCnNewCZ04 | Com-Iltg-dWatt-LF_OSnone | PGE | SCn | New | CZ04 | 3.42 | 0.0007 | 0 | 3.34 | 0.000846 | -0.029 | 3.42 | 0.0007 | 0 | 3.34 | 0.000846 | -0.029 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 0.977 | 1.21 | -0.0084795 | 3420 | 0.7 | 3420 | 0.7 | 0.977 | 1.21 | -0.00848
LFNonePGESCnNewCZ05 | Com-Iltg-dWatt-LF_OSnone | PGE | SCn | New | CZ05 | 3.42 | 0.0007 | 0 | 3.13 | 0.00084 | -0.0366 | 3.42 | 0.0007 | 0 | 3.13 | 0.00084 | -0.0366 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 0.915 | 1.2 | -0.010702 | 3420 | 0.7 | 3420 | 0.7 | 0.915 | 1.2 | -0.0107
LFNonePGESCnNewCZ11 | Com-Iltg-dWatt-LF_OSnone | PGE | SCn | New | CZ11 | 3.42 | 0.0007 | 0 | 3.34 | 0.000836 | -0.0297 | 3.42 | 0.0007 | 0 | 3.34 | 0.000836 | -0.0297 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 0.977 | 1.19 | -0.0086842 | 3420 | 0.7 | 3420 | 0.7 | 0.977 | 1.19 | -0.00868
LFNonePGESCnNewCZ12 | Com-Iltg-dWatt-LF_OSnone | PGE | SCn | New | CZ12 | 3.42 | 0.0007 | 0 | 3.34 | 0.000841 | -0.03 | 3.42 | 0.0007 | 0 | 3.34 | 0.000841 | -0.03 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 0.977 | 1.2 | -0.0087719 | 3420 | 0.7 | 3420 | 0.7 | 0.977 | 1.2 | -0.00877
LFNonePGESCnNewCZ13 | Com-Iltg-dWatt-LF_OSnone | PGE | SCn | New | CZ13 | 3.42 | 0.0007 | 0 | 3.32 | 0.000818 | -0.026 | 3.42 | 0.0007 | 0 | 3.32 | 0.000818 | -0.026 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 0.971 | 1.17 | -0.0076023 | 3420 | 0.7 | 3420 | 0.7 | 0.971 | 1.17 | -0.0076
LFNonePGESCnNewCZ16 | Com-Iltg-dWatt-LF_OSnone | PGE | SCn | New | CZ16 | 3.42 | 0.0007 | 0 | 3.03 | 0.000813 | -0.0424 | 3.42 | 0.0007 | 0 | 3.03 | 0.000813 | -0.0424 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 0.886 | 1.16 | -0.012398 | 3420 | 0.7 | 3420 | 0.7 | 0.886 | 1.16 | -0.0124
LFNonePGESCnNewIOU | Com-Iltg-dWatt-LF_OSnone | PGE | SCn | New | IOU | 3.42 | 0.0007 | 0 | 3.2826 | 0.00084434 | -0.031164 | 3.42 | 0.0007 | 0 | 3.2826 | 0.00084434 | -0.031164 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 0.96 | 1.21 | -0.0091122 | 3420 | 0.7 | 3420 | 0.7 | 0.96 | 1.21 | -0.00911
LFNonePGESUnExCZ01 | Com-Iltg-dWatt-LF_OSnone | PGE | SUn | Ex | CZ01 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0 | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0
LFNonePGESUnExCZ02 | Com-Iltg-dWatt-LF_OSnone | PGE | SUn | Ex | CZ02 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0 | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0
LFNonePGESUnExCZ03 | Com-Iltg-dWatt-LF_OSnone | PGE | SUn | Ex | CZ03 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0 | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0
LFNonePGESUnExCZ04 | Com-Iltg-dWatt-LF_OSnone | PGE | SUn | Ex | CZ04 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0 | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0
LFNonePGESUnExCZ05 | Com-Iltg-dWatt-LF_OSnone | PGE | SUn | Ex | CZ05 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0 | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0
LFNonePGESUnExCZ11 | Com-Iltg-dWatt-LF_OSnone | PGE | SUn | Ex | CZ11 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0 | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0
LFNonePGESUnExCZ12 | Com-Iltg-dWatt-LF_OSnone | PGE | SUn | Ex | CZ12 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0 | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0
LFNonePGESUnExCZ13 | Com-Iltg-dWatt-LF_OSnone | PGE | SUn | Ex | CZ13 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0 | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0
LFNonePGESUnExCZ16 | Com-Iltg-dWatt-LF_OSnone | PGE | SUn | Ex | CZ16 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0 | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0
LFNonePGESUnExIOU | Com-Iltg-dWatt-LF_OSnone | PGE | SUn | Ex | IOU | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0 | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0
LFNonePGESUnNewCZ01 | Com-Iltg-dWatt-LF_OSnone | PGE | SUn | New | CZ01 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0 | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0
LFNonePGESUnNewCZ02 | Com-Iltg-dWatt-LF_OSnone | PGE | SUn | New | CZ02 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0 | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0
LFNonePGESUnNewCZ03 | Com-Iltg-dWatt-LF_OSnone | PGE | SUn | New | CZ03 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0 | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0
LFNonePGESUnNewCZ04 | Com-Iltg-dWatt-LF_OSnone | PGE | SUn | New | CZ04 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0 | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0
LFNonePGESUnNewCZ05 | Com-Iltg-dWatt-LF_OSnone | PGE | SUn | New | CZ05 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0 | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0
LFNonePGESUnNewCZ11 | Com-Iltg-dWatt-LF_OSnone | PGE | SUn | New | CZ11 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0 | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0
LFNonePGESUnNewCZ12 | Com-Iltg-dWatt-LF_OSnone | PGE | SUn | New | CZ12 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0 | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0
LFNonePGESUnNewCZ13 | Com-Iltg-dWatt-LF_OSnone | PGE | SUn | New | CZ13 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0 | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0
LFNonePGESUnNewCZ16 | Com-Iltg-dWatt-LF_OSnone | PGE | SUn | New | CZ16 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0 | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0
LFNonePGESUnNewIOU | Com-Iltg-dWatt-LF_OSnone | PGE | SUn | New | IOU | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0 | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0
LFNonePGEWRfExCZ01 | Com-Iltg-dWatt-LF_OSnone | PGE | WRf | Ex | CZ01 | 4.77 | 0.000556 | 0 | 7.36 | 0.00077 | 0 | 4.77 | 0.000556 | 0 | 7.36 | 0.00077 | 0 |  | LF | None | 4770 | 0.556 | 4770 | 0.556 | 1.54 | 1.38 | 0 | 4770 | 0.556 | 4770 | 0.556 | 1.54 | 1.38 | 0
LFNonePGEWRfExCZ02 | Com-Iltg-dWatt-LF_OSnone | PGE | WRf | Ex | CZ02 | 4.77 | 0.000556 | 0 | 7.5636 | 0.00072 | 0 | 4.77 | 0.000556 | 0 | 7.5636 | 0.00072 | 0 |  | LF | None | 4770 | 0.556 | 4770 | 0.556 | 1.59 | 1.29 | 0 | 4770 | 0.556 | 4770 | 0.556 | 1.59 | 1.29 | 0
LFNonePGEWRfExCZ03 | Com-Iltg-dWatt-LF_OSnone | PGE | WRf | Ex | CZ03 | 4.77 | 0.000556 | 0 | 7.7835 | 0.000735 | 0 | 4.77 | 0.000556 | 0 | 7.7835 | 0.000735 | 0 |  | LF | None | 4770 | 0.556 | 4770 | 0.556 | 1.63 | 1.32 | 0 | 4770 | 0.556 | 4770 | 0.556 | 1.63 | 1.32 | 0
LFNonePGEWRfExCZ04 | Com-Iltg-dWatt-LF_OSnone | PGE | WRf | Ex | CZ04 | 4.77 | 0.000556 | 0 | 7.71 | 0.000733 | 0 | 4.77 | 0.000556 | 0 | 7.71 | 0.000733 | 0 |  | LF | None | 4770 | 0.556 | 4770 | 0.556 | 1.62 | 1.32 | 0 | 4770 | 0.556 | 4770 | 0.556 | 1.62 | 1.32 | 0
LFNonePGEWRfExCZ05 | Com-Iltg-dWatt-LF_OSnone | PGE | WRf | Ex | CZ05 | 4.77 | 0.000556 | 0 | 7.55 | 0.000718 | 0 | 4.77 | 0.000556 | 0 | 7.55 | 0.000718 | 0 |  | LF | None | 4770 | 0.556 | 4770 | 0.556 | 1.58 | 1.29 | 0 | 4770 | 0.556 | 4770 | 0.556 | 1.58 | 1.29 | 0
LFNonePGEWRfExCZ11 | Com-Iltg-dWatt-LF_OSnone | PGE | WRf | Ex | CZ11 | 4.77 | 0.000556 | 0 | 7.37 | 0.000768 | 0 | 4.77 | 0.000556 | 0 | 7.37 | 0.000768 | 0 |  | LF | None | 4770 | 0.556 | 4770 | 0.556 | 1.55 | 1.38 | 0 | 4770 | 0.556 | 4770 | 0.556 | 1.55 | 1.38 | 0
LFNonePGEWRfExCZ12 | Com-Iltg-dWatt-LF_OSnone | PGE | WRf | Ex | CZ12 | 4.77 | 0.000556 | 0 | 7.4708 | 0.000738 | 0 | 4.77 | 0.000556 | 0 | 7.4708 | 0.000738 | 0 |  | LF | None | 4770 | 0.556 | 4770 | 0.556 | 1.57 | 1.33 | 0 | 4770 | 0.556 | 4770 | 0.556 | 1.57 | 1.33 | 0
LFNonePGEWRfExCZ13 | Com-Iltg-dWatt-LF_OSnone | PGE | WRf | Ex | CZ13 | 4.77 | 0.000556 | 0 | 7.4506 | 0.000702 | 0 | 4.77 | 0.000556 | 0 | 7.4506 | 0.000702 | 0 |  | LF | None | 4770 | 0.556 | 4770 | 0.556 | 1.56 | 1.26 | 0 | 4770 | 0.556 | 4770 | 0.556 | 1.56 | 1.26 | 0
LFNonePGEWRfExCZ16 | Com-Iltg-dWatt-LF_OSnone | PGE | WRf | Ex | CZ16 | 4.77 | 0.000556 | 0 | 6.6207 | 0.000771 | -0.00033707 | 4.77 | 0.000556 | 0 | 6.6207 | 0.000771 | -0.00033707 |  | LF | None | 4770 | 0.556 | 4770 | 0.556 | 1.39 | 1.39 | -7.0664e-05 | 4770 | 0.556 | 4770 | 0.556 | 1.39 | 1.39 | -7.07e-05
LFNonePGEWRfExIOU | Com-Iltg-dWatt-LF_OSnone | PGE | WRf | Ex | IOU | 4.77 | 0.000556 | 0 | 7.586 | 0.00072647 | -1.3151e-07 | 4.77 | 0.000556 | 0 | 7.586 | 0.00072647 | -1.3151e-07 |  | LF | None | 4770 | 0.556 | 4770 | 0.556 | 1.59 | 1.31 | -2.7571e-08 | 4770 | 0.556 | 4770 | 0.556 | 1.59 | 1.31 | -2.76e-08
LFNonePGEWRfNewCZ01 | Com-Iltg-dWatt-LF_OSnone | PGE | WRf | New | CZ01 | 4.77 | 0.000556 | 0 | 6.05 | 0.000693 | 0 | 4.77 | 0.000556 | 0 | 6.05 | 0.000693 | 0 |  | LF | None | 4770 | 0.556 | 4770 | 0.556 | 1.27 | 1.25 | 0 | 4770 | 0.556 | 4770 | 0.556 | 1.27 | 1.25 | 0
LFNonePGEWRfNewCZ02 | Com-Iltg-dWatt-LF_OSnone | PGE | WRf | New | CZ02 | 4.77 | 0.000556 | 0 | 6.52 | 0.000909 | 0 | 4.77 | 0.000556 | 0 | 6.52 | 0.000909 | 0 |  | LF | None | 4770 | 0.556 | 4770 | 0.556 | 1.37 | 1.63 | 0 | 4770 | 0.556 | 4770 | 0.556 | 1.37 | 1.63 | 0
LFNonePGEWRfNewCZ03 | Com-Iltg-dWatt-LF_OSnone | PGE | WRf | New | CZ03 | 4.77 | 0.000556 | 0 | 6.3 | 0.00111 | 0 | 4.77 | 0.000556 | 0 | 6.3 | 0.00111 | 0 |  | LF | None | 4770 | 0.556 | 4770 | 0.556 | 1.32 | 2 | 0 | 4770 | 0.556 | 4770 | 0.556 | 1.32 | 2 | 0
LFNonePGEWRfNewCZ04 | Com-Iltg-dWatt-LF_OSnone | PGE | WRf | New | CZ04 | 4.77 | 0.000556 | 0 | 6.65 | 0.00111 | 0 | 4.77 | 0.000556 | 0 | 6.65 | 0.00111 | 0 |  | LF | None | 4770 | 0.556 | 4770 | 0.556 | 1.39 | 2 | 0 | 4770 | 0.556 | 4770 | 0.556 | 1.39 | 2 | 0
LFNonePGEWRfNewCZ05 | Com-Iltg-dWatt-LF_OSnone | PGE | WRf | New | CZ05 | 4.77 | 0.000556 | 0 | 6.17 | 0.000924 | 0 | 4.77 | 0.000556 | 0 | 6.17 | 0.000924 | 0 |  | LF | None | 4770 | 0.556 | 4770 | 0.556 | 1.29 | 1.66 | 0 | 4770 | 0.556 | 4770 | 0.556 | 1.29 | 1.66 | 0
LFNonePGEWRfNewCZ11 | Com-Iltg-dWatt-LF_OSnone | PGE | WRf | New | CZ11 | 4.77 | 0.000556 | 0 | 6.58 | 0.00111 | 0 | 4.77 | 0.000556 | 0 | 6.58 | 0.00111 | 0 |  | LF | None | 4770 | 0.556 | 4770 | 0.556 | 1.38 | 2 | 0 | 4770 | 0.556 | 4770 | 0.556 | 1.38 | 2 | 0
LFNonePGEWRfNewCZ12 | Com-Iltg-dWatt-LF_OSnone | PGE | WRf | New | CZ12 | 4.77 | 0.000556 | 0 | 6.63 | 0.000917 | 0 | 4.77 | 0.000556 | 0 | 6.63 | 0.000917 | 0 |  | LF | None | 4770 | 0.556 | 4770 | 0.556 | 1.39 | 1.65 | 0 | 4770 | 0.556 | 4770 | 0.556 | 1.39 | 1.65 | 0
LFNonePGEWRfNewCZ13 | Com-Iltg-dWatt-LF_OSnone | PGE | WRf | New | CZ13 | 4.77 | 0.000556 | 0 | 6.69 | 0.000696 | 0 | 4.77 | 0.000556 | 0 | 6.69 | 0.000696 | 0 |  | LF | None | 4770 | 0.556 | 4770 | 0.556 | 1.4 | 1.25 | 0 | 4770 | 0.556 | 4770 | 0.556 | 1.4 | 1.25 | 0
LFNonePGEWRfNewCZ16 | Com-Iltg-dWatt-LF_OSnone | PGE | WRf | New | CZ16 | 4.77 | 0.000556 | 0 | 6.01 | 0.00111 | 0 | 4.77 | 0.000556 | 0 | 6.01 | 0.00111 | 0 |  | LF | None | 4770 | 0.556 | 4770 | 0.556 | 1.26 | 2 | 0 | 4770 | 0.556 | 4770 | 0.556 | 1.26 | 2 | 0
LFNonePGEWRfNewIOU | Com-Iltg-dWatt-LF_OSnone | PGE | WRf | New | IOU | 4.77 | 0.000556 | 0 | 6.5604 | 0.00090392 | 0 | 4.77 | 0.000556 | 0 | 6.5604 | 0.00090392 | 0 |  | LF | None | 4770 | 0.556 | 4770 | 0.556 | 1.38 | 1.63 | 0 | 4770 | 0.556 | 4770 | 0.556 | 1.38 | 1.63 | 0
LFNoneSCEAsmExCZ05 | Com-Iltg-dWatt-LF_OSnone | SCE | Asm | Ex | CZ05 | 2.6104 | 0.000532 | 0 | 2.7504 | 0.000636 | -0.026904 | 2.6104 | 0.000532 | 0 | 2.7504 | 0.000636 | -0.026904 |  | LF | None | 2610 | 0.532 | 2610 | 0.532 | 1.05 | 1.2 | -0.010306 | 2610 | 0.532 | 2610 | 0.532 | 1.05 | 1.2 | -0.0103
LFNoneSCEAsmExCZ06 | Com-Iltg-dWatt-LF_OSnone | SCE | Asm | Ex | CZ06 | 2.6147 | 0.000532 | 0 | 2.9347 | 0.000659 | -0.013047 | 2.6147 | 0.000532 | 0 | 2.9347 | 0.000659 | -0.013047 |  | LF | None | 2610 | 0.532 | 2610 | 0.532 | 1.12 | 1.24 | -0.0049899 | 2610 | 0.532 | 2610 | 0.532 | 1.12 | 1.24 | -0.00499
LFNoneSCEAsmExCZ08 | Com-Iltg-dWatt-LF_OSnone | SCE | Asm | Ex | CZ08 | 2.6147 | 0.000532 | 0 | 2.9547 | 0.000642 | -0.011247 | 2.6147 | 0.000532 | 0 | 2.9547 | 0.000642 | -0.011247 |  | LF | None | 2610 | 0.532 | 2610 | 0.532 | 1.13 | 1.21 | -0.0043015 | 2610 | 0.532 | 2610 | 0.532 | 1.13 | 1.21 | -0.0043
LFNoneSCEAsmExCZ09 | Com-Iltg-dWatt-LF_OSnone | SCE | Asm | Ex | CZ09 | 2.6147 | 0.000532 | 0 | 2.9348 | 0.000659 | -0.013648 | 2.6147 | 0.000532 | 0 | 2.9348 | 0.000659 | -0.013648 |  | LF | None | 2610 | 0.532 | 2610 | 0.532 | 1.12 | 1.24 | -0.0052194 | 2610 | 0.532 | 2610 | 0.532 | 1.12 | 1.24 | -0.00522
LFNoneSCEAsmExCZ10 | Com-Iltg-dWatt-LF_OSnone | SCE | Asm | Ex | CZ10 | 2.61 | 0.000532 | 0 | 2.84 | 0.000636 | -0.015 | 2.61 | 0.000532 | 0 | 2.84 | 0.000636 | -0.015 |  | LF | None | 2610 | 0.532 | 2610 | 0.532 | 1.09 | 1.2 | -0.0057471 | 2610 | 0.532 | 2610 | 0.532 | 1.09 | 1.2 | -0.00575
LFNoneSCEAsmExCZ13 | Com-Iltg-dWatt-LF_OSnone | SCE | Asm | Ex | CZ13 | 2.61 | 0.000532 | 0 | 2.79 | 0.000643 | -0.0236 | 2.61 | 0.000532 | 0 | 2.79 | 0.000643 | -0.0236 |  | LF | None | 2610 | 0.532 | 2610 | 0.532 | 1.07 | 1.21 | -0.0090421 | 2610 | 0.532 | 2610 | 0.532 | 1.07 | 1.21 | -0.00904
LFNoneSCEAsmExCZ14 | Com-Iltg-dWatt-LF_OSnone | SCE | Asm | Ex | CZ14 | 2.6112 | 0.000532 | 0 | 2.8012 | 0.000602 | -0.023612 | 2.6112 | 0.000532 | 0 | 2.8012 | 0.000602 | -0.023612 |  | LF | None | 2610 | 0.532 | 2610 | 0.532 | 1.07 | 1.13 | -0.0090426 | 2610 | 0.532 | 2610 | 0.532 | 1.07 | 1.13 | -0.00904
LFNoneSCEAsmExCZ15 | Com-Iltg-dWatt-LF_OSnone | SCE | Asm | Ex | CZ15 | 2.6117 | 0.000532 | 0 | 3.1117 | 0.000631 | -0.006685 | 2.6117 | 0.000532 | 0 | 3.1117 | 0.000631 | -0.006685 |  | LF | None | 2610 | 0.532 | 2610 | 0.532 | 1.19 | 1.19 | -0.0025597 | 2610 | 0.532 | 2610 | 0.532 | 1.19 | 1.19 | -0.00256
LFNoneSCEAsmExCZ16 | Com-Iltg-dWatt-LF_OSnone | SCE | Asm | Ex | CZ16 | 2.6113 | 0.000532 | 0 | 2.5713 | 0.000631 | -0.036813 | 2.6113 | 0.000532 | 0 | 2.5713 | 0.000631 | -0.036813 |  | LF | None | 2610 | 0.532 | 2610 | 0.532 | 0.985 | 1.19 | -0.014098 | 2610 | 0.532 | 2610 | 0.532 | 0.985 | 1.19 | -0.0141
LFNoneSCEAsmExIOU | Com-Iltg-dWatt-LF_OSnone | SCE | Asm | Ex | IOU | 2.6135 | 0.000532 | 0 | 2.9193 | 0.00064488 | -0.013695 | 2.6135 | 0.000532 | 0 | 2.9193 | 0.00064488 | -0.013695 |  | LF | None | 2610 | 0.532 | 2610 | 0.532 | 1.12 | 1.21 | -0.00524 | 2610 | 0.532 | 2610 | 0.532 | 1.12 | 1.21 | -0.00524
LFNoneSCEAsmNewCZ05 | Com-Iltg-dWatt-LF_OSnone | SCE | Asm | New | CZ05 | 2.61 | 0.000532 | 0 | 2.71 | 0.000628 | -0.0277 | 2.61 | 0.000532 | 0 | 2.71 | 0.000628 | -0.0277 |  | LF | None | 2610 | 0.532 | 2610 | 0.532 | 1.04 | 1.18 | -0.010613 | 2610 | 0.532 | 2610 | 0.532 | 1.04 | 1.18 | -0.0106
LFNoneSCEAsmNewCZ06 | Com-Iltg-dWatt-LF_OSnone | SCE | Asm | New | CZ06 | 2.61 | 0.000532 | 0 | 2.83 | 0.000649 | -0.0166 | 2.61 | 0.000532 | 0 | 2.83 | 0.000649 | -0.0166 |  | LF | None | 2610 | 0.532 | 2610 | 0.532 | 1.08 | 1.22 | -0.0063602 | 2610 | 0.532 | 2610 | 0.532 | 1.08 | 1.22 | -0.00636
LFNoneSCEAsmNewCZ08 | Com-Iltg-dWatt-LF_OSnone | SCE | Asm | New | CZ08 | 2.61 | 0.000532 | 0 | 2.86 | 0.000639 | -0.0136 | 2.61 | 0.000532 | 0 | 2.86 | 0.000639 | -0.0136 |  | LF | None | 2610 | 0.532 | 2610 | 0.532 | 1.1 | 1.2 | -0.0052107 | 2610 | 0.532 | 2610 | 0.532 | 1.1 | 1.2 | -0.00521
LFNoneSCEAsmNewCZ09 | Com-Iltg-dWatt-LF_OSnone | SCE | Asm | New | CZ09 | 2.61 | 0.000532 | 0 | 2.84 | 0.000664 | -0.0155 | 2.61 | 0.000532 | 0 | 2.84 | 0.000664 | -0.0155 |  | LF | None | 2610 | 0.532 | 2610 | 0.532 | 1.09 | 1.25 | -0.0059387 | 2610 | 0.532 | 2610 | 0.532 | 1.09 | 1.25 | -0.00594
LFNoneSCEAsmNewCZ10 | Com-Iltg-dWatt-LF_OSnone | SCE | Asm | New | CZ10 | 2.61 | 0.000532 | 0 | 2.84 | 0.000655 | -0.0157 | 2.61 | 0.000532 | 0 | 2.84 | 0.000655 | -0.0157 |  | LF | None | 2610 | 0.532 | 2610 | 0.532 | 1.09 | 1.23 | -0.0060153 | 2610 | 0.532 | 2610 | 0.532 | 1.09 | 1.23 | -0.00602
LFNoneSCEAsmNewCZ13 | Com-Iltg-dWatt-LF_OSnone | SCE | Asm | New | CZ13 | 2.61 | 0.000532 | 0 | 2.79 | 0.000658 | -0.0252 | 2.61 | 0.000532 | 0 | 2.79 | 0.000658 | -0.0252 |  | LF | None | 2610 | 0.532 | 2610 | 0.532 | 1.07 | 1.24 | -0.0096552 | 2610 | 0.532 | 2610 | 0.532 | 1.07 | 1.24 | -0.00966
LFNoneSCEAsmNewCZ14 | Com-Iltg-dWatt-LF_OSnone | SCE | Asm | New | CZ14 | 2.61 | 0.000532 | 0 | 2.78 | 0.000639 | -0.0251 | 2.61 | 0.000532 | 0 | 2.78 | 0.000639 | -0.0251 |  | LF | None | 2610 | 0.532 | 2610 | 0.532 | 1.07 | 1.2 | -0.0096169 | 2610 | 0.532 | 2610 | 0.532 | 1.07 | 1.2 | -0.00962
LFNoneSCEAsmNewCZ15 | Com-Iltg-dWatt-LF_OSnone | SCE | Asm | New | CZ15 | 2.61 | 0.000532 | 0 | 3.04 | 0.000652 | -0.00723 | 2.61 | 0.000532 | 0 | 3.04 | 0.000652 | -0.00723 |  | LF | None | 2610 | 0.532 | 2610 | 0.532 | 1.16 | 1.23 | -0.0027701 | 2610 | 0.532 | 2610 | 0.532 | 1.16 | 1.23 | -0.00277
LFNoneSCEAsmNewCZ16 | Com-Iltg-dWatt-LF_OSnone | SCE | Asm | New | CZ16 | 2.61 | 0.000532 | 0 | 2.59 | 0.000634 | -0.0371 | 2.61 | 0.000532 | 0 | 2.59 | 0.000634 | -0.0371 |  | LF | None | 2610 | 0.532 | 2610 | 0.532 | 0.992 | 1.19 | -0.014215 | 2610 | 0.532 | 2610 | 0.532 | 0.992 | 1.19 | -0.0142
LFNoneSCEAsmNewIOU | Com-Iltg-dWatt-LF_OSnone | SCE | Asm | New | IOU | 2.61 | 0.000532 | 0 | 2.8527 | 0.00064964 | -0.015813 | 2.61 | 0.000532 | 0 | 2.8527 | 0.00064964 | -0.015813 |  | LF | None | 2610 | 0.532 | 2610 | 0.532 | 1.09 | 1.22 | -0.0060585 | 2610 | 0.532 | 2610 | 0.532 | 1.09 | 1.22 | -0.00606
LFNoneSCEComExCZ05 | Com-Iltg-dWatt-LF_OSnone | SCE | Com | Ex | CZ05 | 3.6166 | 0.00073884 | 0 | 3.8771 | 0.00091258 | -0.02978 | 3.6166 | 0.00073884 | 0 | 3.8771 | 0.00091258 | -0.02978 |  | LF | None | 3620 | 0.739 | 3620 | 0.739 | 1.07 | 1.24 | -0.0082342 | 3620 | 0.739 | 3620 | 0.739 | 1.07 | 1.24 | -0.00823
LFNoneSCEComExCZ06 | Com-Iltg-dWatt-LF_OSnone | SCE | Com | Ex | CZ06 | 3.1776 | 0.00071349 | 0 | 3.5869 | 0.00089022 | -0.012404 | 3.1776 | 0.00071349 | 0 | 3.5869 | 0.00089022 | -0.012404 |  | LF | None | 3180 | 0.713 | 3180 | 0.713 | 1.13 | 1.25 | -0.0039036 | 3180 | 0.713 | 3180 | 0.713 | 1.13 | 1.25 | -0.0039
LFNoneSCEComExCZ08 | Com-Iltg-dWatt-LF_OSnone | SCE | Com | Ex | CZ08 | 3.2081 | 0.00072384 | 0 | 3.6027 | 0.00089915 | -0.011137 | 3.2081 | 0.00072384 | 0 | 3.6027 | 0.00089915 | -0.011137 |  | LF | None | 3210 | 0.724 | 3210 | 0.724 | 1.12 | 1.24 | -0.0034716 | 3210 | 0.724 | 3210 | 0.724 | 1.12 | 1.24 | -0.00347
LFNoneSCEComExCZ09 | Com-Iltg-dWatt-LF_OSnone | SCE | Com | Ex | CZ09 | 3.1662 | 0.00071915 | 0 | 3.5699 | 0.00091516 | -0.012745 | 3.1662 | 0.00071915 | 0 | 3.5699 | 0.00091516 | -0.012745 |  | LF | None | 3170 | 0.719 | 3170 | 0.719 | 1.13 | 1.27 | -0.0040252 | 3170 | 0.719 | 3170 | 0.719 | 1.13 | 1.27 | -0.00403
LFNoneSCEComExCZ10 | Com-Iltg-dWatt-LF_OSnone | SCE | Com | Ex | CZ10 | 3.3653 | 0.00073441 | 0 | 3.6687 | 0.00090366 | -0.012898 | 3.3653 | 0.00073441 | 0 | 3.6687 | 0.00090366 | -0.012898 |  | LF | None | 3370 | 0.734 | 3370 | 0.734 | 1.09 | 1.23 | -0.0038325 | 3370 | 0.734 | 3370 | 0.734 | 1.09 | 1.23 | -0.00383
LFNoneSCEComExCZ13 | Com-Iltg-dWatt-LF_OSnone | SCE | Com | Ex | CZ13 | 3.3211 | 0.00062649 | 0 | 3.7124 | 0.00077681 | -0.019535 | 3.3211 | 0.00062649 | 0 | 3.7124 | 0.00077681 | -0.019535 |  | LF | None | 3320 | 0.626 | 3320 | 0.626 | 1.12 | 1.24 | -0.0058821 | 3320 | 0.626 | 3320 | 0.626 | 1.12 | 1.24 | -0.00588
LFNoneSCEComExCZ14 | Com-Iltg-dWatt-LF_OSnone | SCE | Com | Ex | CZ14 | 3.259 | 0.00073388 | 0 | 3.5484 | 0.00092089 | -0.021676 | 3.259 | 0.00073388 | 0 | 3.5484 | 0.00092089 | -0.021676 |  | LF | None | 3260 | 0.734 | 3260 | 0.734 | 1.09 | 1.25 | -0.0066512 | 3260 | 0.734 | 3260 | 0.734 | 1.09 | 1.25 | -0.00665
LFNoneSCEComExCZ15 | Com-Iltg-dWatt-LF_OSnone | SCE | Com | Ex | CZ15 | 3.0423 | 0.00067103 | 0 | 3.5837 | 0.00084494 | -0.0053231 | 3.0423 | 0.00067103 | 0 | 3.5837 | 0.00084494 | -0.0053231 |  | LF | None | 3040 | 0.671 | 3040 | 0.671 | 1.18 | 1.26 | -0.0017497 | 3040 | 0.671 | 3040 | 0.671 | 1.18 | 1.26 | -0.00175
LFNoneSCEComExCZ16 | Com-Iltg-dWatt-LF_OSnone | SCE | Com | Ex | CZ16 | 3.0162 | 0.00057776 | 0 | 3.0381 | 0.0007004 | -0.034731 | 3.0162 | 0.00057776 | 0 | 3.0381 | 0.0007004 | -0.034731 |  | LF | None | 3020 | 0.578 | 3020 | 0.578 | 1.01 | 1.21 | -0.011515 | 3020 | 0.578 | 3020 | 0.578 | 1.01 | 1.21 | -0.0115
LFNoneSCEComExIOU | Com-Iltg-dWatt-LF_OSnone | SCE | Com | Ex | IOU | 3.2207 | 0.00071643 | 0 | 3.5979 | 0.00089284 | -0.012782 | 3.2207 | 0.00071643 | 0 | 3.5979 | 0.00089284 | -0.012782 |  | LF | None | 3220 | 0.716 | 3220 | 0.716 | 1.12 | 1.25 | -0.0039688 | 3220 | 0.716 | 3220 | 0.716 | 1.12 | 1.25 | -0.00397
LFNoneSCEComNewCZ05 | Com-Iltg-dWatt-LF_OSnone | SCE | Com | New | CZ05 | 3.7093 | 0.00075638 | 0 | 3.8506 | 0.00092172 | -0.030866 | 3.7093 | 0.00075638 | 0 | 3.8506 | 0.00092172 | -0.030866 |  | LF | None | 3710 | 0.756 | 3710 | 0.756 | 1.04 | 1.22 | -0.0083212 | 3710 | 0.756 | 3710 | 0.756 | 1.04 | 1.22 | -0.00832
LFNoneSCEComNewCZ06 | Com-Iltg-dWatt-LF_OSnone | SCE | Com | New | CZ06 | 3.339 | 0.0007301 | 0 | 3.668 | 0.00089687 | -0.012226 | 3.339 | 0.0007301 | 0 | 3.668 | 0.00089687 | -0.012226 |  | LF | None | 3340 | 0.73 | 3340 | 0.73 | 1.1 | 1.23 | -0.0036618 | 3340 | 0.73 | 3340 | 0.73 | 1.1 | 1.23 | -0.00366
LFNoneSCEComNewCZ08 | Com-Iltg-dWatt-LF_OSnone | SCE | Com | New | CZ08 | 3.3507 | 0.00073504 | 0 | 3.677 | 0.00090479 | -0.01056 | 3.3507 | 0.00073504 | 0 | 3.677 | 0.00090479 | -0.01056 |  | LF | None | 3350 | 0.735 | 3350 | 0.735 | 1.1 | 1.23 | -0.0031517 | 3350 | 0.735 | 3350 | 0.735 | 1.1 | 1.23 | -0.00315
LFNoneSCEComNewCZ09 | Com-Iltg-dWatt-LF_OSnone | SCE | Com | New | CZ09 | 3.2892 | 0.00072667 | 0 | 3.6401 | 0.00092739 | -0.011581 | 3.2892 | 0.00072667 | 0 | 3.6401 | 0.00092739 | -0.011581 |  | LF | None | 3290 | 0.727 | 3290 | 0.727 | 1.11 | 1.28 | -0.0035208 | 3290 | 0.727 | 3290 | 0.727 | 1.11 | 1.28 | -0.00352
LFNoneSCEComNewCZ10 | Com-Iltg-dWatt-LF_OSnone | SCE | Com | New | CZ10 | 3.4063 | 0.00073202 | 0 | 3.6633 | 0.00090395 | -0.011739 | 3.4063 | 0.00073202 | 0 | 3.6633 | 0.00090395 | -0.011739 |  | LF | None | 3410 | 0.732 | 3410 | 0.732 | 1.08 | 1.23 | -0.0034462 | 3410 | 0.732 | 3410 | 0.732 | 1.08 | 1.23 | -0.00345
LFNoneSCEComNewCZ13 | Com-Iltg-dWatt-LF_OSnone | SCE | Com | New | CZ13 | 3.4238 | 0.00065194 | 0 | 3.8216 | 0.00082125 | -0.018771 | 3.4238 | 0.00065194 | 0 | 3.8216 | 0.00082125 | -0.018771 |  | LF | None | 3420 | 0.652 | 3420 | 0.652 | 1.12 | 1.26 | -0.0054824 | 3420 | 0.652 | 3420 | 0.652 | 1.12 | 1.26 | -0.00548
LFNoneSCEComNewCZ14 | Com-Iltg-dWatt-LF_OSnone | SCE | Com | New | CZ14 | 3.3435 | 0.00073842 | 0 | 3.6593 | 0.00095517 | -0.021576 | 3.3435 | 0.00073842 | 0 | 3.6593 | 0.00095517 | -0.021576 |  | LF | None | 3340 | 0.738 | 3340 | 0.738 | 1.09 | 1.29 | -0.0064531 | 3340 | 0.738 | 3340 | 0.738 | 1.09 | 1.29 | -0.00645
LFNoneSCEComNewCZ15 | Com-Iltg-dWatt-LF_OSnone | SCE | Com | New | CZ15 | 3.0845 | 0.00068426 | 0 | 3.6274 | 0.00089409 | -0.0043267 | 3.0845 | 0.00068426 | 0 | 3.6274 | 0.00089409 | -0.0043267 |  | LF | None | 3080 | 0.684 | 3080 | 0.684 | 1.18 | 1.31 | -0.0014027 | 3080 | 0.684 | 3080 | 0.684 | 1.18 | 1.31 | -0.0014
LFNoneSCEComNewCZ16 | Com-Iltg-dWatt-LF_OSnone | SCE | Com | New | CZ16 | 3.0947 | 0.00061723 | 0 | 3.1194 | 0.00075716 | -0.032956 | 3.0947 | 0.00061723 | 0 | 3.1194 | 0.00075716 | -0.032956 |  | LF | None | 3090 | 0.617 | 3090 | 0.617 | 1.01 | 1.23 | -0.010649 | 3090 | 0.617 | 3090 | 0.617 | 1.01 | 1.23 | -0.0106
LFNoneSCEComNewIOU | Com-Iltg-dWatt-LF_OSnone | SCE | Com | New | IOU | 3.3439 | 0.00072409 | 0 | 3.6545 | 0.00090104 | -0.01226 | 3.3439 | 0.00072409 | 0 | 3.6545 | 0.00090104 | -0.01226 |  | LF | None | 3340 | 0.724 | 3340 | 0.724 | 1.09 | 1.24 | -0.0036664 | 3340 | 0.724 | 3340 | 0.724 | 1.09 | 1.24 | -0.00367
LFNoneSCEECCExCZ05 | Com-Iltg-dWatt-LF_OSnone | SCE | ECC | Ex | CZ05 | 2.42 | 0.000806 | 0 | 2.64 | 0.000994 | -0.0281 | 2.42 | 0.000806 | 0 | 2.64 | 0.000994 | -0.0281 |  | LF | None | 2420 | 0.806 | 2420 | 0.806 | 1.09 | 1.23 | -0.011612 | 2420 | 0.806 | 2420 | 0.806 | 1.09 | 1.23 | -0.0116
LFNoneSCEECCExCZ06 | Com-Iltg-dWatt-LF_OSnone | SCE | ECC | Ex | CZ06 | 2.42 | 0.000806 | 0 | 2.8 | 0.00103 | -0.0136 | 2.42 | 0.000806 | 0 | 2.8 | 0.00103 | -0.0136 |  | LF | None | 2420 | 0.806 | 2420 | 0.806 | 1.16 | 1.28 | -0.0056198 | 2420 | 0.806 | 2420 | 0.806 | 1.16 | 1.28 | -0.00562
LFNoneSCEECCExCZ08 | Com-Iltg-dWatt-LF_OSnone | SCE | ECC | Ex | CZ08 | 2.42 | 0.000806 | 0 | 2.83 | 0.00103 | -0.0123 | 2.42 | 0.000806 | 0 | 2.83 | 0.00103 | -0.0123 |  | LF | None | 2420 | 0.806 | 2420 | 0.806 | 1.17 | 1.28 | -0.0050826 | 2420 | 0.806 | 2420 | 0.806 | 1.17 | 1.28 | -0.00508
LFNoneSCEECCExCZ09 | Com-Iltg-dWatt-LF_OSnone | SCE | ECC | Ex | CZ09 | 2.42 | 0.000806 | 0 | 2.81 | 0.00105 | -0.0141 | 2.42 | 0.000806 | 0 | 2.81 | 0.00105 | -0.0141 |  | LF | None | 2420 | 0.806 | 2420 | 0.806 | 1.16 | 1.3 | -0.0058264 | 2420 | 0.806 | 2420 | 0.806 | 1.16 | 1.3 | -0.00583
LFNoneSCEECCExCZ10 | Com-Iltg-dWatt-LF_OSnone | SCE | ECC | Ex | CZ10 | 2.42 | 0.000806 | 0 | 2.78 | 0.00104 | -0.0135 | 2.42 | 0.000806 | 0 | 2.78 | 0.00104 | -0.0135 |  | LF | None | 2420 | 0.806 | 2420 | 0.806 | 1.15 | 1.29 | -0.0055785 | 2420 | 0.806 | 2420 | 0.806 | 1.15 | 1.29 | -0.00558
LFNoneSCEECCExCZ13 | Com-Iltg-dWatt-LF_OSnone | SCE | ECC | Ex | CZ13 | 2.42 | 0.000487 | 0 | 2.73 | 0.000628 | -0.0208 | 2.42 | 0.000487 | 0 | 2.73 | 0.000628 | -0.0208 |  | LF | None | 2420 | 0.487 | 2420 | 0.487 | 1.13 | 1.29 | -0.008595 | 2420 | 0.487 | 2420 | 0.487 | 1.13 | 1.29 | -0.0086
LFNoneSCEECCExCZ14 | Com-Iltg-dWatt-LF_OSnone | SCE | ECC | Ex | CZ14 | 2.42 | 0.000806 | 0 | 2.72 | 0.00103 | -0.0218 | 2.42 | 0.000806 | 0 | 2.72 | 0.00103 | -0.0218 |  | LF | None | 2420 | 0.806 | 2420 | 0.806 | 1.12 | 1.28 | -0.0090083 | 2420 | 0.806 | 2420 | 0.806 | 1.12 | 1.28 | -0.00901
LFNoneSCEECCExCZ15 | Com-Iltg-dWatt-LF_OSnone | SCE | ECC | Ex | CZ15 | 2.42 | 0.000806 | 0 | 2.99 | 0.00103 | -0.00601 | 2.42 | 0.000806 | 0 | 2.99 | 0.00103 | -0.00601 |  | LF | None | 2420 | 0.806 | 2420 | 0.806 | 1.24 | 1.28 | -0.0024835 | 2420 | 0.806 | 2420 | 0.806 | 1.24 | 1.28 | -0.00248
LFNoneSCEECCExCZ16 | Com-Iltg-dWatt-LF_OSnone | SCE | ECC | Ex | CZ16 | 2.42 | 0.000487 | 0 | 2.53 | 0.000606 | -0.0407 | 2.42 | 0.000487 | 0 | 2.53 | 0.000606 | -0.0407 |  | LF | None | 2420 | 0.487 | 2420 | 0.487 | 1.05 | 1.24 | -0.016818 | 2420 | 0.487 | 2420 | 0.487 | 1.05 | 1.24 | -0.0168
LFNoneSCEECCExIOU | Com-Iltg-dWatt-LF_OSnone | SCE | ECC | Ex | IOU | 2.42 | 0.0007755 | 0 | 2.7921 | 0.0009928 | -0.015345 | 2.42 | 0.0007755 | 0 | 2.7921 | 0.0009928 | -0.015345 |  | LF | None | 2420 | 0.776 | 2420 | 0.776 | 1.15 | 1.28 | -0.0063408 | 2420 | 0.776 | 2420 | 0.776 | 1.15 | 1.28 | -0.00634
LFNoneSCEECCNewCZ05 | Com-Iltg-dWatt-LF_OSnone | SCE | ECC | New | CZ05 | 2.42 | 0.000806 | 0 | 2.62 | 0.00101 | -0.0286 | 2.42 | 0.000806 | 0 | 2.62 | 0.00101 | -0.0286 |  | LF | None | 2420 | 0.806 | 2420 | 0.806 | 1.08 | 1.25 | -0.011818 | 2420 | 0.806 | 2420 | 0.806 | 1.08 | 1.25 | -0.0118
LFNoneSCEECCNewCZ06 | Com-Iltg-dWatt-LF_OSnone | SCE | ECC | New | CZ06 | 2.42 | 0.000806 | 0 | 2.75 | 0.00103 | -0.0129 | 2.42 | 0.000806 | 0 | 2.75 | 0.00103 | -0.0129 |  | LF | None | 2420 | 0.806 | 2420 | 0.806 | 1.14 | 1.28 | -0.0053306 | 2420 | 0.806 | 2420 | 0.806 | 1.14 | 1.28 | -0.00533
LFNoneSCEECCNewCZ08 | Com-Iltg-dWatt-LF_OSnone | SCE | ECC | New | CZ08 | 2.42 | 0.000806 | 0 | 2.78 | 0.00103 | -0.0104 | 2.42 | 0.000806 | 0 | 2.78 | 0.00103 | -0.0104 |  | LF | None | 2420 | 0.806 | 2420 | 0.806 | 1.15 | 1.28 | -0.0042975 | 2420 | 0.806 | 2420 | 0.806 | 1.15 | 1.28 | -0.0043
LFNoneSCEECCNewCZ09 | Com-Iltg-dWatt-LF_OSnone | SCE | ECC | New | CZ09 | 2.42 | 0.000806 | 0 | 2.78 | 0.00106 | -0.0123 | 2.42 | 0.000806 | 0 | 2.78 | 0.00106 | -0.0123 |  | LF | None | 2420 | 0.806 | 2420 | 0.806 | 1.15 | 1.32 | -0.0050826 | 2420 | 0.806 | 2420 | 0.806 | 1.15 | 1.32 | -0.00508
LFNoneSCEECCNewCZ10 | Com-Iltg-dWatt-LF_OSnone | SCE | ECC | New | CZ10 | 2.42 | 0.000806 | 0 | 2.8 | 0.00107 | -0.0124 | 2.42 | 0.000806 | 0 | 2.8 | 0.00107 | -0.0124 |  | LF | None | 2420 | 0.806 | 2420 | 0.806 | 1.16 | 1.33 | -0.005124 | 2420 | 0.806 | 2420 | 0.806 | 1.16 | 1.33 | -0.00512
LFNoneSCEECCNewCZ13 | Com-Iltg-dWatt-LF_OSnone | SCE | ECC | New | CZ13 | 2.42 | 0.000487 | 0 | 2.77 | 0.000674 | -0.0202 | 2.42 | 0.000487 | 0 | 2.77 | 0.000674 | -0.0202 |  | LF | None | 2420 | 0.487 | 2420 | 0.487 | 1.14 | 1.38 | -0.0083471 | 2420 | 0.487 | 2420 | 0.487 | 1.14 | 1.38 | -0.00835
LFNoneSCEECCNewCZ14 | Com-Iltg-dWatt-LF_OSnone | SCE | ECC | New | CZ14 | 2.42 | 0.000806 | 0 | 2.76 | 0.00104 | -0.0213 | 2.42 | 0.000806 | 0 | 2.76 | 0.00104 | -0.0213 |  | LF | None | 2420 | 0.806 | 2420 | 0.806 | 1.14 | 1.29 | -0.0088017 | 2420 | 0.806 | 2420 | 0.806 | 1.14 | 1.29 | -0.0088
LFNoneSCEECCNewCZ15 | Com-Iltg-dWatt-LF_OSnone | SCE | ECC | New | CZ15 | 2.42 | 0.000806 | 0 | 3.11 | 0.00115 | -0.00451 | 2.42 | 0.000806 | 0 | 3.11 | 0.00115 | -0.00451 |  | LF | None | 2420 | 0.806 | 2420 | 0.806 | 1.29 | 1.43 | -0.0018636 | 2420 | 0.806 | 2420 | 0.806 | 1.29 | 1.43 | -0.00186
LFNoneSCEECCNewCZ16 | Com-Iltg-dWatt-LF_OSnone | SCE | ECC | New | CZ16 | 2.42 | 0.000487 | 0 | 2.56 | 0.00064 | -0.0402 | 2.42 | 0.000487 | 0 | 2.56 | 0.00064 | -0.0402 |  | LF | None | 2420 | 0.487 | 2420 | 0.487 | 1.06 | 1.31 | -0.016612 | 2420 | 0.487 | 2420 | 0.487 | 1.06 | 1.31 | -0.0166
LFNoneSCEECCNewIOU | Com-Iltg-dWatt-LF_OSnone | SCE | ECC | New | IOU | 2.42 | 0.0007538 | 0 | 2.7678 | 0.0009839 | -0.015635 | 2.42 | 0.0007538 | 0 | 2.7678 | 0.0009839 | -0.015635 |  | LF | None | 2420 | 0.754 | 2420 | 0.754 | 1.14 | 1.31 | -0.006461 | 2420 | 0.754 | 2420 | 0.754 | 1.14 | 1.31 | -0.00646
LFNoneSCEEPrExCZ05 | Com-Iltg-dWatt-LF_OSnone | SCE | EPr | Ex | CZ05 | 2.14 | 0.000616 | 0 | 2.34 | 0.000785 | -0.0189 | 2.14 | 0.000616 | 0 | 2.34 | 0.000785 | -0.0189 |  | LF | None | 2140 | 0.616 | 2140 | 0.616 | 1.09 | 1.27 | -0.0088318 | 2140 | 0.616 | 2140 | 0.616 | 1.09 | 1.27 | -0.00883
LFNoneSCEEPrExCZ06 | Com-Iltg-dWatt-LF_OSnone | SCE | EPr | Ex | CZ06 | 2.14 | 0.000616 | 0 | 2.5 | 0.0008 | -0.0092 | 2.14 | 0.000616 | 0 | 2.5 | 0.0008 | -0.0092 |  | LF | None | 2140 | 0.616 | 2140 | 0.616 | 1.17 | 1.3 | -0.0042991 | 2140 | 0.616 | 2140 | 0.616 | 1.17 | 1.3 | -0.0043
LFNoneSCEEPrExCZ08 | Com-Iltg-dWatt-LF_OSnone | SCE | EPr | Ex | CZ08 | 2.14 | 0.000616 | 0 | 2.52 | 0.000811 | -0.00755 | 2.14 | 0.000616 | 0 | 2.52 | 0.000811 | -0.00755 |  | LF | None | 2140 | 0.616 | 2140 | 0.616 | 1.18 | 1.32 | -0.003528 | 2140 | 0.616 | 2140 | 0.616 | 1.18 | 1.32 | -0.00353
LFNoneSCEEPrExCZ09 | Com-Iltg-dWatt-LF_OSnone | SCE | EPr | Ex | CZ09 | 2.14 | 0.000616 | 0 | 2.48 | 0.000811 | -0.00946 | 2.14 | 0.000616 | 0 | 2.48 | 0.000811 | -0.00946 |  | LF | None | 2140 | 0.616 | 2140 | 0.616 | 1.16 | 1.32 | -0.0044206 | 2140 | 0.616 | 2140 | 0.616 | 1.16 | 1.32 | -0.00442
LFNoneSCEEPrExCZ10 | Com-Iltg-dWatt-LF_OSnone | SCE | EPr | Ex | CZ10 | 2.14 | 0.000616 | 0 | 2.41 | 0.000793 | -0.0103 | 2.14 | 0.000616 | 0 | 2.41 | 0.000793 | -0.0103 |  | LF | None | 2140 | 0.616 | 2140 | 0.616 | 1.13 | 1.29 | -0.0048131 | 2140 | 0.616 | 2140 | 0.616 | 1.13 | 1.29 | -0.00481
LFNoneSCEEPrExCZ13 | Com-Iltg-dWatt-LF_OSnone | SCE | EPr | Ex | CZ13 | 2.14 | 2e-05 | 0 | 2.35 | 2e-05 | -0.0174 | 2.14 | 2e-05 | 0 | 2.35 | 2e-05 | -0.0174 |  | LF | None | 2140 | 0.02 | 2140 | 0.02 | 1.1 | 1 | -0.0081308 | 2140 | 0.02 | 2140 | 0.02 | 1.1 | 1 | -0.00813
LFNoneSCEEPrExCZ14 | Com-Iltg-dWatt-LF_OSnone | SCE | EPr | Ex | CZ14 | 2.14 | 0.000616 | 0 | 2.34 | 0.000796 | -0.0172 | 2.14 | 0.000616 | 0 | 2.34 | 0.000796 | -0.0172 |  | LF | None | 2140 | 0.616 | 2140 | 0.616 | 1.09 | 1.29 | -0.0080374 | 2140 | 0.616 | 2140 | 0.616 | 1.09 | 1.29 | -0.00804
LFNoneSCEEPrExCZ15 | Com-Iltg-dWatt-LF_OSnone | SCE | EPr | Ex | CZ15 | 2.14 | 0.000616 | 0 | 2.59 | 0.000793 | -0.00422 | 2.14 | 0.000616 | 0 | 2.59 | 0.000793 | -0.00422 |  | LF | None | 2140 | 0.616 | 2140 | 0.616 | 1.21 | 1.29 | -0.001972 | 2140 | 0.616 | 2140 | 0.616 | 1.21 | 1.29 | -0.00197
LFNoneSCEEPrExCZ16 | Com-Iltg-dWatt-LF_OSnone | SCE | EPr | Ex | CZ16 | 2.14 | 2e-05 | 0 | 2.08 | 2e-05 | -0.0355 | 2.14 | 2e-05 | 0 | 2.08 | 2e-05 | -0.0355 |  | LF | None | 2140 | 0.02 | 2140 | 0.02 | 0.972 | 1 | -0.016589 | 2140 | 0.02 | 2140 | 0.02 | 0.972 | 1 | -0.0166
LFNoneSCEEPrExIOU | Com-Iltg-dWatt-LF_OSnone | SCE | EPr | Ex | IOU | 2.14 | 0.00057674 | 0 | 2.4611 | 0.00075212 | -0.010282 | 2.14 | 0.00057674 | 0 | 2.4611 | 0.00075212 | -0.010282 |  | LF | None | 2140 | 0.577 | 2140 | 0.577 | 1.15 | 1.3 | -0.0048047 | 2140 | 0.577 | 2140 | 0.577 | 1.15 | 1.3 | -0.0048
LFNoneSCEEPrNewCZ05 | Com-Iltg-dWatt-LF_OSnone | SCE | EPr | New | CZ05 | 2.14 | 0.000616 | 0 | 2.26 | 0.000803 | -0.0184 | 2.14 | 0.000616 | 0 | 2.26 | 0.000803 | -0.0184 |  | LF | None | 2140 | 0.616 | 2140 | 0.616 | 1.06 | 1.3 | -0.0085981 | 2140 | 0.616 | 2140 | 0.616 | 1.06 | 1.3 | -0.0086
LFNoneSCEEPrNewCZ06 | Com-Iltg-dWatt-LF_OSnone | SCE | EPr | New | CZ06 | 2.14 | 0.000616 | 0 | 2.22 | 0.000585 | -0.0101 | 2.14 | 0.000616 | 0 | 2.22 | 0.000585 | -0.0101 |  | LF | None | 2140 | 0.616 | 2140 | 0.616 | 1.04 | 0.95 | -0.0047196 | 2140 | 0.616 | 2140 | 0.616 | 1.04 | 0.95 | -0.00472
LFNoneSCEEPrNewCZ08 | Com-Iltg-dWatt-LF_OSnone | SCE | EPr | New | CZ08 | 2.14 | 0.000616 | 0 | 2.41 | 0.000856 | -0.0102 | 2.14 | 0.000616 | 0 | 2.41 | 0.000856 | -0.0102 |  | LF | None | 2140 | 0.616 | 2140 | 0.616 | 1.13 | 1.39 | -0.0047664 | 2140 | 0.616 | 2140 | 0.616 | 1.13 | 1.39 | -0.00477
LFNoneSCEEPrNewCZ09 | Com-Iltg-dWatt-LF_OSnone | SCE | EPr | New | CZ09 | 2.14 | 0.000616 | 0 | 2.41 | 0.000888 | -0.0117 | 2.14 | 0.000616 | 0 | 2.41 | 0.000888 | -0.0117 |  | LF | None | 2140 | 0.616 | 2140 | 0.616 | 1.13 | 1.44 | -0.0054673 | 2140 | 0.616 | 2140 | 0.616 | 1.13 | 1.44 | -0.00547
LFNoneSCEEPrNewCZ10 | Com-Iltg-dWatt-LF_OSnone | SCE | EPr | New | CZ10 | 2.14 | 0.000616 | 0 | 2.42 | 0.000902 | -0.0126 | 2.14 | 0.000616 | 0 | 2.42 | 0.000902 | -0.0126 |  | LF | None | 2140 | 0.616 | 2140 | 0.616 | 1.13 | 1.46 | -0.0058879 | 2140 | 0.616 | 2140 | 0.616 | 1.13 | 1.46 | -0.00589
LFNoneSCEEPrNewCZ13 | Com-Iltg-dWatt-LF_OSnone | SCE | EPr | New | CZ13 | 2.14 | 2e-05 | 0 | 2.38 | 2e-05 | -0.0205 | 2.14 | 2e-05 | 0 | 2.38 | 2e-05 | -0.0205 |  | LF | None | 2140 | 0.02 | 2140 | 0.02 | 1.11 | 1 | -0.0095794 | 2140 | 0.02 | 2140 | 0.02 | 1.11 | 1 | -0.00958
LFNoneSCEEPrNewCZ14 | Com-Iltg-dWatt-LF_OSnone | SCE | EPr | New | CZ14 | 2.14 | 0.000616 | 0 | 2.38 | 0.000885 | -0.0206 | 2.14 | 0.000616 | 0 | 2.38 | 0.000885 | -0.0206 |  | LF | None | 2140 | 0.616 | 2140 | 0.616 | 1.11 | 1.44 | -0.0096262 | 2140 | 0.616 | 2140 | 0.616 | 1.11 | 1.44 | -0.00963
LFNoneSCEEPrNewCZ15 | Com-Iltg-dWatt-LF_OSnone | SCE | EPr | New | CZ15 | 2.14 | 0.000616 | 0 | 2.64 | 0.000903 | -0.00544 | 2.14 | 0.000616 | 0 | 2.64 | 0.000903 | -0.00544 |  | LF | None | 2140 | 0.616 | 2140 | 0.616 | 1.23 | 1.47 | -0.0025421 | 2140 | 0.616 | 2140 | 0.616 | 1.23 | 1.47 | -0.00254
LFNoneSCEEPrNewCZ16 | Com-Iltg-dWatt-LF_OSnone | SCE | EPr | New | CZ16 | 2.14 | 2e-05 | 0 | 2.11 | 2e-05 | -0.0332 | 2.14 | 2e-05 | 0 | 2.11 | 2e-05 | -0.0332 |  | LF | None | 2140 | 0.02 | 2140 | 0.02 | 0.986 | 1 | -0.015514 | 2140 | 0.02 | 2140 | 0.02 | 0.986 | 1 | -0.0155
LFNoneSCEEPrNewIOU | Com-Iltg-dWatt-LF_OSnone | SCE | EPr | New | IOU | 2.14 | 0.00054921 | 0 | 2.3812 | 0.00075263 | -0.013463 | 2.14 | 0.00054921 | 0 | 2.3812 | 0.00075263 | -0.013463 |  | LF | None | 2140 | 0.549 | 2140 | 0.549 | 1.11 | 1.37 | -0.006291 | 2140 | 0.549 | 2140 | 0.549 | 1.11 | 1.37 | -0.00629
LFNoneSCEERCExCZ05 | Com-Iltg-dWatt-LF_OSnone | SCE | ERC | Ex | CZ05 | 2.48 | 0.000702 | 0 | 2.6 | 0.000907 | -0.0253 | 2.48 | 0.000702 | 0 | 2.6 | 0.000907 | -0.0253 |  | LF | None | 2480 | 0.702 | 2480 | 0.702 | 1.05 | 1.29 | -0.010202 | 2480 | 0.702 | 2480 | 0.702 | 1.05 | 1.29 | -0.0102
LFNoneSCEERCExCZ06 | Com-Iltg-dWatt-LF_OSnone | SCE | ERC | Ex | CZ06 | 2.48 | 0.000702 | 0 | 2.77 | 0.00089 | -0.0153 | 2.48 | 0.000702 | 0 | 2.77 | 0.00089 | -0.0153 |  | LF | None | 2480 | 0.702 | 2480 | 0.702 | 1.12 | 1.27 | -0.0061694 | 2480 | 0.702 | 2480 | 0.702 | 1.12 | 1.27 | -0.00617
LFNoneSCEERCExCZ08 | Com-Iltg-dWatt-LF_OSnone | SCE | ERC | Ex | CZ08 | 2.48 | 0.000702 | 0 | 2.77 | 0.000901 | -0.0135 | 2.48 | 0.000702 | 0 | 2.77 | 0.000901 | -0.0135 |  | LF | None | 2480 | 0.702 | 2480 | 0.702 | 1.12 | 1.28 | -0.0054435 | 2480 | 0.702 | 2480 | 0.702 | 1.12 | 1.28 | -0.00544
LFNoneSCEERCExCZ09 | Com-Iltg-dWatt-LF_OSnone | SCE | ERC | Ex | CZ09 | 2.48 | 0.000702 | 0 | 2.77 | 0.000901 | -0.0151 | 2.48 | 0.000702 | 0 | 2.77 | 0.000901 | -0.0151 |  | LF | None | 2480 | 0.702 | 2480 | 0.702 | 1.12 | 1.28 | -0.0060887 | 2480 | 0.702 | 2480 | 0.702 | 1.12 | 1.28 | -0.00609
LFNoneSCEERCExCZ10 | Com-Iltg-dWatt-LF_OSnone | SCE | ERC | Ex | CZ10 | 2.48 | 0.000702 | 0 | 2.76 | 0.000896 | -0.0154 | 2.48 | 0.000702 | 0 | 2.76 | 0.000896 | -0.0154 |  | LF | None | 2480 | 0.702 | 2480 | 0.702 | 1.11 | 1.28 | -0.0062097 | 2480 | 0.702 | 2480 | 0.702 | 1.11 | 1.28 | -0.00621
LFNoneSCEERCExCZ13 | Com-Iltg-dWatt-LF_OSnone | SCE | ERC | Ex | CZ13 | 2.48 | 2e-05 | 0 | 2.69 | 2e-05 | -0.022 | 2.48 | 2e-05 | 0 | 2.69 | 2e-05 | -0.022 |  | LF | None | 2480 | 0.02 | 2480 | 0.02 | 1.08 | 1 | -0.008871 | 2480 | 0.02 | 2480 | 0.02 | 1.08 | 1 | -0.00887
LFNoneSCEERCExCZ14 | Com-Iltg-dWatt-LF_OSnone | SCE | ERC | Ex | CZ14 | 2.48 | 0.000702 | 0 | 2.71 | 0.000902 | -0.0206 | 2.48 | 0.000702 | 0 | 2.71 | 0.000902 | -0.0206 |  | LF | None | 2480 | 0.702 | 2480 | 0.702 | 1.09 | 1.28 | -0.0083065 | 2480 | 0.702 | 2480 | 0.702 | 1.09 | 1.28 | -0.00831
LFNoneSCEERCExCZ15 | Com-Iltg-dWatt-LF_OSnone | SCE | ERC | Ex | CZ15 | 2.48 | 0.000702 | 0 | 2.95 | 0.000918 | -0.00714 | 2.48 | 0.000702 | 0 | 2.95 | 0.000918 | -0.00714 |  | LF | None | 2480 | 0.702 | 2480 | 0.702 | 1.19 | 1.31 | -0.002879 | 2480 | 0.702 | 2480 | 0.702 | 1.19 | 1.31 | -0.00288
LFNoneSCEERCExCZ16 | Com-Iltg-dWatt-LF_OSnone | SCE | ERC | Ex | CZ16 | 2.48 | 2e-05 | 0 | 2.48 | 2e-05 | -0.0379 | 2.48 | 2e-05 | 0 | 2.48 | 2e-05 | -0.0379 |  | LF | None | 2480 | 0.02 | 2480 | 0.02 | 1 | 1 | -0.015282 | 2480 | 0.02 | 2480 | 0.02 | 1 | 1 | -0.0153
LFNoneSCEERCExIOU | Com-Iltg-dWatt-LF_OSnone | SCE | ERC | Ex | IOU | 2.48 | 0.00065708 | 0 | 2.7574 | 0.00084034 | -0.015702 | 2.48 | 0.00065708 | 0 | 2.7574 | 0.00084034 | -0.015702 |  | LF | None | 2480 | 0.657 | 2480 | 0.657 | 1.11 | 1.28 | -0.0063316 | 2480 | 0.657 | 2480 | 0.657 | 1.11 | 1.28 | -0.00633
LFNoneSCEERCNewCZ05 | Com-Iltg-dWatt-LF_OSnone | SCE | ERC | New | CZ05 | 2.48 | 0.000702 | 0 | 2.73 | 0.000906 | -0.0245 | 2.48 | 0.000702 | 0 | 2.73 | 0.000906 | -0.0245 |  | LF | None | 2480 | 0.702 | 2480 | 0.702 | 1.1 | 1.29 | -0.009879 | 2480 | 0.702 | 2480 | 0.702 | 1.1 | 1.29 | -0.00988
LFNoneSCEERCNewCZ06 | Com-Iltg-dWatt-LF_OSnone | SCE | ERC | New | CZ06 | 2.48 | 0.000702 | 0 | 2.87 | 0.000914 | -0.0157 | 2.48 | 0.000702 | 0 | 2.87 | 0.000914 | -0.0157 |  | LF | None | 2480 | 0.702 | 2480 | 0.702 | 1.16 | 1.3 | -0.0063306 | 2480 | 0.702 | 2480 | 0.702 | 1.16 | 1.3 | -0.00633
LFNoneSCEERCNewCZ08 | Com-Iltg-dWatt-LF_OSnone | SCE | ERC | New | CZ08 | 2.48 | 0.000702 | 0 | 2.93 | 0.000935 | -0.0132 | 2.48 | 0.000702 | 0 | 2.93 | 0.000935 | -0.0132 |  | LF | None | 2480 | 0.702 | 2480 | 0.702 | 1.18 | 1.33 | -0.0053226 | 2480 | 0.702 | 2480 | 0.702 | 1.18 | 1.33 | -0.00532
LFNoneSCEERCNewCZ09 | Com-Iltg-dWatt-LF_OSnone | SCE | ERC | New | CZ09 | 2.48 | 0.000702 | 0 | 2.92 | 0.000962 | -0.015 | 2.48 | 0.000702 | 0 | 2.92 | 0.000962 | -0.015 |  | LF | None | 2480 | 0.702 | 2480 | 0.702 | 1.18 | 1.37 | -0.0060484 | 2480 | 0.702 | 2480 | 0.702 | 1.18 | 1.37 | -0.00605
LFNoneSCEERCNewCZ10 | Com-Iltg-dWatt-LF_OSnone | SCE | ERC | New | CZ10 | 2.48 | 0.000702 | 0 | 2.94 | 0.00098 | -0.0157 | 2.48 | 0.000702 | 0 | 2.94 | 0.00098 | -0.0157 |  | LF | None | 2480 | 0.702 | 2480 | 0.702 | 1.19 | 1.4 | -0.0063306 | 2480 | 0.702 | 2480 | 0.702 | 1.19 | 1.4 | -0.00633
LFNoneSCEERCNewCZ13 | Com-Iltg-dWatt-LF_OSnone | SCE | ERC | New | CZ13 | 2.48 | 2e-05 | 0 | 2.9 | 2e-05 | -0.0235 | 2.48 | 2e-05 | 0 | 2.9 | 2e-05 | -0.0235 |  | LF | None | 2480 | 0.02 | 2480 | 0.02 | 1.17 | 1 | -0.0094758 | 2480 | 0.02 | 2480 | 0.02 | 1.17 | 1 | -0.00948
LFNoneSCEERCNewCZ14 | Com-Iltg-dWatt-LF_OSnone | SCE | ERC | New | CZ14 | 2.48 | 0.000702 | 0 | 2.89 | 0.000965 | -0.0228 | 2.48 | 0.000702 | 0 | 2.89 | 0.000965 | -0.0228 |  | LF | None | 2480 | 0.702 | 2480 | 0.702 | 1.17 | 1.37 | -0.0091935 | 2480 | 0.702 | 2480 | 0.702 | 1.17 | 1.37 | -0.00919
LFNoneSCEERCNewCZ15 | Com-Iltg-dWatt-LF_OSnone | SCE | ERC | New | CZ15 | 2.48 | 0.000702 | 0 | 3.19 | 0.000982 | -0.00779 | 2.48 | 0.000702 | 0 | 3.19 | 0.000982 | -0.00779 |  | LF | None | 2480 | 0.702 | 2480 | 0.702 | 1.29 | 1.4 | -0.0031411 | 2480 | 0.702 | 2480 | 0.702 | 1.29 | 1.4 | -0.00314
LFNoneSCEERCNewCZ16 | Com-Iltg-dWatt-LF_OSnone | SCE | ERC | New | CZ16 | 2.48 | 2e-05 | 0 | 2.6 | 2e-05 | -0.0417 | 2.48 | 2e-05 | 0 | 2.6 | 2e-05 | -0.0417 |  | LF | None | 2480 | 0.02 | 2480 | 0.02 | 1.05 | 1 | -0.016815 | 2480 | 0.02 | 2480 | 0.02 | 1.05 | 1 | -0.0168
LFNoneSCEERCNewIOU | Com-Iltg-dWatt-LF_OSnone | SCE | ERC | New | IOU | 2.48 | 0.00062558 | 0 | 2.9144 | 0.00085176 | -0.01698 | 2.48 | 0.00062558 | 0 | 2.9144 | 0.00085176 | -0.01698 |  | LF | None | 2480 | 0.626 | 2480 | 0.626 | 1.18 | 1.36 | -0.0068468 | 2480 | 0.626 | 2480 | 0.626 | 1.18 | 1.36 | -0.00685
LFNoneSCEESeExCZ05 | Com-Iltg-dWatt-LF_OSnone | SCE | ESe | Ex | CZ05 | 2.28 | 0.000709 | 0 | 2.43 | 0.000883 | -0.026 | 2.28 | 0.000709 | 0 | 2.43 | 0.000883 | -0.026 |  | LF | None | 2280 | 0.709 | 2280 | 0.709 | 1.07 | 1.25 | -0.011404 | 2280 | 0.709 | 2280 | 0.709 | 1.07 | 1.25 | -0.0114
LFNoneSCEESeExCZ06 | Com-Iltg-dWatt-LF_OSnone | SCE | ESe | Ex | CZ06 | 2.28 | 0.000709 | 0 | 2.62 | 0.00092 | -0.0134 | 2.28 | 0.000709 | 0 | 2.62 | 0.00092 | -0.0134 |  | LF | None | 2280 | 0.709 | 2280 | 0.709 | 1.15 | 1.3 | -0.0058772 | 2280 | 0.709 | 2280 | 0.709 | 1.15 | 1.3 | -0.00588
LFNoneSCEESeExCZ08 | Com-Iltg-dWatt-LF_OSnone | SCE | ESe | Ex | CZ08 | 2.28 | 0.000709 | 0 | 2.64 | 0.000915 | -0.0117 | 2.28 | 0.000709 | 0 | 2.64 | 0.000915 | -0.0117 |  | LF | None | 2280 | 0.709 | 2280 | 0.709 | 1.16 | 1.29 | -0.0051316 | 2280 | 0.709 | 2280 | 0.709 | 1.16 | 1.29 | -0.00513
LFNoneSCEESeExCZ09 | Com-Iltg-dWatt-LF_OSnone | SCE | ESe | Ex | CZ09 | 2.28 | 0.000709 | 0 | 2.62 | 0.000921 | -0.0135 | 2.28 | 0.000709 | 0 | 2.62 | 0.000921 | -0.0135 |  | LF | None | 2280 | 0.709 | 2280 | 0.709 | 1.15 | 1.3 | -0.0059211 | 2280 | 0.709 | 2280 | 0.709 | 1.15 | 1.3 | -0.00592
LFNoneSCEESeExCZ10 | Com-Iltg-dWatt-LF_OSnone | SCE | ESe | Ex | CZ10 | 2.28 | 0.000709 | 0 | 2.55 | 0.000903 | -0.0145 | 2.28 | 0.000709 | 0 | 2.55 | 0.000903 | -0.0145 |  | LF | None | 2280 | 0.709 | 2280 | 0.709 | 1.12 | 1.27 | -0.0063596 | 2280 | 0.709 | 2280 | 0.709 | 1.12 | 1.27 | -0.00636
LFNoneSCEESeExCZ13 | Com-Iltg-dWatt-LF_OSnone | SCE | ESe | Ex | CZ13 | 2.28 | 2e-05 | 0 | 2.51 | 2e-05 | -0.0224 | 2.28 | 2e-05 | 0 | 2.51 | 2e-05 | -0.0224 |  | LF | None | 2280 | 0.02 | 2280 | 0.02 | 1.1 | 1 | -0.0098246 | 2280 | 0.02 | 2280 | 0.02 | 1.1 | 1 | -0.00982
LFNoneSCEESeExCZ14 | Com-Iltg-dWatt-LF_OSnone | SCE | ESe | Ex | CZ14 | 2.28 | 0.000709 | 0 | 2.49 | 0.00088 | -0.0227 | 2.28 | 0.000709 | 0 | 2.49 | 0.00088 | -0.0227 |  | LF | None | 2280 | 0.709 | 2280 | 0.709 | 1.09 | 1.24 | -0.0099561 | 2280 | 0.709 | 2280 | 0.709 | 1.09 | 1.24 | -0.00996
LFNoneSCEESeExCZ15 | Com-Iltg-dWatt-LF_OSnone | SCE | ESe | Ex | CZ15 | 2.28 | 0.000709 | 0 | 2.77 | 0.0009 | -0.00649 | 2.28 | 0.000709 | 0 | 2.77 | 0.0009 | -0.00649 |  | LF | None | 2280 | 0.709 | 2280 | 0.709 | 1.21 | 1.27 | -0.0028465 | 2280 | 0.709 | 2280 | 0.709 | 1.21 | 1.27 | -0.00285
LFNoneSCEESeExCZ16 | Com-Iltg-dWatt-LF_OSnone | SCE | ESe | Ex | CZ16 | 2.28 | 2e-05 | 0 | 2.23 | 2e-05 | -0.0391 | 2.28 | 2e-05 | 0 | 2.23 | 2e-05 | -0.0391 |  | LF | None | 2280 | 0.02 | 2280 | 0.02 | 0.978 | 1 | -0.017149 | 2280 | 0.02 | 2280 | 0.02 | 0.978 | 1 | -0.0171
LFNoneSCEESeExIOU | Com-Iltg-dWatt-LF_OSnone | SCE | ESe | Ex | IOU | 2.28 | 0.00066362 | 0 | 2.5935 | 0.00085334 | -0.014495 | 2.28 | 0.00066362 | 0 | 2.5935 | 0.00085334 | -0.014495 |  | LF | None | 2280 | 0.664 | 2280 | 0.664 | 1.14 | 1.29 | -0.0063576 | 2280 | 0.664 | 2280 | 0.664 | 1.14 | 1.29 | -0.00636
LFNoneSCEESeNewCZ05 | Com-Iltg-dWatt-LF_OSnone | SCE | ESe | New | CZ05 | 2.28 | 0.000709 | 0 | 2.4 | 0.000905 | -0.0231 | 2.28 | 0.000709 | 0 | 2.4 | 0.000905 | -0.0231 |  | LF | None | 2280 | 0.709 | 2280 | 0.709 | 1.05 | 1.28 | -0.010132 | 2280 | 0.709 | 2280 | 0.709 | 1.05 | 1.28 | -0.0101
LFNoneSCEESeNewCZ06 | Com-Iltg-dWatt-LF_OSnone | SCE | ESe | New | CZ06 | 2.28 | 0.000709 | 0 | 2.54 | 0.000947 | -0.0169 | 2.28 | 0.000709 | 0 | 2.54 | 0.000947 | -0.0169 |  | LF | None | 2280 | 0.709 | 2280 | 0.709 | 1.11 | 1.34 | -0.0074123 | 2280 | 0.709 | 2280 | 0.709 | 1.11 | 1.34 | -0.00741
LFNoneSCEESeNewCZ08 | Com-Iltg-dWatt-LF_OSnone | SCE | ESe | New | CZ08 | 2.28 | 0.000709 | 0 | 2.57 | 0.000963 | -0.0129 | 2.28 | 0.000709 | 0 | 2.57 | 0.000963 | -0.0129 |  | LF | None | 2280 | 0.709 | 2280 | 0.709 | 1.13 | 1.36 | -0.0056579 | 2280 | 0.709 | 2280 | 0.709 | 1.13 | 1.36 | -0.00566
LFNoneSCEESeNewCZ09 | Com-Iltg-dWatt-LF_OSnone | SCE | ESe | New | CZ09 | 2.28 | 0.000709 | 0 | 2.57 | 0.000999 | -0.0152 | 2.28 | 0.000709 | 0 | 2.57 | 0.000999 | -0.0152 |  | LF | None | 2280 | 0.709 | 2280 | 0.709 | 1.13 | 1.41 | -0.0066667 | 2280 | 0.709 | 2280 | 0.709 | 1.13 | 1.41 | -0.00667
LFNoneSCEESeNewCZ10 | Com-Iltg-dWatt-LF_OSnone | SCE | ESe | New | CZ10 | 2.28 | 0.000709 | 0 | 2.59 | 0.00101 | -0.0165 | 2.28 | 0.000709 | 0 | 2.59 | 0.00101 | -0.0165 |  | LF | None | 2280 | 0.709 | 2280 | 0.709 | 1.14 | 1.42 | -0.0072368 | 2280 | 0.709 | 2280 | 0.709 | 1.14 | 1.42 | -0.00724
LFNoneSCEESeNewCZ13 | Com-Iltg-dWatt-LF_OSnone | SCE | ESe | New | CZ13 | 2.28 | 2e-05 | 0 | 2.57 | 2e-05 | -0.0244 | 2.28 | 2e-05 | 0 | 2.57 | 2e-05 | -0.0244 |  | LF | None | 2280 | 0.02 | 2280 | 0.02 | 1.13 | 1 | -0.010702 | 2280 | 0.02 | 2280 | 0.02 | 1.13 | 1 | -0.0107
LFNoneSCEESeNewCZ14 | Com-Iltg-dWatt-LF_OSnone | SCE | ESe | New | CZ14 | 2.28 | 0.000709 | 0 | 2.55 | 0.000989 | -0.0247 | 2.28 | 0.000709 | 0 | 2.55 | 0.000989 | -0.0247 |  | LF | None | 2280 | 0.709 | 2280 | 0.709 | 1.12 | 1.39 | -0.010833 | 2280 | 0.709 | 2280 | 0.709 | 1.12 | 1.39 | -0.0108
LFNoneSCEESeNewCZ15 | Com-Iltg-dWatt-LF_OSnone | SCE | ESe | New | CZ15 | 2.28 | 0.000709 | 0 | 2.87 | 0.00101 | -0.00715 | 2.28 | 0.000709 | 0 | 2.87 | 0.00101 | -0.00715 |  | LF | None | 2280 | 0.709 | 2280 | 0.709 | 1.26 | 1.42 | -0.003136 | 2280 | 0.709 | 2280 | 0.709 | 1.26 | 1.42 | -0.00314
LFNoneSCEESeNewCZ16 | Com-Iltg-dWatt-LF_OSnone | SCE | ESe | New | CZ16 | 2.28 | 2e-05 | 0 | 2.28 | 2e-05 | -0.032 | 2.28 | 2e-05 | 0 | 2.28 | 2e-05 | -0.032 |  | LF | None | 2280 | 0.02 | 2280 | 0.02 | 1 | 1 | -0.014035 | 2280 | 0.02 | 2280 | 0.02 | 1 | 1 | -0.014
LFNoneSCEESeNewIOU | Com-Iltg-dWatt-LF_OSnone | SCE | ESe | New | IOU | 2.28 | 0.00063179 | 0 | 2.569 | 0.00087864 | -0.017158 | 2.28 | 0.00063179 | 0 | 2.569 | 0.00087864 | -0.017158 |  | LF | None | 2280 | 0.632 | 2280 | 0.632 | 1.13 | 1.39 | -0.0075253 | 2280 | 0.632 | 2280 | 0.632 | 1.13 | 1.39 | -0.00753
LFNoneSCEEUnExCZ05 | Com-Iltg-dWatt-LF_OSnone | SCE | EUn | Ex | CZ05 | 2.35 | 0.00072 | 0 | 2.62 | 0.000876 | -0.0164 | 2.35 | 0.00072 | 0 | 2.62 | 0.000876 | -0.0164 |  | LF | None | 2350 | 0.72 | 2350 | 0.72 | 1.11 | 1.22 | -0.0069787 | 2350 | 0.72 | 2350 | 0.72 | 1.11 | 1.22 | -0.00698
LFNoneSCEEUnExCZ06 | Com-Iltg-dWatt-LF_OSnone | SCE | EUn | Ex | CZ06 | 2.35 | 0.00072 | 0 | 2.73 | 0.000912 | -0.00969 | 2.35 | 0.00072 | 0 | 2.73 | 0.000912 | -0.00969 |  | LF | None | 2350 | 0.72 | 2350 | 0.72 | 1.16 | 1.27 | -0.0041234 | 2350 | 0.72 | 2350 | 0.72 | 1.16 | 1.27 | -0.00412
LFNoneSCEEUnExCZ08 | Com-Iltg-dWatt-LF_OSnone | SCE | EUn | Ex | CZ08 | 2.35 | 0.00072 | 0 | 2.74 | 0.000914 | -0.00939 | 2.35 | 0.00072 | 0 | 2.74 | 0.000914 | -0.00939 |  | LF | None | 2350 | 0.72 | 2350 | 0.72 | 1.17 | 1.27 | -0.0039957 | 2350 | 0.72 | 2350 | 0.72 | 1.17 | 1.27 | -0.004
LFNoneSCEEUnExCZ09 | Com-Iltg-dWatt-LF_OSnone | SCE | EUn | Ex | CZ09 | 2.35 | 0.00072 | 0 | 2.73 | 0.000929 | -0.0104 | 2.35 | 0.00072 | 0 | 2.73 | 0.000929 | -0.0104 |  | LF | None | 2350 | 0.72 | 2350 | 0.72 | 1.16 | 1.29 | -0.0044255 | 2350 | 0.72 | 2350 | 0.72 | 1.16 | 1.29 | -0.00443
LFNoneSCEEUnExCZ10 | Com-Iltg-dWatt-LF_OSnone | SCE | EUn | Ex | CZ10 | 2.35 | 0.00072 | 0 | 2.71 | 0.000922 | -0.00932 | 2.35 | 0.00072 | 0 | 2.71 | 0.000922 | -0.00932 |  | LF | None | 2350 | 0.72 | 2350 | 0.72 | 1.15 | 1.28 | -0.003966 | 2350 | 0.72 | 2350 | 0.72 | 1.15 | 1.28 | -0.00397
LFNoneSCEEUnExCZ13 | Com-Iltg-dWatt-LF_OSnone | SCE | EUn | Ex | CZ13 | 2.35 | 0.000439 | 0 | 2.66 | 0.000553 | -0.0123 | 2.35 | 0.000439 | 0 | 2.66 | 0.000553 | -0.0123 |  | LF | None | 2350 | 0.439 | 2350 | 0.439 | 1.13 | 1.26 | -0.005234 | 2350 | 0.439 | 2350 | 0.439 | 1.13 | 1.26 | -0.00523
LFNoneSCEEUnExCZ14 | Com-Iltg-dWatt-LF_OSnone | SCE | EUn | Ex | CZ14 | 2.35 | 0.00072 | 0 | 2.66 | 0.000916 | -0.0136 | 2.35 | 0.00072 | 0 | 2.66 | 0.000916 | -0.0136 |  | LF | None | 2350 | 0.72 | 2350 | 0.72 | 1.13 | 1.27 | -0.0057872 | 2350 | 0.72 | 2350 | 0.72 | 1.13 | 1.27 | -0.00579
LFNoneSCEEUnExCZ15 | Com-Iltg-dWatt-LF_OSnone | SCE | EUn | Ex | CZ15 | 2.35 | 0.00072 | 0 | 2.83 | 0.000925 | -0.00496 | 2.35 | 0.00072 | 0 | 2.83 | 0.000925 | -0.00496 |  | LF | None | 2350 | 0.72 | 2350 | 0.72 | 1.2 | 1.28 | -0.0021106 | 2350 | 0.72 | 2350 | 0.72 | 1.2 | 1.28 | -0.00211
LFNoneSCEEUnExCZ16 | Com-Iltg-dWatt-LF_OSnone | SCE | EUn | Ex | CZ16 | 2.35 | 0.000439 | 0 | 2.49 | 0.000531 | -0.0268 | 2.35 | 0.000439 | 0 | 2.49 | 0.000531 | -0.0268 |  | LF | None | 2350 | 0.439 | 2350 | 0.439 | 1.06 | 1.21 | -0.011404 | 2350 | 0.439 | 2350 | 0.439 | 1.06 | 1.21 | -0.0114
LFNoneSCEEUnExIOU | Com-Iltg-dWatt-LF_OSnone | SCE | EUn | Ex | IOU | 2.35 | 0.00069314 | 0 | 2.713 | 0.00088002 | -0.010902 | 2.35 | 0.00069314 | 0 | 2.713 | 0.00088002 | -0.010902 |  | LF | None | 2350 | 0.693 | 2350 | 0.693 | 1.15 | 1.27 | -0.0046393 | 2350 | 0.693 | 2350 | 0.693 | 1.15 | 1.27 | -0.00464
LFNoneSCEEUnNewCZ05 | Com-Iltg-dWatt-LF_OSnone | SCE | EUn | New | CZ05 | 2.35 | 0.00072 | 0 | 2.57 | 0.000896 | -0.0132 | 2.35 | 0.00072 | 0 | 2.57 | 0.000896 | -0.0132 |  | LF | None | 2350 | 0.72 | 2350 | 0.72 | 1.09 | 1.24 | -0.005617 | 2350 | 0.72 | 2350 | 0.72 | 1.09 | 1.24 | -0.00562
LFNoneSCEEUnNewCZ06 | Com-Iltg-dWatt-LF_OSnone | SCE | EUn | New | CZ06 | 2.35 | 0.00072 | 0 | 2.72 | 0.00092 | -0.00591 | 2.35 | 0.00072 | 0 | 2.72 | 0.00092 | -0.00591 |  | LF | None | 2350 | 0.72 | 2350 | 0.72 | 1.16 | 1.28 | -0.0025149 | 2350 | 0.72 | 2350 | 0.72 | 1.16 | 1.28 | -0.00251
LFNoneSCEEUnNewCZ08 | Com-Iltg-dWatt-LF_OSnone | SCE | EUn | New | CZ08 | 2.35 | 0.00072 | 0 | 2.75 | 0.000934 | -0.00527 | 2.35 | 0.00072 | 0 | 2.75 | 0.000934 | -0.00527 |  | LF | None | 2350 | 0.72 | 2350 | 0.72 | 1.17 | 1.3 | -0.0022426 | 2350 | 0.72 | 2350 | 0.72 | 1.17 | 1.3 | -0.00224
LFNoneSCEEUnNewCZ09 | Com-Iltg-dWatt-LF_OSnone | SCE | EUn | New | CZ09 | 2.35 | 0.00072 | 0 | 2.76 | 0.000963 | -0.00607 | 2.35 | 0.00072 | 0 | 2.76 | 0.000963 | -0.00607 |  | LF | None | 2350 | 0.72 | 2350 | 0.72 | 1.17 | 1.34 | -0.002583 | 2350 | 0.72 | 2350 | 0.72 | 1.17 | 1.34 | -0.00258
LFNoneSCEEUnNewCZ10 | Com-Iltg-dWatt-LF_OSnone | SCE | EUn | New | CZ10 | 2.35 | 0.00072 | 0 | 2.77 | 0.000972 | -0.00654 | 2.35 | 0.00072 | 0 | 2.77 | 0.000972 | -0.00654 |  | LF | None | 2350 | 0.72 | 2350 | 0.72 | 1.18 | 1.35 | -0.002783 | 2350 | 0.72 | 2350 | 0.72 | 1.18 | 1.35 | -0.00278
LFNoneSCEEUnNewCZ13 | Com-Iltg-dWatt-LF_OSnone | SCE | EUn | New | CZ13 | 2.35 | 0.000439 | 0 | 2.73 | 0.000608 | -0.0115 | 2.35 | 0.000439 | 0 | 2.73 | 0.000608 | -0.0115 |  | LF | None | 2350 | 0.439 | 2350 | 0.439 | 1.16 | 1.38 | -0.0048936 | 2350 | 0.439 | 2350 | 0.439 | 1.16 | 1.38 | -0.00489
LFNoneSCEEUnNewCZ14 | Com-Iltg-dWatt-LF_OSnone | SCE | EUn | New | CZ14 | 2.35 | 0.00072 | 0 | 2.7 | 0.000936 | -0.0123 | 2.35 | 0.00072 | 0 | 2.7 | 0.000936 | -0.0123 |  | LF | None | 2350 | 0.72 | 2350 | 0.72 | 1.15 | 1.3 | -0.005234 | 2350 | 0.72 | 2350 | 0.72 | 1.15 | 1.3 | -0.00523
LFNoneSCEEUnNewCZ15 | Com-Iltg-dWatt-LF_OSnone | SCE | EUn | New | CZ15 | 2.35 | 0.00072 | 0 | 2.93 | 0.000982 | -0.00254 | 2.35 | 0.00072 | 0 | 2.93 | 0.000982 | -0.00254 |  | LF | None | 2350 | 0.72 | 2350 | 0.72 | 1.25 | 1.36 | -0.0010809 | 2350 | 0.72 | 2350 | 0.72 | 1.25 | 1.36 | -0.00108
LFNoneSCEEUnNewCZ16 | Com-Iltg-dWatt-LF_OSnone | SCE | EUn | New | CZ16 | 2.35 | 0.000439 | 0 | 2.51 | 0.000575 | -0.0256 | 2.35 | 0.000439 | 0 | 2.51 | 0.000575 | -0.0256 |  | LF | None | 2350 | 0.439 | 2350 | 0.439 | 1.07 | 1.31 | -0.010894 | 2350 | 0.439 | 2350 | 0.439 | 1.07 | 1.31 | -0.0109
LFNoneSCEEUnNewIOU | Com-Iltg-dWatt-LF_OSnone | SCE | EUn | New | IOU | 2.35 | 0.00067402 | 0 | 2.7262 | 0.00088573 | -0.0086132 | 2.35 | 0.00067402 | 0 | 2.7262 | 0.00088573 | -0.0086132 |  | LF | None | 2350 | 0.674 | 2350 | 0.674 | 1.16 | 1.31 | -0.0036652 | 2350 | 0.674 | 2350 | 0.674 | 1.16 | 1.31 | -0.00367
LFNoneSCEGroExCZ05 | Com-Iltg-dWatt-LF_OSnone | SCE | Gro | Ex | CZ05 | 4.91 | 0.00069 | 0 | 4.73 | 0.000852 | -0.0834 | 4.91 | 0.00069 | 0 | 4.73 | 0.000852 | -0.0834 |  | LF | None | 4910 | 0.69 | 4910 | 0.69 | 0.963 | 1.23 | -0.016986 | 4910 | 0.69 | 4910 | 0.69 | 0.963 | 1.23 | -0.017
LFNoneSCEGroExCZ06 | Com-Iltg-dWatt-LF_OSnone | SCE | Gro | Ex | CZ06 | 4.91 | 0.00069 | 0 | 5.06 | 0.000863 | -0.0633 | 4.91 | 0.00069 | 0 | 5.06 | 0.000863 | -0.0633 |  | LF | None | 4910 | 0.69 | 4910 | 0.69 | 1.03 | 1.25 | -0.012892 | 4910 | 0.69 | 4910 | 0.69 | 1.03 | 1.25 | -0.0129
LFNoneSCEGroExCZ08 | Com-Iltg-dWatt-LF_OSnone | SCE | Gro | Ex | CZ08 | 4.91 | 0.00069 | 0 | 5.17 | 0.000882 | -0.0569 | 4.91 | 0.00069 | 0 | 5.17 | 0.000882 | -0.0569 |  | LF | None | 4910 | 0.69 | 4910 | 0.69 | 1.05 | 1.28 | -0.011589 | 4910 | 0.69 | 4910 | 0.69 | 1.05 | 1.28 | -0.0116
LFNoneSCEGroExCZ09 | Com-Iltg-dWatt-LF_OSnone | SCE | Gro | Ex | CZ09 | 4.91 | 0.00069 | 0 | 5.19 | 0.000893 | -0.0559 | 4.91 | 0.00069 | 0 | 5.19 | 0.000893 | -0.0559 |  | LF | None | 4910 | 0.69 | 4910 | 0.69 | 1.06 | 1.29 | -0.011385 | 4910 | 0.69 | 4910 | 0.69 | 1.06 | 1.29 | -0.0114
LFNoneSCEGroExCZ10 | Com-Iltg-dWatt-LF_OSnone | SCE | Gro | Ex | CZ10 | 4.91 | 0.00069 | 0 | 5.18 | 0.000911 | -0.0545 | 4.91 | 0.00069 | 0 | 5.18 | 0.000911 | -0.0545 |  | LF | None | 4910 | 0.69 | 4910 | 0.69 | 1.05 | 1.32 | -0.0111 | 4910 | 0.69 | 4910 | 0.69 | 1.05 | 1.32 | -0.0111
LFNoneSCEGroExCZ13 | Com-Iltg-dWatt-LF_OSnone | SCE | Gro | Ex | CZ13 | 4.91 | 0.00069 | 0 | 5.18 | 0.000897 | -0.0559 | 4.91 | 0.00069 | 0 | 5.18 | 0.000897 | -0.0559 |  | LF | None | 4910 | 0.69 | 4910 | 0.69 | 1.05 | 1.3 | -0.011385 | 4910 | 0.69 | 4910 | 0.69 | 1.05 | 1.3 | -0.0114
LFNoneSCEGroExCZ14 | Com-Iltg-dWatt-LF_OSnone | SCE | Gro | Ex | CZ14 | 4.91 | 0.00069 | 0 | 5.15 | 0.000924 | -0.0579 | 4.91 | 0.00069 | 0 | 5.15 | 0.000924 | -0.0579 |  | LF | None | 4910 | 0.69 | 4910 | 0.69 | 1.05 | 1.34 | -0.011792 | 4910 | 0.69 | 4910 | 0.69 | 1.05 | 1.34 | -0.0118
LFNoneSCEGroExCZ15 | Com-Iltg-dWatt-LF_OSnone | SCE | Gro | Ex | CZ15 | 4.91 | 0.00069 | 0 | 5.54 | 0.000906 | -0.0306 | 4.91 | 0.00069 | 0 | 5.54 | 0.000906 | -0.0306 |  | LF | None | 4910 | 0.69 | 4910 | 0.69 | 1.13 | 1.31 | -0.0062322 | 4910 | 0.69 | 4910 | 0.69 | 1.13 | 1.31 | -0.00623
LFNoneSCEGroExCZ16 | Com-Iltg-dWatt-LF_OSnone | SCE | Gro | Ex | CZ16 | 4.91 | 0.00069 | 0 | 4.71 | 0.000858 | -0.078 | 4.91 | 0.00069 | 0 | 4.71 | 0.000858 | -0.078 |  | LF | None | 4910 | 0.69 | 4910 | 0.69 | 0.959 | 1.24 | -0.015886 | 4910 | 0.69 | 4910 | 0.69 | 0.959 | 1.24 | -0.0159
LFNoneSCEGroExIOU | Com-Iltg-dWatt-LF_OSnone | SCE | Gro | Ex | IOU | 4.91 | 0.00069 | 0 | 5.1514 | 0.00088859 | -0.057335 | 4.91 | 0.00069 | 0 | 5.1514 | 0.00088859 | -0.057335 |  | LF | None | 4910 | 0.69 | 4910 | 0.69 | 1.05 | 1.29 | -0.011677 | 4910 | 0.69 | 4910 | 0.69 | 1.05 | 1.29 | -0.0117
LFNoneSCEGroNewCZ05 | Com-Iltg-dWatt-LF_OSnone | SCE | Gro | New | CZ05 | 4.91 | 0.00069 | 0 | 4.88 | 0.000865 | -0.0765 | 4.91 | 0.00069 | 0 | 4.88 | 0.000865 | -0.0765 |  | LF | None | 4910 | 0.69 | 4910 | 0.69 | 0.994 | 1.25 | -0.01558 | 4910 | 0.69 | 4910 | 0.69 | 0.994 | 1.25 | -0.0156
LFNoneSCEGroNewCZ06 | Com-Iltg-dWatt-LF_OSnone | SCE | Gro | New | CZ06 | 4.91 | 0.00069 | 0 | 5.26 | 0.000865 | -0.0481 | 4.91 | 0.00069 | 0 | 5.26 | 0.000865 | -0.0481 |  | LF | None | 4910 | 0.69 | 4910 | 0.69 | 1.07 | 1.25 | -0.0097963 | 4910 | 0.69 | 4910 | 0.69 | 1.07 | 1.25 | -0.0098
LFNoneSCEGroNewCZ08 | Com-Iltg-dWatt-LF_OSnone | SCE | Gro | New | CZ08 | 4.91 | 0.00069 | 0 | 5.32 | 0.000887 | -0.0424 | 4.91 | 0.00069 | 0 | 5.32 | 0.000887 | -0.0424 |  | LF | None | 4910 | 0.69 | 4910 | 0.69 | 1.08 | 1.29 | -0.0086354 | 4910 | 0.69 | 4910 | 0.69 | 1.08 | 1.29 | -0.00864
LFNoneSCEGroNewCZ09 | Com-Iltg-dWatt-LF_OSnone | SCE | Gro | New | CZ09 | 4.91 | 0.00069 | 0 | 5.3 | 0.000945 | -0.0454 | 4.91 | 0.00069 | 0 | 5.3 | 0.000945 | -0.0454 |  | LF | None | 4910 | 0.69 | 4910 | 0.69 | 1.08 | 1.37 | -0.0092464 | 4910 | 0.69 | 4910 | 0.69 | 1.08 | 1.37 | -0.00925
LFNoneSCEGroNewCZ10 | Com-Iltg-dWatt-LF_OSnone | SCE | Gro | New | CZ10 | 4.91 | 0.00069 | 0 | 5.35 | 0.000958 | -0.0453 | 4.91 | 0.00069 | 0 | 5.35 | 0.000958 | -0.0453 |  | LF | None | 4910 | 0.69 | 4910 | 0.69 | 1.09 | 1.39 | -0.0092261 | 4910 | 0.69 | 4910 | 0.69 | 1.09 | 1.39 | -0.00923
LFNoneSCEGroNewCZ13 | Com-Iltg-dWatt-LF_OSnone | SCE | Gro | New | CZ13 | 4.91 | 0.00069 | 0 | 5.35 | 0.000938 | -0.0525 | 4.91 | 0.00069 | 0 | 5.35 | 0.000938 | -0.0525 |  | LF | None | 4910 | 0.69 | 4910 | 0.69 | 1.09 | 1.36 | -0.010692 | 4910 | 0.69 | 4910 | 0.69 | 1.09 | 1.36 | -0.0107
LFNoneSCEGroNewCZ14 | Com-Iltg-dWatt-LF_OSnone | SCE | Gro | New | CZ14 | 4.91 | 0.00069 | 0 | 5.34 | 0.000953 | -0.0545 | 4.91 | 0.00069 | 0 | 5.34 | 0.000953 | -0.0545 |  | LF | None | 4910 | 0.69 | 4910 | 0.69 | 1.09 | 1.38 | -0.0111 | 4910 | 0.69 | 4910 | 0.69 | 1.09 | 1.38 | -0.0111
LFNoneSCEGroNewCZ15 | Com-Iltg-dWatt-LF_OSnone | SCE | Gro | New | CZ15 | 4.91 | 0.00069 | 0 | 5.77 | 0.000964 | -0.025 | 4.91 | 0.00069 | 0 | 5.77 | 0.000964 | -0.025 |  | LF | None | 4910 | 0.69 | 4910 | 0.69 | 1.18 | 1.4 | -0.0050916 | 4910 | 0.69 | 4910 | 0.69 | 1.18 | 1.4 | -0.00509
LFNoneSCEGroNewCZ16 | Com-Iltg-dWatt-LF_OSnone | SCE | Gro | New | CZ16 | 4.91 | 0.00069 | 0 | 4.86 | 0.000881 | -0.0726 | 4.91 | 0.00069 | 0 | 4.86 | 0.000881 | -0.0726 |  | LF | None | 4910 | 0.69 | 4910 | 0.69 | 0.99 | 1.28 | -0.014786 | 4910 | 0.69 | 4910 | 0.69 | 0.99 | 1.28 | -0.0148
LFNoneSCEGroNewIOU | Com-Iltg-dWatt-LF_OSnone | SCE | Gro | New | IOU | 4.91 | 0.00069 | 0 | 5.3262 | 0.00092203 | -0.045952 | 4.91 | 0.00069 | 0 | 5.3262 | 0.00092203 | -0.045952 |  | LF | None | 4910 | 0.69 | 4910 | 0.69 | 1.08 | 1.34 | -0.0093589 | 4910 | 0.69 | 4910 | 0.69 | 1.08 | 1.34 | -0.00936
LFNoneSCEHspExCZ05 | Com-Iltg-dWatt-LF_OSnone | SCE | Hsp | Ex | CZ05 | 5.26 | 0.000827 | 0 | 5.91 | 0.00102 | -0.0361 | 5.26 | 0.000827 | 0 | 5.91 | 0.00102 | -0.0361 |  | LF | None | 5260 | 0.827 | 5260 | 0.827 | 1.12 | 1.23 | -0.0068631 | 5260 | 0.827 | 5260 | 0.827 | 1.12 | 1.23 | -0.00686
LFNoneSCEHspExCZ06 | Com-Iltg-dWatt-LF_OSnone | SCE | Hsp | Ex | CZ06 | 5.26 | 0.000827 | 0 | 6.09 | 0.00104 | -0.0267 | 5.26 | 0.000827 | 0 | 6.09 | 0.00104 | -0.0267 |  | LF | None | 5260 | 0.827 | 5260 | 0.827 | 1.16 | 1.26 | -0.005076 | 5260 | 0.827 | 5260 | 0.827 | 1.16 | 1.26 | -0.00508
LFNoneSCEHspExCZ08 | Com-Iltg-dWatt-LF_OSnone | SCE | Hsp | Ex | CZ08 | 5.26 | 0.000827 | 0 | 6.13 | 0.00104 | -0.0262 | 5.26 | 0.000827 | 0 | 6.13 | 0.00104 | -0.0262 |  | LF | None | 5260 | 0.827 | 5260 | 0.827 | 1.17 | 1.26 | -0.004981 | 5260 | 0.827 | 5260 | 0.827 | 1.17 | 1.26 | -0.00498
LFNoneSCEHspExCZ09 | Com-Iltg-dWatt-LF_OSnone | SCE | Hsp | Ex | CZ09 | 5.26 | 0.000827 | 0 | 6.16 | 0.00107 | -0.0266 | 5.26 | 0.000827 | 0 | 6.16 | 0.00107 | -0.0266 |  | LF | None | 5260 | 0.827 | 5260 | 0.827 | 1.17 | 1.29 | -0.005057 | 5260 | 0.827 | 5260 | 0.827 | 1.17 | 1.29 | -0.00506
LFNoneSCEHspExCZ10 | Com-Iltg-dWatt-LF_OSnone | SCE | Hsp | Ex | CZ10 | 5.26 | 0.000827 | 0 | 6 | 0.00106 | -0.0286 | 5.26 | 0.000827 | 0 | 6 | 0.00106 | -0.0286 |  | LF | None | 5260 | 0.827 | 5260 | 0.827 | 1.14 | 1.28 | -0.0054373 | 5260 | 0.827 | 5260 | 0.827 | 1.14 | 1.28 | -0.00544
LFNoneSCEHspExCZ13 | Com-Iltg-dWatt-LF_OSnone | SCE | Hsp | Ex | CZ13 | 5.26 | 0.000827 | 0 | 5.97 | 0.00106 | -0.0324 | 5.26 | 0.000827 | 0 | 5.97 | 0.00106 | -0.0324 |  | LF | None | 5260 | 0.827 | 5260 | 0.827 | 1.13 | 1.28 | -0.0061597 | 5260 | 0.827 | 5260 | 0.827 | 1.13 | 1.28 | -0.00616
LFNoneSCEHspExCZ14 | Com-Iltg-dWatt-LF_OSnone | SCE | Hsp | Ex | CZ14 | 5.26 | 0.000827 | 0 | 5.95 | 0.00106 | -0.0351 | 5.26 | 0.000827 | 0 | 5.95 | 0.00106 | -0.0351 |  | LF | None | 5260 | 0.827 | 5260 | 0.827 | 1.13 | 1.28 | -0.006673 | 5260 | 0.827 | 5260 | 0.827 | 1.13 | 1.28 | -0.00667
LFNoneSCEHspExCZ15 | Com-Iltg-dWatt-LF_OSnone | SCE | Hsp | Ex | CZ15 | 5.26 | 0.000827 | 0 | 6.24 | 0.00107 | -0.0226 | 5.26 | 0.000827 | 0 | 6.24 | 0.00107 | -0.0226 |  | LF | None | 5260 | 0.827 | 5260 | 0.827 | 1.19 | 1.29 | -0.0042966 | 5260 | 0.827 | 5260 | 0.827 | 1.19 | 1.29 | -0.0043
LFNoneSCEHspExCZ16 | Com-Iltg-dWatt-LF_OSnone | SCE | Hsp | Ex | CZ16 | 5.26 | 0.000827 | 0 | 5.59 | 0.00102 | -0.0477 | 5.26 | 0.000827 | 0 | 5.59 | 0.00102 | -0.0477 |  | LF | None | 5260 | 0.827 | 5260 | 0.827 | 1.06 | 1.23 | -0.0090684 | 5260 | 0.827 | 5260 | 0.827 | 1.06 | 1.23 | -0.00907
LFNoneSCEHspExIOU | Com-Iltg-dWatt-LF_OSnone | SCE | Hsp | Ex | IOU | 5.26 | 0.000827 | 0 | 6.0821 | 0.0010488 | -0.027702 | 5.26 | 0.000827 | 0 | 6.0821 | 0.0010488 | -0.027702 |  | LF | None | 5260 | 0.827 | 5260 | 0.827 | 1.16 | 1.27 | -0.0052665 | 5260 | 0.827 | 5260 | 0.827 | 1.16 | 1.27 | -0.00527
LFNoneSCEHspNewCZ05 | Com-Iltg-dWatt-LF_OSnone | SCE | Hsp | New | CZ05 | 5.26 | 0.000827 | 0 | 5.58 | 0.000985 | -0.0364 | 5.26 | 0.000827 | 0 | 5.58 | 0.000985 | -0.0364 |  | LF | None | 5260 | 0.827 | 5260 | 0.827 | 1.06 | 1.19 | -0.0069202 | 5260 | 0.827 | 5260 | 0.827 | 1.06 | 1.19 | -0.00692
LFNoneSCEHspNewCZ06 | Com-Iltg-dWatt-LF_OSnone | SCE | Hsp | New | CZ06 | 5.26 | 0.000827 | 0 | 5.79 | 0.001 | -0.0285 | 5.26 | 0.000827 | 0 | 5.79 | 0.001 | -0.0285 |  | LF | None | 5260 | 0.827 | 5260 | 0.827 | 1.1 | 1.21 | -0.0054183 | 5260 | 0.827 | 5260 | 0.827 | 1.1 | 1.21 | -0.00542
LFNoneSCEHspNewCZ08 | Com-Iltg-dWatt-LF_OSnone | SCE | Hsp | New | CZ08 | 5.26 | 0.000827 | 0 | 5.84 | 0.00101 | -0.0266 | 5.26 | 0.000827 | 0 | 5.84 | 0.00101 | -0.0266 |  | LF | None | 5260 | 0.827 | 5260 | 0.827 | 1.11 | 1.22 | -0.005057 | 5260 | 0.827 | 5260 | 0.827 | 1.11 | 1.22 | -0.00506
LFNoneSCEHspNewCZ09 | Com-Iltg-dWatt-LF_OSnone | SCE | Hsp | New | CZ09 | 5.26 | 0.000827 | 0 | 5.86 | 0.00103 | -0.0267 | 5.26 | 0.000827 | 0 | 5.86 | 0.00103 | -0.0267 |  | LF | None | 5260 | 0.827 | 5260 | 0.827 | 1.11 | 1.25 | -0.005076 | 5260 | 0.827 | 5260 | 0.827 | 1.11 | 1.25 | -0.00508
LFNoneSCEHspNewCZ10 | Com-Iltg-dWatt-LF_OSnone | SCE | Hsp | New | CZ10 | 5.26 | 0.000827 | 0 | 5.84 | 0.00104 | -0.0283 | 5.26 | 0.000827 | 0 | 5.84 | 0.00104 | -0.0283 |  | LF | None | 5260 | 0.827 | 5260 | 0.827 | 1.11 | 1.26 | -0.0053802 | 5260 | 0.827 | 5260 | 0.827 | 1.11 | 1.26 | -0.00538
LFNoneSCEHspNewCZ13 | Com-Iltg-dWatt-LF_OSnone | SCE | Hsp | New | CZ13 | 5.26 | 0.000827 | 0 | 5.82 | 0.00104 | -0.0325 | 5.26 | 0.000827 | 0 | 5.82 | 0.00104 | -0.0325 |  | LF | None | 5260 | 0.827 | 5260 | 0.827 | 1.11 | 1.26 | -0.0061787 | 5260 | 0.827 | 5260 | 0.827 | 1.11 | 1.26 | -0.00618
LFNoneSCEHspNewCZ14 | Com-Iltg-dWatt-LF_OSnone | SCE | Hsp | New | CZ14 | 5.26 | 0.000827 | 0 | 5.75 | 0.00103 | -0.0359 | 5.26 | 0.000827 | 0 | 5.75 | 0.00103 | -0.0359 |  | LF | None | 5260 | 0.827 | 5260 | 0.827 | 1.09 | 1.25 | -0.0068251 | 5260 | 0.827 | 5260 | 0.827 | 1.09 | 1.25 | -0.00683
LFNoneSCEHspNewCZ15 | Com-Iltg-dWatt-LF_OSnone | SCE | Hsp | New | CZ15 | 5.26 | 0.000827 | 0 | 6.13 | 0.00105 | -0.0201 | 5.26 | 0.000827 | 0 | 6.13 | 0.00105 | -0.0201 |  | LF | None | 5260 | 0.827 | 5260 | 0.827 | 1.17 | 1.27 | -0.0038213 | 5260 | 0.827 | 5260 | 0.827 | 1.17 | 1.27 | -0.00382
LFNoneSCEHspNewCZ16 | Com-Iltg-dWatt-LF_OSnone | SCE | Hsp | New | CZ16 | 5.26 | 0.000827 | 0 | 5.37 | 0.000996 | -0.0515 | 5.26 | 0.000827 | 0 | 5.37 | 0.000996 | -0.0515 |  | LF | None | 5260 | 0.827 | 5260 | 0.827 | 1.02 | 1.2 | -0.0097909 | 5260 | 0.827 | 5260 | 0.827 | 1.02 | 1.2 | -0.00979
LFNoneSCEHspNewIOU | Com-Iltg-dWatt-LF_OSnone | SCE | Hsp | New | IOU | 5.26 | 0.000827 | 0 | 5.8251 | 0.0010214 | -0.028581 | 5.26 | 0.000827 | 0 | 5.8251 | 0.0010214 | -0.028581 |  | LF | None | 5260 | 0.827 | 5260 | 0.827 | 1.11 | 1.24 | -0.0054337 | 5260 | 0.827 | 5260 | 0.827 | 1.11 | 1.24 | -0.00543
LFNoneSCEHtlExCZ05 | Com-Iltg-dWatt-LF_OSnone | SCE | Htl | Ex | CZ05 | 1.95 | 0.000242 | 0 | 1.91 | 0.000305 | -0.0069 | 1.95 | 0.000242 | 0 | 1.91 | 0.000305 | -0.0069 |  | LF | None | 1950 | 0.242 | 1950 | 0.242 | 0.979 | 1.26 | -0.0035385 | 1950 | 0.242 | 1950 | 0.242 | 0.979 | 1.26 | -0.00354
LFNoneSCEHtlExCZ06 | Com-Iltg-dWatt-LF_OSnone | SCE | Htl | Ex | CZ06 | 1.95 | 0.000242 | 0 | 2.12 | 0.000306 | -0.00456 | 1.95 | 0.000242 | 0 | 2.12 | 0.000306 | -0.00456 |  | LF | None | 1950 | 0.242 | 1950 | 0.242 | 1.09 | 1.26 | -0.0023385 | 1950 | 0.242 | 1950 | 0.242 | 1.09 | 1.26 | -0.00234
LFNoneSCEHtlExCZ08 | Com-Iltg-dWatt-LF_OSnone | SCE | Htl | Ex | CZ08 | 1.95 | 0.000242 | 0 | 2.16 | 0.000309 | -0.00405 | 1.95 | 0.000242 | 0 | 2.16 | 0.000309 | -0.00405 |  | LF | None | 1950 | 0.242 | 1950 | 0.242 | 1.11 | 1.28 | -0.0020769 | 1950 | 0.242 | 1950 | 0.242 | 1.11 | 1.28 | -0.00208
LFNoneSCEHtlExCZ09 | Com-Iltg-dWatt-LF_OSnone | SCE | Htl | Ex | CZ09 | 1.95 | 0.000242 | 0 | 2.14 | 0.000314 | -0.00411 | 1.95 | 0.000242 | 0 | 2.14 | 0.000314 | -0.00411 |  | LF | None | 1950 | 0.242 | 1950 | 0.242 | 1.1 | 1.3 | -0.0021077 | 1950 | 0.242 | 1950 | 0.242 | 1.1 | 1.3 | -0.00211
LFNoneSCEHtlExCZ10 | Com-Iltg-dWatt-LF_OSnone | SCE | Htl | Ex | CZ10 | 1.95 | 0.000242 | 0 | 2.08 | 0.000311 | -0.00438 | 1.95 | 0.000242 | 0 | 2.08 | 0.000311 | -0.00438 |  | LF | None | 1950 | 0.242 | 1950 | 0.242 | 1.07 | 1.29 | -0.0022462 | 1950 | 0.242 | 1950 | 0.242 | 1.07 | 1.29 | -0.00225
LFNoneSCEHtlExCZ13 | Com-Iltg-dWatt-LF_OSnone | SCE | Htl | Ex | CZ13 | 1.95 | 0.000242 | 0 | 2.02 | 0.000311 | -0.0059 | 1.95 | 0.000242 | 0 | 2.02 | 0.000311 | -0.0059 |  | LF | None | 1950 | 0.242 | 1950 | 0.242 | 1.04 | 1.29 | -0.0030256 | 1950 | 0.242 | 1950 | 0.242 | 1.04 | 1.29 | -0.00303
LFNoneSCEHtlExCZ14 | Com-Iltg-dWatt-LF_OSnone | SCE | Htl | Ex | CZ14 | 1.95 | 0.000242 | 0 | 2 | 0.000313 | -0.00594 | 1.95 | 0.000242 | 0 | 2 | 0.000313 | -0.00594 |  | LF | None | 1950 | 0.242 | 1950 | 0.242 | 1.03 | 1.29 | -0.0030462 | 1950 | 0.242 | 1950 | 0.242 | 1.03 | 1.29 | -0.00305
LFNoneSCEHtlExCZ15 | Com-Iltg-dWatt-LF_OSnone | SCE | Htl | Ex | CZ15 | 1.95 | 0.000242 | 0 | 2.26 | 0.000314 | -0.00243 | 1.95 | 0.000242 | 0 | 2.26 | 0.000314 | -0.00243 |  | LF | None | 1950 | 0.242 | 1950 | 0.242 | 1.16 | 1.3 | -0.0012462 | 1950 | 0.242 | 1950 | 0.242 | 1.16 | 1.3 | -0.00125
LFNoneSCEHtlExCZ16 | Com-Iltg-dWatt-LF_OSnone | SCE | Htl | Ex | CZ16 | 1.95 | 0.000242 | 0 | 1.74 | 0.000304 | -0.0102 | 1.95 | 0.000242 | 0 | 1.74 | 0.000304 | -0.0102 |  | LF | None | 1950 | 0.242 | 1950 | 0.242 | 0.892 | 1.26 | -0.0052308 | 1950 | 0.242 | 1950 | 0.242 | 0.892 | 1.26 | -0.00523
LFNoneSCEHtlExIOU | Com-Iltg-dWatt-LF_OSnone | SCE | Htl | Ex | IOU | 1.95 | 0.000242 | 0 | 2.1307 | 0.00030951 | -0.0043318 | 1.95 | 0.000242 | 0 | 2.1307 | 0.00030951 | -0.0043318 |  | LF | None | 1950 | 0.242 | 1950 | 0.242 | 1.09 | 1.28 | -0.0022214 | 1950 | 0.242 | 1950 | 0.242 | 1.09 | 1.28 | -0.00222
LFNoneSCEHtlNewCZ05 | Com-Iltg-dWatt-LF_OSnone | SCE | Htl | New | CZ05 | 1.95 | 0.000242 | 0 | 1.81 | 0.000309 | -0.00775 | 1.95 | 0.000242 | 0 | 1.81 | 0.000309 | -0.00775 |  | LF | None | 1950 | 0.242 | 1950 | 0.242 | 0.928 | 1.28 | -0.0039744 | 1950 | 0.242 | 1950 | 0.242 | 0.928 | 1.28 | -0.00397
LFNoneSCEHtlNewCZ06 | Com-Iltg-dWatt-LF_OSnone | SCE | Htl | New | CZ06 | 1.95 | 0.000242 | 0 | 2.07 | 0.000313 | -0.00432 | 1.95 | 0.000242 | 0 | 2.07 | 0.000313 | -0.00432 |  | LF | None | 1950 | 0.242 | 1950 | 0.242 | 1.06 | 1.29 | -0.0022154 | 1950 | 0.242 | 1950 | 0.242 | 1.06 | 1.29 | -0.00222
LFNoneSCEHtlNewCZ08 | Com-Iltg-dWatt-LF_OSnone | SCE | Htl | New | CZ08 | 1.95 | 0.000242 | 0 | 2.11 | 0.000316 | -0.00372 | 1.95 | 0.000242 | 0 | 2.11 | 0.000316 | -0.00372 |  | LF | None | 1950 | 0.242 | 1950 | 0.242 | 1.08 | 1.31 | -0.0019077 | 1950 | 0.242 | 1950 | 0.242 | 1.08 | 1.31 | -0.00191
LFNoneSCEHtlNewCZ09 | Com-Iltg-dWatt-LF_OSnone | SCE | Htl | New | CZ09 | 1.95 | 0.000242 | 0 | 2.09 | 0.000322 | -0.00417 | 1.95 | 0.000242 | 0 | 2.09 | 0.000322 | -0.00417 |  | LF | None | 1950 | 0.242 | 1950 | 0.242 | 1.07 | 1.33 | -0.0021385 | 1950 | 0.242 | 1950 | 0.242 | 1.07 | 1.33 | -0.00214
LFNoneSCEHtlNewCZ10 | Com-Iltg-dWatt-LF_OSnone | SCE | Htl | New | CZ10 | 1.95 | 0.000242 | 0 | 2.07 | 0.000327 | -0.00481 | 1.95 | 0.000242 | 0 | 2.07 | 0.000327 | -0.00481 |  | LF | None | 1950 | 0.242 | 1950 | 0.242 | 1.06 | 1.35 | -0.0024667 | 1950 | 0.242 | 1950 | 0.242 | 1.06 | 1.35 | -0.00247
LFNoneSCEHtlNewCZ13 | Com-Iltg-dWatt-LF_OSnone | SCE | Htl | New | CZ13 | 1.95 | 0.000242 | 0 | 1.99 | 0.000322 | -0.00639 | 1.95 | 0.000242 | 0 | 1.99 | 0.000322 | -0.00639 |  | LF | None | 1950 | 0.242 | 1950 | 0.242 | 1.02 | 1.33 | -0.0032769 | 1950 | 0.242 | 1950 | 0.242 | 1.02 | 1.33 | -0.00328
LFNoneSCEHtlNewCZ14 | Com-Iltg-dWatt-LF_OSnone | SCE | Htl | New | CZ14 | 1.95 | 0.000242 | 0 | 1.96 | 0.000325 | -0.00721 | 1.95 | 0.000242 | 0 | 1.96 | 0.000325 | -0.00721 |  | LF | None | 1950 | 0.242 | 1950 | 0.242 | 1.01 | 1.34 | -0.0036974 | 1950 | 0.242 | 1950 | 0.242 | 1.01 | 1.34 | -0.0037
LFNoneSCEHtlNewCZ15 | Com-Iltg-dWatt-LF_OSnone | SCE | Htl | New | CZ15 | 1.95 | 0.000242 | 0 | 2.28 | 0.00033 | -0.00249 | 1.95 | 0.000242 | 0 | 2.28 | 0.00033 | -0.00249 |  | LF | None | 1950 | 0.242 | 1950 | 0.242 | 1.17 | 1.36 | -0.0012769 | 1950 | 0.242 | 1950 | 0.242 | 1.17 | 1.36 | -0.00128
LFNoneSCEHtlNewCZ16 | Com-Iltg-dWatt-LF_OSnone | SCE | Htl | New | CZ16 | 1.95 | 0.000242 | 0 | 1.68 | 0.00031 | -0.0123 | 1.95 | 0.000242 | 0 | 1.68 | 0.00031 | -0.0123 |  | LF | None | 1950 | 0.242 | 1950 | 0.242 | 0.862 | 1.28 | -0.0063077 | 1950 | 0.242 | 1950 | 0.242 | 0.862 | 1.28 | -0.00631
LFNoneSCEHtlNewIOU | Com-Iltg-dWatt-LF_OSnone | SCE | Htl | New | IOU | 1.95 | 0.000242 | 0 | 2.1055 | 0.00032114 | -0.0043922 | 1.95 | 0.000242 | 0 | 2.1055 | 0.00032114 | -0.0043922 |  | LF | None | 1950 | 0.242 | 1950 | 0.242 | 1.08 | 1.33 | -0.0022524 | 1950 | 0.242 | 1950 | 0.242 | 1.08 | 1.33 | -0.00225
LFNoneSCEMBTExCZ05 | Com-Iltg-dWatt-LF_OSnone | SCE | MBT | Ex | CZ05 | 3.53 | 0.000851 | 0 | 4.05 | 0.00107 | -0.00193 | 3.53 | 0.000851 | 0 | 4.05 | 0.00107 | -0.00193 |  | LF | None | 3530 | 0.851 | 3530 | 0.851 | 1.15 | 1.26 | -0.00054674 | 3530 | 0.851 | 3530 | 0.851 | 1.15 | 1.26 | -0.000547
LFNoneSCEMBTExCZ06 | Com-Iltg-dWatt-LF_OSnone | SCE | MBT | Ex | CZ06 | 3.53 | 0.000851 | 0 | 4.15 | 0.00104 | -0.000882 | 3.53 | 0.000851 | 0 | 4.15 | 0.00104 | -0.000882 |  | LF | None | 3530 | 0.851 | 3530 | 0.851 | 1.18 | 1.22 | -0.00024986 | 3530 | 0.851 | 3530 | 0.851 | 1.18 | 1.22 | -0.00025
LFNoneSCEMBTExCZ08 | Com-Iltg-dWatt-LF_OSnone | SCE | MBT | Ex | CZ08 | 3.53 | 0.000851 | 0 | 4.17 | 0.00108 | -0.000593 | 3.53 | 0.000851 | 0 | 4.17 | 0.00108 | -0.000593 |  | LF | None | 3530 | 0.851 | 3530 | 0.851 | 1.18 | 1.27 | -0.00016799 | 3530 | 0.851 | 3530 | 0.851 | 1.18 | 1.27 | -0.000168
LFNoneSCEMBTExCZ09 | Com-Iltg-dWatt-LF_OSnone | SCE | MBT | Ex | CZ09 | 3.53 | 0.000851 | 0 | 4.16 | 0.00109 | -0.00107 | 3.53 | 0.000851 | 0 | 4.16 | 0.00109 | -0.00107 |  | LF | None | 3530 | 0.851 | 3530 | 0.851 | 1.18 | 1.28 | -0.00030312 | 3530 | 0.851 | 3530 | 0.851 | 1.18 | 1.28 | -0.000303
LFNoneSCEMBTExCZ10 | Com-Iltg-dWatt-LF_OSnone | SCE | MBT | Ex | CZ10 | 3.53 | 0.000851 | 0 | 4.03 | 0.00109 | -0.00116 | 3.53 | 0.000851 | 0 | 4.03 | 0.00109 | -0.00116 |  | LF | None | 3530 | 0.851 | 3530 | 0.851 | 1.14 | 1.28 | -0.00032861 | 3530 | 0.851 | 3530 | 0.851 | 1.14 | 1.28 | -0.000329
LFNoneSCEMBTExCZ13 | Com-Iltg-dWatt-LF_OSnone | SCE | MBT | Ex | CZ13 | 3.53 | 0.000851 | 0 | 4.03 | 0.00105 | -0.00249 | 3.53 | 0.000851 | 0 | 4.03 | 0.00105 | -0.00249 |  | LF | None | 3530 | 0.851 | 3530 | 0.851 | 1.14 | 1.23 | -0.00070538 | 3530 | 0.851 | 3530 | 0.851 | 1.14 | 1.23 | -0.000705
LFNoneSCEMBTExCZ14 | Com-Iltg-dWatt-LF_OSnone | SCE | MBT | Ex | CZ14 | 3.53 | 0.000851 | 0 | 4.03 | 0.00109 | -0.00284 | 3.53 | 0.000851 | 0 | 4.03 | 0.00109 | -0.00284 |  | LF | None | 3530 | 0.851 | 3530 | 0.851 | 1.14 | 1.28 | -0.00080453 | 3530 | 0.851 | 3530 | 0.851 | 1.14 | 1.28 | -0.000805
LFNoneSCEMBTExCZ15 | Com-Iltg-dWatt-LF_OSnone | SCE | MBT | Ex | CZ15 | 3.53 | 0.000851 | 0 | 4.19 | 0.00109 | 0 | 3.53 | 0.000851 | 0 | 4.19 | 0.00109 | 0 |  | LF | None | 3530 | 0.851 | 3530 | 0.851 | 1.19 | 1.28 | 0 | 3530 | 0.851 | 3530 | 0.851 | 1.19 | 1.28 | 0
LFNoneSCEMBTExCZ16 | Com-Iltg-dWatt-LF_OSnone | SCE | MBT | Ex | CZ16 | 3.53 | 0.000851 | 0 | 3.79 | 0.00102 | -0.00967 | 3.53 | 0.000851 | 0 | 3.79 | 0.00102 | -0.00967 |  | LF | None | 3530 | 0.851 | 3530 | 0.851 | 1.07 | 1.2 | -0.0027394 | 3530 | 0.851 | 3530 | 0.851 | 1.07 | 1.2 | -0.00274
LFNoneSCEMBTExIOU | Com-Iltg-dWatt-LF_OSnone | SCE | MBT | Ex | IOU | 3.53 | 0.000851 | 0 | 4.1251 | 0.0010733 | -0.0011185 | 3.53 | 0.000851 | 0 | 4.1251 | 0.0010733 | -0.0011185 |  | LF | None | 3530 | 0.851 | 3530 | 0.851 | 1.17 | 1.26 | -0.00031685 | 3530 | 0.851 | 3530 | 0.851 | 1.17 | 1.26 | -0.000317
LFNoneSCEMBTNewCZ05 | Com-Iltg-dWatt-LF_OSnone | SCE | MBT | New | CZ05 | 3.53 | 0.000851 | 0 | 3.82 | 0.00106 | -0.00118 | 3.53 | 0.000851 | 0 | 3.82 | 0.00106 | -0.00118 |  | LF | None | 3530 | 0.851 | 3530 | 0.851 | 1.08 | 1.25 | -0.00033428 | 3530 | 0.851 | 3530 | 0.851 | 1.08 | 1.25 | -0.000334
LFNoneSCEMBTNewCZ06 | Com-Iltg-dWatt-LF_OSnone | SCE | MBT | New | CZ06 | 3.53 | 0.000851 | 0 | 3.96 | 0.00107 | -0.00118 | 3.53 | 0.000851 | 0 | 3.96 | 0.00107 | -0.00118 |  | LF | None | 3530 | 0.851 | 3530 | 0.851 | 1.12 | 1.26 | -0.00033428 | 3530 | 0.851 | 3530 | 0.851 | 1.12 | 1.26 | -0.000334
LFNoneSCEMBTNewCZ08 | Com-Iltg-dWatt-LF_OSnone | SCE | MBT | New | CZ08 | 3.53 | 0.000851 | 0 | 3.98 | 0.0011 | -0.000942 | 3.53 | 0.000851 | 0 | 3.98 | 0.0011 | -0.000942 |  | LF | None | 3530 | 0.851 | 3530 | 0.851 | 1.13 | 1.29 | -0.00026686 | 3530 | 0.851 | 3530 | 0.851 | 1.13 | 1.29 | -0.000267
LFNoneSCEMBTNewCZ09 | Com-Iltg-dWatt-LF_OSnone | SCE | MBT | New | CZ09 | 3.53 | 0.000851 | 0 | 3.97 | 0.00112 | -0.00111 | 3.53 | 0.000851 | 0 | 3.97 | 0.00112 | -0.00111 |  | LF | None | 3530 | 0.851 | 3530 | 0.851 | 1.12 | 1.32 | -0.00031445 | 3530 | 0.851 | 3530 | 0.851 | 1.12 | 1.32 | -0.000314
LFNoneSCEMBTNewCZ10 | Com-Iltg-dWatt-LF_OSnone | SCE | MBT | New | CZ10 | 3.53 | 0.000851 | 0 | 3.98 | 0.00114 | -0.00118 | 3.53 | 0.000851 | 0 | 3.98 | 0.00114 | -0.00118 |  | LF | None | 3530 | 0.851 | 3530 | 0.851 | 1.13 | 1.34 | -0.00033428 | 3530 | 0.851 | 3530 | 0.851 | 1.13 | 1.34 | -0.000334
LFNoneSCEMBTNewCZ13 | Com-Iltg-dWatt-LF_OSnone | SCE | MBT | New | CZ13 | 3.53 | 0.000851 | 0 | 3.94 | 0.00111 | -0.00206 | 3.53 | 0.000851 | 0 | 3.94 | 0.00111 | -0.00206 |  | LF | None | 3530 | 0.851 | 3530 | 0.851 | 1.12 | 1.3 | -0.00058357 | 3530 | 0.851 | 3530 | 0.851 | 1.12 | 1.3 | -0.000584
LFNoneSCEMBTNewCZ14 | Com-Iltg-dWatt-LF_OSnone | SCE | MBT | New | CZ14 | 3.53 | 0.000851 | 0 | 3.94 | 0.00113 | -0.00223 | 3.53 | 0.000851 | 0 | 3.94 | 0.00113 | -0.00223 |  | LF | None | 3530 | 0.851 | 3530 | 0.851 | 1.12 | 1.33 | -0.00063173 | 3530 | 0.851 | 3530 | 0.851 | 1.12 | 1.33 | -0.000632
LFNoneSCEMBTNewCZ15 | Com-Iltg-dWatt-LF_OSnone | SCE | MBT | New | CZ15 | 3.53 | 0.000851 | 0 | 4.19 | 0.00114 | 0 | 3.53 | 0.000851 | 0 | 4.19 | 0.00114 | 0 |  | LF | None | 3530 | 0.851 | 3530 | 0.851 | 1.19 | 1.34 | 0 | 3530 | 0.851 | 3530 | 0.851 | 1.19 | 1.34 | 0
LFNoneSCEMBTNewCZ16 | Com-Iltg-dWatt-LF_OSnone | SCE | MBT | New | CZ16 | 3.53 | 0.000851 | 0 | 3.74 | 0.00106 | -0.00709 | 3.53 | 0.000851 | 0 | 3.74 | 0.00106 | -0.00709 |  | LF | None | 3530 | 0.851 | 3530 | 0.851 | 1.06 | 1.25 | -0.0020085 | 3530 | 0.851 | 3530 | 0.851 | 1.06 | 1.25 | -0.00201
LFNoneSCEMBTNewIOU | Com-Iltg-dWatt-LF_OSnone | SCE | MBT | New | IOU | 3.53 | 0.000851 | 0 | 3.9883 | 0.0011145 | -0.0012513 | 3.53 | 0.000851 | 0 | 3.9883 | 0.0011145 | -0.0012513 |  | LF | None | 3530 | 0.851 | 3530 | 0.851 | 1.13 | 1.31 | -0.00035446 | 3530 | 0.851 | 3530 | 0.851 | 1.13 | 1.31 | -0.000354
LFNoneSCEMLIExCZ05 | Com-Iltg-dWatt-LF_OSnone | SCE | MLI | Ex | CZ05 | 3.22 | 0.000924 | 0 | 3.37 | 0.00113 | -0.0171 | 3.22 | 0.000924 | 0 | 3.37 | 0.00113 | -0.0171 |  | LF | None | 3220 | 0.924 | 3220 | 0.924 | 1.05 | 1.22 | -0.0053106 | 3220 | 0.924 | 3220 | 0.924 | 1.05 | 1.22 | -0.00531
LFNoneSCEMLIExCZ06 | Com-Iltg-dWatt-LF_OSnone | SCE | MLI | Ex | CZ06 | 3.22 | 0.000924 | 0 | 3.56 | 0.00111 | -0.00582 | 3.22 | 0.000924 | 0 | 3.56 | 0.00111 | -0.00582 |  | LF | None | 3220 | 0.924 | 3220 | 0.924 | 1.11 | 1.2 | -0.0018075 | 3220 | 0.924 | 3220 | 0.924 | 1.11 | 1.2 | -0.00181
LFNoneSCEMLIExCZ08 | Com-Iltg-dWatt-LF_OSnone | SCE | MLI | Ex | CZ08 | 3.22 | 0.000924 | 0 | 3.58 | 0.00111 | -0.00476 | 3.22 | 0.000924 | 0 | 3.58 | 0.00111 | -0.00476 |  | LF | None | 3220 | 0.924 | 3220 | 0.924 | 1.11 | 1.2 | -0.0014783 | 3220 | 0.924 | 3220 | 0.924 | 1.11 | 1.2 | -0.00148
LFNoneSCEMLIExCZ09 | Com-Iltg-dWatt-LF_OSnone | SCE | MLI | Ex | CZ09 | 3.22 | 0.000924 | 0 | 3.56 | 0.00113 | -0.00666 | 3.22 | 0.000924 | 0 | 3.56 | 0.00113 | -0.00666 |  | LF | None | 3220 | 0.924 | 3220 | 0.924 | 1.11 | 1.22 | -0.0020683 | 3220 | 0.924 | 3220 | 0.924 | 1.11 | 1.22 | -0.00207
LFNoneSCEMLIExCZ10 | Com-Iltg-dWatt-LF_OSnone | SCE | MLI | Ex | CZ10 | 3.22 | 0.000924 | 0 | 3.47 | 0.00112 | -0.00727 | 3.22 | 0.000924 | 0 | 3.47 | 0.00112 | -0.00727 |  | LF | None | 3220 | 0.924 | 3220 | 0.924 | 1.08 | 1.21 | -0.0022578 | 3220 | 0.924 | 3220 | 0.924 | 1.08 | 1.21 | -0.00226
LFNoneSCEMLIExCZ13 | Com-Iltg-dWatt-LF_OSnone | SCE | MLI | Ex | CZ13 | 3.22 | 0.000924 | 0 | 3.43 | 0.00111 | -0.0174 | 3.22 | 0.000924 | 0 | 3.43 | 0.00111 | -0.0174 |  | LF | None | 3220 | 0.924 | 3220 | 0.924 | 1.07 | 1.2 | -0.0054037 | 3220 | 0.924 | 3220 | 0.924 | 1.07 | 1.2 | -0.0054
LFNoneSCEMLIExCZ14 | Com-Iltg-dWatt-LF_OSnone | SCE | MLI | Ex | CZ14 | 3.22 | 0.000924 | 0 | 3.4 | 0.00112 | -0.0202 | 3.22 | 0.000924 | 0 | 3.4 | 0.00112 | -0.0202 |  | LF | None | 3220 | 0.924 | 3220 | 0.924 | 1.06 | 1.21 | -0.0062733 | 3220 | 0.924 | 3220 | 0.924 | 1.06 | 1.21 | -0.00627
LFNoneSCEMLIExCZ15 | Com-Iltg-dWatt-LF_OSnone | SCE | MLI | Ex | CZ15 | 3.22 | 0.000924 | 0 | 3.71 | 0.00111 | -0.00193 | 3.22 | 0.000924 | 0 | 3.71 | 0.00111 | -0.00193 |  | LF | None | 3220 | 0.924 | 3220 | 0.924 | 1.15 | 1.2 | -0.00059938 | 3220 | 0.924 | 3220 | 0.924 | 1.15 | 1.2 | -0.000599
LFNoneSCEMLIExCZ16 | Com-Iltg-dWatt-LF_OSnone | SCE | MLI | Ex | CZ16 | 3.22 | 0.000924 | 0 | 3.17 | 0.0011 | -0.0392 | 3.22 | 0.000924 | 0 | 3.17 | 0.0011 | -0.0392 |  | LF | None | 3220 | 0.924 | 3220 | 0.924 | 0.984 | 1.19 | -0.012174 | 3220 | 0.924 | 3220 | 0.924 | 0.984 | 1.19 | -0.0122
LFNoneSCEMLIExIOU | Com-Iltg-dWatt-LF_OSnone | SCE | MLI | Ex | IOU | 3.22 | 0.000924 | 0 | 3.5425 | 0.0011149 | -0.0071813 | 3.22 | 0.000924 | 0 | 3.5425 | 0.0011149 | -0.0071813 |  | LF | None | 3220 | 0.924 | 3220 | 0.924 | 1.1 | 1.21 | -0.0022302 | 3220 | 0.924 | 3220 | 0.924 | 1.1 | 1.21 | -0.00223
LFNoneSCEMLINewCZ05 | Com-Iltg-dWatt-LF_OSnone | SCE | MLI | New | CZ05 | 3.22 | 0.000924 | 0 | 3.24 | 0.0011 | -0.0208 | 3.22 | 0.000924 | 0 | 3.24 | 0.0011 | -0.0208 |  | LF | None | 3220 | 0.924 | 3220 | 0.924 | 1.01 | 1.19 | -0.0064596 | 3220 | 0.924 | 3220 | 0.924 | 1.01 | 1.19 | -0.00646
LFNoneSCEMLINewCZ06 | Com-Iltg-dWatt-LF_OSnone | SCE | MLI | New | CZ06 | 3.22 | 0.000924 | 0 | 3.45 | 0.00113 | -0.00901 | 3.22 | 0.000924 | 0 | 3.45 | 0.00113 | -0.00901 |  | LF | None | 3220 | 0.924 | 3220 | 0.924 | 1.07 | 1.22 | -0.0027981 | 3220 | 0.924 | 3220 | 0.924 | 1.07 | 1.22 | -0.0028
LFNoneSCEMLINewCZ08 | Com-Iltg-dWatt-LF_OSnone | SCE | MLI | New | CZ08 | 3.22 | 0.000924 | 0 | 3.5 | 0.00114 | -0.00701 | 3.22 | 0.000924 | 0 | 3.5 | 0.00114 | -0.00701 |  | LF | None | 3220 | 0.924 | 3220 | 0.924 | 1.09 | 1.23 | -0.002177 | 3220 | 0.924 | 3220 | 0.924 | 1.09 | 1.23 | -0.00218
LFNoneSCEMLINewCZ09 | Com-Iltg-dWatt-LF_OSnone | SCE | MLI | New | CZ09 | 3.22 | 0.000924 | 0 | 3.53 | 0.00119 | -0.00801 | 3.22 | 0.000924 | 0 | 3.53 | 0.00119 | -0.00801 |  | LF | None | 3220 | 0.924 | 3220 | 0.924 | 1.1 | 1.29 | -0.0024876 | 3220 | 0.924 | 3220 | 0.924 | 1.1 | 1.29 | -0.00249
LFNoneSCEMLINewCZ10 | Com-Iltg-dWatt-LF_OSnone | SCE | MLI | New | CZ10 | 3.22 | 0.000924 | 0 | 3.55 | 0.00121 | -0.00862 | 3.22 | 0.000924 | 0 | 3.55 | 0.00121 | -0.00862 |  | LF | None | 3220 | 0.924 | 3220 | 0.924 | 1.1 | 1.31 | -0.002677 | 3220 | 0.924 | 3220 | 0.924 | 1.1 | 1.31 | -0.00268
LFNoneSCEMLINewCZ13 | Com-Iltg-dWatt-LF_OSnone | SCE | MLI | New | CZ13 | 3.22 | 0.000924 | 0 | 3.5 | 0.0012 | -0.0176 | 3.22 | 0.000924 | 0 | 3.5 | 0.0012 | -0.0176 |  | LF | None | 3220 | 0.924 | 3220 | 0.924 | 1.09 | 1.3 | -0.0054658 | 3220 | 0.924 | 3220 | 0.924 | 1.09 | 1.3 | -0.00547
LFNoneSCEMLINewCZ14 | Com-Iltg-dWatt-LF_OSnone | SCE | MLI | New | CZ14 | 3.22 | 0.000924 | 0 | 3.48 | 0.0012 | -0.0195 | 3.22 | 0.000924 | 0 | 3.48 | 0.0012 | -0.0195 |  | LF | None | 3220 | 0.924 | 3220 | 0.924 | 1.08 | 1.3 | -0.0060559 | 3220 | 0.924 | 3220 | 0.924 | 1.08 | 1.3 | -0.00606
LFNoneSCEMLINewCZ15 | Com-Iltg-dWatt-LF_OSnone | SCE | MLI | New | CZ15 | 3.22 | 0.000924 | 0 | 3.78 | 0.00123 | -0.00134 | 3.22 | 0.000924 | 0 | 3.78 | 0.00123 | -0.00134 |  | LF | None | 3220 | 0.924 | 3220 | 0.924 | 1.17 | 1.33 | -0.00041615 | 3220 | 0.924 | 3220 | 0.924 | 1.17 | 1.33 | -0.000416
LFNoneSCEMLINewCZ16 | Com-Iltg-dWatt-LF_OSnone | SCE | MLI | New | CZ16 | 3.22 | 0.000924 | 0 | 3.22 | 0.00112 | -0.0383 | 3.22 | 0.000924 | 0 | 3.22 | 0.00112 | -0.0383 |  | LF | None | 3220 | 0.924 | 3220 | 0.924 | 1 | 1.21 | -0.011894 | 3220 | 0.924 | 3220 | 0.924 | 1 | 1.21 | -0.0119
LFNoneSCEMLINewIOU | Com-Iltg-dWatt-LF_OSnone | SCE | MLI | New | IOU | 3.22 | 0.000924 | 0 | 3.5313 | 0.0011786 | -0.0091812 | 3.22 | 0.000924 | 0 | 3.5313 | 0.0011786 | -0.0091812 |  | LF | None | 3220 | 0.924 | 3220 | 0.924 | 1.1 | 1.28 | -0.0028513 | 3220 | 0.924 | 3220 | 0.924 | 1.1 | 1.28 | -0.00285
LFNoneSCEMtlExCZ05 | Com-Iltg-dWatt-LF_OSnone | SCE | Mtl | Ex | CZ05 | 1.55 | 0.000172 | 0 | 1.61 | 0.000217 | -0.0088 | 1.55 | 0.000172 | 0 | 1.61 | 0.000217 | -0.0088 |  | LF | None | 1550 | 0.172 | 1550 | 0.172 | 1.04 | 1.26 | -0.0056774 | 1550 | 0.172 | 1550 | 0.172 | 1.04 | 1.26 | -0.00568
LFNoneSCEMtlExCZ06 | Com-Iltg-dWatt-LF_OSnone | SCE | Mtl | Ex | CZ06 | 1.55 | 0.000172 | 0 | 1.76 | 0.000219 | -0.00461 | 1.55 | 0.000172 | 0 | 1.76 | 0.000219 | -0.00461 |  | LF | None | 1550 | 0.172 | 1550 | 0.172 | 1.14 | 1.27 | -0.0029742 | 1550 | 0.172 | 1550 | 0.172 | 1.14 | 1.27 | -0.00297
LFNoneSCEMtlExCZ08 | Com-Iltg-dWatt-LF_OSnone | SCE | Mtl | Ex | CZ08 | 1.55 | 0.000172 | 0 | 1.79 | 0.000221 | -0.0039 | 1.55 | 0.000172 | 0 | 1.79 | 0.000221 | -0.0039 |  | LF | None | 1550 | 0.172 | 1550 | 0.172 | 1.15 | 1.28 | -0.0025161 | 1550 | 0.172 | 1550 | 0.172 | 1.15 | 1.28 | -0.00252
LFNoneSCEMtlExCZ09 | Com-Iltg-dWatt-LF_OSnone | SCE | Mtl | Ex | CZ09 | 1.55 | 0.000172 | 0 | 1.78 | 0.000227 | -0.00428 | 1.55 | 0.000172 | 0 | 1.78 | 0.000227 | -0.00428 |  | LF | None | 1550 | 0.172 | 1550 | 0.172 | 1.15 | 1.32 | -0.0027613 | 1550 | 0.172 | 1550 | 0.172 | 1.15 | 1.32 | -0.00276
LFNoneSCEMtlExCZ10 | Com-Iltg-dWatt-LF_OSnone | SCE | Mtl | Ex | CZ10 | 1.55 | 0.000172 | 0 | 1.74 | 0.000226 | -0.00486 | 1.55 | 0.000172 | 0 | 1.74 | 0.000226 | -0.00486 |  | LF | None | 1550 | 0.172 | 1550 | 0.172 | 1.12 | 1.31 | -0.0031355 | 1550 | 0.172 | 1550 | 0.172 | 1.12 | 1.31 | -0.00314
LFNoneSCEMtlExCZ13 | Com-Iltg-dWatt-LF_OSnone | SCE | Mtl | Ex | CZ13 | 1.55 | 0.000172 | 0 | 1.69 | 0.000225 | -0.00677 | 1.55 | 0.000172 | 0 | 1.69 | 0.000225 | -0.00677 |  | LF | None | 1550 | 0.172 | 1550 | 0.172 | 1.09 | 1.31 | -0.0043677 | 1550 | 0.172 | 1550 | 0.172 | 1.09 | 1.31 | -0.00437
LFNoneSCEMtlExCZ14 | Com-Iltg-dWatt-LF_OSnone | SCE | Mtl | Ex | CZ14 | 1.55 | 0.000172 | 0 | 1.68 | 0.000226 | -0.00653 | 1.55 | 0.000172 | 0 | 1.68 | 0.000226 | -0.00653 |  | LF | None | 1550 | 0.172 | 1550 | 0.172 | 1.08 | 1.31 | -0.0042129 | 1550 | 0.172 | 1550 | 0.172 | 1.08 | 1.31 | -0.00421
LFNoneSCEMtlExCZ15 | Com-Iltg-dWatt-LF_OSnone | SCE | Mtl | Ex | CZ15 | 1.55 | 0.000172 | 0 | 1.87 | 0.000229 | -0.00202 | 1.55 | 0.000172 | 0 | 1.87 | 0.000229 | -0.00202 |  | LF | None | 1550 | 0.172 | 1550 | 0.172 | 1.21 | 1.33 | -0.0013032 | 1550 | 0.172 | 1550 | 0.172 | 1.21 | 1.33 | -0.0013
LFNoneSCEMtlExCZ16 | Com-Iltg-dWatt-LF_OSnone | SCE | Mtl | Ex | CZ16 | 1.55 | 0.000172 | 0 | 1.49 | 0.000217 | -0.0114 | 1.55 | 0.000172 | 0 | 1.49 | 0.000217 | -0.0114 |  | LF | None | 1550 | 0.172 | 1550 | 0.172 | 0.961 | 1.26 | -0.0073548 | 1550 | 0.172 | 1550 | 0.172 | 0.961 | 1.26 | -0.00735
LFNoneSCEMtlExIOU | Com-Iltg-dWatt-LF_OSnone | SCE | Mtl | Ex | IOU | 1.55 | 0.000172 | 0 | 1.7709 | 0.00022268 | -0.0043865 | 1.55 | 0.000172 | 0 | 1.7709 | 0.00022268 | -0.0043865 |  | LF | None | 1550 | 0.172 | 1550 | 0.172 | 1.14 | 1.29 | -0.00283 | 1550 | 0.172 | 1550 | 0.172 | 1.14 | 1.29 | -0.00283
LFNoneSCEMtlNewCZ05 | Com-Iltg-dWatt-LF_OSnone | SCE | Mtl | New | CZ05 | 1.55 | 0.000172 | 0 | 1.53 | 0.000219 | -0.0121 | 1.55 | 0.000172 | 0 | 1.53 | 0.000219 | -0.0121 |  | LF | None | 1550 | 0.172 | 1550 | 0.172 | 0.987 | 1.27 | -0.0078065 | 1550 | 0.172 | 1550 | 0.172 | 0.987 | 1.27 | -0.00781
LFNoneSCEMtlNewCZ06 | Com-Iltg-dWatt-LF_OSnone | SCE | Mtl | New | CZ06 | 1.55 | 0.000172 | 0 | 1.72 | 0.000223 | -0.00663 | 1.55 | 0.000172 | 0 | 1.72 | 0.000223 | -0.00663 |  | LF | None | 1550 | 0.172 | 1550 | 0.172 | 1.11 | 1.3 | -0.0042774 | 1550 | 0.172 | 1550 | 0.172 | 1.11 | 1.3 | -0.00428
LFNoneSCEMtlNewCZ08 | Com-Iltg-dWatt-LF_OSnone | SCE | Mtl | New | CZ08 | 1.55 | 0.000172 | 0 | 1.75 | 0.000226 | -0.00549 | 1.55 | 0.000172 | 0 | 1.75 | 0.000226 | -0.00549 |  | LF | None | 1550 | 0.172 | 1550 | 0.172 | 1.13 | 1.31 | -0.0035419 | 1550 | 0.172 | 1550 | 0.172 | 1.13 | 1.31 | -0.00354
LFNoneSCEMtlNewCZ09 | Com-Iltg-dWatt-LF_OSnone | SCE | Mtl | New | CZ09 | 1.55 | 0.000172 | 0 | 1.74 | 0.00023 | -0.00548 | 1.55 | 0.000172 | 0 | 1.74 | 0.00023 | -0.00548 |  | LF | None | 1550 | 0.172 | 1550 | 0.172 | 1.12 | 1.34 | -0.0035355 | 1550 | 0.172 | 1550 | 0.172 | 1.12 | 1.34 | -0.00354
LFNoneSCEMtlNewCZ10 | Com-Iltg-dWatt-LF_OSnone | SCE | Mtl | New | CZ10 | 1.55 | 0.000172 | 0 | 1.71 | 0.000231 | -0.00672 | 1.55 | 0.000172 | 0 | 1.71 | 0.000231 | -0.00672 |  | LF | None | 1550 | 0.172 | 1550 | 0.172 | 1.1 | 1.34 | -0.0043355 | 1550 | 0.172 | 1550 | 0.172 | 1.1 | 1.34 | -0.00434
LFNoneSCEMtlNewCZ13 | Com-Iltg-dWatt-LF_OSnone | SCE | Mtl | New | CZ13 | 1.55 | 0.000172 | 0 | 1.66 | 0.000228 | -0.00852 | 1.55 | 0.000172 | 0 | 1.66 | 0.000228 | -0.00852 |  | LF | None | 1550 | 0.172 | 1550 | 0.172 | 1.07 | 1.33 | -0.0054968 | 1550 | 0.172 | 1550 | 0.172 | 1.07 | 1.33 | -0.0055
LFNoneSCEMtlNewCZ14 | Com-Iltg-dWatt-LF_OSnone | SCE | Mtl | New | CZ14 | 1.55 | 0.000172 | 0 | 1.64 | 0.00023 | -0.00875 | 1.55 | 0.000172 | 0 | 1.64 | 0.00023 | -0.00875 |  | LF | None | 1550 | 0.172 | 1550 | 0.172 | 1.06 | 1.34 | -0.0056452 | 1550 | 0.172 | 1550 | 0.172 | 1.06 | 1.34 | -0.00565
LFNoneSCEMtlNewCZ15 | Com-Iltg-dWatt-LF_OSnone | SCE | Mtl | New | CZ15 | 1.55 | 0.000172 | 0 | 1.85 | 0.000235 | -0.00315 | 1.55 | 0.000172 | 0 | 1.85 | 0.000235 | -0.00315 |  | LF | None | 1550 | 0.172 | 1550 | 0.172 | 1.19 | 1.37 | -0.0020323 | 1550 | 0.172 | 1550 | 0.172 | 1.19 | 1.37 | -0.00203
LFNoneSCEMtlNewCZ16 | Com-Iltg-dWatt-LF_OSnone | SCE | Mtl | New | CZ16 | 1.55 | 0.000172 | 0 | 1.44 | 0.000218 | -0.0136 | 1.55 | 0.000172 | 0 | 1.44 | 0.000218 | -0.0136 |  | LF | None | 1550 | 0.172 | 1550 | 0.172 | 0.929 | 1.27 | -0.0087742 | 1550 | 0.172 | 1550 | 0.172 | 0.929 | 1.27 | -0.00877
LFNoneSCEMtlNewIOU | Com-Iltg-dWatt-LF_OSnone | SCE | Mtl | New | IOU | 1.55 | 0.000172 | 0 | 1.7399 | 0.00022852 | -0.0059156 | 1.55 | 0.000172 | 0 | 1.7399 | 0.00022852 | -0.0059156 |  | LF | None | 1550 | 0.172 | 1550 | 0.172 | 1.12 | 1.33 | -0.0038165 | 1550 | 0.172 | 1550 | 0.172 | 1.12 | 1.33 | -0.00382
LFNoneSCENrsExCZ05 | Com-Iltg-dWatt-LF_OSnone | SCE | Nrs | Ex | CZ05 | 4.16 | 0.000676 | 0 | 4.22 | 0.000837 | -0.0657 | 4.16 | 0.000676 | 0 | 4.22 | 0.000837 | -0.0657 |  | LF | None | 4160 | 0.676 | 4160 | 0.676 | 1.01 | 1.24 | -0.015793 | 4160 | 0.676 | 4160 | 0.676 | 1.01 | 1.24 | -0.0158
LFNoneSCENrsExCZ06 | Com-Iltg-dWatt-LF_OSnone | SCE | Nrs | Ex | CZ06 | 4.16 | 0.000676 | 0 | 4.51 | 0.000882 | -0.0436 | 4.16 | 0.000676 | 0 | 4.51 | 0.000882 | -0.0436 |  | LF | None | 4160 | 0.676 | 4160 | 0.676 | 1.08 | 1.3 | -0.010481 | 4160 | 0.676 | 4160 | 0.676 | 1.08 | 1.3 | -0.0105
LFNoneSCENrsExCZ08 | Com-Iltg-dWatt-LF_OSnone | SCE | Nrs | Ex | CZ08 | 4.16 | 0.000676 | 0 | 4.55 | 0.000879 | -0.0424 | 4.16 | 0.000676 | 0 | 4.55 | 0.000879 | -0.0424 |  | LF | None | 4160 | 0.676 | 4160 | 0.676 | 1.09 | 1.3 | -0.010192 | 4160 | 0.676 | 4160 | 0.676 | 1.09 | 1.3 | -0.0102
LFNoneSCENrsExCZ09 | Com-Iltg-dWatt-LF_OSnone | SCE | Nrs | Ex | CZ09 | 4.16 | 0.000676 | 0 | 4.57 | 0.000911 | -0.0432 | 4.16 | 0.000676 | 0 | 4.57 | 0.000911 | -0.0432 |  | LF | None | 4160 | 0.676 | 4160 | 0.676 | 1.1 | 1.35 | -0.010385 | 4160 | 0.676 | 4160 | 0.676 | 1.1 | 1.35 | -0.0104
LFNoneSCENrsExCZ10 | Com-Iltg-dWatt-LF_OSnone | SCE | Nrs | Ex | CZ10 | 4.16 | 0.000676 | 0 | 4.51 | 0.000911 | -0.0432 | 4.16 | 0.000676 | 0 | 4.51 | 0.000911 | -0.0432 |  | LF | None | 4160 | 0.676 | 4160 | 0.676 | 1.08 | 1.35 | -0.010385 | 4160 | 0.676 | 4160 | 0.676 | 1.08 | 1.35 | -0.0104
LFNoneSCENrsExCZ13 | Com-Iltg-dWatt-LF_OSnone | SCE | Nrs | Ex | CZ13 | 4.16 | 0.000676 | 0 | 4.46 | 0.000899 | -0.0503 | 4.16 | 0.000676 | 0 | 4.46 | 0.000899 | -0.0503 |  | LF | None | 4160 | 0.676 | 4160 | 0.676 | 1.07 | 1.33 | -0.012091 | 4160 | 0.676 | 4160 | 0.676 | 1.07 | 1.33 | -0.0121
LFNoneSCENrsExCZ14 | Com-Iltg-dWatt-LF_OSnone | SCE | Nrs | Ex | CZ14 | 4.16 | 0.000676 | 0 | 4.48 | 0.000896 | -0.0515 | 4.16 | 0.000676 | 0 | 4.48 | 0.000896 | -0.0515 |  | LF | None | 4160 | 0.676 | 4160 | 0.676 | 1.08 | 1.33 | -0.01238 | 4160 | 0.676 | 4160 | 0.676 | 1.08 | 1.33 | -0.0124
LFNoneSCENrsExCZ15 | Com-Iltg-dWatt-LF_OSnone | SCE | Nrs | Ex | CZ15 | 4.16 | 0.000676 | 0 | 4.83 | 0.000917 | -0.0261 | 4.16 | 0.000676 | 0 | 4.83 | 0.000917 | -0.0261 |  | LF | None | 4160 | 0.676 | 4160 | 0.676 | 1.16 | 1.36 | -0.006274 | 4160 | 0.676 | 4160 | 0.676 | 1.16 | 1.36 | -0.00627
LFNoneSCENrsExCZ16 | Com-Iltg-dWatt-LF_OSnone | SCE | Nrs | Ex | CZ16 | 4.16 | 0.000676 | 0 | 4.12 | 0.000858 | -0.0744 | 4.16 | 0.000676 | 0 | 4.12 | 0.000858 | -0.0744 |  | LF | None | 4160 | 0.676 | 4160 | 0.676 | 0.99 | 1.27 | -0.017885 | 4160 | 0.676 | 4160 | 0.676 | 0.99 | 1.27 | -0.0179
LFNoneSCENrsExIOU | Com-Iltg-dWatt-LF_OSnone | SCE | Nrs | Ex | IOU | 4.16 | 0.000676 | 0 | 4.5252 | 0.00089053 | -0.044022 | 4.16 | 0.000676 | 0 | 4.5252 | 0.00089053 | -0.044022 |  | LF | None | 4160 | 0.676 | 4160 | 0.676 | 1.09 | 1.32 | -0.010582 | 4160 | 0.676 | 4160 | 0.676 | 1.09 | 1.32 | -0.0106
LFNoneSCENrsNewCZ05 | Com-Iltg-dWatt-LF_OSnone | SCE | Nrs | New | CZ05 | 4.16 | 0.000676 | 0 | 4.04 | 0.000825 | -0.0748 | 4.16 | 0.000676 | 0 | 4.04 | 0.000825 | -0.0748 |  | LF | None | 4160 | 0.676 | 4160 | 0.676 | 0.971 | 1.22 | -0.017981 | 4160 | 0.676 | 4160 | 0.676 | 0.971 | 1.22 | -0.018
LFNoneSCENrsNewCZ06 | Com-Iltg-dWatt-LF_OSnone | SCE | Nrs | New | CZ06 | 4.16 | 0.000676 | 0 | 4.29 | 0.000866 | -0.0478 | 4.16 | 0.000676 | 0 | 4.29 | 0.000866 | -0.0478 |  | LF | None | 4160 | 0.676 | 4160 | 0.676 | 1.03 | 1.28 | -0.01149 | 4160 | 0.676 | 4160 | 0.676 | 1.03 | 1.28 | -0.0115
LFNoneSCENrsNewCZ08 | Com-Iltg-dWatt-LF_OSnone | SCE | Nrs | New | CZ08 | 4.16 | 0.000676 | 0 | 4.38 | 0.000871 | -0.0449 | 4.16 | 0.000676 | 0 | 4.38 | 0.000871 | -0.0449 |  | LF | None | 4160 | 0.676 | 4160 | 0.676 | 1.05 | 1.29 | -0.010793 | 4160 | 0.676 | 4160 | 0.676 | 1.05 | 1.29 | -0.0108
LFNoneSCENrsNewCZ09 | Com-Iltg-dWatt-LF_OSnone | SCE | Nrs | New | CZ09 | 4.16 | 0.000676 | 0 | 4.41 | 0.000904 | -0.0457 | 4.16 | 0.000676 | 0 | 4.41 | 0.000904 | -0.0457 |  | LF | None | 4160 | 0.676 | 4160 | 0.676 | 1.06 | 1.34 | -0.010986 | 4160 | 0.676 | 4160 | 0.676 | 1.06 | 1.34 | -0.011
LFNoneSCENrsNewCZ10 | Com-Iltg-dWatt-LF_OSnone | SCE | Nrs | New | CZ10 | 4.16 | 0.000676 | 0 | 4.43 | 0.000907 | -0.0424 | 4.16 | 0.000676 | 0 | 4.43 | 0.000907 | -0.0424 |  | LF | None | 4160 | 0.676 | 4160 | 0.676 | 1.06 | 1.34 | -0.010192 | 4160 | 0.676 | 4160 | 0.676 | 1.06 | 1.34 | -0.0102
LFNoneSCENrsNewCZ13 | Com-Iltg-dWatt-LF_OSnone | SCE | Nrs | New | CZ13 | 4.16 | 0.000676 | 0 | 4.39 | 0.000898 | -0.0544 | 4.16 | 0.000676 | 0 | 4.39 | 0.000898 | -0.0544 |  | LF | None | 4160 | 0.676 | 4160 | 0.676 | 1.06 | 1.33 | -0.013077 | 4160 | 0.676 | 4160 | 0.676 | 1.06 | 1.33 | -0.0131
LFNoneSCENrsNewCZ14 | Com-Iltg-dWatt-LF_OSnone | SCE | Nrs | New | CZ14 | 4.16 | 0.000676 | 0 | 4.39 | 0.000879 | -0.0561 | 4.16 | 0.000676 | 0 | 4.39 | 0.000879 | -0.0561 |  | LF | None | 4160 | 0.676 | 4160 | 0.676 | 1.06 | 1.3 | -0.013486 | 4160 | 0.676 | 4160 | 0.676 | 1.06 | 1.3 | -0.0135
LFNoneSCENrsNewCZ15 | Com-Iltg-dWatt-LF_OSnone | SCE | Nrs | New | CZ15 | 4.16 | 0.000676 | 0 | 4.77 | 0.000902 | -0.0259 | 4.16 | 0.000676 | 0 | 4.77 | 0.000902 | -0.0259 |  | LF | None | 4160 | 0.676 | 4160 | 0.676 | 1.15 | 1.33 | -0.006226 | 4160 | 0.676 | 4160 | 0.676 | 1.15 | 1.33 | -0.00623
LFNoneSCENrsNewCZ16 | Com-Iltg-dWatt-LF_OSnone | SCE | Nrs | New | CZ16 | 4.16 | 0.000676 | 0 | 4.06 | 0.000849 | -0.0806 | 4.16 | 0.000676 | 0 | 4.06 | 0.000849 | -0.0806 |  | LF | None | 4160 | 0.676 | 4160 | 0.676 | 0.976 | 1.26 | -0.019375 | 4160 | 0.676 | 4160 | 0.676 | 0.976 | 1.26 | -0.0194
LFNoneSCENrsNewIOU | Com-Iltg-dWatt-LF_OSnone | SCE | Nrs | New | IOU | 4.16 | 0.000676 | 0 | 4.3843 | 0.00088525 | -0.046323 | 4.16 | 0.000676 | 0 | 4.3843 | 0.00088525 | -0.046323 |  | LF | None | 4160 | 0.676 | 4160 | 0.676 | 1.05 | 1.31 | -0.011135 | 4160 | 0.676 | 4160 | 0.676 | 1.05 | 1.31 | -0.0111
LFNoneSCEOfLExCZ05 | Com-Iltg-dWatt-LF_OSnone | SCE | OfL | Ex | CZ05 | 2.64 | 0.00071 | 0 | 2.96 | 0.000907 | -0.0182 | 2.64 | 0.00071 | 0 | 2.96 | 0.000907 | -0.0182 |  | LF | None | 2640 | 0.71 | 2640 | 0.71 | 1.12 | 1.28 | -0.0068939 | 2640 | 0.71 | 2640 | 0.71 | 1.12 | 1.28 | -0.00689
LFNoneSCEOfLExCZ06 | Com-Iltg-dWatt-LF_OSnone | SCE | OfL | Ex | CZ06 | 2.64 | 0.00071 | 0 | 3.09 | 0.000934 | -0.0118 | 2.64 | 0.00071 | 0 | 3.09 | 0.000934 | -0.0118 |  | LF | None | 2640 | 0.71 | 2640 | 0.71 | 1.17 | 1.32 | -0.0044697 | 2640 | 0.71 | 2640 | 0.71 | 1.17 | 1.32 | -0.00447
LFNoneSCEOfLExCZ08 | Com-Iltg-dWatt-LF_OSnone | SCE | OfL | Ex | CZ08 | 2.64 | 0.00071 | 0 | 3.11 | 0.000943 | -0.0117 | 2.64 | 0.00071 | 0 | 3.11 | 0.000943 | -0.0117 |  | LF | None | 2640 | 0.71 | 2640 | 0.71 | 1.18 | 1.33 | -0.0044318 | 2640 | 0.71 | 2640 | 0.71 | 1.18 | 1.33 | -0.00443
LFNoneSCEOfLExCZ09 | Com-Iltg-dWatt-LF_OSnone | SCE | OfL | Ex | CZ09 | 2.64 | 0.00071 | 0 | 3.09 | 0.000958 | -0.0137 | 2.64 | 0.00071 | 0 | 3.09 | 0.000958 | -0.0137 |  | LF | None | 2640 | 0.71 | 2640 | 0.71 | 1.17 | 1.35 | -0.0051894 | 2640 | 0.71 | 2640 | 0.71 | 1.17 | 1.35 | -0.00519
LFNoneSCEOfLExCZ10 | Com-Iltg-dWatt-LF_OSnone | SCE | OfL | Ex | CZ10 | 2.64 | 0.00071 | 0 | 3.08 | 0.000948 | -0.0112 | 2.64 | 0.00071 | 0 | 3.08 | 0.000948 | -0.0112 |  | LF | None | 2640 | 0.71 | 2640 | 0.71 | 1.17 | 1.34 | -0.0042424 | 2640 | 0.71 | 2640 | 0.71 | 1.17 | 1.34 | -0.00424
LFNoneSCEOfLExCZ13 | Com-Iltg-dWatt-LF_OSnone | SCE | OfL | Ex | CZ13 | 2.64 | 0.00071 | 0 | 3.06 | 0.000931 | -0.0159 | 2.64 | 0.00071 | 0 | 3.06 | 0.000931 | -0.0159 |  | LF | None | 2640 | 0.71 | 2640 | 0.71 | 1.16 | 1.31 | -0.0060227 | 2640 | 0.71 | 2640 | 0.71 | 1.16 | 1.31 | -0.00602
LFNoneSCEOfLExCZ14 | Com-Iltg-dWatt-LF_OSnone | SCE | OfL | Ex | CZ14 | 2.64 | 0.00071 | 0 | 3.05 | 0.000949 | -0.0146 | 2.64 | 0.00071 | 0 | 3.05 | 0.000949 | -0.0146 |  | LF | None | 2640 | 0.71 | 2640 | 0.71 | 1.16 | 1.34 | -0.0055303 | 2640 | 0.71 | 2640 | 0.71 | 1.16 | 1.34 | -0.00553
LFNoneSCEOfLExCZ15 | Com-Iltg-dWatt-LF_OSnone | SCE | OfL | Ex | CZ15 | 2.64 | 0.00071 | 0 | 3.24 | 0.000946 | -0.007 | 2.64 | 0.00071 | 0 | 3.24 | 0.000946 | -0.007 |  | LF | None | 2640 | 0.71 | 2640 | 0.71 | 1.23 | 1.33 | -0.0026515 | 2640 | 0.71 | 2640 | 0.71 | 1.23 | 1.33 | -0.00265
LFNoneSCEOfLExCZ16 | Com-Iltg-dWatt-LF_OSnone | SCE | OfL | Ex | CZ16 | 2.64 | 0.00071 | 0 | 2.84 | 0.000904 | -0.0267 | 2.64 | 0.00071 | 0 | 2.84 | 0.000904 | -0.0267 |  | LF | None | 2640 | 0.71 | 2640 | 0.71 | 1.08 | 1.27 | -0.010114 | 2640 | 0.71 | 2640 | 0.71 | 1.08 | 1.27 | -0.0101
LFNoneSCEOfLExIOU | Com-Iltg-dWatt-LF_OSnone | SCE | OfL | Ex | IOU | 2.64 | 0.00071 | 0 | 3.096 | 0.00094359 | -0.012254 | 2.64 | 0.00071 | 0 | 3.096 | 0.00094359 | -0.012254 |  | LF | None | 2640 | 0.71 | 2640 | 0.71 | 1.17 | 1.33 | -0.0046418 | 2640 | 0.71 | 2640 | 0.71 | 1.17 | 1.33 | -0.00464
LFNoneSCEOfLNewCZ05 | Com-Iltg-dWatt-LF_OSnone | SCE | OfL | New | CZ05 | 2.64 | 0.00071 | 0 | 2.97 | 0.000885 | -0.00821 | 2.64 | 0.00071 | 0 | 2.97 | 0.000885 | -0.00821 |  | LF | None | 2640 | 0.71 | 2640 | 0.71 | 1.12 | 1.25 | -0.0031098 | 2640 | 0.71 | 2640 | 0.71 | 1.12 | 1.25 | -0.00311
LFNoneSCEOfLNewCZ06 | Com-Iltg-dWatt-LF_OSnone | SCE | OfL | New | CZ06 | 2.64 | 0.00071 | 0 | 3.08 | 0.0009 | -0.00486 | 2.64 | 0.00071 | 0 | 3.08 | 0.0009 | -0.00486 |  | LF | None | 2640 | 0.71 | 2640 | 0.71 | 1.17 | 1.27 | -0.0018409 | 2640 | 0.71 | 2640 | 0.71 | 1.17 | 1.27 | -0.00184
LFNoneSCEOfLNewCZ08 | Com-Iltg-dWatt-LF_OSnone | SCE | OfL | New | CZ08 | 2.64 | 0.00071 | 0 | 3.09 | 0.000911 | -0.00444 | 2.64 | 0.00071 | 0 | 3.09 | 0.000911 | -0.00444 |  | LF | None | 2640 | 0.71 | 2640 | 0.71 | 1.17 | 1.28 | -0.0016818 | 2640 | 0.71 | 2640 | 0.71 | 1.17 | 1.28 | -0.00168
LFNoneSCEOfLNewCZ09 | Com-Iltg-dWatt-LF_OSnone | SCE | OfL | New | CZ09 | 2.64 | 0.00071 | 0 | 3.09 | 0.000934 | -0.00634 | 2.64 | 0.00071 | 0 | 3.09 | 0.000934 | -0.00634 |  | LF | None | 2640 | 0.71 | 2640 | 0.71 | 1.17 | 1.32 | -0.0024015 | 2640 | 0.71 | 2640 | 0.71 | 1.17 | 1.32 | -0.0024
LFNoneSCEOfLNewCZ10 | Com-Iltg-dWatt-LF_OSnone | SCE | OfL | New | CZ10 | 2.64 | 0.00071 | 0 | 3.11 | 0.000938 | -0.00499 | 2.64 | 0.00071 | 0 | 3.11 | 0.000938 | -0.00499 |  | LF | None | 2640 | 0.71 | 2640 | 0.71 | 1.18 | 1.32 | -0.0018902 | 2640 | 0.71 | 2640 | 0.71 | 1.18 | 1.32 | -0.00189
LFNoneSCEOfLNewCZ13 | Com-Iltg-dWatt-LF_OSnone | SCE | OfL | New | CZ13 | 2.64 | 0.00071 | 0 | 3.05 | 0.000921 | -0.0079 | 2.64 | 0.00071 | 0 | 3.05 | 0.000921 | -0.0079 |  | LF | None | 2640 | 0.71 | 2640 | 0.71 | 1.16 | 1.3 | -0.0029924 | 2640 | 0.71 | 2640 | 0.71 | 1.16 | 1.3 | -0.00299
LFNoneSCEOfLNewCZ14 | Com-Iltg-dWatt-LF_OSnone | SCE | OfL | New | CZ14 | 2.64 | 0.00071 | 0 | 3.07 | 0.000941 | -0.00605 | 2.64 | 0.00071 | 0 | 3.07 | 0.000941 | -0.00605 |  | LF | None | 2640 | 0.71 | 2640 | 0.71 | 1.16 | 1.33 | -0.0022917 | 2640 | 0.71 | 2640 | 0.71 | 1.16 | 1.33 | -0.00229
LFNoneSCEOfLNewCZ15 | Com-Iltg-dWatt-LF_OSnone | SCE | OfL | New | CZ15 | 2.64 | 0.00071 | 0 | 3.23 | 0.000937 | -0.00277 | 2.64 | 0.00071 | 0 | 3.23 | 0.000937 | -0.00277 |  | LF | None | 2640 | 0.71 | 2640 | 0.71 | 1.22 | 1.32 | -0.0010492 | 2640 | 0.71 | 2640 | 0.71 | 1.22 | 1.32 | -0.00105
LFNoneSCEOfLNewCZ16 | Com-Iltg-dWatt-LF_OSnone | SCE | OfL | New | CZ16 | 2.64 | 0.00071 | 0 | 2.88 | 0.000896 | -0.0181 | 2.64 | 0.00071 | 0 | 2.88 | 0.000896 | -0.0181 |  | LF | None | 2640 | 0.71 | 2640 | 0.71 | 1.09 | 1.26 | -0.0068561 | 2640 | 0.71 | 2640 | 0.71 | 1.09 | 1.26 | -0.00686
LFNoneSCEOfLNewIOU | Com-Iltg-dWatt-LF_OSnone | SCE | OfL | New | IOU | 2.64 | 0.00071 | 0 | 3.0945 | 0.00092164 | -0.0053131 | 2.64 | 0.00071 | 0 | 3.0945 | 0.00092164 | -0.0053131 |  | LF | None | 2640 | 0.71 | 2640 | 0.71 | 1.17 | 1.3 | -0.0020125 | 2640 | 0.71 | 2640 | 0.71 | 1.17 | 1.3 | -0.00201
LFNoneSCEOfSExCZ05 | Com-Iltg-dWatt-LF_OSnone | SCE | OfS | Ex | CZ05 | 2.59 | 0.000694 | 0 | 2.85 | 0.000868 | -0.00809 | 2.59 | 0.000694 | 0 | 2.85 | 0.000868 | -0.00809 |  | LF | None | 2590 | 0.694 | 2590 | 0.694 | 1.1 | 1.25 | -0.0031236 | 2590 | 0.694 | 2590 | 0.694 | 1.1 | 1.25 | -0.00312
LFNoneSCEOfSExCZ06 | Com-Iltg-dWatt-LF_OSnone | SCE | OfS | Ex | CZ06 | 2.59 | 0.000694 | 0 | 2.98 | 0.000879 | -0.00394 | 2.59 | 0.000694 | 0 | 2.98 | 0.000879 | -0.00394 |  | LF | None | 2590 | 0.694 | 2590 | 0.694 | 1.15 | 1.27 | -0.0015212 | 2590 | 0.694 | 2590 | 0.694 | 1.15 | 1.27 | -0.00152
LFNoneSCEOfSExCZ08 | Com-Iltg-dWatt-LF_OSnone | SCE | OfS | Ex | CZ08 | 2.59 | 0.000694 | 0 | 3 | 0.000886 | -0.00366 | 2.59 | 0.000694 | 0 | 3 | 0.000886 | -0.00366 |  | LF | None | 2590 | 0.694 | 2590 | 0.694 | 1.16 | 1.28 | -0.0014131 | 2590 | 0.694 | 2590 | 0.694 | 1.16 | 1.28 | -0.00141
LFNoneSCEOfSExCZ09 | Com-Iltg-dWatt-LF_OSnone | SCE | OfS | Ex | CZ09 | 2.59 | 0.000694 | 0 | 2.98 | 0.000895 | -0.00444 | 2.59 | 0.000694 | 0 | 2.98 | 0.000895 | -0.00444 |  | LF | None | 2590 | 0.694 | 2590 | 0.694 | 1.15 | 1.29 | -0.0017143 | 2590 | 0.694 | 2590 | 0.694 | 1.15 | 1.29 | -0.00171
LFNoneSCEOfSExCZ10 | Com-Iltg-dWatt-LF_OSnone | SCE | OfS | Ex | CZ10 | 2.59 | 0.000694 | 0 | 2.94 | 0.000886 | -0.00412 | 2.59 | 0.000694 | 0 | 2.94 | 0.000886 | -0.00412 |  | LF | None | 2590 | 0.694 | 2590 | 0.694 | 1.14 | 1.28 | -0.0015907 | 2590 | 0.694 | 2590 | 0.694 | 1.14 | 1.28 | -0.00159
LFNoneSCEOfSExCZ13 | Com-Iltg-dWatt-LF_OSnone | SCE | OfS | Ex | CZ13 | 2.59 | 0.000694 | 0 | 2.88 | 0.00088 | -0.00999 | 2.59 | 0.000694 | 0 | 2.88 | 0.00088 | -0.00999 |  | LF | None | 2590 | 0.694 | 2590 | 0.694 | 1.11 | 1.27 | -0.0038571 | 2590 | 0.694 | 2590 | 0.694 | 1.11 | 1.27 | -0.00386
LFNoneSCEOfSExCZ14 | Com-Iltg-dWatt-LF_OSnone | SCE | OfS | Ex | CZ14 | 2.59 | 0.000694 | 0 | 2.89 | 0.000897 | -0.00768 | 2.59 | 0.000694 | 0 | 2.89 | 0.000897 | -0.00768 |  | LF | None | 2590 | 0.694 | 2590 | 0.694 | 1.12 | 1.29 | -0.0029653 | 2590 | 0.694 | 2590 | 0.694 | 1.12 | 1.29 | -0.00297
LFNoneSCEOfSExCZ15 | Com-Iltg-dWatt-LF_OSnone | SCE | OfS | Ex | CZ15 | 2.59 | 0.000694 | 0 | 3.13 | 0.000884 | -0.00126 | 2.59 | 0.000694 | 0 | 3.13 | 0.000884 | -0.00126 |  | LF | None | 2590 | 0.694 | 2590 | 0.694 | 1.21 | 1.27 | -0.00048649 | 2590 | 0.694 | 2590 | 0.694 | 1.21 | 1.27 | -0.000486
LFNoneSCEOfSExCZ16 | Com-Iltg-dWatt-LF_OSnone | SCE | OfS | Ex | CZ16 | 2.59 | 0.000694 | 0 | 2.61 | 0.000862 | -0.0189 | 2.59 | 0.000694 | 0 | 2.61 | 0.000862 | -0.0189 |  | LF | None | 2590 | 0.694 | 2590 | 0.694 | 1.01 | 1.24 | -0.0072973 | 2590 | 0.694 | 2590 | 0.694 | 1.01 | 1.24 | -0.0073
LFNoneSCEOfSExIOU | Com-Iltg-dWatt-LF_OSnone | SCE | OfS | Ex | IOU | 2.59 | 0.000694 | 0 | 2.9716 | 0.00088519 | -0.0044831 | 2.59 | 0.000694 | 0 | 2.9716 | 0.00088519 | -0.0044831 |  | LF | None | 2590 | 0.694 | 2590 | 0.694 | 1.15 | 1.28 | -0.0017309 | 2590 | 0.694 | 2590 | 0.694 | 1.15 | 1.28 | -0.00173
LFNoneSCEOfSNewCZ05 | Com-Iltg-dWatt-LF_OSnone | SCE | OfS | New | CZ05 | 2.59 | 0.000694 | 0 | 2.74 | 0.000857 | -0.00661 | 2.59 | 0.000694 | 0 | 2.74 | 0.000857 | -0.00661 |  | LF | None | 2590 | 0.694 | 2590 | 0.694 | 1.06 | 1.23 | -0.0025521 | 2590 | 0.694 | 2590 | 0.694 | 1.06 | 1.23 | -0.00255
LFNoneSCEOfSNewCZ06 | Com-Iltg-dWatt-LF_OSnone | SCE | OfS | New | CZ06 | 2.59 | 0.000694 | 0 | 2.89 | 0.000865 | -0.00265 | 2.59 | 0.000694 | 0 | 2.89 | 0.000865 | -0.00265 |  | LF | None | 2590 | 0.694 | 2590 | 0.694 | 1.12 | 1.25 | -0.0010232 | 2590 | 0.694 | 2590 | 0.694 | 1.12 | 1.25 | -0.00102
LFNoneSCEOfSNewCZ08 | Com-Iltg-dWatt-LF_OSnone | SCE | OfS | New | CZ08 | 2.59 | 0.000694 | 0 | 2.91 | 0.000879 | -0.00238 | 2.59 | 0.000694 | 0 | 2.91 | 0.000879 | -0.00238 |  | LF | None | 2590 | 0.694 | 2590 | 0.694 | 1.12 | 1.27 | -0.00091892 | 2590 | 0.694 | 2590 | 0.694 | 1.12 | 1.27 | -0.000919
LFNoneSCEOfSNewCZ09 | Com-Iltg-dWatt-LF_OSnone | SCE | OfS | New | CZ09 | 2.59 | 0.000694 | 0 | 2.91 | 0.000901 | -0.00262 | 2.59 | 0.000694 | 0 | 2.91 | 0.000901 | -0.00262 |  | LF | None | 2590 | 0.694 | 2590 | 0.694 | 1.12 | 1.3 | -0.0010116 | 2590 | 0.694 | 2590 | 0.694 | 1.12 | 1.3 | -0.00101
LFNoneSCEOfSNewCZ10 | Com-Iltg-dWatt-LF_OSnone | SCE | OfS | New | CZ10 | 2.59 | 0.000694 | 0 | 2.94 | 0.000911 | -0.00189 | 2.59 | 0.000694 | 0 | 2.94 | 0.000911 | -0.00189 |  | LF | None | 2590 | 0.694 | 2590 | 0.694 | 1.14 | 1.31 | -0.00072973 | 2590 | 0.694 | 2590 | 0.694 | 1.14 | 1.31 | -0.00073
LFNoneSCEOfSNewCZ13 | Com-Iltg-dWatt-LF_OSnone | SCE | OfS | New | CZ13 | 2.59 | 0.000694 | 0 | 2.86 | 0.000897 | -0.00739 | 2.59 | 0.000694 | 0 | 2.86 | 0.000897 | -0.00739 |  | LF | None | 2590 | 0.694 | 2590 | 0.694 | 1.1 | 1.29 | -0.0028533 | 2590 | 0.694 | 2590 | 0.694 | 1.1 | 1.29 | -0.00285
LFNoneSCEOfSNewCZ14 | Com-Iltg-dWatt-LF_OSnone | SCE | OfS | New | CZ14 | 2.59 | 0.000694 | 0 | 2.87 | 0.000909 | -0.00591 | 2.59 | 0.000694 | 0 | 2.87 | 0.000909 | -0.00591 |  | LF | None | 2590 | 0.694 | 2590 | 0.694 | 1.11 | 1.31 | -0.0022819 | 2590 | 0.694 | 2590 | 0.694 | 1.11 | 1.31 | -0.00228
LFNoneSCEOfSNewCZ15 | Com-Iltg-dWatt-LF_OSnone | SCE | OfS | New | CZ15 | 2.59 | 0.000694 | 0 | 3.08 | 0.00092 | -0.00017 | 2.59 | 0.000694 | 0 | 3.08 | 0.00092 | -0.00017 |  | LF | None | 2590 | 0.694 | 2590 | 0.694 | 1.19 | 1.33 | -6.5637e-05 | 2590 | 0.694 | 2590 | 0.694 | 1.19 | 1.33 | -6.56e-05
LFNoneSCEOfSNewCZ16 | Com-Iltg-dWatt-LF_OSnone | SCE | OfS | New | CZ16 | 2.59 | 0.000694 | 0 | 2.62 | 0.000865 | -0.0171 | 2.59 | 0.000694 | 0 | 2.62 | 0.000865 | -0.0171 |  | LF | None | 2590 | 0.694 | 2590 | 0.694 | 1.01 | 1.25 | -0.0066023 | 2590 | 0.694 | 2590 | 0.694 | 1.01 | 1.25 | -0.0066
LFNoneSCEOfSNewIOU | Com-Iltg-dWatt-LF_OSnone | SCE | OfS | New | IOU | 2.59 | 0.000694 | 0 | 2.9188 | 0.00089293 | -0.0027739 | 2.59 | 0.000694 | 0 | 2.9188 | 0.00089293 | -0.0027739 |  | LF | None | 2590 | 0.694 | 2590 | 0.694 | 1.13 | 1.29 | -0.001071 | 2590 | 0.694 | 2590 | 0.694 | 1.13 | 1.29 | -0.00107
LFNoneSCERFFExCZ05 | Com-Iltg-dWatt-LF_OSnone | SCE | RFF | Ex | CZ05 | 4.84 | 0.000813 | 0 | 5.03 | 0.000974 | -0.0499 | 4.84 | 0.000813 | 0 | 5.03 | 0.000974 | -0.0499 |  | LF | None | 4840 | 0.813 | 4840 | 0.813 | 1.04 | 1.2 | -0.01031 | 4840 | 0.813 | 4840 | 0.813 | 1.04 | 1.2 | -0.0103
LFNoneSCERFFExCZ06 | Com-Iltg-dWatt-LF_OSnone | SCE | RFF | Ex | CZ06 | 4.84 | 0.000813 | 0 | 5.29 | 0.000994 | -0.0272 | 4.84 | 0.000813 | 0 | 5.29 | 0.000994 | -0.0272 |  | LF | None | 4840 | 0.813 | 4840 | 0.813 | 1.09 | 1.22 | -0.0056198 | 4840 | 0.813 | 4840 | 0.813 | 1.09 | 1.22 | -0.00562
LFNoneSCERFFExCZ08 | Com-Iltg-dWatt-LF_OSnone | SCE | RFF | Ex | CZ08 | 4.84 | 0.000813 | 0 | 5.35 | 0.000986 | -0.0241 | 4.84 | 0.000813 | 0 | 5.35 | 0.000986 | -0.0241 |  | LF | None | 4840 | 0.813 | 4840 | 0.813 | 1.11 | 1.21 | -0.0049793 | 4840 | 0.813 | 4840 | 0.813 | 1.11 | 1.21 | -0.00498
LFNoneSCERFFExCZ09 | Com-Iltg-dWatt-LF_OSnone | SCE | RFF | Ex | CZ09 | 4.84 | 0.000813 | 0 | 5.36 | 0.00101 | -0.025 | 4.84 | 0.000813 | 0 | 5.36 | 0.00101 | -0.025 |  | LF | None | 4840 | 0.813 | 4840 | 0.813 | 1.11 | 1.24 | -0.0051653 | 4840 | 0.813 | 4840 | 0.813 | 1.11 | 1.24 | -0.00517
LFNoneSCERFFExCZ10 | Com-Iltg-dWatt-LF_OSnone | SCE | RFF | Ex | CZ10 | 4.84 | 0.000813 | 0 | 5.25 | 0.000991 | -0.0278 | 4.84 | 0.000813 | 0 | 5.25 | 0.000991 | -0.0278 |  | LF | None | 4840 | 0.813 | 4840 | 0.813 | 1.08 | 1.22 | -0.0057438 | 4840 | 0.813 | 4840 | 0.813 | 1.08 | 1.22 | -0.00574
LFNoneSCERFFExCZ13 | Com-Iltg-dWatt-LF_OSnone | SCE | RFF | Ex | CZ13 | 4.84 | 0.000813 | 0 | 5.24 | 0.000998 | -0.0372 | 4.84 | 0.000813 | 0 | 5.24 | 0.000998 | -0.0372 |  | LF | None | 4840 | 0.813 | 4840 | 0.813 | 1.08 | 1.23 | -0.007686 | 4840 | 0.813 | 4840 | 0.813 | 1.08 | 1.23 | -0.00769
LFNoneSCERFFExCZ14 | Com-Iltg-dWatt-LF_OSnone | SCE | RFF | Ex | CZ14 | 4.84 | 0.000813 | 0 | 5.2 | 0.00101 | -0.0392 | 4.84 | 0.000813 | 0 | 5.2 | 0.00101 | -0.0392 |  | LF | None | 4840 | 0.813 | 4840 | 0.813 | 1.07 | 1.24 | -0.0080992 | 4840 | 0.813 | 4840 | 0.813 | 1.07 | 1.24 | -0.0081
LFNoneSCERFFExCZ15 | Com-Iltg-dWatt-LF_OSnone | SCE | RFF | Ex | CZ15 | 4.84 | 0.000813 | 0 | 5.59 | 0.001 | -0.0128 | 4.84 | 0.000813 | 0 | 5.59 | 0.001 | -0.0128 |  | LF | None | 4840 | 0.813 | 4840 | 0.813 | 1.15 | 1.23 | -0.0026446 | 4840 | 0.813 | 4840 | 0.813 | 1.15 | 1.23 | -0.00264
LFNoneSCERFFExCZ16 | Com-Iltg-dWatt-LF_OSnone | SCE | RFF | Ex | CZ16 | 4.84 | 0.000813 | 0 | 4.84 | 0.000974 | -0.0711 | 4.84 | 0.000813 | 0 | 4.84 | 0.000974 | -0.0711 |  | LF | None | 4840 | 0.813 | 4840 | 0.813 | 1 | 1.2 | -0.01469 | 4840 | 0.813 | 4840 | 0.813 | 1 | 1.2 | -0.0147
LFNoneSCERFFExIOU | Com-Iltg-dWatt-LF_OSnone | SCE | RFF | Ex | IOU | 4.84 | 0.000813 | 0 | 5.306 | 0.00099423 | -0.027193 | 4.84 | 0.000813 | 0 | 5.306 | 0.00099423 | -0.027193 |  | LF | None | 4840 | 0.813 | 4840 | 0.813 | 1.1 | 1.22 | -0.0056185 | 4840 | 0.813 | 4840 | 0.813 | 1.1 | 1.22 | -0.00562
LFNoneSCERFFNewCZ05 | Com-Iltg-dWatt-LF_OSnone | SCE | RFF | New | CZ05 | 4.84 | 0.000813 | 0 | 4.98 | 0.000992 | -0.0489 | 4.84 | 0.000813 | 0 | 4.98 | 0.000992 | -0.0489 |  | LF | None | 4840 | 0.813 | 4840 | 0.813 | 1.03 | 1.22 | -0.010103 | 4840 | 0.813 | 4840 | 0.813 | 1.03 | 1.22 | -0.0101
LFNoneSCERFFNewCZ06 | Com-Iltg-dWatt-LF_OSnone | SCE | RFF | New | CZ06 | 4.84 | 0.000813 | 0 | 5.23 | 0.00102 | -0.0265 | 4.84 | 0.000813 | 0 | 5.23 | 0.00102 | -0.0265 |  | LF | None | 4840 | 0.813 | 4840 | 0.813 | 1.08 | 1.25 | -0.0054752 | 4840 | 0.813 | 4840 | 0.813 | 1.08 | 1.25 | -0.00548
LFNoneSCERFFNewCZ08 | Com-Iltg-dWatt-LF_OSnone | SCE | RFF | New | CZ08 | 4.84 | 0.000813 | 0 | 5.31 | 0.00103 | -0.0288 | 4.84 | 0.000813 | 0 | 5.31 | 0.00103 | -0.0288 |  | LF | None | 4840 | 0.813 | 4840 | 0.813 | 1.1 | 1.27 | -0.0059504 | 4840 | 0.813 | 4840 | 0.813 | 1.1 | 1.27 | -0.00595
LFNoneSCERFFNewCZ09 | Com-Iltg-dWatt-LF_OSnone | SCE | RFF | New | CZ09 | 4.84 | 0.000813 | 0 | 5.34 | 0.00106 | -0.0311 | 4.84 | 0.000813 | 0 | 5.34 | 0.00106 | -0.0311 |  | LF | None | 4840 | 0.813 | 4840 | 0.813 | 1.1 | 1.3 | -0.0064256 | 4840 | 0.813 | 4840 | 0.813 | 1.1 | 1.3 | -0.00643
LFNoneSCERFFNewCZ10 | Com-Iltg-dWatt-LF_OSnone | SCE | RFF | New | CZ10 | 4.84 | 0.000813 | 0 | 5.37 | 0.00107 | -0.0319 | 4.84 | 0.000813 | 0 | 5.37 | 0.00107 | -0.0319 |  | LF | None | 4840 | 0.813 | 4840 | 0.813 | 1.11 | 1.32 | -0.0065909 | 4840 | 0.813 | 4840 | 0.813 | 1.11 | 1.32 | -0.00659
LFNoneSCERFFNewCZ13 | Com-Iltg-dWatt-LF_OSnone | SCE | RFF | New | CZ13 | 4.84 | 0.000813 | 0 | 5.35 | 0.00106 | -0.0429 | 4.84 | 0.000813 | 0 | 5.35 | 0.00106 | -0.0429 |  | LF | None | 4840 | 0.813 | 4840 | 0.813 | 1.11 | 1.3 | -0.0088636 | 4840 | 0.813 | 4840 | 0.813 | 1.11 | 1.3 | -0.00886
LFNoneSCERFFNewCZ14 | Com-Iltg-dWatt-LF_OSnone | SCE | RFF | New | CZ14 | 4.84 | 0.000813 | 0 | 5.34 | 0.00107 | -0.0452 | 4.84 | 0.000813 | 0 | 5.34 | 0.00107 | -0.0452 |  | LF | None | 4840 | 0.813 | 4840 | 0.813 | 1.1 | 1.32 | -0.0093388 | 4840 | 0.813 | 4840 | 0.813 | 1.1 | 1.32 | -0.00934
LFNoneSCERFFNewCZ15 | Com-Iltg-dWatt-LF_OSnone | SCE | RFF | New | CZ15 | 4.84 | 0.000813 | 0 | 5.75 | 0.00109 | -0.0157 | 4.84 | 0.000813 | 0 | 5.75 | 0.00109 | -0.0157 |  | LF | None | 4840 | 0.813 | 4840 | 0.813 | 1.19 | 1.34 | -0.0032438 | 4840 | 0.813 | 4840 | 0.813 | 1.19 | 1.34 | -0.00324
LFNoneSCERFFNewCZ16 | Com-Iltg-dWatt-LF_OSnone | SCE | RFF | New | CZ16 | 4.84 | 0.000813 | 0 | 4.91 | 0.00102 | -0.0765 | 4.84 | 0.000813 | 0 | 4.91 | 0.00102 | -0.0765 |  | LF | None | 4840 | 0.813 | 4840 | 0.813 | 1.01 | 1.25 | -0.015806 | 4840 | 0.813 | 4840 | 0.813 | 1.01 | 1.25 | -0.0158
LFNoneSCERFFNewIOU | Com-Iltg-dWatt-LF_OSnone | SCE | RFF | New | IOU | 4.84 | 0.000813 | 0 | 5.3305 | 0.0010483 | -0.030918 | 4.84 | 0.000813 | 0 | 5.3305 | 0.0010483 | -0.030918 |  | LF | None | 4840 | 0.813 | 4840 | 0.813 | 1.1 | 1.29 | -0.006388 | 4840 | 0.813 | 4840 | 0.813 | 1.1 | 1.29 | -0.00639
LFNoneSCERSDExCZ05 | Com-Iltg-dWatt-LF_OSnone | SCE | RSD | Ex | CZ05 | 4.83 | 0.0008 | 0 | 5 | 0.000985 | -0.057 | 4.83 | 0.0008 | 0 | 5 | 0.000985 | -0.057 |  | LF | None | 4830 | 0.8 | 4830 | 0.8 | 1.04 | 1.23 | -0.011801 | 4830 | 0.8 | 4830 | 0.8 | 1.04 | 1.23 | -0.0118
LFNoneSCERSDExCZ06 | Com-Iltg-dWatt-LF_OSnone | SCE | RSD | Ex | CZ06 | 4.83 | 0.0008 | 0 | 5.35 | 0.000994 | -0.0296 | 4.83 | 0.0008 | 0 | 5.35 | 0.000994 | -0.0296 |  | LF | None | 4830 | 0.8 | 4830 | 0.8 | 1.11 | 1.24 | -0.0061284 | 4830 | 0.8 | 4830 | 0.8 | 1.11 | 1.24 | -0.00613
LFNoneSCERSDExCZ08 | Com-Iltg-dWatt-LF_OSnone | SCE | RSD | Ex | CZ08 | 4.83 | 0.0008 | 0 | 5.39 | 0.000964 | -0.0244 | 4.83 | 0.0008 | 0 | 5.39 | 0.000964 | -0.0244 |  | LF | None | 4830 | 0.8 | 4830 | 0.8 | 1.12 | 1.21 | -0.0050518 | 4830 | 0.8 | 4830 | 0.8 | 1.12 | 1.21 | -0.00505
LFNoneSCERSDExCZ09 | Com-Iltg-dWatt-LF_OSnone | SCE | RSD | Ex | CZ09 | 4.83 | 0.0008 | 0 | 5.37 | 0.000971 | -0.0276 | 4.83 | 0.0008 | 0 | 5.37 | 0.000971 | -0.0276 |  | LF | None | 4830 | 0.8 | 4830 | 0.8 | 1.11 | 1.21 | -0.0057143 | 4830 | 0.8 | 4830 | 0.8 | 1.11 | 1.21 | -0.00571
LFNoneSCERSDExCZ10 | Com-Iltg-dWatt-LF_OSnone | SCE | RSD | Ex | CZ10 | 4.83 | 0.0008 | 0 | 5.29 | 0.000922 | -0.029 | 4.83 | 0.0008 | 0 | 5.29 | 0.000922 | -0.029 |  | LF | None | 4830 | 0.8 | 4830 | 0.8 | 1.1 | 1.15 | -0.0060041 | 4830 | 0.8 | 4830 | 0.8 | 1.1 | 1.15 | -0.006
LFNoneSCERSDExCZ13 | Com-Iltg-dWatt-LF_OSnone | SCE | RSD | Ex | CZ13 | 4.83 | 0.0008 | 0 | 5.22 | 0.000996 | -0.0442 | 4.83 | 0.0008 | 0 | 5.22 | 0.000996 | -0.0442 |  | LF | None | 4830 | 0.8 | 4830 | 0.8 | 1.08 | 1.25 | -0.0091511 | 4830 | 0.8 | 4830 | 0.8 | 1.08 | 1.25 | -0.00915
LFNoneSCERSDExCZ14 | Com-Iltg-dWatt-LF_OSnone | SCE | RSD | Ex | CZ14 | 4.83 | 0.0008 | 0 | 5.17 | 0.000926 | -0.0472 | 4.83 | 0.0008 | 0 | 5.17 | 0.000926 | -0.0472 |  | LF | None | 4830 | 0.8 | 4830 | 0.8 | 1.07 | 1.16 | -0.0097723 | 4830 | 0.8 | 4830 | 0.8 | 1.07 | 1.16 | -0.00977
LFNoneSCERSDExCZ15 | Com-Iltg-dWatt-LF_OSnone | SCE | RSD | Ex | CZ15 | 4.83 | 0.0008 | 0 | 5.66 | 0.00101 | -0.0116 | 4.83 | 0.0008 | 0 | 5.66 | 0.00101 | -0.0116 |  | LF | None | 4830 | 0.8 | 4830 | 0.8 | 1.17 | 1.26 | -0.0024017 | 4830 | 0.8 | 4830 | 0.8 | 1.17 | 1.26 | -0.0024
LFNoneSCERSDExCZ16 | Com-Iltg-dWatt-LF_OSnone | SCE | RSD | Ex | CZ16 | 4.83 | 0.0008 | 0 | 4.79 | 0.000946 | -0.0778 | 4.83 | 0.0008 | 0 | 4.79 | 0.000946 | -0.0778 |  | LF | None | 4830 | 0.8 | 4830 | 0.8 | 0.992 | 1.18 | -0.016108 | 4830 | 0.8 | 4830 | 0.8 | 0.992 | 1.18 | -0.0161
LFNoneSCERSDExIOU | Com-Iltg-dWatt-LF_OSnone | SCE | RSD | Ex | IOU | 4.83 | 0.0008 | 0 | 5.3412 | 0.00096291 | -0.029082 | 4.83 | 0.0008 | 0 | 5.3412 | 0.00096291 | -0.029082 |  | LF | None | 4830 | 0.8 | 4830 | 0.8 | 1.11 | 1.2 | -0.0060211 | 4830 | 0.8 | 4830 | 0.8 | 1.11 | 1.2 | -0.00602
LFNoneSCERSDNewCZ05 | Com-Iltg-dWatt-LF_OSnone | SCE | RSD | New | CZ05 | 4.83 | 0.0008 | 0 | 4.95 | 0.000998 | -0.0642 | 4.83 | 0.0008 | 0 | 4.95 | 0.000998 | -0.0642 |  | LF | None | 4830 | 0.8 | 4830 | 0.8 | 1.02 | 1.25 | -0.013292 | 4830 | 0.8 | 4830 | 0.8 | 1.02 | 1.25 | -0.0133
LFNoneSCERSDNewCZ06 | Com-Iltg-dWatt-LF_OSnone | SCE | RSD | New | CZ06 | 4.83 | 0.0008 | 0 | 5.27 | 0.00101 | -0.0357 | 4.83 | 0.0008 | 0 | 5.27 | 0.00101 | -0.0357 |  | LF | None | 4830 | 0.8 | 4830 | 0.8 | 1.09 | 1.26 | -0.0073913 | 4830 | 0.8 | 4830 | 0.8 | 1.09 | 1.26 | -0.00739
LFNoneSCERSDNewCZ08 | Com-Iltg-dWatt-LF_OSnone | SCE | RSD | New | CZ08 | 4.83 | 0.0008 | 0 | 5.34 | 0.00102 | -0.0293 | 4.83 | 0.0008 | 0 | 5.34 | 0.00102 | -0.0293 |  | LF | None | 4830 | 0.8 | 4830 | 0.8 | 1.11 | 1.27 | -0.0060663 | 4830 | 0.8 | 4830 | 0.8 | 1.11 | 1.27 | -0.00607
LFNoneSCERSDNewCZ09 | Com-Iltg-dWatt-LF_OSnone | SCE | RSD | New | CZ09 | 4.83 | 0.0008 | 0 | 5.37 | 0.00106 | -0.0312 | 4.83 | 0.0008 | 0 | 5.37 | 0.00106 | -0.0312 |  | LF | None | 4830 | 0.8 | 4830 | 0.8 | 1.11 | 1.33 | -0.0064596 | 4830 | 0.8 | 4830 | 0.8 | 1.11 | 1.33 | -0.00646
LFNoneSCERSDNewCZ10 | Com-Iltg-dWatt-LF_OSnone | SCE | RSD | New | CZ10 | 4.83 | 0.0008 | 0 | 5.39 | 0.00106 | -0.0319 | 4.83 | 0.0008 | 0 | 5.39 | 0.00106 | -0.0319 |  | LF | None | 4830 | 0.8 | 4830 | 0.8 | 1.12 | 1.33 | -0.0066046 | 4830 | 0.8 | 4830 | 0.8 | 1.12 | 1.33 | -0.0066
LFNoneSCERSDNewCZ13 | Com-Iltg-dWatt-LF_OSnone | SCE | RSD | New | CZ13 | 4.83 | 0.0008 | 0 | 5.31 | 0.00108 | -0.0493 | 4.83 | 0.0008 | 0 | 5.31 | 0.00108 | -0.0493 |  | LF | None | 4830 | 0.8 | 4830 | 0.8 | 1.1 | 1.35 | -0.010207 | 4830 | 0.8 | 4830 | 0.8 | 1.1 | 1.35 | -0.0102
LFNoneSCERSDNewCZ14 | Com-Iltg-dWatt-LF_OSnone | SCE | RSD | New | CZ14 | 4.83 | 0.0008 | 0 | 5.28 | 0.00106 | -0.0512 | 4.83 | 0.0008 | 0 | 5.28 | 0.00106 | -0.0512 |  | LF | None | 4830 | 0.8 | 4830 | 0.8 | 1.09 | 1.33 | -0.0106 | 4830 | 0.8 | 4830 | 0.8 | 1.09 | 1.33 | -0.0106
LFNoneSCERSDNewCZ15 | Com-Iltg-dWatt-LF_OSnone | SCE | RSD | New | CZ15 | 4.83 | 0.0008 | 0 | 5.8 | 0.0011 | -0.0143 | 4.83 | 0.0008 | 0 | 5.8 | 0.0011 | -0.0143 |  | LF | None | 4830 | 0.8 | 4830 | 0.8 | 1.2 | 1.38 | -0.0029607 | 4830 | 0.8 | 4830 | 0.8 | 1.2 | 1.38 | -0.00296
LFNoneSCERSDNewCZ16 | Com-Iltg-dWatt-LF_OSnone | SCE | RSD | New | CZ16 | 4.83 | 0.0008 | 0 | 4.84 | 0.001 | -0.0609 | 4.83 | 0.0008 | 0 | 4.84 | 0.001 | -0.0609 |  | LF | None | 4830 | 0.8 | 4830 | 0.8 | 1 | 1.25 | -0.012609 | 4830 | 0.8 | 4830 | 0.8 | 1 | 1.25 | -0.0126
LFNoneSCERSDNewIOU | Com-Iltg-dWatt-LF_OSnone | SCE | RSD | New | IOU | 4.83 | 0.0008 | 0 | 5.3525 | 0.001041 | -0.033094 | 4.83 | 0.0008 | 0 | 5.3525 | 0.001041 | -0.033094 |  | LF | None | 4830 | 0.8 | 4830 | 0.8 | 1.11 | 1.3 | -0.0068517 | 4830 | 0.8 | 4830 | 0.8 | 1.11 | 1.3 | -0.00685
LFNoneSCERt3ExCZ05 | Com-Iltg-dWatt-LF_OSnone | SCE | Rt3 | Ex | CZ05 | 3.38 | 0.00075932 | 0 | 3.7 | 0.00092165 | -0.0141 | 3.38 | 0.00075932 | 0 | 3.7 | 0.00092165 | -0.0141 |  | LF | None | 3380 | 0.759 | 3380 | 0.759 | 1.09 | 1.21 | -0.0041716 | 3380 | 0.759 | 3380 | 0.759 | 1.09 | 1.21 | -0.00417
LFNoneSCERt3ExCZ06 | Com-Iltg-dWatt-LF_OSnone | SCE | Rt3 | Ex | CZ06 | 3.38 | 0.00075932 | 0 | 3.93 | 0.00093233 | -0.00337 | 3.38 | 0.00075932 | 0 | 3.93 | 0.00093233 | -0.00337 |  | LF | None | 3380 | 0.759 | 3380 | 0.759 | 1.16 | 1.23 | -0.00099704 | 3380 | 0.759 | 3380 | 0.759 | 1.16 | 1.23 | -0.000997
LFNoneSCERt3ExCZ08 | Com-Iltg-dWatt-LF_OSnone | SCE | Rt3 | Ex | CZ08 | 3.38 | 0.00075933 | 0 | 3.93 | 0.00092333 | -0.00304 | 3.38 | 0.00075933 | 0 | 3.93 | 0.00092333 | -0.00304 |  | LF | None | 3380 | 0.759 | 3380 | 0.759 | 1.16 | 1.22 | -0.00089941 | 3380 | 0.759 | 3380 | 0.759 | 1.16 | 1.22 | -0.000899
LFNoneSCERt3ExCZ09 | Com-Iltg-dWatt-LF_OSnone | SCE | Rt3 | Ex | CZ09 | 3.38 | 0.00075933 | 0 | 3.89 | 0.00093633 | -0.00473 | 3.38 | 0.00075933 | 0 | 3.89 | 0.00093633 | -0.00473 |  | LF | None | 3380 | 0.759 | 3380 | 0.759 | 1.15 | 1.23 | -0.0013994 | 3380 | 0.759 | 3380 | 0.759 | 1.15 | 1.23 | -0.0014
LFNoneSCERt3ExCZ10 | Com-Iltg-dWatt-LF_OSnone | SCE | Rt3 | Ex | CZ10 | 3.38 | 0.00075952 | 0 | 3.8 | 0.00092452 | -0.0054 | 3.38 | 0.00075952 | 0 | 3.8 | 0.00092452 | -0.0054 |  | LF | None | 3380 | 0.76 | 3380 | 0.76 | 1.12 | 1.22 | -0.0015976 | 3380 | 0.76 | 3380 | 0.76 | 1.12 | 1.22 | -0.0016
LFNoneSCERt3ExCZ13 | Com-Iltg-dWatt-LF_OSnone | SCE | Rt3 | Ex | CZ13 | 3.38 | 0.00075947 | 0 | 3.71 | 0.00093847 | -0.0179 | 3.38 | 0.00075947 | 0 | 3.71 | 0.00093847 | -0.0179 |  | LF | None | 3380 | 0.759 | 3380 | 0.759 | 1.1 | 1.24 | -0.0052959 | 3380 | 0.759 | 3380 | 0.759 | 1.1 | 1.24 | -0.0053
LFNoneSCERt3ExCZ14 | Com-Iltg-dWatt-LF_OSnone | SCE | Rt3 | Ex | CZ14 | 3.38 | 0.00075945 | 0 | 3.67 | 0.0009349 | -0.0189 | 3.38 | 0.00075945 | 0 | 3.67 | 0.0009349 | -0.0189 |  | LF | None | 3380 | 0.759 | 3380 | 0.759 | 1.09 | 1.23 | -0.0055917 | 3380 | 0.759 | 3380 | 0.759 | 1.09 | 1.23 | -0.00559
LFNoneSCERt3ExCZ15 | Com-Iltg-dWatt-LF_OSnone | SCE | Rt3 | Ex | CZ15 | 3.38 | 0.00075952 | 0 | 3.94 | 0.00094552 | -0.00122 | 3.38 | 0.00075952 | 0 | 3.94 | 0.00094552 | -0.00122 |  | LF | None | 3380 | 0.76 | 3380 | 0.76 | 1.17 | 1.24 | -0.00036095 | 3380 | 0.76 | 3380 | 0.76 | 1.17 | 1.24 | -0.000361
LFNoneSCERt3ExCZ16 | Com-Iltg-dWatt-LF_OSnone | SCE | Rt3 | Ex | CZ16 | 3.38 | 0.00075947 | 0 | 3.33 | 0.00091447 | -0.0425 | 3.38 | 0.00075947 | 0 | 3.33 | 0.00091447 | -0.0425 |  | LF | None | 3380 | 0.759 | 3380 | 0.759 | 0.985 | 1.2 | -0.012574 | 3380 | 0.759 | 3380 | 0.759 | 0.985 | 1.2 | -0.0126
LFNoneSCERt3ExIOU | Com-Iltg-dWatt-LF_OSnone | SCE | Rt3 | Ex | IOU | 3.38 | 0.00075938 | 0 | 3.8736 | 0.00092921 | -0.0052631 | 3.38 | 0.00075938 | 0 | 3.8736 | 0.00092921 | -0.0052631 |  | LF | None | 3380 | 0.759 | 3380 | 0.759 | 1.15 | 1.22 | -0.0015571 | 3380 | 0.759 | 3380 | 0.759 | 1.15 | 1.22 | -0.00156
LFNoneSCERt3NewCZ05 | Com-Iltg-dWatt-LF_OSnone | SCE | Rt3 | New | CZ05 | 3.38 | 0.00076 | 0 | 3.58 | 0.000933 | -0.0177 | 3.38 | 0.00076 | 0 | 3.58 | 0.000933 | -0.0177 |  | LF | None | 3380 | 0.76 | 3380 | 0.76 | 1.06 | 1.23 | -0.0052367 | 3380 | 0.76 | 3380 | 0.76 | 1.06 | 1.23 | -0.00524
LFNoneSCERt3NewCZ06 | Com-Iltg-dWatt-LF_OSnone | SCE | Rt3 | New | CZ06 | 3.38 | 0.00076 | 0 | 3.81 | 0.000942 | -0.00445 | 3.38 | 0.00076 | 0 | 3.81 | 0.000942 | -0.00445 |  | LF | None | 3380 | 0.76 | 3380 | 0.76 | 1.13 | 1.24 | -0.0013166 | 3380 | 0.76 | 3380 | 0.76 | 1.13 | 1.24 | -0.00132
LFNoneSCERt3NewCZ08 | Com-Iltg-dWatt-LF_OSnone | SCE | Rt3 | New | CZ08 | 3.38 | 0.00076 | 0 | 3.85 | 0.000949 | -0.00375 | 3.38 | 0.00076 | 0 | 3.85 | 0.000949 | -0.00375 |  | LF | None | 3380 | 0.76 | 3380 | 0.76 | 1.14 | 1.25 | -0.0011095 | 3380 | 0.76 | 3380 | 0.76 | 1.14 | 1.25 | -0.00111
LFNoneSCERt3NewCZ09 | Com-Iltg-dWatt-LF_OSnone | SCE | Rt3 | New | CZ09 | 3.38 | 0.00076 | 0 | 3.78 | 0.00091 | -0.00591 | 3.38 | 0.00076 | 0 | 3.78 | 0.00091 | -0.00591 |  | LF | None | 3380 | 0.76 | 3380 | 0.76 | 1.12 | 1.2 | -0.0017485 | 3380 | 0.76 | 3380 | 0.76 | 1.12 | 1.2 | -0.00175
LFNoneSCERt3NewCZ10 | Com-Iltg-dWatt-LF_OSnone | SCE | Rt3 | New | CZ10 | 3.38 | 0.00076 | 0 | 3.81 | 0.000943 | -0.00689 | 3.38 | 0.00076 | 0 | 3.81 | 0.000943 | -0.00689 |  | LF | None | 3380 | 0.76 | 3380 | 0.76 | 1.13 | 1.24 | -0.0020385 | 3380 | 0.76 | 3380 | 0.76 | 1.13 | 1.24 | -0.00204
LFNoneSCERt3NewCZ13 | Com-Iltg-dWatt-LF_OSnone | SCE | Rt3 | New | CZ13 | 3.38 | 0.00076 | 0 | 3.75 | 0.000986 | -0.0194 | 3.38 | 0.00076 | 0 | 3.75 | 0.000986 | -0.0194 |  | LF | None | 3380 | 0.76 | 3380 | 0.76 | 1.11 | 1.3 | -0.0057396 | 3380 | 0.76 | 3380 | 0.76 | 1.11 | 1.3 | -0.00574
LFNoneSCERt3NewCZ14 | Com-Iltg-dWatt-LF_OSnone | SCE | Rt3 | New | CZ14 | 3.38 | 0.00076 | 0 | 3.75 | 0.000982 | -0.0199 | 3.38 | 0.00076 | 0 | 3.75 | 0.000982 | -0.0199 |  | LF | None | 3380 | 0.76 | 3380 | 0.76 | 1.11 | 1.29 | -0.0058876 | 3380 | 0.76 | 3380 | 0.76 | 1.11 | 1.29 | -0.00589
LFNoneSCERt3NewCZ15 | Com-Iltg-dWatt-LF_OSnone | SCE | Rt3 | New | CZ15 | 3.38 | 0.00076 | 0 | 3.81 | 0.000896 | -0.000722 | 3.38 | 0.00076 | 0 | 3.81 | 0.000896 | -0.000722 |  | LF | None | 3380 | 0.76 | 3380 | 0.76 | 1.13 | 1.18 | -0.00021361 | 3380 | 0.76 | 3380 | 0.76 | 1.13 | 1.18 | -0.000214
LFNoneSCERt3NewCZ16 | Com-Iltg-dWatt-LF_OSnone | SCE | Rt3 | New | CZ16 | 3.38 | 0.00076 | 0 | 3.37 | 0.00094 | -0.0432 | 3.38 | 0.00076 | 0 | 3.37 | 0.00094 | -0.0432 |  | LF | None | 3380 | 0.76 | 3380 | 0.76 | 0.997 | 1.24 | -0.012781 | 3380 | 0.76 | 3380 | 0.76 | 0.997 | 1.24 | -0.0128
LFNoneSCERt3NewIOU | Com-Iltg-dWatt-LF_OSnone | SCE | Rt3 | New | IOU | 3.38 | 0.00076 | 0 | 3.8043 | 0.00094147 | -0.00689 | 3.38 | 0.00076 | 0 | 3.8043 | 0.00094147 | -0.00689 |  | LF | None | 3380 | 0.76 | 3380 | 0.76 | 1.13 | 1.24 | -0.0020385 | 3380 | 0.76 | 3380 | 0.76 | 1.13 | 1.24 | -0.00204
LFNoneSCERtLExCZ05 | Com-Iltg-dWatt-LF_OSnone | SCE | RtL | Ex | CZ05 | 4.27 | 0.000848 | 0 | 4.6 | 0.00103 | -0.0254 | 4.27 | 0.000848 | 0 | 4.6 | 0.00103 | -0.0254 |  | LF | None | 4270 | 0.848 | 4270 | 0.848 | 1.08 | 1.21 | -0.0059485 | 4270 | 0.848 | 4270 | 0.848 | 1.08 | 1.21 | -0.00595
LFNoneSCERtLExCZ06 | Com-Iltg-dWatt-LF_OSnone | SCE | RtL | Ex | CZ06 | 4.27 | 0.000848 | 0 | 4.89 | 0.00104 | -0.0099 | 4.27 | 0.000848 | 0 | 4.89 | 0.00104 | -0.0099 |  | LF | None | 4270 | 0.848 | 4270 | 0.848 | 1.15 | 1.23 | -0.0023185 | 4270 | 0.848 | 4270 | 0.848 | 1.15 | 1.23 | -0.00232
LFNoneSCERtLExCZ08 | Com-Iltg-dWatt-LF_OSnone | SCE | RtL | Ex | CZ08 | 4.27 | 0.000848 | 0 | 4.91 | 0.00105 | -0.00858 | 4.27 | 0.000848 | 0 | 4.91 | 0.00105 | -0.00858 |  | LF | None | 4270 | 0.848 | 4270 | 0.848 | 1.15 | 1.24 | -0.0020094 | 4270 | 0.848 | 4270 | 0.848 | 1.15 | 1.24 | -0.00201
LFNoneSCERtLExCZ09 | Com-Iltg-dWatt-LF_OSnone | SCE | RtL | Ex | CZ09 | 4.27 | 0.000848 | 0 | 4.86 | 0.00107 | -0.0102 | 4.27 | 0.000848 | 0 | 4.86 | 0.00107 | -0.0102 |  | LF | None | 4270 | 0.848 | 4270 | 0.848 | 1.14 | 1.26 | -0.0023888 | 4270 | 0.848 | 4270 | 0.848 | 1.14 | 1.26 | -0.00239
LFNoneSCERtLExCZ10 | Com-Iltg-dWatt-LF_OSnone | SCE | RtL | Ex | CZ10 | 4.27 | 0.000848 | 0 | 4.77 | 0.00106 | -0.0114 | 4.27 | 0.000848 | 0 | 4.77 | 0.00106 | -0.0114 |  | LF | None | 4270 | 0.848 | 4270 | 0.848 | 1.12 | 1.25 | -0.0026698 | 4270 | 0.848 | 4270 | 0.848 | 1.12 | 1.25 | -0.00267
LFNoneSCERtLExCZ13 | Com-Iltg-dWatt-LF_OSnone | SCE | RtL | Ex | CZ13 | 4.27 | 0.000848 | 0 | 4.68 | 0.00106 | -0.0235 | 4.27 | 0.000848 | 0 | 4.68 | 0.00106 | -0.0235 |  | LF | None | 4270 | 0.848 | 4270 | 0.848 | 1.1 | 1.25 | -0.0055035 | 4270 | 0.848 | 4270 | 0.848 | 1.1 | 1.25 | -0.0055
LFNoneSCERtLExCZ14 | Com-Iltg-dWatt-LF_OSnone | SCE | RtL | Ex | CZ14 | 4.27 | 0.000848 | 0 | 4.64 | 0.00107 | -0.0241 | 4.27 | 0.000848 | 0 | 4.64 | 0.00107 | -0.0241 |  | LF | None | 4270 | 0.848 | 4270 | 0.848 | 1.09 | 1.26 | -0.005644 | 4270 | 0.848 | 4270 | 0.848 | 1.09 | 1.26 | -0.00564
LFNoneSCERtLExCZ15 | Com-Iltg-dWatt-LF_OSnone | SCE | RtL | Ex | CZ15 | 4.27 | 0.000848 | 0 | 4.99 | 0.00107 | -0.004 | 4.27 | 0.000848 | 0 | 4.99 | 0.00107 | -0.004 |  | LF | None | 4270 | 0.848 | 4270 | 0.848 | 1.17 | 1.26 | -0.00093677 | 4270 | 0.848 | 4270 | 0.848 | 1.17 | 1.26 | -0.000937
LFNoneSCERtLExCZ16 | Com-Iltg-dWatt-LF_OSnone | SCE | RtL | Ex | CZ16 | 4.27 | 0.000848 | 0 | 4.19 | 0.00102 | -0.0546 | 4.27 | 0.000848 | 0 | 4.19 | 0.00102 | -0.0546 |  | LF | None | 4270 | 0.848 | 4270 | 0.848 | 0.981 | 1.2 | -0.012787 | 4270 | 0.848 | 4270 | 0.848 | 0.981 | 1.2 | -0.0128
LFNoneSCERtLExIOU | Com-Iltg-dWatt-LF_OSnone | SCE | RtL | Ex | IOU | 4.27 | 0.000848 | 0 | 4.8451 | 0.0010541 | -0.011119 | 4.27 | 0.000848 | 0 | 4.8451 | 0.0010541 | -0.011119 |  | LF | None | 4270 | 0.848 | 4270 | 0.848 | 1.13 | 1.24 | -0.0026041 | 4270 | 0.848 | 4270 | 0.848 | 1.13 | 1.24 | -0.0026
LFNoneSCERtLNewCZ05 | Com-Iltg-dWatt-LF_OSnone | SCE | RtL | New | CZ05 | 4.27 | 0.000848 | 0 | 4.47 | 0.00104 | -0.03 | 4.27 | 0.000848 | 0 | 4.47 | 0.00104 | -0.03 |  | LF | None | 4270 | 0.848 | 4270 | 0.848 | 1.05 | 1.23 | -0.0070258 | 4270 | 0.848 | 4270 | 0.848 | 1.05 | 1.23 | -0.00703
LFNoneSCERtLNewCZ06 | Com-Iltg-dWatt-LF_OSnone | SCE | RtL | New | CZ06 | 4.27 | 0.000848 | 0 | 4.73 | 0.00106 | -0.0135 | 4.27 | 0.000848 | 0 | 4.73 | 0.00106 | -0.0135 |  | LF | None | 4270 | 0.848 | 4270 | 0.848 | 1.11 | 1.25 | -0.0031616 | 4270 | 0.848 | 4270 | 0.848 | 1.11 | 1.25 | -0.00316
LFNoneSCERtLNewCZ08 | Com-Iltg-dWatt-LF_OSnone | SCE | RtL | New | CZ08 | 4.27 | 0.000848 | 0 | 4.79 | 0.00108 | -0.0115 | 4.27 | 0.000848 | 0 | 4.79 | 0.00108 | -0.0115 |  | LF | None | 4270 | 0.848 | 4270 | 0.848 | 1.12 | 1.27 | -0.0026932 | 4270 | 0.848 | 4270 | 0.848 | 1.12 | 1.27 | -0.00269
LFNoneSCERtLNewCZ09 | Com-Iltg-dWatt-LF_OSnone | SCE | RtL | New | CZ09 | 4.27 | 0.000848 | 0 | 4.81 | 0.00112 | -0.0115 | 4.27 | 0.000848 | 0 | 4.81 | 0.00112 | -0.0115 |  | LF | None | 4270 | 0.848 | 4270 | 0.848 | 1.13 | 1.32 | -0.0026932 | 4270 | 0.848 | 4270 | 0.848 | 1.13 | 1.32 | -0.00269
LFNoneSCERtLNewCZ10 | Com-Iltg-dWatt-LF_OSnone | SCE | RtL | New | CZ10 | 4.27 | 0.000848 | 0 | 4.83 | 0.00112 | -0.0134 | 4.27 | 0.000848 | 0 | 4.83 | 0.00112 | -0.0134 |  | LF | None | 4270 | 0.848 | 4270 | 0.848 | 1.13 | 1.32 | -0.0031382 | 4270 | 0.848 | 4270 | 0.848 | 1.13 | 1.32 | -0.00314
LFNoneSCERtLNewCZ13 | Com-Iltg-dWatt-LF_OSnone | SCE | RtL | New | CZ13 | 4.27 | 0.000848 | 0 | 4.73 | 0.00111 | -0.0262 | 4.27 | 0.000848 | 0 | 4.73 | 0.00111 | -0.0262 |  | LF | None | 4270 | 0.848 | 4270 | 0.848 | 1.11 | 1.31 | -0.0061358 | 4270 | 0.848 | 4270 | 0.848 | 1.11 | 1.31 | -0.00614
LFNoneSCERtLNewCZ14 | Com-Iltg-dWatt-LF_OSnone | SCE | RtL | New | CZ14 | 4.27 | 0.000848 | 0 | 4.72 | 0.00111 | -0.0266 | 4.27 | 0.000848 | 0 | 4.72 | 0.00111 | -0.0266 |  | LF | None | 4270 | 0.848 | 4270 | 0.848 | 1.11 | 1.31 | -0.0062295 | 4270 | 0.848 | 4270 | 0.848 | 1.11 | 1.31 | -0.00623
LFNoneSCERtLNewCZ15 | Com-Iltg-dWatt-LF_OSnone | SCE | RtL | New | CZ15 | 4.27 | 0.000848 | 0 | 5.12 | 0.00113 | -0.00404 | 4.27 | 0.000848 | 0 | 5.12 | 0.00113 | -0.00404 |  | LF | None | 4270 | 0.848 | 4270 | 0.848 | 1.2 | 1.33 | -0.00094614 | 4270 | 0.848 | 4270 | 0.848 | 1.2 | 1.33 | -0.000946
LFNoneSCERtLNewCZ16 | Com-Iltg-dWatt-LF_OSnone | SCE | RtL | New | CZ16 | 4.27 | 0.000848 | 0 | 4.24 | 0.00105 | -0.0576 | 4.27 | 0.000848 | 0 | 4.24 | 0.00105 | -0.0576 |  | LF | None | 4270 | 0.848 | 4270 | 0.848 | 0.993 | 1.24 | -0.013489 | 4270 | 0.848 | 4270 | 0.848 | 0.993 | 1.24 | -0.0135
LFNoneSCERtLNewIOU | Com-Iltg-dWatt-LF_OSnone | SCE | RtL | New | IOU | 4.27 | 0.000848 | 0 | 4.7964 | 0.0010985 | -0.01402 | 4.27 | 0.000848 | 0 | 4.7964 | 0.0010985 | -0.01402 |  | LF | None | 4270 | 0.848 | 4270 | 0.848 | 1.12 | 1.3 | -0.0032834 | 4270 | 0.848 | 4270 | 0.848 | 1.12 | 1.3 | -0.00328
LFNoneSCERtSExCZ05 | Com-Iltg-dWatt-LF_OSnone | SCE | RtS | Ex | CZ05 | 3.38 | 0.000875 | 0 | 3.63 | 0.00106 | -0.0156 | 3.38 | 0.000875 | 0 | 3.63 | 0.00106 | -0.0156 |  | LF | None | 3380 | 0.875 | 3380 | 0.875 | 1.07 | 1.21 | -0.0046154 | 3380 | 0.875 | 3380 | 0.875 | 1.07 | 1.21 | -0.00462
LFNoneSCERtSExCZ06 | Com-Iltg-dWatt-LF_OSnone | SCE | RtS | Ex | CZ06 | 3.38 | 0.000875 | 0 | 3.84 | 0.00107 | -0.00513 | 3.38 | 0.000875 | 0 | 3.84 | 0.00107 | -0.00513 |  | LF | None | 3380 | 0.875 | 3380 | 0.875 | 1.14 | 1.22 | -0.0015178 | 3380 | 0.875 | 3380 | 0.875 | 1.14 | 1.22 | -0.00152
LFNoneSCERtSExCZ08 | Com-Iltg-dWatt-LF_OSnone | SCE | RtS | Ex | CZ08 | 3.38 | 0.000875 | 0 | 3.87 | 0.00107 | -0.00435 | 3.38 | 0.000875 | 0 | 3.87 | 0.00107 | -0.00435 |  | LF | None | 3380 | 0.875 | 3380 | 0.875 | 1.14 | 1.22 | -0.001287 | 3380 | 0.875 | 3380 | 0.875 | 1.14 | 1.22 | -0.00129
LFNoneSCERtSExCZ09 | Com-Iltg-dWatt-LF_OSnone | SCE | RtS | Ex | CZ09 | 3.38 | 0.000875 | 0 | 3.83 | 0.00109 | -0.00584 | 3.38 | 0.000875 | 0 | 3.83 | 0.00109 | -0.00584 |  | LF | None | 3380 | 0.875 | 3380 | 0.875 | 1.13 | 1.25 | -0.0017278 | 3380 | 0.875 | 3380 | 0.875 | 1.13 | 1.25 | -0.00173
LFNoneSCERtSExCZ10 | Com-Iltg-dWatt-LF_OSnone | SCE | RtS | Ex | CZ10 | 3.38 | 0.000875 | 0 | 3.76 | 0.00107 | -0.00655 | 3.38 | 0.000875 | 0 | 3.76 | 0.00107 | -0.00655 |  | LF | None | 3380 | 0.875 | 3380 | 0.875 | 1.11 | 1.22 | -0.0019379 | 3380 | 0.875 | 3380 | 0.875 | 1.11 | 1.22 | -0.00194
LFNoneSCERtSExCZ13 | Com-Iltg-dWatt-LF_OSnone | SCE | RtS | Ex | CZ13 | 3.38 | 0.000875 | 0 | 3.69 | 0.00108 | -0.0185 | 3.38 | 0.000875 | 0 | 3.69 | 0.00108 | -0.0185 |  | LF | None | 3380 | 0.875 | 3380 | 0.875 | 1.09 | 1.23 | -0.0054734 | 3380 | 0.875 | 3380 | 0.875 | 1.09 | 1.23 | -0.00547
LFNoneSCERtSExCZ14 | Com-Iltg-dWatt-LF_OSnone | SCE | RtS | Ex | CZ14 | 3.38 | 0.000875 | 0 | 3.68 | 0.00107 | -0.0162 | 3.38 | 0.000875 | 0 | 3.68 | 0.00107 | -0.0162 |  | LF | None | 3380 | 0.875 | 3380 | 0.875 | 1.09 | 1.22 | -0.0047929 | 3380 | 0.875 | 3380 | 0.875 | 1.09 | 1.22 | -0.00479
LFNoneSCERtSExCZ15 | Com-Iltg-dWatt-LF_OSnone | SCE | RtS | Ex | CZ15 | 3.38 | 0.000875 | 0 | 3.96 | 0.00108 | -0.0014 | 3.38 | 0.000875 | 0 | 3.96 | 0.00108 | -0.0014 |  | LF | None | 3380 | 0.875 | 3380 | 0.875 | 1.17 | 1.23 | -0.0004142 | 3380 | 0.875 | 3380 | 0.875 | 1.17 | 1.23 | -0.000414
LFNoneSCERtSExCZ16 | Com-Iltg-dWatt-LF_OSnone | SCE | RtS | Ex | CZ16 | 3.38 | 0.000875 | 0 | 3.35 | 0.00105 | -0.0375 | 3.38 | 0.000875 | 0 | 3.35 | 0.00105 | -0.0375 |  | LF | None | 3380 | 0.875 | 3380 | 0.875 | 0.991 | 1.2 | -0.011095 | 3380 | 0.875 | 3380 | 0.875 | 0.991 | 1.2 | -0.0111
LFNoneSCERtSExIOU | Com-Iltg-dWatt-LF_OSnone | SCE | RtS | Ex | IOU | 3.38 | 0.000875 | 0 | 3.8175 | 0.0010734 | -0.0063508 | 3.38 | 0.000875 | 0 | 3.8175 | 0.0010734 | -0.0063508 |  | LF | None | 3380 | 0.875 | 3380 | 0.875 | 1.13 | 1.23 | -0.0018789 | 3380 | 0.875 | 3380 | 0.875 | 1.13 | 1.23 | -0.00188
LFNoneSCERtSNewCZ05 | Com-Iltg-dWatt-LF_OSnone | SCE | RtS | New | CZ05 | 3.38 | 0.000875 | 0 | 3.54 | 0.00104 | -0.0178 | 3.38 | 0.000875 | 0 | 3.54 | 0.00104 | -0.0178 |  | LF | None | 3380 | 0.875 | 3380 | 0.875 | 1.05 | 1.19 | -0.0052663 | 3380 | 0.875 | 3380 | 0.875 | 1.05 | 1.19 | -0.00527
LFNoneSCERtSNewCZ06 | Com-Iltg-dWatt-LF_OSnone | SCE | RtS | New | CZ06 | 3.38 | 0.000875 | 0 | 3.74 | 0.00106 | -0.00678 | 3.38 | 0.000875 | 0 | 3.74 | 0.00106 | -0.00678 |  | LF | None | 3380 | 0.875 | 3380 | 0.875 | 1.11 | 1.21 | -0.0020059 | 3380 | 0.875 | 3380 | 0.875 | 1.11 | 1.21 | -0.00201
LFNoneSCERtSNewCZ08 | Com-Iltg-dWatt-LF_OSnone | SCE | RtS | New | CZ08 | 3.38 | 0.000875 | 0 | 3.78 | 0.00107 | -0.0057 | 3.38 | 0.000875 | 0 | 3.78 | 0.00107 | -0.0057 |  | LF | None | 3380 | 0.875 | 3380 | 0.875 | 1.12 | 1.22 | -0.0016864 | 3380 | 0.875 | 3380 | 0.875 | 1.12 | 1.22 | -0.00169
LFNoneSCERtSNewCZ09 | Com-Iltg-dWatt-LF_OSnone | SCE | RtS | New | CZ09 | 3.38 | 0.000875 | 0 | 3.78 | 0.0011 | -0.00692 | 3.38 | 0.000875 | 0 | 3.78 | 0.0011 | -0.00692 |  | LF | None | 3380 | 0.875 | 3380 | 0.875 | 1.12 | 1.26 | -0.0020473 | 3380 | 0.875 | 3380 | 0.875 | 1.12 | 1.26 | -0.00205
LFNoneSCERtSNewCZ10 | Com-Iltg-dWatt-LF_OSnone | SCE | RtS | New | CZ10 | 3.38 | 0.000875 | 0 | 3.81 | 0.00112 | -0.00709 | 3.38 | 0.000875 | 0 | 3.81 | 0.00112 | -0.00709 |  | LF | None | 3380 | 0.875 | 3380 | 0.875 | 1.13 | 1.28 | -0.0020976 | 3380 | 0.875 | 3380 | 0.875 | 1.13 | 1.28 | -0.0021
LFNoneSCERtSNewCZ13 | Com-Iltg-dWatt-LF_OSnone | SCE | RtS | New | CZ13 | 3.38 | 0.000875 | 0 | 3.7 | 0.00109 | -0.0189 | 3.38 | 0.000875 | 0 | 3.7 | 0.00109 | -0.0189 |  | LF | None | 3380 | 0.875 | 3380 | 0.875 | 1.09 | 1.25 | -0.0055917 | 3380 | 0.875 | 3380 | 0.875 | 1.09 | 1.25 | -0.00559
LFNoneSCERtSNewCZ14 | Com-Iltg-dWatt-LF_OSnone | SCE | RtS | New | CZ14 | 3.38 | 0.000875 | 0 | 3.72 | 0.00109 | -0.0171 | 3.38 | 0.000875 | 0 | 3.72 | 0.00109 | -0.0171 |  | LF | None | 3380 | 0.875 | 3380 | 0.875 | 1.1 | 1.25 | -0.0050592 | 3380 | 0.875 | 3380 | 0.875 | 1.1 | 1.25 | -0.00506
LFNoneSCERtSNewCZ15 | Com-Iltg-dWatt-LF_OSnone | SCE | RtS | New | CZ15 | 3.38 | 0.000875 | 0 | 3.98 | 0.00112 | -0.00126 | 3.38 | 0.000875 | 0 | 3.98 | 0.00112 | -0.00126 |  | LF | None | 3380 | 0.875 | 3380 | 0.875 | 1.18 | 1.28 | -0.00037278 | 3380 | 0.875 | 3380 | 0.875 | 1.18 | 1.28 | -0.000373
LFNoneSCERtSNewCZ16 | Com-Iltg-dWatt-LF_OSnone | SCE | RtS | New | CZ16 | 3.38 | 0.000875 | 0 | 3.36 | 0.00105 | -0.0398 | 3.38 | 0.000875 | 0 | 3.36 | 0.00105 | -0.0398 |  | LF | None | 3380 | 0.875 | 3380 | 0.875 | 0.994 | 1.2 | -0.011775 | 3380 | 0.875 | 3380 | 0.875 | 0.994 | 1.2 | -0.0118
LFNoneSCERtSNewIOU | Com-Iltg-dWatt-LF_OSnone | SCE | RtS | New | IOU | 3.38 | 0.000875 | 0 | 3.78 | 0.0010917 | -0.0077691 | 3.38 | 0.000875 | 0 | 3.78 | 0.0010917 | -0.0077691 |  | LF | None | 3380 | 0.875 | 3380 | 0.875 | 1.12 | 1.25 | -0.0022986 | 3380 | 0.875 | 3380 | 0.875 | 1.12 | 1.25 | -0.0023
LFNoneSCEs_AgrExCZ05 | Com-Iltg-dWatt-LF_OSnone | SCE | s_Agr | Ex | CZ05 | 3.094 | 0.000878 | 0 | 3.264 | 0.0010776 | -0.015296 | 3.094 | 0.000878 | 0 | 3.264 | 0.0010776 | -0.015296 |  | LF | None | 3090 | 0.878 | 3090 | 0.878 | 1.05 | 1.23 | -0.0049438 | 3090 | 0.878 | 3090 | 0.878 | 1.05 | 1.23 | -0.00494
LFNoneSCEs_AgrExCZ06 | Com-Iltg-dWatt-LF_OSnone | SCE | s_Agr | Ex | CZ06 | 3.094 | 0.000878 | 0 | 3.444 | 0.0010638 | -0.005452 | 3.094 | 0.000878 | 0 | 3.444 | 0.0010638 | -0.005452 |  | LF | None | 3090 | 0.878 | 3090 | 0.878 | 1.11 | 1.21 | -0.0017621 | 3090 | 0.878 | 3090 | 0.878 | 1.11 | 1.21 | -0.00176
LFNoneSCEs_AgrExCZ08 | Com-Iltg-dWatt-LF_OSnone | SCE | s_Agr | Ex | CZ08 | 3.094 | 0.000878 | 0 | 3.47 | 0.0010652 | -0.004546 | 3.094 | 0.000878 | 0 | 3.47 | 0.0010652 | -0.004546 |  | LF | None | 3090 | 0.878 | 3090 | 0.878 | 1.12 | 1.21 | -0.0014693 | 3090 | 0.878 | 3090 | 0.878 | 1.12 | 1.21 | -0.00147
LFNoneSCEs_AgrExCZ09 | Com-Iltg-dWatt-LF_OSnone | SCE | s_Agr | Ex | CZ09 | 3.094 | 0.000878 | 0 | 3.444 | 0.001083 | -0.006222 | 3.094 | 0.000878 | 0 | 3.444 | 0.001083 | -0.006222 |  | LF | None | 3090 | 0.878 | 3090 | 0.878 | 1.11 | 1.23 | -0.002011 | 3090 | 0.878 | 3090 | 0.878 | 1.11 | 1.23 | -0.00201
LFNoneSCEs_AgrExCZ10 | Com-Iltg-dWatt-LF_OSnone | SCE | s_Agr | Ex | CZ10 | 3.094 | 0.000878 | 0 | 3.364 | 0.0010732 | -0.006648 | 3.094 | 0.000878 | 0 | 3.364 | 0.0010732 | -0.006648 |  | LF | None | 3090 | 0.878 | 3090 | 0.878 | 1.09 | 1.22 | -0.0021487 | 3090 | 0.878 | 3090 | 0.878 | 1.09 | 1.22 | -0.00215
LFNoneSCEs_AgrExCZ13 | Com-Iltg-dWatt-LF_OSnone | SCE | s_Agr | Ex | CZ13 | 3.094 | 0.000878 | 0 | 3.326 | 0.001064 | -0.015994 | 3.094 | 0.000878 | 0 | 3.326 | 0.001064 | -0.015994 |  | LF | None | 3090 | 0.878 | 3090 | 0.878 | 1.07 | 1.21 | -0.0051694 | 3090 | 0.878 | 3090 | 0.878 | 1.07 | 1.21 | -0.00517
LFNoneSCEs_AgrExCZ14 | Com-Iltg-dWatt-LF_OSnone | SCE | s_Agr | Ex | CZ14 | 3.094 | 0.000878 | 0 | 3.304 | 0.0010754 | -0.017694 | 3.094 | 0.000878 | 0 | 3.304 | 0.0010754 | -0.017694 |  | LF | None | 3090 | 0.878 | 3090 | 0.878 | 1.07 | 1.22 | -0.0057188 | 3090 | 0.878 | 3090 | 0.878 | 1.07 | 1.22 | -0.00572
LFNoneSCEs_AgrExCZ15 | Com-Iltg-dWatt-LF_OSnone | SCE | s_Agr | Ex | CZ15 | 3.094 | 0.000878 | 0 | 3.592 | 0.0010648 | -0.001804 | 3.094 | 0.000878 | 0 | 3.592 | 0.0010648 | -0.001804 |  | LF | None | 3090 | 0.878 | 3090 | 0.878 | 1.16 | 1.21 | -0.00058306 | 3090 | 0.878 | 3090 | 0.878 | 1.16 | 1.21 | -0.000583
LFNoneSCEs_AgrExCZ16 | Com-Iltg-dWatt-LF_OSnone | SCE | s_Agr | Ex | CZ16 | 3.094 | 0.000878 | 0 | 3.058 | 0.0010524 | -0.03522 | 3.094 | 0.000878 | 0 | 3.058 | 0.0010524 | -0.03522 |  | LF | None | 3090 | 0.878 | 3090 | 0.878 | 0.988 | 1.2 | -0.011383 | 3090 | 0.878 | 3090 | 0.878 | 0.988 | 1.2 | -0.0114
LFNoneSCEs_AgrExIOU | Com-Iltg-dWatt-LF_OSnone | SCE | s_Agr | Ex | IOU | 3.094 | 0.000878 | 0 | 3.4305 | 0.0010689 | -0.0066513 | 3.094 | 0.000878 | 0 | 3.4305 | 0.0010689 | -0.0066513 |  | LF | None | 3090 | 0.878 | 3090 | 0.878 | 1.11 | 1.22 | -0.0021498 | 3090 | 0.878 | 3090 | 0.878 | 1.11 | 1.22 | -0.00215
LFNoneSCEs_CliExCZ05 | Com-Iltg-dWatt-LF_OSnone | SCE | s_Cli | Ex | CZ05 | 3.375 | 0.000685 | 0 | 3.535 | 0.0008525 | -0.03689 | 3.375 | 0.000685 | 0 | 3.535 | 0.0008525 | -0.03689 |  | LF | None | 3380 | 0.685 | 3380 | 0.685 | 1.05 | 1.24 | -0.01093 | 3380 | 0.685 | 3380 | 0.685 | 1.05 | 1.24 | -0.0109
LFNoneSCEs_CliExCZ06 | Com-Iltg-dWatt-LF_OSnone | SCE | s_Cli | Ex | CZ06 | 3.375 | 0.000685 | 0 | 3.745 | 0.0008805 | -0.02382 | 3.375 | 0.000685 | 0 | 3.745 | 0.0008805 | -0.02382 |  | LF | None | 3380 | 0.685 | 3380 | 0.685 | 1.11 | 1.29 | -0.0070578 | 3380 | 0.685 | 3380 | 0.685 | 1.11 | 1.29 | -0.00706
LFNoneSCEs_CliExCZ08 | Com-Iltg-dWatt-LF_OSnone | SCE | s_Cli | Ex | CZ08 | 3.375 | 0.000685 | 0 | 3.775 | 0.0008825 | -0.023025 | 3.375 | 0.000685 | 0 | 3.775 | 0.0008825 | -0.023025 |  | LF | None | 3380 | 0.685 | 3380 | 0.685 | 1.12 | 1.29 | -0.0068222 | 3380 | 0.685 | 3380 | 0.685 | 1.12 | 1.29 | -0.00682
LFNoneSCEs_CliExCZ09 | Com-Iltg-dWatt-LF_OSnone | SCE | s_Cli | Ex | CZ09 | 3.375 | 0.000685 | 0 | 3.78 | 0.000903 | -0.023865 | 3.375 | 0.000685 | 0 | 3.78 | 0.000903 | -0.023865 |  | LF | None | 3380 | 0.685 | 3380 | 0.685 | 1.12 | 1.32 | -0.0070711 | 3380 | 0.685 | 3380 | 0.685 | 1.12 | 1.32 | -0.00707
LFNoneSCEs_CliExCZ10 | Com-Iltg-dWatt-LF_OSnone | SCE | s_Cli | Ex | CZ10 | 3.375 | 0.000685 | 0 | 3.725 | 0.0008985 | -0.02371 | 3.375 | 0.000685 | 0 | 3.725 | 0.0008985 | -0.02371 |  | LF | None | 3380 | 0.685 | 3380 | 0.685 | 1.1 | 1.31 | -0.0070252 | 3380 | 0.685 | 3380 | 0.685 | 1.1 | 1.31 | -0.00703
LFNoneSCEs_CliExCZ13 | Com-Iltg-dWatt-LF_OSnone | SCE | s_Cli | Ex | CZ13 | 3.375 | 0.000685 | 0 | 3.67 | 0.0008895 | -0.030135 | 3.375 | 0.000685 | 0 | 3.67 | 0.0008895 | -0.030135 |  | LF | None | 3380 | 0.685 | 3380 | 0.685 | 1.09 | 1.3 | -0.0089289 | 3380 | 0.685 | 3380 | 0.685 | 1.09 | 1.3 | -0.00893
LFNoneSCEs_CliExCZ14 | Com-Iltg-dWatt-LF_OSnone | SCE | s_Cli | Ex | CZ14 | 3.375 | 0.000685 | 0 | 3.68 | 0.0008965 | -0.029635 | 3.375 | 0.000685 | 0 | 3.68 | 0.0008965 | -0.029635 |  | LF | None | 3380 | 0.685 | 3380 | 0.685 | 1.09 | 1.31 | -0.0087807 | 3380 | 0.685 | 3380 | 0.685 | 1.09 | 1.31 | -0.00878
LFNoneSCEs_CliExCZ15 | Com-Iltg-dWatt-LF_OSnone | SCE | s_Cli | Ex | CZ15 | 3.375 | 0.000685 | 0 | 3.975 | 0.0009005 | -0.01368 | 3.375 | 0.000685 | 0 | 3.975 | 0.0009005 | -0.01368 |  | LF | None | 3380 | 0.685 | 3380 | 0.685 | 1.18 | 1.31 | -0.0040533 | 3380 | 0.685 | 3380 | 0.685 | 1.18 | 1.31 | -0.00405
LFNoneSCEs_CliExCZ16 | Com-Iltg-dWatt-LF_OSnone | SCE | s_Cli | Ex | CZ16 | 3.375 | 0.000685 | 0 | 3.365 | 0.00086 | -0.0467 | 3.375 | 0.000685 | 0 | 3.365 | 0.00086 | -0.0467 |  | LF | None | 3380 | 0.685 | 3380 | 0.685 | 0.997 | 1.26 | -0.013837 | 3380 | 0.685 | 3380 | 0.685 | 0.997 | 1.26 | -0.0138
LFNoneSCEs_CliExIOU | Com-Iltg-dWatt-LF_OSnone | SCE | s_Cli | Ex | IOU | 3.375 | 0.000685 | 0 | 3.7488 | 0.00088786 | -0.024281 | 3.375 | 0.000685 | 0 | 3.7488 | 0.00088786 | -0.024281 |  | LF | None | 3380 | 0.685 | 3380 | 0.685 | 1.11 | 1.3 | -0.0071943 | 3380 | 0.685 | 3380 | 0.685 | 1.11 | 1.3 | -0.00719
LFNoneSCEs_FStExCZ05 | Com-Iltg-dWatt-LF_OSnone | SCE | s_FSt | Ex | CZ05 | 4.145 | 0.0007825 | 0 | 4.185 | 0.000956 | -0.04955 | 4.145 | 0.0007825 | 0 | 4.185 | 0.000956 | -0.04955 |  | LF | None | 4140 | 0.783 | 4140 | 0.783 | 1.01 | 1.22 | -0.011954 | 4140 | 0.783 | 4140 | 0.783 | 1.01 | 1.22 | -0.012
LFNoneSCEs_FStExCZ06 | Com-Iltg-dWatt-LF_OSnone | SCE | s_FSt | Ex | CZ06 | 4.145 | 0.0007825 | 0 | 4.46 | 0.0009665 | -0.03422 | 4.145 | 0.0007825 | 0 | 4.46 | 0.0009665 | -0.03422 |  | LF | None | 4140 | 0.783 | 4140 | 0.783 | 1.08 | 1.24 | -0.0082557 | 4140 | 0.783 | 4140 | 0.783 | 1.08 | 1.24 | -0.00826
LFNoneSCEs_FStExCZ08 | Com-Iltg-dWatt-LF_OSnone | SCE | s_FSt | Ex | CZ08 | 4.145 | 0.0007825 | 0 | 4.525 | 0.000976 | -0.03068 | 4.145 | 0.0007825 | 0 | 4.525 | 0.000976 | -0.03068 |  | LF | None | 4140 | 0.783 | 4140 | 0.783 | 1.09 | 1.25 | -0.0074017 | 4140 | 0.783 | 4140 | 0.783 | 1.09 | 1.25 | -0.0074
LFNoneSCEs_FStExCZ09 | Com-Iltg-dWatt-LF_OSnone | SCE | s_FSt | Ex | CZ09 | 4.145 | 0.0007825 | 0 | 4.515 | 0.0009915 | -0.030925 | 4.145 | 0.0007825 | 0 | 4.515 | 0.0009915 | -0.030925 |  | LF | None | 4140 | 0.783 | 4140 | 0.783 | 1.09 | 1.27 | -0.0074608 | 4140 | 0.783 | 4140 | 0.783 | 1.09 | 1.27 | -0.00746
LFNoneSCEs_FStExCZ10 | Com-Iltg-dWatt-LF_OSnone | SCE | s_FSt | Ex | CZ10 | 4.145 | 0.0007825 | 0 | 4.475 | 0.0009905 | -0.03053 | 4.145 | 0.0007825 | 0 | 4.475 | 0.0009905 | -0.03053 |  | LF | None | 4140 | 0.783 | 4140 | 0.783 | 1.08 | 1.27 | -0.0073655 | 4140 | 0.783 | 4140 | 0.783 | 1.08 | 1.27 | -0.00737
LFNoneSCEs_FStExCZ13 | Com-Iltg-dWatt-LF_OSnone | SCE | s_FSt | Ex | CZ13 | 4.145 | 0.0007825 | 0 | 4.435 | 0.0009885 | -0.03725 | 4.145 | 0.0007825 | 0 | 4.435 | 0.0009885 | -0.03725 |  | LF | None | 4140 | 0.783 | 4140 | 0.783 | 1.07 | 1.26 | -0.0089867 | 4140 | 0.783 | 4140 | 0.783 | 1.07 | 1.26 | -0.00899
LFNoneSCEs_FStExCZ14 | Com-Iltg-dWatt-LF_OSnone | SCE | s_FSt | Ex | CZ14 | 4.145 | 0.0007825 | 0 | 4.42 | 0.000997 | -0.0371 | 4.145 | 0.0007825 | 0 | 4.42 | 0.000997 | -0.0371 |  | LF | None | 4140 | 0.783 | 4140 | 0.783 | 1.07 | 1.27 | -0.0089505 | 4140 | 0.783 | 4140 | 0.783 | 1.07 | 1.27 | -0.00895
LFNoneSCEs_FStExCZ15 | Com-Iltg-dWatt-LF_OSnone | SCE | s_FSt | Ex | CZ15 | 4.145 | 0.0007825 | 0 | 4.755 | 0.000993 | -0.016005 | 4.145 | 0.0007825 | 0 | 4.755 | 0.000993 | -0.016005 |  | LF | None | 4140 | 0.783 | 4140 | 0.783 | 1.15 | 1.27 | -0.0038613 | 4140 | 0.783 | 4140 | 0.783 | 1.15 | 1.27 | -0.00386
LFNoneSCEs_FStExCZ16 | Com-Iltg-dWatt-LF_OSnone | SCE | s_FSt | Ex | CZ16 | 4.145 | 0.0007825 | 0 | 4.035 | 0.000954 | -0.0578 | 4.145 | 0.0007825 | 0 | 4.035 | 0.000954 | -0.0578 |  | LF | None | 4140 | 0.783 | 4140 | 0.783 | 0.973 | 1.22 | -0.013945 | 4140 | 0.783 | 4140 | 0.783 | 0.973 | 1.22 | -0.0139
LFNoneSCEs_FStExIOU | Com-Iltg-dWatt-LF_OSnone | SCE | s_FSt | Ex | IOU | 4.145 | 0.0007825 | 0 | 4.4905 | 0.00098098 | -0.031875 | 4.145 | 0.0007825 | 0 | 4.4905 | 0.00098098 | -0.031875 |  | LF | None | 4140 | 0.783 | 4140 | 0.783 | 1.08 | 1.25 | -0.0076899 | 4140 | 0.783 | 4140 | 0.783 | 1.08 | 1.25 | -0.00769
LFNoneSCEs_IndExCZ05 | Com-Iltg-dWatt-LF_OSnone | SCE | s_Ind | Ex | CZ05 | 3.375 | 0.0008875 | 0 | 3.715 | 0.0011 | -0.009515 | 3.375 | 0.0008875 | 0 | 3.715 | 0.0011 | -0.009515 |  | LF | None | 3380 | 0.888 | 3380 | 0.888 | 1.1 | 1.24 | -0.0028193 | 3380 | 0.888 | 3380 | 0.888 | 1.1 | 1.24 | -0.00282
LFNoneSCEs_IndExCZ06 | Com-Iltg-dWatt-LF_OSnone | SCE | s_Ind | Ex | CZ06 | 3.375 | 0.0008875 | 0 | 3.855 | 0.001075 | -0.003356 | 3.375 | 0.0008875 | 0 | 3.855 | 0.001075 | -0.003356 |  | LF | None | 3380 | 0.888 | 3380 | 0.888 | 1.14 | 1.21 | -0.00099437 | 3380 | 0.888 | 3380 | 0.888 | 1.14 | 1.21 | -0.000994
LFNoneSCEs_IndExCZ08 | Com-Iltg-dWatt-LF_OSnone | SCE | s_Ind | Ex | CZ08 | 3.375 | 0.0008875 | 0 | 3.88 | 0.001095 | -0.0026815 | 3.375 | 0.0008875 | 0 | 3.88 | 0.001095 | -0.0026815 |  | LF | None | 3380 | 0.888 | 3380 | 0.888 | 1.15 | 1.23 | -0.00079452 | 3380 | 0.888 | 3380 | 0.888 | 1.15 | 1.23 | -0.000795
LFNoneSCEs_IndExCZ09 | Com-Iltg-dWatt-LF_OSnone | SCE | s_Ind | Ex | CZ09 | 3.375 | 0.0008875 | 0 | 3.86 | 0.00111 | -0.00387 | 3.375 | 0.0008875 | 0 | 3.86 | 0.00111 | -0.00387 |  | LF | None | 3380 | 0.888 | 3380 | 0.888 | 1.14 | 1.25 | -0.0011467 | 3380 | 0.888 | 3380 | 0.888 | 1.14 | 1.25 | -0.00115
LFNoneSCEs_IndExCZ10 | Com-Iltg-dWatt-LF_OSnone | SCE | s_Ind | Ex | CZ10 | 3.375 | 0.0008875 | 0 | 3.75 | 0.001105 | -0.00422 | 3.375 | 0.0008875 | 0 | 3.75 | 0.001105 | -0.00422 |  | LF | None | 3380 | 0.888 | 3380 | 0.888 | 1.11 | 1.25 | -0.0012504 | 3380 | 0.888 | 3380 | 0.888 | 1.11 | 1.25 | -0.00125
LFNoneSCEs_IndExCZ13 | Com-Iltg-dWatt-LF_OSnone | SCE | s_Ind | Ex | CZ13 | 3.375 | 0.0008875 | 0 | 3.735 | 0.00108 | -0.009995 | 3.375 | 0.0008875 | 0 | 3.735 | 0.00108 | -0.009995 |  | LF | None | 3380 | 0.888 | 3380 | 0.888 | 1.11 | 1.22 | -0.0029615 | 3380 | 0.888 | 3380 | 0.888 | 1.11 | 1.22 | -0.00296
LFNoneSCEs_IndExCZ14 | Com-Iltg-dWatt-LF_OSnone | SCE | s_Ind | Ex | CZ14 | 3.375 | 0.0008875 | 0 | 3.72 | 0.001105 | -0.01152 | 3.375 | 0.0008875 | 0 | 3.72 | 0.001105 | -0.01152 |  | LF | None | 3380 | 0.888 | 3380 | 0.888 | 1.1 | 1.25 | -0.0034133 | 3380 | 0.888 | 3380 | 0.888 | 1.1 | 1.25 | -0.00341
LFNoneSCEs_IndExCZ15 | Com-Iltg-dWatt-LF_OSnone | SCE | s_Ind | Ex | CZ15 | 3.375 | 0.0008875 | 0 | 3.955 | 0.0011 | -0.00097 | 3.375 | 0.0008875 | 0 | 3.955 | 0.0011 | -0.00097 |  | LF | None | 3380 | 0.888 | 3380 | 0.888 | 1.17 | 1.24 | -0.00028741 | 3380 | 0.888 | 3380 | 0.888 | 1.17 | 1.24 | -0.000287
LFNoneSCEs_IndExCZ16 | Com-Iltg-dWatt-LF_OSnone | SCE | s_Ind | Ex | CZ16 | 3.375 | 0.0008875 | 0 | 3.48 | 0.00106 | -0.024485 | 3.375 | 0.0008875 | 0 | 3.48 | 0.00106 | -0.024485 |  | LF | None | 3380 | 0.888 | 3380 | 0.888 | 1.03 | 1.19 | -0.0072548 | 3380 | 0.888 | 3380 | 0.888 | 1.03 | 1.19 | -0.00725
LFNoneSCEs_IndExIOU | Com-Iltg-dWatt-LF_OSnone | SCE | s_Ind | Ex | IOU | 3.375 | 0.0008875 | 0 | 3.836 | 0.0010941 | -0.0041566 | 3.375 | 0.0008875 | 0 | 3.836 | 0.0010941 | -0.0041566 |  | LF | None | 3380 | 0.888 | 3380 | 0.888 | 1.14 | 1.23 | -0.0012316 | 3380 | 0.888 | 3380 | 0.888 | 1.14 | 1.23 | -0.00123
LFNoneSCEs_MiCExCZ05 | Com-Iltg-dWatt-LF_OSnone | SCE | s_MiC | Ex | CZ05 | 3.6033 | 0.00079033 | 0 | 3.83 | 0.00097167 | -0.026927 | 3.6033 | 0.00079033 | 0 | 3.83 | 0.00097167 | -0.026927 |  | LF | None | 3600 | 0.79 | 3600 | 0.79 | 1.06 | 1.23 | -0.0074727 | 3600 | 0.79 | 3600 | 0.79 | 1.06 | 1.23 | -0.00747
LFNoneSCEs_MiCExCZ06 | Com-Iltg-dWatt-LF_OSnone | SCE | s_MiC | Ex | CZ06 | 3.6033 | 0.00079033 | 0 | 4.0633 | 0.00098167 | -0.012893 | 3.6033 | 0.00079033 | 0 | 4.0633 | 0.00098167 | -0.012893 |  | LF | None | 3600 | 0.79 | 3600 | 0.79 | 1.13 | 1.24 | -0.0035782 | 3600 | 0.79 | 3600 | 0.79 | 1.13 | 1.24 | -0.00358
LFNoneSCEs_MiCExCZ08 | Com-Iltg-dWatt-LF_OSnone | SCE | s_MiC | Ex | CZ08 | 3.6033 | 0.00079033 | 0 | 4.0867 | 0.000974 | -0.010837 | 3.6033 | 0.00079033 | 0 | 4.0867 | 0.000974 | -0.010837 |  | LF | None | 3600 | 0.79 | 3600 | 0.79 | 1.13 | 1.23 | -0.0030074 | 3600 | 0.79 | 3600 | 0.79 | 1.13 | 1.23 | -0.00301
LFNoneSCEs_MiCExCZ09 | Com-Iltg-dWatt-LF_OSnone | SCE | s_MiC | Ex | CZ09 | 3.6033 | 0.00079033 | 0 | 4.0667 | 0.00098633 | -0.01266 | 3.6033 | 0.00079033 | 0 | 4.0667 | 0.00098633 | -0.01266 |  | LF | None | 3600 | 0.79 | 3600 | 0.79 | 1.13 | 1.25 | -0.0035134 | 3600 | 0.79 | 3600 | 0.79 | 1.13 | 1.25 | -0.00351
LFNoneSCEs_MiCExCZ10 | Com-Iltg-dWatt-LF_OSnone | SCE | s_MiC | Ex | CZ10 | 3.6033 | 0.00079033 | 0 | 4.0033 | 0.00096033 | -0.013227 | 3.6033 | 0.00079033 | 0 | 4.0033 | 0.00096033 | -0.013227 |  | LF | None | 3600 | 0.79 | 3600 | 0.79 | 1.11 | 1.22 | -0.0036707 | 3600 | 0.79 | 3600 | 0.79 | 1.11 | 1.22 | -0.00367
LFNoneSCEs_MiCExCZ13 | Com-Iltg-dWatt-LF_OSnone | SCE | s_MiC | Ex | CZ13 | 3.6033 | 0.00079033 | 0 | 3.93 | 0.000986 | -0.024257 | 3.6033 | 0.00079033 | 0 | 3.93 | 0.000986 | -0.024257 |  | LF | None | 3600 | 0.79 | 3600 | 0.79 | 1.09 | 1.25 | -0.0067317 | 3600 | 0.79 | 3600 | 0.79 | 1.09 | 1.25 | -0.00673
LFNoneSCEs_MiCExCZ14 | Com-Iltg-dWatt-LF_OSnone | SCE | s_MiC | Ex | CZ14 | 3.6033 | 0.00079033 | 0 | 3.9133 | 0.000965 | -0.023757 | 3.6033 | 0.00079033 | 0 | 3.9133 | 0.000965 | -0.023757 |  | LF | None | 3600 | 0.79 | 3600 | 0.79 | 1.09 | 1.22 | -0.006593 | 3600 | 0.79 | 3600 | 0.79 | 1.09 | 1.22 | -0.00659
LFNoneSCEs_MiCExCZ15 | Com-Iltg-dWatt-LF_OSnone | SCE | s_MiC | Ex | CZ15 | 3.6033 | 0.00079033 | 0 | 4.25 | 0.00099133 | -0.0047567 | 3.6033 | 0.00079033 | 0 | 4.25 | 0.00099133 | -0.0047567 |  | LF | None | 3600 | 0.79 | 3600 | 0.79 | 1.18 | 1.25 | -0.0013201 | 3600 | 0.79 | 3600 | 0.79 | 1.18 | 1.25 | -0.00132
LFNoneSCEs_MiCExCZ16 | Com-Iltg-dWatt-LF_OSnone | SCE | s_MiC | Ex | CZ16 | 3.6033 | 0.00079033 | 0 | 3.59 | 0.00095333 | -0.044767 | 3.6033 | 0.00079033 | 0 | 3.59 | 0.00095333 | -0.044767 |  | LF | None | 3600 | 0.79 | 3600 | 0.79 | 0.996 | 1.21 | -0.012424 | 3600 | 0.79 | 3600 | 0.79 | 0.996 | 1.21 | -0.0124
LFNoneSCEs_MiCExIOU | Com-Iltg-dWatt-LF_OSnone | SCE | s_MiC | Ex | IOU | 3.6033 | 0.00079033 | 0 | 4.0475 | 0.00097458 | -0.013325 | 3.6033 | 0.00079033 | 0 | 4.0475 | 0.00097458 | -0.013325 |  | LF | None | 3600 | 0.79 | 3600 | 0.79 | 1.12 | 1.23 | -0.0036979 | 3600 | 0.79 | 3600 | 0.79 | 1.12 | 1.23 | -0.0037
LFNoneSCEs_TCUExCZ05 | Com-Iltg-dWatt-LF_OSnone | SCE | s_TCU | Ex | CZ05 | 3.058 | 0.0007456 | 0 | 3.15 | 0.000898 | -0.015856 | 3.058 | 0.0007456 | 0 | 3.15 | 0.000898 | -0.015856 |  | LF | None | 3060 | 0.746 | 3060 | 0.746 | 1.03 | 1.2 | -0.0051851 | 3060 | 0.746 | 3060 | 0.746 | 1.03 | 1.2 | -0.00519
LFNoneSCEs_TCUExCZ06 | Com-Iltg-dWatt-LF_OSnone | SCE | s_TCU | Ex | CZ06 | 3.058 | 0.0007456 | 0 | 3.316 | 0.000908 | -0.008074 | 3.058 | 0.0007456 | 0 | 3.316 | 0.000908 | -0.008074 |  | LF | None | 3060 | 0.746 | 3060 | 0.746 | 1.08 | 1.22 | -0.0026403 | 3060 | 0.746 | 3060 | 0.746 | 1.08 | 1.22 | -0.00264
LFNoneSCEs_TCUExCZ08 | Com-Iltg-dWatt-LF_OSnone | SCE | s_TCU | Ex | CZ08 | 3.058 | 0.0007456 | 0 | 3.336 | 0.0009106 | -0.007264 | 3.058 | 0.0007456 | 0 | 3.336 | 0.0009106 | -0.007264 |  | LF | None | 3060 | 0.746 | 3060 | 0.746 | 1.09 | 1.22 | -0.0023754 | 3060 | 0.746 | 3060 | 0.746 | 1.09 | 1.22 | -0.00238
LFNoneSCEs_TCUExCZ09 | Com-Iltg-dWatt-LF_OSnone | SCE | s_TCU | Ex | CZ09 | 3.058 | 0.0007456 | 0 | 3.324 | 0.0009228 | -0.00878 | 3.058 | 0.0007456 | 0 | 3.324 | 0.0009228 | -0.00878 |  | LF | None | 3060 | 0.746 | 3060 | 0.746 | 1.09 | 1.24 | -0.0028712 | 3060 | 0.746 | 3060 | 0.746 | 1.09 | 1.24 | -0.00287
LFNoneSCEs_TCUExCZ10 | Com-Iltg-dWatt-LF_OSnone | SCE | s_TCU | Ex | CZ10 | 3.058 | 0.0007456 | 0 | 3.292 | 0.0009144 | -0.00854 | 3.058 | 0.0007456 | 0 | 3.292 | 0.0009144 | -0.00854 |  | LF | None | 3060 | 0.746 | 3060 | 0.746 | 1.08 | 1.23 | -0.0027927 | 3060 | 0.746 | 3060 | 0.746 | 1.08 | 1.23 | -0.00279
LFNoneSCEs_TCUExCZ13 | Com-Iltg-dWatt-LF_OSnone | SCE | s_TCU | Ex | CZ13 | 3.058 | 0.0007456 | 0 | 3.254 | 0.0009054 | -0.014014 | 3.058 | 0.0007456 | 0 | 3.254 | 0.0009054 | -0.014014 |  | LF | None | 3060 | 0.746 | 3060 | 0.746 | 1.06 | 1.21 | -0.0045827 | 3060 | 0.746 | 3060 | 0.746 | 1.06 | 1.21 | -0.00458
LFNoneSCEs_TCUExCZ14 | Com-Iltg-dWatt-LF_OSnone | SCE | s_TCU | Ex | CZ14 | 3.058 | 0.0007456 | 0 | 3.244 | 0.0009142 | -0.014374 | 3.058 | 0.0007456 | 0 | 3.244 | 0.0009142 | -0.014374 |  | LF | None | 3060 | 0.746 | 3060 | 0.746 | 1.06 | 1.23 | -0.0047005 | 3060 | 0.746 | 3060 | 0.746 | 1.06 | 1.23 | -0.0047
LFNoneSCEs_TCUExCZ15 | Com-Iltg-dWatt-LF_OSnone | SCE | s_TCU | Ex | CZ15 | 3.058 | 0.0007456 | 0 | 3.458 | 0.0009098 | -0.003648 | 3.058 | 0.0007456 | 0 | 3.458 | 0.0009098 | -0.003648 |  | LF | None | 3060 | 0.746 | 3060 | 0.746 | 1.13 | 1.22 | -0.0011929 | 3060 | 0.746 | 3060 | 0.746 | 1.13 | 1.22 | -0.00119
LFNoneSCEs_TCUExCZ16 | Com-Iltg-dWatt-LF_OSnone | SCE | s_TCU | Ex | CZ16 | 3.058 | 0.0007456 | 0 | 3.032 | 0.0008892 | -0.0254 | 3.058 | 0.0007456 | 0 | 3.032 | 0.0008892 | -0.0254 |  | LF | None | 3060 | 0.746 | 3060 | 0.746 | 0.991 | 1.19 | -0.0083061 | 3060 | 0.746 | 3060 | 0.746 | 0.991 | 1.19 | -0.00831
LFNoneSCEs_TCUExIOU | Com-Iltg-dWatt-LF_OSnone | SCE | s_TCU | Ex | IOU | 3.058 | 0.0007456 | 0 | 3.317 | 0.00091214 | -0.0084819 | 3.058 | 0.0007456 | 0 | 3.317 | 0.00091214 | -0.0084819 |  | LF | None | 3060 | 0.746 | 3060 | 0.746 | 1.08 | 1.22 | -0.0027737 | 3060 | 0.746 | 3060 | 0.746 | 1.08 | 1.22 | -0.00277
LFNoneSCESCnExCZ05 | Com-Iltg-dWatt-LF_OSnone | SCE | SCn | Ex | CZ05 | 3.42 | 0.0007 | 0 | 3.16 | 0.000885 | -0.0359 | 3.42 | 0.0007 | 0 | 3.16 | 0.000885 | -0.0359 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 0.924 | 1.26 | -0.010497 | 3420 | 0.7 | 3420 | 0.7 | 0.924 | 1.26 | -0.0105
LFNoneSCESCnExCZ06 | Com-Iltg-dWatt-LF_OSnone | SCE | SCn | Ex | CZ06 | 3.42 | 0.0007 | 0 | 3.53 | 0.000917 | -0.0189 | 3.42 | 0.0007 | 0 | 3.53 | 0.000917 | -0.0189 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 1.03 | 1.31 | -0.0055263 | 3420 | 0.7 | 3420 | 0.7 | 1.03 | 1.31 | -0.00553
LFNoneSCESCnExCZ08 | Com-Iltg-dWatt-LF_OSnone | SCE | SCn | Ex | CZ08 | 3.42 | 0.0007 | 0 | 3.59 | 0.000914 | -0.0163 | 3.42 | 0.0007 | 0 | 3.59 | 0.000914 | -0.0163 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 1.05 | 1.31 | -0.0047661 | 3420 | 0.7 | 3420 | 0.7 | 1.05 | 1.31 | -0.00477
LFNoneSCESCnExCZ09 | Com-Iltg-dWatt-LF_OSnone | SCE | SCn | Ex | CZ09 | 3.42 | 0.0007 | 0 | 3.57 | 0.000931 | -0.0192 | 3.42 | 0.0007 | 0 | 3.57 | 0.000931 | -0.0192 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 1.04 | 1.33 | -0.005614 | 3420 | 0.7 | 3420 | 0.7 | 1.04 | 1.33 | -0.00561
LFNoneSCESCnExCZ10 | Com-Iltg-dWatt-LF_OSnone | SCE | SCn | Ex | CZ10 | 3.42 | 0.0007 | 0 | 3.56 | 0.000918 | -0.0201 | 3.42 | 0.0007 | 0 | 3.56 | 0.000918 | -0.0201 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 1.04 | 1.31 | -0.0058772 | 3420 | 0.7 | 3420 | 0.7 | 1.04 | 1.31 | -0.00588
LFNoneSCESCnExCZ13 | Com-Iltg-dWatt-LF_OSnone | SCE | SCn | Ex | CZ13 | 3.42 | 0.0007 | 0 | 3.49 | 0.000906 | -0.0267 | 3.42 | 0.0007 | 0 | 3.49 | 0.000906 | -0.0267 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 1.02 | 1.29 | -0.007807 | 3420 | 0.7 | 3420 | 0.7 | 1.02 | 1.29 | -0.00781
LFNoneSCESCnExCZ14 | Com-Iltg-dWatt-LF_OSnone | SCE | SCn | Ex | CZ14 | 3.42 | 0.0007 | 0 | 3.47 | 0.000905 | -0.0294 | 3.42 | 0.0007 | 0 | 3.47 | 0.000905 | -0.0294 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 1.01 | 1.29 | -0.0085965 | 3420 | 0.7 | 3420 | 0.7 | 1.01 | 1.29 | -0.0086
LFNoneSCESCnExCZ15 | Com-Iltg-dWatt-LF_OSnone | SCE | SCn | Ex | CZ15 | 3.42 | 0.0007 | 0 | 3.8 | 0.000909 | -0.00804 | 3.42 | 0.0007 | 0 | 3.8 | 0.000909 | -0.00804 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 1.11 | 1.3 | -0.0023509 | 3420 | 0.7 | 3420 | 0.7 | 1.11 | 1.3 | -0.00235
LFNoneSCESCnExCZ16 | Com-Iltg-dWatt-LF_OSnone | SCE | SCn | Ex | CZ16 | 3.42 | 0.0007 | 0 | 3.12 | 0.00088 | -0.0421 | 3.42 | 0.0007 | 0 | 3.12 | 0.00088 | -0.0421 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 0.912 | 1.26 | -0.01231 | 3420 | 0.7 | 3420 | 0.7 | 0.912 | 1.26 | -0.0123
LFNoneSCESCnExIOU | Com-Iltg-dWatt-LF_OSnone | SCE | SCn | Ex | IOU | 3.42 | 0.0007 | 0 | 3.566 | 0.00091704 | -0.018558 | 3.42 | 0.0007 | 0 | 3.566 | 0.00091704 | -0.018558 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 1.04 | 1.31 | -0.0054262 | 3420 | 0.7 | 3420 | 0.7 | 1.04 | 1.31 | -0.00543
LFNoneSCESCnNewCZ05 | Com-Iltg-dWatt-LF_OSnone | SCE | SCn | New | CZ05 | 3.42 | 0.0007 | 0 | 3.18 | 0.000883 | -0.038 | 3.42 | 0.0007 | 0 | 3.18 | 0.000883 | -0.038 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 0.93 | 1.26 | -0.011111 | 3420 | 0.7 | 3420 | 0.7 | 0.93 | 1.26 | -0.0111
LFNoneSCESCnNewCZ06 | Com-Iltg-dWatt-LF_OSnone | SCE | SCn | New | CZ06 | 3.42 | 0.0007 | 0 | 3.43 | 0.000846 | -0.0202 | 3.42 | 0.0007 | 0 | 3.43 | 0.000846 | -0.0202 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 1 | 1.21 | -0.0059064 | 3420 | 0.7 | 3420 | 0.7 | 1 | 1.21 | -0.00591
LFNoneSCESCnNewCZ08 | Com-Iltg-dWatt-LF_OSnone | SCE | SCn | New | CZ08 | 3.42 | 0.0007 | 0 | 3.51 | 0.00086 | -0.0176 | 3.42 | 0.0007 | 0 | 3.51 | 0.00086 | -0.0176 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 1.03 | 1.23 | -0.0051462 | 3420 | 0.7 | 3420 | 0.7 | 1.03 | 1.23 | -0.00515
LFNoneSCESCnNewCZ09 | Com-Iltg-dWatt-LF_OSnone | SCE | SCn | New | CZ09 | 3.42 | 0.0007 | 0 | 3.51 | 0.000889 | -0.0189 | 3.42 | 0.0007 | 0 | 3.51 | 0.000889 | -0.0189 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 1.03 | 1.27 | -0.0055263 | 3420 | 0.7 | 3420 | 0.7 | 1.03 | 1.27 | -0.00553
LFNoneSCESCnNewCZ10 | Com-Iltg-dWatt-LF_OSnone | SCE | SCn | New | CZ10 | 3.42 | 0.0007 | 0 | 3.52 | 0.000881 | -0.0205 | 3.42 | 0.0007 | 0 | 3.52 | 0.000881 | -0.0205 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 1.03 | 1.26 | -0.0059942 | 3420 | 0.7 | 3420 | 0.7 | 1.03 | 1.26 | -0.00599
LFNoneSCESCnNewCZ13 | Com-Iltg-dWatt-LF_OSnone | SCE | SCn | New | CZ13 | 3.42 | 0.0007 | 0 | 3.41 | 0.000857 | -0.0269 | 3.42 | 0.0007 | 0 | 3.41 | 0.000857 | -0.0269 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 0.997 | 1.22 | -0.0078655 | 3420 | 0.7 | 3420 | 0.7 | 0.997 | 1.22 | -0.00787
LFNoneSCESCnNewCZ14 | Com-Iltg-dWatt-LF_OSnone | SCE | SCn | New | CZ14 | 3.42 | 0.0007 | 0 | 3.45 | 0.000878 | -0.0301 | 3.42 | 0.0007 | 0 | 3.45 | 0.000878 | -0.0301 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 1.01 | 1.25 | -0.0088012 | 3420 | 0.7 | 3420 | 0.7 | 1.01 | 1.25 | -0.0088
LFNoneSCESCnNewCZ15 | Com-Iltg-dWatt-LF_OSnone | SCE | SCn | New | CZ15 | 3.42 | 0.0007 | 0 | 3.74 | 0.000885 | -0.00643 | 3.42 | 0.0007 | 0 | 3.74 | 0.000885 | -0.00643 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 1.09 | 1.26 | -0.0018801 | 3420 | 0.7 | 3420 | 0.7 | 1.09 | 1.26 | -0.00188
LFNoneSCESCnNewCZ16 | Com-Iltg-dWatt-LF_OSnone | SCE | SCn | New | CZ16 | 3.42 | 0.0007 | 0 | 3.1 | 0.000848 | -0.0438 | 3.42 | 0.0007 | 0 | 3.1 | 0.000848 | -0.0438 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 0.906 | 1.21 | -0.012807 | 3420 | 0.7 | 3420 | 0.7 | 0.906 | 1.21 | -0.0128
LFNoneSCESCnNewIOU | Com-Iltg-dWatt-LF_OSnone | SCE | SCn | New | IOU | 3.42 | 0.0007 | 0 | 3.5062 | 0.00087425 | -0.020182 | 3.42 | 0.0007 | 0 | 3.5062 | 0.00087425 | -0.020182 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 1.03 | 1.25 | -0.0059011 | 3420 | 0.7 | 3420 | 0.7 | 1.03 | 1.25 | -0.0059
LFNoneSCESUnExCZ05 | Com-Iltg-dWatt-LF_OSnone | SCE | SUn | Ex | CZ05 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0 | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0
LFNoneSCESUnExCZ06 | Com-Iltg-dWatt-LF_OSnone | SCE | SUn | Ex | CZ06 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0 | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0
LFNoneSCESUnExCZ08 | Com-Iltg-dWatt-LF_OSnone | SCE | SUn | Ex | CZ08 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0 | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0
LFNoneSCESUnExCZ09 | Com-Iltg-dWatt-LF_OSnone | SCE | SUn | Ex | CZ09 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0 | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0
LFNoneSCESUnExCZ10 | Com-Iltg-dWatt-LF_OSnone | SCE | SUn | Ex | CZ10 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0 | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0
LFNoneSCESUnExCZ13 | Com-Iltg-dWatt-LF_OSnone | SCE | SUn | Ex | CZ13 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0 | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0
LFNoneSCESUnExCZ14 | Com-Iltg-dWatt-LF_OSnone | SCE | SUn | Ex | CZ14 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0 | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0
LFNoneSCESUnExCZ15 | Com-Iltg-dWatt-LF_OSnone | SCE | SUn | Ex | CZ15 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0 | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0
LFNoneSCESUnExCZ16 | Com-Iltg-dWatt-LF_OSnone | SCE | SUn | Ex | CZ16 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0 | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0
LFNoneSCESUnExIOU | Com-Iltg-dWatt-LF_OSnone | SCE | SUn | Ex | IOU | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0 | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0
LFNoneSCESUnNewCZ05 | Com-Iltg-dWatt-LF_OSnone | SCE | SUn | New | CZ05 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0 | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0
LFNoneSCESUnNewCZ06 | Com-Iltg-dWatt-LF_OSnone | SCE | SUn | New | CZ06 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0 | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0
LFNoneSCESUnNewCZ08 | Com-Iltg-dWatt-LF_OSnone | SCE | SUn | New | CZ08 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0 | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0
LFNoneSCESUnNewCZ09 | Com-Iltg-dWatt-LF_OSnone | SCE | SUn | New | CZ09 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0 | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0
LFNoneSCESUnNewCZ10 | Com-Iltg-dWatt-LF_OSnone | SCE | SUn | New | CZ10 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0 | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0
LFNoneSCESUnNewCZ13 | Com-Iltg-dWatt-LF_OSnone | SCE | SUn | New | CZ13 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0 | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0
LFNoneSCESUnNewCZ14 | Com-Iltg-dWatt-LF_OSnone | SCE | SUn | New | CZ14 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0 | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0
LFNoneSCESUnNewCZ15 | Com-Iltg-dWatt-LF_OSnone | SCE | SUn | New | CZ15 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0 | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0
LFNoneSCESUnNewCZ16 | Com-Iltg-dWatt-LF_OSnone | SCE | SUn | New | CZ16 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0 | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0
LFNoneSCESUnNewIOU | Com-Iltg-dWatt-LF_OSnone | SCE | SUn | New | IOU | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0 | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0
LFNoneSCEWRfExCZ06 | Com-Iltg-dWatt-LF_OSnone | SCE | WRf | Ex | CZ06 | 4.77 | 0.000556 | 0 | 7.53 | 0.000697 | 0 | 4.77 | 0.000556 | 0 | 7.53 | 0.000697 | 0 |  | LF | None | 4770 | 0.556 | 4770 | 0.556 | 1.58 | 1.25 | 0 | 4770 | 0.556 | 4770 | 0.556 | 1.58 | 1.25 | 0
LFNoneSCEWRfExCZ08 | Com-Iltg-dWatt-LF_OSnone | SCE | WRf | Ex | CZ08 | 4.77 | 0.000556 | 0 | 7.62 | 0.000698 | 0 | 4.77 | 0.000556 | 0 | 7.62 | 0.000698 | 0 |  | LF | None | 4770 | 0.556 | 4770 | 0.556 | 1.6 | 1.26 | 0 | 4770 | 0.556 | 4770 | 0.556 | 1.6 | 1.26 | 0
LFNoneSCEWRfExCZ09 | Com-Iltg-dWatt-LF_OSnone | SCE | WRf | Ex | CZ09 | 4.77 | 0.000556 | 0 | 7.57 | 0.000713 | 0 | 4.77 | 0.000556 | 0 | 7.57 | 0.000713 | 0 |  | LF | None | 4770 | 0.556 | 4770 | 0.556 | 1.59 | 1.28 | 0 | 4770 | 0.556 | 4770 | 0.556 | 1.59 | 1.28 | 0
LFNoneSCEWRfExCZ10 | Com-Iltg-dWatt-LF_OSnone | SCE | WRf | Ex | CZ10 | 4.77 | 0.000556 | 0 | 7.54 | 0.000703 | 0 | 4.77 | 0.000556 | 0 | 7.54 | 0.000703 | 0 |  | LF | None | 4770 | 0.556 | 4770 | 0.556 | 1.58 | 1.26 | 0 | 4770 | 0.556 | 4770 | 0.556 | 1.58 | 1.26 | 0
LFNoneSCEWRfExCZ13 | Com-Iltg-dWatt-LF_OSnone | SCE | WRf | Ex | CZ13 | 4.77 | 0.000556 | 0 | 7.4 | 0.000701 | 0 | 4.77 | 0.000556 | 0 | 7.4 | 0.000701 | 0 |  | LF | None | 4770 | 0.556 | 4770 | 0.556 | 1.55 | 1.26 | 0 | 4770 | 0.556 | 4770 | 0.556 | 1.55 | 1.26 | 0
LFNoneSCEWRfExCZ14 | Com-Iltg-dWatt-LF_OSnone | SCE | WRf | Ex | CZ14 | 4.77 | 0.000556 | 0 | 7.26 | 0.000698 | 0 | 4.77 | 0.000556 | 0 | 7.26 | 0.000698 | 0 |  | LF | None | 4770 | 0.556 | 4770 | 0.556 | 1.52 | 1.26 | 0 | 4770 | 0.556 | 4770 | 0.556 | 1.52 | 1.26 | 0
LFNoneSCEWRfExCZ15 | Com-Iltg-dWatt-LF_OSnone | SCE | WRf | Ex | CZ15 | 4.77 | 0.000556 | 0 | 7.77 | 0.000703 | 0 | 4.77 | 0.000556 | 0 | 7.77 | 0.000703 | 0 |  | LF | None | 4770 | 0.556 | 4770 | 0.556 | 1.63 | 1.26 | 0 | 4770 | 0.556 | 4770 | 0.556 | 1.63 | 1.26 | 0
LFNoneSCEWRfExCZ16 | Com-Iltg-dWatt-LF_OSnone | SCE | WRf | Ex | CZ16 | 4.77 | 0.000556 | 0 | 6.6 | 0.000792 | -0.000163 | 4.77 | 0.000556 | 0 | 6.6 | 0.000792 | -0.000163 |  | LF | None | 4770 | 0.556 | 4770 | 0.556 | 1.38 | 1.42 | -3.4172e-05 | 4770 | 0.556 | 4770 | 0.556 | 1.38 | 1.42 | -3.42e-05
LFNoneSCEWRfExIOU | Com-Iltg-dWatt-LF_OSnone | SCE | WRf | Ex | IOU | 4.77 | 0.000556 | 0 | 7.5434 | 0.00070088 | -5.2358e-07 | 4.77 | 0.000556 | 0 | 7.5434 | 0.00070088 | -5.2358e-07 |  | LF | None | 4770 | 0.556 | 4770 | 0.556 | 1.58 | 1.26 | -1.0977e-07 | 4770 | 0.556 | 4770 | 0.556 | 1.58 | 1.26 | -1.1e-07
LFNoneSCEWRfNewCZ05 | Com-Iltg-dWatt-LF_OSnone | SCE | WRf | New | CZ05 | 4.77 | 0.000556 | 0 | 6.17 | 0.000924 | 0 | 4.77 | 0.000556 | 0 | 6.17 | 0.000924 | 0 |  | LF | None | 4770 | 0.556 | 4770 | 0.556 | 1.29 | 1.66 | 0 | 4770 | 0.556 | 4770 | 0.556 | 1.29 | 1.66 | 0
LFNoneSCEWRfNewCZ06 | Com-Iltg-dWatt-LF_OSnone | SCE | WRf | New | CZ06 | 4.77 | 0.000556 | 0 | 6.87 | 0.000686 | 0 | 4.77 | 0.000556 | 0 | 6.87 | 0.000686 | 0 |  | LF | None | 4770 | 0.556 | 4770 | 0.556 | 1.44 | 1.23 | 0 | 4770 | 0.556 | 4770 | 0.556 | 1.44 | 1.23 | 0
LFNoneSCEWRfNewCZ08 | Com-Iltg-dWatt-LF_OSnone | SCE | WRf | New | CZ08 | 4.77 | 0.000556 | 0 | 6.79 | 0.000688 | 0 | 4.77 | 0.000556 | 0 | 6.79 | 0.000688 | 0 |  | LF | None | 4770 | 0.556 | 4770 | 0.556 | 1.42 | 1.24 | 0 | 4770 | 0.556 | 4770 | 0.556 | 1.42 | 1.24 | 0
LFNoneSCEWRfNewCZ09 | Com-Iltg-dWatt-LF_OSnone | SCE | WRf | New | CZ09 | 4.77 | 0.000556 | 0 | 6.73 | 0.00071 | 0 | 4.77 | 0.000556 | 0 | 6.73 | 0.00071 | 0 |  | LF | None | 4770 | 0.556 | 4770 | 0.556 | 1.41 | 1.28 | 0 | 4770 | 0.556 | 4770 | 0.556 | 1.41 | 1.28 | 0
LFNoneSCEWRfNewCZ10 | Com-Iltg-dWatt-LF_OSnone | SCE | WRf | New | CZ10 | 4.77 | 0.000556 | 0 | 6.7 | 0.000696 | 0 | 4.77 | 0.000556 | 0 | 6.7 | 0.000696 | 0 |  | LF | None | 4770 | 0.556 | 4770 | 0.556 | 1.4 | 1.25 | 0 | 4770 | 0.556 | 4770 | 0.556 | 1.4 | 1.25 | 0
LFNoneSCEWRfNewCZ13 | Com-Iltg-dWatt-LF_OSnone | SCE | WRf | New | CZ13 | 4.77 | 0.000556 | 0 | 6.69 | 0.000696 | 0 | 4.77 | 0.000556 | 0 | 6.69 | 0.000696 | 0 |  | LF | None | 4770 | 0.556 | 4770 | 0.556 | 1.4 | 1.25 | 0 | 4770 | 0.556 | 4770 | 0.556 | 1.4 | 1.25 | 0
LFNoneSCEWRfNewCZ14 | Com-Iltg-dWatt-LF_OSnone | SCE | WRf | New | CZ14 | 4.77 | 0.000556 | 0 | 6.56 | 0.000689 | 0 | 4.77 | 0.000556 | 0 | 6.56 | 0.000689 | 0 |  | LF | None | 4770 | 0.556 | 4770 | 0.556 | 1.38 | 1.24 | 0 | 4770 | 0.556 | 4770 | 0.556 | 1.38 | 1.24 | 0
LFNoneSCEWRfNewCZ15 | Com-Iltg-dWatt-LF_OSnone | SCE | WRf | New | CZ15 | 4.77 | 0.000556 | 0 | 7.01 | 0.000694 | 0 | 4.77 | 0.000556 | 0 | 7.01 | 0.000694 | 0 |  | LF | None | 4770 | 0.556 | 4770 | 0.556 | 1.47 | 1.25 | 0 | 4770 | 0.556 | 4770 | 0.556 | 1.47 | 1.25 | 0
LFNoneSCEWRfNewCZ16 | Com-Iltg-dWatt-LF_OSnone | SCE | WRf | New | CZ16 | 4.77 | 0.000556 | 0 | 6.01 | 0.00111 | 0 | 4.77 | 0.000556 | 0 | 6.01 | 0.00111 | 0 |  | LF | None | 4770 | 0.556 | 4770 | 0.556 | 1.26 | 2 | 0 | 4770 | 0.556 | 4770 | 0.556 | 1.26 | 2 | 0
LFNoneSCEWRfNewIOU | Com-Iltg-dWatt-LF_OSnone | SCE | WRf | New | IOU | 4.77 | 0.000556 | 0 | 6.7543 | 0.00069543 | 0 | 4.77 | 0.000556 | 0 | 6.7543 | 0.00069543 | 0 |  | LF | None | 4770 | 0.556 | 4770 | 0.556 | 1.42 | 1.25 | 0 | 4770 | 0.556 | 4770 | 0.556 | 1.42 | 1.25 | 0
LFNoneSDGAsmExCZ06 | Com-Iltg-dWatt-LF_OSnone | SDG | Asm | Ex | CZ06 | 2.61 | 0.000532 | 0 | 2.87 | 0.000656 | -0.0146 | 2.61 | 0.000532 | 0 | 2.87 | 0.000656 | -0.0146 |  | LF | None | 2610 | 0.532 | 2610 | 0.532 | 1.1 | 1.23 | -0.0055939 | 2610 | 0.532 | 2610 | 0.532 | 1.1 | 1.23 | -0.00559
LFNoneSDGAsmExCZ07 | Com-Iltg-dWatt-LF_OSnone | SDG | Asm | Ex | CZ07 | 2.61 | 0.000532 | 0 | 2.88 | 0.000655 | -0.0135 | 2.61 | 0.000532 | 0 | 2.88 | 0.000655 | -0.0135 |  | LF | None | 2610 | 0.532 | 2610 | 0.532 | 1.1 | 1.23 | -0.0051724 | 2610 | 0.532 | 2610 | 0.532 | 1.1 | 1.23 | -0.00517
LFNoneSDGAsmExCZ08 | Com-Iltg-dWatt-LF_OSnone | SDG | Asm | Ex | CZ08 | 2.61 | 0.000532 | 0 | 2.9 | 0.000637 | -0.0123 | 2.61 | 0.000532 | 0 | 2.9 | 0.000637 | -0.0123 |  | LF | None | 2610 | 0.532 | 2610 | 0.532 | 1.11 | 1.2 | -0.0047126 | 2610 | 0.532 | 2610 | 0.532 | 1.11 | 1.2 | -0.00471
LFNoneSDGAsmExCZ10 | Com-Iltg-dWatt-LF_OSnone | SDG | Asm | Ex | CZ10 | 2.61 | 0.000532 | 0 | 2.87 | 0.000644 | -0.0157 | 2.61 | 0.000532 | 0 | 2.87 | 0.000644 | -0.0157 |  | LF | None | 2610 | 0.532 | 2610 | 0.532 | 1.1 | 1.21 | -0.0060153 | 2610 | 0.532 | 2610 | 0.532 | 1.1 | 1.21 | -0.00602
LFNoneSDGAsmExCZ14 | Com-Iltg-dWatt-LF_OSnone | SDG | Asm | Ex | CZ14 | 2.61 | 0.000532 | 0 | 2.79 | 0.000603 | -0.0252 | 2.61 | 0.000532 | 0 | 2.79 | 0.000603 | -0.0252 |  | LF | None | 2610 | 0.532 | 2610 | 0.532 | 1.07 | 1.13 | -0.0096552 | 2610 | 0.532 | 2610 | 0.532 | 1.07 | 1.13 | -0.00966
LFNoneSDGAsmExCZ15 | Com-Iltg-dWatt-LF_OSnone | SDG | Asm | Ex | CZ15 | 2.61 | 0.000532 | 0 | 3.16 | 0.000637 | -0.00697 | 2.61 | 0.000532 | 0 | 3.16 | 0.000637 | -0.00697 |  | LF | None | 2610 | 0.532 | 2610 | 0.532 | 1.21 | 1.2 | -0.0026705 | 2610 | 0.532 | 2610 | 0.532 | 1.21 | 1.2 | -0.00267
LFNoneSDGAsmExIOU | Com-Iltg-dWatt-LF_OSnone | SDG | Asm | Ex | IOU | 2.61 | 0.000532 | 0 | 2.877 | 0.00065078 | -0.01427 | 2.61 | 0.000532 | 0 | 2.877 | 0.00065078 | -0.01427 |  | LF | None | 2610 | 0.532 | 2610 | 0.532 | 1.1 | 1.22 | -0.0054675 | 2610 | 0.532 | 2610 | 0.532 | 1.1 | 1.22 | -0.00547
LFNoneSDGAsmNewCZ06 | Com-Iltg-dWatt-LF_OSnone | SDG | Asm | New | CZ06 | 2.61 | 0.000532 | 0 | 2.84 | 0.000652 | -0.0178 | 2.61 | 0.000532 | 0 | 2.84 | 0.000652 | -0.0178 |  | LF | None | 2610 | 0.532 | 2610 | 0.532 | 1.09 | 1.23 | -0.0068199 | 2610 | 0.532 | 2610 | 0.532 | 1.09 | 1.23 | -0.00682
LFNoneSDGAsmNewCZ07 | Com-Iltg-dWatt-LF_OSnone | SDG | Asm | New | CZ07 | 2.61 | 0.000532 | 0 | 2.86 | 0.000652 | -0.0163 | 2.61 | 0.000532 | 0 | 2.86 | 0.000652 | -0.0163 |  | LF | None | 2610 | 0.532 | 2610 | 0.532 | 1.1 | 1.23 | -0.0062452 | 2610 | 0.532 | 2610 | 0.532 | 1.1 | 1.23 | -0.00625
LFNoneSDGAsmNewCZ08 | Com-Iltg-dWatt-LF_OSnone | SDG | Asm | New | CZ08 | 2.61 | 0.000532 | 0 | 2.87 | 0.000643 | -0.0146 | 2.61 | 0.000532 | 0 | 2.87 | 0.000643 | -0.0146 |  | LF | None | 2610 | 0.532 | 2610 | 0.532 | 1.1 | 1.21 | -0.0055939 | 2610 | 0.532 | 2610 | 0.532 | 1.1 | 1.21 | -0.00559
LFNoneSDGAsmNewCZ10 | Com-Iltg-dWatt-LF_OSnone | SDG | Asm | New | CZ10 | 2.61 | 0.000532 | 0 | 2.85 | 0.000659 | -0.0169 | 2.61 | 0.000532 | 0 | 2.85 | 0.000659 | -0.0169 |  | LF | None | 2610 | 0.532 | 2610 | 0.532 | 1.09 | 1.24 | -0.0064751 | 2610 | 0.532 | 2610 | 0.532 | 1.09 | 1.24 | -0.00648
LFNoneSDGAsmNewCZ14 | Com-Iltg-dWatt-LF_OSnone | SDG | Asm | New | CZ14 | 2.61 | 0.000532 | 0 | 2.78 | 0.000643 | -0.0269 | 2.61 | 0.000532 | 0 | 2.78 | 0.000643 | -0.0269 |  | LF | None | 2610 | 0.532 | 2610 | 0.532 | 1.07 | 1.21 | -0.010307 | 2610 | 0.532 | 2610 | 0.532 | 1.07 | 1.21 | -0.0103
LFNoneSDGAsmNewCZ15 | Com-Iltg-dWatt-LF_OSnone | SDG | Asm | New | CZ15 | 2.61 | 0.000532 | 0 | 3.05 | 0.000656 | -0.0078 | 2.61 | 0.000532 | 0 | 3.05 | 0.000656 | -0.0078 |  | LF | None | 2610 | 0.532 | 2610 | 0.532 | 1.17 | 1.23 | -0.0029885 | 2610 | 0.532 | 2610 | 0.532 | 1.17 | 1.23 | -0.00299
LFNoneSDGAsmNewIOU | Com-Iltg-dWatt-LF_OSnone | SDG | Asm | New | IOU | 2.61 | 0.000532 | 0 | 2.8563 | 0.00065387 | -0.016571 | 2.61 | 0.000532 | 0 | 2.8563 | 0.00065387 | -0.016571 |  | LF | None | 2610 | 0.532 | 2610 | 0.532 | 1.09 | 1.23 | -0.0063492 | 2610 | 0.532 | 2610 | 0.532 | 1.09 | 1.23 | -0.00635
LFNoneSDGComExCZ06 | Com-Iltg-dWatt-LF_OSnone | SDG | Com | Ex | CZ06 | 3.2156 | 0.00068427 | 0 | 3.5393 | 0.00084332 | -0.014428 | 3.2156 | 0.00068427 | 0 | 3.5393 | 0.00084332 | -0.014428 |  | LF | None | 3220 | 0.684 | 3220 | 0.684 | 1.1 | 1.23 | -0.0044868 | 3220 | 0.684 | 3220 | 0.684 | 1.1 | 1.23 | -0.00449
LFNoneSDGComExCZ07 | Com-Iltg-dWatt-LF_OSnone | SDG | Com | Ex | CZ07 | 3.1198 | 0.00069644 | 0 | 3.4688 | 0.00085414 | -0.010286 | 3.1198 | 0.00069644 | 0 | 3.4688 | 0.00085414 | -0.010286 |  | LF | None | 3120 | 0.696 | 3120 | 0.696 | 1.11 | 1.23 | -0.0032969 | 3120 | 0.696 | 3120 | 0.696 | 1.11 | 1.23 | -0.0033
LFNoneSDGComExCZ08 | Com-Iltg-dWatt-LF_OSnone | SDG | Com | Ex | CZ08 | 3.3595 | 0.00075278 | 0 | 3.7798 | 0.00093293 | -0.011284 | 3.3595 | 0.00075278 | 0 | 3.7798 | 0.00093293 | -0.011284 |  | LF | None | 3360 | 0.753 | 3360 | 0.753 | 1.13 | 1.24 | -0.0033589 | 3360 | 0.753 | 3360 | 0.753 | 1.13 | 1.24 | -0.00336
LFNoneSDGComExCZ10 | Com-Iltg-dWatt-LF_OSnone | SDG | Com | Ex | CZ10 | 3.2073 | 0.00072629 | 0 | 3.555 | 0.00090834 | -0.012597 | 3.2073 | 0.00072629 | 0 | 3.555 | 0.00090834 | -0.012597 |  | LF | None | 3210 | 0.726 | 3210 | 0.726 | 1.11 | 1.25 | -0.0039276 | 3210 | 0.726 | 3210 | 0.726 | 1.11 | 1.25 | -0.00393
LFNoneSDGComExCZ14 | Com-Iltg-dWatt-LF_OSnone | SDG | Com | Ex | CZ14 | 2.8049 | 0.00065733 | 0 | 3.0567 | 0.00082318 | -0.015899 | 2.8049 | 0.00065733 | 0 | 3.0567 | 0.00082318 | -0.015899 |  | LF | None | 2800 | 0.657 | 2800 | 0.657 | 1.09 | 1.25 | -0.0056682 | 2800 | 0.657 | 2800 | 0.657 | 1.09 | 1.25 | -0.00567
LFNoneSDGComExCZ15 | Com-Iltg-dWatt-LF_OSnone | SDG | Com | Ex | CZ15 | 2.539 | 0.00052484 | 0 | 2.9887 | 0.00066237 | -0.0039436 | 2.539 | 0.00052484 | 0 | 2.9887 | 0.00066237 | -0.0039436 |  | LF | None | 2540 | 0.525 | 2540 | 0.525 | 1.18 | 1.26 | -0.0015532 | 2540 | 0.525 | 2540 | 0.525 | 1.18 | 1.26 | -0.00155
LFNoneSDGComExIOU | Com-Iltg-dWatt-LF_OSnone | SDG | Com | Ex | IOU | 3.1473 | 0.00070405 | 0 | 3.497 | 0.00086806 | -0.010991 | 3.1473 | 0.00070405 | 0 | 3.497 | 0.00086806 | -0.010991 |  | LF | None | 3150 | 0.704 | 3150 | 0.704 | 1.11 | 1.23 | -0.0034923 | 3150 | 0.704 | 3150 | 0.704 | 1.11 | 1.23 | -0.00349
LFNoneSDGComNewCZ06 | Com-Iltg-dWatt-LF_OSnone | SDG | Com | New | CZ06 | 3.2079 | 0.00065956 | 0 | 3.492 | 0.00081031 | -0.013821 | 3.2079 | 0.00065956 | 0 | 3.492 | 0.00081031 | -0.013821 |  | LF | None | 3210 | 0.66 | 3210 | 0.66 | 1.09 | 1.23 | -0.0043083 | 3210 | 0.66 | 3210 | 0.66 | 1.09 | 1.23 | -0.00431
LFNoneSDGComNewCZ07 | Com-Iltg-dWatt-LF_OSnone | SDG | Com | New | CZ07 | 3.0958 | 0.0006754 | 0 | 3.3808 | 0.00082118 | -0.0093474 | 3.0958 | 0.0006754 | 0 | 3.3808 | 0.00082118 | -0.0093474 |  | LF | None | 3100 | 0.675 | 3100 | 0.675 | 1.09 | 1.22 | -0.0030194 | 3100 | 0.675 | 3100 | 0.675 | 1.09 | 1.22 | -0.00302
LFNoneSDGComNewCZ08 | Com-Iltg-dWatt-LF_OSnone | SDG | Com | New | CZ08 | 3.4281 | 0.00076025 | 0 | 3.8116 | 0.00095196 | -0.010998 | 3.4281 | 0.00076025 | 0 | 3.8116 | 0.00095196 | -0.010998 |  | LF | None | 3430 | 0.76 | 3430 | 0.76 | 1.11 | 1.25 | -0.0032083 | 3430 | 0.76 | 3430 | 0.76 | 1.11 | 1.25 | -0.00321
LFNoneSDGComNewCZ10 | Com-Iltg-dWatt-LF_OSnone | SDG | Com | New | CZ10 | 3.2596 | 0.00072439 | 0 | 3.6012 | 0.00093253 | -0.012153 | 3.2596 | 0.00072439 | 0 | 3.6012 | 0.00093253 | -0.012153 |  | LF | None | 3260 | 0.724 | 3260 | 0.724 | 1.1 | 1.29 | -0.0037284 | 3260 | 0.724 | 3260 | 0.724 | 1.1 | 1.29 | -0.00373
LFNoneSDGComNewCZ14 | Com-Iltg-dWatt-LF_OSnone | SDG | Com | New | CZ14 | 2.814 | 0.00063057 | 0 | 3.061 | 0.00081851 | -0.015698 | 2.814 | 0.00063057 | 0 | 3.061 | 0.00081851 | -0.015698 |  | LF | None | 2810 | 0.631 | 2810 | 0.631 | 1.09 | 1.3 | -0.0055787 | 2810 | 0.631 | 2810 | 0.631 | 1.09 | 1.3 | -0.00558
LFNoneSDGComNewCZ15 | Com-Iltg-dWatt-LF_OSnone | SDG | Com | New | CZ15 | 2.4474 | 0.00047094 | 0 | 2.8695 | 0.00061888 | -0.0036689 | 2.4474 | 0.00047094 | 0 | 2.8695 | 0.00061888 | -0.0036689 |  | LF | None | 2450 | 0.471 | 2450 | 0.471 | 1.17 | 1.31 | -0.0014991 | 2450 | 0.471 | 2450 | 0.471 | 1.17 | 1.31 | -0.0015
LFNoneSDGComNewIOU | Com-Iltg-dWatt-LF_OSnone | SDG | Com | New | IOU | 3.1434 | 0.00068782 | 0 | 3.4444 | 0.00084971 | -0.010208 | 3.1434 | 0.00068782 | 0 | 3.4444 | 0.00084971 | -0.010208 |  | LF | None | 3140 | 0.688 | 3140 | 0.688 | 1.1 | 1.24 | -0.0032475 | 3140 | 0.688 | 3140 | 0.688 | 1.1 | 1.24 | -0.00325
LFNoneSDGECCExCZ06 | Com-Iltg-dWatt-LF_OSnone | SDG | ECC | Ex | CZ06 | 2.42 | 0.000806 | 0 | 2.74 | 0.00102 | -0.014 | 2.42 | 0.000806 | 0 | 2.74 | 0.00102 | -0.014 |  | LF | None | 2420 | 0.806 | 2420 | 0.806 | 1.13 | 1.27 | -0.0057851 | 2420 | 0.806 | 2420 | 0.806 | 1.13 | 1.27 | -0.00579
LFNoneSDGECCExCZ07 | Com-Iltg-dWatt-LF_OSnone | SDG | ECC | Ex | CZ07 | 2.42 | 0.000806 | 0 | 2.76 | 0.00102 | -0.0117 | 2.42 | 0.000806 | 0 | 2.76 | 0.00102 | -0.0117 |  | LF | None | 2420 | 0.806 | 2420 | 0.806 | 1.14 | 1.27 | -0.0048347 | 2420 | 0.806 | 2420 | 0.806 | 1.14 | 1.27 | -0.00483
LFNoneSDGECCExCZ08 | Com-Iltg-dWatt-LF_OSnone | SDG | ECC | Ex | CZ08 | 2.42 | 0.000806 | 0 | 2.77 | 0.00102 | -0.0127 | 2.42 | 0.000806 | 0 | 2.77 | 0.00102 | -0.0127 |  | LF | None | 2420 | 0.806 | 2420 | 0.806 | 1.14 | 1.27 | -0.0052479 | 2420 | 0.806 | 2420 | 0.806 | 1.14 | 1.27 | -0.00525
LFNoneSDGECCExCZ10 | Com-Iltg-dWatt-LF_OSnone | SDG | ECC | Ex | CZ10 | 2.42 | 0.000806 | 0 | 2.76 | 0.00104 | -0.0151 | 2.42 | 0.000806 | 0 | 2.76 | 0.00104 | -0.0151 |  | LF | None | 2420 | 0.806 | 2420 | 0.806 | 1.14 | 1.29 | -0.0062397 | 2420 | 0.806 | 2420 | 0.806 | 1.14 | 1.29 | -0.00624
LFNoneSDGECCExCZ14 | Com-Iltg-dWatt-LF_OSnone | SDG | ECC | Ex | CZ14 | 2.42 | 0.000806 | 0 | 2.7 | 0.00103 | -0.0227 | 2.42 | 0.000806 | 0 | 2.7 | 0.00103 | -0.0227 |  | LF | None | 2420 | 0.806 | 2420 | 0.806 | 1.12 | 1.28 | -0.0093802 | 2420 | 0.806 | 2420 | 0.806 | 1.12 | 1.28 | -0.00938
LFNoneSDGECCExIOU | Com-Iltg-dWatt-LF_OSnone | SDG | ECC | Ex | IOU | 2.42 | 0.000806 | 0 | 2.7597 | 0.0010247 | -0.012577 | 2.42 | 0.000806 | 0 | 2.7597 | 0.0010247 | -0.012577 |  | LF | None | 2420 | 0.806 | 2420 | 0.806 | 1.14 | 1.27 | -0.0051971 | 2420 | 0.806 | 2420 | 0.806 | 1.14 | 1.27 | -0.0052
LFNoneSDGECCNewCZ06 | Com-Iltg-dWatt-LF_OSnone | SDG | ECC | New | CZ06 | 2.42 | 0.000806 | 0 | 2.75 | 0.00102 | -0.0132 | 2.42 | 0.000806 | 0 | 2.75 | 0.00102 | -0.0132 |  | LF | None | 2420 | 0.806 | 2420 | 0.806 | 1.14 | 1.27 | -0.0054545 | 2420 | 0.806 | 2420 | 0.806 | 1.14 | 1.27 | -0.00545
LFNoneSDGECCNewCZ07 | Com-Iltg-dWatt-LF_OSnone | SDG | ECC | New | CZ07 | 2.42 | 0.000806 | 0 | 2.74 | 0.00102 | -0.0107 | 2.42 | 0.000806 | 0 | 2.74 | 0.00102 | -0.0107 |  | LF | None | 2420 | 0.806 | 2420 | 0.806 | 1.13 | 1.27 | -0.0044215 | 2420 | 0.806 | 2420 | 0.806 | 1.13 | 1.27 | -0.00442
LFNoneSDGECCNewCZ08 | Com-Iltg-dWatt-LF_OSnone | SDG | ECC | New | CZ08 | 2.42 | 0.000806 | 0 | 2.78 | 0.00102 | -0.0109 | 2.42 | 0.000806 | 0 | 2.78 | 0.00102 | -0.0109 |  | LF | None | 2420 | 0.806 | 2420 | 0.806 | 1.15 | 1.27 | -0.0045041 | 2420 | 0.806 | 2420 | 0.806 | 1.15 | 1.27 | -0.0045
LFNoneSDGECCNewCZ10 | Com-Iltg-dWatt-LF_OSnone | SDG | ECC | New | CZ10 | 2.42 | 0.000806 | 0 | 2.81 | 0.00106 | -0.0127 | 2.42 | 0.000806 | 0 | 2.81 | 0.00106 | -0.0127 |  | LF | None | 2420 | 0.806 | 2420 | 0.806 | 1.16 | 1.32 | -0.0052479 | 2420 | 0.806 | 2420 | 0.806 | 1.16 | 1.32 | -0.00525
LFNoneSDGECCNewCZ14 | Com-Iltg-dWatt-LF_OSnone | SDG | ECC | New | CZ14 | 2.42 | 0.000806 | 0 | 2.77 | 0.00102 | -0.021 | 2.42 | 0.000806 | 0 | 2.77 | 0.00102 | -0.021 |  | LF | None | 2420 | 0.806 | 2420 | 0.806 | 1.14 | 1.27 | -0.0086777 | 2420 | 0.806 | 2420 | 0.806 | 1.14 | 1.27 | -0.00868
LFNoneSDGECCNewCZ15 | Com-Iltg-dWatt-LF_OSnone | SDG | ECC | New | CZ15 | 2.42 | 0.000806 | 0 | 3.07 | 0.00111 | -0.00465 | 2.42 | 0.000806 | 0 | 3.07 | 0.00111 | -0.00465 |  | LF | None | 2420 | 0.806 | 2420 | 0.806 | 1.27 | 1.38 | -0.0019215 | 2420 | 0.806 | 2420 | 0.806 | 1.27 | 1.38 | -0.00192
LFNoneSDGECCNewIOU | Com-Iltg-dWatt-LF_OSnone | SDG | ECC | New | IOU | 2.42 | 0.000806 | 0 | 2.757 | 0.0010294 | -0.011238 | 2.42 | 0.000806 | 0 | 2.757 | 0.0010294 | -0.011238 |  | LF | None | 2420 | 0.806 | 2420 | 0.806 | 1.14 | 1.28 | -0.004644 | 2420 | 0.806 | 2420 | 0.806 | 1.14 | 1.28 | -0.00464
LFNoneSDGEPrExCZ06 | Com-Iltg-dWatt-LF_OSnone | SDG | EPr | Ex | CZ06 | 2.14 | 0.000616 | 0 | 2.44 | 0.00079 | -0.0095 | 2.14 | 0.000616 | 0 | 2.44 | 0.00079 | -0.0095 |  | LF | None | 2140 | 0.616 | 2140 | 0.616 | 1.14 | 1.28 | -0.0044393 | 2140 | 0.616 | 2140 | 0.616 | 1.14 | 1.28 | -0.00444
LFNoneSDGEPrExCZ07 | Com-Iltg-dWatt-LF_OSnone | SDG | EPr | Ex | CZ07 | 2.14 | 0.000616 | 0 | 2.43 | 0.000798 | -0.0085 | 2.14 | 0.000616 | 0 | 2.43 | 0.000798 | -0.0085 |  | LF | None | 2140 | 0.616 | 2140 | 0.616 | 1.14 | 1.3 | -0.003972 | 2140 | 0.616 | 2140 | 0.616 | 1.14 | 1.3 | -0.00397
LFNoneSDGEPrExCZ08 | Com-Iltg-dWatt-LF_OSnone | SDG | EPr | Ex | CZ08 | 2.14 | 0.000616 | 0 | 2.46 | 0.000798 | -0.00788 | 2.14 | 0.000616 | 0 | 2.46 | 0.000798 | -0.00788 |  | LF | None | 2140 | 0.616 | 2140 | 0.616 | 1.15 | 1.3 | -0.0036822 | 2140 | 0.616 | 2140 | 0.616 | 1.15 | 1.3 | -0.00368
LFNoneSDGEPrExCZ10 | Com-Iltg-dWatt-LF_OSnone | SDG | EPr | Ex | CZ10 | 2.14 | 0.000616 | 0 | 2.44 | 0.000794 | -0.0101 | 2.14 | 0.000616 | 0 | 2.44 | 0.000794 | -0.0101 |  | LF | None | 2140 | 0.616 | 2140 | 0.616 | 1.14 | 1.29 | -0.0047196 | 2140 | 0.616 | 2140 | 0.616 | 1.14 | 1.29 | -0.00472
LFNoneSDGEPrExCZ14 | Com-Iltg-dWatt-LF_OSnone | SDG | EPr | Ex | CZ14 | 2.14 | 0.000616 | 0 | 2.34 | 0.000795 | -0.0172 | 2.14 | 0.000616 | 0 | 2.34 | 0.000795 | -0.0172 |  | LF | None | 2140 | 0.616 | 2140 | 0.616 | 1.09 | 1.29 | -0.0080374 | 2140 | 0.616 | 2140 | 0.616 | 1.09 | 1.29 | -0.00804
LFNoneSDGEPrExCZ15 | Com-Iltg-dWatt-LF_OSnone | SDG | EPr | Ex | CZ15 | 2.14 | 0.000616 | 0 | 2.62 | 0.000795 | -0.00413 | 2.14 | 0.000616 | 0 | 2.62 | 0.000795 | -0.00413 |  | LF | None | 2140 | 0.616 | 2140 | 0.616 | 1.22 | 1.29 | -0.0019299 | 2140 | 0.616 | 2140 | 0.616 | 1.22 | 1.29 | -0.00193
LFNoneSDGEPrExIOU | Com-Iltg-dWatt-LF_OSnone | SDG | EPr | Ex | IOU | 2.14 | 0.000616 | 0 | 2.4351 | 0.00079627 | -0.0091027 | 2.14 | 0.000616 | 0 | 2.4351 | 0.00079627 | -0.0091027 |  | LF | None | 2140 | 0.616 | 2140 | 0.616 | 1.14 | 1.29 | -0.0042536 | 2140 | 0.616 | 2140 | 0.616 | 1.14 | 1.29 | -0.00425
LFNoneSDGEPrNewCZ06 | Com-Iltg-dWatt-LF_OSnone | SDG | EPr | New | CZ06 | 2.14 | 0.000616 | 0 | 2.21 | 0.000585 | -0.0103 | 2.14 | 0.000616 | 0 | 2.21 | 0.000585 | -0.0103 |  | LF | None | 2140 | 0.616 | 2140 | 0.616 | 1.03 | 0.95 | -0.0048131 | 2140 | 0.616 | 2140 | 0.616 | 1.03 | 0.95 | -0.00481
LFNoneSDGEPrNewCZ07 | Com-Iltg-dWatt-LF_OSnone | SDG | EPr | New | CZ07 | 2.14 | 0.000616 | 0 | 2.34 | 0.000824 | -0.011 | 2.14 | 0.000616 | 0 | 2.34 | 0.000824 | -0.011 |  | LF | None | 2140 | 0.616 | 2140 | 0.616 | 1.09 | 1.34 | -0.0051402 | 2140 | 0.616 | 2140 | 0.616 | 1.09 | 1.34 | -0.00514
LFNoneSDGEPrNewCZ08 | Com-Iltg-dWatt-LF_OSnone | SDG | EPr | New | CZ08 | 2.14 | 0.000616 | 0 | 2.41 | 0.000849 | -0.0103 | 2.14 | 0.000616 | 0 | 2.41 | 0.000849 | -0.0103 |  | LF | None | 2140 | 0.616 | 2140 | 0.616 | 1.13 | 1.38 | -0.0048131 | 2140 | 0.616 | 2140 | 0.616 | 1.13 | 1.38 | -0.00481
LFNoneSDGEPrNewCZ10 | Com-Iltg-dWatt-LF_OSnone | SDG | EPr | New | CZ10 | 2.14 | 0.000616 | 0 | 2.42 | 0.000895 | -0.0127 | 2.14 | 0.000616 | 0 | 2.42 | 0.000895 | -0.0127 |  | LF | None | 2140 | 0.616 | 2140 | 0.616 | 1.13 | 1.45 | -0.0059346 | 2140 | 0.616 | 2140 | 0.616 | 1.13 | 1.45 | -0.00593
LFNoneSDGEPrNewCZ14 | Com-Iltg-dWatt-LF_OSnone | SDG | EPr | New | CZ14 | 2.14 | 0.000616 | 0 | 2.37 | 0.000878 | -0.0208 | 2.14 | 0.000616 | 0 | 2.37 | 0.000878 | -0.0208 |  | LF | None | 2140 | 0.616 | 2140 | 0.616 | 1.11 | 1.43 | -0.0097196 | 2140 | 0.616 | 2140 | 0.616 | 1.11 | 1.43 | -0.00972
LFNoneSDGEPrNewCZ15 | Com-Iltg-dWatt-LF_OSnone | SDG | EPr | New | CZ15 | 2.14 | 0.000616 | 0 | 2.63 | 0.000895 | -0.00548 | 2.14 | 0.000616 | 0 | 2.63 | 0.000895 | -0.00548 |  | LF | None | 2140 | 0.616 | 2140 | 0.616 | 1.23 | 1.45 | -0.0025607 | 2140 | 0.616 | 2140 | 0.616 | 1.23 | 1.45 | -0.00256
LFNoneSDGEPrNewIOU | Com-Iltg-dWatt-LF_OSnone | SDG | EPr | New | IOU | 2.14 | 0.000616 | 0 | 2.3645 | 0.00083747 | -0.011556 | 2.14 | 0.000616 | 0 | 2.3645 | 0.00083747 | -0.011556 |  | LF | None | 2140 | 0.616 | 2140 | 0.616 | 1.1 | 1.36 | -0.0054 | 2140 | 0.616 | 2140 | 0.616 | 1.1 | 1.36 | -0.0054
LFNoneSDGERCExCZ06 | Com-Iltg-dWatt-LF_OSnone | SDG | ERC | Ex | CZ06 | 2.48 | 0.000702 | 0 | 2.76 | 0.000882 | -0.0152 | 2.48 | 0.000702 | 0 | 2.76 | 0.000882 | -0.0152 |  | LF | None | 2480 | 0.702 | 2480 | 0.702 | 1.11 | 1.26 | -0.006129 | 2480 | 0.702 | 2480 | 0.702 | 1.11 | 1.26 | -0.00613
LFNoneSDGERCExCZ07 | Com-Iltg-dWatt-LF_OSnone | SDG | ERC | Ex | CZ07 | 2.48 | 0.000702 | 0 | 2.8 | 0.000898 | -0.0126 | 2.48 | 0.000702 | 0 | 2.8 | 0.000898 | -0.0126 |  | LF | None | 2480 | 0.702 | 2480 | 0.702 | 1.13 | 1.28 | -0.0050806 | 2480 | 0.702 | 2480 | 0.702 | 1.13 | 1.28 | -0.00508
LFNoneSDGERCExCZ08 | Com-Iltg-dWatt-LF_OSnone | SDG | ERC | Ex | CZ08 | 2.48 | 0.000702 | 0 | 2.76 | 0.000892 | -0.0133 | 2.48 | 0.000702 | 0 | 2.76 | 0.000892 | -0.0133 |  | LF | None | 2480 | 0.702 | 2480 | 0.702 | 1.11 | 1.27 | -0.0053629 | 2480 | 0.702 | 2480 | 0.702 | 1.11 | 1.27 | -0.00536
LFNoneSDGERCExCZ10 | Com-Iltg-dWatt-LF_OSnone | SDG | ERC | Ex | CZ10 | 2.48 | 0.000702 | 0 | 2.75 | 0.000894 | -0.0157 | 2.48 | 0.000702 | 0 | 2.75 | 0.000894 | -0.0157 |  | LF | None | 2480 | 0.702 | 2480 | 0.702 | 1.11 | 1.27 | -0.0063306 | 2480 | 0.702 | 2480 | 0.702 | 1.11 | 1.27 | -0.00633
LFNoneSDGERCExCZ14 | Com-Iltg-dWatt-LF_OSnone | SDG | ERC | Ex | CZ14 | 2.48 | 0.000702 | 0 | 2.71 | 0.000899 | -0.0208 | 2.48 | 0.000702 | 0 | 2.71 | 0.000899 | -0.0208 |  | LF | None | 2480 | 0.702 | 2480 | 0.702 | 1.09 | 1.28 | -0.0083871 | 2480 | 0.702 | 2480 | 0.702 | 1.09 | 1.28 | -0.00839
LFNoneSDGERCExCZ15 | Com-Iltg-dWatt-LF_OSnone | SDG | ERC | Ex | CZ15 | 2.48 | 0.000702 | 0 | 2.94 | 0.000916 | -0.00732 | 2.48 | 0.000702 | 0 | 2.94 | 0.000916 | -0.00732 |  | LF | None | 2480 | 0.702 | 2480 | 0.702 | 1.19 | 1.3 | -0.0029516 | 2480 | 0.702 | 2480 | 0.702 | 1.19 | 1.3 | -0.00295
LFNoneSDGERCExIOU | Com-Iltg-dWatt-LF_OSnone | SDG | ERC | Ex | IOU | 2.48 | 0.000702 | 0 | 2.7791 | 0.00089564 | -0.013835 | 2.48 | 0.000702 | 0 | 2.7791 | 0.00089564 | -0.013835 |  | LF | None | 2480 | 0.702 | 2480 | 0.702 | 1.12 | 1.28 | -0.0055787 | 2480 | 0.702 | 2480 | 0.702 | 1.12 | 1.28 | -0.00558
LFNoneSDGERCNewCZ06 | Com-Iltg-dWatt-LF_OSnone | SDG | ERC | New | CZ06 | 2.48 | 0.000702 | 0 | 2.86 | 0.000908 | -0.0159 | 2.48 | 0.000702 | 0 | 2.86 | 0.000908 | -0.0159 |  | LF | None | 2480 | 0.702 | 2480 | 0.702 | 1.15 | 1.29 | -0.0064113 | 2480 | 0.702 | 2480 | 0.702 | 1.15 | 1.29 | -0.00641
LFNoneSDGERCNewCZ07 | Com-Iltg-dWatt-LF_OSnone | SDG | ERC | New | CZ07 | 2.48 | 0.000702 | 0 | 2.87 | 0.000914 | -0.0125 | 2.48 | 0.000702 | 0 | 2.87 | 0.000914 | -0.0125 |  | LF | None | 2480 | 0.702 | 2480 | 0.702 | 1.16 | 1.3 | -0.0050403 | 2480 | 0.702 | 2480 | 0.702 | 1.16 | 1.3 | -0.00504
LFNoneSDGERCNewCZ08 | Com-Iltg-dWatt-LF_OSnone | SDG | ERC | New | CZ08 | 2.48 | 0.000702 | 0 | 2.92 | 0.000929 | -0.0134 | 2.48 | 0.000702 | 0 | 2.92 | 0.000929 | -0.0134 |  | LF | None | 2480 | 0.702 | 2480 | 0.702 | 1.18 | 1.32 | -0.0054032 | 2480 | 0.702 | 2480 | 0.702 | 1.18 | 1.32 | -0.0054
LFNoneSDGERCNewCZ10 | Com-Iltg-dWatt-LF_OSnone | SDG | ERC | New | CZ10 | 2.48 | 0.000702 | 0 | 2.93 | 0.000972 | -0.0159 | 2.48 | 0.000702 | 0 | 2.93 | 0.000972 | -0.0159 |  | LF | None | 2480 | 0.702 | 2480 | 0.702 | 1.18 | 1.38 | -0.0064113 | 2480 | 0.702 | 2480 | 0.702 | 1.18 | 1.38 | -0.00641
LFNoneSDGERCNewCZ14 | Com-Iltg-dWatt-LF_OSnone | SDG | ERC | New | CZ14 | 2.48 | 0.000702 | 0 | 2.88 | 0.000957 | -0.0231 | 2.48 | 0.000702 | 0 | 2.88 | 0.000957 | -0.0231 |  | LF | None | 2480 | 0.702 | 2480 | 0.702 | 1.16 | 1.36 | -0.0093145 | 2480 | 0.702 | 2480 | 0.702 | 1.16 | 1.36 | -0.00931
LFNoneSDGERCNewCZ15 | Com-Iltg-dWatt-LF_OSnone | SDG | ERC | New | CZ15 | 2.48 | 0.000702 | 0 | 3.17 | 0.000974 | -0.00789 | 2.48 | 0.000702 | 0 | 3.17 | 0.000974 | -0.00789 |  | LF | None | 2480 | 0.702 | 2480 | 0.702 | 1.28 | 1.39 | -0.0031815 | 2480 | 0.702 | 2480 | 0.702 | 1.28 | 1.39 | -0.00318
LFNoneSDGERCNewIOU | Com-Iltg-dWatt-LF_OSnone | SDG | ERC | New | IOU | 2.48 | 0.000702 | 0 | 2.8926 | 0.00093395 | -0.013907 | 2.48 | 0.000702 | 0 | 2.8926 | 0.00093395 | -0.013907 |  | LF | None | 2480 | 0.702 | 2480 | 0.702 | 1.17 | 1.33 | -0.0056078 | 2480 | 0.702 | 2480 | 0.702 | 1.17 | 1.33 | -0.00561
LFNoneSDGESeExCZ06 | Com-Iltg-dWatt-LF_OSnone | SDG | ESe | Ex | CZ06 | 2.28 | 0.000709 | 0 | 2.56 | 0.000905 | -0.0129 | 2.28 | 0.000709 | 0 | 2.56 | 0.000905 | -0.0129 |  | LF | None | 2280 | 0.709 | 2280 | 0.709 | 1.12 | 1.28 | -0.0056579 | 2280 | 0.709 | 2280 | 0.709 | 1.12 | 1.28 | -0.00566
LFNoneSDGESeExCZ07 | Com-Iltg-dWatt-LF_OSnone | SDG | ESe | Ex | CZ07 | 2.28 | 0.000709 | 0 | 2.56 | 0.000891 | -0.0113 | 2.28 | 0.000709 | 0 | 2.56 | 0.000891 | -0.0113 |  | LF | None | 2280 | 0.709 | 2280 | 0.709 | 1.12 | 1.26 | -0.0049561 | 2280 | 0.709 | 2280 | 0.709 | 1.12 | 1.26 | -0.00496
LFNoneSDGESeExCZ08 | Com-Iltg-dWatt-LF_OSnone | SDG | ESe | Ex | CZ08 | 2.28 | 0.000709 | 0 | 2.59 | 0.0009 | -0.011 | 2.28 | 0.000709 | 0 | 2.59 | 0.0009 | -0.011 |  | LF | None | 2280 | 0.709 | 2280 | 0.709 | 1.14 | 1.27 | -0.0048246 | 2280 | 0.709 | 2280 | 0.709 | 1.14 | 1.27 | -0.00482
LFNoneSDGESeExCZ10 | Com-Iltg-dWatt-LF_OSnone | SDG | ESe | Ex | CZ10 | 2.28 | 0.000709 | 0 | 2.58 | 0.000899 | -0.0138 | 2.28 | 0.000709 | 0 | 2.58 | 0.000899 | -0.0138 |  | LF | None | 2280 | 0.709 | 2280 | 0.709 | 1.13 | 1.27 | -0.0060526 | 2280 | 0.709 | 2280 | 0.709 | 1.13 | 1.27 | -0.00605
LFNoneSDGESeExCZ14 | Com-Iltg-dWatt-LF_OSnone | SDG | ESe | Ex | CZ14 | 2.28 | 0.000709 | 0 | 2.49 | 0.000873 | -0.0222 | 2.28 | 0.000709 | 0 | 2.49 | 0.000873 | -0.0222 |  | LF | None | 2280 | 0.709 | 2280 | 0.709 | 1.09 | 1.23 | -0.0097368 | 2280 | 0.709 | 2280 | 0.709 | 1.09 | 1.23 | -0.00974
LFNoneSDGESeExCZ15 | Com-Iltg-dWatt-LF_OSnone | SDG | ESe | Ex | CZ15 | 2.28 | 0.000709 | 0 | 2.79 | 0.000898 | -0.00608 | 2.28 | 0.000709 | 0 | 2.79 | 0.000898 | -0.00608 |  | LF | None | 2280 | 0.709 | 2280 | 0.709 | 1.22 | 1.27 | -0.0026667 | 2280 | 0.709 | 2280 | 0.709 | 1.22 | 1.27 | -0.00267
LFNoneSDGESeExIOU | Com-Iltg-dWatt-LF_OSnone | SDG | ESe | Ex | IOU | 2.28 | 0.000709 | 0 | 2.5681 | 0.00089464 | -0.01226 | 2.28 | 0.000709 | 0 | 2.5681 | 0.00089464 | -0.01226 |  | LF | None | 2280 | 0.709 | 2280 | 0.709 | 1.13 | 1.26 | -0.0053773 | 2280 | 0.709 | 2280 | 0.709 | 1.13 | 1.26 | -0.00538
LFNoneSDGESeNewCZ06 | Com-Iltg-dWatt-LF_OSnone | SDG | ESe | New | CZ06 | 2.28 | 0.000709 | 0 | 2.52 | 0.000937 | -0.017 | 2.28 | 0.000709 | 0 | 2.52 | 0.000937 | -0.017 |  | LF | None | 2280 | 0.709 | 2280 | 0.709 | 1.11 | 1.32 | -0.0074561 | 2280 | 0.709 | 2280 | 0.709 | 1.11 | 1.32 | -0.00746
LFNoneSDGESeNewCZ07 | Com-Iltg-dWatt-LF_OSnone | SDG | ESe | New | CZ07 | 2.28 | 0.000709 | 0 | 2.49 | 0.000917 | -0.0133 | 2.28 | 0.000709 | 0 | 2.49 | 0.000917 | -0.0133 |  | LF | None | 2280 | 0.709 | 2280 | 0.709 | 1.09 | 1.29 | -0.0058333 | 2280 | 0.709 | 2280 | 0.709 | 1.09 | 1.29 | -0.00583
LFNoneSDGESeNewCZ08 | Com-Iltg-dWatt-LF_OSnone | SDG | ESe | New | CZ08 | 2.28 | 0.000709 | 0 | 2.56 | 0.000952 | -0.0129 | 2.28 | 0.000709 | 0 | 2.56 | 0.000952 | -0.0129 |  | LF | None | 2280 | 0.709 | 2280 | 0.709 | 1.12 | 1.34 | -0.0056579 | 2280 | 0.709 | 2280 | 0.709 | 1.12 | 1.34 | -0.00566
LFNoneSDGESeNewCZ10 | Com-Iltg-dWatt-LF_OSnone | SDG | ESe | New | CZ10 | 2.28 | 0.000709 | 0 | 2.58 | 0.001 | -0.0166 | 2.28 | 0.000709 | 0 | 2.58 | 0.001 | -0.0166 |  | LF | None | 2280 | 0.709 | 2280 | 0.709 | 1.13 | 1.41 | -0.0072807 | 2280 | 0.709 | 2280 | 0.709 | 1.13 | 1.41 | -0.00728
LFNoneSDGESeNewCZ14 | Com-Iltg-dWatt-LF_OSnone | SDG | ESe | New | CZ14 | 2.28 | 0.000709 | 0 | 2.54 | 0.000978 | -0.0249 | 2.28 | 0.000709 | 0 | 2.54 | 0.000978 | -0.0249 |  | LF | None | 2280 | 0.709 | 2280 | 0.709 | 1.11 | 1.38 | -0.010921 | 2280 | 0.709 | 2280 | 0.709 | 1.11 | 1.38 | -0.0109
LFNoneSDGESeNewCZ15 | Com-Iltg-dWatt-LF_OSnone | SDG | ESe | New | CZ15 | 2.28 | 0.000709 | 0 | 2.85 | 0.000995 | -0.00715 | 2.28 | 0.000709 | 0 | 2.85 | 0.000995 | -0.00715 |  | LF | None | 2280 | 0.709 | 2280 | 0.709 | 1.25 | 1.4 | -0.003136 | 2280 | 0.709 | 2280 | 0.709 | 1.25 | 1.4 | -0.00314
LFNoneSDGESeNewIOU | Com-Iltg-dWatt-LF_OSnone | SDG | ESe | New | IOU | 2.28 | 0.000709 | 0 | 2.5259 | 0.00094766 | -0.014623 | 2.28 | 0.000709 | 0 | 2.5259 | 0.00094766 | -0.014623 |  | LF | None | 2280 | 0.709 | 2280 | 0.709 | 1.11 | 1.34 | -0.0064138 | 2280 | 0.709 | 2280 | 0.709 | 1.11 | 1.34 | -0.00641
LFNoneSDGEUnExCZ06 | Com-Iltg-dWatt-LF_OSnone | SDG | EUn | Ex | CZ06 | 2.35 | 0.00072 | 0 | 2.69 | 0.000909 | -0.01 | 2.35 | 0.00072 | 0 | 2.69 | 0.000909 | -0.01 |  | LF | None | 2350 | 0.72 | 2350 | 0.72 | 1.14 | 1.26 | -0.0042553 | 2350 | 0.72 | 2350 | 0.72 | 1.14 | 1.26 | -0.00426
LFNoneSDGEUnExCZ07 | Com-Iltg-dWatt-LF_OSnone | SDG | EUn | Ex | CZ07 | 2.35 | 0.00072 | 0 | 2.68 | 0.000901 | -0.00871 | 2.35 | 0.00072 | 0 | 2.68 | 0.000901 | -0.00871 |  | LF | None | 2350 | 0.72 | 2350 | 0.72 | 1.14 | 1.25 | -0.0037064 | 2350 | 0.72 | 2350 | 0.72 | 1.14 | 1.25 | -0.00371
LFNoneSDGEUnExCZ08 | Com-Iltg-dWatt-LF_OSnone | SDG | EUn | Ex | CZ08 | 2.35 | 0.00072 | 0 | 2.71 | 0.000912 | -0.00965 | 2.35 | 0.00072 | 0 | 2.71 | 0.000912 | -0.00965 |  | LF | None | 2350 | 0.72 | 2350 | 0.72 | 1.15 | 1.27 | -0.0041064 | 2350 | 0.72 | 2350 | 0.72 | 1.15 | 1.27 | -0.00411
LFNoneSDGEUnExCZ10 | Com-Iltg-dWatt-LF_OSnone | SDG | EUn | Ex | CZ10 | 2.35 | 0.00072 | 0 | 2.7 | 0.000927 | -0.0112 | 2.35 | 0.00072 | 0 | 2.7 | 0.000927 | -0.0112 |  | LF | None | 2350 | 0.72 | 2350 | 0.72 | 1.15 | 1.29 | -0.004766 | 2350 | 0.72 | 2350 | 0.72 | 1.15 | 1.29 | -0.00477
LFNoneSDGEUnExCZ14 | Com-Iltg-dWatt-LF_OSnone | SDG | EUn | Ex | CZ14 | 2.35 | 0.00072 | 0 | 2.67 | 0.000918 | -0.015 | 2.35 | 0.00072 | 0 | 2.67 | 0.000918 | -0.015 |  | LF | None | 2350 | 0.72 | 2350 | 0.72 | 1.14 | 1.27 | -0.006383 | 2350 | 0.72 | 2350 | 0.72 | 1.14 | 1.27 | -0.00638
LFNoneSDGEUnExIOU | Com-Iltg-dWatt-LF_OSnone | SDG | EUn | Ex | IOU | 2.35 | 0.00072 | 0 | 2.685 | 0.00090734 | -0.0093429 | 2.35 | 0.00072 | 0 | 2.685 | 0.00090734 | -0.0093429 |  | LF | None | 2350 | 0.72 | 2350 | 0.72 | 1.14 | 1.26 | -0.0039757 | 2350 | 0.72 | 2350 | 0.72 | 1.14 | 1.26 | -0.00398
LFNoneSDGEUnNewCZ06 | Com-Iltg-dWatt-LF_OSnone | SDG | EUn | New | CZ06 | 2.35 | 0.00072 | 0 | 2.73 | 0.00091 | -0.00664 | 2.35 | 0.00072 | 0 | 2.73 | 0.00091 | -0.00664 |  | LF | None | 2350 | 0.72 | 2350 | 0.72 | 1.16 | 1.26 | -0.0028255 | 2350 | 0.72 | 2350 | 0.72 | 1.16 | 1.26 | -0.00283
LFNoneSDGEUnNewCZ07 | Com-Iltg-dWatt-LF_OSnone | SDG | EUn | New | CZ07 | 2.35 | 0.00072 | 0 | 2.71 | 0.000903 | -0.00544 | 2.35 | 0.00072 | 0 | 2.71 | 0.000903 | -0.00544 |  | LF | None | 2350 | 0.72 | 2350 | 0.72 | 1.15 | 1.25 | -0.0023149 | 2350 | 0.72 | 2350 | 0.72 | 1.15 | 1.25 | -0.00231
LFNoneSDGEUnNewCZ08 | Com-Iltg-dWatt-LF_OSnone | SDG | EUn | New | CZ08 | 2.35 | 0.00072 | 0 | 2.76 | 0.000921 | -0.00595 | 2.35 | 0.00072 | 0 | 2.76 | 0.000921 | -0.00595 |  | LF | None | 2350 | 0.72 | 2350 | 0.72 | 1.17 | 1.28 | -0.0025319 | 2350 | 0.72 | 2350 | 0.72 | 1.17 | 1.28 | -0.00253
LFNoneSDGEUnNewCZ10 | Com-Iltg-dWatt-LF_OSnone | SDG | EUn | New | CZ10 | 2.35 | 0.00072 | 0 | 2.77 | 0.000953 | -0.00706 | 2.35 | 0.00072 | 0 | 2.77 | 0.000953 | -0.00706 |  | LF | None | 2350 | 0.72 | 2350 | 0.72 | 1.18 | 1.32 | -0.0030043 | 2350 | 0.72 | 2350 | 0.72 | 1.18 | 1.32 | -0.003
LFNoneSDGEUnNewCZ14 | Com-Iltg-dWatt-LF_OSnone | SDG | EUn | New | CZ14 | 2.35 | 0.00072 | 0 | 2.72 | 0.000919 | -0.0129 | 2.35 | 0.00072 | 0 | 2.72 | 0.000919 | -0.0129 |  | LF | None | 2350 | 0.72 | 2350 | 0.72 | 1.16 | 1.28 | -0.0054894 | 2350 | 0.72 | 2350 | 0.72 | 1.16 | 1.28 | -0.00549
LFNoneSDGEUnNewCZ15 | Com-Iltg-dWatt-LF_OSnone | SDG | EUn | New | CZ15 | 2.35 | 0.00072 | 0 | 2.91 | 0.000958 | -0.00278 | 2.35 | 0.00072 | 0 | 2.91 | 0.000958 | -0.00278 |  | LF | None | 2350 | 0.72 | 2350 | 0.72 | 1.24 | 1.33 | -0.001183 | 2350 | 0.72 | 2350 | 0.72 | 1.24 | 1.33 | -0.00118
LFNoneSDGEUnNewIOU | Com-Iltg-dWatt-LF_OSnone | SDG | EUn | New | IOU | 2.35 | 0.00072 | 0 | 2.7247 | 0.00091503 | -0.0058703 | 2.35 | 0.00072 | 0 | 2.7247 | 0.00091503 | -0.0058703 |  | LF | None | 2350 | 0.72 | 2350 | 0.72 | 1.16 | 1.27 | -0.002498 | 2350 | 0.72 | 2350 | 0.72 | 1.16 | 1.27 | -0.0025
LFNoneSDGGroExCZ06 | Com-Iltg-dWatt-LF_OSnone | SDG | Gro | Ex | CZ06 | 4.91 | 0.00069 | 0 | 4.96 | 0.000848 | -0.0623 | 4.91 | 0.00069 | 0 | 4.96 | 0.000848 | -0.0623 |  | LF | None | 4910 | 0.69 | 4910 | 0.69 | 1.01 | 1.23 | -0.012688 | 4910 | 0.69 | 4910 | 0.69 | 1.01 | 1.23 | -0.0127
LFNoneSDGGroExCZ07 | Com-Iltg-dWatt-LF_OSnone | SDG | Gro | Ex | CZ07 | 4.91 | 0.00069 | 0 | 4.89 | 0.000827 | -0.0662 | 4.91 | 0.00069 | 0 | 4.89 | 0.000827 | -0.0662 |  | LF | None | 4910 | 0.69 | 4910 | 0.69 | 0.996 | 1.2 | -0.013483 | 4910 | 0.69 | 4910 | 0.69 | 0.996 | 1.2 | -0.0135
LFNoneSDGGroExCZ08 | Com-Iltg-dWatt-LF_OSnone | SDG | Gro | Ex | CZ08 | 4.91 | 0.00069 | 0 | 5.07 | 0.000869 | -0.0564 | 4.91 | 0.00069 | 0 | 5.07 | 0.000869 | -0.0564 |  | LF | None | 4910 | 0.69 | 4910 | 0.69 | 1.03 | 1.26 | -0.011487 | 4910 | 0.69 | 4910 | 0.69 | 1.03 | 1.26 | -0.0115
LFNoneSDGGroExCZ10 | Com-Iltg-dWatt-LF_OSnone | SDG | Gro | Ex | CZ10 | 4.91 | 0.00069 | 0 | 5.14 | 0.000905 | -0.0535 | 4.91 | 0.00069 | 0 | 5.14 | 0.000905 | -0.0535 |  | LF | None | 4910 | 0.69 | 4910 | 0.69 | 1.05 | 1.31 | -0.010896 | 4910 | 0.69 | 4910 | 0.69 | 1.05 | 1.31 | -0.0109
LFNoneSDGGroExCZ14 | Com-Iltg-dWatt-LF_OSnone | SDG | Gro | Ex | CZ14 | 4.91 | 0.00069 | 0 | 5.11 | 0.000916 | -0.0564 | 4.91 | 0.00069 | 0 | 5.11 | 0.000916 | -0.0564 |  | LF | None | 4910 | 0.69 | 4910 | 0.69 | 1.04 | 1.33 | -0.011487 | 4910 | 0.69 | 4910 | 0.69 | 1.04 | 1.33 | -0.0115
LFNoneSDGGroExCZ15 | Com-Iltg-dWatt-LF_OSnone | SDG | Gro | Ex | CZ15 | 4.91 | 0.00069 | 0 | 5.51 | 0.0009 | -0.0301 | 4.91 | 0.00069 | 0 | 5.51 | 0.0009 | -0.0301 |  | LF | None | 4910 | 0.69 | 4910 | 0.69 | 1.12 | 1.3 | -0.0061303 | 4910 | 0.69 | 4910 | 0.69 | 1.12 | 1.3 | -0.00613
LFNoneSDGGroExIOU | Com-Iltg-dWatt-LF_OSnone | SDG | Gro | Ex | IOU | 4.91 | 0.00069 | 0 | 4.9678 | 0.00085082 | -0.062211 | 4.91 | 0.00069 | 0 | 4.9678 | 0.00085082 | -0.062211 |  | LF | None | 4910 | 0.69 | 4910 | 0.69 | 1.01 | 1.23 | -0.01267 | 4910 | 0.69 | 4910 | 0.69 | 1.01 | 1.23 | -0.0127
LFNoneSDGGroNewCZ06 | Com-Iltg-dWatt-LF_OSnone | SDG | Gro | New | CZ06 | 4.91 | 0.00069 | 0 | 5.22 | 0.00086 | -0.0462 | 4.91 | 0.00069 | 0 | 5.22 | 0.00086 | -0.0462 |  | LF | None | 4910 | 0.69 | 4910 | 0.69 | 1.06 | 1.25 | -0.0094094 | 4910 | 0.69 | 4910 | 0.69 | 1.06 | 1.25 | -0.00941
LFNoneSDGGroNewCZ07 | Com-Iltg-dWatt-LF_OSnone | SDG | Gro | New | CZ07 | 4.91 | 0.00069 | 0 | 5.18 | 0.000838 | -0.0462 | 4.91 | 0.00069 | 0 | 5.18 | 0.000838 | -0.0462 |  | LF | None | 4910 | 0.69 | 4910 | 0.69 | 1.05 | 1.21 | -0.0094094 | 4910 | 0.69 | 4910 | 0.69 | 1.05 | 1.21 | -0.00941
LFNoneSDGGroNewCZ08 | Com-Iltg-dWatt-LF_OSnone | SDG | Gro | New | CZ08 | 4.91 | 0.00069 | 0 | 5.28 | 0.00088 | -0.0407 | 4.91 | 0.00069 | 0 | 5.28 | 0.00088 | -0.0407 |  | LF | None | 4910 | 0.69 | 4910 | 0.69 | 1.08 | 1.28 | -0.0082892 | 4910 | 0.69 | 4910 | 0.69 | 1.08 | 1.28 | -0.00829
LFNoneSDGGroNewCZ10 | Com-Iltg-dWatt-LF_OSnone | SDG | Gro | New | CZ10 | 4.91 | 0.00069 | 0 | 5.31 | 0.000949 | -0.0435 | 4.91 | 0.00069 | 0 | 5.31 | 0.000949 | -0.0435 |  | LF | None | 4910 | 0.69 | 4910 | 0.69 | 1.08 | 1.38 | -0.0088595 | 4910 | 0.69 | 4910 | 0.69 | 1.08 | 1.38 | -0.00886
LFNoneSDGGroNewCZ14 | Com-Iltg-dWatt-LF_OSnone | SDG | Gro | New | CZ14 | 4.91 | 0.00069 | 0 | 5.29 | 0.000944 | -0.052 | 4.91 | 0.00069 | 0 | 5.29 | 0.000944 | -0.052 |  | LF | None | 4910 | 0.69 | 4910 | 0.69 | 1.08 | 1.37 | -0.010591 | 4910 | 0.69 | 4910 | 0.69 | 1.08 | 1.37 | -0.0106
LFNoneSDGGroNewCZ15 | Com-Iltg-dWatt-LF_OSnone | SDG | Gro | New | CZ15 | 4.91 | 0.00069 | 0 | 5.73 | 0.000954 | -0.024 | 4.91 | 0.00069 | 0 | 5.73 | 0.000954 | -0.024 |  | LF | None | 4910 | 0.69 | 4910 | 0.69 | 1.17 | 1.38 | -0.004888 | 4910 | 0.69 | 4910 | 0.69 | 1.17 | 1.38 | -0.00489
LFNoneSDGGroNewIOU | Com-Iltg-dWatt-LF_OSnone | SDG | Gro | New | IOU | 4.91 | 0.00069 | 0 | 5.2211 | 0.00087093 | -0.045331 | 4.91 | 0.00069 | 0 | 5.2211 | 0.00087093 | -0.045331 |  | LF | None | 4910 | 0.69 | 4910 | 0.69 | 1.06 | 1.26 | -0.0092323 | 4910 | 0.69 | 4910 | 0.69 | 1.06 | 1.26 | -0.00923
LFNoneSDGHspExCZ06 | Com-Iltg-dWatt-LF_OSnone | SDG | Hsp | Ex | CZ06 | 5.26 | 0.000827 | 0 | 6.03 | 0.00103 | -0.0271 | 5.26 | 0.000827 | 0 | 6.03 | 0.00103 | -0.0271 |  | LF | None | 5260 | 0.827 | 5260 | 0.827 | 1.15 | 1.25 | -0.0051521 | 5260 | 0.827 | 5260 | 0.827 | 1.15 | 1.25 | -0.00515
LFNoneSDGHspExCZ07 | Com-Iltg-dWatt-LF_OSnone | SDG | Hsp | Ex | CZ07 | 5.26 | 0.000827 | 0 | 6.03 | 0.00102 | -0.0248 | 5.26 | 0.000827 | 0 | 6.03 | 0.00102 | -0.0248 |  | LF | None | 5260 | 0.827 | 5260 | 0.827 | 1.15 | 1.23 | -0.0047148 | 5260 | 0.827 | 5260 | 0.827 | 1.15 | 1.23 | -0.00471
LFNoneSDGHspExCZ08 | Com-Iltg-dWatt-LF_OSnone | SDG | Hsp | Ex | CZ08 | 5.26 | 0.000827 | 0 | 6.06 | 0.00103 | -0.0267 | 5.26 | 0.000827 | 0 | 6.06 | 0.00103 | -0.0267 |  | LF | None | 5260 | 0.827 | 5260 | 0.827 | 1.15 | 1.25 | -0.005076 | 5260 | 0.827 | 5260 | 0.827 | 1.15 | 1.25 | -0.00508
LFNoneSDGHspExCZ10 | Com-Iltg-dWatt-LF_OSnone | SDG | Hsp | Ex | CZ10 | 5.26 | 0.000827 | 0 | 6.06 | 0.00106 | -0.0288 | 5.26 | 0.000827 | 0 | 6.06 | 0.00106 | -0.0288 |  | LF | None | 5260 | 0.827 | 5260 | 0.827 | 1.15 | 1.28 | -0.0054753 | 5260 | 0.827 | 5260 | 0.827 | 1.15 | 1.28 | -0.00548
LFNoneSDGHspExCZ14 | Com-Iltg-dWatt-LF_OSnone | SDG | Hsp | Ex | CZ14 | 5.26 | 0.000827 | 0 | 5.96 | 0.00105 | -0.0353 | 5.26 | 0.000827 | 0 | 5.96 | 0.00105 | -0.0353 |  | LF | None | 5260 | 0.827 | 5260 | 0.827 | 1.13 | 1.27 | -0.006711 | 5260 | 0.827 | 5260 | 0.827 | 1.13 | 1.27 | -0.00671
LFNoneSDGHspExIOU | Com-Iltg-dWatt-LF_OSnone | SDG | Hsp | Ex | IOU | 5.26 | 0.000827 | 0 | 6.0355 | 0.0010263 | -0.025509 | 5.26 | 0.000827 | 0 | 6.0355 | 0.0010263 | -0.025509 |  | LF | None | 5260 | 0.827 | 5260 | 0.827 | 1.15 | 1.24 | -0.0048495 | 5260 | 0.827 | 5260 | 0.827 | 1.15 | 1.24 | -0.00485
LFNoneSDGHspNewCZ06 | Com-Iltg-dWatt-LF_OSnone | SDG | Hsp | New | CZ06 | 5.26 | 0.000827 | 0 | 5.79 | 0.000995 | -0.0282 | 5.26 | 0.000827 | 0 | 5.79 | 0.000995 | -0.0282 |  | LF | None | 5260 | 0.827 | 5260 | 0.827 | 1.1 | 1.2 | -0.0053612 | 5260 | 0.827 | 5260 | 0.827 | 1.1 | 1.2 | -0.00536
LFNoneSDGHspNewCZ07 | Com-Iltg-dWatt-LF_OSnone | SDG | Hsp | New | CZ07 | 5.26 | 0.000827 | 0 | 5.81 | 0.000987 | -0.0234 | 5.26 | 0.000827 | 0 | 5.81 | 0.000987 | -0.0234 |  | LF | None | 5260 | 0.827 | 5260 | 0.827 | 1.1 | 1.19 | -0.0044487 | 5260 | 0.827 | 5260 | 0.827 | 1.1 | 1.19 | -0.00445
LFNoneSDGHspNewCZ08 | Com-Iltg-dWatt-LF_OSnone | SDG | Hsp | New | CZ08 | 5.26 | 0.000827 | 0 | 5.84 | 0.000998 | -0.0264 | 5.26 | 0.000827 | 0 | 5.84 | 0.000998 | -0.0264 |  | LF | None | 5260 | 0.827 | 5260 | 0.827 | 1.11 | 1.21 | -0.005019 | 5260 | 0.827 | 5260 | 0.827 | 1.11 | 1.21 | -0.00502
LFNoneSDGHspNewCZ10 | Com-Iltg-dWatt-LF_OSnone | SDG | Hsp | New | CZ10 | 5.26 | 0.000827 | 0 | 5.83 | 0.00103 | -0.0283 | 5.26 | 0.000827 | 0 | 5.83 | 0.00103 | -0.0283 |  | LF | None | 5260 | 0.827 | 5260 | 0.827 | 1.11 | 1.25 | -0.0053802 | 5260 | 0.827 | 5260 | 0.827 | 1.11 | 1.25 | -0.00538
LFNoneSDGHspNewCZ14 | Com-Iltg-dWatt-LF_OSnone | SDG | Hsp | New | CZ14 | 5.26 | 0.000827 | 0 | 5.75 | 0.00102 | -0.036 | 5.26 | 0.000827 | 0 | 5.75 | 0.00102 | -0.036 |  | LF | None | 5260 | 0.827 | 5260 | 0.827 | 1.09 | 1.23 | -0.0068441 | 5260 | 0.827 | 5260 | 0.827 | 1.09 | 1.23 | -0.00684
LFNoneSDGHspNewCZ15 | Com-Iltg-dWatt-LF_OSnone | SDG | Hsp | New | CZ15 | 5.26 | 0.000827 | 0 | 6.1 | 0.00104 | -0.0201 | 5.26 | 0.000827 | 0 | 6.1 | 0.00104 | -0.0201 |  | LF | None | 5260 | 0.827 | 5260 | 0.827 | 1.16 | 1.26 | -0.0038213 | 5260 | 0.827 | 5260 | 0.827 | 1.16 | 1.26 | -0.00382
LFNoneSDGHspNewIOU | Com-Iltg-dWatt-LF_OSnone | SDG | Hsp | New | IOU | 5.26 | 0.000827 | 0 | 5.8136 | 0.00099375 | -0.024348 | 5.26 | 0.000827 | 0 | 5.8136 | 0.00099375 | -0.024348 |  | LF | None | 5260 | 0.827 | 5260 | 0.827 | 1.11 | 1.2 | -0.0046288 | 5260 | 0.827 | 5260 | 0.827 | 1.11 | 1.2 | -0.00463
LFNoneSDGHtlExCZ06 | Com-Iltg-dWatt-LF_OSnone | SDG | Htl | Ex | CZ06 | 1.95 | 0.000242 | 0 | 2.09 | 0.000303 | -0.00487 | 1.95 | 0.000242 | 0 | 2.09 | 0.000303 | -0.00487 |  | LF | None | 1950 | 0.242 | 1950 | 0.242 | 1.07 | 1.25 | -0.0024974 | 1950 | 0.242 | 1950 | 0.242 | 1.07 | 1.25 | -0.0025
LFNoneSDGHtlExCZ07 | Com-Iltg-dWatt-LF_OSnone | SDG | Htl | Ex | CZ07 | 1.95 | 0.000242 | 0 | 2.14 | 0.000301 | -0.00393 | 1.95 | 0.000242 | 0 | 2.14 | 0.000301 | -0.00393 |  | LF | None | 1950 | 0.242 | 1950 | 0.242 | 1.1 | 1.24 | -0.0020154 | 1950 | 0.242 | 1950 | 0.242 | 1.1 | 1.24 | -0.00202
LFNoneSDGHtlExCZ08 | Com-Iltg-dWatt-LF_OSnone | SDG | Htl | Ex | CZ08 | 1.95 | 0.000242 | 0 | 2.12 | 0.000305 | -0.00432 | 1.95 | 0.000242 | 0 | 2.12 | 0.000305 | -0.00432 |  | LF | None | 1950 | 0.242 | 1950 | 0.242 | 1.09 | 1.26 | -0.0022154 | 1950 | 0.242 | 1950 | 0.242 | 1.09 | 1.26 | -0.00222
LFNoneSDGHtlExCZ10 | Com-Iltg-dWatt-LF_OSnone | SDG | Htl | Ex | CZ10 | 1.95 | 0.000242 | 0 | 2.09 | 0.000309 | -0.00483 | 1.95 | 0.000242 | 0 | 2.09 | 0.000309 | -0.00483 |  | LF | None | 1950 | 0.242 | 1950 | 0.242 | 1.07 | 1.28 | -0.0024769 | 1950 | 0.242 | 1950 | 0.242 | 1.07 | 1.28 | -0.00248
LFNoneSDGHtlExCZ14 | Com-Iltg-dWatt-LF_OSnone | SDG | Htl | Ex | CZ14 | 1.95 | 0.000242 | 0 | 1.99 | 0.000311 | -0.00649 | 1.95 | 0.000242 | 0 | 1.99 | 0.000311 | -0.00649 |  | LF | None | 1950 | 0.242 | 1950 | 0.242 | 1.02 | 1.29 | -0.0033282 | 1950 | 0.242 | 1950 | 0.242 | 1.02 | 1.29 | -0.00333
LFNoneSDGHtlExCZ15 | Com-Iltg-dWatt-LF_OSnone | SDG | Htl | Ex | CZ15 | 1.95 | 0.000242 | 0 | 2.26 | 0.000312 | -0.00279 | 1.95 | 0.000242 | 0 | 2.26 | 0.000312 | -0.00279 |  | LF | None | 1950 | 0.242 | 1950 | 0.242 | 1.16 | 1.29 | -0.0014308 | 1950 | 0.242 | 1950 | 0.242 | 1.16 | 1.29 | -0.00143
LFNoneSDGHtlExIOU | Com-Iltg-dWatt-LF_OSnone | SDG | Htl | Ex | IOU | 1.95 | 0.000242 | 0 | 2.1328 | 0.00030208 | -0.0040726 | 1.95 | 0.000242 | 0 | 2.1328 | 0.00030208 | -0.0040726 |  | LF | None | 1950 | 0.242 | 1950 | 0.242 | 1.09 | 1.25 | -0.0020885 | 1950 | 0.242 | 1950 | 0.242 | 1.09 | 1.25 | -0.00209
LFNoneSDGHtlNewCZ06 | Com-Iltg-dWatt-LF_OSnone | SDG | Htl | New | CZ06 | 1.95 | 0.000242 | 0 | 2.07 | 0.000311 | -0.00471 | 1.95 | 0.000242 | 0 | 2.07 | 0.000311 | -0.00471 |  | LF | None | 1950 | 0.242 | 1950 | 0.242 | 1.06 | 1.29 | -0.0024154 | 1950 | 0.242 | 1950 | 0.242 | 1.06 | 1.29 | -0.00242
LFNoneSDGHtlNewCZ07 | Com-Iltg-dWatt-LF_OSnone | SDG | Htl | New | CZ07 | 1.95 | 0.000242 | 0 | 2.11 | 0.000305 | -0.00314 | 1.95 | 0.000242 | 0 | 2.11 | 0.000305 | -0.00314 |  | LF | None | 1950 | 0.242 | 1950 | 0.242 | 1.08 | 1.26 | -0.0016103 | 1950 | 0.242 | 1950 | 0.242 | 1.08 | 1.26 | -0.00161
LFNoneSDGHtlNewCZ08 | Com-Iltg-dWatt-LF_OSnone | SDG | Htl | New | CZ08 | 1.95 | 0.000242 | 0 | 2.11 | 0.000313 | -0.00403 | 1.95 | 0.000242 | 0 | 2.11 | 0.000313 | -0.00403 |  | LF | None | 1950 | 0.242 | 1950 | 0.242 | 1.08 | 1.29 | -0.0020667 | 1950 | 0.242 | 1950 | 0.242 | 1.08 | 1.29 | -0.00207
LFNoneSDGHtlNewCZ10 | Com-Iltg-dWatt-LF_OSnone | SDG | Htl | New | CZ10 | 1.95 | 0.000242 | 0 | 2.07 | 0.000324 | -0.0052 | 1.95 | 0.000242 | 0 | 2.07 | 0.000324 | -0.0052 |  | LF | None | 1950 | 0.242 | 1950 | 0.242 | 1.06 | 1.34 | -0.0026667 | 1950 | 0.242 | 1950 | 0.242 | 1.06 | 1.34 | -0.00267
LFNoneSDGHtlNewCZ14 | Com-Iltg-dWatt-LF_OSnone | SDG | Htl | New | CZ14 | 1.95 | 0.000242 | 0 | 1.96 | 0.000322 | -0.00771 | 1.95 | 0.000242 | 0 | 1.96 | 0.000322 | -0.00771 |  | LF | None | 1950 | 0.242 | 1950 | 0.242 | 1.01 | 1.33 | -0.0039538 | 1950 | 0.242 | 1950 | 0.242 | 1.01 | 1.33 | -0.00395
LFNoneSDGHtlNewCZ15 | Com-Iltg-dWatt-LF_OSnone | SDG | Htl | New | CZ15 | 1.95 | 0.000242 | 0 | 2.27 | 0.000327 | -0.00275 | 1.95 | 0.000242 | 0 | 2.27 | 0.000327 | -0.00275 |  | LF | None | 1950 | 0.242 | 1950 | 0.242 | 1.16 | 1.35 | -0.0014103 | 1950 | 0.242 | 1950 | 0.242 | 1.16 | 1.35 | -0.00141
LFNoneSDGHtlNewIOU | Com-Iltg-dWatt-LF_OSnone | SDG | Htl | New | IOU | 1.95 | 0.000242 | 0 | 2.1047 | 0.00030752 | -0.0034516 | 1.95 | 0.000242 | 0 | 2.1047 | 0.00030752 | -0.0034516 |  | LF | None | 1950 | 0.242 | 1950 | 0.242 | 1.08 | 1.27 | -0.00177 | 1950 | 0.242 | 1950 | 0.242 | 1.08 | 1.27 | -0.00177
LFNoneSDGMBTExCZ06 | Com-Iltg-dWatt-LF_OSnone | SDG | MBT | Ex | CZ06 | 3.53 | 0.000851 | 0 | 4.11 | 0.00103 | -0.000931 | 3.53 | 0.000851 | 0 | 4.11 | 0.00103 | -0.000931 |  | LF | None | 3530 | 0.851 | 3530 | 0.851 | 1.16 | 1.21 | -0.00026374 | 3530 | 0.851 | 3530 | 0.851 | 1.16 | 1.21 | -0.000264
LFNoneSDGMBTExCZ07 | Com-Iltg-dWatt-LF_OSnone | SDG | MBT | Ex | CZ07 | 3.53 | 0.000851 | 0 | 4.12 | 0.00102 | -0.000182 | 3.53 | 0.000851 | 0 | 4.12 | 0.00102 | -0.000182 |  | LF | None | 3530 | 0.851 | 3530 | 0.851 | 1.17 | 1.2 | -5.1558e-05 | 3530 | 0.851 | 3530 | 0.851 | 1.17 | 1.2 | -5.16e-05
LFNoneSDGMBTExCZ08 | Com-Iltg-dWatt-LF_OSnone | SDG | MBT | Ex | CZ08 | 3.53 | 0.000851 | 0 | 4.11 | 0.00108 | -0.000593 | 3.53 | 0.000851 | 0 | 4.11 | 0.00108 | -0.000593 |  | LF | None | 3530 | 0.851 | 3530 | 0.851 | 1.16 | 1.27 | -0.00016799 | 3530 | 0.851 | 3530 | 0.851 | 1.16 | 1.27 | -0.000168
LFNoneSDGMBTExCZ10 | Com-Iltg-dWatt-LF_OSnone | SDG | MBT | Ex | CZ10 | 3.53 | 0.000851 | 0 | 4.09 | 0.0011 | -0.00121 | 3.53 | 0.000851 | 0 | 4.09 | 0.0011 | -0.00121 |  | LF | None | 3530 | 0.851 | 3530 | 0.851 | 1.16 | 1.29 | -0.00034278 | 3530 | 0.851 | 3530 | 0.851 | 1.16 | 1.29 | -0.000343
LFNoneSDGMBTExCZ14 | Com-Iltg-dWatt-LF_OSnone | SDG | MBT | Ex | CZ14 | 3.53 | 0.000851 | 0 | 4.03 | 0.0011 | -0.00291 | 3.53 | 0.000851 | 0 | 4.03 | 0.0011 | -0.00291 |  | LF | None | 3530 | 0.851 | 3530 | 0.851 | 1.14 | 1.29 | -0.00082436 | 3530 | 0.851 | 3530 | 0.851 | 1.14 | 1.29 | -0.000824
LFNoneSDGMBTExCZ15 | Com-Iltg-dWatt-LF_OSnone | SDG | MBT | Ex | CZ15 | 3.53 | 0.000851 | 0 | 4.26 | 0.00111 | 0 | 3.53 | 0.000851 | 0 | 4.26 | 0.00111 | 0 |  | LF | None | 3530 | 0.851 | 3530 | 0.851 | 1.21 | 1.3 | 0 | 3530 | 0.851 | 3530 | 0.851 | 1.21 | 1.3 | 0
LFNoneSDGMBTExIOU | Com-Iltg-dWatt-LF_OSnone | SDG | MBT | Ex | IOU | 3.53 | 0.000851 | 0 | 4.11 | 0.0010468 | -0.00055189 | 3.53 | 0.000851 | 0 | 4.11 | 0.0010468 | -0.00055189 |  | LF | None | 3530 | 0.851 | 3530 | 0.851 | 1.16 | 1.23 | -0.00015634 | 3530 | 0.851 | 3530 | 0.851 | 1.16 | 1.23 | -0.000156
LFNoneSDGMBTNewCZ06 | Com-Iltg-dWatt-LF_OSnone | SDG | MBT | New | CZ06 | 3.53 | 0.000851 | 0 | 3.98 | 0.00107 | -0.00122 | 3.53 | 0.000851 | 0 | 3.98 | 0.00107 | -0.00122 |  | LF | None | 3530 | 0.851 | 3530 | 0.851 | 1.13 | 1.26 | -0.00034561 | 3530 | 0.851 | 3530 | 0.851 | 1.13 | 1.26 | -0.000346
LFNoneSDGMBTNewCZ07 | Com-Iltg-dWatt-LF_OSnone | SDG | MBT | New | CZ07 | 3.53 | 0.000851 | 0 | 3.97 | 0.00106 | 0 | 3.53 | 0.000851 | 0 | 3.97 | 0.00106 | 0 |  | LF | None | 3530 | 0.851 | 3530 | 0.851 | 1.12 | 1.25 | 0 | 3530 | 0.851 | 3530 | 0.851 | 1.12 | 1.25 | 0
LFNoneSDGMBTNewCZ08 | Com-Iltg-dWatt-LF_OSnone | SDG | MBT | New | CZ08 | 3.53 | 0.000851 | 0 | 3.99 | 0.0011 | -0.000974 | 3.53 | 0.000851 | 0 | 3.99 | 0.0011 | -0.000974 |  | LF | None | 3530 | 0.851 | 3530 | 0.851 | 1.13 | 1.29 | -0.00027592 | 3530 | 0.851 | 3530 | 0.851 | 1.13 | 1.29 | -0.000276
LFNoneSDGMBTNewCZ10 | Com-Iltg-dWatt-LF_OSnone | SDG | MBT | New | CZ10 | 3.53 | 0.000851 | 0 | 4 | 0.00115 | -0.00122 | 3.53 | 0.000851 | 0 | 4 | 0.00115 | -0.00122 |  | LF | None | 3530 | 0.851 | 3530 | 0.851 | 1.13 | 1.35 | -0.00034561 | 3530 | 0.851 | 3530 | 0.851 | 1.13 | 1.35 | -0.000346
LFNoneSDGMBTNewCZ14 | Com-Iltg-dWatt-LF_OSnone | SDG | MBT | New | CZ14 | 3.53 | 0.000851 | 0 | 3.96 | 0.00114 | -0.00231 | 3.53 | 0.000851 | 0 | 3.96 | 0.00114 | -0.00231 |  | LF | None | 3530 | 0.851 | 3530 | 0.851 | 1.12 | 1.34 | -0.00065439 | 3530 | 0.851 | 3530 | 0.851 | 1.12 | 1.34 | -0.000654
LFNoneSDGMBTNewCZ15 | Com-Iltg-dWatt-LF_OSnone | SDG | MBT | New | CZ15 | 3.53 | 0.000851 | 0 | 4.21 | 0.00115 | 0 | 3.53 | 0.000851 | 0 | 4.21 | 0.00115 | 0 |  | LF | None | 3530 | 0.851 | 3530 | 0.851 | 1.19 | 1.35 | 0 | 3530 | 0.851 | 3530 | 0.851 | 1.19 | 1.35 | 0
LFNoneSDGMBTNewIOU | Com-Iltg-dWatt-LF_OSnone | SDG | MBT | New | IOU | 3.53 | 0.000851 | 0 | 3.9805 | 0.0010895 | -0.00045141 | 3.53 | 0.000851 | 0 | 3.9805 | 0.0010895 | -0.00045141 |  | LF | None | 3530 | 0.851 | 3530 | 0.851 | 1.13 | 1.28 | -0.00012788 | 3530 | 0.851 | 3530 | 0.851 | 1.13 | 1.28 | -0.000128
LFNoneSDGMLIExCZ06 | Com-Iltg-dWatt-LF_OSnone | SDG | MLI | Ex | CZ06 | 3.22 | 0.000924 | 0 | 3.48 | 0.00111 | -0.00676 | 3.22 | 0.000924 | 0 | 3.48 | 0.00111 | -0.00676 |  | LF | None | 3220 | 0.924 | 3220 | 0.924 | 1.08 | 1.2 | -0.0020994 | 3220 | 0.924 | 3220 | 0.924 | 1.08 | 1.2 | -0.0021
LFNoneSDGMLIExCZ07 | Com-Iltg-dWatt-LF_OSnone | SDG | MLI | Ex | CZ07 | 3.22 | 0.000924 | 0 | 3.47 | 0.0011 | -0.00338 | 3.22 | 0.000924 | 0 | 3.47 | 0.0011 | -0.00338 |  | LF | None | 3220 | 0.924 | 3220 | 0.924 | 1.08 | 1.19 | -0.0010497 | 3220 | 0.924 | 3220 | 0.924 | 1.08 | 1.19 | -0.00105
LFNoneSDGMLIExCZ08 | Com-Iltg-dWatt-LF_OSnone | SDG | MLI | Ex | CZ08 | 3.22 | 0.000924 | 0 | 3.51 | 0.00111 | -0.00553 | 3.22 | 0.000924 | 0 | 3.51 | 0.00111 | -0.00553 |  | LF | None | 3220 | 0.924 | 3220 | 0.924 | 1.09 | 1.2 | -0.0017174 | 3220 | 0.924 | 3220 | 0.924 | 1.09 | 1.2 | -0.00172
LFNoneSDGMLIExCZ10 | Com-Iltg-dWatt-LF_OSnone | SDG | MLI | Ex | CZ10 | 3.22 | 0.000924 | 0 | 3.5 | 0.00114 | -0.00762 | 3.22 | 0.000924 | 0 | 3.5 | 0.00114 | -0.00762 |  | LF | None | 3220 | 0.924 | 3220 | 0.924 | 1.09 | 1.23 | -0.0023665 | 3220 | 0.924 | 3220 | 0.924 | 1.09 | 1.23 | -0.00237
LFNoneSDGMLIExCZ14 | Com-Iltg-dWatt-LF_OSnone | SDG | MLI | Ex | CZ14 | 3.22 | 0.000924 | 0 | 3.4 | 0.00112 | -0.0216 | 3.22 | 0.000924 | 0 | 3.4 | 0.00112 | -0.0216 |  | LF | None | 3220 | 0.924 | 3220 | 0.924 | 1.06 | 1.21 | -0.0067081 | 3220 | 0.924 | 3220 | 0.924 | 1.06 | 1.21 | -0.00671
LFNoneSDGMLIExCZ15 | Com-Iltg-dWatt-LF_OSnone | SDG | MLI | Ex | CZ15 | 3.22 | 0.000924 | 0 | 3.76 | 0.00112 | -0.00207 | 3.22 | 0.000924 | 0 | 3.76 | 0.00112 | -0.00207 |  | LF | None | 3220 | 0.924 | 3220 | 0.924 | 1.17 | 1.21 | -0.00064286 | 3220 | 0.924 | 3220 | 0.924 | 1.17 | 1.21 | -0.000643
LFNoneSDGMLIExIOU | Com-Iltg-dWatt-LF_OSnone | SDG | MLI | Ex | IOU | 3.22 | 0.000924 | 0 | 3.4805 | 0.0011129 | -0.0049886 | 3.22 | 0.000924 | 0 | 3.4805 | 0.0011129 | -0.0049886 |  | LF | None | 3220 | 0.924 | 3220 | 0.924 | 1.08 | 1.2 | -0.0015493 | 3220 | 0.924 | 3220 | 0.924 | 1.08 | 1.2 | -0.00155
LFNoneSDGMLINewCZ06 | Com-Iltg-dWatt-LF_OSnone | SDG | MLI | New | CZ06 | 3.22 | 0.000924 | 0 | 3.46 | 0.00114 | -0.00968 | 3.22 | 0.000924 | 0 | 3.46 | 0.00114 | -0.00968 |  | LF | None | 3220 | 0.924 | 3220 | 0.924 | 1.07 | 1.23 | -0.0030062 | 3220 | 0.924 | 3220 | 0.924 | 1.07 | 1.23 | -0.00301
LFNoneSDGMLINewCZ07 | Com-Iltg-dWatt-LF_OSnone | SDG | MLI | New | CZ07 | 3.22 | 0.000924 | 0 | 3.41 | 0.0011 | -0.00495 | 3.22 | 0.000924 | 0 | 3.41 | 0.0011 | -0.00495 |  | LF | None | 3220 | 0.924 | 3220 | 0.924 | 1.06 | 1.19 | -0.0015373 | 3220 | 0.924 | 3220 | 0.924 | 1.06 | 1.19 | -0.00154
LFNoneSDGMLINewCZ08 | Com-Iltg-dWatt-LF_OSnone | SDG | MLI | New | CZ08 | 3.22 | 0.000924 | 0 | 3.51 | 0.00115 | -0.00753 | 3.22 | 0.000924 | 0 | 3.51 | 0.00115 | -0.00753 |  | LF | None | 3220 | 0.924 | 3220 | 0.924 | 1.09 | 1.24 | -0.0023385 | 3220 | 0.924 | 3220 | 0.924 | 1.09 | 1.24 | -0.00234
LFNoneSDGMLINewCZ10 | Com-Iltg-dWatt-LF_OSnone | SDG | MLI | New | CZ10 | 3.22 | 0.000924 | 0 | 3.56 | 0.00122 | -0.00926 | 3.22 | 0.000924 | 0 | 3.56 | 0.00122 | -0.00926 |  | LF | None | 3220 | 0.924 | 3220 | 0.924 | 1.11 | 1.32 | -0.0028758 | 3220 | 0.924 | 3220 | 0.924 | 1.11 | 1.32 | -0.00288
LFNoneSDGMLINewCZ14 | Com-Iltg-dWatt-LF_OSnone | SDG | MLI | New | CZ14 | 3.22 | 0.000924 | 0 | 3.49 | 0.00121 | -0.0209 | 3.22 | 0.000924 | 0 | 3.49 | 0.00121 | -0.0209 |  | LF | None | 3220 | 0.924 | 3220 | 0.924 | 1.08 | 1.31 | -0.0064907 | 3220 | 0.924 | 3220 | 0.924 | 1.08 | 1.31 | -0.00649
LFNoneSDGMLINewCZ15 | Com-Iltg-dWatt-LF_OSnone | SDG | MLI | New | CZ15 | 3.22 | 0.000924 | 0 | 3.8 | 0.00124 | -0.00143 | 3.22 | 0.000924 | 0 | 3.8 | 0.00124 | -0.00143 |  | LF | None | 3220 | 0.924 | 3220 | 0.924 | 1.18 | 1.34 | -0.0004441 | 3220 | 0.924 | 3220 | 0.924 | 1.18 | 1.34 | -0.000444
LFNoneSDGMLINewIOU | Com-Iltg-dWatt-LF_OSnone | SDG | MLI | New | IOU | 3.22 | 0.000924 | 0 | 3.4611 | 0.0011402 | -0.0066044 | 3.22 | 0.000924 | 0 | 3.4611 | 0.0011402 | -0.0066044 |  | LF | None | 3220 | 0.924 | 3220 | 0.924 | 1.07 | 1.23 | -0.0020511 | 3220 | 0.924 | 3220 | 0.924 | 1.07 | 1.23 | -0.00205
LFNoneSDGMtlExCZ06 | Com-Iltg-dWatt-LF_OSnone | SDG | Mtl | Ex | CZ06 | 1.55 | 0.000172 | 0 | 1.73 | 0.000216 | -0.005 | 1.55 | 0.000172 | 0 | 1.73 | 0.000216 | -0.005 |  | LF | None | 1550 | 0.172 | 1550 | 0.172 | 1.12 | 1.26 | -0.0032258 | 1550 | 0.172 | 1550 | 0.172 | 1.12 | 1.26 | -0.00323
LFNoneSDGMtlExCZ07 | Com-Iltg-dWatt-LF_OSnone | SDG | Mtl | Ex | CZ07 | 1.55 | 0.000172 | 0 | 1.78 | 0.000215 | -0.00366 | 1.55 | 0.000172 | 0 | 1.78 | 0.000215 | -0.00366 |  | LF | None | 1550 | 0.172 | 1550 | 0.172 | 1.15 | 1.25 | -0.0023613 | 1550 | 0.172 | 1550 | 0.172 | 1.15 | 1.25 | -0.00236
LFNoneSDGMtlExCZ08 | Com-Iltg-dWatt-LF_OSnone | SDG | Mtl | Ex | CZ08 | 1.55 | 0.000172 | 0 | 1.76 | 0.000219 | -0.00421 | 1.55 | 0.000172 | 0 | 1.76 | 0.000219 | -0.00421 |  | LF | None | 1550 | 0.172 | 1550 | 0.172 | 1.14 | 1.27 | -0.0027161 | 1550 | 0.172 | 1550 | 0.172 | 1.14 | 1.27 | -0.00272
LFNoneSDGMtlExCZ10 | Com-Iltg-dWatt-LF_OSnone | SDG | Mtl | Ex | CZ10 | 1.55 | 0.000172 | 0 | 1.74 | 0.000225 | -0.00494 | 1.55 | 0.000172 | 0 | 1.74 | 0.000225 | -0.00494 |  | LF | None | 1550 | 0.172 | 1550 | 0.172 | 1.12 | 1.31 | -0.0031871 | 1550 | 0.172 | 1550 | 0.172 | 1.12 | 1.31 | -0.00319
LFNoneSDGMtlExCZ14 | Com-Iltg-dWatt-LF_OSnone | SDG | Mtl | Ex | CZ14 | 1.55 | 0.000172 | 0 | 1.68 | 0.000225 | -0.00678 | 1.55 | 0.000172 | 0 | 1.68 | 0.000225 | -0.00678 |  | LF | None | 1550 | 0.172 | 1550 | 0.172 | 1.08 | 1.31 | -0.0043742 | 1550 | 0.172 | 1550 | 0.172 | 1.08 | 1.31 | -0.00437
LFNoneSDGMtlExCZ15 | Com-Iltg-dWatt-LF_OSnone | SDG | Mtl | Ex | CZ15 | 1.55 | 0.000172 | 0 | 1.86 | 0.000229 | -0.00208 | 1.55 | 0.000172 | 0 | 1.86 | 0.000229 | -0.00208 |  | LF | None | 1550 | 0.172 | 1550 | 0.172 | 1.2 | 1.33 | -0.0013419 | 1550 | 0.172 | 1550 | 0.172 | 1.2 | 1.33 | -0.00134
LFNoneSDGMtlExIOU | Com-Iltg-dWatt-LF_OSnone | SDG | Mtl | Ex | IOU | 1.55 | 0.000172 | 0 | 1.7737 | 0.00021626 | -0.0038585 | 1.55 | 0.000172 | 0 | 1.7737 | 0.00021626 | -0.0038585 |  | LF | None | 1550 | 0.172 | 1550 | 0.172 | 1.14 | 1.26 | -0.0024893 | 1550 | 0.172 | 1550 | 0.172 | 1.14 | 1.26 | -0.00249
LFNoneSDGMtlNewCZ06 | Com-Iltg-dWatt-LF_OSnone | SDG | Mtl | New | CZ06 | 1.55 | 0.000172 | 0 | 1.71 | 0.000221 | -0.00681 | 1.55 | 0.000172 | 0 | 1.71 | 0.000221 | -0.00681 |  | LF | None | 1550 | 0.172 | 1550 | 0.172 | 1.1 | 1.28 | -0.0043935 | 1550 | 0.172 | 1550 | 0.172 | 1.1 | 1.28 | -0.00439
LFNoneSDGMtlNewCZ07 | Com-Iltg-dWatt-LF_OSnone | SDG | Mtl | New | CZ07 | 1.55 | 0.000172 | 0 | 1.74 | 0.000216 | -0.00489 | 1.55 | 0.000172 | 0 | 1.74 | 0.000216 | -0.00489 |  | LF | None | 1550 | 0.172 | 1550 | 0.172 | 1.12 | 1.26 | -0.0031548 | 1550 | 0.172 | 1550 | 0.172 | 1.12 | 1.26 | -0.00315
LFNoneSDGMtlNewCZ08 | Com-Iltg-dWatt-LF_OSnone | SDG | Mtl | New | CZ08 | 1.55 | 0.000172 | 0 | 1.75 | 0.000225 | -0.00563 | 1.55 | 0.000172 | 0 | 1.75 | 0.000225 | -0.00563 |  | LF | None | 1550 | 0.172 | 1550 | 0.172 | 1.13 | 1.31 | -0.0036323 | 1550 | 0.172 | 1550 | 0.172 | 1.13 | 1.31 | -0.00363
LFNoneSDGMtlNewCZ10 | Com-Iltg-dWatt-LF_OSnone | SDG | Mtl | New | CZ10 | 1.55 | 0.000172 | 0 | 1.71 | 0.000229 | -0.00692 | 1.55 | 0.000172 | 0 | 1.71 | 0.000229 | -0.00692 |  | LF | None | 1550 | 0.172 | 1550 | 0.172 | 1.1 | 1.33 | -0.0044645 | 1550 | 0.172 | 1550 | 0.172 | 1.1 | 1.33 | -0.00446
LFNoneSDGMtlNewCZ14 | Com-Iltg-dWatt-LF_OSnone | SDG | Mtl | New | CZ14 | 1.55 | 0.000172 | 0 | 1.63 | 0.000229 | -0.00902 | 1.55 | 0.000172 | 0 | 1.63 | 0.000229 | -0.00902 |  | LF | None | 1550 | 0.172 | 1550 | 0.172 | 1.05 | 1.33 | -0.0058194 | 1550 | 0.172 | 1550 | 0.172 | 1.05 | 1.33 | -0.00582
LFNoneSDGMtlNewCZ15 | Com-Iltg-dWatt-LF_OSnone | SDG | Mtl | New | CZ15 | 1.55 | 0.000172 | 0 | 1.85 | 0.000233 | -0.00324 | 1.55 | 0.000172 | 0 | 1.85 | 0.000233 | -0.00324 |  | LF | None | 1550 | 0.172 | 1550 | 0.172 | 1.19 | 1.35 | -0.0020903 | 1550 | 0.172 | 1550 | 0.172 | 1.19 | 1.35 | -0.00209
LFNoneSDGMtlNewIOU | Com-Iltg-dWatt-LF_OSnone | SDG | Mtl | New | IOU | 1.55 | 0.000172 | 0 | 1.736 | 0.00021781 | -0.0051966 | 1.55 | 0.000172 | 0 | 1.736 | 0.00021781 | -0.0051966 |  | LF | None | 1550 | 0.172 | 1550 | 0.172 | 1.12 | 1.27 | -0.0033526 | 1550 | 0.172 | 1550 | 0.172 | 1.12 | 1.27 | -0.00335
LFNoneSDGNrsExCZ06 | Com-Iltg-dWatt-LF_OSnone | SDG | Nrs | Ex | CZ06 | 4.16 | 0.000676 | 0 | 4.47 | 0.00088 | -0.0428 | 4.16 | 0.000676 | 0 | 4.47 | 0.00088 | -0.0428 |  | LF | None | 4160 | 0.676 | 4160 | 0.676 | 1.07 | 1.3 | -0.010288 | 4160 | 0.676 | 4160 | 0.676 | 1.07 | 1.3 | -0.0103
LFNoneSDGNrsExCZ07 | Com-Iltg-dWatt-LF_OSnone | SDG | Nrs | Ex | CZ07 | 4.16 | 0.000676 | 0 | 4.45 | 0.000867 | -0.0391 | 4.16 | 0.000676 | 0 | 4.45 | 0.000867 | -0.0391 |  | LF | None | 4160 | 0.676 | 4160 | 0.676 | 1.07 | 1.28 | -0.009399 | 4160 | 0.676 | 4160 | 0.676 | 1.07 | 1.28 | -0.0094
LFNoneSDGNrsExCZ08 | Com-Iltg-dWatt-LF_OSnone | SDG | Nrs | Ex | CZ08 | 4.16 | 0.000676 | 0 | 4.52 | 0.000877 | -0.0415 | 4.16 | 0.000676 | 0 | 4.52 | 0.000877 | -0.0415 |  | LF | None | 4160 | 0.676 | 4160 | 0.676 | 1.09 | 1.3 | -0.009976 | 4160 | 0.676 | 4160 | 0.676 | 1.09 | 1.3 | -0.00998
LFNoneSDGNrsExCZ10 | Com-Iltg-dWatt-LF_OSnone | SDG | Nrs | Ex | CZ10 | 4.16 | 0.000676 | 0 | 4.54 | 0.000913 | -0.0441 | 4.16 | 0.000676 | 0 | 4.54 | 0.000913 | -0.0441 |  | LF | None | 4160 | 0.676 | 4160 | 0.676 | 1.09 | 1.35 | -0.010601 | 4160 | 0.676 | 4160 | 0.676 | 1.09 | 1.35 | -0.0106
LFNoneSDGNrsExCZ14 | Com-Iltg-dWatt-LF_OSnone | SDG | Nrs | Ex | CZ14 | 4.16 | 0.000676 | 0 | 4.48 | 0.000896 | -0.0515 | 4.16 | 0.000676 | 0 | 4.48 | 0.000896 | -0.0515 |  | LF | None | 4160 | 0.676 | 4160 | 0.676 | 1.08 | 1.33 | -0.01238 | 4160 | 0.676 | 4160 | 0.676 | 1.08 | 1.33 | -0.0124
LFNoneSDGNrsExIOU | Com-Iltg-dWatt-LF_OSnone | SDG | Nrs | Ex | IOU | 4.16 | 0.000676 | 0 | 4.4662 | 0.00087424 | -0.040007 | 4.16 | 0.000676 | 0 | 4.4662 | 0.00087424 | -0.040007 |  | LF | None | 4160 | 0.676 | 4160 | 0.676 | 1.07 | 1.29 | -0.009617 | 4160 | 0.676 | 4160 | 0.676 | 1.07 | 1.29 | -0.00962
LFNoneSDGNrsNewCZ06 | Com-Iltg-dWatt-LF_OSnone | SDG | Nrs | New | CZ06 | 4.16 | 0.000676 | 0 | 4.3 | 0.000865 | -0.0482 | 4.16 | 0.000676 | 0 | 4.3 | 0.000865 | -0.0482 |  | LF | None | 4160 | 0.676 | 4160 | 0.676 | 1.03 | 1.28 | -0.011587 | 4160 | 0.676 | 4160 | 0.676 | 1.03 | 1.28 | -0.0116
LFNoneSDGNrsNewCZ07 | Com-Iltg-dWatt-LF_OSnone | SDG | Nrs | New | CZ07 | 4.16 | 0.000676 | 0 | 4.26 | 0.000868 | -0.0457 | 4.16 | 0.000676 | 0 | 4.26 | 0.000868 | -0.0457 |  | LF | None | 4160 | 0.676 | 4160 | 0.676 | 1.02 | 1.28 | -0.010986 | 4160 | 0.676 | 4160 | 0.676 | 1.02 | 1.28 | -0.011
LFNoneSDGNrsNewCZ08 | Com-Iltg-dWatt-LF_OSnone | SDG | Nrs | New | CZ08 | 4.16 | 0.000676 | 0 | 4.38 | 0.00087 | -0.0453 | 4.16 | 0.000676 | 0 | 4.38 | 0.00087 | -0.0453 |  | LF | None | 4160 | 0.676 | 4160 | 0.676 | 1.05 | 1.29 | -0.010889 | 4160 | 0.676 | 4160 | 0.676 | 1.05 | 1.29 | -0.0109
LFNoneSDGNrsNewCZ10 | Com-Iltg-dWatt-LF_OSnone | SDG | Nrs | New | CZ10 | 4.16 | 0.000676 | 0 | 4.43 | 0.000907 | -0.0428 | 4.16 | 0.000676 | 0 | 4.43 | 0.000907 | -0.0428 |  | LF | None | 4160 | 0.676 | 4160 | 0.676 | 1.06 | 1.34 | -0.010288 | 4160 | 0.676 | 4160 | 0.676 | 1.06 | 1.34 | -0.0103
LFNoneSDGNrsNewCZ14 | Com-Iltg-dWatt-LF_OSnone | SDG | Nrs | New | CZ14 | 4.16 | 0.000676 | 0 | 4.39 | 0.000877 | -0.0565 | 4.16 | 0.000676 | 0 | 4.39 | 0.000877 | -0.0565 |  | LF | None | 4160 | 0.676 | 4160 | 0.676 | 1.06 | 1.3 | -0.013582 | 4160 | 0.676 | 4160 | 0.676 | 1.06 | 1.3 | -0.0136
LFNoneSDGNrsNewCZ15 | Com-Iltg-dWatt-LF_OSnone | SDG | Nrs | New | CZ15 | 4.16 | 0.000676 | 0 | 4.77 | 0.0009 | -0.0261 | 4.16 | 0.000676 | 0 | 4.77 | 0.0009 | -0.0261 |  | LF | None | 4160 | 0.676 | 4160 | 0.676 | 1.15 | 1.33 | -0.006274 | 4160 | 0.676 | 4160 | 0.676 | 1.15 | 1.33 | -0.00627
LFNoneSDGNrsNewIOU | Com-Iltg-dWatt-LF_OSnone | SDG | Nrs | New | IOU | 4.16 | 0.000676 | 0 | 4.2903 | 0.0008735 | -0.045344 | 4.16 | 0.000676 | 0 | 4.2903 | 0.0008735 | -0.045344 |  | LF | None | 4160 | 0.676 | 4160 | 0.676 | 1.03 | 1.29 | -0.0109 | 4160 | 0.676 | 4160 | 0.676 | 1.03 | 1.29 | -0.0109
LFNoneSDGOfLExCZ06 | Com-Iltg-dWatt-LF_OSnone | SDG | OfL | Ex | CZ06 | 2.64 | 0.00071 | 0 | 3.07 | 0.000903 | -0.00602 | 2.64 | 0.00071 | 0 | 3.07 | 0.000903 | -0.00602 |  | LF | None | 2640 | 0.71 | 2640 | 0.71 | 1.16 | 1.27 | -0.0022803 | 2640 | 0.71 | 2640 | 0.71 | 1.16 | 1.27 | -0.00228
LFNoneSDGOfLExCZ07 | Com-Iltg-dWatt-LF_OSnone | SDG | OfL | Ex | CZ07 | 2.64 | 0.00071 | 0 | 3.06 | 0.000894 | -0.00533 | 2.64 | 0.00071 | 0 | 3.06 | 0.000894 | -0.00533 |  | LF | None | 2640 | 0.71 | 2640 | 0.71 | 1.16 | 1.26 | -0.0020189 | 2640 | 0.71 | 2640 | 0.71 | 1.16 | 1.26 | -0.00202
LFNoneSDGOfLExCZ08 | Com-Iltg-dWatt-LF_OSnone | SDG | OfL | Ex | CZ08 | 2.64 | 0.00071 | 0 | 3.08 | 0.000912 | -0.006 | 2.64 | 0.00071 | 0 | 3.08 | 0.000912 | -0.006 |  | LF | None | 2640 | 0.71 | 2640 | 0.71 | 1.17 | 1.28 | -0.0022727 | 2640 | 0.71 | 2640 | 0.71 | 1.17 | 1.28 | -0.00227
LFNoneSDGOfLExCZ10 | Com-Iltg-dWatt-LF_OSnone | SDG | OfL | Ex | CZ10 | 2.64 | 0.00071 | 0 | 3.07 | 0.000925 | -0.00705 | 2.64 | 0.00071 | 0 | 3.07 | 0.000925 | -0.00705 |  | LF | None | 2640 | 0.71 | 2640 | 0.71 | 1.16 | 1.3 | -0.0026705 | 2640 | 0.71 | 2640 | 0.71 | 1.16 | 1.3 | -0.00267
LFNoneSDGOfLExCZ14 | Com-Iltg-dWatt-LF_OSnone | SDG | OfL | Ex | CZ14 | 2.64 | 0.00071 | 0 | 3.03 | 0.00092 | -0.00882 | 2.64 | 0.00071 | 0 | 3.03 | 0.00092 | -0.00882 |  | LF | None | 2640 | 0.71 | 2640 | 0.71 | 1.15 | 1.3 | -0.0033409 | 2640 | 0.71 | 2640 | 0.71 | 1.15 | 1.3 | -0.00334
LFNoneSDGOfLExCZ15 | Com-Iltg-dWatt-LF_OSnone | SDG | OfL | Ex | CZ15 | 2.64 | 0.00071 | 0 | 3.22 | 0.00093 | -0.00409 | 2.64 | 0.00071 | 0 | 3.22 | 0.00093 | -0.00409 |  | LF | None | 2640 | 0.71 | 2640 | 0.71 | 1.22 | 1.31 | -0.0015492 | 2640 | 0.71 | 2640 | 0.71 | 1.22 | 1.31 | -0.00155
LFNoneSDGOfLExIOU | Com-Iltg-dWatt-LF_OSnone | SDG | OfL | Ex | IOU | 2.64 | 0.00071 | 0 | 3.0624 | 0.00090009 | -0.0056699 | 2.64 | 0.00071 | 0 | 3.0624 | 0.00090009 | -0.0056699 |  | LF | None | 2640 | 0.71 | 2640 | 0.71 | 1.16 | 1.27 | -0.0021477 | 2640 | 0.71 | 2640 | 0.71 | 1.16 | 1.27 | -0.00215
LFNoneSDGOfLNewCZ06 | Com-Iltg-dWatt-LF_OSnone | SDG | OfL | New | CZ06 | 2.64 | 0.00071 | 0 | 3.07 | 0.000894 | -0.00354 | 2.64 | 0.00071 | 0 | 3.07 | 0.000894 | -0.00354 |  | LF | None | 2640 | 0.71 | 2640 | 0.71 | 1.16 | 1.26 | -0.0013409 | 2640 | 0.71 | 2640 | 0.71 | 1.16 | 1.26 | -0.00134
LFNoneSDGOfLNewCZ07 | Com-Iltg-dWatt-LF_OSnone | SDG | OfL | New | CZ07 | 2.64 | 0.00071 | 0 | 3.06 | 0.00088 | -0.00244 | 2.64 | 0.00071 | 0 | 3.06 | 0.00088 | -0.00244 |  | LF | None | 2640 | 0.71 | 2640 | 0.71 | 1.16 | 1.24 | -0.00092424 | 2640 | 0.71 | 2640 | 0.71 | 1.16 | 1.24 | -0.000924
LFNoneSDGOfLNewCZ08 | Com-Iltg-dWatt-LF_OSnone | SDG | OfL | New | CZ08 | 2.64 | 0.00071 | 0 | 3.08 | 0.000905 | -0.00314 | 2.64 | 0.00071 | 0 | 3.08 | 0.000905 | -0.00314 |  | LF | None | 2640 | 0.71 | 2640 | 0.71 | 1.17 | 1.27 | -0.0011894 | 2640 | 0.71 | 2640 | 0.71 | 1.17 | 1.27 | -0.00119
LFNoneSDGOfLNewCZ10 | Com-Iltg-dWatt-LF_OSnone | SDG | OfL | New | CZ10 | 2.64 | 0.00071 | 0 | 3.1 | 0.000932 | -0.00349 | 2.64 | 0.00071 | 0 | 3.1 | 0.000932 | -0.00349 |  | LF | None | 2640 | 0.71 | 2640 | 0.71 | 1.17 | 1.31 | -0.001322 | 2640 | 0.71 | 2640 | 0.71 | 1.17 | 1.31 | -0.00132
LFNoneSDGOfLNewCZ14 | Com-Iltg-dWatt-LF_OSnone | SDG | OfL | New | CZ14 | 2.64 | 0.00071 | 0 | 3.06 | 0.000939 | -0.0051 | 2.64 | 0.00071 | 0 | 3.06 | 0.000939 | -0.0051 |  | LF | None | 2640 | 0.71 | 2640 | 0.71 | 1.16 | 1.32 | -0.0019318 | 2640 | 0.71 | 2640 | 0.71 | 1.16 | 1.32 | -0.00193
LFNoneSDGOfLNewCZ15 | Com-Iltg-dWatt-LF_OSnone | SDG | OfL | New | CZ15 | 2.64 | 0.00071 | 0 | 3.23 | 0.000933 | -0.0018 | 2.64 | 0.00071 | 0 | 3.23 | 0.000933 | -0.0018 |  | LF | None | 2640 | 0.71 | 2640 | 0.71 | 1.22 | 1.31 | -0.00068182 | 2640 | 0.71 | 2640 | 0.71 | 1.22 | 1.31 | -0.000682
LFNoneSDGOfLNewIOU | Com-Iltg-dWatt-LF_OSnone | SDG | OfL | New | IOU | 2.64 | 0.00071 | 0 | 3.0678 | 0.00089015 | -0.0026705 | 2.64 | 0.00071 | 0 | 3.0678 | 0.00089015 | -0.0026705 |  | LF | None | 2640 | 0.71 | 2640 | 0.71 | 1.16 | 1.25 | -0.0010116 | 2640 | 0.71 | 2640 | 0.71 | 1.16 | 1.25 | -0.00101
LFNoneSDGOfSExCZ06 | Com-Iltg-dWatt-LF_OSnone | SDG | OfS | Ex | CZ06 | 2.59 | 0.000694 | 0 | 2.99 | 0.000869 | -0.00201 | 2.59 | 0.000694 | 0 | 2.99 | 0.000869 | -0.00201 |  | LF | None | 2590 | 0.694 | 2590 | 0.694 | 1.15 | 1.25 | -0.00077606 | 2590 | 0.694 | 2590 | 0.694 | 1.15 | 1.25 | -0.000776
LFNoneSDGOfSExCZ07 | Com-Iltg-dWatt-LF_OSnone | SDG | OfS | Ex | CZ07 | 2.59 | 0.000694 | 0 | 3 | 0.000861 | -0.000573 | 2.59 | 0.000694 | 0 | 3 | 0.000861 | -0.000573 |  | LF | None | 2590 | 0.694 | 2590 | 0.694 | 1.16 | 1.24 | -0.00022124 | 2590 | 0.694 | 2590 | 0.694 | 1.16 | 1.24 | -0.000221
LFNoneSDGOfSExCZ08 | Com-Iltg-dWatt-LF_OSnone | SDG | OfS | Ex | CZ08 | 2.59 | 0.000694 | 0 | 3.01 | 0.000874 | -0.00173 | 2.59 | 0.000694 | 0 | 3.01 | 0.000874 | -0.00173 |  | LF | None | 2590 | 0.694 | 2590 | 0.694 | 1.16 | 1.26 | -0.00066795 | 2590 | 0.694 | 2590 | 0.694 | 1.16 | 1.26 | -0.000668
LFNoneSDGOfSExCZ10 | Com-Iltg-dWatt-LF_OSnone | SDG | OfS | Ex | CZ10 | 2.59 | 0.000694 | 0 | 3 | 0.000879 | -0.00262 | 2.59 | 0.000694 | 0 | 3 | 0.000879 | -0.00262 |  | LF | None | 2590 | 0.694 | 2590 | 0.694 | 1.16 | 1.27 | -0.0010116 | 2590 | 0.694 | 2590 | 0.694 | 1.16 | 1.27 | -0.00101
LFNoneSDGOfSExCZ14 | Com-Iltg-dWatt-LF_OSnone | SDG | OfS | Ex | CZ14 | 2.59 | 0.000694 | 0 | 2.93 | 0.000889 | -0.00649 | 2.59 | 0.000694 | 0 | 2.93 | 0.000889 | -0.00649 |  | LF | None | 2590 | 0.694 | 2590 | 0.694 | 1.13 | 1.28 | -0.0025058 | 2590 | 0.694 | 2590 | 0.694 | 1.13 | 1.28 | -0.00251
LFNoneSDGOfSExCZ15 | Com-Iltg-dWatt-LF_OSnone | SDG | OfS | Ex | CZ15 | 2.59 | 0.000694 | 0 | 3.18 | 0.000877 | -0.000537 | 2.59 | 0.000694 | 0 | 3.18 | 0.000877 | -0.000537 |  | LF | None | 2590 | 0.694 | 2590 | 0.694 | 1.23 | 1.26 | -0.00020734 | 2590 | 0.694 | 2590 | 0.694 | 1.23 | 1.26 | -0.000207
LFNoneSDGOfSExIOU | Com-Iltg-dWatt-LF_OSnone | SDG | OfS | Ex | IOU | 2.59 | 0.000694 | 0 | 2.9999 | 0.0008647 | -0.0010075 | 2.59 | 0.000694 | 0 | 2.9999 | 0.0008647 | -0.0010075 |  | LF | None | 2590 | 0.694 | 2590 | 0.694 | 1.16 | 1.25 | -0.00038899 | 2590 | 0.694 | 2590 | 0.694 | 1.16 | 1.25 | -0.000389
LFNoneSDGOfSNewCZ06 | Com-Iltg-dWatt-LF_OSnone | SDG | OfS | New | CZ06 | 2.59 | 0.000694 | 0 | 2.87 | 0.000856 | -0.00205 | 2.59 | 0.000694 | 0 | 2.87 | 0.000856 | -0.00205 |  | LF | None | 2590 | 0.694 | 2590 | 0.694 | 1.11 | 1.23 | -0.00079151 | 2590 | 0.694 | 2590 | 0.694 | 1.11 | 1.23 | -0.000792
LFNoneSDGOfSNewCZ07 | Com-Iltg-dWatt-LF_OSnone | SDG | OfS | New | CZ07 | 2.59 | 0.000694 | 0 | 2.86 | 0.000845 | -0.00047 | 2.59 | 0.000694 | 0 | 2.86 | 0.000845 | -0.00047 |  | LF | None | 2590 | 0.694 | 2590 | 0.694 | 1.1 | 1.22 | -0.00018147 | 2590 | 0.694 | 2590 | 0.694 | 1.1 | 1.22 | -0.000181
LFNoneSDGOfSNewCZ08 | Com-Iltg-dWatt-LF_OSnone | SDG | OfS | New | CZ08 | 2.59 | 0.000694 | 0 | 2.89 | 0.000868 | -0.00177 | 2.59 | 0.000694 | 0 | 2.89 | 0.000868 | -0.00177 |  | LF | None | 2590 | 0.694 | 2590 | 0.694 | 1.12 | 1.25 | -0.0006834 | 2590 | 0.694 | 2590 | 0.694 | 1.12 | 1.25 | -0.000683
LFNoneSDGOfSNewCZ10 | Com-Iltg-dWatt-LF_OSnone | SDG | OfS | New | CZ10 | 2.59 | 0.000694 | 0 | 2.92 | 0.000897 | -0.0014 | 2.59 | 0.000694 | 0 | 2.92 | 0.000897 | -0.0014 |  | LF | None | 2590 | 0.694 | 2590 | 0.694 | 1.13 | 1.29 | -0.00054054 | 2590 | 0.694 | 2590 | 0.694 | 1.13 | 1.29 | -0.000541
LFNoneSDGOfSNewCZ14 | Com-Iltg-dWatt-LF_OSnone | SDG | OfS | New | CZ14 | 2.59 | 0.000694 | 0 | 2.85 | 0.000897 | -0.0054 | 2.59 | 0.000694 | 0 | 2.85 | 0.000897 | -0.0054 |  | LF | None | 2590 | 0.694 | 2590 | 0.694 | 1.1 | 1.29 | -0.0020849 | 2590 | 0.694 | 2590 | 0.694 | 1.1 | 1.29 | -0.00208
LFNoneSDGOfSNewCZ15 | Com-Iltg-dWatt-LF_OSnone | SDG | OfS | New | CZ15 | 2.59 | 0.000694 | 0 | 3.06 | 0.000908 | 0 | 2.59 | 0.000694 | 0 | 3.06 | 0.000908 | 0 |  | LF | None | 2590 | 0.694 | 2590 | 0.694 | 1.18 | 1.31 | 0 | 2590 | 0.694 | 2590 | 0.694 | 1.18 | 1.31 | 0
LFNoneSDGOfSNewIOU | Com-Iltg-dWatt-LF_OSnone | SDG | OfS | New | IOU | 2.59 | 0.000694 | 0 | 2.8714 | 0.00085502 | -0.00071222 | 2.59 | 0.000694 | 0 | 2.8714 | 0.00085502 | -0.00071222 |  | LF | None | 2590 | 0.694 | 2590 | 0.694 | 1.11 | 1.23 | -0.00027499 | 2590 | 0.694 | 2590 | 0.694 | 1.11 | 1.23 | -0.000275
LFNoneSDGRFFExCZ06 | Com-Iltg-dWatt-LF_OSnone | SDG | RFF | Ex | CZ06 | 4.84 | 0.000813 | 0 | 5.4 | 0.001 | -0.0278 | 4.84 | 0.000813 | 0 | 5.4 | 0.001 | -0.0278 |  | LF | None | 4840 | 0.813 | 4840 | 0.813 | 1.12 | 1.23 | -0.0057438 | 4840 | 0.813 | 4840 | 0.813 | 1.12 | 1.23 | -0.00574
LFNoneSDGRFFExCZ07 | Com-Iltg-dWatt-LF_OSnone | SDG | RFF | Ex | CZ07 | 4.84 | 0.000813 | 0 | 5.41 | 0.000998 | -0.0254 | 4.84 | 0.000813 | 0 | 5.41 | 0.000998 | -0.0254 |  | LF | None | 4840 | 0.813 | 4840 | 0.813 | 1.12 | 1.23 | -0.0052479 | 4840 | 0.813 | 4840 | 0.813 | 1.12 | 1.23 | -0.00525
LFNoneSDGRFFExCZ08 | Com-Iltg-dWatt-LF_OSnone | SDG | RFF | Ex | CZ08 | 4.84 | 0.000813 | 0 | 5.44 | 0.000995 | -0.0247 | 4.84 | 0.000813 | 0 | 5.44 | 0.000995 | -0.0247 |  | LF | None | 4840 | 0.813 | 4840 | 0.813 | 1.12 | 1.22 | -0.0051033 | 4840 | 0.813 | 4840 | 0.813 | 1.12 | 1.22 | -0.0051
LFNoneSDGRFFExCZ10 | Com-Iltg-dWatt-LF_OSnone | SDG | RFF | Ex | CZ10 | 4.84 | 0.000813 | 0 | 5.44 | 0.00101 | -0.0273 | 4.84 | 0.000813 | 0 | 5.44 | 0.00101 | -0.0273 |  | LF | None | 4840 | 0.813 | 4840 | 0.813 | 1.12 | 1.24 | -0.0056405 | 4840 | 0.813 | 4840 | 0.813 | 1.12 | 1.24 | -0.00564
LFNoneSDGRFFExCZ14 | Com-Iltg-dWatt-LF_OSnone | SDG | RFF | Ex | CZ14 | 4.84 | 0.000813 | 0 | 5.33 | 0.00103 | -0.0388 | 4.84 | 0.000813 | 0 | 5.33 | 0.00103 | -0.0388 |  | LF | None | 4840 | 0.813 | 4840 | 0.813 | 1.1 | 1.27 | -0.0080165 | 4840 | 0.813 | 4840 | 0.813 | 1.1 | 1.27 | -0.00802
LFNoneSDGRFFExCZ15 | Com-Iltg-dWatt-LF_OSnone | SDG | RFF | Ex | CZ15 | 4.84 | 0.000813 | 0 | 5.77 | 0.00102 | -0.0125 | 4.84 | 0.000813 | 0 | 5.77 | 0.00102 | -0.0125 |  | LF | None | 4840 | 0.813 | 4840 | 0.813 | 1.19 | 1.25 | -0.0025826 | 4840 | 0.813 | 4840 | 0.813 | 1.19 | 1.25 | -0.00258
LFNoneSDGRFFExIOU | Com-Iltg-dWatt-LF_OSnone | SDG | RFF | Ex | IOU | 4.84 | 0.000813 | 0 | 5.4172 | 0.0010007 | -0.025921 | 4.84 | 0.000813 | 0 | 5.4172 | 0.0010007 | -0.025921 |  | LF | None | 4840 | 0.813 | 4840 | 0.813 | 1.12 | 1.23 | -0.0053555 | 4840 | 0.813 | 4840 | 0.813 | 1.12 | 1.23 | -0.00536
LFNoneSDGRFFNewCZ06 | Com-Iltg-dWatt-LF_OSnone | SDG | RFF | New | CZ06 | 4.84 | 0.000813 | 0 | 5.22 | 0.00102 | -0.0276 | 4.84 | 0.000813 | 0 | 5.22 | 0.00102 | -0.0276 |  | LF | None | 4840 | 0.813 | 4840 | 0.813 | 1.08 | 1.25 | -0.0057025 | 4840 | 0.813 | 4840 | 0.813 | 1.08 | 1.25 | -0.0057
LFNoneSDGRFFNewCZ07 | Com-Iltg-dWatt-LF_OSnone | SDG | RFF | New | CZ07 | 4.84 | 0.000813 | 0 | 5.19 | 0.00101 | -0.0315 | 4.84 | 0.000813 | 0 | 5.19 | 0.00101 | -0.0315 |  | LF | None | 4840 | 0.813 | 4840 | 0.813 | 1.07 | 1.24 | -0.0065083 | 4840 | 0.813 | 4840 | 0.813 | 1.07 | 1.24 | -0.00651
LFNoneSDGRFFNewCZ08 | Com-Iltg-dWatt-LF_OSnone | SDG | RFF | New | CZ08 | 4.84 | 0.000813 | 0 | 5.3 | 0.00103 | -0.0299 | 4.84 | 0.000813 | 0 | 5.3 | 0.00103 | -0.0299 |  | LF | None | 4840 | 0.813 | 4840 | 0.813 | 1.1 | 1.27 | -0.0061777 | 4840 | 0.813 | 4840 | 0.813 | 1.1 | 1.27 | -0.00618
LFNoneSDGRFFNewCZ10 | Com-Iltg-dWatt-LF_OSnone | SDG | RFF | New | CZ10 | 4.84 | 0.000813 | 0 | 5.36 | 0.00107 | -0.0331 | 4.84 | 0.000813 | 0 | 5.36 | 0.00107 | -0.0331 |  | LF | None | 4840 | 0.813 | 4840 | 0.813 | 1.11 | 1.32 | -0.0068388 | 4840 | 0.813 | 4840 | 0.813 | 1.11 | 1.32 | -0.00684
LFNoneSDGRFFNewCZ14 | Com-Iltg-dWatt-LF_OSnone | SDG | RFF | New | CZ14 | 4.84 | 0.000813 | 0 | 5.33 | 0.00108 | -0.0469 | 4.84 | 0.000813 | 0 | 5.33 | 0.00108 | -0.0469 |  | LF | None | 4840 | 0.813 | 4840 | 0.813 | 1.1 | 1.33 | -0.0096901 | 4840 | 0.813 | 4840 | 0.813 | 1.1 | 1.33 | -0.00969
LFNoneSDGRFFNewCZ15 | Com-Iltg-dWatt-LF_OSnone | SDG | RFF | New | CZ15 | 4.84 | 0.000813 | 0 | 5.75 | 0.00109 | -0.0163 | 4.84 | 0.000813 | 0 | 5.75 | 0.00109 | -0.0163 |  | LF | None | 4840 | 0.813 | 4840 | 0.813 | 1.19 | 1.34 | -0.0033678 | 4840 | 0.813 | 4840 | 0.813 | 1.19 | 1.34 | -0.00337
LFNoneSDGRFFNewIOU | Com-Iltg-dWatt-LF_OSnone | SDG | RFF | New | IOU | 4.84 | 0.000813 | 0 | 5.2329 | 0.0010245 | -0.03164 | 4.84 | 0.000813 | 0 | 5.2329 | 0.0010245 | -0.03164 |  | LF | None | 4840 | 0.813 | 4840 | 0.813 | 1.08 | 1.26 | -0.0065371 | 4840 | 0.813 | 4840 | 0.813 | 1.08 | 1.26 | -0.00654
LFNoneSDGRSDExCZ06 | Com-Iltg-dWatt-LF_OSnone | SDG | RSD | Ex | CZ06 | 4.83 | 0.0008 | 0 | 5.42 | 0.001 | -0.0305 | 4.83 | 0.0008 | 0 | 5.42 | 0.001 | -0.0305 |  | LF | None | 4830 | 0.8 | 4830 | 0.8 | 1.12 | 1.25 | -0.0063147 | 4830 | 0.8 | 4830 | 0.8 | 1.12 | 1.25 | -0.00631
LFNoneSDGRSDExCZ07 | Com-Iltg-dWatt-LF_OSnone | SDG | RSD | Ex | CZ07 | 4.83 | 0.0008 | 0 | 5.42 | 0.00102 | -0.028 | 4.83 | 0.0008 | 0 | 5.42 | 0.00102 | -0.028 |  | LF | None | 4830 | 0.8 | 4830 | 0.8 | 1.12 | 1.27 | -0.0057971 | 4830 | 0.8 | 4830 | 0.8 | 1.12 | 1.27 | -0.0058
LFNoneSDGRSDExCZ08 | Com-Iltg-dWatt-LF_OSnone | SDG | RSD | Ex | CZ08 | 4.83 | 0.0008 | 0 | 5.46 | 0.00097 | -0.0253 | 4.83 | 0.0008 | 0 | 5.46 | 0.00097 | -0.0253 |  | LF | None | 4830 | 0.8 | 4830 | 0.8 | 1.13 | 1.21 | -0.0052381 | 4830 | 0.8 | 4830 | 0.8 | 1.13 | 1.21 | -0.00524
LFNoneSDGRSDExCZ10 | Com-Iltg-dWatt-LF_OSnone | SDG | RSD | Ex | CZ10 | 4.83 | 0.0008 | 0 | 5.42 | 0.000923 | -0.0298 | 4.83 | 0.0008 | 0 | 5.42 | 0.000923 | -0.0298 |  | LF | None | 4830 | 0.8 | 4830 | 0.8 | 1.12 | 1.15 | -0.0061698 | 4830 | 0.8 | 4830 | 0.8 | 1.12 | 1.15 | -0.00617
LFNoneSDGRSDExCZ14 | Com-Iltg-dWatt-LF_OSnone | SDG | RSD | Ex | CZ14 | 4.83 | 0.0008 | 0 | 5.24 | 0.000922 | -0.0488 | 4.83 | 0.0008 | 0 | 5.24 | 0.000922 | -0.0488 |  | LF | None | 4830 | 0.8 | 4830 | 0.8 | 1.08 | 1.15 | -0.010104 | 4830 | 0.8 | 4830 | 0.8 | 1.08 | 1.15 | -0.0101
LFNoneSDGRSDExCZ15 | Com-Iltg-dWatt-LF_OSnone | SDG | RSD | Ex | CZ15 | 4.83 | 0.0008 | 0 | 5.84 | 0.00103 | -0.0114 | 4.83 | 0.0008 | 0 | 5.84 | 0.00103 | -0.0114 |  | LF | None | 4830 | 0.8 | 4830 | 0.8 | 1.21 | 1.29 | -0.0023602 | 4830 | 0.8 | 4830 | 0.8 | 1.21 | 1.29 | -0.00236
LFNoneSDGRSDExIOU | Com-Iltg-dWatt-LF_OSnone | SDG | RSD | Ex | IOU | 4.83 | 0.0008 | 0 | 5.4213 | 0.00099606 | -0.028454 | 4.83 | 0.0008 | 0 | 5.4213 | 0.00099606 | -0.028454 |  | LF | None | 4830 | 0.8 | 4830 | 0.8 | 1.12 | 1.25 | -0.005891 | 4830 | 0.8 | 4830 | 0.8 | 1.12 | 1.25 | -0.00589
LFNoneSDGRSDNewCZ06 | Com-Iltg-dWatt-LF_OSnone | SDG | RSD | New | CZ06 | 4.83 | 0.0008 | 0 | 5.27 | 0.00101 | -0.0371 | 4.83 | 0.0008 | 0 | 5.27 | 0.00101 | -0.0371 |  | LF | None | 4830 | 0.8 | 4830 | 0.8 | 1.09 | 1.26 | -0.0076812 | 4830 | 0.8 | 4830 | 0.8 | 1.09 | 1.26 | -0.00768
LFNoneSDGRSDNewCZ07 | Com-Iltg-dWatt-LF_OSnone | SDG | RSD | New | CZ07 | 4.83 | 0.0008 | 0 | 5.24 | 0.00103 | -0.0352 | 4.83 | 0.0008 | 0 | 5.24 | 0.00103 | -0.0352 |  | LF | None | 4830 | 0.8 | 4830 | 0.8 | 1.08 | 1.29 | -0.0072878 | 4830 | 0.8 | 4830 | 0.8 | 1.08 | 1.29 | -0.00729
LFNoneSDGRSDNewCZ08 | Com-Iltg-dWatt-LF_OSnone | SDG | RSD | New | CZ08 | 4.83 | 0.0008 | 0 | 5.33 | 0.00102 | -0.0304 | 4.83 | 0.0008 | 0 | 5.33 | 0.00102 | -0.0304 |  | LF | None | 4830 | 0.8 | 4830 | 0.8 | 1.1 | 1.27 | -0.006294 | 4830 | 0.8 | 4830 | 0.8 | 1.1 | 1.27 | -0.00629
LFNoneSDGRSDNewCZ10 | Com-Iltg-dWatt-LF_OSnone | SDG | RSD | New | CZ10 | 4.83 | 0.0008 | 0 | 5.39 | 0.00107 | -0.033 | 4.83 | 0.0008 | 0 | 5.39 | 0.00107 | -0.033 |  | LF | None | 4830 | 0.8 | 4830 | 0.8 | 1.12 | 1.34 | -0.0068323 | 4830 | 0.8 | 4830 | 0.8 | 1.12 | 1.34 | -0.00683
LFNoneSDGRSDNewCZ14 | Com-Iltg-dWatt-LF_OSnone | SDG | RSD | New | CZ14 | 4.83 | 0.0008 | 0 | 5.26 | 0.00106 | -0.0531 | 4.83 | 0.0008 | 0 | 5.26 | 0.00106 | -0.0531 |  | LF | None | 4830 | 0.8 | 4830 | 0.8 | 1.09 | 1.33 | -0.010994 | 4830 | 0.8 | 4830 | 0.8 | 1.09 | 1.33 | -0.011
LFNoneSDGRSDNewCZ15 | Com-Iltg-dWatt-LF_OSnone | SDG | RSD | New | CZ15 | 4.83 | 0.0008 | 0 | 5.81 | 0.0011 | -0.0148 | 4.83 | 0.0008 | 0 | 5.81 | 0.0011 | -0.0148 |  | LF | None | 4830 | 0.8 | 4830 | 0.8 | 1.2 | 1.38 | -0.0030642 | 4830 | 0.8 | 4830 | 0.8 | 1.2 | 1.38 | -0.00306
LFNoneSDGRSDNewIOU | Com-Iltg-dWatt-LF_OSnone | SDG | RSD | New | IOU | 4.83 | 0.0008 | 0 | 5.2777 | 0.0010377 | -0.034673 | 4.83 | 0.0008 | 0 | 5.2777 | 0.0010377 | -0.034673 |  | LF | None | 4830 | 0.8 | 4830 | 0.8 | 1.09 | 1.3 | -0.0071787 | 4830 | 0.8 | 4830 | 0.8 | 1.09 | 1.3 | -0.00718
LFNoneSDGRt3ExCZ06 | Com-Iltg-dWatt-LF_OSnone | SDG | Rt3 | Ex | CZ06 | 3.38 | 0.00075938 | 0 | 3.87 | 0.00092738 | -0.00322 | 3.38 | 0.00075938 | 0 | 3.87 | 0.00092738 | -0.00322 |  | LF | None | 3380 | 0.759 | 3380 | 0.759 | 1.14 | 1.22 | -0.00095266 | 3380 | 0.759 | 3380 | 0.759 | 1.14 | 1.22 | -0.000953
LFNoneSDGRt3ExCZ07 | Com-Iltg-dWatt-LF_OSnone | SDG | Rt3 | Ex | CZ07 | 3.38 | 0.00075938 | 0 | 3.89 | 0.00091338 | -0.00139 | 3.38 | 0.00075938 | 0 | 3.89 | 0.00091338 | -0.00139 |  | LF | None | 3380 | 0.759 | 3380 | 0.759 | 1.15 | 1.2 | -0.00041124 | 3380 | 0.759 | 3380 | 0.759 | 1.15 | 1.2 | -0.000411
LFNoneSDGRt3ExCZ08 | Com-Iltg-dWatt-LF_OSnone | SDG | Rt3 | Ex | CZ08 | 3.38 | 0.00075938 | 0 | 3.89 | 0.00091838 | -0.00288 | 3.38 | 0.00075938 | 0 | 3.89 | 0.00091838 | -0.00288 |  | LF | None | 3380 | 0.759 | 3380 | 0.759 | 1.15 | 1.21 | -0.00085207 | 3380 | 0.759 | 3380 | 0.759 | 1.15 | 1.21 | -0.000852
LFNoneSDGRt3ExCZ10 | Com-Iltg-dWatt-LF_OSnone | SDG | Rt3 | Ex | CZ10 | 3.38 | 0.00075938 | 0 | 3.85 | 0.00093138 | -0.00526 | 3.38 | 0.00075938 | 0 | 3.85 | 0.00093138 | -0.00526 |  | LF | None | 3380 | 0.759 | 3380 | 0.759 | 1.14 | 1.23 | -0.0015562 | 3380 | 0.759 | 3380 | 0.759 | 1.14 | 1.23 | -0.00156
LFNoneSDGRt3ExCZ14 | Com-Iltg-dWatt-LF_OSnone | SDG | Rt3 | Ex | CZ14 | 3.38 | 0.00075938 | 0 | 3.68 | 0.00093738 | -0.0192 | 3.38 | 0.00075938 | 0 | 3.68 | 0.00093738 | -0.0192 |  | LF | None | 3380 | 0.759 | 3380 | 0.759 | 1.09 | 1.23 | -0.0056805 | 3380 | 0.759 | 3380 | 0.759 | 1.09 | 1.23 | -0.00568
LFNoneSDGRt3ExCZ15 | Com-Iltg-dWatt-LF_OSnone | SDG | Rt3 | Ex | CZ15 | 3.38 | 0.00075938 | 0 | 3.98 | 0.00095077 | -0.00124 | 3.38 | 0.00075938 | 0 | 3.98 | 0.00095077 | -0.00124 |  | LF | None | 3380 | 0.759 | 3380 | 0.759 | 1.18 | 1.25 | -0.00036686 | 3380 | 0.759 | 3380 | 0.759 | 1.18 | 1.25 | -0.000367
LFNoneSDGRt3ExIOU | Com-Iltg-dWatt-LF_OSnone | SDG | Rt3 | Ex | IOU | 3.38 | 0.00075938 | 0 | 3.8793 | 0.00091861 | -0.0025079 | 3.38 | 0.00075938 | 0 | 3.8793 | 0.00091861 | -0.0025079 |  | LF | None | 3380 | 0.759 | 3380 | 0.759 | 1.15 | 1.21 | -0.000742 | 3380 | 0.759 | 3380 | 0.759 | 1.15 | 1.21 | -0.000742
LFNoneSDGRt3NewCZ06 | Com-Iltg-dWatt-LF_OSnone | SDG | Rt3 | New | CZ06 | 3.38 | 0.00076 | 0 | 3.81 | 0.00094 | -0.00456 | 3.38 | 0.00076 | 0 | 3.81 | 0.00094 | -0.00456 |  | LF | None | 3380 | 0.76 | 3380 | 0.76 | 1.13 | 1.24 | -0.0013491 | 3380 | 0.76 | 3380 | 0.76 | 1.13 | 1.24 | -0.00135
LFNoneSDGRt3NewCZ07 | Com-Iltg-dWatt-LF_OSnone | SDG | Rt3 | New | CZ07 | 3.38 | 0.00076 | 0 | 3.8 | 0.000923 | -0.00176 | 3.38 | 0.00076 | 0 | 3.8 | 0.000923 | -0.00176 |  | LF | None | 3380 | 0.76 | 3380 | 0.76 | 1.12 | 1.21 | -0.00052071 | 3380 | 0.76 | 3380 | 0.76 | 1.12 | 1.21 | -0.000521
LFNoneSDGRt3NewCZ08 | Com-Iltg-dWatt-LF_OSnone | SDG | Rt3 | New | CZ08 | 3.38 | 0.00076 | 0 | 3.85 | 0.000948 | -0.00381 | 3.38 | 0.00076 | 0 | 3.85 | 0.000948 | -0.00381 |  | LF | None | 3380 | 0.76 | 3380 | 0.76 | 1.14 | 1.25 | -0.0011272 | 3380 | 0.76 | 3380 | 0.76 | 1.14 | 1.25 | -0.00113
LFNoneSDGRt3NewCZ10 | Com-Iltg-dWatt-LF_OSnone | SDG | Rt3 | New | CZ10 | 3.38 | 0.00076 | 0 | 3.8 | 0.000941 | -0.00702 | 3.38 | 0.00076 | 0 | 3.8 | 0.000941 | -0.00702 |  | LF | None | 3380 | 0.76 | 3380 | 0.76 | 1.12 | 1.24 | -0.0020769 | 3380 | 0.76 | 3380 | 0.76 | 1.12 | 1.24 | -0.00208
LFNoneSDGRt3NewCZ14 | Com-Iltg-dWatt-LF_OSnone | SDG | Rt3 | New | CZ14 | 3.38 | 0.00076 | 0 | 3.74 | 0.00098 | -0.0206 | 3.38 | 0.00076 | 0 | 3.74 | 0.00098 | -0.0206 |  | LF | None | 3380 | 0.76 | 3380 | 0.76 | 1.11 | 1.29 | -0.0060947 | 3380 | 0.76 | 3380 | 0.76 | 1.11 | 1.29 | -0.00609
LFNoneSDGRt3NewCZ15 | Com-Iltg-dWatt-LF_OSnone | SDG | Rt3 | New | CZ15 | 3.38 | 0.00076 | 0 | 3.8 | 0.000894 | -0.000705 | 3.38 | 0.00076 | 0 | 3.8 | 0.000894 | -0.000705 |  | LF | None | 3380 | 0.76 | 3380 | 0.76 | 1.12 | 1.18 | -0.00020858 | 3380 | 0.76 | 3380 | 0.76 | 1.12 | 1.18 | -0.000209
LFNoneSDGRt3NewIOU | Com-Iltg-dWatt-LF_OSnone | SDG | Rt3 | New | IOU | 3.38 | 0.00076 | 0 | 3.8033 | 0.00092955 | -0.0032861 | 3.38 | 0.00076 | 0 | 3.8033 | 0.00092955 | -0.0032861 |  | LF | None | 3380 | 0.76 | 3380 | 0.76 | 1.13 | 1.22 | -0.00097222 | 3380 | 0.76 | 3380 | 0.76 | 1.13 | 1.22 | -0.000972
LFNoneSDGRtLExCZ06 | Com-Iltg-dWatt-LF_OSnone | SDG | RtL | Ex | CZ06 | 4.27 | 0.000848 | 0 | 4.84 | 0.00104 | -0.0102 | 4.27 | 0.000848 | 0 | 4.84 | 0.00104 | -0.0102 |  | LF | None | 4270 | 0.848 | 4270 | 0.848 | 1.13 | 1.23 | -0.0023888 | 4270 | 0.848 | 4270 | 0.848 | 1.13 | 1.23 | -0.00239
LFNoneSDGRtLExCZ07 | Com-Iltg-dWatt-LF_OSnone | SDG | RtL | Ex | CZ07 | 4.27 | 0.000848 | 0 | 4.87 | 0.00104 | -0.00743 | 4.27 | 0.000848 | 0 | 4.87 | 0.00104 | -0.00743 |  | LF | None | 4270 | 0.848 | 4270 | 0.848 | 1.14 | 1.23 | -0.00174 | 4270 | 0.848 | 4270 | 0.848 | 1.14 | 1.23 | -0.00174
LFNoneSDGRtLExCZ08 | Com-Iltg-dWatt-LF_OSnone | SDG | RtL | Ex | CZ08 | 4.27 | 0.000848 | 0 | 4.86 | 0.00104 | -0.00879 | 4.27 | 0.000848 | 0 | 4.86 | 0.00104 | -0.00879 |  | LF | None | 4270 | 0.848 | 4270 | 0.848 | 1.14 | 1.23 | -0.0020585 | 4270 | 0.848 | 4270 | 0.848 | 1.14 | 1.23 | -0.00206
LFNoneSDGRtLExCZ10 | Com-Iltg-dWatt-LF_OSnone | SDG | RtL | Ex | CZ10 | 4.27 | 0.000848 | 0 | 4.82 | 0.00106 | -0.0117 | 4.27 | 0.000848 | 0 | 4.82 | 0.00106 | -0.0117 |  | LF | None | 4270 | 0.848 | 4270 | 0.848 | 1.13 | 1.25 | -0.00274 | 4270 | 0.848 | 4270 | 0.848 | 1.13 | 1.25 | -0.00274
LFNoneSDGRtLExCZ14 | Com-Iltg-dWatt-LF_OSnone | SDG | RtL | Ex | CZ14 | 4.27 | 0.000848 | 0 | 4.65 | 0.00107 | -0.0247 | 4.27 | 0.000848 | 0 | 4.65 | 0.00107 | -0.0247 |  | LF | None | 4270 | 0.848 | 4270 | 0.848 | 1.09 | 1.26 | -0.0057845 | 4270 | 0.848 | 4270 | 0.848 | 1.09 | 1.26 | -0.00578
LFNoneSDGRtLExCZ15 | Com-Iltg-dWatt-LF_OSnone | SDG | RtL | Ex | CZ15 | 4.27 | 0.000848 | 0 | 5.04 | 0.00108 | -0.00415 | 4.27 | 0.000848 | 0 | 5.04 | 0.00108 | -0.00415 |  | LF | None | 4270 | 0.848 | 4270 | 0.848 | 1.18 | 1.27 | -0.0009719 | 4270 | 0.848 | 4270 | 0.848 | 1.18 | 1.27 | -0.000972
LFNoneSDGRtLExIOU | Com-Iltg-dWatt-LF_OSnone | SDG | RtL | Ex | IOU | 4.27 | 0.000848 | 0 | 4.856 | 0.0010449 | -0.0086686 | 4.27 | 0.000848 | 0 | 4.856 | 0.0010449 | -0.0086686 |  | LF | None | 4270 | 0.848 | 4270 | 0.848 | 1.14 | 1.23 | -0.0020301 | 4270 | 0.848 | 4270 | 0.848 | 1.14 | 1.23 | -0.00203
LFNoneSDGRtLNewCZ06 | Com-Iltg-dWatt-LF_OSnone | SDG | RtL | New | CZ06 | 4.27 | 0.000848 | 0 | 4.73 | 0.00106 | -0.014 | 4.27 | 0.000848 | 0 | 4.73 | 0.00106 | -0.014 |  | LF | None | 4270 | 0.848 | 4270 | 0.848 | 1.11 | 1.25 | -0.0032787 | 4270 | 0.848 | 4270 | 0.848 | 1.11 | 1.25 | -0.00328
LFNoneSDGRtLNewCZ07 | Com-Iltg-dWatt-LF_OSnone | SDG | RtL | New | CZ07 | 4.27 | 0.000848 | 0 | 4.68 | 0.00102 | -0.0101 | 4.27 | 0.000848 | 0 | 4.68 | 0.00102 | -0.0101 |  | LF | None | 4270 | 0.848 | 4270 | 0.848 | 1.1 | 1.2 | -0.0023653 | 4270 | 0.848 | 4270 | 0.848 | 1.1 | 1.2 | -0.00237
LFNoneSDGRtLNewCZ08 | Com-Iltg-dWatt-LF_OSnone | SDG | RtL | New | CZ08 | 4.27 | 0.000848 | 0 | 4.79 | 0.00108 | -0.0119 | 4.27 | 0.000848 | 0 | 4.79 | 0.00108 | -0.0119 |  | LF | None | 4270 | 0.848 | 4270 | 0.848 | 1.12 | 1.27 | -0.0027869 | 4270 | 0.848 | 4270 | 0.848 | 1.12 | 1.27 | -0.00279
LFNoneSDGRtLNewCZ10 | Com-Iltg-dWatt-LF_OSnone | SDG | RtL | New | CZ10 | 4.27 | 0.000848 | 0 | 4.82 | 0.00112 | -0.0137 | 4.27 | 0.000848 | 0 | 4.82 | 0.00112 | -0.0137 |  | LF | None | 4270 | 0.848 | 4270 | 0.848 | 1.13 | 1.32 | -0.0032084 | 4270 | 0.848 | 4270 | 0.848 | 1.13 | 1.32 | -0.00321
LFNoneSDGRtLNewCZ14 | Com-Iltg-dWatt-LF_OSnone | SDG | RtL | New | CZ14 | 4.27 | 0.000848 | 0 | 4.71 | 0.00111 | -0.0275 | 4.27 | 0.000848 | 0 | 4.71 | 0.00111 | -0.0275 |  | LF | None | 4270 | 0.848 | 4270 | 0.848 | 1.1 | 1.31 | -0.0064403 | 4270 | 0.848 | 4270 | 0.848 | 1.1 | 1.31 | -0.00644
LFNoneSDGRtLNewCZ15 | Com-Iltg-dWatt-LF_OSnone | SDG | RtL | New | CZ15 | 4.27 | 0.000848 | 0 | 5.11 | 0.00113 | -0.00414 | 4.27 | 0.000848 | 0 | 5.11 | 0.00113 | -0.00414 |  | LF | None | 4270 | 0.848 | 4270 | 0.848 | 1.2 | 1.33 | -0.00096956 | 4270 | 0.848 | 4270 | 0.848 | 1.2 | 1.33 | -0.00097
LFNoneSDGRtLNewIOU | Com-Iltg-dWatt-LF_OSnone | SDG | RtL | New | IOU | 4.27 | 0.000848 | 0 | 4.7229 | 0.0010496 | -0.011238 | 4.27 | 0.000848 | 0 | 4.7229 | 0.0010496 | -0.011238 |  | LF | None | 4270 | 0.848 | 4270 | 0.848 | 1.11 | 1.24 | -0.0026319 | 4270 | 0.848 | 4270 | 0.848 | 1.11 | 1.24 | -0.00263
LFNoneSDGRtSExCZ06 | Com-Iltg-dWatt-LF_OSnone | SDG | RtS | Ex | CZ06 | 3.38 | 0.000875 | 0 | 3.8 | 0.00107 | -0.0053 | 3.38 | 0.000875 | 0 | 3.8 | 0.00107 | -0.0053 |  | LF | None | 3380 | 0.875 | 3380 | 0.875 | 1.12 | 1.22 | -0.001568 | 3380 | 0.875 | 3380 | 0.875 | 1.12 | 1.22 | -0.00157
LFNoneSDGRtSExCZ07 | Com-Iltg-dWatt-LF_OSnone | SDG | RtS | Ex | CZ07 | 3.38 | 0.000875 | 0 | 3.81 | 0.00105 | -0.00315 | 3.38 | 0.000875 | 0 | 3.81 | 0.00105 | -0.00315 |  | LF | None | 3380 | 0.875 | 3380 | 0.875 | 1.13 | 1.2 | -0.00093195 | 3380 | 0.875 | 3380 | 0.875 | 1.13 | 1.2 | -0.000932
LFNoneSDGRtSExCZ08 | Com-Iltg-dWatt-LF_OSnone | SDG | RtS | Ex | CZ08 | 3.38 | 0.000875 | 0 | 3.83 | 0.00107 | -0.00449 | 3.38 | 0.000875 | 0 | 3.83 | 0.00107 | -0.00449 |  | LF | None | 3380 | 0.875 | 3380 | 0.875 | 1.13 | 1.22 | -0.0013284 | 3380 | 0.875 | 3380 | 0.875 | 1.13 | 1.22 | -0.00133
LFNoneSDGRtSExCZ10 | Com-Iltg-dWatt-LF_OSnone | SDG | RtS | Ex | CZ10 | 3.38 | 0.000875 | 0 | 3.81 | 0.00108 | -0.00661 | 3.38 | 0.000875 | 0 | 3.81 | 0.00108 | -0.00661 |  | LF | None | 3380 | 0.875 | 3380 | 0.875 | 1.13 | 1.23 | -0.0019556 | 3380 | 0.875 | 3380 | 0.875 | 1.13 | 1.23 | -0.00196
LFNoneSDGRtSExCZ14 | Com-Iltg-dWatt-LF_OSnone | SDG | RtS | Ex | CZ14 | 3.38 | 0.000875 | 0 | 3.69 | 0.00107 | -0.0166 | 3.38 | 0.000875 | 0 | 3.69 | 0.00107 | -0.0166 |  | LF | None | 3380 | 0.875 | 3380 | 0.875 | 1.09 | 1.22 | -0.0049112 | 3380 | 0.875 | 3380 | 0.875 | 1.09 | 1.22 | -0.00491
LFNoneSDGRtSExCZ15 | Com-Iltg-dWatt-LF_OSnone | SDG | RtS | Ex | CZ15 | 3.38 | 0.000875 | 0 | 4 | 0.00109 | -0.00142 | 3.38 | 0.000875 | 0 | 4 | 0.00109 | -0.00142 |  | LF | None | 3380 | 0.875 | 3380 | 0.875 | 1.18 | 1.25 | -0.00042012 | 3380 | 0.875 | 3380 | 0.875 | 1.18 | 1.25 | -0.00042
LFNoneSDGRtSExIOU | Com-Iltg-dWatt-LF_OSnone | SDG | RtS | Ex | IOU | 3.38 | 0.000875 | 0 | 3.8108 | 0.0010593 | -0.0041647 | 3.38 | 0.000875 | 0 | 3.8108 | 0.0010593 | -0.0041647 |  | LF | None | 3380 | 0.875 | 3380 | 0.875 | 1.13 | 1.21 | -0.0012321 | 3380 | 0.875 | 3380 | 0.875 | 1.13 | 1.21 | -0.00123
LFNoneSDGRtSNewCZ06 | Com-Iltg-dWatt-LF_OSnone | SDG | RtS | New | CZ06 | 3.38 | 0.000875 | 0 | 3.74 | 0.00106 | -0.00699 | 3.38 | 0.000875 | 0 | 3.74 | 0.00106 | -0.00699 |  | LF | None | 3380 | 0.875 | 3380 | 0.875 | 1.11 | 1.21 | -0.002068 | 3380 | 0.875 | 3380 | 0.875 | 1.11 | 1.21 | -0.00207
LFNoneSDGRtSNewCZ07 | Com-Iltg-dWatt-LF_OSnone | SDG | RtS | New | CZ07 | 3.38 | 0.000875 | 0 | 3.71 | 0.00105 | -0.00412 | 3.38 | 0.000875 | 0 | 3.71 | 0.00105 | -0.00412 |  | LF | None | 3380 | 0.875 | 3380 | 0.875 | 1.1 | 1.2 | -0.0012189 | 3380 | 0.875 | 3380 | 0.875 | 1.1 | 1.2 | -0.00122
LFNoneSDGRtSNewCZ08 | Com-Iltg-dWatt-LF_OSnone | SDG | RtS | New | CZ08 | 3.38 | 0.000875 | 0 | 3.77 | 0.00107 | -0.00584 | 3.38 | 0.000875 | 0 | 3.77 | 0.00107 | -0.00584 |  | LF | None | 3380 | 0.875 | 3380 | 0.875 | 1.12 | 1.22 | -0.0017278 | 3380 | 0.875 | 3380 | 0.875 | 1.12 | 1.22 | -0.00173
LFNoneSDGRtSNewCZ10 | Com-Iltg-dWatt-LF_OSnone | SDG | RtS | New | CZ10 | 3.38 | 0.000875 | 0 | 3.81 | 0.00111 | -0.00729 | 3.38 | 0.000875 | 0 | 3.81 | 0.00111 | -0.00729 |  | LF | None | 3380 | 0.875 | 3380 | 0.875 | 1.13 | 1.27 | -0.0021568 | 3380 | 0.875 | 3380 | 0.875 | 1.13 | 1.27 | -0.00216
LFNoneSDGRtSNewCZ14 | Com-Iltg-dWatt-LF_OSnone | SDG | RtS | New | CZ14 | 3.38 | 0.000875 | 0 | 3.72 | 0.00109 | -0.0177 | 3.38 | 0.000875 | 0 | 3.72 | 0.00109 | -0.0177 |  | LF | None | 3380 | 0.875 | 3380 | 0.875 | 1.1 | 1.25 | -0.0052367 | 3380 | 0.875 | 3380 | 0.875 | 1.1 | 1.25 | -0.00524
LFNoneSDGRtSNewCZ15 | Com-Iltg-dWatt-LF_OSnone | SDG | RtS | New | CZ15 | 3.38 | 0.000875 | 0 | 3.98 | 0.00112 | -0.00125 | 3.38 | 0.000875 | 0 | 3.98 | 0.00112 | -0.00125 |  | LF | None | 3380 | 0.875 | 3380 | 0.875 | 1.18 | 1.28 | -0.00036982 | 3380 | 0.875 | 3380 | 0.875 | 1.18 | 1.28 | -0.00037
LFNoneSDGRtSNewIOU | Com-Iltg-dWatt-LF_OSnone | SDG | RtS | New | IOU | 3.38 | 0.000875 | 0 | 3.7393 | 0.0010663 | -0.0051104 | 3.38 | 0.000875 | 0 | 3.7393 | 0.0010663 | -0.0051104 |  | LF | None | 3380 | 0.875 | 3380 | 0.875 | 1.11 | 1.22 | -0.001512 | 3380 | 0.875 | 3380 | 0.875 | 1.11 | 1.22 | -0.00151
LFNoneSDGSCnExCZ06 | Com-Iltg-dWatt-LF_OSnone | SDG | SCn | Ex | CZ06 | 3.42 | 0.0007 | 0 | 3.51 | 0.000909 | -0.019 | 3.42 | 0.0007 | 0 | 3.51 | 0.000909 | -0.019 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 1.03 | 1.3 | -0.0055556 | 3420 | 0.7 | 3420 | 0.7 | 1.03 | 1.3 | -0.00556
LFNoneSDGSCnExCZ07 | Com-Iltg-dWatt-LF_OSnone | SDG | SCn | Ex | CZ07 | 3.42 | 0.0007 | 0 | 3.45 | 0.000915 | -0.0156 | 3.42 | 0.0007 | 0 | 3.45 | 0.000915 | -0.0156 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 1.01 | 1.31 | -0.0045614 | 3420 | 0.7 | 3420 | 0.7 | 1.01 | 1.31 | -0.00456
LFNoneSDGSCnExCZ08 | Com-Iltg-dWatt-LF_OSnone | SDG | SCn | Ex | CZ08 | 3.42 | 0.0007 | 0 | 3.56 | 0.000907 | -0.0162 | 3.42 | 0.0007 | 0 | 3.56 | 0.000907 | -0.0162 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 1.04 | 1.3 | -0.0047368 | 3420 | 0.7 | 3420 | 0.7 | 1.04 | 1.3 | -0.00474
LFNoneSDGSCnExCZ10 | Com-Iltg-dWatt-LF_OSnone | SDG | SCn | Ex | CZ10 | 3.42 | 0.0007 | 0 | 3.57 | 0.000919 | -0.02 | 3.42 | 0.0007 | 0 | 3.57 | 0.000919 | -0.02 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 1.04 | 1.31 | -0.005848 | 3420 | 0.7 | 3420 | 0.7 | 1.04 | 1.31 | -0.00585
LFNoneSDGSCnExCZ14 | Com-Iltg-dWatt-LF_OSnone | SDG | SCn | Ex | CZ14 | 3.42 | 0.0007 | 0 | 3.46 | 0.000903 | -0.0293 | 3.42 | 0.0007 | 0 | 3.46 | 0.000903 | -0.0293 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 1.01 | 1.29 | -0.0085673 | 3420 | 0.7 | 3420 | 0.7 | 1.01 | 1.29 | -0.00857
LFNoneSDGSCnExCZ15 | Com-Iltg-dWatt-LF_OSnone | SDG | SCn | Ex | CZ15 | 3.42 | 0.0007 | 0 | 3.82 | 0.000903 | -0.00855 | 3.42 | 0.0007 | 0 | 3.82 | 0.000903 | -0.00855 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 1.12 | 1.29 | -0.0025 | 3420 | 0.7 | 3420 | 0.7 | 1.12 | 1.29 | -0.0025
LFNoneSDGSCnExIOU | Com-Iltg-dWatt-LF_OSnone | SDG | SCn | Ex | IOU | 3.42 | 0.0007 | 0 | 3.4897 | 0.00091587 | -0.017042 | 3.42 | 0.0007 | 0 | 3.4897 | 0.00091587 | -0.017042 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 1.02 | 1.31 | -0.0049831 | 3420 | 0.7 | 3420 | 0.7 | 1.02 | 1.31 | -0.00498
LFNoneSDGSCnNewCZ06 | Com-Iltg-dWatt-LF_OSnone | SDG | SCn | New | CZ06 | 3.42 | 0.0007 | 0 | 3.42 | 0.000843 | -0.0203 | 3.42 | 0.0007 | 0 | 3.42 | 0.000843 | -0.0203 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 1 | 1.2 | -0.0059357 | 3420 | 0.7 | 3420 | 0.7 | 1 | 1.2 | -0.00594
LFNoneSDGSCnNewCZ07 | Com-Iltg-dWatt-LF_OSnone | SDG | SCn | New | CZ07 | 3.42 | 0.0007 | 0 | 3.41 | 0.000862 | -0.0169 | 3.42 | 0.0007 | 0 | 3.41 | 0.000862 | -0.0169 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 0.997 | 1.23 | -0.0049415 | 3420 | 0.7 | 3420 | 0.7 | 0.997 | 1.23 | -0.00494
LFNoneSDGSCnNewCZ08 | Com-Iltg-dWatt-LF_OSnone | SDG | SCn | New | CZ08 | 3.42 | 0.0007 | 0 | 3.5 | 0.000855 | -0.0177 | 3.42 | 0.0007 | 0 | 3.5 | 0.000855 | -0.0177 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 1.02 | 1.22 | -0.0051754 | 3420 | 0.7 | 3420 | 0.7 | 1.02 | 1.22 | -0.00518
LFNoneSDGSCnNewCZ10 | Com-Iltg-dWatt-LF_OSnone | SDG | SCn | New | CZ10 | 3.42 | 0.0007 | 0 | 3.51 | 0.000876 | -0.0207 | 3.42 | 0.0007 | 0 | 3.51 | 0.000876 | -0.0207 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 1.03 | 1.25 | -0.0060526 | 3420 | 0.7 | 3420 | 0.7 | 1.03 | 1.25 | -0.00605
LFNoneSDGSCnNewCZ14 | Com-Iltg-dWatt-LF_OSnone | SDG | SCn | New | CZ14 | 3.42 | 0.0007 | 0 | 3.44 | 0.000874 | -0.0303 | 3.42 | 0.0007 | 0 | 3.44 | 0.000874 | -0.0303 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 1.01 | 1.25 | -0.0088596 | 3420 | 0.7 | 3420 | 0.7 | 1.01 | 1.25 | -0.00886
LFNoneSDGSCnNewCZ15 | Com-Iltg-dWatt-LF_OSnone | SDG | SCn | New | CZ15 | 3.42 | 0.0007 | 0 | 3.73 | 0.000881 | -0.00647 | 3.42 | 0.0007 | 0 | 3.73 | 0.000881 | -0.00647 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 1.09 | 1.26 | -0.0018918 | 3420 | 0.7 | 3420 | 0.7 | 1.09 | 1.26 | -0.00189
LFNoneSDGSCnNewIOU | Com-Iltg-dWatt-LF_OSnone | SDG | SCn | New | IOU | 3.42 | 0.0007 | 0 | 3.4421 | 0.00086567 | -0.01816 | 3.42 | 0.0007 | 0 | 3.4421 | 0.00086567 | -0.01816 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 1.01 | 1.24 | -0.00531 | 3420 | 0.7 | 3420 | 0.7 | 1.01 | 1.24 | -0.00531
LFNoneSDGSUnExCZ06 | Com-Iltg-dWatt-LF_OSnone | SDG | SUn | Ex | CZ06 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0 | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0
LFNoneSDGSUnExCZ07 | Com-Iltg-dWatt-LF_OSnone | SDG | SUn | Ex | CZ07 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0 | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0
LFNoneSDGSUnExCZ08 | Com-Iltg-dWatt-LF_OSnone | SDG | SUn | Ex | CZ08 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0 | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0
LFNoneSDGSUnExCZ10 | Com-Iltg-dWatt-LF_OSnone | SDG | SUn | Ex | CZ10 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0 | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0
LFNoneSDGSUnExCZ14 | Com-Iltg-dWatt-LF_OSnone | SDG | SUn | Ex | CZ14 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0 | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0
LFNoneSDGSUnExCZ15 | Com-Iltg-dWatt-LF_OSnone | SDG | SUn | Ex | CZ15 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0 | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0
LFNoneSDGSUnExIOU | Com-Iltg-dWatt-LF_OSnone | SDG | SUn | Ex | IOU | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0 | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0
LFNoneSDGSUnNewCZ06 | Com-Iltg-dWatt-LF_OSnone | SDG | SUn | New | CZ06 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0 | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0
LFNoneSDGSUnNewCZ07 | Com-Iltg-dWatt-LF_OSnone | SDG | SUn | New | CZ07 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0 | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0
LFNoneSDGSUnNewCZ08 | Com-Iltg-dWatt-LF_OSnone | SDG | SUn | New | CZ08 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0 | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0
LFNoneSDGSUnNewCZ10 | Com-Iltg-dWatt-LF_OSnone | SDG | SUn | New | CZ10 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0 | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0
LFNoneSDGSUnNewCZ14 | Com-Iltg-dWatt-LF_OSnone | SDG | SUn | New | CZ14 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0 | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0
LFNoneSDGSUnNewCZ15 | Com-Iltg-dWatt-LF_OSnone | SDG | SUn | New | CZ15 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0 | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0
LFNoneSDGSUnNewIOU | Com-Iltg-dWatt-LF_OSnone | SDG | SUn | New | IOU | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 | 3.42 | 0.0007 | 0 |  | LF | None | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0 | 3420 | 0.7 | 3420 | 0.7 | 1 | 1 | 0
LFNoneSDGWRfExCZ06 | Com-Iltg-dWatt-LF_OSnone | SDG | WRf | Ex | CZ06 | 4.77 | 0.000556 | 0 | 7.65 | 0.000697 | 0 | 4.77 | 0.000556 | 0 | 7.65 | 0.000697 | 0 |  | LF | None | 4770 | 0.556 | 4770 | 0.556 | 1.6 | 1.25 | 0 | 4770 | 0.556 | 4770 | 0.556 | 1.6 | 1.25 | 0
LFNoneSDGWRfExCZ07 | Com-Iltg-dWatt-LF_OSnone | SDG | WRf | Ex | CZ07 | 4.77 | 0.000556 | 0 | 7.7 | 0.000697 | 0 | 4.77 | 0.000556 | 0 | 7.7 | 0.000697 | 0 |  | LF | None | 4770 | 0.556 | 4770 | 0.556 | 1.61 | 1.25 | 0 | 4770 | 0.556 | 4770 | 0.556 | 1.61 | 1.25 | 0
LFNoneSDGWRfExCZ10 | Com-Iltg-dWatt-LF_OSnone | SDG | WRf | Ex | CZ10 | 4.77 | 0.000556 | 0 | 7.56 | 0.000703 | 0 | 4.77 | 0.000556 | 0 | 7.56 | 0.000703 | 0 |  | LF | None | 4770 | 0.556 | 4770 | 0.556 | 1.58 | 1.26 | 0 | 4770 | 0.556 | 4770 | 0.556 | 1.58 | 1.26 | 0
LFNoneSDGWRfExIOU | Com-Iltg-dWatt-LF_OSnone | SDG | WRf | Ex | IOU | 4.77 | 0.000556 | 0 | 7.6688 | 0.00069832 | 0 | 4.77 | 0.000556 | 0 | 7.6688 | 0.00069832 | 0 |  | LF | None | 4770 | 0.556 | 4770 | 0.556 | 1.61 | 1.26 | 0 | 4770 | 0.556 | 4770 | 0.556 | 1.61 | 1.26 | 0
LFNoneSDGWRfNewCZ06 | Com-Iltg-dWatt-LF_OSnone | SDG | WRf | New | CZ06 | 4.77 | 0.000556 | 0 | 6.87 | 0.000686 | 0 | 4.77 | 0.000556 | 0 | 6.87 | 0.000686 | 0 |  | LF | None | 4770 | 0.556 | 4770 | 0.556 | 1.44 | 1.23 | 0 | 4770 | 0.556 | 4770 | 0.556 | 1.44 | 1.23 | 0
LFNoneSDGWRfNewCZ07 | Com-Iltg-dWatt-LF_OSnone | SDG | WRf | New | CZ07 | 4.77 | 0.000556 | 0 | 6.82 | 0.000686 | 0 | 4.77 | 0.000556 | 0 | 6.82 | 0.000686 | 0 |  | LF | None | 4770 | 0.556 | 4770 | 0.556 | 1.43 | 1.23 | 0 | 4770 | 0.556 | 4770 | 0.556 | 1.43 | 1.23 | 0
LFNoneSDGWRfNewCZ08 | Com-Iltg-dWatt-LF_OSnone | SDG | WRf | New | CZ08 | 4.77 | 0.000556 | 0 | 6.79 | 0.000688 | 0 | 4.77 | 0.000556 | 0 | 6.79 | 0.000688 | 0 |  | LF | None | 4770 | 0.556 | 4770 | 0.556 | 1.42 | 1.24 | 0 | 4770 | 0.556 | 4770 | 0.556 | 1.42 | 1.24 | 0
LFNoneSDGWRfNewCZ10 | Com-Iltg-dWatt-LF_OSnone | SDG | WRf | New | CZ10 | 4.77 | 0.000556 | 0 | 6.7 | 0.000696 | 0 | 4.77 | 0.000556 | 0 | 6.7 | 0.000696 | 0 |  | LF | None | 4770 | 0.556 | 4770 | 0.556 | 1.4 | 1.25 | 0 | 4770 | 0.556 | 4770 | 0.556 | 1.4 | 1.25 | 0
LFNoneSDGWRfNewCZ14 | Com-Iltg-dWatt-LF_OSnone | SDG | WRf | New | CZ14 | 4.77 | 0.000556 | 0 | 6.56 | 0.000689 | 0 | 4.77 | 0.000556 | 0 | 6.56 | 0.000689 | 0 |  | LF | None | 4770 | 0.556 | 4770 | 0.556 | 1.38 | 1.24 | 0 | 4770 | 0.556 | 4770 | 0.556 | 1.38 | 1.24 | 0
LFNoneSDGWRfNewCZ15 | Com-Iltg-dWatt-LF_OSnone | SDG | WRf | New | CZ15 | 4.77 | 0.000556 | 0 | 7.01 | 0.000694 | 0 | 4.77 | 0.000556 | 0 | 7.01 | 0.000694 | 0 |  | LF | None | 4770 | 0.556 | 4770 | 0.556 | 1.47 | 1.25 | 0 | 4770 | 0.556 | 4770 | 0.556 | 1.47 | 1.25 | 0
LFNoneSDGWRfNewIOU | Com-Iltg-dWatt-LF_OSnone | SDG | WRf | New | IOU | 4.77 | 0.000556 | 0 | 6.7942 | 0.00068819 | 0 | 4.77 | 0.000556 | 0 | 6.7942 | 0.00068819 | 0 |  | LF | None | 4770 | 0.556 | 4770 | 0.556 | 1.42 | 1.24 | 0 | 4770 | 0.556 | 4770 | 0.556 | 1.42 | 1.24 | 0
LFAllSpcPGEAsmExCZ01 | Com-Iltg-dWatt-LF_OSspc | PGE | Asm | Ex | CZ01 | 2.2205 | 0.00043195 | 0 | 2.1105 | 0.00049295 | -0.04261 | 2.2205 | 0.00043195 | 0 | 2.1105 | 0.00049295 | -0.04261 |  | LF | AllSpc | 2220 | 0.432 | 2220 | 0.432 | 0.95 | 1.14 | -0.019189 | 2220 | 0.432 | 2220 | 0.432 | 0.95 | 1.14 | -0.0192
LFAllSpcPGEAsmExCZ02 | Com-Iltg-dWatt-LF_OSspc | PGE | Asm | Ex | CZ02 | 2.2204 | 0.00043196 | 0 | 2.2904 | 0.00050296 | -0.024004 | 2.2204 | 0.00043196 | 0 | 2.2904 | 0.00050296 | -0.024004 |  | LF | AllSpc | 2220 | 0.432 | 2220 | 0.432 | 1.03 | 1.16 | -0.010811 | 2220 | 0.432 | 2220 | 0.432 | 1.03 | 1.16 | -0.0108
LFAllSpcPGEAsmExCZ03 | Com-Iltg-dWatt-LF_OSspc | PGE | Asm | Ex | CZ03 | 2.2203 | 0.00043197 | 0 | 2.2703 | 0.00050397 | -0.026403 | 2.2203 | 0.00043197 | 0 | 2.2703 | 0.00050397 | -0.026403 |  | LF | AllSpc | 2220 | 0.432 | 2220 | 0.432 | 1.02 | 1.17 | -0.011892 | 2220 | 0.432 | 2220 | 0.432 | 1.02 | 1.17 | -0.0119
LFAllSpcPGEAsmExCZ04 | Com-Iltg-dWatt-LF_OSspc | PGE | Asm | Ex | CZ04 | 2.2204 | 0.00043196 | 0 | 2.3304 | 0.00050296 | -0.0198 | 2.2204 | 0.00043196 | 0 | 2.3304 | 0.00050296 | -0.0198 |  | LF | AllSpc | 2220 | 0.432 | 2220 | 0.432 | 1.05 | 1.16 | -0.0089172 | 2220 | 0.432 | 2220 | 0.432 | 1.05 | 1.16 | -0.00892
LFAllSpcPGEAsmExCZ05 | Com-Iltg-dWatt-LF_OSspc | PGE | Asm | Ex | CZ05 | 2.2204 | 0.00043196 | 0 | 2.29 | 0.00049496 | -0.0238 | 2.2204 | 0.00043196 | 0 | 2.29 | 0.00049496 | -0.0238 |  | LF | AllSpc | 2220 | 0.432 | 2220 | 0.432 | 1.03 | 1.15 | -0.010719 | 2220 | 0.432 | 2220 | 0.432 | 1.03 | 1.15 | -0.0107
LFAllSpcPGEAsmExCZ11 | Com-Iltg-dWatt-LF_OSspc | PGE | Asm | Ex | CZ11 | 2.2207 | 0.00043193 | 0 | 2.3307 | 0.00050193 | -0.0208 | 2.2207 | 0.00043193 | 0 | 2.3307 | 0.00050193 | -0.0208 |  | LF | AllSpc | 2220 | 0.432 | 2220 | 0.432 | 1.05 | 1.16 | -0.0093666 | 2220 | 0.432 | 2220 | 0.432 | 1.05 | 1.16 | -0.00937
LFAllSpcPGEAsmExCZ12 | Com-Iltg-dWatt-LF_OSspc | PGE | Asm | Ex | CZ12 | 2.2205 | 0.00043195 | 0 | 2.32 | 0.00050595 | -0.021905 | 2.2205 | 0.00043195 | 0 | 2.32 | 0.00050595 | -0.021905 |  | LF | AllSpc | 2220 | 0.432 | 2220 | 0.432 | 1.04 | 1.17 | -0.0098649 | 2220 | 0.432 | 2220 | 0.432 | 1.04 | 1.17 | -0.00986
LFAllSpcPGEAsmExCZ13 | Com-Iltg-dWatt-LF_OSspc | PGE | Asm | Ex | CZ13 | 2.2206 | 0.00043194 | 0 | 2.3306 | 0.00050194 | -0.0202 | 2.2206 | 0.00043194 | 0 | 2.3306 | 0.00050194 | -0.0202 |  | LF | AllSpc | 2220 | 0.432 | 2220 | 0.432 | 1.05 | 1.16 | -0.0090965 | 2220 | 0.432 | 2220 | 0.432 | 1.05 | 1.16 | -0.0091
LFAllSpcPGEAsmExCZ16 | Com-Iltg-dWatt-LF_OSspc | PGE | Asm | Ex | CZ16 | 2.2206 | 0.00043194 | 0 | 2.17 | 0.00049494 | -0.031806 | 2.2206 | 0.00043194 | 0 | 2.17 | 0.00049494 | -0.031806 |  | LF | AllSpc | 2220 | 0.432 | 2220 | 0.432 | 0.977 | 1.15 | -0.014323 | 2220 | 0.432 | 2220 | 0.432 | 0.977 | 1.15 | -0.0143
LFAllSpcPGEAsmExIOU | Com-Iltg-dWatt-LF_OSspc | PGE | Asm | Ex | IOU | 2.2204 | 0.00043196 | 0 | 2.3008 | 0.00050338 | -0.023245 | 2.2204 | 0.00043196 | 0 | 2.3008 | 0.00050338 | -0.023245 |  | LF | AllSpc | 2220 | 0.432 | 2220 | 0.432 | 1.04 | 1.17 | -0.010469 | 2220 | 0.432 | 2220 | 0.432 | 1.04 | 1.17 | -0.0105
LFAllSpcPGEAsmNewCZ01 | Com-Iltg-dWatt-LF_OSspc | PGE | Asm | New | CZ01 | 2.23 | 0.000431 | 0 | 2.13 | 0.000496 | -0.0423 | 2.23 | 0.000431 | 0 | 2.13 | 0.000496 | -0.0423 |  | LF | AllSpc | 2230 | 0.431 | 2230 | 0.431 | 0.955 | 1.15 | -0.018969 | 2230 | 0.431 | 2230 | 0.431 | 0.955 | 1.15 | -0.019
LFAllSpcPGEAsmNewCZ02 | Com-Iltg-dWatt-LF_OSspc | PGE | Asm | New | CZ02 | 2.23 | 0.000431 | 0 | 2.27 | 0.000505 | -0.0263 | 2.23 | 0.000431 | 0 | 2.27 | 0.000505 | -0.0263 |  | LF | AllSpc | 2230 | 0.431 | 2230 | 0.431 | 1.02 | 1.17 | -0.011794 | 2230 | 0.431 | 2230 | 0.431 | 1.02 | 1.17 | -0.0118
LFAllSpcPGEAsmNewCZ03 | Com-Iltg-dWatt-LF_OSspc | PGE | Asm | New | CZ03 | 2.23 | 0.000431 | 0 | 2.25 | 0.000498 | -0.0278 | 2.23 | 0.000431 | 0 | 2.25 | 0.000498 | -0.0278 |  | LF | AllSpc | 2230 | 0.431 | 2230 | 0.431 | 1.01 | 1.16 | -0.012466 | 2230 | 0.431 | 2230 | 0.431 | 1.01 | 1.16 | -0.0125
LFAllSpcPGEAsmNewCZ04 | Com-Iltg-dWatt-LF_OSspc | PGE | Asm | New | CZ04 | 2.23 | 0.000431 | 0 | 2.31 | 0.000502 | -0.0218 | 2.23 | 0.000431 | 0 | 2.31 | 0.000502 | -0.0218 |  | LF | AllSpc | 2230 | 0.431 | 2230 | 0.431 | 1.04 | 1.16 | -0.0097758 | 2230 | 0.431 | 2230 | 0.431 | 1.04 | 1.16 | -0.00978
LFAllSpcPGEAsmNewCZ05 | Com-Iltg-dWatt-LF_OSspc | PGE | Asm | New | CZ05 | 2.23 | 0.000431 | 0 | 2.27 | 0.000492 | -0.0243 | 2.23 | 0.000431 | 0 | 2.27 | 0.000492 | -0.0243 |  | LF | AllSpc | 2230 | 0.431 | 2230 | 0.431 | 1.02 | 1.14 | -0.010897 | 2230 | 0.431 | 2230 | 0.431 | 1.02 | 1.14 | -0.0109
LFAllSpcPGEAsmNewCZ11 | Com-Iltg-dWatt-LF_OSspc | PGE | Asm | New | CZ11 | 2.23 | 0.000431 | 0 | 2.33 | 0.000511 | -0.0225 | 2.23 | 0.000431 | 0 | 2.33 | 0.000511 | -0.0225 |  | LF | AllSpc | 2230 | 0.431 | 2230 | 0.431 | 1.04 | 1.19 | -0.01009 | 2230 | 0.431 | 2230 | 0.431 | 1.04 | 1.19 | -0.0101
LFAllSpcPGEAsmNewCZ12 | Com-Iltg-dWatt-LF_OSspc | PGE | Asm | New | CZ12 | 2.23 | 0.000431 | 0 | 2.31 | 0.00051 | -0.0241 | 2.23 | 0.000431 | 0 | 2.31 | 0.00051 | -0.0241 |  | LF | AllSpc | 2230 | 0.431 | 2230 | 0.431 | 1.04 | 1.18 | -0.010807 | 2230 | 0.431 | 2230 | 0.431 | 1.04 | 1.18 | -0.0108
LFAllSpcPGEAsmNewCZ13 | Com-Iltg-dWatt-LF_OSspc | PGE | Asm | New | CZ13 | 2.23 | 0.000431 | 0 | 2.33 | 0.00051 | -0.0218 | 2.23 | 0.000431 | 0 | 2.33 | 0.00051 | -0.0218 |  | LF | AllSpc | 2230 | 0.431 | 2230 | 0.431 | 1.04 | 1.18 | -0.0097758 | 2230 | 0.431 | 2230 | 0.431 | 1.04 | 1.18 | -0.00978
LFAllSpcPGEAsmNewCZ16 | Com-Iltg-dWatt-LF_OSspc | PGE | Asm | New | CZ16 | 2.23 | 0.000431 | 0 | 2.19 | 0.000495 | -0.0321 | 2.23 | 0.000431 | 0 | 2.19 | 0.000495 | -0.0321 |  | LF | AllSpc | 2230 | 0.431 | 2230 | 0.431 | 0.982 | 1.15 | -0.014395 | 2230 | 0.431 | 2230 | 0.431 | 0.982 | 1.15 | -0.0144
LFAllSpcPGEAsmNewIOU | Com-Iltg-dWatt-LF_OSspc | PGE | Asm | New | IOU | 2.23 | 0.000431 | 0 | 2.2944 | 0.0005048 | -0.024439 | 2.23 | 0.000431 | 0 | 2.2944 | 0.0005048 | -0.024439 |  | LF | AllSpc | 2230 | 0.431 | 2230 | 0.431 | 1.03 | 1.17 | -0.010959 | 2230 | 0.431 | 2230 | 0.431 | 1.03 | 1.17 | -0.011
LFAllSpcPGEComExCZ01 | Com-Iltg-dWatt-LF_OSspc | PGE | Com | Ex | CZ01 | 2.7768 | 0.0006106 | 0 | 2.7169 | 0.00070608 | -0.034564 | 2.7768 | 0.0006106 | 0 | 2.7169 | 0.00070608 | -0.034564 |  | LF | AllSpc | 2780 | 0.611 | 2780 | 0.611 | 0.978 | 1.16 | -0.012447 | 2780 | 0.611 | 2780 | 0.611 | 0.978 | 1.16 | -0.0124
LFAllSpcPGEComExCZ02 | Com-Iltg-dWatt-LF_OSspc | PGE | Com | Ex | CZ02 | 2.9003 | 0.00055544 | 0 | 3.0247 | 0.00067207 | -0.022012 | 2.9003 | 0.00055544 | 0 | 3.0247 | 0.00067207 | -0.022012 |  | LF | AllSpc | 2900 | 0.555 | 2900 | 0.555 | 1.04 | 1.21 | -0.0075894 | 2900 | 0.555 | 2900 | 0.555 | 1.04 | 1.21 | -0.00759
LFAllSpcPGEComExCZ03 | Com-Iltg-dWatt-LF_OSspc | PGE | Com | Ex | CZ03 | 2.7229 | 0.00055599 | 0 | 2.8568 | 0.0006735 | -0.019306 | 2.7229 | 0.00055599 | 0 | 2.8568 | 0.0006735 | -0.019306 |  | LF | AllSpc | 2720 | 0.556 | 2720 | 0.556 | 1.05 | 1.21 | -0.0070904 | 2720 | 0.556 | 2720 | 0.556 | 1.05 | 1.21 | -0.00709
LFAllSpcPGEComExCZ04 | Com-Iltg-dWatt-LF_OSspc | PGE | Com | Ex | CZ04 | 2.7222 | 0.00061419 | 0 | 2.9059 | 0.00074985 | -0.015545 | 2.7222 | 0.00061419 | 0 | 2.9059 | 0.00074985 | -0.015545 |  | LF | AllSpc | 2720 | 0.614 | 2720 | 0.614 | 1.07 | 1.22 | -0.0057104 | 2720 | 0.614 | 2720 | 0.614 | 1.07 | 1.22 | -0.00571
LFAllSpcPGEComExCZ05 | Com-Iltg-dWatt-LF_OSspc | PGE | Com | Ex | CZ05 | 2.6986 | 0.00059164 | 0 | 2.8283 | 0.00070525 | -0.020021 | 2.6986 | 0.00059164 | 0 | 2.8283 | 0.00070525 | -0.020021 |  | LF | AllSpc | 2700 | 0.592 | 2700 | 0.592 | 1.05 | 1.19 | -0.0074189 | 2700 | 0.592 | 2700 | 0.592 | 1.05 | 1.19 | -0.00742
LFAllSpcPGEComExCZ11 | Com-Iltg-dWatt-LF_OSspc | PGE | Com | Ex | CZ11 | 2.9248 | 0.00054908 | 0 | 3.097 | 0.00066385 | -0.019986 | 2.9248 | 0.00054908 | 0 | 3.097 | 0.00066385 | -0.019986 |  | LF | AllSpc | 2920 | 0.549 | 2920 | 0.549 | 1.06 | 1.21 | -0.0068335 | 2920 | 0.549 | 2920 | 0.549 | 1.06 | 1.21 | -0.00683
LFAllSpcPGEComExCZ12 | Com-Iltg-dWatt-LF_OSspc | PGE | Com | Ex | CZ12 | 2.9072 | 0.00056871 | 0 | 3.074 | 0.00068754 | -0.019277 | 2.9072 | 0.00056871 | 0 | 3.074 | 0.00068754 | -0.019277 |  | LF | AllSpc | 2910 | 0.569 | 2910 | 0.569 | 1.06 | 1.21 | -0.0066309 | 2910 | 0.569 | 2910 | 0.569 | 1.06 | 1.21 | -0.00663
LFAllSpcPGEComExCZ13 | Com-Iltg-dWatt-LF_OSspc | PGE | Com | Ex | CZ13 | 2.9069 | 0.0005515 | 0 | 3.1282 | 0.0006637 | -0.017716 | 2.9069 | 0.0005515 | 0 | 3.1282 | 0.0006637 | -0.017716 |  | LF | AllSpc | 2910 | 0.551 | 2910 | 0.551 | 1.08 | 1.2 | -0.0060945 | 2910 | 0.551 | 2910 | 0.551 | 1.08 | 1.2 | -0.00609
LFAllSpcPGEComExCZ16 | Com-Iltg-dWatt-LF_OSspc | PGE | Com | Ex | CZ16 | 2.7548 | 0.00050878 | 0 | 2.6812 | 0.00059394 | -0.029764 | 2.7548 | 0.00050878 | 0 | 2.6812 | 0.00059394 | -0.029764 |  | LF | AllSpc | 2750 | 0.509 | 2750 | 0.509 | 0.973 | 1.17 | -0.010805 | 2750 | 0.509 | 2750 | 0.509 | 0.973 | 1.17 | -0.0108
LFAllSpcPGEComExIOU | Com-Iltg-dWatt-LF_OSspc | PGE | Com | Ex | IOU | 2.8058 | 0.00056767 | 0 | 2.9634 | 0.00068684 | -0.018956 | 2.8058 | 0.00056767 | 0 | 2.9634 | 0.00068684 | -0.018956 |  | LF | AllSpc | 2810 | 0.568 | 2810 | 0.568 | 1.06 | 1.21 | -0.0067562 | 2810 | 0.568 | 2810 | 0.568 | 1.06 | 1.21 | -0.00676
LFAllSpcPGEComNewCZ05 | Com-Iltg-dWatt-LF_OSspc | PGE | Com | New | CZ05 | 2.6541 | 0.00057631 | 0 | 2.7373 | 0.00069044 | -0.019304 | 2.6541 | 0.00057631 | 0 | 2.7373 | 0.00069044 | -0.019304 |  | LF | AllSpc | 2650 | 0.576 | 2650 | 0.576 | 1.03 | 1.2 | -0.007273 | 2650 | 0.576 | 2650 | 0.576 | 1.03 | 1.2 | -0.00727
LFAllSpcPGEComNewCZ11 | Com-Iltg-dWatt-LF_OSspc | PGE | Com | New | CZ11 | 2.9589 | 0.00055929 | 0 | 3.134 | 0.00068688 | -0.019029 | 2.9589 | 0.00055929 | 0 | 3.134 | 0.00068688 | -0.019029 |  | LF | AllSpc | 2960 | 0.559 | 2960 | 0.559 | 1.06 | 1.23 | -0.006431 | 2960 | 0.559 | 2960 | 0.559 | 1.06 | 1.23 | -0.00643
LFAllSpcPGEComNewCZ12 | Com-Iltg-dWatt-LF_OSspc | PGE | Com | New | CZ12 | 2.9115 | 0.00057255 | 0 | 3.0812 | 0.00070069 | -0.018105 | 2.9115 | 0.00057255 | 0 | 3.0812 | 0.00070069 | -0.018105 |  | LF | AllSpc | 2910 | 0.573 | 2910 | 0.573 | 1.06 | 1.22 | -0.0062184 | 2910 | 0.573 | 2910 | 0.573 | 1.06 | 1.22 | -0.00622
LFAllSpcPGEComNewCZ13 | Com-Iltg-dWatt-LF_OSspc | PGE | Com | New | CZ13 | 2.9543 | 0.00056634 | 0 | 3.1695 | 0.00068762 | -0.017133 | 2.9543 | 0.00056634 | 0 | 3.1695 | 0.00068762 | -0.017133 |  | LF | AllSpc | 2950 | 0.566 | 2950 | 0.566 | 1.07 | 1.21 | -0.0057993 | 2950 | 0.566 | 2950 | 0.566 | 1.07 | 1.21 | -0.0058
LFAllSpcPGEComNewCZ16 | Com-Iltg-dWatt-LF_OSspc | PGE | Com | New | CZ16 | 2.7875 | 0.00051332 | 0 | 2.7139 | 0.00060039 | -0.028037 | 2.7875 | 0.00051332 | 0 | 2.7139 | 0.00060039 | -0.028037 |  | LF | AllSpc | 2790 | 0.513 | 2790 | 0.513 | 0.974 | 1.17 | -0.010058 | 2790 | 0.513 | 2790 | 0.513 | 0.974 | 1.17 | -0.0101
LFAllSpcPGEComNewIOU | Com-Iltg-dWatt-LF_OSspc | PGE | Com | New | IOU | 2.8458 | 0.00057712 | 0 | 2.9932 | 0.00070157 | -0.017944 | 2.8458 | 0.00057712 | 0 | 2.9932 | 0.00070157 | -0.017944 |  | LF | AllSpc | 2850 | 0.577 | 2850 | 0.577 | 1.05 | 1.22 | -0.0063054 | 2850 | 0.577 | 2850 | 0.577 | 1.05 | 1.22 | -0.00631
LFAllSpcPGEECCExCZ01 | Com-Iltg-dWatt-LF_OSspc | PGE | ECC | Ex | CZ01 | 2.1303 | 0.00066097 | 0 | 2.2 | 0.00079697 | -0.0429 | 2.1303 | 0.00066097 | 0 | 2.2 | 0.00079697 | -0.0429 |  | LF | AllSpc | 2130 | 0.661 | 2130 | 0.661 | 1.03 | 1.21 | -0.020138 | 2130 | 0.661 | 2130 | 0.661 | 1.03 | 1.21 | -0.0201
LFAllSpcPGEECCExCZ02 | Com-Iltg-dWatt-LF_OSspc | PGE | ECC | Ex | CZ02 | 2.1305 | 0.000399 | 0 | 2.33 | 0.00052095 | -0.0258 | 2.1305 | 0.000399 | 0 | 2.33 | 0.00052095 | -0.0258 |  | LF | AllSpc | 2130 | 0.399 | 2130 | 0.399 | 1.09 | 1.31 | -0.01211 | 2130 | 0.399 | 2130 | 0.399 | 1.09 | 1.31 | -0.0121
LFAllSpcPGEECCExCZ03 | Com-Iltg-dWatt-LF_OSspc | PGE | ECC | Ex | CZ03 | 2.1304 | 0.000399 | 0 | 2.31 | 0.000495 | -0.0269 | 2.1304 | 0.000399 | 0 | 2.31 | 0.000495 | -0.0269 |  | LF | AllSpc | 2130 | 0.399 | 2130 | 0.399 | 1.08 | 1.24 | -0.012627 | 2130 | 0.399 | 2130 | 0.399 | 1.08 | 1.24 | -0.0126
LFAllSpcPGEECCExCZ04 | Com-Iltg-dWatt-LF_OSspc | PGE | ECC | Ex | CZ04 | 2.1305 | 0.00066095 | 0 | 2.37 | 0.0008559 | -0.0203 | 2.1305 | 0.00066095 | 0 | 2.37 | 0.0008559 | -0.0203 |  | LF | AllSpc | 2130 | 0.661 | 2130 | 0.661 | 1.11 | 1.29 | -0.0095282 | 2130 | 0.661 | 2130 | 0.661 | 1.11 | 1.29 | -0.00953
LFAllSpcPGEECCExCZ05 | Com-Iltg-dWatt-LF_OSspc | PGE | ECC | Ex | CZ05 | 2.1305 | 0.00066095 | 0 | 2.31 | 0.00080595 | -0.0258 | 2.1305 | 0.00066095 | 0 | 2.31 | 0.00080595 | -0.0258 |  | LF | AllSpc | 2130 | 0.661 | 2130 | 0.661 | 1.08 | 1.22 | -0.01211 | 2130 | 0.661 | 2130 | 0.661 | 1.08 | 1.22 | -0.0121
LFAllSpcPGEECCExCZ11 | Com-Iltg-dWatt-LF_OSspc | PGE | ECC | Ex | CZ11 | 2.1306 | 0.000399 | 0 | 2.39 | 0.00049694 | -0.0233 | 2.1306 | 0.000399 | 0 | 2.39 | 0.00049694 | -0.0233 |  | LF | AllSpc | 2130 | 0.399 | 2130 | 0.399 | 1.12 | 1.25 | -0.010936 | 2130 | 0.399 | 2130 | 0.399 | 1.12 | 1.25 | -0.0109
LFAllSpcPGEECCExCZ12 | Com-Iltg-dWatt-LF_OSspc | PGE | ECC | Ex | CZ12 | 2.1306 | 0.000399 | 0 | 2.37 | 0.00051394 | -0.023006 | 2.1306 | 0.000399 | 0 | 2.37 | 0.00051394 | -0.023006 |  | LF | AllSpc | 2130 | 0.399 | 2130 | 0.399 | 1.11 | 1.29 | -0.010798 | 2130 | 0.399 | 2130 | 0.399 | 1.11 | 1.29 | -0.0108
LFAllSpcPGEECCExCZ13 | Com-Iltg-dWatt-LF_OSspc | PGE | ECC | Ex | CZ13 | 2.1306 | 0.000399 | 0 | 2.41 | 0.000519 | -0.0205 | 2.1306 | 0.000399 | 0 | 2.41 | 0.000519 | -0.0205 |  | LF | AllSpc | 2130 | 0.399 | 2130 | 0.399 | 1.13 | 1.3 | -0.0096217 | 2130 | 0.399 | 2130 | 0.399 | 1.13 | 1.3 | -0.00962
LFAllSpcPGEECCExCZ16 | Com-Iltg-dWatt-LF_OSspc | PGE | ECC | Ex | CZ16 | 2.1305 | 0.000399 | 0 | 2.26 | 0.00048896 | -0.037505 | 2.1305 | 0.000399 | 0 | 2.26 | 0.00048896 | -0.037505 |  | LF | AllSpc | 2130 | 0.399 | 2130 | 0.399 | 1.06 | 1.23 | -0.017604 | 2130 | 0.399 | 2130 | 0.399 | 1.06 | 1.23 | -0.0176
LFAllSpcPGEECCExIOU | Com-Iltg-dWatt-LF_OSspc | PGE | ECC | Ex | IOU | 2.1305 | 0.00044895 | 0 | 2.3424 | 0.00056646 | -0.024919 | 2.1305 | 0.00044895 | 0 | 2.3424 | 0.00056646 | -0.024919 |  | LF | AllSpc | 2130 | 0.449 | 2130 | 0.449 | 1.1 | 1.26 | -0.011696 | 2130 | 0.449 | 2130 | 0.449 | 1.1 | 1.26 | -0.0117
LFAllSpcPGEECCNewCZ01 | Com-Iltg-dWatt-LF_OSspc | PGE | ECC | New | CZ01 | 2.14 | 0.00066 | 0 | 2.2 | 0.000774 | -0.0412 | 2.14 | 0.00066 | 0 | 2.2 | 0.000774 | -0.0412 |  | LF | AllSpc | 2140 | 0.66 | 2140 | 0.66 | 1.03 | 1.17 | -0.019252 | 2140 | 0.66 | 2140 | 0.66 | 1.03 | 1.17 | -0.0193
LFAllSpcPGEECCNewCZ02 | Com-Iltg-dWatt-LF_OSspc | PGE | ECC | New | CZ02 | 2.14 | 0.000399 | 0 | 2.34 | 0.000534 | -0.0239 | 2.14 | 0.000399 | 0 | 2.34 | 0.000534 | -0.0239 |  | LF | AllSpc | 2140 | 0.399 | 2140 | 0.399 | 1.09 | 1.34 | -0.011168 | 2140 | 0.399 | 2140 | 0.399 | 1.09 | 1.34 | -0.0112
LFAllSpcPGEECCNewCZ03 | Com-Iltg-dWatt-LF_OSspc | PGE | ECC | New | CZ03 | 2.14 | 0.000399 | 0 | 2.3 | 0.000517 | -0.0252 | 2.14 | 0.000399 | 0 | 2.3 | 0.000517 | -0.0252 |  | LF | AllSpc | 2140 | 0.399 | 2140 | 0.399 | 1.07 | 1.3 | -0.011776 | 2140 | 0.399 | 2140 | 0.399 | 1.07 | 1.3 | -0.0118
LFAllSpcPGEECCNewCZ04 | Com-Iltg-dWatt-LF_OSspc | PGE | ECC | New | CZ04 | 2.14 | 0.00066 | 0 | 2.37 | 0.000831 | -0.0187 | 2.14 | 0.00066 | 0 | 2.37 | 0.000831 | -0.0187 |  | LF | AllSpc | 2140 | 0.66 | 2140 | 0.66 | 1.11 | 1.26 | -0.0087383 | 2140 | 0.66 | 2140 | 0.66 | 1.11 | 1.26 | -0.00874
LFAllSpcPGEECCNewCZ05 | Com-Iltg-dWatt-LF_OSspc | PGE | ECC | New | CZ05 | 2.14 | 0.00066 | 0 | 2.31 | 0.000803 | -0.0246 | 2.14 | 0.00066 | 0 | 2.31 | 0.000803 | -0.0246 |  | LF | AllSpc | 2140 | 0.66 | 2140 | 0.66 | 1.08 | 1.22 | -0.011495 | 2140 | 0.66 | 2140 | 0.66 | 1.08 | 1.22 | -0.0115
LFAllSpcPGEECCNewCZ11 | Com-Iltg-dWatt-LF_OSspc | PGE | ECC | New | CZ11 | 2.14 | 0.000399 | 0 | 2.4 | 0.000525 | -0.0202 | 2.14 | 0.000399 | 0 | 2.4 | 0.000525 | -0.0202 |  | LF | AllSpc | 2140 | 0.399 | 2140 | 0.399 | 1.12 | 1.32 | -0.0094393 | 2140 | 0.399 | 2140 | 0.399 | 1.12 | 1.32 | -0.00944
LFAllSpcPGEECCNewCZ12 | Com-Iltg-dWatt-LF_OSspc | PGE | ECC | New | CZ12 | 2.14 | 0.000399 | 0 | 2.39 | 0.000535 | -0.0204 | 2.14 | 0.000399 | 0 | 2.39 | 0.000535 | -0.0204 |  | LF | AllSpc | 2140 | 0.399 | 2140 | 0.399 | 1.12 | 1.34 | -0.0095327 | 2140 | 0.399 | 2140 | 0.399 | 1.12 | 1.34 | -0.00953
LFAllSpcPGEECCNewCZ13 | Com-Iltg-dWatt-LF_OSspc | PGE | ECC | New | CZ13 | 2.14 | 0.000399 | 0 | 2.42 | 0.000529 | -0.0178 | 2.14 | 0.000399 | 0 | 2.42 | 0.000529 | -0.0178 |  | LF | AllSpc | 2140 | 0.399 | 2140 | 0.399 | 1.13 | 1.33 | -0.0083178 | 2140 | 0.399 | 2140 | 0.399 | 1.13 | 1.33 | -0.00832
LFAllSpcPGEECCNewCZ16 | Com-Iltg-dWatt-LF_OSspc | PGE | ECC | New | CZ16 | 2.14 | 0.000399 | 0 | 2.27 | 0.000507 | -0.0348 | 2.14 | 0.000399 | 0 | 2.27 | 0.000507 | -0.0348 |  | LF | AllSpc | 2140 | 0.399 | 2140 | 0.399 | 1.06 | 1.27 | -0.016262 | 2140 | 0.399 | 2140 | 0.399 | 1.06 | 1.27 | -0.0163
LFAllSpcPGEECCNewIOU | Com-Iltg-dWatt-LF_OSspc | PGE | ECC | New | IOU | 2.14 | 0.00044908 | 0 | 2.3557 | 0.00058132 | -0.022063 | 2.14 | 0.00044908 | 0 | 2.3557 | 0.00058132 | -0.022063 |  | LF | AllSpc | 2140 | 0.449 | 2140 | 0.449 | 1.1 | 1.29 | -0.01031 | 2140 | 0.449 | 2140 | 0.449 | 1.1 | 1.29 | -0.0103
LFAllSpcPGEEPrExCZ01 | Com-Iltg-dWatt-LF_OSspc | PGE | EPr | Ex | CZ01 | 1.86 | 0.00053227 | 0 | 1.85 | 0.00063631 | -0.0337 | 1.86 | 0.00053227 | 0 | 1.85 | 0.00063631 | -0.0337 |  | LF | AllSpc | 1860 | 0.532 | 1860 | 0.532 | 0.995 | 1.2 | -0.018118 | 1860 | 0.532 | 1860 | 0.532 | 0.995 | 1.2 | -0.0181
LFAllSpcPGEEPrExCZ02 | Com-Iltg-dWatt-LF_OSspc | PGE | EPr | Ex | CZ02 | 1.86 | 1.7306e-05 | 0 | 1.97 | 1.7306e-05 | -0.0198 | 1.86 | 1.7306e-05 | 0 | 1.97 | 1.7306e-05 | -0.0198 |  | LF | AllSpc | 1860 | 0.0173 | 1860 | 0.0173 | 1.06 | 1 | -0.010645 | 1860 | 0.0173 | 1860 | 0.0173 | 1.06 | 1 | -0.0106
LFAllSpcPGEEPrExCZ03 | Com-Iltg-dWatt-LF_OSspc | PGE | EPr | Ex | CZ03 | 1.86 | 1.7305e-05 | 0 | 1.99 | 1.7305e-05 | -0.0192 | 1.86 | 1.7305e-05 | 0 | 1.99 | 1.7305e-05 | -0.0192 |  | LF | AllSpc | 1860 | 0.0173 | 1860 | 0.0173 | 1.07 | 1 | -0.010323 | 1860 | 0.0173 | 1860 | 0.0173 | 1.07 | 1 | -0.0103
LFAllSpcPGEEPrExCZ04 | Com-Iltg-dWatt-LF_OSspc | PGE | EPr | Ex | CZ04 | 1.86 | 0.00053222 | 0 | 2.02 | 0.00065625 | -0.0151 | 1.86 | 0.00053222 | 0 | 2.02 | 0.00065625 | -0.0151 |  | LF | AllSpc | 1860 | 0.532 | 1860 | 0.532 | 1.09 | 1.23 | -0.0081183 | 1860 | 0.532 | 1860 | 0.532 | 1.09 | 1.23 | -0.00812
LFAllSpcPGEEPrExCZ05 | Com-Iltg-dWatt-LF_OSspc | PGE | EPr | Ex | CZ05 | 1.86 | 0.00053222 | 0 | 1.98 | 0.00064226 | -0.018 | 1.86 | 0.00053222 | 0 | 1.98 | 0.00064226 | -0.018 |  | LF | AllSpc | 1860 | 0.532 | 1860 | 0.532 | 1.06 | 1.21 | -0.0096774 | 1860 | 0.532 | 1860 | 0.532 | 1.06 | 1.21 | -0.00968
LFAllSpcPGEEPrExCZ11 | Com-Iltg-dWatt-LF_OSspc | PGE | EPr | Ex | CZ11 | 1.86 | 1.7312e-05 | 0 | 1.98 | 1.7312e-05 | -0.0182 | 1.86 | 1.7312e-05 | 0 | 1.98 | 1.7312e-05 | -0.0182 |  | LF | AllSpc | 1860 | 0.0173 | 1860 | 0.0173 | 1.06 | 1 | -0.0097849 | 1860 | 0.0173 | 1860 | 0.0173 | 1.06 | 1 | -0.00978
LFAllSpcPGEEPrExCZ12 | Com-Iltg-dWatt-LF_OSspc | PGE | EPr | Ex | CZ12 | 1.86 | 1.731e-05 | 0 | 1.99 | 1.731e-05 | -0.0188 | 1.86 | 1.731e-05 | 0 | 1.99 | 1.731e-05 | -0.0188 |  | LF | AllSpc | 1860 | 0.0173 | 1860 | 0.0173 | 1.07 | 1 | -0.010108 | 1860 | 0.0173 | 1860 | 0.0173 | 1.07 | 1 | -0.0101
LFAllSpcPGEEPrExCZ13 | Com-Iltg-dWatt-LF_OSspc | PGE | EPr | Ex | CZ13 | 1.86 | 1.7311e-05 | 0 | 2.0005 | 1.7311e-05 | -0.0163 | 1.86 | 1.7311e-05 | 0 | 2.0005 | 1.7311e-05 | -0.0163 |  | LF | AllSpc | 1860 | 0.0173 | 1860 | 0.0173 | 1.08 | 1 | -0.0087634 | 1860 | 0.0173 | 1860 | 0.0173 | 1.08 | 1 | -0.00876
LFAllSpcPGEEPrExCZ16 | Com-Iltg-dWatt-LF_OSspc | PGE | EPr | Ex | CZ16 | 1.86 | 1.7311e-05 | 0 | 1.81 | 1.7311e-05 | -0.0334 | 1.86 | 1.7311e-05 | 0 | 1.81 | 1.7311e-05 | -0.0334 |  | LF | AllSpc | 1860 | 0.0173 | 1860 | 0.0173 | 0.973 | 1 | -0.017957 | 1860 | 0.0173 | 1860 | 0.0173 | 0.973 | 1 | -0.018
LFAllSpcPGEEPrExIOU | Com-Iltg-dWatt-LF_OSspc | PGE | EPr | Ex | IOU | 1.86 | 0.00010791 | 0 | 1.9907 | 0.00012926 | -0.018265 | 1.86 | 0.00010791 | 0 | 1.9907 | 0.00012926 | -0.018265 |  | LF | AllSpc | 1860 | 0.108 | 1860 | 0.108 | 1.07 | 1.2 | -0.0098197 | 1860 | 0.108 | 1860 | 0.108 | 1.07 | 1.2 | -0.00982
LFAllSpcPGEEPrNewCZ01 | Com-Iltg-dWatt-LF_OSspc | PGE | EPr | New | CZ01 | 1.86 | 0.000539 | 0 | 1.85 | 0.000627 | -0.0367 | 1.86 | 0.000539 | 0 | 1.85 | 0.000627 | -0.0367 |  | LF | AllSpc | 1860 | 0.539 | 1860 | 0.539 | 0.995 | 1.16 | -0.019731 | 1860 | 0.539 | 1860 | 0.539 | 0.995 | 1.16 | -0.0197
LFAllSpcPGEEPrNewCZ02 | Com-Iltg-dWatt-LF_OSspc | PGE | EPr | New | CZ02 | 1.86 | 1.75e-05 | 0 | 1.96 | 1.75e-05 | -0.0239 | 1.86 | 1.75e-05 | 0 | 1.96 | 1.75e-05 | -0.0239 |  | LF | AllSpc | 1860 | 0.0175 | 1860 | 0.0175 | 1.05 | 1 | -0.012849 | 1860 | 0.0175 | 1860 | 0.0175 | 1.05 | 1 | -0.0128
LFAllSpcPGEEPrNewCZ03 | Com-Iltg-dWatt-LF_OSspc | PGE | EPr | New | CZ03 | 1.86 | 1.75e-05 | 0 | 1.94 | 1.75e-05 | -0.0201 | 1.86 | 1.75e-05 | 0 | 1.94 | 1.75e-05 | -0.0201 |  | LF | AllSpc | 1860 | 0.0175 | 1860 | 0.0175 | 1.04 | 1 | -0.010806 | 1860 | 0.0175 | 1860 | 0.0175 | 1.04 | 1 | -0.0108
LFAllSpcPGEEPrNewCZ04 | Com-Iltg-dWatt-LF_OSspc | PGE | EPr | New | CZ04 | 1.86 | 0.000539 | 0 | 2 | 0.000712 | -0.018 | 1.86 | 0.000539 | 0 | 2 | 0.000712 | -0.018 |  | LF | AllSpc | 1860 | 0.539 | 1860 | 0.539 | 1.08 | 1.32 | -0.0096774 | 1860 | 0.539 | 1860 | 0.539 | 1.08 | 1.32 | -0.00968
LFAllSpcPGEEPrNewCZ05 | Com-Iltg-dWatt-LF_OSspc | PGE | EPr | New | CZ05 | 1.86 | 0.000539 | 0 | 1.95 | 0.000672 | -0.0175 | 1.86 | 0.000539 | 0 | 1.95 | 0.000672 | -0.0175 |  | LF | AllSpc | 1860 | 0.539 | 1860 | 0.539 | 1.05 | 1.25 | -0.0094086 | 1860 | 0.539 | 1860 | 0.539 | 1.05 | 1.25 | -0.00941
LFAllSpcPGEEPrNewCZ11 | Com-Iltg-dWatt-LF_OSspc | PGE | EPr | New | CZ11 | 1.86 | 1.75e-05 | 0 | 2.03 | 1.75e-05 | -0.0212 | 1.86 | 1.75e-05 | 0 | 2.03 | 1.75e-05 | -0.0212 |  | LF | AllSpc | 1860 | 0.0175 | 1860 | 0.0175 | 1.09 | 1 | -0.011398 | 1860 | 0.0175 | 1860 | 0.0175 | 1.09 | 1 | -0.0114
LFAllSpcPGEEPrNewCZ12 | Com-Iltg-dWatt-LF_OSspc | PGE | EPr | New | CZ12 | 1.86 | 1.75e-05 | 0 | 2 | 1.75e-05 | -0.0216 | 1.86 | 1.75e-05 | 0 | 2 | 1.75e-05 | -0.0216 |  | LF | AllSpc | 1860 | 0.0175 | 1860 | 0.0175 | 1.08 | 1 | -0.011613 | 1860 | 0.0175 | 1860 | 0.0175 | 1.08 | 1 | -0.0116
LFAllSpcPGEEPrNewCZ13 | Com-Iltg-dWatt-LF_OSspc | PGE | EPr | New | CZ13 | 1.86 | 1.75e-05 | 0 | 2.04 | 1.75e-05 | -0.0194 | 1.86 | 1.75e-05 | 0 | 2.04 | 1.75e-05 | -0.0194 |  | LF | AllSpc | 1860 | 0.0175 | 1860 | 0.0175 | 1.1 | 1 | -0.01043 | 1860 | 0.0175 | 1860 | 0.0175 | 1.1 | 1 | -0.0104
LFAllSpcPGEEPrNewCZ16 | Com-Iltg-dWatt-LF_OSspc | PGE | EPr | New | CZ16 | 1.86 | 1.75e-05 | 0 | 1.85 | 1.75e-05 | -0.0311 | 1.86 | 1.75e-05 | 0 | 1.85 | 1.75e-05 | -0.0311 |  | LF | AllSpc | 1860 | 0.0175 | 1860 | 0.0175 | 0.995 | 1 | -0.01672 | 1860 | 0.0175 | 1860 | 0.0175 | 0.995 | 1 | -0.0167
LFAllSpcPGEEPrNewIOU | Com-Iltg-dWatt-LF_OSspc | PGE | EPr | New | IOU | 1.86 | 9.1056e-05 | 0 | 1.9953 | 0.000114 | -0.020721 | 1.86 | 9.1056e-05 | 0 | 1.9953 | 0.000114 | -0.020721 |  | LF | AllSpc | 1860 | 0.0911 | 1860 | 0.0911 | 1.07 | 1.25 | -0.01114 | 1860 | 0.0911 | 1860 | 0.0911 | 1.07 | 1.25 | -0.0111
LFAllSpcPGEERCExCZ01 | Com-Iltg-dWatt-LF_OSspc | PGE | ERC | Ex | CZ01 | 2.19 | 0.0006013 | 0 | 2.12 | 0.00071338 | -0.0378 | 2.19 | 0.0006013 | 0 | 2.12 | 0.00071338 | -0.0378 |  | LF | AllSpc | 2190 | 0.601 | 2190 | 0.601 | 0.968 | 1.19 | -0.01726 | 2190 | 0.601 | 2190 | 0.601 | 0.968 | 1.19 | -0.0173
LFAllSpcPGEERCExCZ02 | Com-Iltg-dWatt-LF_OSspc | PGE | ERC | Ex | CZ02 | 2.19 | 1.7106e-05 | 0 | 2.23 | 1.7106e-05 | -0.0267 | 2.19 | 1.7106e-05 | 0 | 2.23 | 1.7106e-05 | -0.0267 |  | LF | AllSpc | 2190 | 0.0171 | 2190 | 0.0171 | 1.02 | 1 | -0.012192 | 2190 | 0.0171 | 2190 | 0.0171 | 1.02 | 1 | -0.0122
LFAllSpcPGEERCExCZ03 | Com-Iltg-dWatt-LF_OSspc | PGE | ERC | Ex | CZ03 | 2.19 | 1.7105e-05 | 0 | 2.2 | 1.7105e-05 | -0.0247 | 2.19 | 1.7105e-05 | 0 | 2.2 | 1.7105e-05 | -0.0247 |  | LF | AllSpc | 2190 | 0.0171 | 2190 | 0.0171 | 1 | 1 | -0.011279 | 2190 | 0.0171 | 2190 | 0.0171 | 1 | 1 | -0.0113
LFAllSpcPGEERCExCZ04 | Com-Iltg-dWatt-LF_OSspc | PGE | ERC | Ex | CZ04 | 2.19 | 0.00060125 | 0 | 2.29 | 0.00072832 | -0.0208 | 2.19 | 0.00060125 | 0 | 2.29 | 0.00072832 | -0.0208 |  | LF | AllSpc | 2190 | 0.601 | 2190 | 0.601 | 1.05 | 1.21 | -0.0094977 | 2190 | 0.601 | 2190 | 0.601 | 1.05 | 1.21 | -0.0095
LFAllSpcPGEERCExCZ05 | Com-Iltg-dWatt-LF_OSspc | PGE | ERC | Ex | CZ05 | 2.19 | 0.00060125 | 0 | 2.23 | 0.00073432 | -0.0243 | 2.19 | 0.00060125 | 0 | 2.23 | 0.00073432 | -0.0243 |  | LF | AllSpc | 2190 | 0.601 | 2190 | 0.601 | 1.02 | 1.22 | -0.011096 | 2190 | 0.601 | 2190 | 0.601 | 1.02 | 1.22 | -0.0111
LFAllSpcPGEERCExCZ11 | Com-Iltg-dWatt-LF_OSspc | PGE | ERC | Ex | CZ11 | 2.19 | 1.7112e-05 | 0 | 2.28 | 1.7112e-05 | -0.0225 | 2.19 | 1.7112e-05 | 0 | 2.28 | 1.7112e-05 | -0.0225 |  | LF | AllSpc | 2190 | 0.0171 | 2190 | 0.0171 | 1.04 | 1 | -0.010274 | 2190 | 0.0171 | 2190 | 0.0171 | 1.04 | 1 | -0.0103
LFAllSpcPGEERCExCZ12 | Com-Iltg-dWatt-LF_OSspc | PGE | ERC | Ex | CZ12 | 2.19 | 1.711e-05 | 0 | 2.27 | 1.711e-05 | -0.0238 | 2.19 | 1.711e-05 | 0 | 2.27 | 1.711e-05 | -0.0238 |  | LF | AllSpc | 2190 | 0.0171 | 2190 | 0.0171 | 1.04 | 1 | -0.010868 | 2190 | 0.0171 | 2190 | 0.0171 | 1.04 | 1 | -0.0109
LFAllSpcPGEERCExCZ13 | Com-Iltg-dWatt-LF_OSspc | PGE | ERC | Ex | CZ13 | 2.19 | 1.7111e-05 | 0 | 2.31 | 1.7111e-05 | -0.0212 | 2.19 | 1.7111e-05 | 0 | 2.31 | 1.7111e-05 | -0.0212 |  | LF | AllSpc | 2190 | 0.0171 | 2190 | 0.0171 | 1.05 | 1 | -0.0096804 | 2190 | 0.0171 | 2190 | 0.0171 | 1.05 | 1 | -0.00968
LFAllSpcPGEERCExCZ16 | Com-Iltg-dWatt-LF_OSspc | PGE | ERC | Ex | CZ16 | 2.19 | 1.7111e-05 | 0 | 2.17 | 1.7111e-05 | -0.0363 | 2.19 | 1.7111e-05 | 0 | 2.17 | 1.7111e-05 | -0.0363 |  | LF | AllSpc | 2190 | 0.0171 | 2190 | 0.0171 | 0.991 | 1 | -0.016575 | 2190 | 0.0171 | 2190 | 0.0171 | 0.991 | 1 | -0.0166
LFAllSpcPGEERCExIOU | Com-Iltg-dWatt-LF_OSspc | PGE | ERC | Ex | IOU | 2.19 | 0.0001199 | 0 | 2.2539 | 0.00014223 | -0.023588 | 2.19 | 0.0001199 | 0 | 2.2539 | 0.00014223 | -0.023588 |  | LF | AllSpc | 2190 | 0.12 | 2190 | 0.12 | 1.03 | 1.19 | -0.010771 | 2190 | 0.12 | 2190 | 0.12 | 1.03 | 1.19 | -0.0108
LFAllSpcPGEERCNewCZ01 | Com-Iltg-dWatt-LF_OSspc | PGE | ERC | New | CZ01 | 2.19 | 0.000609 | 0 | 2.27 | 0.000728 | -0.0422 | 2.19 | 0.000609 | 0 | 2.27 | 0.000728 | -0.0422 |  | LF | AllSpc | 2190 | 0.609 | 2190 | 0.609 | 1.04 | 1.2 | -0.019269 | 2190 | 0.609 | 2190 | 0.609 | 1.04 | 1.2 | -0.0193
LFAllSpcPGEERCNewCZ02 | Com-Iltg-dWatt-LF_OSspc | PGE | ERC | New | CZ02 | 2.19 | 1.73e-05 | 0 | 2.39 | 1.73e-05 | -0.0276 | 2.19 | 1.73e-05 | 0 | 2.39 | 1.73e-05 | -0.0276 |  | LF | AllSpc | 2190 | 0.0173 | 2190 | 0.0173 | 1.09 | 1 | -0.012603 | 2190 | 0.0173 | 2190 | 0.0173 | 1.09 | 1 | -0.0126
LFAllSpcPGEERCNewCZ03 | Com-Iltg-dWatt-LF_OSspc | PGE | ERC | New | CZ03 | 2.19 | 1.73e-05 | 0 | 2.39 | 1.73e-05 | -0.0247 | 2.19 | 1.73e-05 | 0 | 2.39 | 1.73e-05 | -0.0247 |  | LF | AllSpc | 2190 | 0.0173 | 2190 | 0.0173 | 1.09 | 1 | -0.011279 | 2190 | 0.0173 | 2190 | 0.0173 | 1.09 | 1 | -0.0113
LFAllSpcPGEERCNewCZ04 | Com-Iltg-dWatt-LF_OSspc | PGE | ERC | New | CZ04 | 2.19 | 0.000609 | 0 | 2.44 | 0.000777 | -0.0212 | 2.19 | 0.000609 | 0 | 2.44 | 0.000777 | -0.0212 |  | LF | AllSpc | 2190 | 0.609 | 2190 | 0.609 | 1.11 | 1.28 | -0.0096804 | 2190 | 0.609 | 2190 | 0.609 | 1.11 | 1.28 | -0.00968
LFAllSpcPGEERCNewCZ05 | Com-Iltg-dWatt-LF_OSspc | PGE | ERC | New | CZ05 | 2.19 | 0.000609 | 0 | 2.37 | 0.000754 | -0.0234 | 2.19 | 0.000609 | 0 | 2.37 | 0.000754 | -0.0234 |  | LF | AllSpc | 2190 | 0.609 | 2190 | 0.609 | 1.08 | 1.24 | -0.010685 | 2190 | 0.609 | 2190 | 0.609 | 1.08 | 1.24 | -0.0107
LFAllSpcPGEERCNewCZ11 | Com-Iltg-dWatt-LF_OSspc | PGE | ERC | New | CZ11 | 2.19 | 1.73e-05 | 0 | 2.47 | 1.73e-05 | -0.0247 | 2.19 | 1.73e-05 | 0 | 2.47 | 1.73e-05 | -0.0247 |  | LF | AllSpc | 2190 | 0.0173 | 2190 | 0.0173 | 1.13 | 1 | -0.011279 | 2190 | 0.0173 | 2190 | 0.0173 | 1.13 | 1 | -0.0113
LFAllSpcPGEERCNewCZ12 | Com-Iltg-dWatt-LF_OSspc | PGE | ERC | New | CZ12 | 2.19 | 1.73e-05 | 0 | 2.44 | 1.73e-05 | -0.0254 | 2.19 | 1.73e-05 | 0 | 2.44 | 1.73e-05 | -0.0254 |  | LF | AllSpc | 2190 | 0.0173 | 2190 | 0.0173 | 1.11 | 1 | -0.011598 | 2190 | 0.0173 | 2190 | 0.0173 | 1.11 | 1 | -0.0116
LFAllSpcPGEERCNewCZ13 | Com-Iltg-dWatt-LF_OSspc | PGE | ERC | New | CZ13 | 2.19 | 1.73e-05 | 0 | 2.49 | 1.73e-05 | -0.0225 | 2.19 | 1.73e-05 | 0 | 2.49 | 1.73e-05 | -0.0225 |  | LF | AllSpc | 2190 | 0.0173 | 2190 | 0.0173 | 1.14 | 1 | -0.010274 | 2190 | 0.0173 | 2190 | 0.0173 | 1.14 | 1 | -0.0103
LFAllSpcPGEERCNewCZ16 | Com-Iltg-dWatt-LF_OSspc | PGE | ERC | New | CZ16 | 2.19 | 1.73e-05 | 0 | 2.29 | 1.73e-05 | -0.0398 | 2.19 | 1.73e-05 | 0 | 2.29 | 1.73e-05 | -0.0398 |  | LF | AllSpc | 2190 | 0.0173 | 2190 | 0.0173 | 1.05 | 1 | -0.018174 | 2190 | 0.0173 | 2190 | 0.0173 | 1.05 | 1 | -0.0182
LFAllSpcPGEERCNewIOU | Com-Iltg-dWatt-LF_OSspc | PGE | ERC | New | IOU | 2.19 | 0.00010076 | 0 | 2.4382 | 0.00012361 | -0.024508 | 2.19 | 0.00010076 | 0 | 2.4382 | 0.00012361 | -0.024508 |  | LF | AllSpc | 2190 | 0.101 | 2190 | 0.101 | 1.11 | 1.23 | -0.011191 | 2190 | 0.101 | 2190 | 0.101 | 1.11 | 1.23 | -0.0112
LFAllSpcPGEESeExCZ01 | Com-Iltg-dWatt-LF_OSspc | PGE | ESe | Ex | CZ01 | 1.99 | 0.0006153 | 0 | 1.93 | 0.00073034 | -0.0421 | 1.99 | 0.0006153 | 0 | 1.93 | 0.00073034 | -0.0421 |  | LF | AllSpc | 1990 | 0.615 | 1990 | 0.615 | 0.97 | 1.19 | -0.021156 | 1990 | 0.615 | 1990 | 0.615 | 0.97 | 1.19 | -0.0212
LFAllSpcPGEESeExCZ02 | Com-Iltg-dWatt-LF_OSspc | PGE | ESe | Ex | CZ02 | 1.99 | 1.7309e-05 | 0 | 2.08 | 1.7309e-05 | -0.0259 | 1.99 | 1.7309e-05 | 0 | 2.08 | 1.7309e-05 | -0.0259 |  | LF | AllSpc | 1990 | 0.0173 | 1990 | 0.0173 | 1.05 | 1 | -0.013015 | 1990 | 0.0173 | 1990 | 0.0173 | 1.05 | 1 | -0.013
LFAllSpcPGEESeExCZ03 | Com-Iltg-dWatt-LF_OSspc | PGE | ESe | Ex | CZ03 | 1.99 | 1.7307e-05 | 0 | 2.08 | 1.7307e-05 | -0.0267 | 1.99 | 1.7307e-05 | 0 | 2.08 | 1.7307e-05 | -0.0267 |  | LF | AllSpc | 1990 | 0.0173 | 1990 | 0.0173 | 1.05 | 1 | -0.013417 | 1990 | 0.0173 | 1990 | 0.0173 | 1.05 | 1 | -0.0134
LFAllSpcPGEESeExCZ04 | Com-Iltg-dWatt-LF_OSspc | PGE | ESe | Ex | CZ04 | 1.99 | 0.00061525 | 0 | 2.13 | 0.00075129 | -0.0203 | 1.99 | 0.00061525 | 0 | 2.13 | 0.00075129 | -0.0203 |  | LF | AllSpc | 1990 | 0.615 | 1990 | 0.615 | 1.07 | 1.22 | -0.010201 | 1990 | 0.615 | 1990 | 0.615 | 1.07 | 1.22 | -0.0102
LFAllSpcPGEESeExCZ05 | Com-Iltg-dWatt-LF_OSspc | PGE | ESe | Ex | CZ05 | 1.99 | 0.00061525 | 0 | 2.08 | 0.00073229 | -0.0245 | 1.99 | 0.00061525 | 0 | 2.08 | 0.00073229 | -0.0245 |  | LF | AllSpc | 1990 | 0.615 | 1990 | 0.615 | 1.05 | 1.19 | -0.012312 | 1990 | 0.615 | 1990 | 0.615 | 1.05 | 1.19 | -0.0123
LFAllSpcPGEESeExCZ11 | Com-Iltg-dWatt-LF_OSspc | PGE | ESe | Ex | CZ11 | 1.99 | 1.7318e-05 | 0 | 2.12 | 1.7318e-05 | -0.0229 | 1.99 | 1.7318e-05 | 0 | 2.12 | 1.7318e-05 | -0.0229 |  | LF | AllSpc | 1990 | 0.0173 | 1990 | 0.0173 | 1.07 | 1 | -0.011508 | 1990 | 0.0173 | 1990 | 0.0173 | 1.07 | 1 | -0.0115
LFAllSpcPGEESeExCZ12 | Com-Iltg-dWatt-LF_OSspc | PGE | ESe | Ex | CZ12 | 1.99 | 1.7316e-05 | 0 | 2.11 | 1.7316e-05 | -0.0237 | 1.99 | 1.7316e-05 | 0 | 2.11 | 1.7316e-05 | -0.0237 |  | LF | AllSpc | 1990 | 0.0173 | 1990 | 0.0173 | 1.06 | 1 | -0.01191 | 1990 | 0.0173 | 1990 | 0.0173 | 1.06 | 1 | -0.0119
LFAllSpcPGEESeExCZ13 | Com-Iltg-dWatt-LF_OSspc | PGE | ESe | Ex | CZ13 | 1.99 | 1.7316e-05 | 0 | 2.15 | 1.7316e-05 | -0.0207 | 1.99 | 1.7316e-05 | 0 | 2.15 | 1.7316e-05 | -0.0207 |  | LF | AllSpc | 1990 | 0.0173 | 1990 | 0.0173 | 1.08 | 1 | -0.010402 | 1990 | 0.0173 | 1990 | 0.0173 | 1.08 | 1 | -0.0104
LFAllSpcPGEESeExCZ16 | Com-Iltg-dWatt-LF_OSspc | PGE | ESe | Ex | CZ16 | 1.99 | 1.7316e-05 | 0 | 1.95 | 1.7316e-05 | -0.0363 | 1.99 | 1.7316e-05 | 0 | 1.95 | 1.7316e-05 | -0.0363 |  | LF | AllSpc | 1990 | 0.0173 | 1990 | 0.0173 | 0.98 | 1 | -0.018241 | 1990 | 0.0173 | 1990 | 0.0173 | 0.98 | 1 | -0.0182
LFAllSpcPGEESeExIOU | Com-Iltg-dWatt-LF_OSspc | PGE | ESe | Ex | IOU | 1.99 | 0.00012253 | 0 | 2.1055 | 0.00014587 | -0.023996 | 1.99 | 0.00012253 | 0 | 2.1055 | 0.00014587 | -0.023996 |  | LF | AllSpc | 1990 | 0.123 | 1990 | 0.123 | 1.06 | 1.19 | -0.012058 | 1990 | 0.123 | 1990 | 0.123 | 1.06 | 1.19 | -0.0121
LFAllSpcPGEESeNewCZ01 | Com-Iltg-dWatt-LF_OSspc | PGE | ESe | New | CZ01 | 1.99 | 0.000623 | 0 | 1.98 | 0.000722 | -0.0309 | 1.99 | 0.000623 | 0 | 1.98 | 0.000722 | -0.0309 |  | LF | AllSpc | 1990 | 0.623 | 1990 | 0.623 | 0.995 | 1.16 | -0.015528 | 1990 | 0.623 | 1990 | 0.623 | 0.995 | 1.16 | -0.0155
LFAllSpcPGEESeNewCZ02 | Com-Iltg-dWatt-LF_OSspc | PGE | ESe | New | CZ02 | 1.99 | 1.76e-05 | 0 | 2.11 | 1.76e-05 | -0.0291 | 1.99 | 1.76e-05 | 0 | 2.11 | 1.76e-05 | -0.0291 |  | LF | AllSpc | 1990 | 0.0176 | 1990 | 0.0176 | 1.06 | 1 | -0.014623 | 1990 | 0.0176 | 1990 | 0.0176 | 1.06 | 1 | -0.0146
LFAllSpcPGEESeNewCZ03 | Com-Iltg-dWatt-LF_OSspc | PGE | ESe | New | CZ03 | 1.99 | 1.76e-05 | 0 | 2.09 | 1.76e-05 | -0.0271 | 1.99 | 1.76e-05 | 0 | 2.09 | 1.76e-05 | -0.0271 |  | LF | AllSpc | 1990 | 0.0176 | 1990 | 0.0176 | 1.05 | 1 | -0.013618 | 1990 | 0.0176 | 1990 | 0.0176 | 1.05 | 1 | -0.0136
LFAllSpcPGEESeNewCZ04 | Com-Iltg-dWatt-LF_OSspc | PGE | ESe | New | CZ04 | 1.99 | 0.000623 | 0 | 2.15 | 0.000817 | -0.0229 | 1.99 | 0.000623 | 0 | 2.15 | 0.000817 | -0.0229 |  | LF | AllSpc | 1990 | 0.623 | 1990 | 0.623 | 1.08 | 1.31 | -0.011508 | 1990 | 0.623 | 1990 | 0.623 | 1.08 | 1.31 | -0.0115
LFAllSpcPGEESeNewCZ05 | Com-Iltg-dWatt-LF_OSspc | PGE | ESe | New | CZ05 | 1.99 | 0.000623 | 0 | 2.08 | 0.000764 | -0.0219 | 1.99 | 0.000623 | 0 | 2.08 | 0.000764 | -0.0219 |  | LF | AllSpc | 1990 | 0.623 | 1990 | 0.623 | 1.05 | 1.23 | -0.011005 | 1990 | 0.623 | 1990 | 0.623 | 1.05 | 1.23 | -0.011
LFAllSpcPGEESeNewCZ11 | Com-Iltg-dWatt-LF_OSspc | PGE | ESe | New | CZ11 | 1.99 | 1.76e-05 | 0 | 2.18 | 1.76e-05 | -0.0249 | 1.99 | 1.76e-05 | 0 | 2.18 | 1.76e-05 | -0.0249 |  | LF | AllSpc | 1990 | 0.0176 | 1990 | 0.0176 | 1.1 | 1 | -0.012513 | 1990 | 0.0176 | 1990 | 0.0176 | 1.1 | 1 | -0.0125
LFAllSpcPGEESeNewCZ12 | Com-Iltg-dWatt-LF_OSspc | PGE | ESe | New | CZ12 | 1.99 | 1.76e-05 | 0 | 2.16 | 1.76e-05 | -0.0259 | 1.99 | 1.76e-05 | 0 | 2.16 | 1.76e-05 | -0.0259 |  | LF | AllSpc | 1990 | 0.0176 | 1990 | 0.0176 | 1.09 | 1 | -0.013015 | 1990 | 0.0176 | 1990 | 0.0176 | 1.09 | 1 | -0.013
LFAllSpcPGEESeNewCZ13 | Com-Iltg-dWatt-LF_OSspc | PGE | ESe | New | CZ13 | 1.99 | 1.76e-05 | 0 | 2.21 | 1.76e-05 | -0.0229 | 1.99 | 1.76e-05 | 0 | 2.21 | 1.76e-05 | -0.0229 |  | LF | AllSpc | 1990 | 0.0176 | 1990 | 0.0176 | 1.11 | 1 | -0.011508 | 1990 | 0.0176 | 1990 | 0.0176 | 1.11 | 1 | -0.0115
LFAllSpcPGEESeNewCZ16 | Com-Iltg-dWatt-LF_OSspc | PGE | ESe | New | CZ16 | 1.99 | 1.76e-05 | 0 | 2 | 1.76e-05 | -0.0299 | 1.99 | 1.76e-05 | 0 | 2 | 1.76e-05 | -0.0299 |  | LF | AllSpc | 1990 | 0.0176 | 1990 | 0.0176 | 1.01 | 1 | -0.015025 | 1990 | 0.0176 | 1990 | 0.0176 | 1.01 | 1 | -0.015
LFAllSpcPGEESeNewIOU | Com-Iltg-dWatt-LF_OSspc | PGE | ESe | New | IOU | 1.99 | 0.00010299 | 0 | 2.1523 | 0.00012859 | -0.025193 | 1.99 | 0.00010299 | 0 | 2.1523 | 0.00012859 | -0.025193 |  | LF | AllSpc | 1990 | 0.103 | 1990 | 0.103 | 1.08 | 1.25 | -0.01266 | 1990 | 0.103 | 1990 | 0.103 | 1.08 | 1.25 | -0.0127
LFAllSpcPGEEUnExCZ01 | Com-Iltg-dWatt-LF_OSspc | PGE | EUn | Ex | CZ01 | 2.07 | 0.00059297 | 0 | 2.19 | 0.00072297 | -0.0217 | 2.07 | 0.00059297 | 0 | 2.19 | 0.00072297 | -0.0217 |  | LF | AllSpc | 2070 | 0.593 | 2070 | 0.593 | 1.06 | 1.22 | -0.010483 | 2070 | 0.593 | 2070 | 0.593 | 1.06 | 1.22 | -0.0105
LFAllSpcPGEEUnExCZ02 | Com-Iltg-dWatt-LF_OSspc | PGE | EUn | Ex | CZ02 | 2.07 | 0.000361 | 0 | 2.28 | 0.00044495 | -0.0158 | 2.07 | 0.000361 | 0 | 2.28 | 0.00044495 | -0.0158 |  | LF | AllSpc | 2070 | 0.361 | 2070 | 0.361 | 1.1 | 1.23 | -0.0076329 | 2070 | 0.361 | 2070 | 0.361 | 1.1 | 1.23 | -0.00763
LFAllSpcPGEEUnExCZ03 | Com-Iltg-dWatt-LF_OSspc | PGE | EUn | Ex | CZ03 | 2.07 | 0.000361 | 0 | 2.27 | 0.00042996 | -0.0155 | 2.07 | 0.000361 | 0 | 2.27 | 0.00042996 | -0.0155 |  | LF | AllSpc | 2070 | 0.361 | 2070 | 0.361 | 1.1 | 1.19 | -0.0074879 | 2070 | 0.361 | 2070 | 0.361 | 1.1 | 1.19 | -0.00749
LFAllSpcPGEEUnExCZ04 | Com-Iltg-dWatt-LF_OSspc | PGE | EUn | Ex | CZ04 | 2.07 | 0.00059295 | 0 | 2.31 | 0.00075895 | -0.0124 | 2.07 | 0.00059295 | 0 | 2.31 | 0.00075895 | -0.0124 |  | LF | AllSpc | 2070 | 0.593 | 2070 | 0.593 | 1.12 | 1.28 | -0.0059903 | 2070 | 0.593 | 2070 | 0.593 | 1.12 | 1.28 | -0.00599
LFAllSpcPGEEUnExCZ05 | Com-Iltg-dWatt-LF_OSspc | PGE | EUn | Ex | CZ05 | 2.07 | 0.00059295 | 0 | 2.27 | 0.00071895 | -0.0148 | 2.07 | 0.00059295 | 0 | 2.27 | 0.00071895 | -0.0148 |  | LF | AllSpc | 2070 | 0.593 | 2070 | 0.593 | 1.1 | 1.21 | -0.0071498 | 2070 | 0.593 | 2070 | 0.593 | 1.1 | 1.21 | -0.00715
LFAllSpcPGEEUnExCZ11 | Com-Iltg-dWatt-LF_OSspc | PGE | EUn | Ex | CZ11 | 2.07 | 0.000361 | 0 | 2.32 | 0.00045094 | -0.0141 | 2.07 | 0.000361 | 0 | 2.32 | 0.00045094 | -0.0141 |  | LF | AllSpc | 2070 | 0.361 | 2070 | 0.361 | 1.12 | 1.25 | -0.0068116 | 2070 | 0.361 | 2070 | 0.361 | 1.12 | 1.25 | -0.00681
LFAllSpcPGEEUnExCZ12 | Com-Iltg-dWatt-LF_OSspc | PGE | EUn | Ex | CZ12 | 2.07 | 0.000361 | 0 | 2.31 | 0.00044694 | -0.0142 | 2.07 | 0.000361 | 0 | 2.31 | 0.00044694 | -0.0142 |  | LF | AllSpc | 2070 | 0.361 | 2070 | 0.361 | 1.12 | 1.24 | -0.0068599 | 2070 | 0.361 | 2070 | 0.361 | 1.12 | 1.24 | -0.00686
LFAllSpcPGEEUnExCZ13 | Com-Iltg-dWatt-LF_OSspc | PGE | EUn | Ex | CZ13 | 2.07 | 0.000361 | 0 | 2.34 | 0.000457 | -0.0124 | 2.07 | 0.000361 | 0 | 2.34 | 0.000457 | -0.0124 |  | LF | AllSpc | 2070 | 0.361 | 2070 | 0.361 | 1.13 | 1.27 | -0.0059903 | 2070 | 0.361 | 2070 | 0.361 | 1.13 | 1.27 | -0.00599
LFAllSpcPGEEUnExCZ16 | Com-Iltg-dWatt-LF_OSspc | PGE | EUn | Ex | CZ16 | 2.07 | 0.000361 | 0 | 2.2004 | 0.00043395 | -0.0225 | 2.07 | 0.000361 | 0 | 2.2004 | 0.00043395 | -0.0225 |  | LF | AllSpc | 2070 | 0.361 | 2070 | 0.361 | 1.06 | 1.2 | -0.01087 | 2070 | 0.361 | 2070 | 0.361 | 1.06 | 1.2 | -0.0109
LFAllSpcPGEEUnExIOU | Com-Iltg-dWatt-LF_OSspc | PGE | EUn | Ex | IOU | 2.07 | 0.00040523 | 0 | 2.2912 | 0.00049779 | -0.014667 | 2.07 | 0.00040523 | 0 | 2.2912 | 0.00049779 | -0.014667 |  | LF | AllSpc | 2070 | 0.405 | 2070 | 0.405 | 1.11 | 1.23 | -0.0070855 | 2070 | 0.405 | 2070 | 0.405 | 1.11 | 1.23 | -0.00709
LFAllSpcPGEEUnNewCZ01 | Com-Iltg-dWatt-LF_OSspc | PGE | EUn | New | CZ01 | 2.07 | 0.000592 | 0 | 2.18 | 0.000698 | -0.017 | 2.07 | 0.000592 | 0 | 2.18 | 0.000698 | -0.017 |  | LF | AllSpc | 2070 | 0.592 | 2070 | 0.592 | 1.05 | 1.18 | -0.0082126 | 2070 | 0.592 | 2070 | 0.592 | 1.05 | 1.18 | -0.00821
LFAllSpcPGEEUnNewCZ02 | Com-Iltg-dWatt-LF_OSspc | PGE | EUn | New | CZ02 | 2.07 | 0.000361 | 0 | 2.31 | 0.000473 | -0.0122 | 2.07 | 0.000361 | 0 | 2.31 | 0.000473 | -0.0122 |  | LF | AllSpc | 2070 | 0.361 | 2070 | 0.361 | 1.12 | 1.31 | -0.0058937 | 2070 | 0.361 | 2070 | 0.361 | 1.12 | 1.31 | -0.00589
LFAllSpcPGEEUnNewCZ03 | Com-Iltg-dWatt-LF_OSspc | PGE | EUn | New | CZ03 | 2.07 | 0.000361 | 0 | 2.26 | 0.000459 | -0.0116 | 2.07 | 0.000361 | 0 | 2.26 | 0.000459 | -0.0116 |  | LF | AllSpc | 2070 | 0.361 | 2070 | 0.361 | 1.09 | 1.27 | -0.0056039 | 2070 | 0.361 | 2070 | 0.361 | 1.09 | 1.27 | -0.0056
LFAllSpcPGEEUnNewCZ04 | Com-Iltg-dWatt-LF_OSspc | PGE | EUn | New | CZ04 | 2.07 | 0.000592 | 0 | 2.33 | 0.000746 | -0.00974 | 2.07 | 0.000592 | 0 | 2.33 | 0.000746 | -0.00974 |  | LF | AllSpc | 2070 | 0.592 | 2070 | 0.592 | 1.13 | 1.26 | -0.0047053 | 2070 | 0.592 | 2070 | 0.592 | 1.13 | 1.26 | -0.00471
LFAllSpcPGEEUnNewCZ05 | Com-Iltg-dWatt-LF_OSspc | PGE | EUn | New | CZ05 | 2.07 | 0.000592 | 0 | 2.26 | 0.000715 | -0.0112 | 2.07 | 0.000592 | 0 | 2.26 | 0.000715 | -0.0112 |  | LF | AllSpc | 2070 | 0.592 | 2070 | 0.592 | 1.09 | 1.21 | -0.0054106 | 2070 | 0.592 | 2070 | 0.592 | 1.09 | 1.21 | -0.00541
LFAllSpcPGEEUnNewCZ11 | Com-Iltg-dWatt-LF_OSspc | PGE | EUn | New | CZ11 | 2.07 | 0.000361 | 0 | 2.37 | 0.000474 | -0.011 | 2.07 | 0.000361 | 0 | 2.37 | 0.000474 | -0.011 |  | LF | AllSpc | 2070 | 0.361 | 2070 | 0.361 | 1.14 | 1.31 | -0.005314 | 2070 | 0.361 | 2070 | 0.361 | 1.14 | 1.31 | -0.00531
LFAllSpcPGEEUnNewCZ12 | Com-Iltg-dWatt-LF_OSspc | PGE | EUn | New | CZ12 | 2.07 | 0.000361 | 0 | 2.35 | 0.000474 | -0.0103 | 2.07 | 0.000361 | 0 | 2.35 | 0.000474 | -0.0103 |  | LF | AllSpc | 2070 | 0.361 | 2070 | 0.361 | 1.14 | 1.31 | -0.0049758 | 2070 | 0.361 | 2070 | 0.361 | 1.14 | 1.31 | -0.00498
LFAllSpcPGEEUnNewCZ13 | Com-Iltg-dWatt-LF_OSspc | PGE | EUn | New | CZ13 | 2.07 | 0.000361 | 0 | 2.38 | 0.000474 | -0.00988 | 2.07 | 0.000361 | 0 | 2.38 | 0.000474 | -0.00988 |  | LF | AllSpc | 2070 | 0.361 | 2070 | 0.361 | 1.15 | 1.31 | -0.0047729 | 2070 | 0.361 | 2070 | 0.361 | 1.15 | 1.31 | -0.00477
LFAllSpcPGEEUnNewCZ16 | Com-Iltg-dWatt-LF_OSspc | PGE | EUn | New | CZ16 | 2.07 | 0.000361 | 0 | 2.22 | 0.000454 | -0.0198 | 2.07 | 0.000361 | 0 | 2.22 | 0.000454 | -0.0198 |  | LF | AllSpc | 2070 | 0.361 | 2070 | 0.361 | 1.07 | 1.26 | -0.0095652 | 2070 | 0.361 | 2070 | 0.361 | 1.07 | 1.26 | -0.00957
LFAllSpcPGEEUnNewIOU | Com-Iltg-dWatt-LF_OSspc | PGE | EUn | New | IOU | 2.07 | 0.00040533 | 0 | 2.3171 | 0.0005187 | -0.010961 | 2.07 | 0.00040533 | 0 | 2.3171 | 0.0005187 | -0.010961 |  | LF | AllSpc | 2070 | 0.405 | 2070 | 0.405 | 1.12 | 1.28 | -0.0052954 | 2070 | 0.405 | 2070 | 0.405 | 1.12 | 1.28 | -0.0053
LFAllSpcPGEGroExCZ01 | Com-Iltg-dWatt-LF_OSspc | PGE | Gro | Ex | CZ01 | 4.7695 | 0.00066791 | 0 | 3.8095 | 0.00066291 | -0.085795 | 4.7695 | 0.00066791 | 0 | 3.8095 | 0.00066291 | -0.085795 |  | LF | AllSpc | 4770 | 0.668 | 4770 | 0.668 | 0.799 | 0.993 | -0.017988 | 4770 | 0.668 | 4770 | 0.668 | 0.799 | 0.993 | -0.018
LFAllSpcPGEGroExCZ02 | Com-Iltg-dWatt-LF_OSspc | PGE | Gro | Ex | CZ02 | 4.7695 | 0.0006679 | 0 | 4.3595 | 0.0008639 | -0.063395 | 4.7695 | 0.0006679 | 0 | 4.3595 | 0.0008639 | -0.063395 |  | LF | AllSpc | 4770 | 0.668 | 4770 | 0.668 | 0.914 | 1.29 | -0.013292 | 4770 | 0.668 | 4770 | 0.668 | 0.914 | 1.29 | -0.0133
LFAllSpcPGEGroExCZ03 | Com-Iltg-dWatt-LF_OSspc | PGE | Gro | Ex | CZ03 | 4.7695 | 0.00066791 | 0 | 4.16 | 0.00082786 | -0.072495 | 4.7695 | 0.00066791 | 0 | 4.16 | 0.00082786 | -0.072495 |  | LF | AllSpc | 4770 | 0.668 | 4770 | 0.668 | 0.872 | 1.24 | -0.0152 | 4770 | 0.668 | 4770 | 0.668 | 0.872 | 1.24 | -0.0152
LFAllSpcPGEGroExCZ04 | Com-Iltg-dWatt-LF_OSspc | PGE | Gro | Ex | CZ04 | 4.7695 | 0.0006679 | 0 | 4.46 | 0.00085185 | -0.060095 | 4.7695 | 0.0006679 | 0 | 4.46 | 0.00085185 | -0.060095 |  | LF | AllSpc | 4770 | 0.668 | 4770 | 0.668 | 0.935 | 1.28 | -0.0126 | 4770 | 0.668 | 4770 | 0.668 | 0.935 | 1.28 | -0.0126
LFAllSpcPGEGroExCZ05 | Com-Iltg-dWatt-LF_OSspc | PGE | Gro | Ex | CZ05 | 4.7695 | 0.0006679 | 0 | 4.1295 | 0.0008149 | -0.072495 | 4.7695 | 0.0006679 | 0 | 4.1295 | 0.0008149 | -0.072495 |  | LF | AllSpc | 4770 | 0.668 | 4770 | 0.668 | 0.866 | 1.22 | -0.0152 | 4770 | 0.668 | 4770 | 0.668 | 0.866 | 1.22 | -0.0152
LFAllSpcPGEGroExCZ11 | Com-Iltg-dWatt-LF_OSspc | PGE | Gro | Ex | CZ11 | 4.7693 | 0.00066785 | 0 | 4.6993 | 0.00087978 | -0.051493 | 4.7693 | 0.00066785 | 0 | 4.6993 | 0.00087978 | -0.051493 |  | LF | AllSpc | 4770 | 0.668 | 4770 | 0.668 | 0.985 | 1.32 | -0.010797 | 4770 | 0.668 | 4770 | 0.668 | 0.985 | 1.32 | -0.0108
LFAllSpcPGEGroExCZ12 | Com-Iltg-dWatt-LF_OSspc | PGE | Gro | Ex | CZ12 | 4.7694 | 0.00066787 | 0 | 4.5993 | 0.00086287 | -0.055794 | 4.7694 | 0.00066787 | 0 | 4.5993 | 0.00086287 | -0.055794 |  | LF | AllSpc | 4770 | 0.668 | 4770 | 0.668 | 0.964 | 1.29 | -0.011698 | 4770 | 0.668 | 4770 | 0.668 | 0.964 | 1.29 | -0.0117
LFAllSpcPGEGroExCZ13 | Com-Iltg-dWatt-LF_OSspc | PGE | Gro | Ex | CZ13 | 4.7692 | 0.00066785 | 0 | 4.7492 | 0.00086285 | -0.0486 | 4.7692 | 0.00066785 | 0 | 4.7492 | 0.00086285 | -0.0486 |  | LF | AllSpc | 4770 | 0.668 | 4770 | 0.668 | 0.996 | 1.29 | -0.01019 | 4770 | 0.668 | 4770 | 0.668 | 0.996 | 1.29 | -0.0102
LFAllSpcPGEGroExCZ16 | Com-Iltg-dWatt-LF_OSspc | PGE | Gro | Ex | CZ16 | 4.7693 | 0.00066787 | 0 | 4.1693 | 0.0008298 | -0.067693 | 4.7693 | 0.00066787 | 0 | 4.1693 | 0.0008298 | -0.067693 |  | LF | AllSpc | 4770 | 0.668 | 4770 | 0.668 | 0.874 | 1.24 | -0.014193 | 4770 | 0.668 | 4770 | 0.668 | 0.874 | 1.24 | -0.0142
LFAllSpcPGEGroExIOU | Com-Iltg-dWatt-LF_OSspc | PGE | Gro | Ex | IOU | 4.7694 | 0.00066788 | 0 | 4.4456 | 0.00084915 | -0.061029 | 4.7694 | 0.00066788 | 0 | 4.4456 | 0.00084915 | -0.061029 |  | LF | AllSpc | 4770 | 0.668 | 4770 | 0.668 | 0.932 | 1.27 | -0.012796 | 4770 | 0.668 | 4770 | 0.668 | 0.932 | 1.27 | -0.0128
LFAllSpcPGEGroNewCZ01 | Com-Iltg-dWatt-LF_OSspc | PGE | Gro | New | CZ01 | 4.76 | 0.000666 | 0 | 3.98 | 0.000755 | -0.0881 | 4.76 | 0.000666 | 0 | 3.98 | 0.000755 | -0.0881 |  | LF | AllSpc | 4760 | 0.666 | 4760 | 0.666 | 0.836 | 1.13 | -0.018508 | 4760 | 0.666 | 4760 | 0.666 | 0.836 | 1.13 | -0.0185
LFAllSpcPGEGroNewCZ02 | Com-Iltg-dWatt-LF_OSspc | PGE | Gro | New | CZ02 | 4.76 | 0.000666 | 0 | 4.58 | 0.000893 | -0.0614 | 4.76 | 0.000666 | 0 | 4.58 | 0.000893 | -0.0614 |  | LF | AllSpc | 4760 | 0.666 | 4760 | 0.666 | 0.962 | 1.34 | -0.012899 | 4760 | 0.666 | 4760 | 0.666 | 0.962 | 1.34 | -0.0129
LFAllSpcPGEGroNewCZ03 | Com-Iltg-dWatt-LF_OSspc | PGE | Gro | New | CZ03 | 4.76 | 0.000666 | 0 | 4.36 | 0.000843 | -0.0686 | 4.76 | 0.000666 | 0 | 4.36 | 0.000843 | -0.0686 |  | LF | AllSpc | 4760 | 0.666 | 4760 | 0.666 | 0.916 | 1.27 | -0.014412 | 4760 | 0.666 | 4760 | 0.666 | 0.916 | 1.27 | -0.0144
LFAllSpcPGEGroNewCZ04 | Com-Iltg-dWatt-LF_OSspc | PGE | Gro | New | CZ04 | 4.76 | 0.000666 | 0 | 4.71 | 0.000869 | -0.0547 | 4.76 | 0.000666 | 0 | 4.71 | 0.000869 | -0.0547 |  | LF | AllSpc | 4760 | 0.666 | 4760 | 0.666 | 0.989 | 1.3 | -0.011492 | 4760 | 0.666 | 4760 | 0.666 | 0.989 | 1.3 | -0.0115
LFAllSpcPGEGroNewCZ05 | Com-Iltg-dWatt-LF_OSspc | PGE | Gro | New | CZ05 | 4.76 | 0.000666 | 0 | 4.34 | 0.000825 | -0.0681 | 4.76 | 0.000666 | 0 | 4.34 | 0.000825 | -0.0681 |  | LF | AllSpc | 4760 | 0.666 | 4760 | 0.666 | 0.912 | 1.24 | -0.014307 | 4760 | 0.666 | 4760 | 0.666 | 0.912 | 1.24 | -0.0143
LFAllSpcPGEGroNewCZ11 | Com-Iltg-dWatt-LF_OSspc | PGE | Gro | New | CZ11 | 4.76 | 0.000666 | 0 | 4.88 | 0.000914 | -0.049 | 4.76 | 0.000666 | 0 | 4.88 | 0.000914 | -0.049 |  | LF | AllSpc | 4760 | 0.666 | 4760 | 0.666 | 1.03 | 1.37 | -0.010294 | 4760 | 0.666 | 4760 | 0.666 | 1.03 | 1.37 | -0.0103
LFAllSpcPGEGroNewCZ12 | Com-Iltg-dWatt-LF_OSspc | PGE | Gro | New | CZ12 | 4.76 | 0.000666 | 0 | 4.79 | 0.000901 | -0.0528 | 4.76 | 0.000666 | 0 | 4.79 | 0.000901 | -0.0528 |  | LF | AllSpc | 4760 | 0.666 | 4760 | 0.666 | 1.01 | 1.35 | -0.011092 | 4760 | 0.666 | 4760 | 0.666 | 1.01 | 1.35 | -0.0111
LFAllSpcPGEGroNewCZ13 | Com-Iltg-dWatt-LF_OSspc | PGE | Gro | New | CZ13 | 4.76 | 0.000666 | 0 | 4.94 | 0.000897 | -0.0464 | 4.76 | 0.000666 | 0 | 4.94 | 0.000897 | -0.0464 |  | LF | AllSpc | 4760 | 0.666 | 4760 | 0.666 | 1.04 | 1.35 | -0.0097479 | 4760 | 0.666 | 4760 | 0.666 | 1.04 | 1.35 | -0.00975
LFAllSpcPGEGroNewCZ16 | Com-Iltg-dWatt-LF_OSspc | PGE | Gro | New | CZ16 | 4.76 | 0.000666 | 0 | 4.36 | 0.000842 | -0.0643 | 4.76 | 0.000666 | 0 | 4.36 | 0.000842 | -0.0643 |  | LF | AllSpc | 4760 | 0.666 | 4760 | 0.666 | 0.916 | 1.26 | -0.013508 | 4760 | 0.666 | 4760 | 0.666 | 0.916 | 1.26 | -0.0135
LFAllSpcPGEGroNewIOU | Com-Iltg-dWatt-LF_OSspc | PGE | Gro | New | IOU | 4.76 | 0.000666 | 0 | 4.6929 | 0.00088122 | -0.056039 | 4.76 | 0.000666 | 0 | 4.6929 | 0.00088122 | -0.056039 |  | LF | AllSpc | 4760 | 0.666 | 4760 | 0.666 | 0.986 | 1.32 | -0.011773 | 4760 | 0.666 | 4760 | 0.666 | 0.986 | 1.32 | -0.0118
LFAllSpcPGEHspExCZ01 | Com-Iltg-dWatt-LF_OSspc | PGE | Hsp | Ex | CZ01 | 4.8796 | 0.00075896 | 0 | 5.2396 | 0.00088296 | -0.041752 | 4.8796 | 0.00075896 | 0 | 5.2396 | 0.00088296 | -0.041752 |  | LF | AllSpc | 4880 | 0.759 | 4880 | 0.759 | 1.07 | 1.16 | -0.0085565 | 4880 | 0.759 | 4880 | 0.759 | 1.07 | 1.16 | -0.00856
LFAllSpcPGEHspExCZ02 | Com-Iltg-dWatt-LF_OSspc | PGE | Hsp | Ex | CZ02 | 4.8795 | 0.00075895 | 0 | 5.3846 | 0.00094195 | -0.032695 | 4.8795 | 0.00075895 | 0 | 5.3846 | 0.00094195 | -0.032695 |  | LF | AllSpc | 4880 | 0.759 | 4880 | 0.759 | 1.1 | 1.24 | -0.0067005 | 4880 | 0.759 | 4880 | 0.759 | 1.1 | 1.24 | -0.0067
LFAllSpcPGEHspExCZ03 | Com-Iltg-dWatt-LF_OSspc | PGE | Hsp | Ex | CZ03 | 4.8795 | 0.00075895 | 0 | 5.4095 | 0.00091895 | -0.030795 | 4.8795 | 0.00075895 | 0 | 5.4095 | 0.00091895 | -0.030795 |  | LF | AllSpc | 4880 | 0.759 | 4880 | 0.759 | 1.11 | 1.21 | -0.0063111 | 4880 | 0.759 | 4880 | 0.759 | 1.11 | 1.21 | -0.00631
LFAllSpcPGEHspExCZ04 | Com-Iltg-dWatt-LF_OSspc | PGE | Hsp | Ex | CZ04 | 4.8795 | 0.00075895 | 0 | 5.4095 | 0.0009349 | -0.0292 | 4.8795 | 0.00075895 | 0 | 5.4095 | 0.0009349 | -0.0292 |  | LF | AllSpc | 4880 | 0.759 | 4880 | 0.759 | 1.11 | 1.23 | -0.0059843 | 4880 | 0.759 | 4880 | 0.759 | 1.11 | 1.23 | -0.00598
LFAllSpcPGEHspExCZ05 | Com-Iltg-dWatt-LF_OSspc | PGE | Hsp | Ex | CZ05 | 4.8795 | 0.00075895 | 0 | 5.32 | 0.00090295 | -0.032795 | 4.8795 | 0.00075895 | 0 | 5.32 | 0.00090295 | -0.032795 |  | LF | AllSpc | 4880 | 0.759 | 4880 | 0.759 | 1.09 | 1.19 | -0.006721 | 4880 | 0.759 | 4880 | 0.759 | 1.09 | 1.19 | -0.00672
LFAllSpcPGEHspExCZ11 | Com-Iltg-dWatt-LF_OSspc | PGE | Hsp | Ex | CZ11 | 4.8794 | 0.00075894 | 0 | 5.431 | 0.00094494 | -0.030494 | 4.8794 | 0.00075894 | 0 | 5.431 | 0.00094494 | -0.030494 |  | LF | AllSpc | 4880 | 0.759 | 4880 | 0.759 | 1.11 | 1.25 | -0.0062495 | 4880 | 0.759 | 4880 | 0.759 | 1.11 | 1.25 | -0.00625
LFAllSpcPGEHspExCZ12 | Com-Iltg-dWatt-LF_OSspc | PGE | Hsp | Ex | CZ12 | 4.8794 | 0.00075894 | 0 | 5.4194 | 0.00094594 | -0.029607 | 4.8794 | 0.00075894 | 0 | 5.4194 | 0.00094594 | -0.029607 |  | LF | AllSpc | 4880 | 0.759 | 4880 | 0.759 | 1.11 | 1.25 | -0.0060679 | 4880 | 0.759 | 4880 | 0.759 | 1.11 | 1.25 | -0.00607
LFAllSpcPGEHspExCZ13 | Com-Iltg-dWatt-LF_OSspc | PGE | Hsp | Ex | CZ13 | 4.8794 | 0.00075894 | 0 | 5.4604 | 0.00094384 | -0.0285 | 4.8794 | 0.00075894 | 0 | 5.4604 | 0.00094384 | -0.0285 |  | LF | AllSpc | 4880 | 0.759 | 4880 | 0.759 | 1.12 | 1.24 | -0.0058409 | 4880 | 0.759 | 4880 | 0.759 | 1.12 | 1.24 | -0.00584
LFAllSpcPGEHspExCZ16 | Com-Iltg-dWatt-LF_OSspc | PGE | Hsp | Ex | CZ16 | 4.8795 | 0.00075895 | 0 | 5.1595 | 0.00091495 | -0.046795 | 4.8795 | 0.00075895 | 0 | 5.1595 | 0.00091495 | -0.046795 |  | LF | AllSpc | 4880 | 0.759 | 4880 | 0.759 | 1.06 | 1.21 | -0.0095901 | 4880 | 0.759 | 4880 | 0.759 | 1.06 | 1.21 | -0.00959
LFAllSpcPGEHspExIOU | Com-Iltg-dWatt-LF_OSspc | PGE | Hsp | Ex | IOU | 4.8794 | 0.00075895 | 0 | 5.4145 | 0.00093423 | -0.030335 | 4.8794 | 0.00075895 | 0 | 5.4145 | 0.00093423 | -0.030335 |  | LF | AllSpc | 4880 | 0.759 | 4880 | 0.759 | 1.11 | 1.23 | -0.006217 | 4880 | 0.759 | 4880 | 0.759 | 1.11 | 1.23 | -0.00622
LFAllSpcPGEHspNewCZ01 | Com-Iltg-dWatt-LF_OSspc | PGE | Hsp | New | CZ01 | 4.87 | 0.000758 | 0 | 4.99 | 0.000854 | -0.0411 | 4.87 | 0.000758 | 0 | 4.99 | 0.000854 | -0.0411 |  | LF | AllSpc | 4870 | 0.758 | 4870 | 0.758 | 1.02 | 1.13 | -0.0084394 | 4870 | 0.758 | 4870 | 0.758 | 1.02 | 1.13 | -0.00844
LFAllSpcPGEHspNewCZ02 | Com-Iltg-dWatt-LF_OSspc | PGE | Hsp | New | CZ02 | 4.87 | 0.000758 | 0 | 5.18 | 0.000911 | -0.0338 | 4.87 | 0.000758 | 0 | 5.18 | 0.000911 | -0.0338 |  | LF | AllSpc | 4870 | 0.758 | 4870 | 0.758 | 1.06 | 1.2 | -0.0069405 | 4870 | 0.758 | 4870 | 0.758 | 1.06 | 1.2 | -0.00694
LFAllSpcPGEHspNewCZ03 | Com-Iltg-dWatt-LF_OSspc | PGE | Hsp | New | CZ03 | 4.87 | 0.000758 | 0 | 5.16 | 0.000888 | -0.0305 | 4.87 | 0.000758 | 0 | 5.16 | 0.000888 | -0.0305 |  | LF | AllSpc | 4870 | 0.758 | 4870 | 0.758 | 1.06 | 1.17 | -0.0062628 | 4870 | 0.758 | 4870 | 0.758 | 1.06 | 1.17 | -0.00626
LFAllSpcPGEHspNewCZ04 | Com-Iltg-dWatt-LF_OSspc | PGE | Hsp | New | CZ04 | 4.87 | 0.000758 | 0 | 5.21 | 0.000903 | -0.0302 | 4.87 | 0.000758 | 0 | 5.21 | 0.000903 | -0.0302 |  | LF | AllSpc | 4870 | 0.758 | 4870 | 0.758 | 1.07 | 1.19 | -0.0062012 | 4870 | 0.758 | 4870 | 0.758 | 1.07 | 1.19 | -0.0062
LFAllSpcPGEHspNewCZ05 | Com-Iltg-dWatt-LF_OSspc | PGE | Hsp | New | CZ05 | 4.87 | 0.000758 | 0 | 5.13 | 0.000878 | -0.0336 | 4.87 | 0.000758 | 0 | 5.13 | 0.000878 | -0.0336 |  | LF | AllSpc | 4870 | 0.758 | 4870 | 0.758 | 1.05 | 1.16 | -0.0068994 | 4870 | 0.758 | 4870 | 0.758 | 1.05 | 1.16 | -0.0069
LFAllSpcPGEHspNewCZ11 | Com-Iltg-dWatt-LF_OSspc | PGE | Hsp | New | CZ11 | 4.87 | 0.000758 | 0 | 5.29 | 0.000915 | -0.031 | 4.87 | 0.000758 | 0 | 5.29 | 0.000915 | -0.031 |  | LF | AllSpc | 4870 | 0.758 | 4870 | 0.758 | 1.09 | 1.21 | -0.0063655 | 4870 | 0.758 | 4870 | 0.758 | 1.09 | 1.21 | -0.00637
LFAllSpcPGEHspNewCZ12 | Com-Iltg-dWatt-LF_OSspc | PGE | Hsp | New | CZ12 | 4.87 | 0.000758 | 0 | 5.25 | 0.000918 | -0.0304 | 4.87 | 0.000758 | 0 | 5.25 | 0.000918 | -0.0304 |  | LF | AllSpc | 4870 | 0.758 | 4870 | 0.758 | 1.08 | 1.21 | -0.0062423 | 4870 | 0.758 | 4870 | 0.758 | 1.08 | 1.21 | -0.00624
LFAllSpcPGEHspNewCZ13 | Com-Iltg-dWatt-LF_OSspc | PGE | Hsp | New | CZ13 | 4.87 | 0.000758 | 0 | 5.3 | 0.000915 | -0.0295 | 4.87 | 0.000758 | 0 | 5.3 | 0.000915 | -0.0295 |  | LF | AllSpc | 4870 | 0.758 | 4870 | 0.758 | 1.09 | 1.21 | -0.0060575 | 4870 | 0.758 | 4870 | 0.758 | 1.09 | 1.21 | -0.00606
LFAllSpcPGEHspNewCZ16 | Com-Iltg-dWatt-LF_OSspc | PGE | Hsp | New | CZ16 | 4.87 | 0.000758 | 0 | 4.97 | 0.000886 | -0.0497 | 4.87 | 0.000758 | 0 | 4.97 | 0.000886 | -0.0497 |  | LF | AllSpc | 4870 | 0.758 | 4870 | 0.758 | 1.02 | 1.17 | -0.010205 | 4870 | 0.758 | 4870 | 0.758 | 1.02 | 1.17 | -0.0102
LFAllSpcPGEHspNewIOU | Com-Iltg-dWatt-LF_OSspc | PGE | Hsp | New | IOU | 4.87 | 0.000758 | 0 | 5.2241 | 0.00090602 | -0.030799 | 4.87 | 0.000758 | 0 | 5.2241 | 0.00090602 | -0.030799 |  | LF | AllSpc | 4870 | 0.758 | 4870 | 0.758 | 1.07 | 1.2 | -0.0063241 | 4870 | 0.758 | 4870 | 0.758 | 1.07 | 1.2 | -0.00632
LFAllSpcPGEHtlExCZ01 | Com-Iltg-dWatt-LF_OSspc | PGE | Htl | Ex | CZ01 | 1.6308 | 0.000207 | 0 | 1.4304 | 0.00025106 | -0.010004 | 1.6308 | 0.000207 | 0 | 1.4304 | 0.00025106 | -0.010004 |  | LF | AllSpc | 1630 | 0.207 | 1630 | 0.207 | 0.877 | 1.21 | -0.0061344 | 1630 | 0.207 | 1630 | 0.207 | 0.877 | 1.21 | -0.00613
LFAllSpcPGEHtlExCZ02 | Com-Iltg-dWatt-LF_OSspc | PGE | Htl | Ex | CZ02 | 1.6308 | 0.000207 | 0 | 1.5808 | 0.000257 | -0.0071837 | 1.6308 | 0.000207 | 0 | 1.5808 | 0.000257 | -0.0071837 |  | LF | AllSpc | 1630 | 0.207 | 1630 | 0.207 | 0.969 | 1.24 | -0.0044051 | 1630 | 0.207 | 1630 | 0.207 | 0.969 | 1.24 | -0.00441
LFAllSpcPGEHtlExCZ03 | Com-Iltg-dWatt-LF_OSspc | PGE | Htl | Ex | CZ03 | 1.6304 | 0.000207 | 0 | 1.6004 | 0.00025403 | -0.0070415 | 1.6304 | 0.000207 | 0 | 1.6004 | 0.00025403 | -0.0070415 |  | LF | AllSpc | 1630 | 0.207 | 1630 | 0.207 | 0.982 | 1.23 | -0.0043189 | 1630 | 0.207 | 1630 | 0.207 | 0.982 | 1.23 | -0.00432
LFAllSpcPGEHtlExCZ04 | Com-Iltg-dWatt-LF_OSspc | PGE | Htl | Ex | CZ04 | 1.6312 | 0.000207 | 0 | 1.6412 | 0.00025606 | -0.0058343 | 1.6312 | 0.000207 | 0 | 1.6412 | 0.00025606 | -0.0058343 |  | LF | AllSpc | 1630 | 0.207 | 1630 | 0.207 | 1.01 | 1.24 | -0.0035766 | 1630 | 0.207 | 1630 | 0.207 | 1.01 | 1.24 | -0.00358
LFAllSpcPGEHtlExCZ05 | Com-Iltg-dWatt-LF_OSspc | PGE | Htl | Ex | CZ05 | 1.6313 | 0.000207 | 0 | 1.5812 | 0.000252 | -0.007175 | 1.6313 | 0.000207 | 0 | 1.5812 | 0.000252 | -0.007175 |  | LF | AllSpc | 1630 | 0.207 | 1630 | 0.207 | 0.969 | 1.22 | -0.0043985 | 1630 | 0.207 | 1630 | 0.207 | 0.969 | 1.22 | -0.0044
LFAllSpcPGEHtlExCZ11 | Com-Iltg-dWatt-LF_OSspc | PGE | Htl | Ex | CZ11 | 1.6314 | 0.000207 | 0 | 1.6614 | 0.00026116 | -0.0061148 | 1.6314 | 0.000207 | 0 | 1.6614 | 0.00026116 | -0.0061148 |  | LF | AllSpc | 1630 | 0.207 | 1630 | 0.207 | 1.02 | 1.26 | -0.0037483 | 1630 | 0.207 | 1630 | 0.207 | 1.02 | 1.26 | -0.00375
LFAllSpcPGEHtlExCZ12 | Com-Iltg-dWatt-LF_OSspc | PGE | Htl | Ex | CZ12 | 1.6315 | 0.000207 | 0 | 1.6315 | 0.000261 | -0.0063454 | 1.6315 | 0.000207 | 0 | 1.6315 | 0.000261 | -0.0063454 |  | LF | AllSpc | 1630 | 0.207 | 1630 | 0.207 | 1 | 1.26 | -0.0038892 | 1630 | 0.207 | 1630 | 0.207 | 1 | 1.26 | -0.00389
LFAllSpcPGEHtlExCZ13 | Com-Iltg-dWatt-LF_OSspc | PGE | Htl | Ex | CZ13 | 1.6313 | 0.000207 | 0 | 1.6813 | 0.00025916 | -0.0056855 | 1.6313 | 0.000207 | 0 | 1.6813 | 0.00025916 | -0.0056855 |  | LF | AllSpc | 1630 | 0.207 | 1630 | 0.207 | 1.03 | 1.25 | -0.0034852 | 1630 | 0.207 | 1630 | 0.207 | 1.03 | 1.25 | -0.00349
LFAllSpcPGEHtlExCZ16 | Com-Iltg-dWatt-LF_OSspc | PGE | Htl | Ex | CZ16 | 1.6313 | 0.000207 | 0 | 1.4613 | 0.00025215 | -0.010506 | 1.6313 | 0.000207 | 0 | 1.4613 | 0.00025215 | -0.010506 |  | LF | AllSpc | 1630 | 0.207 | 1630 | 0.207 | 0.896 | 1.22 | -0.0064406 | 1630 | 0.207 | 1630 | 0.207 | 0.896 | 1.22 | -0.00644
LFAllSpcPGEHtlExIOU | Com-Iltg-dWatt-LF_OSspc | PGE | Htl | Ex | IOU | 1.6309 | 0.000207 | 0 | 1.6123 | 0.00025595 | -0.006743 | 1.6309 | 0.000207 | 0 | 1.6123 | 0.00025595 | -0.006743 |  | LF | AllSpc | 1630 | 0.207 | 1630 | 0.207 | 0.989 | 1.24 | -0.0041346 | 1630 | 0.207 | 1630 | 0.207 | 0.989 | 1.24 | -0.00413
LFAllSpcPGEHtlNewCZ01 | Com-Iltg-dWatt-LF_OSspc | PGE | Htl | New | CZ01 | 1.65 | 0.000207 | 0 | 1.38 | 0.000246 | -0.0127 | 1.65 | 0.000207 | 0 | 1.38 | 0.000246 | -0.0127 |  | LF | AllSpc | 1650 | 0.207 | 1650 | 0.207 | 0.836 | 1.19 | -0.007697 | 1650 | 0.207 | 1650 | 0.207 | 0.836 | 1.19 | -0.0077
LFAllSpcPGEHtlNewCZ02 | Com-Iltg-dWatt-LF_OSspc | PGE | Htl | New | CZ02 | 1.65 | 0.000207 | 0 | 1.57 | 0.000264 | -0.00916 | 1.65 | 0.000207 | 0 | 1.57 | 0.000264 | -0.00916 |  | LF | AllSpc | 1650 | 0.207 | 1650 | 0.207 | 0.952 | 1.28 | -0.0055515 | 1650 | 0.207 | 1650 | 0.207 | 0.952 | 1.28 | -0.00555
LFAllSpcPGEHtlNewCZ03 | Com-Iltg-dWatt-LF_OSspc | PGE | Htl | New | CZ03 | 1.65 | 0.000207 | 0 | 1.55 | 0.000256 | -0.0086 | 1.65 | 0.000207 | 0 | 1.55 | 0.000256 | -0.0086 |  | LF | AllSpc | 1650 | 0.207 | 1650 | 0.207 | 0.939 | 1.24 | -0.0052121 | 1650 | 0.207 | 1650 | 0.207 | 0.939 | 1.24 | -0.00521
LFAllSpcPGEHtlNewCZ04 | Com-Iltg-dWatt-LF_OSspc | PGE | Htl | New | CZ04 | 1.65 | 0.000207 | 0 | 1.63 | 0.000261 | -0.00741 | 1.65 | 0.000207 | 0 | 1.63 | 0.000261 | -0.00741 |  | LF | AllSpc | 1650 | 0.207 | 1650 | 0.207 | 0.988 | 1.26 | -0.0044909 | 1650 | 0.207 | 1650 | 0.207 | 0.988 | 1.26 | -0.00449
LFAllSpcPGEHtlNewCZ05 | Com-Iltg-dWatt-LF_OSspc | PGE | Htl | New | CZ05 | 1.65 | 0.000207 | 0 | 1.55 | 0.000254 | -0.00891 | 1.65 | 0.000207 | 0 | 1.55 | 0.000254 | -0.00891 |  | LF | AllSpc | 1650 | 0.207 | 1650 | 0.207 | 0.939 | 1.23 | -0.0054 | 1650 | 0.207 | 1650 | 0.207 | 0.939 | 1.23 | -0.0054
LFAllSpcPGEHtlNewCZ11 | Com-Iltg-dWatt-LF_OSspc | PGE | Htl | New | CZ11 | 1.65 | 0.000207 | 0 | 1.65 | 0.000266 | -0.00794 | 1.65 | 0.000207 | 0 | 1.65 | 0.000266 | -0.00794 |  | LF | AllSpc | 1650 | 0.207 | 1650 | 0.207 | 1 | 1.29 | -0.0048121 | 1650 | 0.207 | 1650 | 0.207 | 1 | 1.29 | -0.00481
LFAllSpcPGEHtlNewCZ12 | Com-Iltg-dWatt-LF_OSspc | PGE | Htl | New | CZ12 | 1.65 | 0.000207 | 0 | 1.63 | 0.000265 | -0.00796 | 1.65 | 0.000207 | 0 | 1.63 | 0.000265 | -0.00796 |  | LF | AllSpc | 1650 | 0.207 | 1650 | 0.207 | 0.988 | 1.28 | -0.0048242 | 1650 | 0.207 | 1650 | 0.207 | 0.988 | 1.28 | -0.00482
LFAllSpcPGEHtlNewCZ13 | Com-Iltg-dWatt-LF_OSspc | PGE | Htl | New | CZ13 | 1.65 | 0.000207 | 0 | 1.67 | 0.000263 | -0.00727 | 1.65 | 0.000207 | 0 | 1.67 | 0.000263 | -0.00727 |  | LF | AllSpc | 1650 | 0.207 | 1650 | 0.207 | 1.01 | 1.27 | -0.0044061 | 1650 | 0.207 | 1650 | 0.207 | 1.01 | 1.27 | -0.00441
LFAllSpcPGEHtlNewCZ16 | Com-Iltg-dWatt-LF_OSspc | PGE | Htl | New | CZ16 | 1.65 | 0.000207 | 0 | 1.45 | 0.000255 | -0.0133 | 1.65 | 0.000207 | 0 | 1.45 | 0.000255 | -0.0133 |  | LF | AllSpc | 1650 | 0.207 | 1650 | 0.207 | 0.879 | 1.23 | -0.0080606 | 1650 | 0.207 | 1650 | 0.207 | 0.879 | 1.23 | -0.00806
LFAllSpcPGEHtlNewIOU | Com-Iltg-dWatt-LF_OSspc | PGE | Htl | New | IOU | 1.65 | 0.000207 | 0 | 1.5964 | 0.0002604 | -0.0083109 | 1.65 | 0.000207 | 0 | 1.5964 | 0.0002604 | -0.0083109 |  | LF | AllSpc | 1650 | 0.207 | 1650 | 0.207 | 0.968 | 1.26 | -0.0050369 | 1650 | 0.207 | 1650 | 0.207 | 0.968 | 1.26 | -0.00504
LFAllSpcPGEMBTExCZ01 | Com-Iltg-dWatt-LF_OSspc | PGE | MBT | Ex | CZ01 | 3.0298 | 0.00072702 | 0 | 3.2698 | 0.00086702 | -0.0037802 | 3.0298 | 0.00072702 | 0 | 3.2698 | 0.00086702 | -0.0037802 |  | LF | AllSpc | 3030 | 0.727 | 3030 | 0.727 | 1.08 | 1.19 | -0.0012477 | 3030 | 0.727 | 3030 | 0.727 | 1.08 | 1.19 | -0.00125
LFAllSpcPGEMBTExCZ02 | Com-Iltg-dWatt-LF_OSspc | PGE | MBT | Ex | CZ02 | 3.0299 | 0.00072701 | 0 | 3.3603 | 0.000867 | -0.0018999 | 3.0299 | 0.00072701 | 0 | 3.3603 | 0.000867 | -0.0018999 |  | LF | AllSpc | 3030 | 0.727 | 3030 | 0.727 | 1.11 | 1.19 | -0.00062705 | 3030 | 0.727 | 3030 | 0.727 | 1.11 | 1.19 | -0.000627
LFAllSpcPGEMBTExCZ03 | Com-Iltg-dWatt-LF_OSspc | PGE | MBT | Ex | CZ03 | 3.0299 | 0.00072701 | 0 | 3.3901 | 0.000867 | -0.0016599 | 3.0299 | 0.00072701 | 0 | 3.3901 | 0.000867 | -0.0016599 |  | LF | AllSpc | 3030 | 0.727 | 3030 | 0.727 | 1.12 | 1.19 | -0.00054784 | 3030 | 0.727 | 3030 | 0.727 | 1.12 | 1.19 | -0.000548
LFAllSpcPGEMBTExCZ04 | Com-Iltg-dWatt-LF_OSspc | PGE | MBT | Ex | CZ04 | 3.0296 | 0.00072704 | 0 | 3.3896 | 0.00087804 | -0.0012796 | 3.0296 | 0.00072704 | 0 | 3.3896 | 0.00087804 | -0.0012796 |  | LF | AllSpc | 3030 | 0.727 | 3030 | 0.727 | 1.12 | 1.21 | -0.00042236 | 3030 | 0.727 | 3030 | 0.727 | 1.12 | 1.21 | -0.000422
LFAllSpcPGEMBTExCZ05 | Com-Iltg-dWatt-LF_OSspc | PGE | MBT | Ex | CZ05 | 3.0296 | 0.00072704 | 0 | 3.36 | 0.00086704 | -0.00125 | 3.0296 | 0.00072704 | 0 | 3.36 | 0.00086704 | -0.00125 |  | LF | AllSpc | 3030 | 0.727 | 3030 | 0.727 | 1.11 | 1.19 | -0.0004126 | 3030 | 0.727 | 3030 | 0.727 | 1.11 | 1.19 | -0.000413
LFAllSpcPGEMBTExCZ11 | Com-Iltg-dWatt-LF_OSspc | PGE | MBT | Ex | CZ11 | 3.0293 | 0.00072707 | 0 | 3.3819 | 0.00088307 | -0.0019926 | 3.0293 | 0.00072707 | 0 | 3.3819 | 0.00088307 | -0.0019926 |  | LF | AllSpc | 3030 | 0.727 | 3030 | 0.727 | 1.12 | 1.21 | -0.00065776 | 3030 | 0.727 | 3030 | 0.727 | 1.12 | 1.21 | -0.000658
LFAllSpcPGEMBTExCZ12 | Com-Iltg-dWatt-LF_OSspc | PGE | MBT | Ex | CZ12 | 3.0295 | 0.00072705 | 0 | 3.3695 | 0.000861 | -0.0019927 | 3.0295 | 0.00072705 | 0 | 3.3695 | 0.000861 | -0.0019927 |  | LF | AllSpc | 3030 | 0.727 | 3030 | 0.727 | 1.11 | 1.18 | -0.00065776 | 3030 | 0.727 | 3030 | 0.727 | 1.11 | 1.18 | -0.000658
LFAllSpcPGEMBTExCZ13 | Com-Iltg-dWatt-LF_OSspc | PGE | MBT | Ex | CZ13 | 3.0294 | 0.00072706 | 0 | 3.392 | 0.00086106 | -0.00178 | 3.0294 | 0.00072706 | 0 | 3.392 | 0.00086106 | -0.00178 |  | LF | AllSpc | 3030 | 0.727 | 3030 | 0.727 | 1.12 | 1.18 | -0.00058758 | 3030 | 0.727 | 3030 | 0.727 | 1.12 | 1.18 | -0.000588
LFAllSpcPGEMBTExCZ16 | Com-Iltg-dWatt-LF_OSspc | PGE | MBT | Ex | CZ16 | 3.0294 | 0.00072706 | 0 | 3.2394 | 0.000845 | -0.0084712 | 3.0294 | 0.00072706 | 0 | 3.2394 | 0.000845 | -0.0084712 |  | LF | AllSpc | 3030 | 0.727 | 3030 | 0.727 | 1.07 | 1.16 | -0.0027963 | 3030 | 0.727 | 3030 | 0.727 | 1.07 | 1.16 | -0.0028
LFAllSpcPGEMBTExIOU | Com-Iltg-dWatt-LF_OSspc | PGE | MBT | Ex | IOU | 3.0296 | 0.00072704 | 0 | 3.3807 | 0.0008677 | -0.0017815 | 3.0296 | 0.00072704 | 0 | 3.3807 | 0.0008677 | -0.0017815 |  | LF | AllSpc | 3030 | 0.727 | 3030 | 0.727 | 1.12 | 1.19 | -0.00058801 | 3030 | 0.727 | 3030 | 0.727 | 1.12 | 1.19 | -0.000588
LFAllSpcPGEMBTNewCZ01 | Com-Iltg-dWatt-LF_OSspc | PGE | MBT | New | CZ01 | 3.02 | 0.000728 | 0 | 3.1 | 0.000834 | -0.00326 | 3.02 | 0.000728 | 0 | 3.1 | 0.000834 | -0.00326 |  | LF | AllSpc | 3020 | 0.728 | 3020 | 0.728 | 1.03 | 1.15 | -0.0010795 | 3020 | 0.728 | 3020 | 0.728 | 1.03 | 1.15 | -0.00108
LFAllSpcPGEMBTNewCZ02 | Com-Iltg-dWatt-LF_OSspc | PGE | MBT | New | CZ02 | 3.02 | 0.000728 | 0 | 3.23 | 0.000901 | -0.00164 | 3.02 | 0.000728 | 0 | 3.23 | 0.000901 | -0.00164 |  | LF | AllSpc | 3020 | 0.728 | 3020 | 0.728 | 1.07 | 1.24 | -0.00054305 | 3020 | 0.728 | 3020 | 0.728 | 1.07 | 1.24 | -0.000543
LFAllSpcPGEMBTNewCZ03 | Com-Iltg-dWatt-LF_OSspc | PGE | MBT | New | CZ03 | 3.02 | 0.000728 | 0 | 3.2 | 0.000873 | -0.00153 | 3.02 | 0.000728 | 0 | 3.2 | 0.000873 | -0.00153 |  | LF | AllSpc | 3020 | 0.728 | 3020 | 0.728 | 1.06 | 1.2 | -0.00050662 | 3020 | 0.728 | 3020 | 0.728 | 1.06 | 1.2 | -0.000507
LFAllSpcPGEMBTNewCZ04 | Com-Iltg-dWatt-LF_OSspc | PGE | MBT | New | CZ04 | 3.02 | 0.000728 | 0 | 3.26 | 0.000893 | -0.00123 | 3.02 | 0.000728 | 0 | 3.26 | 0.000893 | -0.00123 |  | LF | AllSpc | 3020 | 0.728 | 3020 | 0.728 | 1.08 | 1.23 | -0.00040728 | 3020 | 0.728 | 3020 | 0.728 | 1.08 | 1.23 | -0.000407
LFAllSpcPGEMBTNewCZ05 | Com-Iltg-dWatt-LF_OSspc | PGE | MBT | New | CZ05 | 3.02 | 0.000728 | 0 | 3.22 | 0.000867 | -0.000782 | 3.02 | 0.000728 | 0 | 3.22 | 0.000867 | -0.000782 |  | LF | AllSpc | 3020 | 0.728 | 3020 | 0.728 | 1.07 | 1.19 | -0.00025894 | 3020 | 0.728 | 3020 | 0.728 | 1.07 | 1.19 | -0.000259
LFAllSpcPGEMBTNewCZ11 | Com-Iltg-dWatt-LF_OSspc | PGE | MBT | New | CZ11 | 3.02 | 0.000728 | 0 | 3.29 | 0.00091 | -0.00142 | 3.02 | 0.000728 | 0 | 3.29 | 0.00091 | -0.00142 |  | LF | AllSpc | 3020 | 0.728 | 3020 | 0.728 | 1.09 | 1.25 | -0.0004702 | 3020 | 0.728 | 3020 | 0.728 | 1.09 | 1.25 | -0.00047
LFAllSpcPGEMBTNewCZ12 | Com-Iltg-dWatt-LF_OSspc | PGE | MBT | New | CZ12 | 3.02 | 0.000728 | 0 | 3.27 | 0.000902 | -0.00147 | 3.02 | 0.000728 | 0 | 3.27 | 0.000902 | -0.00147 |  | LF | AllSpc | 3020 | 0.728 | 3020 | 0.728 | 1.08 | 1.24 | -0.00048675 | 3020 | 0.728 | 3020 | 0.728 | 1.08 | 1.24 | -0.000487
LFAllSpcPGEMBTNewCZ13 | Com-Iltg-dWatt-LF_OSspc | PGE | MBT | New | CZ13 | 3.02 | 0.000728 | 0 | 3.3 | 0.000901 | -0.00136 | 3.02 | 0.000728 | 0 | 3.3 | 0.000901 | -0.00136 |  | LF | AllSpc | 3020 | 0.728 | 3020 | 0.728 | 1.09 | 1.24 | -0.00045033 | 3020 | 0.728 | 3020 | 0.728 | 1.09 | 1.24 | -0.00045
LFAllSpcPGEMBTNewCZ16 | Com-Iltg-dWatt-LF_OSspc | PGE | MBT | New | CZ16 | 3.02 | 0.000728 | 0 | 3.16 | 0.000869 | -0.00576 | 3.02 | 0.000728 | 0 | 3.16 | 0.000869 | -0.00576 |  | LF | AllSpc | 3020 | 0.728 | 3020 | 0.728 | 1.05 | 1.19 | -0.0019073 | 3020 | 0.728 | 3020 | 0.728 | 1.05 | 1.19 | -0.00191
LFAllSpcPGEMBTNewIOU | Com-Iltg-dWatt-LF_OSspc | PGE | MBT | New | IOU | 3.02 | 0.000728 | 0 | 3.252 | 0.00089215 | -0.0014879 | 3.02 | 0.000728 | 0 | 3.252 | 0.00089215 | -0.0014879 |  | LF | AllSpc | 3020 | 0.728 | 3020 | 0.728 | 1.08 | 1.23 | -0.00049268 | 3020 | 0.728 | 3020 | 0.728 | 1.08 | 1.23 | -0.000493
LFAllSpcPGEMLIExCZ01 | Com-Iltg-dWatt-LF_OSspc | PGE | MLI | Ex | CZ01 | 2.83 | 0.000784 | 0 | 2.74 | 0.00090795 | -0.034205 | 2.83 | 0.000784 | 0 | 2.74 | 0.00090795 | -0.034205 |  | LF | AllSpc | 2830 | 0.784 | 2830 | 0.784 | 0.968 | 1.16 | -0.012087 | 2830 | 0.784 | 2830 | 0.784 | 0.968 | 1.16 | -0.0121
LFAllSpcPGEMLIExCZ02 | Com-Iltg-dWatt-LF_OSspc | PGE | MLI | Ex | CZ02 | 2.83 | 0.000784 | 0 | 2.94 | 0.000918 | -0.0175 | 2.83 | 0.000784 | 0 | 2.94 | 0.000918 | -0.0175 |  | LF | AllSpc | 2830 | 0.784 | 2830 | 0.784 | 1.04 | 1.17 | -0.0061837 | 2830 | 0.784 | 2830 | 0.784 | 1.04 | 1.17 | -0.00618
LFAllSpcPGEMLIExCZ03 | Com-Iltg-dWatt-LF_OSspc | PGE | MLI | Ex | CZ03 | 2.83 | 0.000784 | 0 | 2.93 | 0.00091897 | -0.0164 | 2.83 | 0.000784 | 0 | 2.93 | 0.00091897 | -0.0164 |  | LF | AllSpc | 2830 | 0.784 | 2830 | 0.784 | 1.04 | 1.17 | -0.0057951 | 2830 | 0.784 | 2830 | 0.784 | 1.04 | 1.17 | -0.0058
LFAllSpcPGEMLIExCZ04 | Com-Iltg-dWatt-LF_OSspc | PGE | MLI | Ex | CZ04 | 2.83 | 0.000784 | 0 | 2.97 | 0.000914 | -0.0133 | 2.83 | 0.000784 | 0 | 2.97 | 0.000914 | -0.0133 |  | LF | AllSpc | 2830 | 0.784 | 2830 | 0.784 | 1.05 | 1.17 | -0.0046996 | 2830 | 0.784 | 2830 | 0.784 | 1.05 | 1.17 | -0.0047
LFAllSpcPGEMLIExCZ05 | Com-Iltg-dWatt-LF_OSspc | PGE | MLI | Ex | CZ05 | 2.83 | 0.000784 | 0 | 2.92 | 0.000915 | -0.015204 | 2.83 | 0.000784 | 0 | 2.92 | 0.000915 | -0.015204 |  | LF | AllSpc | 2830 | 0.784 | 2830 | 0.784 | 1.03 | 1.17 | -0.0053726 | 2830 | 0.784 | 2830 | 0.784 | 1.03 | 1.17 | -0.00537
LFAllSpcPGEMLIExCZ11 | Com-Iltg-dWatt-LF_OSspc | PGE | MLI | Ex | CZ11 | 2.83 | 0.000784 | 0 | 2.95 | 0.000917 | -0.0175 | 2.83 | 0.000784 | 0 | 2.95 | 0.000917 | -0.0175 |  | LF | AllSpc | 2830 | 0.784 | 2830 | 0.784 | 1.04 | 1.17 | -0.0061837 | 2830 | 0.784 | 2830 | 0.784 | 1.04 | 1.17 | -0.00618
LFAllSpcPGEMLIExCZ12 | Com-Iltg-dWatt-LF_OSspc | PGE | MLI | Ex | CZ12 | 2.83 | 0.000784 | 0 | 2.95 | 0.000922 | -0.017205 | 2.83 | 0.000784 | 0 | 2.95 | 0.000922 | -0.017205 |  | LF | AllSpc | 2830 | 0.784 | 2830 | 0.784 | 1.04 | 1.18 | -0.0060796 | 2830 | 0.784 | 2830 | 0.784 | 1.04 | 1.18 | -0.00608
LFAllSpcPGEMLIExCZ13 | Com-Iltg-dWatt-LF_OSspc | PGE | MLI | Ex | CZ13 | 2.83 | 0.000784 | 0 | 2.98 | 0.000908 | -0.0154 | 2.83 | 0.000784 | 0 | 2.98 | 0.000908 | -0.0154 |  | LF | AllSpc | 2830 | 0.784 | 2830 | 0.784 | 1.05 | 1.16 | -0.0054417 | 2830 | 0.784 | 2830 | 0.784 | 1.05 | 1.16 | -0.00544
LFAllSpcPGEMLIExCZ16 | Com-Iltg-dWatt-LF_OSspc | PGE | MLI | Ex | CZ16 | 2.83 | 0.000784 | 0 | 2.78 | 0.000899 | -0.0348 | 2.83 | 0.000784 | 0 | 2.78 | 0.000899 | -0.0348 |  | LF | AllSpc | 2830 | 0.784 | 2830 | 0.784 | 0.982 | 1.15 | -0.012297 | 2830 | 0.784 | 2830 | 0.784 | 0.982 | 1.15 | -0.0123
LFAllSpcPGEMLIExIOU | Com-Iltg-dWatt-LF_OSspc | PGE | MLI | Ex | IOU | 2.83 | 0.000784 | 0 | 2.9458 | 0.00091676 | -0.016292 | 2.83 | 0.000784 | 0 | 2.9458 | 0.00091676 | -0.016292 |  | LF | AllSpc | 2830 | 0.784 | 2830 | 0.784 | 1.04 | 1.17 | -0.005757 | 2830 | 0.784 | 2830 | 0.784 | 1.04 | 1.17 | -0.00576
LFAllSpcPGEMLINewCZ01 | Com-Iltg-dWatt-LF_OSspc | PGE | MLI | New | CZ01 | 2.83 | 0.000784 | 0 | 2.7 | 0.000847 | -0.0374 | 2.83 | 0.000784 | 0 | 2.7 | 0.000847 | -0.0374 |  | LF | AllSpc | 2830 | 0.784 | 2830 | 0.784 | 0.954 | 1.08 | -0.013216 | 2830 | 0.784 | 2830 | 0.784 | 0.954 | 1.08 | -0.0132
LFAllSpcPGEMLINewCZ02 | Com-Iltg-dWatt-LF_OSspc | PGE | MLI | New | CZ02 | 2.83 | 0.000784 | 0 | 2.91 | 0.00094 | -0.0204 | 2.83 | 0.000784 | 0 | 2.91 | 0.00094 | -0.0204 |  | LF | AllSpc | 2830 | 0.784 | 2830 | 0.784 | 1.03 | 1.2 | -0.0072085 | 2830 | 0.784 | 2830 | 0.784 | 1.03 | 1.2 | -0.00721
LFAllSpcPGEMLINewCZ03 | Com-Iltg-dWatt-LF_OSspc | PGE | MLI | New | CZ03 | 2.83 | 0.000784 | 0 | 2.83 | 0.000911 | -0.0189 | 2.83 | 0.000784 | 0 | 2.83 | 0.000911 | -0.0189 |  | LF | AllSpc | 2830 | 0.784 | 2830 | 0.784 | 1 | 1.16 | -0.0066784 | 2830 | 0.784 | 2830 | 0.784 | 1 | 1.16 | -0.00668
LFAllSpcPGEMLINewCZ04 | Com-Iltg-dWatt-LF_OSspc | PGE | MLI | New | CZ04 | 2.83 | 0.000784 | 0 | 2.94 | 0.000929 | -0.0155 | 2.83 | 0.000784 | 0 | 2.94 | 0.000929 | -0.0155 |  | LF | AllSpc | 2830 | 0.784 | 2830 | 0.784 | 1.04 | 1.18 | -0.005477 | 2830 | 0.784 | 2830 | 0.784 | 1.04 | 1.18 | -0.00548
LFAllSpcPGEMLINewCZ05 | Com-Iltg-dWatt-LF_OSspc | PGE | MLI | New | CZ05 | 2.83 | 0.000784 | 0 | 2.83 | 0.000901 | -0.0186 | 2.83 | 0.000784 | 0 | 2.83 | 0.000901 | -0.0186 |  | LF | AllSpc | 2830 | 0.784 | 2830 | 0.784 | 1 | 1.15 | -0.0065724 | 2830 | 0.784 | 2830 | 0.784 | 1 | 1.15 | -0.00657
LFAllSpcPGEMLINewCZ11 | Com-Iltg-dWatt-LF_OSspc | PGE | MLI | New | CZ11 | 2.83 | 0.000784 | 0 | 3.01 | 0.000972 | -0.0168 | 2.83 | 0.000784 | 0 | 3.01 | 0.000972 | -0.0168 |  | LF | AllSpc | 2830 | 0.784 | 2830 | 0.784 | 1.06 | 1.24 | -0.0059364 | 2830 | 0.784 | 2830 | 0.784 | 1.06 | 1.24 | -0.00594
LFAllSpcPGEMLINewCZ12 | Com-Iltg-dWatt-LF_OSspc | PGE | MLI | New | CZ12 | 2.83 | 0.000784 | 0 | 2.98 | 0.000964 | -0.019 | 2.83 | 0.000784 | 0 | 2.98 | 0.000964 | -0.019 |  | LF | AllSpc | 2830 | 0.784 | 2830 | 0.784 | 1.05 | 1.23 | -0.0067138 | 2830 | 0.784 | 2830 | 0.784 | 1.05 | 1.23 | -0.00671
LFAllSpcPGEMLINewCZ13 | Com-Iltg-dWatt-LF_OSspc | PGE | MLI | New | CZ13 | 2.83 | 0.000784 | 0 | 3.03 | 0.000966 | -0.0157 | 2.83 | 0.000784 | 0 | 3.03 | 0.000966 | -0.0157 |  | LF | AllSpc | 2830 | 0.784 | 2830 | 0.784 | 1.07 | 1.23 | -0.0055477 | 2830 | 0.784 | 2830 | 0.784 | 1.07 | 1.23 | -0.00555
LFAllSpcPGEMLINewCZ16 | Com-Iltg-dWatt-LF_OSspc | PGE | MLI | New | CZ16 | 2.83 | 0.000784 | 0 | 2.81 | 0.000911 | -0.0343 | 2.83 | 0.000784 | 0 | 2.81 | 0.000911 | -0.0343 |  | LF | AllSpc | 2830 | 0.784 | 2830 | 0.784 | 0.993 | 1.16 | -0.01212 | 2830 | 0.784 | 2830 | 0.784 | 0.993 | 1.16 | -0.0121
LFAllSpcPGEMLINewIOU | Com-Iltg-dWatt-LF_OSspc | PGE | MLI | New | IOU | 2.83 | 0.000784 | 0 | 2.9362 | 0.00094168 | -0.018052 | 2.83 | 0.000784 | 0 | 2.9362 | 0.00094168 | -0.018052 |  | LF | AllSpc | 2830 | 0.784 | 2830 | 0.784 | 1.04 | 1.2 | -0.0063788 | 2830 | 0.784 | 2830 | 0.784 | 1.04 | 1.2 | -0.00638
LFAllSpcPGEMtlExCZ01 | Com-Iltg-dWatt-LF_OSspc | PGE | Mtl | Ex | CZ01 | 1.35 | 0.000148 | 0 | 1.28 | 0.000176 | -0.0134 | 1.35 | 0.000148 | 0 | 1.28 | 0.000176 | -0.0134 |  | LF | AllSpc | 1350 | 0.148 | 1350 | 0.148 | 0.948 | 1.19 | -0.0099259 | 1350 | 0.148 | 1350 | 0.148 | 0.948 | 1.19 | -0.00993
LFAllSpcPGEMtlExCZ02 | Com-Iltg-dWatt-LF_OSspc | PGE | Mtl | Ex | CZ02 | 1.35 | 0.000148 | 0 | 1.37 | 0.000184 | -0.0088306 | 1.35 | 0.000148 | 0 | 1.37 | 0.000184 | -0.0088306 |  | LF | AllSpc | 1350 | 0.148 | 1350 | 0.148 | 1.01 | 1.24 | -0.0065412 | 1350 | 0.148 | 1350 | 0.148 | 1.01 | 1.24 | -0.00654
LFAllSpcPGEMtlExCZ03 | Com-Iltg-dWatt-LF_OSspc | PGE | Mtl | Ex | CZ03 | 1.35 | 0.000148 | 0 | 1.39 | 0.00018 | -0.00862 | 1.35 | 0.000148 | 0 | 1.39 | 0.00018 | -0.00862 |  | LF | AllSpc | 1350 | 0.148 | 1350 | 0.148 | 1.03 | 1.22 | -0.0063852 | 1350 | 0.148 | 1350 | 0.148 | 1.03 | 1.22 | -0.00639
LFAllSpcPGEMtlExCZ04 | Com-Iltg-dWatt-LF_OSspc | PGE | Mtl | Ex | CZ04 | 1.35 | 0.000148 | 0 | 1.41 | 0.000182 | -0.0071906 | 1.35 | 0.000148 | 0 | 1.41 | 0.000182 | -0.0071906 |  | LF | AllSpc | 1350 | 0.148 | 1350 | 0.148 | 1.04 | 1.23 | -0.0053264 | 1350 | 0.148 | 1350 | 0.148 | 1.04 | 1.23 | -0.00533
LFAllSpcPGEMtlExCZ05 | Com-Iltg-dWatt-LF_OSspc | PGE | Mtl | Ex | CZ05 | 1.35 | 0.000148 | 0 | 1.37 | 0.000178 | -0.0092 | 1.35 | 0.000148 | 0 | 1.37 | 0.000178 | -0.0092 |  | LF | AllSpc | 1350 | 0.148 | 1350 | 0.148 | 1.01 | 1.2 | -0.0068148 | 1350 | 0.148 | 1350 | 0.148 | 1.01 | 1.2 | -0.00681
LFAllSpcPGEMtlExCZ11 | Com-Iltg-dWatt-LF_OSspc | PGE | Mtl | Ex | CZ11 | 1.35 | 0.000148 | 0 | 1.42 | 0.000185 | -0.00745 | 1.35 | 0.000148 | 0 | 1.42 | 0.000185 | -0.00745 |  | LF | AllSpc | 1350 | 0.148 | 1350 | 0.148 | 1.05 | 1.25 | -0.0055185 | 1350 | 0.148 | 1350 | 0.148 | 1.05 | 1.25 | -0.00552
LFAllSpcPGEMtlExCZ12 | Com-Iltg-dWatt-LF_OSspc | PGE | Mtl | Ex | CZ12 | 1.35 | 0.000148 | 0 | 1.41 | 0.000184 | -0.00784 | 1.35 | 0.000148 | 0 | 1.41 | 0.000184 | -0.00784 |  | LF | AllSpc | 1350 | 0.148 | 1350 | 0.148 | 1.04 | 1.24 | -0.0058074 | 1350 | 0.148 | 1350 | 0.148 | 1.04 | 1.24 | -0.00581
LFAllSpcPGEMtlExCZ13 | Com-Iltg-dWatt-LF_OSspc | PGE | Mtl | Ex | CZ13 | 1.35 | 0.000148 | 0 | 1.44 | 0.000184 | -0.00695 | 1.35 | 0.000148 | 0 | 1.44 | 0.000184 | -0.00695 |  | LF | AllSpc | 1350 | 0.148 | 1350 | 0.148 | 1.07 | 1.24 | -0.0051481 | 1350 | 0.148 | 1350 | 0.148 | 1.07 | 1.24 | -0.00515
LFAllSpcPGEMtlExCZ16 | Com-Iltg-dWatt-LF_OSspc | PGE | Mtl | Ex | CZ16 | 1.35 | 0.000148 | 0 | 1.29 | 0.000178 | -0.0116 | 1.35 | 0.000148 | 0 | 1.29 | 0.000178 | -0.0116 |  | LF | AllSpc | 1350 | 0.148 | 1350 | 0.148 | 0.956 | 1.2 | -0.0085926 | 1350 | 0.148 | 1350 | 0.148 | 0.956 | 1.2 | -0.00859
LFAllSpcPGEMtlExIOU | Com-Iltg-dWatt-LF_OSspc | PGE | Mtl | Ex | IOU | 1.35 | 0.000148 | 0 | 1.3951 | 0.00018141 | -0.0082933 | 1.35 | 0.000148 | 0 | 1.3951 | 0.00018141 | -0.0082933 |  | LF | AllSpc | 1350 | 0.148 | 1350 | 0.148 | 1.03 | 1.23 | -0.0061432 | 1350 | 0.148 | 1350 | 0.148 | 1.03 | 1.23 | -0.00614
LFAllSpcPGEMtlNewCZ01 | Com-Iltg-dWatt-LF_OSspc | PGE | Mtl | New | CZ01 | 1.35 | 0.000148 | 0 | 1.22 | 0.000176 | -0.0174 | 1.35 | 0.000148 | 0 | 1.22 | 0.000176 | -0.0174 |  | LF | AllSpc | 1350 | 0.148 | 1350 | 0.148 | 0.904 | 1.19 | -0.012889 | 1350 | 0.148 | 1350 | 0.148 | 0.904 | 1.19 | -0.0129
LFAllSpcPGEMtlNewCZ02 | Com-Iltg-dWatt-LF_OSspc | PGE | Mtl | New | CZ02 | 1.35 | 0.000148 | 0 | 1.34 | 0.000187 | -0.0118 | 1.35 | 0.000148 | 0 | 1.34 | 0.000187 | -0.0118 |  | LF | AllSpc | 1350 | 0.148 | 1350 | 0.148 | 0.993 | 1.26 | -0.0087407 | 1350 | 0.148 | 1350 | 0.148 | 0.993 | 1.26 | -0.00874
LFAllSpcPGEMtlNewCZ03 | Com-Iltg-dWatt-LF_OSspc | PGE | Mtl | New | CZ03 | 1.35 | 0.000148 | 0 | 1.35 | 0.000182 | -0.0112 | 1.35 | 0.000148 | 0 | 1.35 | 0.000182 | -0.0112 |  | LF | AllSpc | 1350 | 0.148 | 1350 | 0.148 | 1 | 1.23 | -0.0082963 | 1350 | 0.148 | 1350 | 0.148 | 1 | 1.23 | -0.0083
LFAllSpcPGEMtlNewCZ04 | Com-Iltg-dWatt-LF_OSspc | PGE | Mtl | New | CZ04 | 1.35 | 0.000148 | 0 | 1.39 | 0.000185 | -0.00945 | 1.35 | 0.000148 | 0 | 1.39 | 0.000185 | -0.00945 |  | LF | AllSpc | 1350 | 0.148 | 1350 | 0.148 | 1.03 | 1.25 | -0.007 | 1350 | 0.148 | 1350 | 0.148 | 1.03 | 1.25 | -0.007
LFAllSpcPGEMtlNewCZ05 | Com-Iltg-dWatt-LF_OSspc | PGE | Mtl | New | CZ05 | 1.35 | 0.000148 | 0 | 1.32 | 0.00018 | -0.0127 | 1.35 | 0.000148 | 0 | 1.32 | 0.00018 | -0.0127 |  | LF | AllSpc | 1350 | 0.148 | 1350 | 0.148 | 0.978 | 1.22 | -0.0094074 | 1350 | 0.148 | 1350 | 0.148 | 0.978 | 1.22 | -0.00941
LFAllSpcPGEMtlNewCZ11 | Com-Iltg-dWatt-LF_OSspc | PGE | Mtl | New | CZ11 | 1.35 | 0.000148 | 0 | 1.4 | 0.000187 | -0.00935 | 1.35 | 0.000148 | 0 | 1.4 | 0.000187 | -0.00935 |  | LF | AllSpc | 1350 | 0.148 | 1350 | 0.148 | 1.04 | 1.26 | -0.0069259 | 1350 | 0.148 | 1350 | 0.148 | 1.04 | 1.26 | -0.00693
LFAllSpcPGEMtlNewCZ12 | Com-Iltg-dWatt-LF_OSspc | PGE | Mtl | New | CZ12 | 1.35 | 0.000148 | 0 | 1.39 | 0.000187 | -0.00976 | 1.35 | 0.000148 | 0 | 1.39 | 0.000187 | -0.00976 |  | LF | AllSpc | 1350 | 0.148 | 1350 | 0.148 | 1.03 | 1.26 | -0.0072296 | 1350 | 0.148 | 1350 | 0.148 | 1.03 | 1.26 | -0.00723
LFAllSpcPGEMtlNewCZ13 | Com-Iltg-dWatt-LF_OSspc | PGE | Mtl | New | CZ13 | 1.35 | 0.000148 | 0 | 1.41 | 0.000187 | -0.00881 | 1.35 | 0.000148 | 0 | 1.41 | 0.000187 | -0.00881 |  | LF | AllSpc | 1350 | 0.148 | 1350 | 0.148 | 1.04 | 1.26 | -0.0065259 | 1350 | 0.148 | 1350 | 0.148 | 1.04 | 1.26 | -0.00653
LFAllSpcPGEMtlNewCZ16 | Com-Iltg-dWatt-LF_OSspc | PGE | Mtl | New | CZ16 | 1.35 | 0.000148 | 0 | 1.25 | 0.00018 | -0.0137 | 1.35 | 0.000148 | 0 | 1.25 | 0.00018 | -0.0137 |  | LF | AllSpc | 1350 | 0.148 | 1350 | 0.148 | 0.926 | 1.22 | -0.010148 | 1350 | 0.148 | 1350 | 0.148 | 0.926 | 1.22 | -0.0101
LFAllSpcPGEMtlNewIOU | Com-Iltg-dWatt-LF_OSspc | PGE | Mtl | New | IOU | 1.35 | 0.000148 | 0 | 1.3674 | 0.00018452 | -0.010546 | 1.35 | 0.000148 | 0 | 1.3674 | 0.00018452 | -0.010546 |  | LF | AllSpc | 1350 | 0.148 | 1350 | 0.148 | 1.01 | 1.25 | -0.0078122 | 1350 | 0.148 | 1350 | 0.148 | 1.01 | 1.25 | -0.00781
LFAllSpcPGENrsExCZ01 | Com-Iltg-dWatt-LF_OSspc | PGE | Nrs | Ex | CZ01 | 3.6004 | 0.00058009 | 0 | 3.5004 | 0.00066204 | -0.078809 | 3.6004 | 0.00058009 | 0 | 3.5004 | 0.00066204 | -0.078809 |  | LF | AllSpc | 3600 | 0.58 | 3600 | 0.58 | 0.972 | 1.14 | -0.021889 | 3600 | 0.58 | 3600 | 0.58 | 0.972 | 1.14 | -0.0219
LFAllSpcPGENrsExCZ02 | Com-Iltg-dWatt-LF_OSspc | PGE | Nrs | Ex | CZ02 | 3.6005 | 0.0005801 | 0 | 3.7105 | 0.0007341 | -0.056905 | 3.6005 | 0.0005801 | 0 | 3.7105 | 0.0007341 | -0.056905 |  | LF | AllSpc | 3600 | 0.58 | 3600 | 0.58 | 1.03 | 1.27 | -0.015805 | 3600 | 0.58 | 3600 | 0.58 | 1.03 | 1.27 | -0.0158
LFAllSpcPGENrsExCZ03 | Com-Iltg-dWatt-LF_OSspc | PGE | Nrs | Ex | CZ03 | 3.6005 | 0.00058009 | 0 | 3.6705 | 0.00070609 | -0.058305 | 3.6005 | 0.00058009 | 0 | 3.6705 | 0.00070609 | -0.058305 |  | LF | AllSpc | 3600 | 0.58 | 3600 | 0.58 | 1.02 | 1.22 | -0.016194 | 3600 | 0.58 | 3600 | 0.58 | 1.02 | 1.22 | -0.0162
LFAllSpcPGENrsExCZ04 | Com-Iltg-dWatt-LF_OSspc | PGE | Nrs | Ex | CZ04 | 3.6005 | 0.0005801 | 0 | 3.77 | 0.00072405 | -0.049005 | 3.6005 | 0.0005801 | 0 | 3.77 | 0.00072405 | -0.049005 |  | LF | AllSpc | 3600 | 0.58 | 3600 | 0.58 | 1.05 | 1.25 | -0.013611 | 3600 | 0.58 | 3600 | 0.58 | 1.05 | 1.25 | -0.0136
LFAllSpcPGENrsExCZ05 | Com-Iltg-dWatt-LF_OSspc | PGE | Nrs | Ex | CZ05 | 3.6005 | 0.0005801 | 0 | 3.6405 | 0.0006861 | -0.05901 | 3.6005 | 0.0005801 | 0 | 3.6405 | 0.0006861 | -0.05901 |  | LF | AllSpc | 3600 | 0.58 | 3600 | 0.58 | 1.01 | 1.18 | -0.016389 | 3600 | 0.58 | 3600 | 0.58 | 1.01 | 1.18 | -0.0164
LFAllSpcPGENrsExCZ11 | Com-Iltg-dWatt-LF_OSspc | PGE | Nrs | Ex | CZ11 | 3.6006 | 0.00058013 | 0 | 3.8206 | 0.00074106 | -0.047206 | 3.6006 | 0.00058013 | 0 | 3.8206 | 0.00074106 | -0.047206 |  | LF | AllSpc | 3600 | 0.58 | 3600 | 0.58 | 1.06 | 1.28 | -0.013111 | 3600 | 0.58 | 3600 | 0.58 | 1.06 | 1.28 | -0.0131
LFAllSpcPGENrsExCZ12 | Com-Iltg-dWatt-LF_OSspc | PGE | Nrs | Ex | CZ12 | 3.6006 | 0.00058013 | 0 | 3.7806 | 0.00074113 | -0.049706 | 3.6006 | 0.00058013 | 0 | 3.7806 | 0.00074113 | -0.049706 |  | LF | AllSpc | 3600 | 0.58 | 3600 | 0.58 | 1.05 | 1.28 | -0.013805 | 3600 | 0.58 | 3600 | 0.58 | 1.05 | 1.28 | -0.0138
LFAllSpcPGENrsExCZ13 | Com-Iltg-dWatt-LF_OSspc | PGE | Nrs | Ex | CZ13 | 3.6006 | 0.00058013 | 0 | 3.8406 | 0.00074013 | -0.0454 | 3.6006 | 0.00058013 | 0 | 3.8406 | 0.00074013 | -0.0454 |  | LF | AllSpc | 3600 | 0.58 | 3600 | 0.58 | 1.07 | 1.28 | -0.012609 | 3600 | 0.58 | 3600 | 0.58 | 1.07 | 1.28 | -0.0126
LFAllSpcPGENrsExCZ16 | Com-Iltg-dWatt-LF_OSspc | PGE | Nrs | Ex | CZ16 | 3.6005 | 0.00058011 | 0 | 3.6 | 0.00070211 | -0.068011 | 3.6005 | 0.00058011 | 0 | 3.6 | 0.00070211 | -0.068011 |  | LF | AllSpc | 3600 | 0.58 | 3600 | 0.58 | 1 | 1.21 | -0.018889 | 3600 | 0.58 | 3600 | 0.58 | 1 | 1.21 | -0.0189
LFAllSpcPGENrsExIOU | Com-Iltg-dWatt-LF_OSspc | PGE | Nrs | Ex | IOU | 3.6005 | 0.00058011 | 0 | 3.7468 | 0.00072581 | -0.052486 | 3.6005 | 0.00058011 | 0 | 3.7468 | 0.00072581 | -0.052486 |  | LF | AllSpc | 3600 | 0.58 | 3600 | 0.58 | 1.04 | 1.25 | -0.014577 | 3600 | 0.58 | 3600 | 0.58 | 1.04 | 1.25 | -0.0146
LFAllSpcPGENrsNewCZ01 | Com-Iltg-dWatt-LF_OSspc | PGE | Nrs | New | CZ01 | 3.61 | 0.000582 | 0 | 3.39 | 0.000632 | -0.0884 | 3.61 | 0.000582 | 0 | 3.39 | 0.000632 | -0.0884 |  | LF | AllSpc | 3610 | 0.582 | 3610 | 0.582 | 0.939 | 1.09 | -0.024488 | 3610 | 0.582 | 3610 | 0.582 | 0.939 | 1.09 | -0.0245
LFAllSpcPGENrsNewCZ02 | Com-Iltg-dWatt-LF_OSspc | PGE | Nrs | New | CZ02 | 3.61 | 0.000582 | 0 | 3.61 | 0.000743 | -0.0631 | 3.61 | 0.000582 | 0 | 3.61 | 0.000743 | -0.0631 |  | LF | AllSpc | 3610 | 0.582 | 3610 | 0.582 | 1 | 1.28 | -0.017479 | 3610 | 0.582 | 3610 | 0.582 | 1 | 1.28 | -0.0175
LFAllSpcPGENrsNewCZ03 | Com-Iltg-dWatt-LF_OSspc | PGE | Nrs | New | CZ03 | 3.61 | 0.000582 | 0 | 3.51 | 0.000719 | -0.066 | 3.61 | 0.000582 | 0 | 3.51 | 0.000719 | -0.066 |  | LF | AllSpc | 3610 | 0.582 | 3610 | 0.582 | 0.972 | 1.24 | -0.018283 | 3610 | 0.582 | 3610 | 0.582 | 0.972 | 1.24 | -0.0183
LFAllSpcPGENrsNewCZ04 | Com-Iltg-dWatt-LF_OSspc | PGE | Nrs | New | CZ04 | 3.61 | 0.000582 | 0 | 3.68 | 0.000733 | -0.0541 | 3.61 | 0.000582 | 0 | 3.68 | 0.000733 | -0.0541 |  | LF | AllSpc | 3610 | 0.582 | 3610 | 0.582 | 1.02 | 1.26 | -0.014986 | 3610 | 0.582 | 3610 | 0.582 | 1.02 | 1.26 | -0.015
LFAllSpcPGENrsNewCZ05 | Com-Iltg-dWatt-LF_OSspc | PGE | Nrs | New | CZ05 | 3.61 | 0.000582 | 0 | 3.52 | 0.000691 | -0.0664 | 3.61 | 0.000582 | 0 | 3.52 | 0.000691 | -0.0664 |  | LF | AllSpc | 3610 | 0.582 | 3610 | 0.582 | 0.975 | 1.19 | -0.018393 | 3610 | 0.582 | 3610 | 0.582 | 0.975 | 1.19 | -0.0184
LFAllSpcPGENrsNewCZ11 | Com-Iltg-dWatt-LF_OSspc | PGE | Nrs | New | CZ11 | 3.61 | 0.000582 | 0 | 3.76 | 0.000741 | -0.0501 | 3.61 | 0.000582 | 0 | 3.76 | 0.000741 | -0.0501 |  | LF | AllSpc | 3610 | 0.582 | 3610 | 0.582 | 1.04 | 1.27 | -0.013878 | 3610 | 0.582 | 3610 | 0.582 | 1.04 | 1.27 | -0.0139
LFAllSpcPGENrsNewCZ12 | Com-Iltg-dWatt-LF_OSspc | PGE | Nrs | New | CZ12 | 3.61 | 0.000582 | 0 | 3.72 | 0.000746 | -0.053 | 3.61 | 0.000582 | 0 | 3.72 | 0.000746 | -0.053 |  | LF | AllSpc | 3610 | 0.582 | 3610 | 0.582 | 1.03 | 1.28 | -0.014681 | 3610 | 0.582 | 3610 | 0.582 | 1.03 | 1.28 | -0.0147
LFAllSpcPGENrsNewCZ13 | Com-Iltg-dWatt-LF_OSspc | PGE | Nrs | New | CZ13 | 3.61 | 0.000582 | 0 | 3.78 | 0.000745 | -0.048 | 3.61 | 0.000582 | 0 | 3.78 | 0.000745 | -0.048 |  | LF | AllSpc | 3610 | 0.582 | 3610 | 0.582 | 1.05 | 1.28 | -0.013296 | 3610 | 0.582 | 3610 | 0.582 | 1.05 | 1.28 | -0.0133
LFAllSpcPGENrsNewCZ16 | Com-Iltg-dWatt-LF_OSspc | PGE | Nrs | New | CZ16 | 3.61 | 0.000582 | 0 | 3.53 | 0.000709 | -0.0721 | 3.61 | 0.000582 | 0 | 3.53 | 0.000709 | -0.0721 |  | LF | AllSpc | 3610 | 0.582 | 3610 | 0.582 | 0.978 | 1.22 | -0.019972 | 3610 | 0.582 | 3610 | 0.582 | 0.978 | 1.22 | -0.02
LFAllSpcPGENrsNewIOU | Com-Iltg-dWatt-LF_OSspc | PGE | Nrs | New | IOU | 3.61 | 0.000582 | 0 | 3.6617 | 0.00073483 | -0.056631 | 3.61 | 0.000582 | 0 | 3.6617 | 0.00073483 | -0.056631 |  | LF | AllSpc | 3610 | 0.582 | 3610 | 0.582 | 1.01 | 1.26 | -0.015687 | 3610 | 0.582 | 3610 | 0.582 | 1.01 | 1.26 | -0.0157
LFAllSpcPGEOfLExCZ01 | Com-Iltg-dWatt-LF_OSspc | PGE | OfL | Ex | CZ01 | 2.11 | 0.00057596 | 0 | 2.27 | 0.00071396 | -0.0197 | 2.11 | 0.00057596 | 0 | 2.27 | 0.00071396 | -0.0197 |  | LF | AllSpc | 2110 | 0.576 | 2110 | 0.576 | 1.08 | 1.24 | -0.0093365 | 2110 | 0.576 | 2110 | 0.576 | 1.08 | 1.24 | -0.00934
LFAllSpcPGEOfLExCZ02 | Com-Iltg-dWatt-LF_OSspc | PGE | OfL | Ex | CZ02 | 2.11 | 0.00057595 | 0 | 2.34 | 0.00075995 | -0.0145 | 2.11 | 0.00057595 | 0 | 2.34 | 0.00075995 | -0.0145 |  | LF | AllSpc | 2110 | 0.576 | 2110 | 0.576 | 1.11 | 1.32 | -0.006872 | 2110 | 0.576 | 2110 | 0.576 | 1.11 | 1.32 | -0.00687
LFAllSpcPGEOfLExCZ03 | Com-Iltg-dWatt-LF_OSspc | PGE | OfL | Ex | CZ03 | 2.11 | 0.00057595 | 0 | 2.33 | 0.00073595 | -0.0134 | 2.11 | 0.00057595 | 0 | 2.33 | 0.00073595 | -0.0134 |  | LF | AllSpc | 2110 | 0.576 | 2110 | 0.576 | 1.1 | 1.28 | -0.0063507 | 2110 | 0.576 | 2110 | 0.576 | 1.1 | 1.28 | -0.00635
LFAllSpcPGEOfLExCZ04 | Com-Iltg-dWatt-LF_OSspc | PGE | OfL | Ex | CZ04 | 2.11 | 0.00057594 | 0 | 2.36 | 0.000757 | -0.0121 | 2.11 | 0.00057594 | 0 | 2.36 | 0.000757 | -0.0121 |  | LF | AllSpc | 2110 | 0.576 | 2110 | 0.576 | 1.12 | 1.31 | -0.0057346 | 2110 | 0.576 | 2110 | 0.576 | 1.12 | 1.31 | -0.00573
LFAllSpcPGEOfLExCZ05 | Com-Iltg-dWatt-LF_OSspc | PGE | OfL | Ex | CZ05 | 2.11 | 0.00057594 | 0 | 2.3294 | 0.00072394 | -0.013 | 2.11 | 0.00057594 | 0 | 2.3294 | 0.00072394 | -0.013 |  | LF | AllSpc | 2110 | 0.576 | 2110 | 0.576 | 1.1 | 1.26 | -0.0061611 | 2110 | 0.576 | 2110 | 0.576 | 1.1 | 1.26 | -0.00616
LFAllSpcPGEOfLExCZ11 | Com-Iltg-dWatt-LF_OSspc | PGE | OfL | Ex | CZ11 | 2.11 | 0.00057592 | 0 | 2.38 | 0.00076592 | -0.0138 | 2.11 | 0.00057592 | 0 | 2.38 | 0.00076592 | -0.0138 |  | LF | AllSpc | 2110 | 0.576 | 2110 | 0.576 | 1.13 | 1.33 | -0.0065403 | 2110 | 0.576 | 2110 | 0.576 | 1.13 | 1.33 | -0.00654
LFAllSpcPGEOfLExCZ12 | Com-Iltg-dWatt-LF_OSspc | PGE | OfL | Ex | CZ12 | 2.11 | 0.00057592 | 0 | 2.36 | 0.000753 | -0.0134 | 2.11 | 0.00057592 | 0 | 2.36 | 0.000753 | -0.0134 |  | LF | AllSpc | 2110 | 0.576 | 2110 | 0.576 | 1.12 | 1.31 | -0.0063507 | 2110 | 0.576 | 2110 | 0.576 | 1.12 | 1.31 | -0.00635
LFAllSpcPGEOfLExCZ13 | Com-Iltg-dWatt-LF_OSspc | PGE | OfL | Ex | CZ13 | 2.11 | 0.00057592 | 0 | 2.41 | 0.00076492 | -0.0125 | 2.11 | 0.00057592 | 0 | 2.41 | 0.00076492 | -0.0125 |  | LF | AllSpc | 2110 | 0.576 | 2110 | 0.576 | 1.14 | 1.33 | -0.0059242 | 2110 | 0.576 | 2110 | 0.576 | 1.14 | 1.33 | -0.00592
LFAllSpcPGEOfLExCZ16 | Com-Iltg-dWatt-LF_OSspc | PGE | OfL | Ex | CZ16 | 2.11 | 0.00057594 | 0 | 2.24 | 0.00072894 | -0.0236 | 2.11 | 0.00057594 | 0 | 2.24 | 0.00072894 | -0.0236 |  | LF | AllSpc | 2110 | 0.576 | 2110 | 0.576 | 1.06 | 1.27 | -0.011185 | 2110 | 0.576 | 2110 | 0.576 | 1.06 | 1.27 | -0.0112
LFAllSpcPGEOfLExIOU | Com-Iltg-dWatt-LF_OSspc | PGE | OfL | Ex | IOU | 2.11 | 0.00057594 | 0 | 2.3465 | 0.000746 | -0.013174 | 2.11 | 0.00057594 | 0 | 2.3465 | 0.000746 | -0.013174 |  | LF | AllSpc | 2110 | 0.576 | 2110 | 0.576 | 1.11 | 1.3 | -0.0062436 | 2110 | 0.576 | 2110 | 0.576 | 1.11 | 1.3 | -0.00624
LFAllSpcPGEOfLNewCZ01 | Com-Iltg-dWatt-LF_OSspc | PGE | OfL | New | CZ01 | 2.11 | 0.000575 | 0 | 2.27 | 0.000693 | -0.00976 | 2.11 | 0.000575 | 0 | 2.27 | 0.000693 | -0.00976 |  | LF | AllSpc | 2110 | 0.575 | 2110 | 0.575 | 1.08 | 1.21 | -0.0046256 | 2110 | 0.575 | 2110 | 0.575 | 1.08 | 1.21 | -0.00463
LFAllSpcPGEOfLNewCZ02 | Com-Iltg-dWatt-LF_OSspc | PGE | OfL | New | CZ02 | 2.11 | 0.000575 | 0 | 2.36 | 0.000719 | -0.00704 | 2.11 | 0.000575 | 0 | 2.36 | 0.000719 | -0.00704 |  | LF | AllSpc | 2110 | 0.575 | 2110 | 0.575 | 1.12 | 1.25 | -0.0033365 | 2110 | 0.575 | 2110 | 0.575 | 1.12 | 1.25 | -0.00334
LFAllSpcPGEOfLNewCZ03 | Com-Iltg-dWatt-LF_OSspc | PGE | OfL | New | CZ03 | 2.11 | 0.000575 | 0 | 2.35 | 0.000708 | -0.00628 | 2.11 | 0.000575 | 0 | 2.35 | 0.000708 | -0.00628 |  | LF | AllSpc | 2110 | 0.575 | 2110 | 0.575 | 1.11 | 1.23 | -0.0029763 | 2110 | 0.575 | 2110 | 0.575 | 1.11 | 1.23 | -0.00298
LFAllSpcPGEOfLNewCZ04 | Com-Iltg-dWatt-LF_OSspc | PGE | OfL | New | CZ04 | 2.11 | 0.000575 | 0 | 2.38 | 0.000717 | -0.00584 | 2.11 | 0.000575 | 0 | 2.38 | 0.000717 | -0.00584 |  | LF | AllSpc | 2110 | 0.575 | 2110 | 0.575 | 1.13 | 1.25 | -0.0027678 | 2110 | 0.575 | 2110 | 0.575 | 1.13 | 1.25 | -0.00277
LFAllSpcPGEOfLNewCZ05 | Com-Iltg-dWatt-LF_OSspc | PGE | OfL | New | CZ05 | 2.11 | 0.000575 | 0 | 2.34 | 0.0007 | -0.00643 | 2.11 | 0.000575 | 0 | 2.34 | 0.0007 | -0.00643 |  | LF | AllSpc | 2110 | 0.575 | 2110 | 0.575 | 1.11 | 1.22 | -0.0030474 | 2110 | 0.575 | 2110 | 0.575 | 1.11 | 1.22 | -0.00305
LFAllSpcPGEOfLNewCZ11 | Com-Iltg-dWatt-LF_OSspc | PGE | OfL | New | CZ11 | 2.11 | 0.000575 | 0 | 2.4 | 0.00073 | -0.00571 | 2.11 | 0.000575 | 0 | 2.4 | 0.00073 | -0.00571 |  | LF | AllSpc | 2110 | 0.575 | 2110 | 0.575 | 1.14 | 1.27 | -0.0027062 | 2110 | 0.575 | 2110 | 0.575 | 1.14 | 1.27 | -0.00271
LFAllSpcPGEOfLNewCZ12 | Com-Iltg-dWatt-LF_OSspc | PGE | OfL | New | CZ12 | 2.11 | 0.000575 | 0 | 2.38 | 0.000724 | -0.0067 | 2.11 | 0.000575 | 0 | 2.38 | 0.000724 | -0.0067 |  | LF | AllSpc | 2110 | 0.575 | 2110 | 0.575 | 1.13 | 1.26 | -0.0031754 | 2110 | 0.575 | 2110 | 0.575 | 1.13 | 1.26 | -0.00318
LFAllSpcPGEOfLNewCZ13 | Com-Iltg-dWatt-LF_OSspc | PGE | OfL | New | CZ13 | 2.11 | 0.000575 | 0 | 2.4 | 0.000724 | -0.00628 | 2.11 | 0.000575 | 0 | 2.4 | 0.000724 | -0.00628 |  | LF | AllSpc | 2110 | 0.575 | 2110 | 0.575 | 1.14 | 1.26 | -0.0029763 | 2110 | 0.575 | 2110 | 0.575 | 1.14 | 1.26 | -0.00298
LFAllSpcPGEOfLNewCZ16 | Com-Iltg-dWatt-LF_OSspc | PGE | OfL | New | CZ16 | 2.11 | 0.000575 | 0 | 2.28 | 0.000709 | -0.0146 | 2.11 | 0.000575 | 0 | 2.28 | 0.000709 | -0.0146 |  | LF | AllSpc | 2110 | 0.575 | 2110 | 0.575 | 1.08 | 1.23 | -0.0069194 | 2110 | 0.575 | 2110 | 0.575 | 1.08 | 1.23 | -0.00692
LFAllSpcPGEOfLNewIOU | Com-Iltg-dWatt-LF_OSspc | PGE | OfL | New | IOU | 2.11 | 0.000575 | 0 | 2.3683 | 0.00071554 | -0.0063188 | 2.11 | 0.000575 | 0 | 2.3683 | 0.00071554 | -0.0063188 |  | LF | AllSpc | 2110 | 0.575 | 2110 | 0.575 | 1.12 | 1.24 | -0.0029947 | 2110 | 0.575 | 2110 | 0.575 | 1.12 | 1.24 | -0.00299
LFAllSpcPGEOfSExCZ01 | Com-Iltg-dWatt-LF_OSspc | PGE | OfS | Ex | CZ01 | 1.8705 | 0.00051405 | 0 | 1.89 | 0.00060505 | -0.0121 | 1.8705 | 0.00051405 | 0 | 1.89 | 0.00060505 | -0.0121 |  | LF | AllSpc | 1870 | 0.514 | 1870 | 0.514 | 1.01 | 1.18 | -0.0064689 | 1870 | 0.514 | 1870 | 0.514 | 1.01 | 1.18 | -0.00647
LFAllSpcPGEOfSExCZ02 | Com-Iltg-dWatt-LF_OSspc | PGE | OfS | Ex | CZ02 | 1.8706 | 0.00051406 | 0 | 1.98 | 0.00062506 | -0.0077811 | 1.8706 | 0.00051406 | 0 | 1.98 | 0.00062506 | -0.0077811 |  | LF | AllSpc | 1870 | 0.514 | 1870 | 0.514 | 1.06 | 1.22 | -0.0041598 | 1870 | 0.514 | 1870 | 0.514 | 1.06 | 1.22 | -0.00416
LFAllSpcPGEOfSExCZ03 | Com-Iltg-dWatt-LF_OSspc | PGE | OfS | Ex | CZ03 | 1.8706 | 0.00051406 | 0 | 1.9706 | 0.00062306 | -0.0066911 | 1.8706 | 0.00051406 | 0 | 1.9706 | 0.00062306 | -0.0066911 |  | LF | AllSpc | 1870 | 0.514 | 1870 | 0.514 | 1.05 | 1.21 | -0.0035771 | 1870 | 0.514 | 1870 | 0.514 | 1.05 | 1.21 | -0.00358
LFAllSpcPGEOfSExCZ04 | Com-Iltg-dWatt-LF_OSspc | PGE | OfS | Ex | CZ04 | 1.8706 | 0.00051406 | 0 | 2.0106 | 0.00062712 | -0.0053212 | 1.8706 | 0.00051406 | 0 | 2.0106 | 0.00062712 | -0.0053212 |  | LF | AllSpc | 1870 | 0.514 | 1870 | 0.514 | 1.07 | 1.22 | -0.0028447 | 1870 | 0.514 | 1870 | 0.514 | 1.07 | 1.22 | -0.00284
LFAllSpcPGEOfSExCZ05 | Com-Iltg-dWatt-LF_OSspc | PGE | OfS | Ex | CZ05 | 1.8706 | 0.00051406 | 0 | 1.9806 | 0.00061306 | -0.0054606 | 1.8706 | 0.00051406 | 0 | 1.9806 | 0.00061306 | -0.0054606 |  | LF | AllSpc | 1870 | 0.514 | 1870 | 0.514 | 1.06 | 1.19 | -0.0029192 | 1870 | 0.514 | 1870 | 0.514 | 1.06 | 1.19 | -0.00292
LFAllSpcPGEOfSExCZ11 | Com-Iltg-dWatt-LF_OSspc | PGE | OfS | Ex | CZ11 | 1.8706 | 0.00051406 | 0 | 2.0106 | 0.00062806 | -0.0082317 | 1.8706 | 0.00051406 | 0 | 2.0106 | 0.00062806 | -0.0082317 |  | LF | AllSpc | 1870 | 0.514 | 1870 | 0.514 | 1.07 | 1.22 | -0.0044006 | 1870 | 0.514 | 1870 | 0.514 | 1.07 | 1.22 | -0.0044
LFAllSpcPGEOfSExCZ12 | Com-Iltg-dWatt-LF_OSspc | PGE | OfS | Ex | CZ12 | 1.8706 | 0.00051406 | 0 | 2 | 0.00062612 | -0.0080018 | 1.8706 | 0.00051406 | 0 | 2 | 0.00062612 | -0.0080018 |  | LF | AllSpc | 1870 | 0.514 | 1870 | 0.514 | 1.07 | 1.22 | -0.0042777 | 1870 | 0.514 | 1870 | 0.514 | 1.07 | 1.22 | -0.00428
LFAllSpcPGEOfSExCZ13 | Com-Iltg-dWatt-LF_OSspc | PGE | OfS | Ex | CZ13 | 1.8706 | 0.00051406 | 0 | 2.02 | 0.00062106 | -0.0075412 | 1.8706 | 0.00051406 | 0 | 2.02 | 0.00062106 | -0.0075412 |  | LF | AllSpc | 1870 | 0.514 | 1870 | 0.514 | 1.08 | 1.21 | -0.0040315 | 1870 | 0.514 | 1870 | 0.514 | 1.08 | 1.21 | -0.00403
LFAllSpcPGEOfSExCZ16 | Com-Iltg-dWatt-LF_OSspc | PGE | OfS | Ex | CZ16 | 1.8705 | 0.00051405 | 0 | 1.87 | 0.00061405 | -0.015005 | 1.8705 | 0.00051405 | 0 | 1.87 | 0.00061405 | -0.015005 |  | LF | AllSpc | 1870 | 0.514 | 1870 | 0.514 | 1 | 1.19 | -0.0080219 | 1870 | 0.514 | 1870 | 0.514 | 1 | 1.19 | -0.00802
LFAllSpcPGEOfSExIOU | Com-Iltg-dWatt-LF_OSspc | PGE | OfS | Ex | IOU | 1.8706 | 0.00051406 | 0 | 1.9957 | 0.00062398 | -0.0071914 | 1.8706 | 0.00051406 | 0 | 1.9957 | 0.00062398 | -0.0071914 |  | LF | AllSpc | 1870 | 0.514 | 1870 | 0.514 | 1.07 | 1.21 | -0.0038445 | 1870 | 0.514 | 1870 | 0.514 | 1.07 | 1.21 | -0.00384
LFAllSpcPGEOfSNewCZ01 | Com-Iltg-dWatt-LF_OSspc | PGE | OfS | New | CZ01 | 1.88 | 0.000515 | 0 | 1.86 | 0.000602 | -0.0102 | 1.88 | 0.000515 | 0 | 1.86 | 0.000602 | -0.0102 |  | LF | AllSpc | 1880 | 0.515 | 1880 | 0.515 | 0.989 | 1.17 | -0.0054255 | 1880 | 0.515 | 1880 | 0.515 | 0.989 | 1.17 | -0.00543
LFAllSpcPGEOfSNewCZ02 | Com-Iltg-dWatt-LF_OSspc | PGE | OfS | New | CZ02 | 1.88 | 0.000515 | 0 | 1.98 | 0.000625 | -0.00542 | 1.88 | 0.000515 | 0 | 1.98 | 0.000625 | -0.00542 |  | LF | AllSpc | 1880 | 0.515 | 1880 | 0.515 | 1.05 | 1.21 | -0.002883 | 1880 | 0.515 | 1880 | 0.515 | 1.05 | 1.21 | -0.00288
LFAllSpcPGEOfSNewCZ03 | Com-Iltg-dWatt-LF_OSspc | PGE | OfS | New | CZ03 | 1.88 | 0.000515 | 0 | 1.95 | 0.000624 | -0.00602 | 1.88 | 0.000515 | 0 | 1.95 | 0.000624 | -0.00602 |  | LF | AllSpc | 1880 | 0.515 | 1880 | 0.515 | 1.04 | 1.21 | -0.0032021 | 1880 | 0.515 | 1880 | 0.515 | 1.04 | 1.21 | -0.0032
LFAllSpcPGEOfSNewCZ04 | Com-Iltg-dWatt-LF_OSspc | PGE | OfS | New | CZ04 | 1.88 | 0.000515 | 0 | 2 | 0.000635 | -0.00431 | 1.88 | 0.000515 | 0 | 2 | 0.000635 | -0.00431 |  | LF | AllSpc | 1880 | 0.515 | 1880 | 0.515 | 1.06 | 1.23 | -0.0022926 | 1880 | 0.515 | 1880 | 0.515 | 1.06 | 1.23 | -0.00229
LFAllSpcPGEOfSNewCZ05 | Com-Iltg-dWatt-LF_OSspc | PGE | OfS | New | CZ05 | 1.88 | 0.000515 | 0 | 1.97 | 0.000614 | -0.00461 | 1.88 | 0.000515 | 0 | 1.97 | 0.000614 | -0.00461 |  | LF | AllSpc | 1880 | 0.515 | 1880 | 0.515 | 1.05 | 1.19 | -0.0024521 | 1880 | 0.515 | 1880 | 0.515 | 1.05 | 1.19 | -0.00245
LFAllSpcPGEOfSNewCZ11 | Com-Iltg-dWatt-LF_OSspc | PGE | OfS | New | CZ11 | 1.88 | 0.000515 | 0 | 2.02 | 0.000646 | -0.00617 | 1.88 | 0.000515 | 0 | 2.02 | 0.000646 | -0.00617 |  | LF | AllSpc | 1880 | 0.515 | 1880 | 0.515 | 1.07 | 1.25 | -0.0032819 | 1880 | 0.515 | 1880 | 0.515 | 1.07 | 1.25 | -0.00328
LFAllSpcPGEOfSNewCZ12 | Com-Iltg-dWatt-LF_OSspc | PGE | OfS | New | CZ12 | 1.88 | 0.000515 | 0 | 2.01 | 0.00064 | -0.00596 | 1.88 | 0.000515 | 0 | 2.01 | 0.00064 | -0.00596 |  | LF | AllSpc | 1880 | 0.515 | 1880 | 0.515 | 1.07 | 1.24 | -0.0031702 | 1880 | 0.515 | 1880 | 0.515 | 1.07 | 1.24 | -0.00317
LFAllSpcPGEOfSNewCZ13 | Com-Iltg-dWatt-LF_OSspc | PGE | OfS | New | CZ13 | 1.88 | 0.000515 | 0 | 2.03 | 0.000639 | -0.00572 | 1.88 | 0.000515 | 0 | 2.03 | 0.000639 | -0.00572 |  | LF | AllSpc | 1880 | 0.515 | 1880 | 0.515 | 1.08 | 1.24 | -0.0030426 | 1880 | 0.515 | 1880 | 0.515 | 1.08 | 1.24 | -0.00304
LFAllSpcPGEOfSNewCZ16 | Com-Iltg-dWatt-LF_OSspc | PGE | OfS | New | CZ16 | 1.88 | 0.000515 | 0 | 1.88 | 0.00062 | -0.0134 | 1.88 | 0.000515 | 0 | 1.88 | 0.00062 | -0.0134 |  | LF | AllSpc | 1880 | 0.515 | 1880 | 0.515 | 1 | 1.2 | -0.0071277 | 1880 | 0.515 | 1880 | 0.515 | 1 | 1.2 | -0.00713
LFAllSpcPGEOfSNewIOU | Com-Iltg-dWatt-LF_OSspc | PGE | OfS | New | IOU | 1.88 | 0.000515 | 0 | 1.9942 | 0.00063388 | -0.0056996 | 1.88 | 0.000515 | 0 | 1.9942 | 0.00063388 | -0.0056996 |  | LF | AllSpc | 1880 | 0.515 | 1880 | 0.515 | 1.06 | 1.23 | -0.0030317 | 1880 | 0.515 | 1880 | 0.515 | 1.06 | 1.23 | -0.00303
LFAllSpcPGERFFExCZ01 | Com-Iltg-dWatt-LF_OSspc | PGE | RFF | Ex | CZ01 | 4.02 | 0.000691 | 0 | 3.89 | 0.000791 | -0.0531 | 4.02 | 0.000691 | 0 | 3.89 | 0.000791 | -0.0531 |  | LF | AllSpc | 4020 | 0.691 | 4020 | 0.691 | 0.968 | 1.14 | -0.013209 | 4020 | 0.691 | 4020 | 0.691 | 0.968 | 1.14 | -0.0132
LFAllSpcPGERFFExCZ02 | Com-Iltg-dWatt-LF_OSspc | PGE | RFF | Ex | CZ02 | 4.02 | 0.000691 | 0 | 4.15 | 0.000809 | -0.0337 | 4.02 | 0.000691 | 0 | 4.15 | 0.000809 | -0.0337 |  | LF | AllSpc | 4020 | 0.691 | 4020 | 0.691 | 1.03 | 1.17 | -0.0083831 | 4020 | 0.691 | 4020 | 0.691 | 1.03 | 1.17 | -0.00838
LFAllSpcPGERFFExCZ03 | Com-Iltg-dWatt-LF_OSspc | PGE | RFF | Ex | CZ03 | 4.02 | 0.000691 | 0 | 4.1 | 0.000806 | -0.0358 | 4.02 | 0.000691 | 0 | 4.1 | 0.000806 | -0.0358 |  | LF | AllSpc | 4020 | 0.691 | 4020 | 0.691 | 1.02 | 1.17 | -0.0089055 | 4020 | 0.691 | 4020 | 0.691 | 1.02 | 1.17 | -0.00891
LFAllSpcPGERFFExCZ04 | Com-Iltg-dWatt-LF_OSspc | PGE | RFF | Ex | CZ04 | 4.02 | 0.000691 | 0 | 4.21 | 0.000809 | -0.0281 | 4.02 | 0.000691 | 0 | 4.21 | 0.000809 | -0.0281 |  | LF | AllSpc | 4020 | 0.691 | 4020 | 0.691 | 1.05 | 1.17 | -0.00699 | 4020 | 0.691 | 4020 | 0.691 | 1.05 | 1.17 | -0.00699
LFAllSpcPGERFFExCZ05 | Com-Iltg-dWatt-LF_OSspc | PGE | RFF | Ex | CZ05 | 4.02 | 0.000691 | 0 | 4.09 | 0.000796 | -0.0363 | 4.02 | 0.000691 | 0 | 4.09 | 0.000796 | -0.0363 |  | LF | AllSpc | 4020 | 0.691 | 4020 | 0.691 | 1.02 | 1.15 | -0.0090299 | 4020 | 0.691 | 4020 | 0.691 | 1.02 | 1.15 | -0.00903
LFAllSpcPGERFFExCZ11 | Com-Iltg-dWatt-LF_OSspc | PGE | RFF | Ex | CZ11 | 4.02 | 0.000691 | 0 | 4.23 | 0.000824 | -0.0276 | 4.02 | 0.000691 | 0 | 4.23 | 0.000824 | -0.0276 |  | LF | AllSpc | 4020 | 0.691 | 4020 | 0.691 | 1.05 | 1.19 | -0.0068657 | 4020 | 0.691 | 4020 | 0.691 | 1.05 | 1.19 | -0.00687
LFAllSpcPGERFFExCZ12 | Com-Iltg-dWatt-LF_OSspc | PGE | RFF | Ex | CZ12 | 4.02 | 0.000691 | 0 | 4.22 | 0.000817 | -0.0288 | 4.02 | 0.000691 | 0 | 4.22 | 0.000817 | -0.0288 |  | LF | AllSpc | 4020 | 0.691 | 4020 | 0.691 | 1.05 | 1.18 | -0.0071642 | 4020 | 0.691 | 4020 | 0.691 | 1.05 | 1.18 | -0.00716
LFAllSpcPGERFFExCZ13 | Com-Iltg-dWatt-LF_OSspc | PGE | RFF | Ex | CZ13 | 4.02 | 0.000691 | 0 | 4.25 | 0.000813 | -0.0263 | 4.02 | 0.000691 | 0 | 4.25 | 0.000813 | -0.0263 |  | LF | AllSpc | 4020 | 0.691 | 4020 | 0.691 | 1.06 | 1.18 | -0.0065423 | 4020 | 0.691 | 4020 | 0.691 | 1.06 | 1.18 | -0.00654
LFAllSpcPGERFFExCZ16 | Com-Iltg-dWatt-LF_OSspc | PGE | RFF | Ex | CZ16 | 4.02 | 0.000691 | 0 | 3.93 | 0.000801 | -0.0507 | 4.02 | 0.000691 | 0 | 3.93 | 0.000801 | -0.0507 |  | LF | AllSpc | 4020 | 0.691 | 4020 | 0.691 | 0.978 | 1.16 | -0.012612 | 4020 | 0.691 | 4020 | 0.691 | 0.978 | 1.16 | -0.0126
LFAllSpcPGERFFExIOU | Com-Iltg-dWatt-LF_OSspc | PGE | RFF | Ex | IOU | 4.02 | 0.000691 | 0 | 4.1688 | 0.00081054 | -0.031651 | 4.02 | 0.000691 | 0 | 4.1688 | 0.00081054 | -0.031651 |  | LF | AllSpc | 4020 | 0.691 | 4020 | 0.691 | 1.04 | 1.17 | -0.0078733 | 4020 | 0.691 | 4020 | 0.691 | 1.04 | 1.17 | -0.00787
LFAllSpcPGERFFNewCZ01 | Com-Iltg-dWatt-LF_OSspc | PGE | RFF | New | CZ01 | 4.02 | 0.000691 | 0 | 3.77 | 0.000756 | -0.0567 | 4.02 | 0.000691 | 0 | 3.77 | 0.000756 | -0.0567 |  | LF | AllSpc | 4020 | 0.691 | 4020 | 0.691 | 0.938 | 1.09 | -0.014104 | 4020 | 0.691 | 4020 | 0.691 | 0.938 | 1.09 | -0.0141
LFAllSpcPGERFFNewCZ02 | Com-Iltg-dWatt-LF_OSspc | PGE | RFF | New | CZ02 | 4.02 | 0.000691 | 0 | 4.07 | 0.000846 | -0.0414 | 4.02 | 0.000691 | 0 | 4.07 | 0.000846 | -0.0414 |  | LF | AllSpc | 4020 | 0.691 | 4020 | 0.691 | 1.01 | 1.22 | -0.010299 | 4020 | 0.691 | 4020 | 0.691 | 1.01 | 1.22 | -0.0103
LFAllSpcPGERFFNewCZ03 | Com-Iltg-dWatt-LF_OSspc | PGE | RFF | New | CZ03 | 4.02 | 0.000691 | 0 | 3.98 | 0.000819 | -0.0414 | 4.02 | 0.000691 | 0 | 3.98 | 0.000819 | -0.0414 |  | LF | AllSpc | 4020 | 0.691 | 4020 | 0.691 | 0.99 | 1.19 | -0.010299 | 4020 | 0.691 | 4020 | 0.691 | 0.99 | 1.19 | -0.0103
LFAllSpcPGERFFNewCZ04 | Com-Iltg-dWatt-LF_OSspc | PGE | RFF | New | CZ04 | 4.02 | 0.000691 | 0 | 4.14 | 0.000835 | -0.0338 | 4.02 | 0.000691 | 0 | 4.14 | 0.000835 | -0.0338 |  | LF | AllSpc | 4020 | 0.691 | 4020 | 0.691 | 1.03 | 1.21 | -0.008408 | 4020 | 0.691 | 4020 | 0.691 | 1.03 | 1.21 | -0.00841
LFAllSpcPGERFFNewCZ05 | Com-Iltg-dWatt-LF_OSspc | PGE | RFF | New | CZ05 | 4.02 | 0.000691 | 0 | 3.98 | 0.000806 | -0.0365 | 4.02 | 0.000691 | 0 | 3.98 | 0.000806 | -0.0365 |  | LF | AllSpc | 4020 | 0.691 | 4020 | 0.691 | 0.99 | 1.17 | -0.0090796 | 4020 | 0.691 | 4020 | 0.691 | 0.99 | 1.17 | -0.00908
LFAllSpcPGERFFNewCZ11 | Com-Iltg-dWatt-LF_OSspc | PGE | RFF | New | CZ11 | 4.02 | 0.000691 | 0 | 4.24 | 0.000862 | -0.0333 | 4.02 | 0.000691 | 0 | 4.24 | 0.000862 | -0.0333 |  | LF | AllSpc | 4020 | 0.691 | 4020 | 0.691 | 1.05 | 1.25 | -0.0082836 | 4020 | 0.691 | 4020 | 0.691 | 1.05 | 1.25 | -0.00828
LFAllSpcPGERFFNewCZ12 | Com-Iltg-dWatt-LF_OSspc | PGE | RFF | New | CZ12 | 4.02 | 0.000691 | 0 | 4.19 | 0.000854 | -0.0359 | 4.02 | 0.000691 | 0 | 4.19 | 0.000854 | -0.0359 |  | LF | AllSpc | 4020 | 0.691 | 4020 | 0.691 | 1.04 | 1.24 | -0.0089303 | 4020 | 0.691 | 4020 | 0.691 | 1.04 | 1.24 | -0.00893
LFAllSpcPGERFFNewCZ13 | Com-Iltg-dWatt-LF_OSspc | PGE | RFF | New | CZ13 | 4.02 | 0.000691 | 0 | 4.25 | 0.000853 | -0.0317 | 4.02 | 0.000691 | 0 | 4.25 | 0.000853 | -0.0317 |  | LF | AllSpc | 4020 | 0.691 | 4020 | 0.691 | 1.06 | 1.23 | -0.0078856 | 4020 | 0.691 | 4020 | 0.691 | 1.06 | 1.23 | -0.00789
LFAllSpcPGERFFNewCZ16 | Com-Iltg-dWatt-LF_OSspc | PGE | RFF | New | CZ16 | 4.02 | 0.000691 | 0 | 3.92 | 0.000822 | -0.0563 | 4.02 | 0.000691 | 0 | 3.92 | 0.000822 | -0.0563 |  | LF | AllSpc | 4020 | 0.691 | 4020 | 0.691 | 0.975 | 1.19 | -0.014005 | 4020 | 0.691 | 4020 | 0.691 | 0.975 | 1.19 | -0.014
LFAllSpcPGERFFNewIOU | Com-Iltg-dWatt-LF_OSspc | PGE | RFF | New | IOU | 4.02 | 0.000691 | 0 | 4.1098 | 0.00083781 | -0.037366 | 4.02 | 0.000691 | 0 | 4.1098 | 0.00083781 | -0.037366 |  | LF | AllSpc | 4020 | 0.691 | 4020 | 0.691 | 1.02 | 1.21 | -0.0092951 | 4020 | 0.691 | 4020 | 0.691 | 1.02 | 1.21 | -0.0093
LFAllSpcPGERSDExCZ01 | Com-Iltg-dWatt-LF_OSspc | PGE | RSD | Ex | CZ01 | 3.87 | 0.000679 | 0 | 3.54 | 0.000782 | -0.0662 | 3.87 | 0.000679 | 0 | 3.54 | 0.000782 | -0.0662 |  | LF | AllSpc | 3870 | 0.679 | 3870 | 0.679 | 0.915 | 1.15 | -0.017106 | 3870 | 0.679 | 3870 | 0.679 | 0.915 | 1.15 | -0.0171
LFAllSpcPGERSDExCZ02 | Com-Iltg-dWatt-LF_OSspc | PGE | RSD | Ex | CZ02 | 3.87 | 0.000679 | 0 | 3.93 | 0.000797 | -0.0375 | 3.87 | 0.000679 | 0 | 3.93 | 0.000797 | -0.0375 |  | LF | AllSpc | 3870 | 0.679 | 3870 | 0.679 | 1.02 | 1.17 | -0.0096899 | 3870 | 0.679 | 3870 | 0.679 | 1.02 | 1.17 | -0.00969
LFAllSpcPGERSDExCZ03 | Com-Iltg-dWatt-LF_OSspc | PGE | RSD | Ex | CZ03 | 3.87 | 0.000679 | 0 | 3.86 | 0.000803 | -0.0414 | 3.87 | 0.000679 | 0 | 3.86 | 0.000803 | -0.0414 |  | LF | AllSpc | 3870 | 0.679 | 3870 | 0.679 | 0.997 | 1.18 | -0.010698 | 3870 | 0.679 | 3870 | 0.679 | 0.997 | 1.18 | -0.0107
LFAllSpcPGERSDExCZ04 | Com-Iltg-dWatt-LF_OSspc | PGE | RSD | Ex | CZ04 | 3.87 | 0.000679 | 0 | 4.02 | 0.000804 | -0.0303 | 3.87 | 0.000679 | 0 | 4.02 | 0.000804 | -0.0303 |  | LF | AllSpc | 3870 | 0.679 | 3870 | 0.679 | 1.04 | 1.18 | -0.0078295 | 3870 | 0.679 | 3870 | 0.679 | 1.04 | 1.18 | -0.00783
LFAllSpcPGERSDExCZ05 | Com-Iltg-dWatt-LF_OSspc | PGE | RSD | Ex | CZ05 | 3.8717 | 0.00067917 | 0 | 3.88 | 0.00079834 | -0.039917 | 3.8717 | 0.00067917 | 0 | 3.88 | 0.00079834 | -0.039917 |  | LF | AllSpc | 3870 | 0.679 | 3870 | 0.679 | 1 | 1.18 | -0.01031 | 3870 | 0.679 | 3870 | 0.679 | 1 | 1.18 | -0.0103
LFAllSpcPGERSDExCZ11 | Com-Iltg-dWatt-LF_OSspc | PGE | RSD | Ex | CZ11 | 3.87 | 0.000679 | 0 | 4.01 | 0.000799 | -0.0328 | 3.87 | 0.000679 | 0 | 4.01 | 0.000799 | -0.0328 |  | LF | AllSpc | 3870 | 0.679 | 3870 | 0.679 | 1.04 | 1.18 | -0.0084755 | 3870 | 0.679 | 3870 | 0.679 | 1.04 | 1.18 | -0.00848
LFAllSpcPGERSDExCZ12 | Com-Iltg-dWatt-LF_OSspc | PGE | RSD | Ex | CZ12 | 3.87 | 0.000679 | 0 | 3.98 | 0.00076996 | -0.0338 | 3.87 | 0.000679 | 0 | 3.98 | 0.00076996 | -0.0338 |  | LF | AllSpc | 3870 | 0.679 | 3870 | 0.679 | 1.03 | 1.13 | -0.0087338 | 3870 | 0.679 | 3870 | 0.679 | 1.03 | 1.13 | -0.00873
LFAllSpcPGERSDExCZ13 | Com-Iltg-dWatt-LF_OSspc | PGE | RSD | Ex | CZ13 | 3.87 | 0.000679 | 0 | 4.04 | 0.000806 | -0.0304 | 3.87 | 0.000679 | 0 | 4.04 | 0.000806 | -0.0304 |  | LF | AllSpc | 3870 | 0.679 | 3870 | 0.679 | 1.04 | 1.19 | -0.0078553 | 3870 | 0.679 | 3870 | 0.679 | 1.04 | 1.19 | -0.00786
LFAllSpcPGERSDExCZ16 | Com-Iltg-dWatt-LF_OSspc | PGE | RSD | Ex | CZ16 | 3.87 | 0.000679 | 0 | 3.68 | 0.000773 | -0.0538 | 3.87 | 0.000679 | 0 | 3.68 | 0.000773 | -0.0538 |  | LF | AllSpc | 3870 | 0.679 | 3870 | 0.679 | 0.951 | 1.14 | -0.013902 | 3870 | 0.679 | 3870 | 0.679 | 0.951 | 1.14 | -0.0139
LFAllSpcPGERSDExIOU | Com-Iltg-dWatt-LF_OSspc | PGE | RSD | Ex | IOU | 3.87 | 0.000679 | 0 | 3.9418 | 0.00079509 | -0.036309 | 3.87 | 0.000679 | 0 | 3.9418 | 0.00079509 | -0.036309 |  | LF | AllSpc | 3870 | 0.679 | 3870 | 0.679 | 1.02 | 1.17 | -0.0093822 | 3870 | 0.679 | 3870 | 0.679 | 1.02 | 1.17 | -0.00938
LFAllSpcPGERSDNewCZ01 | Com-Iltg-dWatt-LF_OSspc | PGE | RSD | New | CZ01 | 3.87 | 0.000679 | 0 | 3.57 | 0.000786 | -0.0317 | 3.87 | 0.000679 | 0 | 3.57 | 0.000786 | -0.0317 |  | LF | AllSpc | 3870 | 0.679 | 3870 | 0.679 | 0.922 | 1.16 | -0.0081912 | 3870 | 0.679 | 3870 | 0.679 | 0.922 | 1.16 | -0.00819
LFAllSpcPGERSDNewCZ02 | Com-Iltg-dWatt-LF_OSspc | PGE | RSD | New | CZ02 | 3.87 | 0.000679 | 0 | 3.9 | 0.000838 | -0.0426 | 3.87 | 0.000679 | 0 | 3.9 | 0.000838 | -0.0426 |  | LF | AllSpc | 3870 | 0.679 | 3870 | 0.679 | 1.01 | 1.23 | -0.011008 | 3870 | 0.679 | 3870 | 0.679 | 1.01 | 1.23 | -0.011
LFAllSpcPGERSDNewCZ03 | Com-Iltg-dWatt-LF_OSspc | PGE | RSD | New | CZ03 | 3.87 | 0.000679 | 0 | 3.81 | 0.000826 | -0.0472 | 3.87 | 0.000679 | 0 | 3.81 | 0.000826 | -0.0472 |  | LF | AllSpc | 3870 | 0.679 | 3870 | 0.679 | 0.984 | 1.22 | -0.012196 | 3870 | 0.679 | 3870 | 0.679 | 0.984 | 1.22 | -0.0122
LFAllSpcPGERSDNewCZ04 | Com-Iltg-dWatt-LF_OSspc | PGE | RSD | New | CZ04 | 3.87 | 0.000679 | 0 | 4 | 0.000839 | -0.0344 | 3.87 | 0.000679 | 0 | 4 | 0.000839 | -0.0344 |  | LF | AllSpc | 3870 | 0.679 | 3870 | 0.679 | 1.03 | 1.24 | -0.0088889 | 3870 | 0.679 | 3870 | 0.679 | 1.03 | 1.24 | -0.00889
LFAllSpcPGERSDNewCZ05 | Com-Iltg-dWatt-LF_OSspc | PGE | RSD | New | CZ05 | 3.87 | 0.000679 | 0 | 3.81 | 0.000805 | -0.0457 | 3.87 | 0.000679 | 0 | 3.81 | 0.000805 | -0.0457 |  | LF | AllSpc | 3870 | 0.679 | 3870 | 0.679 | 0.984 | 1.19 | -0.011809 | 3870 | 0.679 | 3870 | 0.679 | 0.984 | 1.19 | -0.0118
LFAllSpcPGERSDNewCZ11 | Com-Iltg-dWatt-LF_OSspc | PGE | RSD | New | CZ11 | 3.87 | 0.000679 | 0 | 4.03 | 0.000855 | -0.0367 | 3.87 | 0.000679 | 0 | 4.03 | 0.000855 | -0.0367 |  | LF | AllSpc | 3870 | 0.679 | 3870 | 0.679 | 1.04 | 1.26 | -0.0094832 | 3870 | 0.679 | 3870 | 0.679 | 1.04 | 1.26 | -0.00948
LFAllSpcPGERSDNewCZ12 | Com-Iltg-dWatt-LF_OSspc | PGE | RSD | New | CZ12 | 3.87 | 0.000679 | 0 | 4 | 0.000843 | -0.0369 | 3.87 | 0.000679 | 0 | 4 | 0.000843 | -0.0369 |  | LF | AllSpc | 3870 | 0.679 | 3870 | 0.679 | 1.03 | 1.24 | -0.0095349 | 3870 | 0.679 | 3870 | 0.679 | 1.03 | 1.24 | -0.00953
LFAllSpcPGERSDNewCZ13 | Com-Iltg-dWatt-LF_OSspc | PGE | RSD | New | CZ13 | 3.87 | 0.000679 | 0 | 4.05 | 0.000854 | -0.0347 | 3.87 | 0.000679 | 0 | 4.05 | 0.000854 | -0.0347 |  | LF | AllSpc | 3870 | 0.679 | 3870 | 0.679 | 1.05 | 1.26 | -0.0089664 | 3870 | 0.679 | 3870 | 0.679 | 1.05 | 1.26 | -0.00897
LFAllSpcPGERSDNewCZ16 | Com-Iltg-dWatt-LF_OSspc | PGE | RSD | New | CZ16 | 3.87 | 0.000679 | 0 | 3.67 | 0.00081 | -0.043 | 3.87 | 0.000679 | 0 | 3.67 | 0.00081 | -0.043 |  | LF | AllSpc | 3870 | 0.679 | 3870 | 0.679 | 0.948 | 1.19 | -0.011111 | 3870 | 0.679 | 3870 | 0.679 | 0.948 | 1.19 | -0.0111
LFAllSpcPGERSDNewIOU | Com-Iltg-dWatt-LF_OSspc | PGE | RSD | New | IOU | 3.87 | 0.000679 | 0 | 3.9304 | 0.00083739 | -0.040056 | 3.87 | 0.000679 | 0 | 3.9304 | 0.00083739 | -0.040056 |  | LF | AllSpc | 3870 | 0.679 | 3870 | 0.679 | 1.02 | 1.23 | -0.01035 | 3870 | 0.679 | 3870 | 0.679 | 1.02 | 1.23 | -0.0104
LFAllSpcPGERt3ExCZ01 | Com-Iltg-dWatt-LF_OSspc | PGE | Rt3 | Ex | CZ01 | 3.34 | 0.00074915 | 0 | 3.28 | 0.00088639 | -0.042495 | 3.34 | 0.00074915 | 0 | 3.28 | 0.00088639 | -0.042495 |  | LF | AllSpc | 3340 | 0.749 | 3340 | 0.749 | 0.982 | 1.18 | -0.012723 | 3340 | 0.749 | 3340 | 0.749 | 0.982 | 1.18 | -0.0127
LFAllSpcPGERt3ExCZ02 | Com-Iltg-dWatt-LF_OSspc | PGE | Rt3 | Ex | CZ02 | 3.34 | 0.00074918 | 0 | 3.57 | 0.00089118 | -0.020495 | 3.34 | 0.00074918 | 0 | 3.57 | 0.00089118 | -0.020495 |  | LF | AllSpc | 3340 | 0.749 | 3340 | 0.749 | 1.07 | 1.19 | -0.0061363 | 3340 | 0.749 | 3340 | 0.749 | 1.07 | 1.19 | -0.00614
LFAllSpcPGERt3ExCZ03 | Com-Iltg-dWatt-LF_OSspc | PGE | Rt3 | Ex | CZ03 | 3.34 | 0.00074915 | 0 | 3.5996 | 0.00088915 | -0.0186 | 3.34 | 0.00074915 | 0 | 3.5996 | 0.00088915 | -0.0186 |  | LF | AllSpc | 3340 | 0.749 | 3340 | 0.749 | 1.08 | 1.19 | -0.0055689 | 3340 | 0.749 | 3340 | 0.749 | 1.08 | 1.19 | -0.00557
LFAllSpcPGERt3ExCZ04 | Com-Iltg-dWatt-LF_OSspc | PGE | Rt3 | Ex | CZ04 | 3.34 | 0.00074919 | 0 | 3.65 | 0.00089324 | -0.0124 | 3.34 | 0.00074919 | 0 | 3.65 | 0.00089324 | -0.0124 |  | LF | AllSpc | 3340 | 0.749 | 3340 | 0.749 | 1.09 | 1.19 | -0.0037126 | 3340 | 0.749 | 3340 | 0.749 | 1.09 | 1.19 | -0.00371
LFAllSpcPGERt3ExCZ05 | Com-Iltg-dWatt-LF_OSspc | PGE | Rt3 | Ex | CZ05 | 3.34 | 0.0007492 | 0 | 3.5995 | 0.0008772 | -0.0149 | 3.34 | 0.0007492 | 0 | 3.5995 | 0.0008772 | -0.0149 |  | LF | AllSpc | 3340 | 0.749 | 3340 | 0.749 | 1.08 | 1.17 | -0.0044611 | 3340 | 0.749 | 3340 | 0.749 | 1.08 | 1.17 | -0.00446
LFAllSpcPGERt3ExCZ11 | Com-Iltg-dWatt-LF_OSspc | PGE | Rt3 | Ex | CZ11 | 3.34 | 0.00074921 | 0 | 3.5793 | 0.00089721 | -0.0203 | 3.34 | 0.00074921 | 0 | 3.5793 | 0.00089721 | -0.0203 |  | LF | AllSpc | 3340 | 0.749 | 3340 | 0.749 | 1.07 | 1.2 | -0.0060778 | 3340 | 0.749 | 3340 | 0.749 | 1.07 | 1.2 | -0.00608
LFAllSpcPGERt3ExCZ12 | Com-Iltg-dWatt-LF_OSspc | PGE | Rt3 | Ex | CZ12 | 3.34 | 0.00074924 | 0 | 3.5894 | 0.0009016 | -0.0193 | 3.34 | 0.00074924 | 0 | 3.5894 | 0.0009016 | -0.0193 |  | LF | AllSpc | 3340 | 0.749 | 3340 | 0.749 | 1.07 | 1.2 | -0.0057784 | 3340 | 0.749 | 3340 | 0.749 | 1.07 | 1.2 | -0.00578
LFAllSpcPGERt3ExCZ13 | Com-Iltg-dWatt-LF_OSspc | PGE | Rt3 | Ex | CZ13 | 3.34 | 0.0007492 | 0 | 3.6 | 0.00089255 | -0.0187 | 3.34 | 0.0007492 | 0 | 3.6 | 0.00089255 | -0.0187 |  | LF | AllSpc | 3340 | 0.749 | 3340 | 0.749 | 1.08 | 1.19 | -0.0055988 | 3340 | 0.749 | 3340 | 0.749 | 1.08 | 1.19 | -0.0056
LFAllSpcPGERt3ExCZ16 | Com-Iltg-dWatt-LF_OSspc | PGE | Rt3 | Ex | CZ16 | 3.34 | 0.00074918 | 0 | 3.28 | 0.00087524 | -0.0451 | 3.34 | 0.00074918 | 0 | 3.28 | 0.00087524 | -0.0451 |  | LF | AllSpc | 3340 | 0.749 | 3340 | 0.749 | 0.982 | 1.17 | -0.013503 | 3340 | 0.749 | 3340 | 0.749 | 0.982 | 1.17 | -0.0135
LFAllSpcPGERt3ExIOU | Com-Iltg-dWatt-LF_OSspc | PGE | Rt3 | Ex | IOU | 3.34 | 0.00074919 | 0 | 3.5969 | 0.00089333 | -0.018371 | 3.34 | 0.00074919 | 0 | 3.5969 | 0.00089333 | -0.018371 |  | LF | AllSpc | 3340 | 0.749 | 3340 | 0.749 | 1.08 | 1.19 | -0.0055002 | 3340 | 0.749 | 3340 | 0.749 | 1.08 | 1.19 | -0.0055
LFAllSpcPGERt3NewCZ01 | Com-Iltg-dWatt-LF_OSspc | PGE | Rt3 | New | CZ01 | 3.34 | 0.000748 | 0 | 3.23 | 0.000884 | -0.0484 | 3.34 | 0.000748 | 0 | 3.23 | 0.000884 | -0.0484 |  | LF | AllSpc | 3340 | 0.748 | 3340 | 0.748 | 0.967 | 1.18 | -0.014491 | 3340 | 0.748 | 3340 | 0.748 | 0.967 | 1.18 | -0.0145
LFAllSpcPGERt3NewCZ02 | Com-Iltg-dWatt-LF_OSspc | PGE | Rt3 | New | CZ02 | 3.34 | 0.000748 | 0 | 3.52 | 0.000918 | -0.0249 | 3.34 | 0.000748 | 0 | 3.52 | 0.000918 | -0.0249 |  | LF | AllSpc | 3340 | 0.748 | 3340 | 0.748 | 1.05 | 1.23 | -0.0074551 | 3340 | 0.748 | 3340 | 0.748 | 1.05 | 1.23 | -0.00746
LFAllSpcPGERt3NewCZ03 | Com-Iltg-dWatt-LF_OSspc | PGE | Rt3 | New | CZ03 | 3.34 | 0.000748 | 0 | 3.47 | 0.0009 | -0.0236 | 3.34 | 0.000748 | 0 | 3.47 | 0.0009 | -0.0236 |  | LF | AllSpc | 3340 | 0.748 | 3340 | 0.748 | 1.04 | 1.2 | -0.0070659 | 3340 | 0.748 | 3340 | 0.748 | 1.04 | 1.2 | -0.00707
LFAllSpcPGERt3NewCZ04 | Com-Iltg-dWatt-LF_OSspc | PGE | Rt3 | New | CZ04 | 3.34 | 0.000748 | 0 | 3.59 | 0.000914 | -0.0162 | 3.34 | 0.000748 | 0 | 3.59 | 0.000914 | -0.0162 |  | LF | AllSpc | 3340 | 0.748 | 3340 | 0.748 | 1.07 | 1.22 | -0.0048503 | 3340 | 0.748 | 3340 | 0.748 | 1.07 | 1.22 | -0.00485
LFAllSpcPGERt3NewCZ05 | Com-Iltg-dWatt-LF_OSspc | PGE | Rt3 | New | CZ05 | 3.34 | 0.000748 | 0 | 3.5 | 0.000888 | -0.0189 | 3.34 | 0.000748 | 0 | 3.5 | 0.000888 | -0.0189 |  | LF | AllSpc | 3340 | 0.748 | 3340 | 0.748 | 1.05 | 1.19 | -0.0056587 | 3340 | 0.748 | 3340 | 0.748 | 1.05 | 1.19 | -0.00566
LFAllSpcPGERt3NewCZ11 | Com-Iltg-dWatt-LF_OSspc | PGE | Rt3 | New | CZ11 | 3.34 | 0.000748 | 0 | 3.59 | 0.000906 | -0.021 | 3.34 | 0.000748 | 0 | 3.59 | 0.000906 | -0.021 |  | LF | AllSpc | 3340 | 0.748 | 3340 | 0.748 | 1.07 | 1.21 | -0.0062874 | 3340 | 0.748 | 3340 | 0.748 | 1.07 | 1.21 | -0.00629
LFAllSpcPGERt3NewCZ12 | Com-Iltg-dWatt-LF_OSspc | PGE | Rt3 | New | CZ12 | 3.34 | 0.000748 | 0 | 3.6 | 0.000935 | -0.0228 | 3.34 | 0.000748 | 0 | 3.6 | 0.000935 | -0.0228 |  | LF | AllSpc | 3340 | 0.748 | 3340 | 0.748 | 1.08 | 1.25 | -0.0068263 | 3340 | 0.748 | 3340 | 0.748 | 1.08 | 1.25 | -0.00683
LFAllSpcPGERt3NewCZ13 | Com-Iltg-dWatt-LF_OSspc | PGE | Rt3 | New | CZ13 | 3.34 | 0.000748 | 0 | 3.63 | 0.000931 | -0.0204 | 3.34 | 0.000748 | 0 | 3.63 | 0.000931 | -0.0204 |  | LF | AllSpc | 3340 | 0.748 | 3340 | 0.748 | 1.09 | 1.24 | -0.0061078 | 3340 | 0.748 | 3340 | 0.748 | 1.09 | 1.24 | -0.00611
LFAllSpcPGERt3NewCZ16 | Com-Iltg-dWatt-LF_OSspc | PGE | Rt3 | New | CZ16 | 3.34 | 0.000748 | 0 | 3.3 | 0.000893 | -0.0458 | 3.34 | 0.000748 | 0 | 3.3 | 0.000893 | -0.0458 |  | LF | AllSpc | 3340 | 0.748 | 3340 | 0.748 | 0.988 | 1.19 | -0.013713 | 3340 | 0.748 | 3340 | 0.748 | 0.988 | 1.19 | -0.0137
LFAllSpcPGERt3NewIOU | Com-Iltg-dWatt-LF_OSspc | PGE | Rt3 | New | IOU | 3.34 | 0.000748 | 0 | 3.5584 | 0.00091778 | -0.021932 | 3.34 | 0.000748 | 0 | 3.5584 | 0.00091778 | -0.021932 |  | LF | AllSpc | 3340 | 0.748 | 3340 | 0.748 | 1.07 | 1.23 | -0.0065666 | 3340 | 0.748 | 3340 | 0.748 | 1.07 | 1.23 | -0.00657
LFAllSpcPGERtLExCZ01 | Com-Iltg-dWatt-LF_OSspc | PGE | RtL | Ex | CZ01 | 4.23 | 0.00083895 | 0 | 4.1095 | 0.00099695 | -0.059695 | 4.23 | 0.00083895 | 0 | 4.1095 | 0.00099695 | -0.059695 |  | LF | AllSpc | 4230 | 0.839 | 4230 | 0.839 | 0.972 | 1.19 | -0.014112 | 4230 | 0.839 | 4230 | 0.839 | 0.972 | 1.19 | -0.0141
LFAllSpcPGERtLExCZ02 | Com-Iltg-dWatt-LF_OSspc | PGE | RtL | Ex | CZ02 | 4.23 | 0.00083895 | 0 | 4.4695 | 0.00099695 | -0.029895 | 4.23 | 0.00083895 | 0 | 4.4695 | 0.00099695 | -0.029895 |  | LF | AllSpc | 4230 | 0.839 | 4230 | 0.839 | 1.06 | 1.19 | -0.0070674 | 4230 | 0.839 | 4230 | 0.839 | 1.06 | 1.19 | -0.00707
LFAllSpcPGERtLExCZ03 | Com-Iltg-dWatt-LF_OSspc | PGE | RtL | Ex | CZ03 | 4.23 | 0.00083895 | 0 | 4.49 | 0.00099296 | -0.0285 | 4.23 | 0.00083895 | 0 | 4.49 | 0.00099296 | -0.0285 |  | LF | AllSpc | 4230 | 0.839 | 4230 | 0.839 | 1.06 | 1.18 | -0.0067376 | 4230 | 0.839 | 4230 | 0.839 | 1.06 | 1.18 | -0.00674
LFAllSpcPGERtLExCZ04 | Com-Iltg-dWatt-LF_OSspc | PGE | RtL | Ex | CZ04 | 4.23 | 0.00083895 | 0 | 4.5695 | 0.00099795 | -0.0208 | 4.23 | 0.00083895 | 0 | 4.5695 | 0.00099795 | -0.0208 |  | LF | AllSpc | 4230 | 0.839 | 4230 | 0.839 | 1.08 | 1.19 | -0.0049173 | 4230 | 0.839 | 4230 | 0.839 | 1.08 | 1.19 | -0.00492
LFAllSpcPGERtLExCZ05 | Com-Iltg-dWatt-LF_OSspc | PGE | RtL | Ex | CZ05 | 4.23 | 0.00083895 | 0 | 4.47 | 0.0009799 | -0.0279 | 4.23 | 0.00083895 | 0 | 4.47 | 0.0009799 | -0.0279 |  | LF | AllSpc | 4230 | 0.839 | 4230 | 0.839 | 1.06 | 1.17 | -0.0065957 | 4230 | 0.839 | 4230 | 0.839 | 1.06 | 1.17 | -0.0066
LFAllSpcPGERtLExCZ11 | Com-Iltg-dWatt-LF_OSspc | PGE | RtL | Ex | CZ11 | 4.23 | 0.00083893 | 0 | 4.4993 | 0.00101 | -0.0287 | 4.23 | 0.00083893 | 0 | 4.4993 | 0.00101 | -0.0287 |  | LF | AllSpc | 4230 | 0.839 | 4230 | 0.839 | 1.06 | 1.2 | -0.0067849 | 4230 | 0.839 | 4230 | 0.839 | 1.06 | 1.2 | -0.00678
LFAllSpcPGERtLExCZ12 | Com-Iltg-dWatt-LF_OSspc | PGE | RtL | Ex | CZ12 | 4.23 | 0.00083894 | 0 | 4.5 | 0.00101 | -0.0263 | 4.23 | 0.00083894 | 0 | 4.5 | 0.00101 | -0.0263 |  | LF | AllSpc | 4230 | 0.839 | 4230 | 0.839 | 1.06 | 1.2 | -0.0062175 | 4230 | 0.839 | 4230 | 0.839 | 1.06 | 1.2 | -0.00622
LFAllSpcPGERtLExCZ13 | Com-Iltg-dWatt-LF_OSspc | PGE | RtL | Ex | CZ13 | 4.23 | 0.00083893 | 0 | 4.5393 | 0.00101 | -0.025493 | 4.23 | 0.00083893 | 0 | 4.5393 | 0.00101 | -0.025493 |  | LF | AllSpc | 4230 | 0.839 | 4230 | 0.839 | 1.07 | 1.2 | -0.0060267 | 4230 | 0.839 | 4230 | 0.839 | 1.07 | 1.2 | -0.00603
LFAllSpcPGERtLExCZ16 | Com-Iltg-dWatt-LF_OSspc | PGE | RtL | Ex | CZ16 | 4.23 | 0.00083894 | 0 | 4.12 | 0.00096994 | -0.057994 | 4.23 | 0.00083894 | 0 | 4.12 | 0.00096994 | -0.057994 |  | LF | AllSpc | 4230 | 0.839 | 4230 | 0.839 | 0.974 | 1.16 | -0.01371 | 4230 | 0.839 | 4230 | 0.839 | 0.974 | 1.16 | -0.0137
LFAllSpcPGERtLExIOU | Com-Iltg-dWatt-LF_OSspc | PGE | RtL | Ex | IOU | 4.23 | 0.00083894 | 0 | 4.504 | 0.0010009 | -0.026988 | 4.23 | 0.00083894 | 0 | 4.504 | 0.0010009 | -0.026988 |  | LF | AllSpc | 4230 | 0.839 | 4230 | 0.839 | 1.06 | 1.19 | -0.00638 | 4230 | 0.839 | 4230 | 0.839 | 1.06 | 1.19 | -0.00638
LFAllSpcPGERtLNewCZ01 | Com-Iltg-dWatt-LF_OSspc | PGE | RtL | New | CZ01 | 4.23 | 0.000838 | 0 | 4.09 | 0.000978 | -0.0647 | 4.23 | 0.000838 | 0 | 4.09 | 0.000978 | -0.0647 |  | LF | AllSpc | 4230 | 0.838 | 4230 | 0.838 | 0.967 | 1.17 | -0.015296 | 4230 | 0.838 | 4230 | 0.838 | 0.967 | 1.17 | -0.0153
LFAllSpcPGERtLNewCZ02 | Com-Iltg-dWatt-LF_OSspc | PGE | RtL | New | CZ02 | 4.23 | 0.000838 | 0 | 4.44 | 0.00105 | -0.0336 | 4.23 | 0.000838 | 0 | 4.44 | 0.00105 | -0.0336 |  | LF | AllSpc | 4230 | 0.838 | 4230 | 0.838 | 1.05 | 1.25 | -0.0079433 | 4230 | 0.838 | 4230 | 0.838 | 1.05 | 1.25 | -0.00794
LFAllSpcPGERtLNewCZ03 | Com-Iltg-dWatt-LF_OSspc | PGE | RtL | New | CZ03 | 4.23 | 0.000838 | 0 | 4.37 | 0.00101 | -0.0316 | 4.23 | 0.000838 | 0 | 4.37 | 0.00101 | -0.0316 |  | LF | AllSpc | 4230 | 0.838 | 4230 | 0.838 | 1.03 | 1.21 | -0.0074704 | 4230 | 0.838 | 4230 | 0.838 | 1.03 | 1.21 | -0.00747
LFAllSpcPGERtLNewCZ04 | Com-Iltg-dWatt-LF_OSspc | PGE | RtL | New | CZ04 | 4.23 | 0.000838 | 0 | 4.53 | 0.00103 | -0.0235 | 4.23 | 0.000838 | 0 | 4.53 | 0.00103 | -0.0235 |  | LF | AllSpc | 4230 | 0.838 | 4230 | 0.838 | 1.07 | 1.23 | -0.0055556 | 4230 | 0.838 | 4230 | 0.838 | 1.07 | 1.23 | -0.00556
LFAllSpcPGERtLNewCZ05 | Com-Iltg-dWatt-LF_OSspc | PGE | RtL | New | CZ05 | 4.23 | 0.000838 | 0 | 4.38 | 0.000993 | -0.0326 | 4.23 | 0.000838 | 0 | 4.38 | 0.000993 | -0.0326 |  | LF | AllSpc | 4230 | 0.838 | 4230 | 0.838 | 1.04 | 1.18 | -0.0077069 | 4230 | 0.838 | 4230 | 0.838 | 1.04 | 1.18 | -0.00771
LFAllSpcPGERtLNewCZ11 | Com-Iltg-dWatt-LF_OSspc | PGE | RtL | New | CZ11 | 4.23 | 0.000838 | 0 | 4.56 | 0.00105 | -0.0304 | 4.23 | 0.000838 | 0 | 4.56 | 0.00105 | -0.0304 |  | LF | AllSpc | 4230 | 0.838 | 4230 | 0.838 | 1.08 | 1.25 | -0.0071868 | 4230 | 0.838 | 4230 | 0.838 | 1.08 | 1.25 | -0.00719
LFAllSpcPGERtLNewCZ12 | Com-Iltg-dWatt-LF_OSspc | PGE | RtL | New | CZ12 | 4.23 | 0.000838 | 0 | 4.54 | 0.00106 | -0.0298 | 4.23 | 0.000838 | 0 | 4.54 | 0.00106 | -0.0298 |  | LF | AllSpc | 4230 | 0.838 | 4230 | 0.838 | 1.07 | 1.26 | -0.0070449 | 4230 | 0.838 | 4230 | 0.838 | 1.07 | 1.26 | -0.00704
LFAllSpcPGERtLNewCZ13 | Com-Iltg-dWatt-LF_OSspc | PGE | RtL | New | CZ13 | 4.23 | 0.000838 | 0 | 4.59 | 0.00105 | -0.0284 | 4.23 | 0.000838 | 0 | 4.59 | 0.00105 | -0.0284 |  | LF | AllSpc | 4230 | 0.838 | 4230 | 0.838 | 1.09 | 1.25 | -0.0067139 | 4230 | 0.838 | 4230 | 0.838 | 1.09 | 1.25 | -0.00671
LFAllSpcPGERtLNewCZ16 | Com-Iltg-dWatt-LF_OSspc | PGE | RtL | New | CZ16 | 4.23 | 0.000838 | 0 | 4.17 | 0.001 | -0.0613 | 4.23 | 0.000838 | 0 | 4.17 | 0.001 | -0.0613 |  | LF | AllSpc | 4230 | 0.838 | 4230 | 0.838 | 0.986 | 1.19 | -0.014492 | 4230 | 0.838 | 4230 | 0.838 | 0.986 | 1.19 | -0.0145
LFAllSpcPGERtLNewIOU | Com-Iltg-dWatt-LF_OSspc | PGE | RtL | New | IOU | 4.23 | 0.000838 | 0 | 4.4902 | 0.0010376 | -0.02994 | 4.23 | 0.000838 | 0 | 4.4902 | 0.0010376 | -0.02994 |  | LF | AllSpc | 4230 | 0.838 | 4230 | 0.838 | 1.06 | 1.24 | -0.0070779 | 4230 | 0.838 | 4230 | 0.838 | 1.06 | 1.24 | -0.00708
LFAllSpcPGERtSExCZ01 | Com-Iltg-dWatt-LF_OSspc | PGE | RtS | Ex | CZ01 | 3.3295 | 0.00086286 | 0 | 3.2495 | 0.00099386 | -0.040291 | 3.3295 | 0.00086286 | 0 | 3.2495 | 0.00099386 | -0.040291 |  | LF | AllSpc | 3330 | 0.863 | 3330 | 0.863 | 0.976 | 1.15 | -0.012101 | 3330 | 0.863 | 3330 | 0.863 | 0.976 | 1.15 | -0.0121
LFAllSpcPGERtSExCZ02 | Com-Iltg-dWatt-LF_OSspc | PGE | RtS | Ex | CZ02 | 3.3295 | 0.00086285 | 0 | 3.5195 | 0.00101 | -0.021395 | 3.3295 | 0.00086285 | 0 | 3.5195 | 0.00101 | -0.021395 |  | LF | AllSpc | 3330 | 0.863 | 3330 | 0.863 | 1.06 | 1.17 | -0.0064259 | 3330 | 0.863 | 3330 | 0.863 | 1.06 | 1.17 | -0.00643
LFAllSpcPGERtSExCZ03 | Com-Iltg-dWatt-LF_OSspc | PGE | RtS | Ex | CZ03 | 3.3296 | 0.00086287 | 0 | 3.5196 | 0.00102 | -0.019895 | 3.3296 | 0.00086287 | 0 | 3.5196 | 0.00102 | -0.019895 |  | LF | AllSpc | 3330 | 0.863 | 3330 | 0.863 | 1.06 | 1.18 | -0.0059754 | 3330 | 0.863 | 3330 | 0.863 | 1.06 | 1.18 | -0.00598
LFAllSpcPGERtSExCZ04 | Com-Iltg-dWatt-LF_OSspc | PGE | RtS | Ex | CZ04 | 3.3295 | 0.00086285 | 0 | 3.5895 | 0.00102 | -0.0144 | 3.3295 | 0.00086285 | 0 | 3.5895 | 0.00102 | -0.0144 |  | LF | AllSpc | 3330 | 0.863 | 3330 | 0.863 | 1.08 | 1.18 | -0.004325 | 3330 | 0.863 | 3330 | 0.863 | 1.08 | 1.18 | -0.00433
LFAllSpcPGERtSExCZ05 | Com-Iltg-dWatt-LF_OSspc | PGE | RtS | Ex | CZ05 | 3.3295 | 0.00086285 | 0 | 3.5295 | 0.001 | -0.0164 | 3.3295 | 0.00086285 | 0 | 3.5295 | 0.001 | -0.0164 |  | LF | AllSpc | 3330 | 0.863 | 3330 | 0.863 | 1.06 | 1.16 | -0.0049257 | 3330 | 0.863 | 3330 | 0.863 | 1.06 | 1.16 | -0.00493
LFAllSpcPGERtSExCZ11 | Com-Iltg-dWatt-LF_OSspc | PGE | RtS | Ex | CZ11 | 3.3293 | 0.00086279 | 0 | 3.5393 | 0.00103 | -0.020593 | 3.3293 | 0.00086279 | 0 | 3.5393 | 0.00103 | -0.020593 |  | LF | AllSpc | 3330 | 0.863 | 3330 | 0.863 | 1.06 | 1.19 | -0.0061854 | 3330 | 0.863 | 3330 | 0.863 | 1.06 | 1.19 | -0.00619
LFAllSpcPGERtSExCZ12 | Com-Iltg-dWatt-LF_OSspc | PGE | RtS | Ex | CZ12 | 3.3294 | 0.00086281 | 0 | 3.5294 | 0.00103 | -0.0207 | 3.3294 | 0.00086281 | 0 | 3.5294 | 0.00103 | -0.0207 |  | LF | AllSpc | 3330 | 0.863 | 3330 | 0.863 | 1.06 | 1.19 | -0.0062174 | 3330 | 0.863 | 3330 | 0.863 | 1.06 | 1.19 | -0.00622
LFAllSpcPGERtSExCZ13 | Com-Iltg-dWatt-LF_OSspc | PGE | RtS | Ex | CZ13 | 3.3293 | 0.00086279 | 0 | 3.5493 | 0.00102 | -0.019393 | 3.3293 | 0.00086279 | 0 | 3.5493 | 0.00102 | -0.019393 |  | LF | AllSpc | 3330 | 0.863 | 3330 | 0.863 | 1.07 | 1.18 | -0.0058249 | 3330 | 0.863 | 3330 | 0.863 | 1.07 | 1.18 | -0.00582
LFAllSpcPGERtSExCZ16 | Com-Iltg-dWatt-LF_OSspc | PGE | RtS | Ex | CZ16 | 3.3294 | 0.00086283 | 0 | 3.2794 | 0.001 | -0.039289 | 3.3294 | 0.00086283 | 0 | 3.2794 | 0.001 | -0.039289 |  | LF | AllSpc | 3330 | 0.863 | 3330 | 0.863 | 0.985 | 1.16 | -0.0118 | 3330 | 0.863 | 3330 | 0.863 | 0.985 | 1.16 | -0.0118
LFAllSpcPGERtSExIOU | Com-Iltg-dWatt-LF_OSspc | PGE | RtS | Ex | IOU | 3.3294 | 0.00086283 | 0 | 3.5337 | 0.0010214 | -0.019568 | 3.3294 | 0.00086283 | 0 | 3.5337 | 0.0010214 | -0.019568 |  | LF | AllSpc | 3330 | 0.863 | 3330 | 0.863 | 1.06 | 1.18 | -0.0058773 | 3330 | 0.863 | 3330 | 0.863 | 1.06 | 1.18 | -0.00588
LFAllSpcPGERtSNewCZ01 | Com-Iltg-dWatt-LF_OSspc | PGE | RtS | New | CZ01 | 3.32 | 0.00086 | 0 | 3.24 | 0.000979 | -0.0451 | 3.32 | 0.00086 | 0 | 3.24 | 0.000979 | -0.0451 |  | LF | AllSpc | 3320 | 0.86 | 3320 | 0.86 | 0.976 | 1.14 | -0.013584 | 3320 | 0.86 | 3320 | 0.86 | 0.976 | 1.14 | -0.0136
LFAllSpcPGERtSNewCZ02 | Com-Iltg-dWatt-LF_OSspc | PGE | RtS | New | CZ02 | 3.32 | 0.00086 | 0 | 3.49 | 0.00104 | -0.0236 | 3.32 | 0.00086 | 0 | 3.49 | 0.00104 | -0.0236 |  | LF | AllSpc | 3320 | 0.86 | 3320 | 0.86 | 1.05 | 1.21 | -0.0071084 | 3320 | 0.86 | 3320 | 0.86 | 1.05 | 1.21 | -0.00711
LFAllSpcPGERtSNewCZ03 | Com-Iltg-dWatt-LF_OSspc | PGE | RtS | New | CZ03 | 3.32 | 0.00086 | 0 | 3.37 | 0.000986 | -0.0217 | 3.32 | 0.00086 | 0 | 3.37 | 0.000986 | -0.0217 |  | LF | AllSpc | 3320 | 0.86 | 3320 | 0.86 | 1.02 | 1.15 | -0.0065361 | 3320 | 0.86 | 3320 | 0.86 | 1.02 | 1.15 | -0.00654
LFAllSpcPGERtSNewCZ04 | Com-Iltg-dWatt-LF_OSspc | PGE | RtS | New | CZ04 | 3.32 | 0.00086 | 0 | 3.54 | 0.00102 | -0.0163 | 3.32 | 0.00086 | 0 | 3.54 | 0.00102 | -0.0163 |  | LF | AllSpc | 3320 | 0.86 | 3320 | 0.86 | 1.07 | 1.19 | -0.0049096 | 3320 | 0.86 | 3320 | 0.86 | 1.07 | 1.19 | -0.00491
LFAllSpcPGERtSNewCZ05 | Com-Iltg-dWatt-LF_OSspc | PGE | RtS | New | CZ05 | 3.32 | 0.00086 | 0 | 3.45 | 0.000996 | -0.0189 | 3.32 | 0.00086 | 0 | 3.45 | 0.000996 | -0.0189 |  | LF | AllSpc | 3320 | 0.86 | 3320 | 0.86 | 1.04 | 1.16 | -0.0056928 | 3320 | 0.86 | 3320 | 0.86 | 1.04 | 1.16 | -0.00569
LFAllSpcPGERtSNewCZ11 | Com-Iltg-dWatt-LF_OSspc | PGE | RtS | New | CZ11 | 3.32 | 0.00086 | 0 | 3.58 | 0.00105 | -0.0204 | 3.32 | 0.00086 | 0 | 3.58 | 0.00105 | -0.0204 |  | LF | AllSpc | 3320 | 0.86 | 3320 | 0.86 | 1.08 | 1.22 | -0.0061446 | 3320 | 0.86 | 3320 | 0.86 | 1.08 | 1.22 | -0.00614
LFAllSpcPGERtSNewCZ12 | Com-Iltg-dWatt-LF_OSspc | PGE | RtS | New | CZ12 | 3.32 | 0.00086 | 0 | 3.55 | 0.00104 | -0.0219 | 3.32 | 0.00086 | 0 | 3.55 | 0.00104 | -0.0219 |  | LF | AllSpc | 3320 | 0.86 | 3320 | 0.86 | 1.07 | 1.21 | -0.0065964 | 3320 | 0.86 | 3320 | 0.86 | 1.07 | 1.21 | -0.0066
LFAllSpcPGERtSNewCZ13 | Com-Iltg-dWatt-LF_OSspc | PGE | RtS | New | CZ13 | 3.32 | 0.00086 | 0 | 3.57 | 0.00104 | -0.02 | 3.32 | 0.00086 | 0 | 3.57 | 0.00104 | -0.02 |  | LF | AllSpc | 3320 | 0.86 | 3320 | 0.86 | 1.08 | 1.21 | -0.0060241 | 3320 | 0.86 | 3320 | 0.86 | 1.08 | 1.21 | -0.00602
LFAllSpcPGERtSNewCZ16 | Com-Iltg-dWatt-LF_OSspc | PGE | RtS | New | CZ16 | 3.32 | 0.00086 | 0 | 3.28 | 0.00101 | -0.0418 | 3.32 | 0.00086 | 0 | 3.28 | 0.00101 | -0.0418 |  | LF | AllSpc | 3320 | 0.86 | 3320 | 0.86 | 0.988 | 1.17 | -0.01259 | 3320 | 0.86 | 3320 | 0.86 | 0.988 | 1.17 | -0.0126
LFAllSpcPGERtSNewIOU | Com-Iltg-dWatt-LF_OSspc | PGE | RtS | New | IOU | 3.32 | 0.00086 | 0 | 3.4981 | 0.0010225 | -0.020977 | 3.32 | 0.00086 | 0 | 3.4981 | 0.0010225 | -0.020977 |  | LF | AllSpc | 3320 | 0.86 | 3320 | 0.86 | 1.05 | 1.19 | -0.0063184 | 3320 | 0.86 | 3320 | 0.86 | 1.05 | 1.19 | -0.00632
LFAllSpcPGESCnExCZ01 | Com-Iltg-dWatt-LF_OSspc | PGE | SCn | Ex | CZ01 | 3.14 | 0.000588 | 0 | 2.65 | 0.000588 | -0.0534 | 3.14 | 0.000588 | 0 | 2.65 | 0.000588 | -0.0534 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 0.844 | 1 | -0.017006 | 3140 | 0.588 | 3140 | 0.588 | 0.844 | 1 | -0.017
LFAllSpcPGESCnExCZ02 | Com-Iltg-dWatt-LF_OSspc | PGE | SCn | Ex | CZ02 | 3.14 | 0.000588 | 0 | 3 | 0.000741 | -0.0287 | 3.14 | 0.000588 | 0 | 3 | 0.000741 | -0.0287 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 0.955 | 1.26 | -0.0091401 | 3140 | 0.588 | 3140 | 0.588 | 0.955 | 1.26 | -0.00914
LFAllSpcPGESCnExCZ03 | Com-Iltg-dWatt-LF_OSspc | PGE | SCn | Ex | CZ03 | 3.14 | 0.000588 | 0 | 2.89 | 0.000788 | -0.0317 | 3.14 | 0.000588 | 0 | 2.89 | 0.000788 | -0.0317 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 0.92 | 1.34 | -0.010096 | 3140 | 0.588 | 3140 | 0.588 | 0.92 | 1.34 | -0.0101
LFAllSpcPGESCnExCZ04 | Com-Iltg-dWatt-LF_OSspc | PGE | SCn | Ex | CZ04 | 3.14 | 0.000588 | 0 | 3.08 | 0.00074 | -0.0252 | 3.14 | 0.000588 | 0 | 3.08 | 0.00074 | -0.0252 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 0.981 | 1.26 | -0.0080255 | 3140 | 0.588 | 3140 | 0.588 | 0.981 | 1.26 | -0.00803
LFAllSpcPGESCnExCZ05 | Com-Iltg-dWatt-LF_OSspc | PGE | SCn | Ex | CZ05 | 3.14 | 0.000588 | 0 | 2.86 | 0.000707 | -0.032 | 3.14 | 0.000588 | 0 | 2.86 | 0.000707 | -0.032 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 0.911 | 1.2 | -0.010191 | 3140 | 0.588 | 3140 | 0.588 | 0.911 | 1.2 | -0.0102
LFAllSpcPGESCnExCZ11 | Com-Iltg-dWatt-LF_OSspc | PGE | SCn | Ex | CZ11 | 3.14 | 0.000588 | 0 | 3.07 | 0.00072 | -0.0263 | 3.14 | 0.000588 | 0 | 3.07 | 0.00072 | -0.0263 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 0.978 | 1.22 | -0.0083758 | 3140 | 0.588 | 3140 | 0.588 | 0.978 | 1.22 | -0.00838
LFAllSpcPGESCnExCZ12 | Com-Iltg-dWatt-LF_OSspc | PGE | SCn | Ex | CZ12 | 3.14 | 0.000588 | 0 | 3.08 | 0.000731 | -0.0264 | 3.14 | 0.000588 | 0 | 3.08 | 0.000731 | -0.0264 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 0.981 | 1.24 | -0.0084076 | 3140 | 0.588 | 3140 | 0.588 | 0.981 | 1.24 | -0.00841
LFAllSpcPGESCnExCZ13 | Com-Iltg-dWatt-LF_OSspc | PGE | SCn | Ex | CZ13 | 3.14 | 0.000588 | 0 | 3.11 | 0.000717 | -0.0236 | 3.14 | 0.000588 | 0 | 3.11 | 0.000717 | -0.0236 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 0.99 | 1.22 | -0.0075159 | 3140 | 0.588 | 3140 | 0.588 | 0.99 | 1.22 | -0.00752
LFAllSpcPGESCnExCZ16 | Com-Iltg-dWatt-LF_OSspc | PGE | SCn | Ex | CZ16 | 3.14 | 0.000588 | 0 | 2.78 | 0.000704 | -0.037 | 3.14 | 0.000588 | 0 | 2.78 | 0.000704 | -0.037 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 0.885 | 1.2 | -0.011783 | 3140 | 0.588 | 3140 | 0.588 | 0.885 | 1.2 | -0.0118
LFAllSpcPGESCnExIOU | Com-Iltg-dWatt-LF_OSspc | PGE | SCn | Ex | IOU | 3.14 | 0.000588 | 0 | 3.0056 | 0.00074801 | -0.028155 | 3.14 | 0.000588 | 0 | 3.0056 | 0.00074801 | -0.028155 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 0.957 | 1.27 | -0.0089665 | 3140 | 0.588 | 3140 | 0.588 | 0.957 | 1.27 | -0.00897
LFAllSpcPGESCnNewCZ01 | Com-Iltg-dWatt-LF_OSspc | PGE | SCn | New | CZ01 | 3.14 | 0.000588 | 0 | 2.69 | 0.000588 | -0.0571 | 3.14 | 0.000588 | 0 | 2.69 | 0.000588 | -0.0571 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 0.857 | 1 | -0.018185 | 3140 | 0.588 | 3140 | 0.588 | 0.857 | 1 | -0.0182
LFAllSpcPGESCnNewCZ02 | Com-Iltg-dWatt-LF_OSspc | PGE | SCn | New | CZ02 | 3.14 | 0.000588 | 0 | 2.99 | 0.000717 | -0.0298 | 3.14 | 0.000588 | 0 | 2.99 | 0.000717 | -0.0298 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 0.952 | 1.22 | -0.0094904 | 3140 | 0.588 | 3140 | 0.588 | 0.952 | 1.22 | -0.00949
LFAllSpcPGESCnNewCZ03 | Com-Iltg-dWatt-LF_OSspc | PGE | SCn | New | CZ03 | 3.14 | 0.000588 | 0 | 2.9 | 0.000738 | -0.0336 | 3.14 | 0.000588 | 0 | 2.9 | 0.000738 | -0.0336 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 0.924 | 1.26 | -0.010701 | 3140 | 0.588 | 3140 | 0.588 | 0.924 | 1.26 | -0.0107
LFAllSpcPGESCnNewCZ04 | Com-Iltg-dWatt-LF_OSspc | PGE | SCn | New | CZ04 | 3.14 | 0.000588 | 0 | 3.06 | 0.00071 | -0.0266 | 3.14 | 0.000588 | 0 | 3.06 | 0.00071 | -0.0266 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 0.975 | 1.21 | -0.0084713 | 3140 | 0.588 | 3140 | 0.588 | 0.975 | 1.21 | -0.00847
LFAllSpcPGESCnNewCZ05 | Com-Iltg-dWatt-LF_OSspc | PGE | SCn | New | CZ05 | 3.14 | 0.000588 | 0 | 2.88 | 0.000706 | -0.0336 | 3.14 | 0.000588 | 0 | 2.88 | 0.000706 | -0.0336 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 0.917 | 1.2 | -0.010701 | 3140 | 0.588 | 3140 | 0.588 | 0.917 | 1.2 | -0.0107
LFAllSpcPGESCnNewCZ11 | Com-Iltg-dWatt-LF_OSspc | PGE | SCn | New | CZ11 | 3.14 | 0.000588 | 0 | 3.06 | 0.000703 | -0.0273 | 3.14 | 0.000588 | 0 | 3.06 | 0.000703 | -0.0273 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 0.975 | 1.2 | -0.0086943 | 3140 | 0.588 | 3140 | 0.588 | 0.975 | 1.2 | -0.00869
LFAllSpcPGESCnNewCZ12 | Com-Iltg-dWatt-LF_OSspc | PGE | SCn | New | CZ12 | 3.14 | 0.000588 | 0 | 3.07 | 0.000707 | -0.0275 | 3.14 | 0.000588 | 0 | 3.07 | 0.000707 | -0.0275 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 0.978 | 1.2 | -0.008758 | 3140 | 0.588 | 3140 | 0.588 | 0.978 | 1.2 | -0.00876
LFAllSpcPGESCnNewCZ13 | Com-Iltg-dWatt-LF_OSspc | PGE | SCn | New | CZ13 | 3.14 | 0.000588 | 0 | 3.05 | 0.000687 | -0.0239 | 3.14 | 0.000588 | 0 | 3.05 | 0.000687 | -0.0239 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 0.971 | 1.17 | -0.0076115 | 3140 | 0.588 | 3140 | 0.588 | 0.971 | 1.17 | -0.00761
LFAllSpcPGESCnNewCZ16 | Com-Iltg-dWatt-LF_OSspc | PGE | SCn | New | CZ16 | 3.14 | 0.000588 | 0 | 2.78 | 0.000683 | -0.0389 | 3.14 | 0.000588 | 0 | 2.78 | 0.000683 | -0.0389 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 0.885 | 1.16 | -0.012389 | 3140 | 0.588 | 3140 | 0.588 | 0.885 | 1.16 | -0.0124
LFAllSpcPGESCnNewIOU | Com-Iltg-dWatt-LF_OSspc | PGE | SCn | New | IOU | 3.14 | 0.000588 | 0 | 3.0138 | 0.00070951 | -0.028601 | 3.14 | 0.000588 | 0 | 3.0138 | 0.00070951 | -0.028601 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 0.96 | 1.21 | -0.0091085 | 3140 | 0.588 | 3140 | 0.588 | 0.96 | 1.21 | -0.00911
LFAllSpcPGESUnExCZ01 | Com-Iltg-dWatt-LF_OSspc | PGE | SUn | Ex | CZ01 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0 | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0
LFAllSpcPGESUnExCZ02 | Com-Iltg-dWatt-LF_OSspc | PGE | SUn | Ex | CZ02 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0 | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0
LFAllSpcPGESUnExCZ03 | Com-Iltg-dWatt-LF_OSspc | PGE | SUn | Ex | CZ03 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0 | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0
LFAllSpcPGESUnExCZ04 | Com-Iltg-dWatt-LF_OSspc | PGE | SUn | Ex | CZ04 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0 | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0
LFAllSpcPGESUnExCZ05 | Com-Iltg-dWatt-LF_OSspc | PGE | SUn | Ex | CZ05 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0 | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0
LFAllSpcPGESUnExCZ11 | Com-Iltg-dWatt-LF_OSspc | PGE | SUn | Ex | CZ11 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0 | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0
LFAllSpcPGESUnExCZ12 | Com-Iltg-dWatt-LF_OSspc | PGE | SUn | Ex | CZ12 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0 | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0
LFAllSpcPGESUnExCZ13 | Com-Iltg-dWatt-LF_OSspc | PGE | SUn | Ex | CZ13 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0 | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0
LFAllSpcPGESUnExCZ16 | Com-Iltg-dWatt-LF_OSspc | PGE | SUn | Ex | CZ16 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0 | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0
LFAllSpcPGESUnExIOU | Com-Iltg-dWatt-LF_OSspc | PGE | SUn | Ex | IOU | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0 | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0
LFAllSpcPGESUnNewCZ01 | Com-Iltg-dWatt-LF_OSspc | PGE | SUn | New | CZ01 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0 | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0
LFAllSpcPGESUnNewCZ02 | Com-Iltg-dWatt-LF_OSspc | PGE | SUn | New | CZ02 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0 | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0
LFAllSpcPGESUnNewCZ03 | Com-Iltg-dWatt-LF_OSspc | PGE | SUn | New | CZ03 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0 | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0
LFAllSpcPGESUnNewCZ04 | Com-Iltg-dWatt-LF_OSspc | PGE | SUn | New | CZ04 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0 | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0
LFAllSpcPGESUnNewCZ05 | Com-Iltg-dWatt-LF_OSspc | PGE | SUn | New | CZ05 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0 | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0
LFAllSpcPGESUnNewCZ11 | Com-Iltg-dWatt-LF_OSspc | PGE | SUn | New | CZ11 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0 | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0
LFAllSpcPGESUnNewCZ12 | Com-Iltg-dWatt-LF_OSspc | PGE | SUn | New | CZ12 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0 | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0
LFAllSpcPGESUnNewCZ13 | Com-Iltg-dWatt-LF_OSspc | PGE | SUn | New | CZ13 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0 | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0
LFAllSpcPGESUnNewCZ16 | Com-Iltg-dWatt-LF_OSspc | PGE | SUn | New | CZ16 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0 | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0
LFAllSpcPGESUnNewIOU | Com-Iltg-dWatt-LF_OSspc | PGE | SUn | New | IOU | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0 | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0
LFAllSpcPGEWRfExCZ01 | Com-Iltg-dWatt-LF_OSspc | PGE | WRf | Ex | CZ01 | 3.13 | 0.000473 | 0 | 4.8394 | 0.000655 | 0 | 3.13 | 0.000473 | 0 | 4.8394 | 0.000655 | 0 |  | LF | AllSpc | 3130 | 0.473 | 3130 | 0.473 | 1.55 | 1.38 | 0 | 3130 | 0.473 | 3130 | 0.473 | 1.55 | 1.38 | 0
LFAllSpcPGEWRfExCZ02 | Com-Iltg-dWatt-LF_OSspc | PGE | WRf | Ex | CZ02 | 3.13 | 0.000473 | 0 | 4.9694 | 0.000612 | 0 | 3.13 | 0.000473 | 0 | 4.9694 | 0.000612 | 0 |  | LF | AllSpc | 3130 | 0.473 | 3130 | 0.473 | 1.59 | 1.29 | 0 | 3130 | 0.473 | 3130 | 0.473 | 1.59 | 1.29 | 0
LFAllSpcPGEWRfExCZ03 | Com-Iltg-dWatt-LF_OSspc | PGE | WRf | Ex | CZ03 | 3.13 | 0.000473 | 0 | 5.1095 | 0.000625 | 0 | 3.13 | 0.000473 | 0 | 5.1095 | 0.000625 | 0 |  | LF | AllSpc | 3130 | 0.473 | 3130 | 0.473 | 1.63 | 1.32 | 0 | 3130 | 0.473 | 3130 | 0.473 | 1.63 | 1.32 | 0
LFAllSpcPGEWRfExCZ04 | Com-Iltg-dWatt-LF_OSspc | PGE | WRf | Ex | CZ04 | 3.13 | 0.000473 | 0 | 5.0595 | 0.000623 | 0 | 3.13 | 0.000473 | 0 | 5.0595 | 0.000623 | 0 |  | LF | AllSpc | 3130 | 0.473 | 3130 | 0.473 | 1.62 | 1.32 | 0 | 3130 | 0.473 | 3130 | 0.473 | 1.62 | 1.32 | 0
LFAllSpcPGEWRfExCZ05 | Com-Iltg-dWatt-LF_OSspc | PGE | WRf | Ex | CZ05 | 3.13 | 0.000473 | 0 | 4.9595 | 0.00061 | 0 | 3.13 | 0.000473 | 0 | 4.9595 | 0.00061 | 0 |  | LF | AllSpc | 3130 | 0.473 | 3130 | 0.473 | 1.58 | 1.29 | 0 | 3130 | 0.473 | 3130 | 0.473 | 1.58 | 1.29 | 0
LFAllSpcPGEWRfExCZ11 | Com-Iltg-dWatt-LF_OSspc | PGE | WRf | Ex | CZ11 | 3.13 | 0.000473 | 0 | 4.839 | 0.000653 | 0 | 3.13 | 0.000473 | 0 | 4.839 | 0.000653 | 0 |  | LF | AllSpc | 3130 | 0.473 | 3130 | 0.473 | 1.55 | 1.38 | 0 | 3130 | 0.473 | 3130 | 0.473 | 1.55 | 1.38 | 0
LFAllSpcPGEWRfExCZ12 | Com-Iltg-dWatt-LF_OSspc | PGE | WRf | Ex | CZ12 | 3.13 | 0.000473 | 0 | 4.9088 | 0.000628 | 0 | 3.13 | 0.000473 | 0 | 4.9088 | 0.000628 | 0 |  | LF | AllSpc | 3130 | 0.473 | 3130 | 0.473 | 1.57 | 1.33 | 0 | 3130 | 0.473 | 3130 | 0.473 | 1.57 | 1.33 | 0
LFAllSpcPGEWRfExCZ13 | Com-Iltg-dWatt-LF_OSspc | PGE | WRf | Ex | CZ13 | 3.13 | 0.000473 | 0 | 4.8991 | 0.000596 | 0 | 3.13 | 0.000473 | 0 | 4.8991 | 0.000596 | 0 |  | LF | AllSpc | 3130 | 0.473 | 3130 | 0.473 | 1.57 | 1.26 | 0 | 3130 | 0.473 | 3130 | 0.473 | 1.57 | 1.26 | 0
LFAllSpcPGEWRfExCZ16 | Com-Iltg-dWatt-LF_OSspc | PGE | WRf | Ex | CZ16 | 3.13 | 0.000473 | 0 | 4.349 | 0.000655 | -0.0002219 | 3.13 | 0.000473 | 0 | 4.349 | 0.000655 | -0.0002219 |  | LF | AllSpc | 3130 | 0.473 | 3130 | 0.473 | 1.39 | 1.38 | -7.0895e-05 | 3130 | 0.473 | 3130 | 0.473 | 1.39 | 1.38 | -7.09e-05
LFAllSpcPGEWRfExIOU | Com-Iltg-dWatt-LF_OSspc | PGE | WRf | Ex | IOU | 3.13 | 0.000473 | 0 | 4.9833 | 0.00061752 | -8.6579e-08 | 3.13 | 0.000473 | 0 | 4.9833 | 0.00061752 | -8.6579e-08 |  | LF | AllSpc | 3130 | 0.473 | 3130 | 0.473 | 1.59 | 1.31 | -2.7661e-08 | 3130 | 0.473 | 3130 | 0.473 | 1.59 | 1.31 | -2.77e-08
LFAllSpcPGEWRfNewCZ01 | Com-Iltg-dWatt-LF_OSspc | PGE | WRf | New | CZ01 | 3.13 | 0.000473 | 0 | 3.97 | 0.000589 | 0 | 3.13 | 0.000473 | 0 | 3.97 | 0.000589 | 0 |  | LF | AllSpc | 3130 | 0.473 | 3130 | 0.473 | 1.27 | 1.25 | 0 | 3130 | 0.473 | 3130 | 0.473 | 1.27 | 1.25 | 0
LFAllSpcPGEWRfNewCZ02 | Com-Iltg-dWatt-LF_OSspc | PGE | WRf | New | CZ02 | 3.13 | 0.000473 | 0 | 4.27 | 0.000772 | 0 | 3.13 | 0.000473 | 0 | 4.27 | 0.000772 | 0 |  | LF | AllSpc | 3130 | 0.473 | 3130 | 0.473 | 1.36 | 1.63 | 0 | 3130 | 0.473 | 3130 | 0.473 | 1.36 | 1.63 | 0
LFAllSpcPGEWRfNewCZ03 | Com-Iltg-dWatt-LF_OSspc | PGE | WRf | New | CZ03 | 3.13 | 0.000473 | 0 | 4.13 | 0.000945 | 0 | 3.13 | 0.000473 | 0 | 4.13 | 0.000945 | 0 |  | LF | AllSpc | 3130 | 0.473 | 3130 | 0.473 | 1.32 | 2 | 0 | 3130 | 0.473 | 3130 | 0.473 | 1.32 | 2 | 0
LFAllSpcPGEWRfNewCZ04 | Com-Iltg-dWatt-LF_OSspc | PGE | WRf | New | CZ04 | 3.13 | 0.000473 | 0 | 4.36 | 0.000945 | 0 | 3.13 | 0.000473 | 0 | 4.36 | 0.000945 | 0 |  | LF | AllSpc | 3130 | 0.473 | 3130 | 0.473 | 1.39 | 2 | 0 | 3130 | 0.473 | 3130 | 0.473 | 1.39 | 2 | 0
LFAllSpcPGEWRfNewCZ05 | Com-Iltg-dWatt-LF_OSspc | PGE | WRf | New | CZ05 | 3.13 | 0.000473 | 0 | 4.04 | 0.000785 | 0 | 3.13 | 0.000473 | 0 | 4.04 | 0.000785 | 0 |  | LF | AllSpc | 3130 | 0.473 | 3130 | 0.473 | 1.29 | 1.66 | 0 | 3130 | 0.473 | 3130 | 0.473 | 1.29 | 1.66 | 0
LFAllSpcPGEWRfNewCZ11 | Com-Iltg-dWatt-LF_OSspc | PGE | WRf | New | CZ11 | 3.13 | 0.000473 | 0 | 4.31 | 0.000945 | 0 | 3.13 | 0.000473 | 0 | 4.31 | 0.000945 | 0 |  | LF | AllSpc | 3130 | 0.473 | 3130 | 0.473 | 1.38 | 2 | 0 | 3130 | 0.473 | 3130 | 0.473 | 1.38 | 2 | 0
LFAllSpcPGEWRfNewCZ12 | Com-Iltg-dWatt-LF_OSspc | PGE | WRf | New | CZ12 | 3.13 | 0.000473 | 0 | 4.35 | 0.00078 | 0 | 3.13 | 0.000473 | 0 | 4.35 | 0.00078 | 0 |  | LF | AllSpc | 3130 | 0.473 | 3130 | 0.473 | 1.39 | 1.65 | 0 | 3130 | 0.473 | 3130 | 0.473 | 1.39 | 1.65 | 0
LFAllSpcPGEWRfNewCZ13 | Com-Iltg-dWatt-LF_OSspc | PGE | WRf | New | CZ13 | 3.13 | 0.000473 | 0 | 4.39 | 0.000591 | 0 | 3.13 | 0.000473 | 0 | 4.39 | 0.000591 | 0 |  | LF | AllSpc | 3130 | 0.473 | 3130 | 0.473 | 1.4 | 1.25 | 0 | 3130 | 0.473 | 3130 | 0.473 | 1.4 | 1.25 | 0
LFAllSpcPGEWRfNewCZ16 | Com-Iltg-dWatt-LF_OSspc | PGE | WRf | New | CZ16 | 3.13 | 0.000473 | 0 | 3.94 | 0.000945 | 0 | 3.13 | 0.000473 | 0 | 3.94 | 0.000945 | 0 |  | LF | AllSpc | 3130 | 0.473 | 3130 | 0.473 | 1.26 | 2 | 0 | 3130 | 0.473 | 3130 | 0.473 | 1.26 | 2 | 0
LFAllSpcPGEWRfNewIOU | Com-Iltg-dWatt-LF_OSspc | PGE | WRf | New | IOU | 3.13 | 0.000473 | 0 | 4.3029 | 0.00076875 | 0 | 3.13 | 0.000473 | 0 | 4.3029 | 0.00076875 | 0 |  | LF | AllSpc | 3130 | 0.473 | 3130 | 0.473 | 1.37 | 1.63 | 0 | 3130 | 0.473 | 3130 | 0.473 | 1.37 | 1.63 | 0
LFAllSpcSCEAsmExCZ05 | Com-Iltg-dWatt-LF_OSspc | SCE | Asm | Ex | CZ05 | 2.2206 | 0.00043194 | 0 | 2.34 | 0.00051689 | -0.0229 | 2.2206 | 0.00043194 | 0 | 2.34 | 0.00051689 | -0.0229 |  | LF | AllSpc | 2220 | 0.432 | 2220 | 0.432 | 1.05 | 1.2 | -0.010313 | 2220 | 0.432 | 2220 | 0.432 | 1.05 | 1.2 | -0.0103
LFAllSpcSCEAsmExCZ06 | Com-Iltg-dWatt-LF_OSspc | SCE | Asm | Ex | CZ06 | 2.2206 | 0.00043194 | 0 | 2.5 | 0.00053494 | -0.0111 | 2.2206 | 0.00043194 | 0 | 2.5 | 0.00053494 | -0.0111 |  | LF | AllSpc | 2220 | 0.432 | 2220 | 0.432 | 1.13 | 1.24 | -0.0049987 | 2220 | 0.432 | 2220 | 0.432 | 1.13 | 1.24 | -0.005
LFAllSpcSCEAsmExCZ08 | Com-Iltg-dWatt-LF_OSspc | SCE | Asm | Ex | CZ08 | 2.2206 | 0.00043194 | 0 | 2.51 | 0.00052094 | -0.0095517 | 2.2206 | 0.00043194 | 0 | 2.51 | 0.00052094 | -0.0095517 |  | LF | AllSpc | 2220 | 0.432 | 2220 | 0.432 | 1.13 | 1.21 | -0.0043015 | 2220 | 0.432 | 2220 | 0.432 | 1.13 | 1.21 | -0.0043
LFAllSpcSCEAsmExCZ09 | Com-Iltg-dWatt-LF_OSspc | SCE | Asm | Ex | CZ09 | 2.2206 | 0.00043194 | 0 | 2.4906 | 0.00053494 | -0.0116 | 2.2206 | 0.00043194 | 0 | 2.4906 | 0.00053494 | -0.0116 |  | LF | AllSpc | 2220 | 0.432 | 2220 | 0.432 | 1.12 | 1.24 | -0.0052239 | 2220 | 0.432 | 2220 | 0.432 | 1.12 | 1.24 | -0.00522
LFAllSpcSCEAsmExCZ10 | Com-Iltg-dWatt-LF_OSspc | SCE | Asm | Ex | CZ10 | 2.2214 | 0.00043186 | 0 | 2.4214 | 0.00051672 | -0.012714 | 2.2214 | 0.00043186 | 0 | 2.4214 | 0.00051672 | -0.012714 |  | LF | AllSpc | 2220 | 0.432 | 2220 | 0.432 | 1.09 | 1.2 | -0.0057234 | 2220 | 0.432 | 2220 | 0.432 | 1.09 | 1.2 | -0.00572
LFAllSpcSCEAsmExCZ13 | Com-Iltg-dWatt-LF_OSspc | SCE | Asm | Ex | CZ13 | 2.2209 | 0.00043191 | 0 | 2.38 | 0.00052191 | -0.020109 | 2.2209 | 0.00043191 | 0 | 2.38 | 0.00052191 | -0.020109 |  | LF | AllSpc | 2220 | 0.432 | 2220 | 0.432 | 1.07 | 1.21 | -0.0090544 | 2220 | 0.432 | 2220 | 0.432 | 1.07 | 1.21 | -0.00905
LFAllSpcSCEAsmExCZ14 | Com-Iltg-dWatt-LF_OSspc | SCE | Asm | Ex | CZ14 | 2.221 | 0.0004319 | 0 | 2.381 | 0.0004889 | -0.0201 | 2.221 | 0.0004319 | 0 | 2.381 | 0.0004889 | -0.0201 |  | LF | AllSpc | 2220 | 0.432 | 2220 | 0.432 | 1.07 | 1.13 | -0.0090498 | 2220 | 0.432 | 2220 | 0.432 | 1.07 | 1.13 | -0.00905
LFAllSpcSCEAsmExCZ15 | Com-Iltg-dWatt-LF_OSspc | SCE | Asm | Ex | CZ15 | 2.2214 | 0.00043186 | 0 | 2.6414 | 0.00051186 | -0.0056914 | 2.2214 | 0.00043186 | 0 | 2.6414 | 0.00051186 | -0.0056914 |  | LF | AllSpc | 2220 | 0.432 | 2220 | 0.432 | 1.19 | 1.19 | -0.0025621 | 2220 | 0.432 | 2220 | 0.432 | 1.19 | 1.19 | -0.00256
LFAllSpcSCEAsmExCZ16 | Com-Iltg-dWatt-LF_OSspc | SCE | Asm | Ex | CZ16 | 2.2211 | 0.00043189 | 0 | 2.1911 | 0.00051189 | -0.031311 | 2.2211 | 0.00043189 | 0 | 2.1911 | 0.00051189 | -0.031311 |  | LF | AllSpc | 2220 | 0.432 | 2220 | 0.432 | 0.986 | 1.19 | -0.014097 | 2220 | 0.432 | 2220 | 0.432 | 0.986 | 1.19 | -0.0141
LFAllSpcSCEAsmExIOU | Com-Iltg-dWatt-LF_OSspc | SCE | Asm | Ex | IOU | 2.2208 | 0.00043192 | 0 | 2.4829 | 0.00052347 | -0.011637 | 2.2208 | 0.00043192 | 0 | 2.4829 | 0.00052347 | -0.011637 |  | LF | AllSpc | 2220 | 0.432 | 2220 | 0.432 | 1.12 | 1.21 | -0.0052401 | 2220 | 0.432 | 2220 | 0.432 | 1.12 | 1.21 | -0.00524
LFAllSpcSCEAsmNewCZ05 | Com-Iltg-dWatt-LF_OSspc | SCE | Asm | New | CZ05 | 2.23 | 0.000431 | 0 | 2.31 | 0.000509 | -0.0236 | 2.23 | 0.000431 | 0 | 2.31 | 0.000509 | -0.0236 |  | LF | AllSpc | 2230 | 0.431 | 2230 | 0.431 | 1.04 | 1.18 | -0.010583 | 2230 | 0.431 | 2230 | 0.431 | 1.04 | 1.18 | -0.0106
LFAllSpcSCEAsmNewCZ06 | Com-Iltg-dWatt-LF_OSspc | SCE | Asm | New | CZ06 | 2.23 | 0.000431 | 0 | 2.42 | 0.000525 | -0.0142 | 2.23 | 0.000431 | 0 | 2.42 | 0.000525 | -0.0142 |  | LF | AllSpc | 2230 | 0.431 | 2230 | 0.431 | 1.09 | 1.22 | -0.0063677 | 2230 | 0.431 | 2230 | 0.431 | 1.09 | 1.22 | -0.00637
LFAllSpcSCEAsmNewCZ08 | Com-Iltg-dWatt-LF_OSspc | SCE | Asm | New | CZ08 | 2.23 | 0.000431 | 0 | 2.44 | 0.000518 | -0.0116 | 2.23 | 0.000431 | 0 | 2.44 | 0.000518 | -0.0116 |  | LF | AllSpc | 2230 | 0.431 | 2230 | 0.431 | 1.09 | 1.2 | -0.0052018 | 2230 | 0.431 | 2230 | 0.431 | 1.09 | 1.2 | -0.0052
LFAllSpcSCEAsmNewCZ09 | Com-Iltg-dWatt-LF_OSspc | SCE | Asm | New | CZ09 | 2.23 | 0.000431 | 0 | 2.42 | 0.000538 | -0.0132 | 2.23 | 0.000431 | 0 | 2.42 | 0.000538 | -0.0132 |  | LF | AllSpc | 2230 | 0.431 | 2230 | 0.431 | 1.09 | 1.25 | -0.0059193 | 2230 | 0.431 | 2230 | 0.431 | 1.09 | 1.25 | -0.00592
LFAllSpcSCEAsmNewCZ10 | Com-Iltg-dWatt-LF_OSspc | SCE | Asm | New | CZ10 | 2.23 | 0.000431 | 0 | 2.43 | 0.000531 | -0.0134 | 2.23 | 0.000431 | 0 | 2.43 | 0.000531 | -0.0134 |  | LF | AllSpc | 2230 | 0.431 | 2230 | 0.431 | 1.09 | 1.23 | -0.006009 | 2230 | 0.431 | 2230 | 0.431 | 1.09 | 1.23 | -0.00601
LFAllSpcSCEAsmNewCZ13 | Com-Iltg-dWatt-LF_OSspc | SCE | Asm | New | CZ13 | 2.23 | 0.000431 | 0 | 2.38 | 0.000533 | -0.0215 | 2.23 | 0.000431 | 0 | 2.38 | 0.000533 | -0.0215 |  | LF | AllSpc | 2230 | 0.431 | 2230 | 0.431 | 1.07 | 1.24 | -0.0096413 | 2230 | 0.431 | 2230 | 0.431 | 1.07 | 1.24 | -0.00964
LFAllSpcSCEAsmNewCZ14 | Com-Iltg-dWatt-LF_OSspc | SCE | Asm | New | CZ14 | 2.23 | 0.000431 | 0 | 2.37 | 0.000518 | -0.0214 | 2.23 | 0.000431 | 0 | 2.37 | 0.000518 | -0.0214 |  | LF | AllSpc | 2230 | 0.431 | 2230 | 0.431 | 1.06 | 1.2 | -0.0095964 | 2230 | 0.431 | 2230 | 0.431 | 1.06 | 1.2 | -0.0096
LFAllSpcSCEAsmNewCZ15 | Com-Iltg-dWatt-LF_OSspc | SCE | Asm | New | CZ15 | 2.23 | 0.000431 | 0 | 2.59 | 0.000528 | -0.00617 | 2.23 | 0.000431 | 0 | 2.59 | 0.000528 | -0.00617 |  | LF | AllSpc | 2230 | 0.431 | 2230 | 0.431 | 1.16 | 1.23 | -0.0027668 | 2230 | 0.431 | 2230 | 0.431 | 1.16 | 1.23 | -0.00277
LFAllSpcSCEAsmNewCZ16 | Com-Iltg-dWatt-LF_OSspc | SCE | Asm | New | CZ16 | 2.23 | 0.000431 | 0 | 2.21 | 0.000514 | -0.0316 | 2.23 | 0.000431 | 0 | 2.21 | 0.000514 | -0.0316 |  | LF | AllSpc | 2230 | 0.431 | 2230 | 0.431 | 0.991 | 1.19 | -0.01417 | 2230 | 0.431 | 2230 | 0.431 | 0.991 | 1.19 | -0.0142
LFAllSpcSCEAsmNewIOU | Com-Iltg-dWatt-LF_OSspc | SCE | Asm | New | IOU | 2.23 | 0.000431 | 0 | 2.436 | 0.00052637 | -0.013493 | 2.23 | 0.000431 | 0 | 2.436 | 0.00052637 | -0.013493 |  | LF | AllSpc | 2230 | 0.431 | 2230 | 0.431 | 1.09 | 1.22 | -0.0060506 | 2230 | 0.431 | 2230 | 0.431 | 1.09 | 1.22 | -0.00605
LFAllSpcSCEComExCZ05 | Com-Iltg-dWatt-LF_OSspc | SCE | Com | Ex | CZ05 | 3.254 | 0.00065843 | 0 | 3.4876 | 0.00081188 | -0.026751 | 3.254 | 0.00065843 | 0 | 3.4876 | 0.00081188 | -0.026751 |  | LF | AllSpc | 3250 | 0.658 | 3250 | 0.658 | 1.07 | 1.23 | -0.0082209 | 3250 | 0.658 | 3250 | 0.658 | 1.07 | 1.23 | -0.00822
LFAllSpcSCEComExCZ06 | Com-Iltg-dWatt-LF_OSspc | SCE | Com | Ex | CZ06 | 2.8098 | 0.00062049 | 0 | 3.1662 | 0.00077362 | -0.010994 | 2.8098 | 0.00062049 | 0 | 3.1662 | 0.00077362 | -0.010994 |  | LF | AllSpc | 2810 | 0.62 | 2810 | 0.62 | 1.13 | 1.25 | -0.0039127 | 2810 | 0.62 | 2810 | 0.62 | 1.13 | 1.25 | -0.00391
LFAllSpcSCEComExCZ08 | Com-Iltg-dWatt-LF_OSspc | SCE | Com | Ex | CZ08 | 2.8481 | 0.00062528 | 0 | 3.189 | 0.00077661 | -0.0099058 | 2.8481 | 0.00062528 | 0 | 3.189 | 0.00077661 | -0.0099058 |  | LF | AllSpc | 2850 | 0.625 | 2850 | 0.625 | 1.12 | 1.24 | -0.0034781 | 2850 | 0.625 | 2850 | 0.625 | 1.12 | 1.24 | -0.00348
LFAllSpcSCEComExCZ09 | Com-Iltg-dWatt-LF_OSspc | SCE | Com | Ex | CZ09 | 2.796 | 0.00062346 | 0 | 3.1459 | 0.00079264 | -0.011229 | 2.796 | 0.00062346 | 0 | 3.1459 | 0.00079264 | -0.011229 |  | LF | AllSpc | 2800 | 0.623 | 2800 | 0.623 | 1.13 | 1.27 | -0.0040162 | 2800 | 0.623 | 2800 | 0.623 | 1.13 | 1.27 | -0.00402
LFAllSpcSCEComExCZ10 | Com-Iltg-dWatt-LF_OSspc | SCE | Com | Ex | CZ10 | 3.0349 | 0.00064244 | 0 | 3.302 | 0.00079103 | -0.011679 | 3.0349 | 0.00064244 | 0 | 3.302 | 0.00079103 | -0.011679 |  | LF | AllSpc | 3030 | 0.642 | 3030 | 0.642 | 1.09 | 1.23 | -0.0038482 | 3030 | 0.642 | 3030 | 0.642 | 1.09 | 1.23 | -0.00385
LFAllSpcSCEComExCZ13 | Com-Iltg-dWatt-LF_OSspc | SCE | Com | Ex | CZ13 | 2.9264 | 0.00055012 | 0 | 3.2471 | 0.00068217 | -0.017645 | 2.9264 | 0.00055012 | 0 | 3.2471 | 0.00068217 | -0.017645 |  | LF | AllSpc | 2930 | 0.55 | 2930 | 0.55 | 1.11 | 1.24 | -0.0060295 | 2930 | 0.55 | 2930 | 0.55 | 1.11 | 1.24 | -0.00603
LFAllSpcSCEComExCZ14 | Com-Iltg-dWatt-LF_OSspc | SCE | Com | Ex | CZ14 | 2.9261 | 0.00064771 | 0 | 3.1825 | 0.00081275 | -0.019602 | 2.9261 | 0.00064771 | 0 | 3.1825 | 0.00081275 | -0.019602 |  | LF | AllSpc | 2930 | 0.648 | 2930 | 0.648 | 1.09 | 1.25 | -0.006699 | 2930 | 0.648 | 2930 | 0.648 | 1.09 | 1.25 | -0.0067
LFAllSpcSCEComExCZ15 | Com-Iltg-dWatt-LF_OSspc | SCE | Com | Ex | CZ15 | 2.6665 | 0.00057978 | 0 | 3.136 | 0.00073083 | -0.0047074 | 2.6665 | 0.00057978 | 0 | 3.136 | 0.00073083 | -0.0047074 |  | LF | AllSpc | 2670 | 0.58 | 2670 | 0.58 | 1.18 | 1.26 | -0.0017654 | 2670 | 0.58 | 2670 | 0.58 | 1.18 | 1.26 | -0.00177
LFAllSpcSCEComExCZ16 | Com-Iltg-dWatt-LF_OSspc | SCE | Com | Ex | CZ16 | 2.6567 | 0.00049617 | 0 | 2.6744 | 0.00060176 | -0.030788 | 2.6567 | 0.00049617 | 0 | 2.6744 | 0.00060176 | -0.030788 |  | LF | AllSpc | 2660 | 0.496 | 2660 | 0.496 | 1.01 | 1.21 | -0.011589 | 2660 | 0.496 | 2660 | 0.496 | 1.01 | 1.21 | -0.0116
LFAllSpcSCEComExIOU | Com-Iltg-dWatt-LF_OSspc | SCE | Com | Ex | IOU | 2.8624 | 0.00062231 | 0 | 3.1899 | 0.00077539 | -0.011398 | 2.8624 | 0.00062231 | 0 | 3.1899 | 0.00077539 | -0.011398 |  | LF | AllSpc | 2860 | 0.622 | 2860 | 0.622 | 1.11 | 1.25 | -0.0039818 | 2860 | 0.622 | 2860 | 0.622 | 1.11 | 1.25 | -0.00398
LFAllSpcSCEComNewCZ05 | Com-Iltg-dWatt-LF_OSspc | SCE | Com | New | CZ05 | 3.3794 | 0.00068365 | 0 | 3.5081 | 0.00083308 | -0.02816 | 3.3794 | 0.00068365 | 0 | 3.5081 | 0.00083308 | -0.02816 |  | LF | AllSpc | 3380 | 0.684 | 3380 | 0.684 | 1.04 | 1.22 | -0.0083328 | 3380 | 0.684 | 3380 | 0.684 | 1.04 | 1.22 | -0.00833
LFAllSpcSCEComNewCZ06 | Com-Iltg-dWatt-LF_OSspc | SCE | Com | New | CZ06 | 2.9903 | 0.00064311 | 0 | 3.279 | 0.00078997 | -0.011052 | 2.9903 | 0.00064311 | 0 | 3.279 | 0.00078997 | -0.011052 |  | LF | AllSpc | 2990 | 0.643 | 2990 | 0.643 | 1.1 | 1.23 | -0.003696 | 2990 | 0.643 | 2990 | 0.643 | 1.1 | 1.23 | -0.0037
LFAllSpcSCEComNewCZ08 | Com-Iltg-dWatt-LF_OSspc | SCE | Com | New | CZ08 | 3.0071 | 0.00064147 | 0 | 3.2931 | 0.00079057 | -0.0095618 | 3.0071 | 0.00064147 | 0 | 3.2931 | 0.00079057 | -0.0095618 |  | LF | AllSpc | 3010 | 0.641 | 3010 | 0.641 | 1.1 | 1.23 | -0.0031797 | 3010 | 0.641 | 3010 | 0.641 | 1.1 | 1.23 | -0.00318
LFAllSpcSCEComNewCZ09 | Com-Iltg-dWatt-LF_OSspc | SCE | Com | New | CZ09 | 2.9369 | 0.00063611 | 0 | 3.2436 | 0.00081161 | -0.010419 | 2.9369 | 0.00063611 | 0 | 3.2436 | 0.00081161 | -0.010419 |  | LF | AllSpc | 2940 | 0.636 | 2940 | 0.636 | 1.1 | 1.28 | -0.0035475 | 2940 | 0.636 | 2940 | 0.636 | 1.1 | 1.28 | -0.00355
LFAllSpcSCEComNewCZ10 | Com-Iltg-dWatt-LF_OSspc | SCE | Com | New | CZ10 | 3.0955 | 0.0006369 | 0 | 3.3251 | 0.00078843 | -0.010717 | 3.0955 | 0.0006369 | 0 | 3.3251 | 0.00078843 | -0.010717 |  | LF | AllSpc | 3100 | 0.637 | 3100 | 0.637 | 1.07 | 1.24 | -0.0034622 | 3100 | 0.637 | 3100 | 0.637 | 1.07 | 1.24 | -0.00346
LFAllSpcSCEComNewCZ13 | Com-Iltg-dWatt-LF_OSspc | SCE | Com | New | CZ13 | 3.0275 | 0.00057591 | 0 | 3.3518 | 0.00072592 | -0.017205 | 3.0275 | 0.00057591 | 0 | 3.3518 | 0.00072592 | -0.017205 |  | LF | AllSpc | 3030 | 0.576 | 3030 | 0.576 | 1.11 | 1.26 | -0.0056828 | 3030 | 0.576 | 3030 | 0.576 | 1.11 | 1.26 | -0.00568
LFAllSpcSCEComNewCZ14 | Com-Iltg-dWatt-LF_OSspc | SCE | Com | New | CZ14 | 3.024 | 0.00065449 | 0 | 3.3078 | 0.00084806 | -0.019692 | 3.024 | 0.00065449 | 0 | 3.3078 | 0.00084806 | -0.019692 |  | LF | AllSpc | 3020 | 0.654 | 3020 | 0.654 | 1.09 | 1.3 | -0.006512 | 3020 | 0.654 | 3020 | 0.654 | 1.09 | 1.3 | -0.00651
LFAllSpcSCEComNewCZ15 | Com-Iltg-dWatt-LF_OSspc | SCE | Com | New | CZ15 | 2.721 | 0.00059236 | 0 | 3.1947 | 0.00077485 | -0.003852 | 2.721 | 0.00059236 | 0 | 3.1947 | 0.00077485 | -0.003852 |  | LF | AllSpc | 2720 | 0.592 | 2720 | 0.592 | 1.17 | 1.31 | -0.0014156 | 2720 | 0.592 | 2720 | 0.592 | 1.17 | 1.31 | -0.00142
LFAllSpcSCEComNewCZ16 | Com-Iltg-dWatt-LF_OSspc | SCE | Com | New | CZ16 | 2.7483 | 0.00053099 | 0 | 2.7668 | 0.00065165 | -0.029498 | 2.7483 | 0.00053099 | 0 | 2.7668 | 0.00065165 | -0.029498 |  | LF | AllSpc | 2750 | 0.531 | 2750 | 0.531 | 1.01 | 1.23 | -0.010733 | 2750 | 0.531 | 2750 | 0.531 | 1.01 | 1.23 | -0.0107
LFAllSpcSCEComNewIOU | Com-Iltg-dWatt-LF_OSspc | SCE | Com | New | IOU | 3.0089 | 0.00063249 | 0 | 3.282 | 0.00078809 | -0.011125 | 3.0089 | 0.00063249 | 0 | 3.282 | 0.00078809 | -0.011125 |  | LF | AllSpc | 3010 | 0.632 | 3010 | 0.632 | 1.09 | 1.25 | -0.0036973 | 3010 | 0.632 | 3010 | 0.632 | 1.09 | 1.25 | -0.0037
LFAllSpcSCEECCExCZ05 | Com-Iltg-dWatt-LF_OSspc | SCE | ECC | Ex | CZ05 | 2.1305 | 0.00066095 | 0 | 2.33 | 0.00081495 | -0.024705 | 2.1305 | 0.00066095 | 0 | 2.33 | 0.00081495 | -0.024705 |  | LF | AllSpc | 2130 | 0.661 | 2130 | 0.661 | 1.09 | 1.23 | -0.011596 | 2130 | 0.661 | 2130 | 0.661 | 1.09 | 1.23 | -0.0116
LFAllSpcSCEECCExCZ06 | Com-Iltg-dWatt-LF_OSspc | SCE | ECC | Ex | CZ06 | 2.1305 | 0.00066095 | 0 | 2.47 | 0.00084795 | -0.011905 | 2.1305 | 0.00066095 | 0 | 2.47 | 0.00084795 | -0.011905 |  | LF | AllSpc | 2130 | 0.661 | 2130 | 0.661 | 1.16 | 1.28 | -0.0055879 | 2130 | 0.661 | 2130 | 0.661 | 1.16 | 1.28 | -0.00559
LFAllSpcSCEECCExCZ08 | Com-Iltg-dWatt-LF_OSspc | SCE | ECC | Ex | CZ08 | 2.1305 | 0.00066095 | 0 | 2.49 | 0.00084295 | -0.0108 | 2.1305 | 0.00066095 | 0 | 2.49 | 0.00084295 | -0.0108 |  | LF | AllSpc | 2130 | 0.661 | 2130 | 0.661 | 1.17 | 1.28 | -0.0050693 | 2130 | 0.661 | 2130 | 0.661 | 1.17 | 1.28 | -0.00507
LFAllSpcSCEECCExCZ09 | Com-Iltg-dWatt-LF_OSspc | SCE | ECC | Ex | CZ09 | 2.1305 | 0.00066095 | 0 | 2.47 | 0.00086194 | -0.0124 | 2.1305 | 0.00066095 | 0 | 2.47 | 0.00086194 | -0.0124 |  | LF | AllSpc | 2130 | 0.661 | 2130 | 0.661 | 1.16 | 1.3 | -0.0058201 | 2130 | 0.661 | 2130 | 0.661 | 1.16 | 1.3 | -0.00582
LFAllSpcSCEECCExCZ10 | Com-Iltg-dWatt-LF_OSspc | SCE | ECC | Ex | CZ10 | 2.131 | 0.0006609 | 0 | 2.45 | 0.00085181 | -0.0119 | 2.131 | 0.0006609 | 0 | 2.45 | 0.00085181 | -0.0119 |  | LF | AllSpc | 2130 | 0.661 | 2130 | 0.661 | 1.15 | 1.29 | -0.0055843 | 2130 | 0.661 | 2130 | 0.661 | 1.15 | 1.29 | -0.00558
LFAllSpcSCEECCExCZ13 | Com-Iltg-dWatt-LF_OSspc | SCE | ECC | Ex | CZ13 | 2.1312 | 0.000399 | 0 | 2.4012 | 0.000515 | -0.0183 | 2.1312 | 0.000399 | 0 | 2.4012 | 0.000515 | -0.0183 |  | LF | AllSpc | 2130 | 0.399 | 2130 | 0.399 | 1.13 | 1.29 | -0.0085866 | 2130 | 0.399 | 2130 | 0.399 | 1.13 | 1.29 | -0.00859
LFAllSpcSCEECCExCZ14 | Com-Iltg-dWatt-LF_OSspc | SCE | ECC | Ex | CZ14 | 2.1309 | 0.00066091 | 0 | 2.4 | 0.00084691 | -0.0192 | 2.1309 | 0.00066091 | 0 | 2.4 | 0.00084691 | -0.0192 |  | LF | AllSpc | 2130 | 0.661 | 2130 | 0.661 | 1.13 | 1.28 | -0.0090102 | 2130 | 0.661 | 2130 | 0.661 | 1.13 | 1.28 | -0.00901
LFAllSpcSCEECCExCZ15 | Com-Iltg-dWatt-LF_OSspc | SCE | ECC | Ex | CZ15 | 2.131 | 0.0006609 | 0 | 2.64 | 0.0008459 | -0.005291 | 2.131 | 0.0006609 | 0 | 2.64 | 0.0008459 | -0.005291 |  | LF | AllSpc | 2130 | 0.661 | 2130 | 0.661 | 1.24 | 1.28 | -0.0024829 | 2130 | 0.661 | 2130 | 0.661 | 1.24 | 1.28 | -0.00248
LFAllSpcSCEECCExCZ16 | Com-Iltg-dWatt-LF_OSspc | SCE | ECC | Ex | CZ16 | 2.131 | 0.000399 | 0 | 2.23 | 0.000497 | -0.03581 | 2.131 | 0.000399 | 0 | 2.23 | 0.000497 | -0.03581 |  | LF | AllSpc | 2130 | 0.399 | 2130 | 0.399 | 1.05 | 1.25 | -0.016804 | 2130 | 0.399 | 2130 | 0.399 | 1.05 | 1.25 | -0.0168
LFAllSpcSCEECCExIOU | Com-Iltg-dWatt-LF_OSspc | SCE | ECC | Ex | IOU | 2.1306 | 0.0006359 | 0 | 2.4592 | 0.00081437 | -0.01348 | 2.1306 | 0.0006359 | 0 | 2.4592 | 0.00081437 | -0.01348 |  | LF | AllSpc | 2130 | 0.636 | 2130 | 0.636 | 1.15 | 1.28 | -0.006327 | 2130 | 0.636 | 2130 | 0.636 | 1.15 | 1.28 | -0.00633
LFAllSpcSCEECCNewCZ05 | Com-Iltg-dWatt-LF_OSspc | SCE | ECC | New | CZ05 | 2.14 | 0.00066 | 0 | 2.31 | 0.000827 | -0.0252 | 2.14 | 0.00066 | 0 | 2.31 | 0.000827 | -0.0252 |  | LF | AllSpc | 2140 | 0.66 | 2140 | 0.66 | 1.08 | 1.25 | -0.011776 | 2140 | 0.66 | 2140 | 0.66 | 1.08 | 1.25 | -0.0118
LFAllSpcSCEECCNewCZ06 | Com-Iltg-dWatt-LF_OSspc | SCE | ECC | New | CZ06 | 2.14 | 0.00066 | 0 | 2.42 | 0.000841 | -0.0114 | 2.14 | 0.00066 | 0 | 2.42 | 0.000841 | -0.0114 |  | LF | AllSpc | 2140 | 0.66 | 2140 | 0.66 | 1.13 | 1.27 | -0.0053271 | 2140 | 0.66 | 2140 | 0.66 | 1.13 | 1.27 | -0.00533
LFAllSpcSCEECCNewCZ08 | Com-Iltg-dWatt-LF_OSspc | SCE | ECC | New | CZ08 | 2.14 | 0.00066 | 0 | 2.45 | 0.000846 | -0.00918 | 2.14 | 0.00066 | 0 | 2.45 | 0.000846 | -0.00918 |  | LF | AllSpc | 2140 | 0.66 | 2140 | 0.66 | 1.14 | 1.28 | -0.0042897 | 2140 | 0.66 | 2140 | 0.66 | 1.14 | 1.28 | -0.00429
LFAllSpcSCEECCNewCZ09 | Com-Iltg-dWatt-LF_OSspc | SCE | ECC | New | CZ09 | 2.14 | 0.00066 | 0 | 2.45 | 0.00087 | -0.0109 | 2.14 | 0.00066 | 0 | 2.45 | 0.00087 | -0.0109 |  | LF | AllSpc | 2140 | 0.66 | 2140 | 0.66 | 1.14 | 1.32 | -0.0050935 | 2140 | 0.66 | 2140 | 0.66 | 1.14 | 1.32 | -0.00509
LFAllSpcSCEECCNewCZ10 | Com-Iltg-dWatt-LF_OSspc | SCE | ECC | New | CZ10 | 2.14 | 0.00066 | 0 | 2.47 | 0.000879 | -0.0109 | 2.14 | 0.00066 | 0 | 2.47 | 0.000879 | -0.0109 |  | LF | AllSpc | 2140 | 0.66 | 2140 | 0.66 | 1.15 | 1.33 | -0.0050935 | 2140 | 0.66 | 2140 | 0.66 | 1.15 | 1.33 | -0.00509
LFAllSpcSCEECCNewCZ13 | Com-Iltg-dWatt-LF_OSspc | SCE | ECC | New | CZ13 | 2.14 | 0.000399 | 0 | 2.44 | 0.000552 | -0.0178 | 2.14 | 0.000399 | 0 | 2.44 | 0.000552 | -0.0178 |  | LF | AllSpc | 2140 | 0.399 | 2140 | 0.399 | 1.14 | 1.38 | -0.0083178 | 2140 | 0.399 | 2140 | 0.399 | 1.14 | 1.38 | -0.00832
LFAllSpcSCEECCNewCZ14 | Com-Iltg-dWatt-LF_OSspc | SCE | ECC | New | CZ14 | 2.14 | 0.00066 | 0 | 2.44 | 0.000854 | -0.0188 | 2.14 | 0.00066 | 0 | 2.44 | 0.000854 | -0.0188 |  | LF | AllSpc | 2140 | 0.66 | 2140 | 0.66 | 1.14 | 1.29 | -0.008785 | 2140 | 0.66 | 2140 | 0.66 | 1.14 | 1.29 | -0.00879
LFAllSpcSCEECCNewCZ15 | Com-Iltg-dWatt-LF_OSspc | SCE | ECC | New | CZ15 | 2.14 | 0.00066 | 0 | 2.74 | 0.000942 | -0.00397 | 2.14 | 0.00066 | 0 | 2.74 | 0.000942 | -0.00397 |  | LF | AllSpc | 2140 | 0.66 | 2140 | 0.66 | 1.28 | 1.43 | -0.0018551 | 2140 | 0.66 | 2140 | 0.66 | 1.28 | 1.43 | -0.00186
LFAllSpcSCEECCNewCZ16 | Com-Iltg-dWatt-LF_OSspc | SCE | ECC | New | CZ16 | 2.14 | 0.000399 | 0 | 2.26 | 0.000525 | -0.0355 | 2.14 | 0.000399 | 0 | 2.26 | 0.000525 | -0.0355 |  | LF | AllSpc | 2140 | 0.399 | 2140 | 0.399 | 1.06 | 1.32 | -0.016589 | 2140 | 0.399 | 2140 | 0.399 | 1.06 | 1.32 | -0.0166
LFAllSpcSCEECCNewIOU | Com-Iltg-dWatt-LF_OSspc | SCE | ECC | New | IOU | 2.14 | 0.00061729 | 0 | 2.4398 | 0.0008069 | -0.013799 | 2.14 | 0.00061729 | 0 | 2.4398 | 0.0008069 | -0.013799 |  | LF | AllSpc | 2140 | 0.617 | 2140 | 0.617 | 1.14 | 1.31 | -0.0064479 | 2140 | 0.617 | 2140 | 0.617 | 1.14 | 1.31 | -0.00645
LFAllSpcSCEEPrExCZ05 | Com-Iltg-dWatt-LF_OSspc | SCE | EPr | Ex | CZ05 | 1.86 | 0.00053217 | 0 | 2.04 | 0.00067822 | -0.0165 | 1.86 | 0.00053217 | 0 | 2.04 | 0.00067822 | -0.0165 |  | LF | AllSpc | 1860 | 0.532 | 1860 | 0.532 | 1.1 | 1.27 | -0.008871 | 1860 | 0.532 | 1860 | 0.532 | 1.1 | 1.27 | -0.00887
LFAllSpcSCEEPrExCZ06 | Com-Iltg-dWatt-LF_OSspc | SCE | EPr | Ex | CZ06 | 1.86 | 0.00053218 | 0 | 2.17 | 0.00069123 | -0.00801 | 1.86 | 0.00053218 | 0 | 2.17 | 0.00069123 | -0.00801 |  | LF | AllSpc | 1860 | 0.532 | 1860 | 0.532 | 1.17 | 1.3 | -0.0043065 | 1860 | 0.532 | 1860 | 0.532 | 1.17 | 1.3 | -0.00431
LFAllSpcSCEEPrExCZ08 | Com-Iltg-dWatt-LF_OSspc | SCE | EPr | Ex | CZ08 | 1.86 | 0.00053218 | 0 | 2.1903 | 0.00070023 | -0.00658 | 1.86 | 0.00053218 | 0 | 2.1903 | 0.00070023 | -0.00658 |  | LF | AllSpc | 1860 | 0.532 | 1860 | 0.532 | 1.18 | 1.32 | -0.0035376 | 1860 | 0.532 | 1860 | 0.532 | 1.18 | 1.32 | -0.00354
LFAllSpcSCEEPrExCZ09 | Com-Iltg-dWatt-LF_OSspc | SCE | EPr | Ex | CZ09 | 1.86 | 0.00053219 | 0 | 2.16 | 0.00070025 | -0.00824 | 1.86 | 0.00053219 | 0 | 2.16 | 0.00070025 | -0.00824 |  | LF | AllSpc | 1860 | 0.532 | 1860 | 0.532 | 1.16 | 1.32 | -0.0044301 | 1860 | 0.532 | 1860 | 0.532 | 1.16 | 1.32 | -0.00443
LFAllSpcSCEEPrExCZ10 | Com-Iltg-dWatt-LF_OSspc | SCE | EPr | Ex | CZ10 | 1.86 | 0.00053242 | 0 | 2.1 | 0.00068549 | -0.00894 | 1.86 | 0.00053242 | 0 | 2.1 | 0.00068549 | -0.00894 |  | LF | AllSpc | 1860 | 0.532 | 1860 | 0.532 | 1.13 | 1.29 | -0.0048065 | 1860 | 0.532 | 1860 | 0.532 | 1.13 | 1.29 | -0.00481
LFAllSpcSCEEPrExCZ13 | Com-Iltg-dWatt-LF_OSspc | SCE | EPr | Ex | CZ13 | 1.86 | 1.7313e-05 | 0 | 2.05 | 1.7313e-05 | -0.0151 | 1.86 | 1.7313e-05 | 0 | 2.05 | 1.7313e-05 | -0.0151 |  | LF | AllSpc | 1860 | 0.0173 | 1860 | 0.0173 | 1.1 | 1 | -0.0081183 | 1860 | 0.0173 | 1860 | 0.0173 | 1.1 | 1 | -0.00812
LFAllSpcSCEEPrExCZ14 | Com-Iltg-dWatt-LF_OSspc | SCE | EPr | Ex | CZ14 | 1.86 | 0.00053237 | 0 | 2.03 | 0.00068842 | -0.015 | 1.86 | 0.00053237 | 0 | 2.03 | 0.00068842 | -0.015 |  | LF | AllSpc | 1860 | 0.532 | 1860 | 0.532 | 1.09 | 1.29 | -0.0080645 | 1860 | 0.532 | 1860 | 0.532 | 1.09 | 1.29 | -0.00806
LFAllSpcSCEEPrExCZ15 | Com-Iltg-dWatt-LF_OSspc | SCE | EPr | Ex | CZ15 | 1.86 | 0.00053242 | 0 | 2.25 | 0.00068555 | -0.00367 | 1.86 | 0.00053242 | 0 | 2.25 | 0.00068555 | -0.00367 |  | LF | AllSpc | 1860 | 0.532 | 1860 | 0.532 | 1.21 | 1.29 | -0.0019731 | 1860 | 0.532 | 1860 | 0.532 | 1.21 | 1.29 | -0.00197
LFAllSpcSCEEPrExCZ16 | Com-Iltg-dWatt-LF_OSspc | SCE | EPr | Ex | CZ16 | 1.86 | 1.7312e-05 | 0 | 1.81 | 1.7312e-05 | -0.0309 | 1.86 | 1.7312e-05 | 0 | 1.81 | 1.7312e-05 | -0.0309 |  | LF | AllSpc | 1860 | 0.0173 | 1860 | 0.0173 | 0.973 | 1 | -0.016613 | 1860 | 0.0173 | 1860 | 0.0173 | 0.973 | 1 | -0.0166
LFAllSpcSCEEPrExIOU | Com-Iltg-dWatt-LF_OSspc | SCE | EPr | Ex | IOU | 1.86 | 0.00049833 | 0 | 2.1405 | 0.00064973 | -0.0089482 | 1.86 | 0.00049833 | 0 | 2.1405 | 0.00064973 | -0.0089482 |  | LF | AllSpc | 1860 | 0.498 | 1860 | 0.498 | 1.15 | 1.3 | -0.0048108 | 1860 | 0.498 | 1860 | 0.498 | 1.15 | 1.3 | -0.00481
LFAllSpcSCEEPrNewCZ05 | Com-Iltg-dWatt-LF_OSspc | SCE | EPr | New | CZ05 | 1.86 | 0.000539 | 0 | 1.96 | 0.000702 | -0.0161 | 1.86 | 0.000539 | 0 | 1.96 | 0.000702 | -0.0161 |  | LF | AllSpc | 1860 | 0.539 | 1860 | 0.539 | 1.05 | 1.3 | -0.0086559 | 1860 | 0.539 | 1860 | 0.539 | 1.05 | 1.3 | -0.00866
LFAllSpcSCEEPrNewCZ06 | Com-Iltg-dWatt-LF_OSspc | SCE | EPr | New | CZ06 | 1.86 | 0.000539 | 0 | 1.93 | 0.000512 | -0.00883 | 1.86 | 0.000539 | 0 | 1.93 | 0.000512 | -0.00883 |  | LF | AllSpc | 1860 | 0.539 | 1860 | 0.539 | 1.04 | 0.95 | -0.0047473 | 1860 | 0.539 | 1860 | 0.539 | 1.04 | 0.95 | -0.00475
LFAllSpcSCEEPrNewCZ08 | Com-Iltg-dWatt-LF_OSspc | SCE | EPr | New | CZ08 | 1.86 | 0.000539 | 0 | 2.1 | 0.000749 | -0.00891 | 1.86 | 0.000539 | 0 | 2.1 | 0.000749 | -0.00891 |  | LF | AllSpc | 1860 | 0.539 | 1860 | 0.539 | 1.13 | 1.39 | -0.0047903 | 1860 | 0.539 | 1860 | 0.539 | 1.13 | 1.39 | -0.00479
LFAllSpcSCEEPrNewCZ09 | Com-Iltg-dWatt-LF_OSspc | SCE | EPr | New | CZ09 | 1.86 | 0.000539 | 0 | 2.1 | 0.000777 | -0.0102 | 1.86 | 0.000539 | 0 | 2.1 | 0.000777 | -0.0102 |  | LF | AllSpc | 1860 | 0.539 | 1860 | 0.539 | 1.13 | 1.44 | -0.0054839 | 1860 | 0.539 | 1860 | 0.539 | 1.13 | 1.44 | -0.00548
LFAllSpcSCEEPrNewCZ10 | Com-Iltg-dWatt-LF_OSspc | SCE | EPr | New | CZ10 | 1.86 | 0.000539 | 0 | 2.11 | 0.000789 | -0.011 | 1.86 | 0.000539 | 0 | 2.11 | 0.000789 | -0.011 |  | LF | AllSpc | 1860 | 0.539 | 1860 | 0.539 | 1.13 | 1.46 | -0.005914 | 1860 | 0.539 | 1860 | 0.539 | 1.13 | 1.46 | -0.00591
LFAllSpcSCEEPrNewCZ13 | Com-Iltg-dWatt-LF_OSspc | SCE | EPr | New | CZ13 | 1.86 | 1.75e-05 | 0 | 2.07 | 1.75e-05 | -0.0179 | 1.86 | 1.75e-05 | 0 | 2.07 | 1.75e-05 | -0.0179 |  | LF | AllSpc | 1860 | 0.0175 | 1860 | 0.0175 | 1.11 | 1 | -0.0096237 | 1860 | 0.0175 | 1860 | 0.0175 | 1.11 | 1 | -0.00962
LFAllSpcSCEEPrNewCZ14 | Com-Iltg-dWatt-LF_OSspc | SCE | EPr | New | CZ14 | 1.86 | 0.000539 | 0 | 2.07 | 0.000774 | -0.0179 | 1.86 | 0.000539 | 0 | 2.07 | 0.000774 | -0.0179 |  | LF | AllSpc | 1860 | 0.539 | 1860 | 0.539 | 1.11 | 1.44 | -0.0096237 | 1860 | 0.539 | 1860 | 0.539 | 1.11 | 1.44 | -0.00962
LFAllSpcSCEEPrNewCZ15 | Com-Iltg-dWatt-LF_OSspc | SCE | EPr | New | CZ15 | 1.86 | 0.000539 | 0 | 2.3 | 0.000789 | -0.00473 | 1.86 | 0.000539 | 0 | 2.3 | 0.000789 | -0.00473 |  | LF | AllSpc | 1860 | 0.539 | 1860 | 0.539 | 1.24 | 1.46 | -0.002543 | 1860 | 0.539 | 1860 | 0.539 | 1.24 | 1.46 | -0.00254
LFAllSpcSCEEPrNewCZ16 | Com-Iltg-dWatt-LF_OSspc | SCE | EPr | New | CZ16 | 1.86 | 1.75e-05 | 0 | 1.84 | 1.75e-05 | -0.0289 | 1.86 | 1.75e-05 | 0 | 1.84 | 1.75e-05 | -0.0289 |  | LF | AllSpc | 1860 | 0.0175 | 1860 | 0.0175 | 0.989 | 1 | -0.015538 | 1860 | 0.0175 | 1860 | 0.0175 | 0.989 | 1 | -0.0155
LFAllSpcSCEEPrNewIOU | Com-Iltg-dWatt-LF_OSspc | SCE | EPr | New | IOU | 1.86 | 0.00048056 | 0 | 2.0742 | 0.00065842 | -0.011744 | 1.86 | 0.00048056 | 0 | 2.0742 | 0.00065842 | -0.011744 |  | LF | AllSpc | 1860 | 0.481 | 1860 | 0.481 | 1.12 | 1.37 | -0.006314 | 1860 | 0.481 | 1860 | 0.481 | 1.12 | 1.37 | -0.00631
LFAllSpcSCEERCExCZ05 | Com-Iltg-dWatt-LF_OSspc | SCE | ERC | Ex | CZ05 | 2.19 | 0.0006012 | 0 | 2.3 | 0.00077627 | -0.0223 | 2.19 | 0.0006012 | 0 | 2.3 | 0.00077627 | -0.0223 |  | LF | AllSpc | 2190 | 0.601 | 2190 | 0.601 | 1.05 | 1.29 | -0.010183 | 2190 | 0.601 | 2190 | 0.601 | 1.05 | 1.29 | -0.0102
LFAllSpcSCEERCExCZ06 | Com-Iltg-dWatt-LF_OSspc | SCE | ERC | Ex | CZ06 | 2.19 | 0.0006012 | 0 | 2.44 | 0.00076225 | -0.0135 | 2.19 | 0.0006012 | 0 | 2.44 | 0.00076225 | -0.0135 |  | LF | AllSpc | 2190 | 0.601 | 2190 | 0.601 | 1.11 | 1.27 | -0.0061644 | 2190 | 0.601 | 2190 | 0.601 | 1.11 | 1.27 | -0.00616
LFAllSpcSCEERCExCZ08 | Com-Iltg-dWatt-LF_OSspc | SCE | ERC | Ex | CZ08 | 2.19 | 0.00060121 | 0 | 2.44 | 0.00077126 | -0.0119 | 2.19 | 0.00060121 | 0 | 2.44 | 0.00077126 | -0.0119 |  | LF | AllSpc | 2190 | 0.601 | 2190 | 0.601 | 1.11 | 1.28 | -0.0054338 | 2190 | 0.601 | 2190 | 0.601 | 1.11 | 1.28 | -0.00543
LFAllSpcSCEERCExCZ09 | Com-Iltg-dWatt-LF_OSspc | SCE | ERC | Ex | CZ09 | 2.19 | 0.00060122 | 0 | 2.44 | 0.00077128 | -0.0133 | 2.19 | 0.00060122 | 0 | 2.44 | 0.00077128 | -0.0133 |  | LF | AllSpc | 2190 | 0.601 | 2190 | 0.601 | 1.11 | 1.28 | -0.0060731 | 2190 | 0.601 | 2190 | 0.601 | 1.11 | 1.28 | -0.00607
LFAllSpcSCEERCExCZ10 | Com-Iltg-dWatt-LF_OSspc | SCE | ERC | Ex | CZ10 | 2.19 | 0.00060149 | 0 | 2.43 | 0.00076761 | -0.0136 | 2.19 | 0.00060149 | 0 | 2.43 | 0.00076761 | -0.0136 |  | LF | AllSpc | 2190 | 0.601 | 2190 | 0.601 | 1.11 | 1.28 | -0.00621 | 2190 | 0.601 | 2190 | 0.601 | 1.11 | 1.28 | -0.00621
LFAllSpcSCEERCExCZ13 | Com-Iltg-dWatt-LF_OSspc | SCE | ERC | Ex | CZ13 | 2.19 | 1.7113e-05 | 0 | 2.37 | 1.7113e-05 | -0.0194 | 2.19 | 1.7113e-05 | 0 | 2.37 | 1.7113e-05 | -0.0194 |  | LF | AllSpc | 2190 | 0.0171 | 2190 | 0.0171 | 1.08 | 1 | -0.0088584 | 2190 | 0.0171 | 2190 | 0.0171 | 1.08 | 1 | -0.00886
LFAllSpcSCEERCExCZ14 | Com-Iltg-dWatt-LF_OSspc | SCE | ERC | Ex | CZ14 | 2.19 | 0.00060142 | 0 | 2.39 | 0.00077253 | -0.0182 | 2.19 | 0.00060142 | 0 | 2.39 | 0.00077253 | -0.0182 |  | LF | AllSpc | 2190 | 0.601 | 2190 | 0.601 | 1.09 | 1.28 | -0.0083105 | 2190 | 0.601 | 2190 | 0.601 | 1.09 | 1.28 | -0.00831
LFAllSpcSCEERCExCZ15 | Com-Iltg-dWatt-LF_OSspc | SCE | ERC | Ex | CZ15 | 2.19 | 0.00060149 | 0 | 2.6 | 0.00078567 | -0.0063 | 2.19 | 0.00060149 | 0 | 2.6 | 0.00078567 | -0.0063 |  | LF | AllSpc | 2190 | 0.601 | 2190 | 0.601 | 1.19 | 1.31 | -0.0028767 | 2190 | 0.601 | 2190 | 0.601 | 1.19 | 1.31 | -0.00288
LFAllSpcSCEERCExCZ16 | Com-Iltg-dWatt-LF_OSspc | SCE | ERC | Ex | CZ16 | 2.19 | 1.7112e-05 | 0 | 2.19 | 1.7112e-05 | -0.0335 | 2.19 | 1.7112e-05 | 0 | 2.19 | 1.7112e-05 | -0.0335 |  | LF | AllSpc | 2190 | 0.0171 | 2190 | 0.0171 | 1 | 1 | -0.015297 | 2190 | 0.0171 | 2190 | 0.0171 | 1 | 1 | -0.0153
LFAllSpcSCEERCExIOU | Com-Iltg-dWatt-LF_OSspc | SCE | ERC | Ex | IOU | 2.19 | 0.00056281 | 0 | 2.429 | 0.00071956 | -0.013852 | 2.19 | 0.00056281 | 0 | 2.429 | 0.00071956 | -0.013852 |  | LF | AllSpc | 2190 | 0.563 | 2190 | 0.563 | 1.11 | 1.28 | -0.0063251 | 2190 | 0.563 | 2190 | 0.563 | 1.11 | 1.28 | -0.00633
LFAllSpcSCEERCNewCZ05 | Com-Iltg-dWatt-LF_OSspc | SCE | ERC | New | CZ05 | 2.19 | 0.000609 | 0 | 2.41 | 0.000785 | -0.0216 | 2.19 | 0.000609 | 0 | 2.41 | 0.000785 | -0.0216 |  | LF | AllSpc | 2190 | 0.609 | 2190 | 0.609 | 1.1 | 1.29 | -0.009863 | 2190 | 0.609 | 2190 | 0.609 | 1.1 | 1.29 | -0.00986
LFAllSpcSCEERCNewCZ06 | Com-Iltg-dWatt-LF_OSspc | SCE | ERC | New | CZ06 | 2.19 | 0.000609 | 0 | 2.53 | 0.000793 | -0.0139 | 2.19 | 0.000609 | 0 | 2.53 | 0.000793 | -0.0139 |  | LF | AllSpc | 2190 | 0.609 | 2190 | 0.609 | 1.16 | 1.3 | -0.006347 | 2190 | 0.609 | 2190 | 0.609 | 1.16 | 1.3 | -0.00635
LFAllSpcSCEERCNewCZ08 | Com-Iltg-dWatt-LF_OSspc | SCE | ERC | New | CZ08 | 2.19 | 0.000609 | 0 | 2.58 | 0.000811 | -0.0117 | 2.19 | 0.000609 | 0 | 2.58 | 0.000811 | -0.0117 |  | LF | AllSpc | 2190 | 0.609 | 2190 | 0.609 | 1.18 | 1.33 | -0.0053425 | 2190 | 0.609 | 2190 | 0.609 | 1.18 | 1.33 | -0.00534
LFAllSpcSCEERCNewCZ09 | Com-Iltg-dWatt-LF_OSspc | SCE | ERC | New | CZ09 | 2.19 | 0.000609 | 0 | 2.58 | 0.000834 | -0.0132 | 2.19 | 0.000609 | 0 | 2.58 | 0.000834 | -0.0132 |  | LF | AllSpc | 2190 | 0.609 | 2190 | 0.609 | 1.18 | 1.37 | -0.0060274 | 2190 | 0.609 | 2190 | 0.609 | 1.18 | 1.37 | -0.00603
LFAllSpcSCEERCNewCZ10 | Com-Iltg-dWatt-LF_OSspc | SCE | ERC | New | CZ10 | 2.19 | 0.000609 | 0 | 2.59 | 0.00085 | -0.0139 | 2.19 | 0.000609 | 0 | 2.59 | 0.00085 | -0.0139 |  | LF | AllSpc | 2190 | 0.609 | 2190 | 0.609 | 1.18 | 1.4 | -0.006347 | 2190 | 0.609 | 2190 | 0.609 | 1.18 | 1.4 | -0.00635
LFAllSpcSCEERCNewCZ13 | Com-Iltg-dWatt-LF_OSspc | SCE | ERC | New | CZ13 | 2.19 | 1.73e-05 | 0 | 2.56 | 1.73e-05 | -0.0208 | 2.19 | 1.73e-05 | 0 | 2.56 | 1.73e-05 | -0.0208 |  | LF | AllSpc | 2190 | 0.0173 | 2190 | 0.0173 | 1.17 | 1 | -0.0094977 | 2190 | 0.0173 | 2190 | 0.0173 | 1.17 | 1 | -0.0095
LFAllSpcSCEERCNewCZ14 | Com-Iltg-dWatt-LF_OSspc | SCE | ERC | New | CZ14 | 2.19 | 0.000609 | 0 | 2.55 | 0.000837 | -0.0201 | 2.19 | 0.000609 | 0 | 2.55 | 0.000837 | -0.0201 |  | LF | AllSpc | 2190 | 0.609 | 2190 | 0.609 | 1.16 | 1.37 | -0.0091781 | 2190 | 0.609 | 2190 | 0.609 | 1.16 | 1.37 | -0.00918
LFAllSpcSCEERCNewCZ15 | Com-Iltg-dWatt-LF_OSspc | SCE | ERC | New | CZ15 | 2.19 | 0.000609 | 0 | 2.82 | 0.000852 | -0.00687 | 2.19 | 0.000609 | 0 | 2.82 | 0.000852 | -0.00687 |  | LF | AllSpc | 2190 | 0.609 | 2190 | 0.609 | 1.29 | 1.4 | -0.003137 | 2190 | 0.609 | 2190 | 0.609 | 1.29 | 1.4 | -0.00314
LFAllSpcSCEERCNewCZ16 | Com-Iltg-dWatt-LF_OSspc | SCE | ERC | New | CZ16 | 2.19 | 1.73e-05 | 0 | 2.29 | 1.73e-05 | -0.0367 | 2.19 | 1.73e-05 | 0 | 2.29 | 1.73e-05 | -0.0367 |  | LF | AllSpc | 2190 | 0.0173 | 2190 | 0.0173 | 1.05 | 1 | -0.016758 | 2190 | 0.0173 | 2190 | 0.0173 | 1.05 | 1 | -0.0168
LFAllSpcSCEERCNewIOU | Com-Iltg-dWatt-LF_OSspc | SCE | ERC | New | IOU | 2.19 | 0.00054269 | 0 | 2.5693 | 0.00073877 | -0.01501 | 2.19 | 0.00054269 | 0 | 2.5693 | 0.00073877 | -0.01501 |  | LF | AllSpc | 2190 | 0.543 | 2190 | 0.543 | 1.17 | 1.36 | -0.006854 | 2190 | 0.543 | 2190 | 0.543 | 1.17 | 1.36 | -0.00685
LFAllSpcSCEESeExCZ05 | Com-Iltg-dWatt-LF_OSspc | SCE | ESe | Ex | CZ05 | 1.99 | 0.0006152 | 0 | 2.12 | 0.00076625 | -0.0227 | 1.99 | 0.0006152 | 0 | 2.12 | 0.00076625 | -0.0227 |  | LF | AllSpc | 1990 | 0.615 | 1990 | 0.615 | 1.07 | 1.25 | -0.011407 | 1990 | 0.615 | 1990 | 0.615 | 1.07 | 1.25 | -0.0114
LFAllSpcSCEESeExCZ06 | Com-Iltg-dWatt-LF_OSspc | SCE | ESe | Ex | CZ06 | 1.99 | 0.0006152 | 0 | 2.28 | 0.00079823 | -0.0117 | 1.99 | 0.0006152 | 0 | 2.28 | 0.00079823 | -0.0117 |  | LF | AllSpc | 1990 | 0.615 | 1990 | 0.615 | 1.15 | 1.3 | -0.0058794 | 1990 | 0.615 | 1990 | 0.615 | 1.15 | 1.3 | -0.00588
LFAllSpcSCEESeExCZ08 | Com-Iltg-dWatt-LF_OSspc | SCE | ESe | Ex | CZ08 | 1.99 | 0.00061521 | 0 | 2.3 | 0.00079426 | -0.0102 | 1.99 | 0.00061521 | 0 | 2.3 | 0.00079426 | -0.0102 |  | LF | AllSpc | 1990 | 0.615 | 1990 | 0.615 | 1.16 | 1.29 | -0.0051256 | 1990 | 0.615 | 1990 | 0.615 | 1.16 | 1.29 | -0.00513
LFAllSpcSCEESeExCZ09 | Com-Iltg-dWatt-LF_OSspc | SCE | ESe | Ex | CZ09 | 1.99 | 0.00061522 | 0 | 2.28 | 0.00079928 | -0.0118 | 1.99 | 0.00061522 | 0 | 2.28 | 0.00079928 | -0.0118 |  | LF | AllSpc | 1990 | 0.615 | 1990 | 0.615 | 1.15 | 1.3 | -0.0059296 | 1990 | 0.615 | 1990 | 0.615 | 1.15 | 1.3 | -0.00593
LFAllSpcSCEESeExCZ10 | Com-Iltg-dWatt-LF_OSspc | SCE | ESe | Ex | CZ10 | 1.99 | 0.00061549 | 0 | 2.23 | 0.00078454 | -0.0126 | 1.99 | 0.00061549 | 0 | 2.23 | 0.00078454 | -0.0126 |  | LF | AllSpc | 1990 | 0.615 | 1990 | 0.615 | 1.12 | 1.27 | -0.0063317 | 1990 | 0.615 | 1990 | 0.615 | 1.12 | 1.27 | -0.00633
LFAllSpcSCEESeExCZ13 | Com-Iltg-dWatt-LF_OSspc | SCE | ESe | Ex | CZ13 | 1.99 | 1.732e-05 | 0 | 2.19 | 1.732e-05 | -0.0196 | 1.99 | 1.732e-05 | 0 | 2.19 | 1.732e-05 | -0.0196 |  | LF | AllSpc | 1990 | 0.0173 | 1990 | 0.0173 | 1.1 | 1 | -0.0098492 | 1990 | 0.0173 | 1990 | 0.0173 | 1.1 | 1 | -0.00985
LFAllSpcSCEESeExCZ14 | Com-Iltg-dWatt-LF_OSspc | SCE | ESe | Ex | CZ14 | 1.99 | 0.00061542 | 0 | 2.17 | 0.00076353 | -0.0198 | 1.99 | 0.00061542 | 0 | 2.17 | 0.00076353 | -0.0198 |  | LF | AllSpc | 1990 | 0.615 | 1990 | 0.615 | 1.09 | 1.24 | -0.0099497 | 1990 | 0.615 | 1990 | 0.615 | 1.09 | 1.24 | -0.00995
LFAllSpcSCEESeExCZ15 | Com-Iltg-dWatt-LF_OSspc | SCE | ESe | Ex | CZ15 | 1.99 | 0.00061549 | 0 | 2.42 | 0.00078161 | -0.00566 | 1.99 | 0.00061549 | 0 | 2.42 | 0.00078161 | -0.00566 |  | LF | AllSpc | 1990 | 0.615 | 1990 | 0.615 | 1.22 | 1.27 | -0.0028442 | 1990 | 0.615 | 1990 | 0.615 | 1.22 | 1.27 | -0.00284
LFAllSpcSCEESeExCZ16 | Com-Iltg-dWatt-LF_OSspc | SCE | ESe | Ex | CZ16 | 1.99 | 1.7318e-05 | 0 | 1.95 | 1.7318e-05 | -0.0341 | 1.99 | 1.7318e-05 | 0 | 1.95 | 1.7318e-05 | -0.0341 |  | LF | AllSpc | 1990 | 0.0173 | 1990 | 0.0173 | 0.98 | 1 | -0.017136 | 1990 | 0.0173 | 1990 | 0.0173 | 0.98 | 1 | -0.0171
LFAllSpcSCEESeExIOU | Com-Iltg-dWatt-LF_OSspc | SCE | ESe | Ex | IOU | 1.99 | 0.0005759 | 0 | 2.2608 | 0.00074077 | -0.012641 | 1.99 | 0.0005759 | 0 | 2.2608 | 0.00074077 | -0.012641 |  | LF | AllSpc | 1990 | 0.576 | 1990 | 0.576 | 1.14 | 1.29 | -0.0063522 | 1990 | 0.576 | 1990 | 0.576 | 1.14 | 1.29 | -0.00635
LFAllSpcSCEESeNewCZ05 | Com-Iltg-dWatt-LF_OSspc | SCE | ESe | New | CZ05 | 1.99 | 0.000623 | 0 | 2.1 | 0.000794 | -0.0201 | 1.99 | 0.000623 | 0 | 2.1 | 0.000794 | -0.0201 |  | LF | AllSpc | 1990 | 0.623 | 1990 | 0.623 | 1.06 | 1.27 | -0.010101 | 1990 | 0.623 | 1990 | 0.623 | 1.06 | 1.27 | -0.0101
LFAllSpcSCEESeNewCZ06 | Com-Iltg-dWatt-LF_OSspc | SCE | ESe | New | CZ06 | 1.99 | 0.000623 | 0 | 2.21 | 0.000832 | -0.0148 | 1.99 | 0.000623 | 0 | 2.21 | 0.000832 | -0.0148 |  | LF | AllSpc | 1990 | 0.623 | 1990 | 0.623 | 1.11 | 1.34 | -0.0074372 | 1990 | 0.623 | 1990 | 0.623 | 1.11 | 1.34 | -0.00744
LFAllSpcSCEESeNewCZ08 | Com-Iltg-dWatt-LF_OSspc | SCE | ESe | New | CZ08 | 1.99 | 0.000623 | 0 | 2.24 | 0.000845 | -0.0112 | 1.99 | 0.000623 | 0 | 2.24 | 0.000845 | -0.0112 |  | LF | AllSpc | 1990 | 0.623 | 1990 | 0.623 | 1.13 | 1.36 | -0.0056281 | 1990 | 0.623 | 1990 | 0.623 | 1.13 | 1.36 | -0.00563
LFAllSpcSCEESeNewCZ09 | Com-Iltg-dWatt-LF_OSspc | SCE | ESe | New | CZ09 | 1.99 | 0.000623 | 0 | 2.25 | 0.000877 | -0.0133 | 1.99 | 0.000623 | 0 | 2.25 | 0.000877 | -0.0133 |  | LF | AllSpc | 1990 | 0.623 | 1990 | 0.623 | 1.13 | 1.41 | -0.0066834 | 1990 | 0.623 | 1990 | 0.623 | 1.13 | 1.41 | -0.00668
LFAllSpcSCEESeNewCZ10 | Com-Iltg-dWatt-LF_OSspc | SCE | ESe | New | CZ10 | 1.99 | 0.000623 | 0 | 2.26 | 0.00089 | -0.0144 | 1.99 | 0.000623 | 0 | 2.26 | 0.00089 | -0.0144 |  | LF | AllSpc | 1990 | 0.623 | 1990 | 0.623 | 1.14 | 1.43 | -0.0072362 | 1990 | 0.623 | 1990 | 0.623 | 1.14 | 1.43 | -0.00724
LFAllSpcSCEESeNewCZ13 | Com-Iltg-dWatt-LF_OSspc | SCE | ESe | New | CZ13 | 1.99 | 1.76e-05 | 0 | 2.24 | 1.76e-05 | -0.0213 | 1.99 | 1.76e-05 | 0 | 2.24 | 1.76e-05 | -0.0213 |  | LF | AllSpc | 1990 | 0.0176 | 1990 | 0.0176 | 1.13 | 1 | -0.010704 | 1990 | 0.0176 | 1990 | 0.0176 | 1.13 | 1 | -0.0107
LFAllSpcSCEESeNewCZ14 | Com-Iltg-dWatt-LF_OSspc | SCE | ESe | New | CZ14 | 1.99 | 0.000623 | 0 | 2.23 | 0.000868 | -0.0215 | 1.99 | 0.000623 | 0 | 2.23 | 0.000868 | -0.0215 |  | LF | AllSpc | 1990 | 0.623 | 1990 | 0.623 | 1.12 | 1.39 | -0.010804 | 1990 | 0.623 | 1990 | 0.623 | 1.12 | 1.39 | -0.0108
LFAllSpcSCEESeNewCZ15 | Com-Iltg-dWatt-LF_OSspc | SCE | ESe | New | CZ15 | 1.99 | 0.000623 | 0 | 2.51 | 0.000883 | -0.00624 | 1.99 | 0.000623 | 0 | 2.51 | 0.000883 | -0.00624 |  | LF | AllSpc | 1990 | 0.623 | 1990 | 0.623 | 1.26 | 1.42 | -0.0031357 | 1990 | 0.623 | 1990 | 0.623 | 1.26 | 1.42 | -0.00314
LFAllSpcSCEESeNewCZ16 | Com-Iltg-dWatt-LF_OSspc | SCE | ESe | New | CZ16 | 1.99 | 1.76e-05 | 0 | 1.99 | 1.76e-05 | -0.0279 | 1.99 | 1.76e-05 | 0 | 1.99 | 1.76e-05 | -0.0279 |  | LF | AllSpc | 1990 | 0.0176 | 1990 | 0.0176 | 1 | 1 | -0.01402 | 1990 | 0.0176 | 1990 | 0.0176 | 1 | 1 | -0.014
LFAllSpcSCEESeNewIOU | Com-Iltg-dWatt-LF_OSspc | SCE | ESe | New | IOU | 1.99 | 0.00055516 | 0 | 2.2416 | 0.00077232 | -0.014967 | 1.99 | 0.00055516 | 0 | 2.2416 | 0.00077232 | -0.014967 |  | LF | AllSpc | 1990 | 0.555 | 1990 | 0.555 | 1.13 | 1.39 | -0.007521 | 1990 | 0.555 | 1990 | 0.555 | 1.13 | 1.39 | -0.00752
LFAllSpcSCEEUnExCZ05 | Com-Iltg-dWatt-LF_OSspc | SCE | EUn | Ex | CZ05 | 2.07 | 0.00059295 | 0 | 2.3 | 0.00072095 | -0.0144 | 2.07 | 0.00059295 | 0 | 2.3 | 0.00072095 | -0.0144 |  | LF | AllSpc | 2070 | 0.593 | 2070 | 0.593 | 1.11 | 1.22 | -0.0069565 | 2070 | 0.593 | 2070 | 0.593 | 1.11 | 1.22 | -0.00696
LFAllSpcSCEEUnExCZ06 | Com-Iltg-dWatt-LF_OSspc | SCE | EUn | Ex | CZ06 | 2.07 | 0.00059295 | 0 | 2.4 | 0.00075095 | -0.0085105 | 2.07 | 0.00059295 | 0 | 2.4 | 0.00075095 | -0.0085105 |  | LF | AllSpc | 2070 | 0.593 | 2070 | 0.593 | 1.16 | 1.27 | -0.0041113 | 2070 | 0.593 | 2070 | 0.593 | 1.16 | 1.27 | -0.00411
LFAllSpcSCEEUnExCZ08 | Com-Iltg-dWatt-LF_OSspc | SCE | EUn | Ex | CZ08 | 2.07 | 0.00059295 | 0 | 2.41 | 0.00075295 | -0.0082405 | 2.07 | 0.00059295 | 0 | 2.41 | 0.00075295 | -0.0082405 |  | LF | AllSpc | 2070 | 0.593 | 2070 | 0.593 | 1.16 | 1.27 | -0.0039809 | 2070 | 0.593 | 2070 | 0.593 | 1.16 | 1.27 | -0.00398
LFAllSpcSCEEUnExCZ09 | Com-Iltg-dWatt-LF_OSspc | SCE | EUn | Ex | CZ09 | 2.07 | 0.00059295 | 0 | 2.4 | 0.00076394 | -0.0090906 | 2.07 | 0.00059295 | 0 | 2.4 | 0.00076394 | -0.0090906 |  | LF | AllSpc | 2070 | 0.593 | 2070 | 0.593 | 1.16 | 1.29 | -0.0043916 | 2070 | 0.593 | 2070 | 0.593 | 1.16 | 1.29 | -0.00439
LFAllSpcSCEEUnExCZ10 | Com-Iltg-dWatt-LF_OSspc | SCE | EUn | Ex | CZ10 | 2.07 | 0.0005929 | 0 | 2.38 | 0.0007579 | -0.008181 | 2.07 | 0.0005929 | 0 | 2.38 | 0.0007579 | -0.008181 |  | LF | AllSpc | 2070 | 0.593 | 2070 | 0.593 | 1.15 | 1.28 | -0.0039522 | 2070 | 0.593 | 2070 | 0.593 | 1.15 | 1.28 | -0.00395
LFAllSpcSCEEUnExCZ13 | Com-Iltg-dWatt-LF_OSspc | SCE | EUn | Ex | CZ13 | 2.07 | 0.000361 | 0 | 2.34 | 0.000455 | -0.0108 | 2.07 | 0.000361 | 0 | 2.34 | 0.000455 | -0.0108 |  | LF | AllSpc | 2070 | 0.361 | 2070 | 0.361 | 1.13 | 1.26 | -0.0052174 | 2070 | 0.361 | 2070 | 0.361 | 1.13 | 1.26 | -0.00522
LFAllSpcSCEEUnExCZ14 | Com-Iltg-dWatt-LF_OSspc | SCE | EUn | Ex | CZ14 | 2.07 | 0.00059291 | 0 | 2.34 | 0.00075391 | -0.0119 | 2.07 | 0.00059291 | 0 | 2.34 | 0.00075391 | -0.0119 |  | LF | AllSpc | 2070 | 0.593 | 2070 | 0.593 | 1.13 | 1.27 | -0.0057488 | 2070 | 0.593 | 2070 | 0.593 | 1.13 | 1.27 | -0.00575
LFAllSpcSCEEUnExCZ15 | Com-Iltg-dWatt-LF_OSspc | SCE | EUn | Ex | CZ15 | 2.07 | 0.0005929 | 0 | 2.481 | 0.0007609 | -0.00436 | 2.07 | 0.0005929 | 0 | 2.481 | 0.0007609 | -0.00436 |  | LF | AllSpc | 2070 | 0.593 | 2070 | 0.593 | 1.2 | 1.28 | -0.0021063 | 2070 | 0.593 | 2070 | 0.593 | 1.2 | 1.28 | -0.00211
LFAllSpcSCEEUnExCZ16 | Com-Iltg-dWatt-LF_OSspc | SCE | EUn | Ex | CZ16 | 2.07 | 0.000361 | 0 | 2.181 | 0.000437 | -0.0236 | 2.07 | 0.000361 | 0 | 2.181 | 0.000437 | -0.0236 |  | LF | AllSpc | 2070 | 0.361 | 2070 | 0.361 | 1.05 | 1.21 | -0.011401 | 2070 | 0.361 | 2070 | 0.361 | 1.05 | 1.21 | -0.0114
LFAllSpcSCEEUnExIOU | Com-Iltg-dWatt-LF_OSspc | SCE | EUn | Ex | IOU | 2.07 | 0.00057077 | 0 | 2.3846 | 0.00072446 | -0.0095712 | 2.07 | 0.00057077 | 0 | 2.3846 | 0.00072446 | -0.0095712 |  | LF | AllSpc | 2070 | 0.571 | 2070 | 0.571 | 1.15 | 1.27 | -0.0046238 | 2070 | 0.571 | 2070 | 0.571 | 1.15 | 1.27 | -0.00462
LFAllSpcSCEEUnNewCZ05 | Com-Iltg-dWatt-LF_OSspc | SCE | EUn | New | CZ05 | 2.07 | 0.000592 | 0 | 2.26 | 0.000737 | -0.0116 | 2.07 | 0.000592 | 0 | 2.26 | 0.000737 | -0.0116 |  | LF | AllSpc | 2070 | 0.592 | 2070 | 0.592 | 1.09 | 1.24 | -0.0056039 | 2070 | 0.592 | 2070 | 0.592 | 1.09 | 1.24 | -0.0056
LFAllSpcSCEEUnNewCZ06 | Com-Iltg-dWatt-LF_OSspc | SCE | EUn | New | CZ06 | 2.07 | 0.000592 | 0 | 2.39 | 0.000756 | -0.00519 | 2.07 | 0.000592 | 0 | 2.39 | 0.000756 | -0.00519 |  | LF | AllSpc | 2070 | 0.592 | 2070 | 0.592 | 1.15 | 1.28 | -0.0025072 | 2070 | 0.592 | 2070 | 0.592 | 1.15 | 1.28 | -0.00251
LFAllSpcSCEEUnNewCZ08 | Com-Iltg-dWatt-LF_OSspc | SCE | EUn | New | CZ08 | 2.07 | 0.000592 | 0 | 2.41 | 0.000767 | -0.00463 | 2.07 | 0.000592 | 0 | 2.41 | 0.000767 | -0.00463 |  | LF | AllSpc | 2070 | 0.592 | 2070 | 0.592 | 1.16 | 1.3 | -0.0022367 | 2070 | 0.592 | 2070 | 0.592 | 1.16 | 1.3 | -0.00224
LFAllSpcSCEEUnNewCZ09 | Com-Iltg-dWatt-LF_OSspc | SCE | EUn | New | CZ09 | 2.07 | 0.000592 | 0 | 2.42 | 0.000792 | -0.00533 | 2.07 | 0.000592 | 0 | 2.42 | 0.000792 | -0.00533 |  | LF | AllSpc | 2070 | 0.592 | 2070 | 0.592 | 1.17 | 1.34 | -0.0025749 | 2070 | 0.592 | 2070 | 0.592 | 1.17 | 1.34 | -0.00257
LFAllSpcSCEEUnNewCZ10 | Com-Iltg-dWatt-LF_OSspc | SCE | EUn | New | CZ10 | 2.07 | 0.000592 | 0 | 2.43 | 0.000799 | -0.00575 | 2.07 | 0.000592 | 0 | 2.43 | 0.000799 | -0.00575 |  | LF | AllSpc | 2070 | 0.592 | 2070 | 0.592 | 1.17 | 1.35 | -0.0027778 | 2070 | 0.592 | 2070 | 0.592 | 1.17 | 1.35 | -0.00278
LFAllSpcSCEEUnNewCZ13 | Com-Iltg-dWatt-LF_OSspc | SCE | EUn | New | CZ13 | 2.07 | 0.000361 | 0 | 2.4 | 0.0005 | -0.0101 | 2.07 | 0.000361 | 0 | 2.4 | 0.0005 | -0.0101 |  | LF | AllSpc | 2070 | 0.361 | 2070 | 0.361 | 1.16 | 1.39 | -0.0048792 | 2070 | 0.361 | 2070 | 0.361 | 1.16 | 1.39 | -0.00488
LFAllSpcSCEEUnNewCZ14 | Com-Iltg-dWatt-LF_OSspc | SCE | EUn | New | CZ14 | 2.07 | 0.000592 | 0 | 2.37 | 0.000769 | -0.0108 | 2.07 | 0.000592 | 0 | 2.37 | 0.000769 | -0.0108 |  | LF | AllSpc | 2070 | 0.592 | 2070 | 0.592 | 1.14 | 1.3 | -0.0052174 | 2070 | 0.592 | 2070 | 0.592 | 1.14 | 1.3 | -0.00522
LFAllSpcSCEEUnNewCZ15 | Com-Iltg-dWatt-LF_OSspc | SCE | EUn | New | CZ15 | 2.07 | 0.000592 | 0 | 2.57 | 0.000807 | -0.00223 | 2.07 | 0.000592 | 0 | 2.57 | 0.000807 | -0.00223 |  | LF | AllSpc | 2070 | 0.592 | 2070 | 0.592 | 1.24 | 1.36 | -0.0010773 | 2070 | 0.592 | 2070 | 0.592 | 1.24 | 1.36 | -0.00108
LFAllSpcSCEEUnNewCZ16 | Com-Iltg-dWatt-LF_OSspc | SCE | EUn | New | CZ16 | 2.07 | 0.000361 | 0 | 2.21 | 0.000473 | -0.0225 | 2.07 | 0.000361 | 0 | 2.21 | 0.000473 | -0.0225 |  | LF | AllSpc | 2070 | 0.361 | 2070 | 0.361 | 1.07 | 1.31 | -0.01087 | 2070 | 0.361 | 2070 | 0.361 | 1.07 | 1.31 | -0.0109
LFAllSpcSCEEUnNewIOU | Com-Iltg-dWatt-LF_OSspc | SCE | EUn | New | IOU | 2.07 | 0.0005542 | 0 | 2.3927 | 0.00072786 | -0.0075677 | 2.07 | 0.0005542 | 0 | 2.3927 | 0.00072786 | -0.0075677 |  | LF | AllSpc | 2070 | 0.554 | 2070 | 0.554 | 1.16 | 1.31 | -0.0036559 | 2070 | 0.554 | 2070 | 0.554 | 1.16 | 1.31 | -0.00366
LFAllSpcSCEGroExCZ05 | Com-Iltg-dWatt-LF_OSspc | SCE | Gro | Ex | CZ05 | 4.7694 | 0.00066788 | 0 | 4.5994 | 0.00082488 | -0.081088 | 4.7694 | 0.00066788 | 0 | 4.5994 | 0.00082488 | -0.081088 |  | LF | AllSpc | 4770 | 0.668 | 4770 | 0.668 | 0.964 | 1.24 | -0.017002 | 4770 | 0.668 | 4770 | 0.668 | 0.964 | 1.24 | -0.017
LFAllSpcSCEGroExCZ06 | Com-Iltg-dWatt-LF_OSspc | SCE | Gro | Ex | CZ06 | 4.7694 | 0.00066788 | 0 | 4.9194 | 0.00083488 | -0.061494 | 4.7694 | 0.00066788 | 0 | 4.9194 | 0.00083488 | -0.061494 |  | LF | AllSpc | 4770 | 0.668 | 4770 | 0.668 | 1.03 | 1.25 | -0.012893 | 4770 | 0.668 | 4770 | 0.668 | 1.03 | 1.25 | -0.0129
LFAllSpcSCEGroExCZ08 | Com-Iltg-dWatt-LF_OSspc | SCE | Gro | Ex | CZ08 | 4.7694 | 0.00066788 | 0 | 5.0294 | 0.00085381 | -0.055294 | 4.7694 | 0.00066788 | 0 | 5.0294 | 0.00085381 | -0.055294 |  | LF | AllSpc | 4770 | 0.668 | 4770 | 0.668 | 1.05 | 1.28 | -0.011593 | 4770 | 0.668 | 4770 | 0.668 | 1.05 | 1.28 | -0.0116
LFAllSpcSCEGroExCZ09 | Com-Iltg-dWatt-LF_OSspc | SCE | Gro | Ex | CZ09 | 4.7694 | 0.00066787 | 0 | 5.0394 | 0.00086387 | -0.054394 | 4.7694 | 0.00066787 | 0 | 5.0394 | 0.00086387 | -0.054394 |  | LF | AllSpc | 4770 | 0.668 | 4770 | 0.668 | 1.06 | 1.29 | -0.011405 | 4770 | 0.668 | 4770 | 0.668 | 1.06 | 1.29 | -0.0114
LFAllSpcSCEGroExCZ10 | Com-Iltg-dWatt-LF_OSspc | SCE | Gro | Ex | CZ10 | 4.7689 | 0.00066778 | 0 | 5.0289 | 0.00088178 | -0.052889 | 4.7689 | 0.00066778 | 0 | 5.0289 | 0.00088178 | -0.052889 |  | LF | AllSpc | 4770 | 0.668 | 4770 | 0.668 | 1.05 | 1.32 | -0.01109 | 4770 | 0.668 | 4770 | 0.668 | 1.05 | 1.32 | -0.0111
LFAllSpcSCEGroExCZ13 | Com-Iltg-dWatt-LF_OSspc | SCE | Gro | Ex | CZ13 | 4.769 | 0.00066781 | 0 | 5.029 | 0.0008678 | -0.05439 | 4.769 | 0.00066781 | 0 | 5.029 | 0.0008678 | -0.05439 |  | LF | AllSpc | 4770 | 0.668 | 4770 | 0.668 | 1.05 | 1.3 | -0.011405 | 4770 | 0.668 | 4770 | 0.668 | 1.05 | 1.3 | -0.0114
LFAllSpcSCEGroExCZ14 | Com-Iltg-dWatt-LF_OSspc | SCE | Gro | Ex | CZ14 | 4.769 | 0.00066779 | 0 | 5.009 | 0.00089379 | -0.05629 | 4.769 | 0.00066779 | 0 | 5.009 | 0.00089379 | -0.05629 |  | LF | AllSpc | 4770 | 0.668 | 4770 | 0.668 | 1.05 | 1.34 | -0.011803 | 4770 | 0.668 | 4770 | 0.668 | 1.05 | 1.34 | -0.0118
LFAllSpcSCEGroExCZ15 | Com-Iltg-dWatt-LF_OSspc | SCE | Gro | Ex | CZ15 | 4.7689 | 0.00066778 | 0 | 5.3889 | 0.00087678 | -0.029789 | 4.7689 | 0.00066778 | 0 | 5.3889 | 0.00087678 | -0.029789 |  | LF | AllSpc | 4770 | 0.668 | 4770 | 0.668 | 1.13 | 1.31 | -0.0062465 | 4770 | 0.668 | 4770 | 0.668 | 1.13 | 1.31 | -0.00625
LFAllSpcSCEGroExCZ16 | Com-Iltg-dWatt-LF_OSspc | SCE | Gro | Ex | CZ16 | 4.769 | 0.00066779 | 0 | 4.579 | 0.00083079 | -0.07579 | 4.769 | 0.00066779 | 0 | 4.579 | 0.00083079 | -0.07579 |  | LF | AllSpc | 4770 | 0.668 | 4770 | 0.668 | 0.96 | 1.24 | -0.015892 | 4770 | 0.668 | 4770 | 0.668 | 0.96 | 1.24 | -0.0159
LFAllSpcSCEGroExIOU | Com-Iltg-dWatt-LF_OSspc | SCE | Gro | Ex | IOU | 4.7692 | 0.00066784 | 0 | 5.0067 | 0.00085992 | -0.055712 | 4.7692 | 0.00066784 | 0 | 5.0067 | 0.00085992 | -0.055712 |  | LF | AllSpc | 4770 | 0.668 | 4770 | 0.668 | 1.05 | 1.29 | -0.011682 | 4770 | 0.668 | 4770 | 0.668 | 1.05 | 1.29 | -0.0117
LFAllSpcSCEGroNewCZ05 | Com-Iltg-dWatt-LF_OSspc | SCE | Gro | New | CZ05 | 4.76 | 0.000666 | 0 | 4.74 | 0.000835 | -0.0743 | 4.76 | 0.000666 | 0 | 4.74 | 0.000835 | -0.0743 |  | LF | AllSpc | 4760 | 0.666 | 4760 | 0.666 | 0.996 | 1.25 | -0.015609 | 4760 | 0.666 | 4760 | 0.666 | 0.996 | 1.25 | -0.0156
LFAllSpcSCEGroNewCZ06 | Com-Iltg-dWatt-LF_OSspc | SCE | Gro | New | CZ06 | 4.76 | 0.000666 | 0 | 5.11 | 0.000835 | -0.0467 | 4.76 | 0.000666 | 0 | 5.11 | 0.000835 | -0.0467 |  | LF | AllSpc | 4760 | 0.666 | 4760 | 0.666 | 1.07 | 1.25 | -0.0098109 | 4760 | 0.666 | 4760 | 0.666 | 1.07 | 1.25 | -0.00981
LFAllSpcSCEGroNewCZ08 | Com-Iltg-dWatt-LF_OSspc | SCE | Gro | New | CZ08 | 4.76 | 0.000666 | 0 | 5.16 | 0.000857 | -0.0412 | 4.76 | 0.000666 | 0 | 5.16 | 0.000857 | -0.0412 |  | LF | AllSpc | 4760 | 0.666 | 4760 | 0.666 | 1.08 | 1.29 | -0.0086555 | 4760 | 0.666 | 4760 | 0.666 | 1.08 | 1.29 | -0.00866
LFAllSpcSCEGroNewCZ09 | Com-Iltg-dWatt-LF_OSspc | SCE | Gro | New | CZ09 | 4.76 | 0.000666 | 0 | 5.15 | 0.000912 | -0.0441 | 4.76 | 0.000666 | 0 | 5.15 | 0.000912 | -0.0441 |  | LF | AllSpc | 4760 | 0.666 | 4760 | 0.666 | 1.08 | 1.37 | -0.0092647 | 4760 | 0.666 | 4760 | 0.666 | 1.08 | 1.37 | -0.00926
LFAllSpcSCEGroNewCZ10 | Com-Iltg-dWatt-LF_OSspc | SCE | Gro | New | CZ10 | 4.76 | 0.000666 | 0 | 5.19 | 0.000925 | -0.0439 | 4.76 | 0.000666 | 0 | 5.19 | 0.000925 | -0.0439 |  | LF | AllSpc | 4760 | 0.666 | 4760 | 0.666 | 1.09 | 1.39 | -0.0092227 | 4760 | 0.666 | 4760 | 0.666 | 1.09 | 1.39 | -0.00922
LFAllSpcSCEGroNewCZ13 | Com-Iltg-dWatt-LF_OSspc | SCE | Gro | New | CZ13 | 4.76 | 0.000666 | 0 | 5.19 | 0.000905 | -0.0509 | 4.76 | 0.000666 | 0 | 5.19 | 0.000905 | -0.0509 |  | LF | AllSpc | 4760 | 0.666 | 4760 | 0.666 | 1.09 | 1.36 | -0.010693 | 4760 | 0.666 | 4760 | 0.666 | 1.09 | 1.36 | -0.0107
LFAllSpcSCEGroNewCZ14 | Com-Iltg-dWatt-LF_OSspc | SCE | Gro | New | CZ14 | 4.76 | 0.000666 | 0 | 5.18 | 0.00092 | -0.0528 | 4.76 | 0.000666 | 0 | 5.18 | 0.00092 | -0.0528 |  | LF | AllSpc | 4760 | 0.666 | 4760 | 0.666 | 1.09 | 1.38 | -0.011092 | 4760 | 0.666 | 4760 | 0.666 | 1.09 | 1.38 | -0.0111
LFAllSpcSCEGroNewCZ15 | Com-Iltg-dWatt-LF_OSspc | SCE | Gro | New | CZ15 | 4.76 | 0.000666 | 0 | 5.6 | 0.000931 | -0.0243 | 4.76 | 0.000666 | 0 | 5.6 | 0.000931 | -0.0243 |  | LF | AllSpc | 4760 | 0.666 | 4760 | 0.666 | 1.18 | 1.4 | -0.005105 | 4760 | 0.666 | 4760 | 0.666 | 1.18 | 1.4 | -0.00511
LFAllSpcSCEGroNewCZ16 | Com-Iltg-dWatt-LF_OSspc | SCE | Gro | New | CZ16 | 4.76 | 0.000666 | 0 | 4.72 | 0.000851 | -0.0705 | 4.76 | 0.000666 | 0 | 4.72 | 0.000851 | -0.0705 |  | LF | AllSpc | 4760 | 0.666 | 4760 | 0.666 | 0.992 | 1.28 | -0.014811 | 4760 | 0.666 | 4760 | 0.666 | 0.992 | 1.28 | -0.0148
LFAllSpcSCEGroNewIOU | Com-Iltg-dWatt-LF_OSspc | SCE | Gro | New | IOU | 4.76 | 0.000666 | 0 | 5.1691 | 0.0008903 | -0.04459 | 4.76 | 0.000666 | 0 | 5.1691 | 0.0008903 | -0.04459 |  | LF | AllSpc | 4760 | 0.666 | 4760 | 0.666 | 1.09 | 1.34 | -0.0093677 | 4760 | 0.666 | 4760 | 0.666 | 1.09 | 1.34 | -0.00937
LFAllSpcSCEHspExCZ05 | Com-Iltg-dWatt-LF_OSspc | SCE | Hsp | Ex | CZ05 | 4.8796 | 0.00075896 | 0 | 5.4796 | 0.00093396 | -0.0335 | 4.8796 | 0.00075896 | 0 | 5.4796 | 0.00093396 | -0.0335 |  | LF | AllSpc | 4880 | 0.759 | 4880 | 0.759 | 1.12 | 1.23 | -0.0068653 | 4880 | 0.759 | 4880 | 0.759 | 1.12 | 1.23 | -0.00687
LFAllSpcSCEHspExCZ06 | Com-Iltg-dWatt-LF_OSspc | SCE | Hsp | Ex | CZ06 | 4.8796 | 0.00075896 | 0 | 5.6496 | 0.00095696 | -0.0247 | 4.8796 | 0.00075896 | 0 | 5.6496 | 0.00095696 | -0.0247 |  | LF | AllSpc | 4880 | 0.759 | 4880 | 0.759 | 1.16 | 1.26 | -0.0050619 | 4880 | 0.759 | 4880 | 0.759 | 1.16 | 1.26 | -0.00506
LFAllSpcSCEHspExCZ08 | Com-Iltg-dWatt-LF_OSspc | SCE | Hsp | Ex | CZ08 | 4.8796 | 0.00075896 | 0 | 5.6796 | 0.00095696 | -0.0243 | 4.8796 | 0.00075896 | 0 | 5.6796 | 0.00095696 | -0.0243 |  | LF | AllSpc | 4880 | 0.759 | 4880 | 0.759 | 1.16 | 1.26 | -0.0049799 | 4880 | 0.759 | 4880 | 0.759 | 1.16 | 1.26 | -0.00498
LFAllSpcSCEHspExCZ09 | Com-Iltg-dWatt-LF_OSspc | SCE | Hsp | Ex | CZ09 | 4.8795 | 0.00075895 | 0 | 5.7095 | 0.00098495 | -0.024695 | 4.8795 | 0.00075895 | 0 | 5.7095 | 0.00098495 | -0.024695 |  | LF | AllSpc | 4880 | 0.759 | 4880 | 0.759 | 1.17 | 1.3 | -0.005061 | 4880 | 0.759 | 4880 | 0.759 | 1.17 | 1.3 | -0.00506
LFAllSpcSCEHspExCZ10 | Com-Iltg-dWatt-LF_OSspc | SCE | Hsp | Ex | CZ10 | 4.8792 | 0.00075892 | 0 | 5.5692 | 0.00097284 | -0.0265 | 4.8792 | 0.00075892 | 0 | 5.5692 | 0.00097284 | -0.0265 |  | LF | AllSpc | 4880 | 0.759 | 4880 | 0.759 | 1.14 | 1.28 | -0.0054312 | 4880 | 0.759 | 4880 | 0.759 | 1.14 | 1.28 | -0.00543
LFAllSpcSCEHspExCZ13 | Com-Iltg-dWatt-LF_OSspc | SCE | Hsp | Ex | CZ13 | 4.8794 | 0.00075893 | 0 | 5.5394 | 0.00096894 | -0.03 | 4.8794 | 0.00075893 | 0 | 5.5394 | 0.00096894 | -0.03 |  | LF | AllSpc | 4880 | 0.759 | 4880 | 0.759 | 1.14 | 1.28 | -0.0061484 | 4880 | 0.759 | 4880 | 0.759 | 1.14 | 1.28 | -0.00615
LFAllSpcSCEHspExCZ14 | Com-Iltg-dWatt-LF_OSspc | SCE | Hsp | Ex | CZ14 | 4.8793 | 0.00075893 | 0 | 5.51 | 0.00096985 | -0.0325 | 4.8793 | 0.00075893 | 0 | 5.51 | 0.00096985 | -0.0325 |  | LF | AllSpc | 4880 | 0.759 | 4880 | 0.759 | 1.13 | 1.28 | -0.0066608 | 4880 | 0.759 | 4880 | 0.759 | 1.13 | 1.28 | -0.00666
LFAllSpcSCEHspExCZ15 | Com-Iltg-dWatt-LF_OSspc | SCE | Hsp | Ex | CZ15 | 4.8792 | 0.00075892 | 0 | 5.78 | 0.00098192 | -0.0209 | 4.8792 | 0.00075892 | 0 | 5.78 | 0.00098192 | -0.0209 |  | LF | AllSpc | 4880 | 0.759 | 4880 | 0.759 | 1.18 | 1.29 | -0.0042835 | 4880 | 0.759 | 4880 | 0.759 | 1.18 | 1.29 | -0.00428
LFAllSpcSCEHspExCZ16 | Com-Iltg-dWatt-LF_OSspc | SCE | Hsp | Ex | CZ16 | 4.8792 | 0.00075892 | 0 | 5.1892 | 0.00093892 | -0.0442 | 4.8792 | 0.00075892 | 0 | 5.1892 | 0.00093892 | -0.0442 |  | LF | AllSpc | 4880 | 0.759 | 4880 | 0.759 | 1.06 | 1.24 | -0.0090588 | 4880 | 0.759 | 4880 | 0.759 | 1.06 | 1.24 | -0.00906
LFAllSpcSCEHspExIOU | Com-Iltg-dWatt-LF_OSspc | SCE | Hsp | Ex | IOU | 4.8795 | 0.00075895 | 0 | 5.6394 | 0.00096424 | -0.025669 | 4.8795 | 0.00075895 | 0 | 5.6394 | 0.00096424 | -0.025669 |  | LF | AllSpc | 4880 | 0.759 | 4880 | 0.759 | 1.16 | 1.27 | -0.0052607 | 4880 | 0.759 | 4880 | 0.759 | 1.16 | 1.27 | -0.00526
LFAllSpcSCEHspNewCZ05 | Com-Iltg-dWatt-LF_OSspc | SCE | Hsp | New | CZ05 | 4.87 | 0.000758 | 0 | 5.17 | 0.000903 | -0.0338 | 4.87 | 0.000758 | 0 | 5.17 | 0.000903 | -0.0338 |  | LF | AllSpc | 4870 | 0.758 | 4870 | 0.758 | 1.06 | 1.19 | -0.0069405 | 4870 | 0.758 | 4870 | 0.758 | 1.06 | 1.19 | -0.00694
LFAllSpcSCEHspNewCZ06 | Com-Iltg-dWatt-LF_OSspc | SCE | Hsp | New | CZ06 | 4.87 | 0.000758 | 0 | 5.36 | 0.000918 | -0.0264 | 4.87 | 0.000758 | 0 | 5.36 | 0.000918 | -0.0264 |  | LF | AllSpc | 4870 | 0.758 | 4870 | 0.758 | 1.1 | 1.21 | -0.0054209 | 4870 | 0.758 | 4870 | 0.758 | 1.1 | 1.21 | -0.00542
LFAllSpcSCEHspNewCZ08 | Com-Iltg-dWatt-LF_OSspc | SCE | Hsp | New | CZ08 | 4.87 | 0.000758 | 0 | 5.41 | 0.000922 | -0.0246 | 4.87 | 0.000758 | 0 | 5.41 | 0.000922 | -0.0246 |  | LF | AllSpc | 4870 | 0.758 | 4870 | 0.758 | 1.11 | 1.22 | -0.0050513 | 4870 | 0.758 | 4870 | 0.758 | 1.11 | 1.22 | -0.00505
LFAllSpcSCEHspNewCZ09 | Com-Iltg-dWatt-LF_OSspc | SCE | Hsp | New | CZ09 | 4.87 | 0.000758 | 0 | 5.43 | 0.000949 | -0.0247 | 4.87 | 0.000758 | 0 | 5.43 | 0.000949 | -0.0247 |  | LF | AllSpc | 4870 | 0.758 | 4870 | 0.758 | 1.11 | 1.25 | -0.0050719 | 4870 | 0.758 | 4870 | 0.758 | 1.11 | 1.25 | -0.00507
LFAllSpcSCEHspNewCZ10 | Com-Iltg-dWatt-LF_OSspc | SCE | Hsp | New | CZ10 | 4.87 | 0.000758 | 0 | 5.41 | 0.000956 | -0.0262 | 4.87 | 0.000758 | 0 | 5.41 | 0.000956 | -0.0262 |  | LF | AllSpc | 4870 | 0.758 | 4870 | 0.758 | 1.11 | 1.26 | -0.0053799 | 4870 | 0.758 | 4870 | 0.758 | 1.11 | 1.26 | -0.00538
LFAllSpcSCEHspNewCZ13 | Com-Iltg-dWatt-LF_OSspc | SCE | Hsp | New | CZ13 | 4.87 | 0.000758 | 0 | 5.39 | 0.000949 | -0.0301 | 4.87 | 0.000758 | 0 | 5.39 | 0.000949 | -0.0301 |  | LF | AllSpc | 4870 | 0.758 | 4870 | 0.758 | 1.11 | 1.25 | -0.0061807 | 4870 | 0.758 | 4870 | 0.758 | 1.11 | 1.25 | -0.00618
LFAllSpcSCEHspNewCZ14 | Com-Iltg-dWatt-LF_OSspc | SCE | Hsp | New | CZ14 | 4.87 | 0.000758 | 0 | 5.33 | 0.000946 | -0.0333 | 4.87 | 0.000758 | 0 | 5.33 | 0.000946 | -0.0333 |  | LF | AllSpc | 4870 | 0.758 | 4870 | 0.758 | 1.09 | 1.25 | -0.0068378 | 4870 | 0.758 | 4870 | 0.758 | 1.09 | 1.25 | -0.00684
LFAllSpcSCEHspNewCZ15 | Com-Iltg-dWatt-LF_OSspc | SCE | Hsp | New | CZ15 | 4.87 | 0.000758 | 0 | 5.67 | 0.000965 | -0.0187 | 4.87 | 0.000758 | 0 | 5.67 | 0.000965 | -0.0187 |  | LF | AllSpc | 4870 | 0.758 | 4870 | 0.758 | 1.16 | 1.27 | -0.0038398 | 4870 | 0.758 | 4870 | 0.758 | 1.16 | 1.27 | -0.00384
LFAllSpcSCEHspNewCZ16 | Com-Iltg-dWatt-LF_OSspc | SCE | Hsp | New | CZ16 | 4.87 | 0.000758 | 0 | 4.97 | 0.000913 | -0.0477 | 4.87 | 0.000758 | 0 | 4.97 | 0.000913 | -0.0477 |  | LF | AllSpc | 4870 | 0.758 | 4870 | 0.758 | 1.02 | 1.2 | -0.0097947 | 4870 | 0.758 | 4870 | 0.758 | 1.02 | 1.2 | -0.00979
LFAllSpcSCEHspNewIOU | Com-Iltg-dWatt-LF_OSspc | SCE | Hsp | New | IOU | 4.87 | 0.000758 | 0 | 5.3952 | 0.0009371 | -0.026465 | 4.87 | 0.000758 | 0 | 5.3952 | 0.0009371 | -0.026465 |  | LF | AllSpc | 4870 | 0.758 | 4870 | 0.758 | 1.11 | 1.24 | -0.0054342 | 4870 | 0.758 | 4870 | 0.758 | 1.11 | 1.24 | -0.00543
LFAllSpcSCEHtlExCZ05 | Com-Iltg-dWatt-LF_OSspc | SCE | Htl | Ex | CZ05 | 1.6307 | 0.000207 | 0 | 1.6007 | 0.00026003 | -0.005772 | 1.6307 | 0.000207 | 0 | 1.6007 | 0.00026003 | -0.005772 |  | LF | AllSpc | 1630 | 0.207 | 1630 | 0.207 | 0.982 | 1.26 | -0.0035397 | 1630 | 0.207 | 1630 | 0.207 | 0.982 | 1.26 | -0.00354
LFAllSpcSCEHtlExCZ06 | Com-Iltg-dWatt-LF_OSspc | SCE | Htl | Ex | CZ06 | 1.6308 | 0.000207 | 0 | 1.7808 | 0.00026104 | -0.003812 | 1.6308 | 0.000207 | 0 | 1.7808 | 0.00026104 | -0.003812 |  | LF | AllSpc | 1630 | 0.207 | 1630 | 0.207 | 1.09 | 1.26 | -0.0023375 | 1630 | 0.207 | 1630 | 0.207 | 1.09 | 1.26 | -0.00234
LFAllSpcSCEHtlExCZ08 | Com-Iltg-dWatt-LF_OSspc | SCE | Htl | Ex | CZ08 | 1.6308 | 0.000207 | 0 | 1.8108 | 0.00026404 | -0.0033915 | 1.6308 | 0.000207 | 0 | 1.8108 | 0.00026404 | -0.0033915 |  | LF | AllSpc | 1630 | 0.207 | 1630 | 0.207 | 1.11 | 1.28 | -0.0020797 | 1630 | 0.207 | 1630 | 0.207 | 1.11 | 1.28 | -0.00208
LFAllSpcSCEHtlExCZ09 | Com-Iltg-dWatt-LF_OSspc | SCE | Htl | Ex | CZ09 | 1.631 | 0.000207 | 0 | 1.791 | 0.00026805 | -0.0034421 | 1.631 | 0.000207 | 0 | 1.791 | 0.00026805 | -0.0034421 |  | LF | AllSpc | 1630 | 0.207 | 1630 | 0.207 | 1.1 | 1.29 | -0.0021104 | 1630 | 0.207 | 1630 | 0.207 | 1.1 | 1.29 | -0.00211
LFAllSpcSCEHtlExCZ10 | Com-Iltg-dWatt-LF_OSspc | SCE | Htl | Ex | CZ10 | 1.6321 | 0.000207 | 0 | 1.7421 | 0.0002661 | -0.0036652 | 1.6321 | 0.000207 | 0 | 1.7421 | 0.0002661 | -0.0036652 |  | LF | AllSpc | 1630 | 0.207 | 1630 | 0.207 | 1.07 | 1.29 | -0.0022457 | 1630 | 0.207 | 1630 | 0.207 | 1.07 | 1.29 | -0.00225
LFAllSpcSCEHtlExCZ13 | Com-Iltg-dWatt-LF_OSspc | SCE | Htl | Ex | CZ13 | 1.6315 | 0.000207 | 0 | 1.6915 | 0.00026508 | -0.0049346 | 1.6315 | 0.000207 | 0 | 1.6915 | 0.00026508 | -0.0049346 |  | LF | AllSpc | 1630 | 0.207 | 1630 | 0.207 | 1.04 | 1.28 | -0.0030245 | 1630 | 0.207 | 1630 | 0.207 | 1.04 | 1.28 | -0.00302
LFAllSpcSCEHtlExCZ14 | Com-Iltg-dWatt-LF_OSspc | SCE | Htl | Ex | CZ14 | 1.6319 | 0.000207 | 0 | 1.6719 | 0.000268 | -0.0049748 | 1.6319 | 0.000207 | 0 | 1.6719 | 0.000268 | -0.0049748 |  | LF | AllSpc | 1630 | 0.207 | 1630 | 0.207 | 1.02 | 1.29 | -0.0030484 | 1630 | 0.207 | 1630 | 0.207 | 1.02 | 1.29 | -0.00305
LFAllSpcSCEHtlExCZ15 | Com-Iltg-dWatt-LF_OSspc | SCE | Htl | Ex | CZ15 | 1.6321 | 0.000207 | 0 | 1.8921 | 0.0002681 | -0.0020421 | 1.6321 | 0.000207 | 0 | 1.8921 | 0.0002681 | -0.0020421 |  | LF | AllSpc | 1630 | 0.207 | 1630 | 0.207 | 1.16 | 1.3 | -0.0012512 | 1630 | 0.207 | 1630 | 0.207 | 1.16 | 1.3 | -0.00125
LFAllSpcSCEHtlExCZ16 | Com-Iltg-dWatt-LF_OSspc | SCE | Htl | Ex | CZ16 | 1.6317 | 0.000207 | 0 | 1.4609 | 0.00025909 | -0.0085785 | 1.6317 | 0.000207 | 0 | 1.4609 | 0.00025909 | -0.0085785 |  | LF | AllSpc | 1630 | 0.207 | 1630 | 0.207 | 0.895 | 1.25 | -0.0052574 | 1630 | 0.207 | 1630 | 0.207 | 0.895 | 1.25 | -0.00526
LFAllSpcSCEHtlExIOU | Com-Iltg-dWatt-LF_OSspc | SCE | Htl | Ex | IOU | 1.6311 | 0.000207 | 0 | 1.7864 | 0.00026425 | -0.0036274 | 1.6311 | 0.000207 | 0 | 1.7864 | 0.00026425 | -0.0036274 |  | LF | AllSpc | 1630 | 0.207 | 1630 | 0.207 | 1.1 | 1.28 | -0.0022238 | 1630 | 0.207 | 1630 | 0.207 | 1.1 | 1.28 | -0.00222
LFAllSpcSCEHtlNewCZ05 | Com-Iltg-dWatt-LF_OSspc | SCE | Htl | New | CZ05 | 1.65 | 0.000207 | 0 | 1.53 | 0.000264 | -0.00656 | 1.65 | 0.000207 | 0 | 1.53 | 0.000264 | -0.00656 |  | LF | AllSpc | 1650 | 0.207 | 1650 | 0.207 | 0.927 | 1.28 | -0.0039758 | 1650 | 0.207 | 1650 | 0.207 | 0.927 | 1.28 | -0.00398
LFAllSpcSCEHtlNewCZ06 | Com-Iltg-dWatt-LF_OSspc | SCE | Htl | New | CZ06 | 1.65 | 0.000207 | 0 | 1.75 | 0.000268 | -0.00366 | 1.65 | 0.000207 | 0 | 1.75 | 0.000268 | -0.00366 |  | LF | AllSpc | 1650 | 0.207 | 1650 | 0.207 | 1.06 | 1.29 | -0.0022182 | 1650 | 0.207 | 1650 | 0.207 | 1.06 | 1.29 | -0.00222
LFAllSpcSCEHtlNewCZ08 | Com-Iltg-dWatt-LF_OSspc | SCE | Htl | New | CZ08 | 1.65 | 0.000207 | 0 | 1.78 | 0.00027 | -0.00315 | 1.65 | 0.000207 | 0 | 1.78 | 0.00027 | -0.00315 |  | LF | AllSpc | 1650 | 0.207 | 1650 | 0.207 | 1.08 | 1.3 | -0.0019091 | 1650 | 0.207 | 1650 | 0.207 | 1.08 | 1.3 | -0.00191
LFAllSpcSCEHtlNewCZ09 | Com-Iltg-dWatt-LF_OSspc | SCE | Htl | New | CZ09 | 1.65 | 0.000207 | 0 | 1.77 | 0.000276 | -0.00353 | 1.65 | 0.000207 | 0 | 1.77 | 0.000276 | -0.00353 |  | LF | AllSpc | 1650 | 0.207 | 1650 | 0.207 | 1.07 | 1.33 | -0.0021394 | 1650 | 0.207 | 1650 | 0.207 | 1.07 | 1.33 | -0.00214
LFAllSpcSCEHtlNewCZ10 | Com-Iltg-dWatt-LF_OSspc | SCE | Htl | New | CZ10 | 1.65 | 0.000207 | 0 | 1.75 | 0.00028 | -0.00407 | 1.65 | 0.000207 | 0 | 1.75 | 0.00028 | -0.00407 |  | LF | AllSpc | 1650 | 0.207 | 1650 | 0.207 | 1.06 | 1.35 | -0.0024667 | 1650 | 0.207 | 1650 | 0.207 | 1.06 | 1.35 | -0.00247
LFAllSpcSCEHtlNewCZ13 | Com-Iltg-dWatt-LF_OSspc | SCE | Htl | New | CZ13 | 1.65 | 0.000207 | 0 | 1.68 | 0.000276 | -0.0054 | 1.65 | 0.000207 | 0 | 1.68 | 0.000276 | -0.0054 |  | LF | AllSpc | 1650 | 0.207 | 1650 | 0.207 | 1.02 | 1.33 | -0.0032727 | 1650 | 0.207 | 1650 | 0.207 | 1.02 | 1.33 | -0.00327
LFAllSpcSCEHtlNewCZ14 | Com-Iltg-dWatt-LF_OSspc | SCE | Htl | New | CZ14 | 1.65 | 0.000207 | 0 | 1.65 | 0.000278 | -0.0061 | 1.65 | 0.000207 | 0 | 1.65 | 0.000278 | -0.0061 |  | LF | AllSpc | 1650 | 0.207 | 1650 | 0.207 | 1 | 1.34 | -0.003697 | 1650 | 0.207 | 1650 | 0.207 | 1 | 1.34 | -0.0037
LFAllSpcSCEHtlNewCZ15 | Com-Iltg-dWatt-LF_OSspc | SCE | Htl | New | CZ15 | 1.65 | 0.000207 | 0 | 1.93 | 0.000283 | -0.00211 | 1.65 | 0.000207 | 0 | 1.93 | 0.000283 | -0.00211 |  | LF | AllSpc | 1650 | 0.207 | 1650 | 0.207 | 1.17 | 1.37 | -0.0012788 | 1650 | 0.207 | 1650 | 0.207 | 1.17 | 1.37 | -0.00128
LFAllSpcSCEHtlNewCZ16 | Com-Iltg-dWatt-LF_OSspc | SCE | Htl | New | CZ16 | 1.65 | 0.000207 | 0 | 1.42 | 0.000265 | -0.0104 | 1.65 | 0.000207 | 0 | 1.42 | 0.000265 | -0.0104 |  | LF | AllSpc | 1650 | 0.207 | 1650 | 0.207 | 0.861 | 1.28 | -0.006303 | 1650 | 0.207 | 1650 | 0.207 | 0.861 | 1.28 | -0.0063
LFAllSpcSCEHtlNewIOU | Com-Iltg-dWatt-LF_OSspc | SCE | Htl | New | IOU | 1.65 | 0.000207 | 0 | 1.7802 | 0.00027501 | -0.0037183 | 1.65 | 0.000207 | 0 | 1.7802 | 0.00027501 | -0.0037183 |  | LF | AllSpc | 1650 | 0.207 | 1650 | 0.207 | 1.08 | 1.33 | -0.0022535 | 1650 | 0.207 | 1650 | 0.207 | 1.08 | 1.33 | -0.00225
LFAllSpcSCEMBTExCZ05 | Com-Iltg-dWatt-LF_OSspc | SCE | MBT | Ex | CZ05 | 3.0294 | 0.00072706 | 0 | 3.4794 | 0.00091306 | -0.00165 | 3.0294 | 0.00072706 | 0 | 3.4794 | 0.00091306 | -0.00165 |  | LF | AllSpc | 3030 | 0.727 | 3030 | 0.727 | 1.15 | 1.26 | -0.00054466 | 3030 | 0.727 | 3030 | 0.727 | 1.15 | 1.26 | -0.000545
LFAllSpcSCEMBTExCZ06 | Com-Iltg-dWatt-LF_OSspc | SCE | MBT | Ex | CZ06 | 3.0294 | 0.00072706 | 0 | 3.5594 | 0.00088906 | -0.00075589 | 3.0294 | 0.00072706 | 0 | 3.5594 | 0.00088906 | -0.00075589 |  | LF | AllSpc | 3030 | 0.727 | 3030 | 0.727 | 1.17 | 1.22 | -0.00024951 | 3030 | 0.727 | 3030 | 0.727 | 1.17 | 1.22 | -0.00025
LFAllSpcSCEMBTExCZ08 | Com-Iltg-dWatt-LF_OSspc | SCE | MBT | Ex | CZ08 | 3.0294 | 0.00072706 | 0 | 3.5794 | 0.000925 | -0.00050794 | 3.0294 | 0.00072706 | 0 | 3.5794 | 0.000925 | -0.00050794 |  | LF | AllSpc | 3030 | 0.727 | 3030 | 0.727 | 1.18 | 1.27 | -0.00016767 | 3030 | 0.727 | 3030 | 0.727 | 1.18 | 1.27 | -0.000168
LFAllSpcSCEMBTExCZ09 | Com-Iltg-dWatt-LF_OSspc | SCE | MBT | Ex | CZ09 | 3.0294 | 0.00072706 | 0 | 3.5594 | 0.000928 | -0.00091683 | 3.0294 | 0.00072706 | 0 | 3.5594 | 0.000928 | -0.00091683 |  | LF | AllSpc | 3030 | 0.727 | 3030 | 0.727 | 1.17 | 1.28 | -0.00030264 | 3030 | 0.727 | 3030 | 0.727 | 1.17 | 1.28 | -0.000303
LFAllSpcSCEMBTExCZ10 | Com-Iltg-dWatt-LF_OSspc | SCE | MBT | Ex | CZ10 | 3.0286 | 0.00072714 | 0 | 3.4586 | 0.00092914 | -0.00099772 | 3.0286 | 0.00072714 | 0 | 3.4586 | 0.00092914 | -0.00099772 |  | LF | AllSpc | 3030 | 0.727 | 3030 | 0.727 | 1.14 | 1.28 | -0.00032943 | 3030 | 0.727 | 3030 | 0.727 | 1.14 | 1.28 | -0.000329
LFAllSpcSCEMBTExCZ13 | Com-Iltg-dWatt-LF_OSspc | SCE | MBT | Ex | CZ13 | 3.0291 | 0.00072709 | 0 | 3.4491 | 0.000899 | -0.0021391 | 3.0291 | 0.00072709 | 0 | 3.4491 | 0.000899 | -0.0021391 |  | LF | AllSpc | 3030 | 0.727 | 3030 | 0.727 | 1.14 | 1.24 | -0.00070619 | 3030 | 0.727 | 3030 | 0.727 | 1.14 | 1.24 | -0.000706
LFAllSpcSCEMBTExCZ14 | Com-Iltg-dWatt-LF_OSspc | SCE | MBT | Ex | CZ14 | 3.029 | 0.0007271 | 0 | 3.459 | 0.0009281 | -0.002439 | 3.029 | 0.0007271 | 0 | 3.459 | 0.0009281 | -0.002439 |  | LF | AllSpc | 3030 | 0.727 | 3030 | 0.727 | 1.14 | 1.28 | -0.00080521 | 3030 | 0.727 | 3030 | 0.727 | 1.14 | 1.28 | -0.000805
LFAllSpcSCEMBTExCZ15 | Com-Iltg-dWatt-LF_OSspc | SCE | MBT | Ex | CZ15 | 3.0286 | 0.00072714 | 0 | 3.5986 | 0.00093214 | 0 | 3.0286 | 0.00072714 | 0 | 3.5986 | 0.00093214 | 0 |  | LF | AllSpc | 3030 | 0.727 | 3030 | 0.727 | 1.19 | 1.28 | 0 | 3030 | 0.727 | 3030 | 0.727 | 1.19 | 1.28 | 0
LFAllSpcSCEMBTExCZ16 | Com-Iltg-dWatt-LF_OSspc | SCE | MBT | Ex | CZ16 | 3.0289 | 0.00072711 | 0 | 3.2489 | 0.000875 | -0.0082878 | 3.0289 | 0.00072711 | 0 | 3.2489 | 0.000875 | -0.0082878 |  | LF | AllSpc | 3030 | 0.727 | 3030 | 0.727 | 1.07 | 1.2 | -0.0027362 | 3030 | 0.727 | 3030 | 0.727 | 1.07 | 1.2 | -0.00274
LFAllSpcSCEMBTExIOU | Com-Iltg-dWatt-LF_OSspc | SCE | MBT | Ex | IOU | 3.0292 | 0.00072708 | 0 | 3.5383 | 0.00091708 | -0.00095934 | 3.0292 | 0.00072708 | 0 | 3.5383 | 0.00091708 | -0.00095934 |  | LF | AllSpc | 3030 | 0.727 | 3030 | 0.727 | 1.17 | 1.26 | -0.0003167 | 3030 | 0.727 | 3030 | 0.727 | 1.17 | 1.26 | -0.000317
LFAllSpcSCEMBTNewCZ05 | Com-Iltg-dWatt-LF_OSspc | SCE | MBT | New | CZ05 | 3.02 | 0.000728 | 0 | 3.27 | 0.000904 | -0.00101 | 3.02 | 0.000728 | 0 | 3.27 | 0.000904 | -0.00101 |  | LF | AllSpc | 3020 | 0.728 | 3020 | 0.728 | 1.08 | 1.24 | -0.00033444 | 3020 | 0.728 | 3020 | 0.728 | 1.08 | 1.24 | -0.000334
LFAllSpcSCEMBTNewCZ06 | Com-Iltg-dWatt-LF_OSspc | SCE | MBT | New | CZ06 | 3.02 | 0.000728 | 0 | 3.39 | 0.000912 | -0.00101 | 3.02 | 0.000728 | 0 | 3.39 | 0.000912 | -0.00101 |  | LF | AllSpc | 3020 | 0.728 | 3020 | 0.728 | 1.12 | 1.25 | -0.00033444 | 3020 | 0.728 | 3020 | 0.728 | 1.12 | 1.25 | -0.000334
LFAllSpcSCEMBTNewCZ08 | Com-Iltg-dWatt-LF_OSspc | SCE | MBT | New | CZ08 | 3.02 | 0.000728 | 0 | 3.4 | 0.000936 | -0.000806 | 3.02 | 0.000728 | 0 | 3.4 | 0.000936 | -0.000806 |  | LF | AllSpc | 3020 | 0.728 | 3020 | 0.728 | 1.13 | 1.29 | -0.00026689 | 3020 | 0.728 | 3020 | 0.728 | 1.13 | 1.29 | -0.000267
LFAllSpcSCEMBTNewCZ09 | Com-Iltg-dWatt-LF_OSspc | SCE | MBT | New | CZ09 | 3.02 | 0.000728 | 0 | 3.39 | 0.000959 | -0.000951 | 3.02 | 0.000728 | 0 | 3.39 | 0.000959 | -0.000951 |  | LF | AllSpc | 3020 | 0.728 | 3020 | 0.728 | 1.12 | 1.32 | -0.0003149 | 3020 | 0.728 | 3020 | 0.728 | 1.12 | 1.32 | -0.000315
LFAllSpcSCEMBTNewCZ10 | Com-Iltg-dWatt-LF_OSspc | SCE | MBT | New | CZ10 | 3.02 | 0.000728 | 0 | 3.41 | 0.000974 | -0.00101 | 3.02 | 0.000728 | 0 | 3.41 | 0.000974 | -0.00101 |  | LF | AllSpc | 3020 | 0.728 | 3020 | 0.728 | 1.13 | 1.34 | -0.00033444 | 3020 | 0.728 | 3020 | 0.728 | 1.13 | 1.34 | -0.000334
LFAllSpcSCEMBTNewCZ13 | Com-Iltg-dWatt-LF_OSspc | SCE | MBT | New | CZ13 | 3.02 | 0.000728 | 0 | 3.37 | 0.000947 | -0.00176 | 3.02 | 0.000728 | 0 | 3.37 | 0.000947 | -0.00176 |  | LF | AllSpc | 3020 | 0.728 | 3020 | 0.728 | 1.12 | 1.3 | -0.00058278 | 3020 | 0.728 | 3020 | 0.728 | 1.12 | 1.3 | -0.000583
LFAllSpcSCEMBTNewCZ14 | Com-Iltg-dWatt-LF_OSspc | SCE | MBT | New | CZ14 | 3.02 | 0.000728 | 0 | 3.37 | 0.000962 | -0.00191 | 3.02 | 0.000728 | 0 | 3.37 | 0.000962 | -0.00191 |  | LF | AllSpc | 3020 | 0.728 | 3020 | 0.728 | 1.12 | 1.32 | -0.00063245 | 3020 | 0.728 | 3020 | 0.728 | 1.12 | 1.32 | -0.000632
LFAllSpcSCEMBTNewCZ15 | Com-Iltg-dWatt-LF_OSspc | SCE | MBT | New | CZ15 | 3.02 | 0.000728 | 0 | 3.58 | 0.000975 | 0 | 3.02 | 0.000728 | 0 | 3.58 | 0.000975 | 0 |  | LF | AllSpc | 3020 | 0.728 | 3020 | 0.728 | 1.19 | 1.34 | 0 | 3020 | 0.728 | 3020 | 0.728 | 1.19 | 1.34 | 0
LFAllSpcSCEMBTNewCZ16 | Com-Iltg-dWatt-LF_OSspc | SCE | MBT | New | CZ16 | 3.02 | 0.000728 | 0 | 3.2 | 0.000907 | -0.00607 | 3.02 | 0.000728 | 0 | 3.2 | 0.000907 | -0.00607 |  | LF | AllSpc | 3020 | 0.728 | 3020 | 0.728 | 1.06 | 1.25 | -0.0020099 | 3020 | 0.728 | 3020 | 0.728 | 1.06 | 1.25 | -0.00201
LFAllSpcSCEMBTNewIOU | Com-Iltg-dWatt-LF_OSspc | SCE | MBT | New | IOU | 3.02 | 0.000728 | 0 | 3.4116 | 0.00095118 | -0.001071 | 3.02 | 0.000728 | 0 | 3.4116 | 0.00095118 | -0.001071 |  | LF | AllSpc | 3020 | 0.728 | 3020 | 0.728 | 1.13 | 1.31 | -0.00035465 | 3020 | 0.728 | 3020 | 0.728 | 1.13 | 1.31 | -0.000355
LFAllSpcSCEMLIExCZ05 | Com-Iltg-dWatt-LF_OSspc | SCE | MLI | Ex | CZ05 | 2.83 | 0.000784 | 0 | 2.96 | 0.000957 | -0.015 | 2.83 | 0.000784 | 0 | 2.96 | 0.000957 | -0.015 |  | LF | AllSpc | 2830 | 0.784 | 2830 | 0.784 | 1.05 | 1.22 | -0.0053004 | 2830 | 0.784 | 2830 | 0.784 | 1.05 | 1.22 | -0.0053
LFAllSpcSCEMLIExCZ06 | Com-Iltg-dWatt-LF_OSspc | SCE | MLI | Ex | CZ06 | 2.83 | 0.000784 | 0 | 3.13 | 0.000941 | -0.0051206 | 2.83 | 0.000784 | 0 | 3.13 | 0.000941 | -0.0051206 |  | LF | AllSpc | 2830 | 0.784 | 2830 | 0.784 | 1.11 | 1.2 | -0.0018094 | 2830 | 0.784 | 2830 | 0.784 | 1.11 | 1.2 | -0.00181
LFAllSpcSCEMLIExCZ08 | Com-Iltg-dWatt-LF_OSspc | SCE | MLI | Ex | CZ08 | 2.83 | 0.000784 | 0 | 3.15 | 0.00094094 | -0.0041806 | 2.83 | 0.000784 | 0 | 3.15 | 0.00094094 | -0.0041806 |  | LF | AllSpc | 2830 | 0.784 | 2830 | 0.784 | 1.11 | 1.2 | -0.0014772 | 2830 | 0.784 | 2830 | 0.784 | 1.11 | 1.2 | -0.00148
LFAllSpcSCEMLIExCZ09 | Com-Iltg-dWatt-LF_OSspc | SCE | MLI | Ex | CZ09 | 2.83 | 0.000784 | 0 | 3.13 | 0.00096294 | -0.0058505 | 2.83 | 0.000784 | 0 | 3.13 | 0.00096294 | -0.0058505 |  | LF | AllSpc | 2830 | 0.784 | 2830 | 0.784 | 1.11 | 1.23 | -0.0020673 | 2830 | 0.784 | 2830 | 0.784 | 1.11 | 1.23 | -0.00207
LFAllSpcSCEMLIExCZ10 | Com-Iltg-dWatt-LF_OSspc | SCE | MLI | Ex | CZ10 | 2.83 | 0.000784 | 0 | 3.05 | 0.000954 | -0.0063914 | 2.83 | 0.000784 | 0 | 3.05 | 0.000954 | -0.0063914 |  | LF | AllSpc | 2830 | 0.784 | 2830 | 0.784 | 1.08 | 1.22 | -0.0022584 | 2830 | 0.784 | 2830 | 0.784 | 1.08 | 1.22 | -0.00226
LFAllSpcSCEMLIExCZ13 | Com-Iltg-dWatt-LF_OSspc | SCE | MLI | Ex | CZ13 | 2.83 | 0.000784 | 0 | 3.02 | 0.00094491 | -0.0153 | 2.83 | 0.000784 | 0 | 3.02 | 0.00094491 | -0.0153 |  | LF | AllSpc | 2830 | 0.784 | 2830 | 0.784 | 1.07 | 1.21 | -0.0054064 | 2830 | 0.784 | 2830 | 0.784 | 1.07 | 1.21 | -0.00541
LFAllSpcSCEMLIExCZ14 | Com-Iltg-dWatt-LF_OSspc | SCE | MLI | Ex | CZ14 | 2.83 | 0.000784 | 0 | 2.991 | 0.000949 | -0.0178 | 2.83 | 0.000784 | 0 | 2.991 | 0.000949 | -0.0178 |  | LF | AllSpc | 2830 | 0.784 | 2830 | 0.784 | 1.06 | 1.21 | -0.0062898 | 2830 | 0.784 | 2830 | 0.784 | 1.06 | 1.21 | -0.00629
LFAllSpcSCEMLIExCZ15 | Com-Iltg-dWatt-LF_OSspc | SCE | MLI | Ex | CZ15 | 2.83 | 0.000784 | 0 | 3.26 | 0.000946 | -0.0017 | 2.83 | 0.000784 | 0 | 3.26 | 0.000946 | -0.0017 |  | LF | AllSpc | 2830 | 0.784 | 2830 | 0.784 | 1.15 | 1.21 | -0.00060071 | 2830 | 0.784 | 2830 | 0.784 | 1.15 | 1.21 | -0.000601
LFAllSpcSCEMLIExCZ16 | Com-Iltg-dWatt-LF_OSspc | SCE | MLI | Ex | CZ16 | 2.83 | 0.000784 | 0 | 2.79 | 0.000932 | -0.0345 | 2.83 | 0.000784 | 0 | 2.79 | 0.000932 | -0.0345 |  | LF | AllSpc | 2830 | 0.784 | 2830 | 0.784 | 0.986 | 1.19 | -0.012191 | 2830 | 0.784 | 2830 | 0.784 | 0.986 | 1.19 | -0.0122
LFAllSpcSCEMLIExIOU | Com-Iltg-dWatt-LF_OSspc | SCE | MLI | Ex | IOU | 2.83 | 0.000784 | 0 | 3.1153 | 0.00094695 | -0.0063148 | 2.83 | 0.000784 | 0 | 3.1153 | 0.00094695 | -0.0063148 |  | LF | AllSpc | 2830 | 0.784 | 2830 | 0.784 | 1.1 | 1.21 | -0.0022314 | 2830 | 0.784 | 2830 | 0.784 | 1.1 | 1.21 | -0.00223
LFAllSpcSCEMLINewCZ05 | Com-Iltg-dWatt-LF_OSspc | SCE | MLI | New | CZ05 | 2.83 | 0.000784 | 0 | 2.85 | 0.000936 | -0.0183 | 2.83 | 0.000784 | 0 | 2.85 | 0.000936 | -0.0183 |  | LF | AllSpc | 2830 | 0.784 | 2830 | 0.784 | 1.01 | 1.19 | -0.0064664 | 2830 | 0.784 | 2830 | 0.784 | 1.01 | 1.19 | -0.00647
LFAllSpcSCEMLINewCZ06 | Com-Iltg-dWatt-LF_OSspc | SCE | MLI | New | CZ06 | 2.83 | 0.000784 | 0 | 3.04 | 0.000958 | -0.00793 | 2.83 | 0.000784 | 0 | 3.04 | 0.000958 | -0.00793 |  | LF | AllSpc | 2830 | 0.784 | 2830 | 0.784 | 1.07 | 1.22 | -0.0028021 | 2830 | 0.784 | 2830 | 0.784 | 1.07 | 1.22 | -0.0028
LFAllSpcSCEMLINewCZ08 | Com-Iltg-dWatt-LF_OSspc | SCE | MLI | New | CZ08 | 2.83 | 0.000784 | 0 | 3.08 | 0.000968 | -0.00617 | 2.83 | 0.000784 | 0 | 3.08 | 0.000968 | -0.00617 |  | LF | AllSpc | 2830 | 0.784 | 2830 | 0.784 | 1.09 | 1.23 | -0.0021802 | 2830 | 0.784 | 2830 | 0.784 | 1.09 | 1.23 | -0.00218
LFAllSpcSCEMLINewCZ09 | Com-Iltg-dWatt-LF_OSspc | SCE | MLI | New | CZ09 | 2.83 | 0.000784 | 0 | 3.1 | 0.00101 | -0.00705 | 2.83 | 0.000784 | 0 | 3.1 | 0.00101 | -0.00705 |  | LF | AllSpc | 2830 | 0.784 | 2830 | 0.784 | 1.1 | 1.29 | -0.0024912 | 2830 | 0.784 | 2830 | 0.784 | 1.1 | 1.29 | -0.00249
LFAllSpcSCEMLINewCZ10 | Com-Iltg-dWatt-LF_OSspc | SCE | MLI | New | CZ10 | 2.83 | 0.000784 | 0 | 3.12 | 0.00103 | -0.00759 | 2.83 | 0.000784 | 0 | 3.12 | 0.00103 | -0.00759 |  | LF | AllSpc | 2830 | 0.784 | 2830 | 0.784 | 1.1 | 1.31 | -0.002682 | 2830 | 0.784 | 2830 | 0.784 | 1.1 | 1.31 | -0.00268
LFAllSpcSCEMLINewCZ13 | Com-Iltg-dWatt-LF_OSspc | SCE | MLI | New | CZ13 | 2.83 | 0.000784 | 0 | 3.08 | 0.00101 | -0.0155 | 2.83 | 0.000784 | 0 | 3.08 | 0.00101 | -0.0155 |  | LF | AllSpc | 2830 | 0.784 | 2830 | 0.784 | 1.09 | 1.29 | -0.005477 | 2830 | 0.784 | 2830 | 0.784 | 1.09 | 1.29 | -0.00548
LFAllSpcSCEMLINewCZ14 | Com-Iltg-dWatt-LF_OSspc | SCE | MLI | New | CZ14 | 2.83 | 0.000784 | 0 | 3.07 | 0.00102 | -0.0172 | 2.83 | 0.000784 | 0 | 3.07 | 0.00102 | -0.0172 |  | LF | AllSpc | 2830 | 0.784 | 2830 | 0.784 | 1.08 | 1.3 | -0.0060777 | 2830 | 0.784 | 2830 | 0.784 | 1.08 | 1.3 | -0.00608
LFAllSpcSCEMLINewCZ15 | Com-Iltg-dWatt-LF_OSspc | SCE | MLI | New | CZ15 | 2.83 | 0.000784 | 0 | 3.32 | 0.00105 | -0.00118 | 2.83 | 0.000784 | 0 | 3.32 | 0.00105 | -0.00118 |  | LF | AllSpc | 2830 | 0.784 | 2830 | 0.784 | 1.17 | 1.34 | -0.00041696 | 2830 | 0.784 | 2830 | 0.784 | 1.17 | 1.34 | -0.000417
LFAllSpcSCEMLINewCZ16 | Com-Iltg-dWatt-LF_OSspc | SCE | MLI | New | CZ16 | 2.83 | 0.000784 | 0 | 2.83 | 0.000947 | -0.0337 | 2.83 | 0.000784 | 0 | 2.83 | 0.000947 | -0.0337 |  | LF | AllSpc | 2830 | 0.784 | 2830 | 0.784 | 1 | 1.21 | -0.011908 | 2830 | 0.784 | 2830 | 0.784 | 1 | 1.21 | -0.0119
LFAllSpcSCEMLINewIOU | Com-Iltg-dWatt-LF_OSspc | SCE | MLI | New | IOU | 2.83 | 0.000784 | 0 | 3.1058 | 0.0010016 | -0.0080836 | 2.83 | 0.000784 | 0 | 3.1058 | 0.0010016 | -0.0080836 |  | LF | AllSpc | 2830 | 0.784 | 2830 | 0.784 | 1.1 | 1.28 | -0.0028564 | 2830 | 0.784 | 2830 | 0.784 | 1.1 | 1.28 | -0.00286
LFAllSpcSCEMtlExCZ05 | Com-Iltg-dWatt-LF_OSspc | SCE | Mtl | Ex | CZ05 | 1.35 | 0.000148 | 0 | 1.4 | 0.000187 | -0.00764 | 1.35 | 0.000148 | 0 | 1.4 | 0.000187 | -0.00764 |  | LF | AllSpc | 1350 | 0.148 | 1350 | 0.148 | 1.04 | 1.26 | -0.0056593 | 1350 | 0.148 | 1350 | 0.148 | 1.04 | 1.26 | -0.00566
LFAllSpcSCEMtlExCZ06 | Com-Iltg-dWatt-LF_OSspc | SCE | Mtl | Ex | CZ06 | 1.35 | 0.000148 | 0 | 1.53 | 0.000188 | -0.004 | 1.35 | 0.000148 | 0 | 1.53 | 0.000188 | -0.004 |  | LF | AllSpc | 1350 | 0.148 | 1350 | 0.148 | 1.13 | 1.27 | -0.002963 | 1350 | 0.148 | 1350 | 0.148 | 1.13 | 1.27 | -0.00296
LFAllSpcSCEMtlExCZ08 | Com-Iltg-dWatt-LF_OSspc | SCE | Mtl | Ex | CZ08 | 1.35 | 0.000148 | 0 | 1.55 | 0.00019 | -0.00338 | 1.35 | 0.000148 | 0 | 1.55 | 0.00019 | -0.00338 |  | LF | AllSpc | 1350 | 0.148 | 1350 | 0.148 | 1.15 | 1.28 | -0.0025037 | 1350 | 0.148 | 1350 | 0.148 | 1.15 | 1.28 | -0.0025
LFAllSpcSCEMtlExCZ09 | Com-Iltg-dWatt-LF_OSspc | SCE | Mtl | Ex | CZ09 | 1.35 | 0.000148 | 0 | 1.54 | 0.00019505 | -0.00372 | 1.35 | 0.000148 | 0 | 1.54 | 0.00019505 | -0.00372 |  | LF | AllSpc | 1350 | 0.148 | 1350 | 0.148 | 1.14 | 1.32 | -0.0027556 | 1350 | 0.148 | 1350 | 0.148 | 1.14 | 1.32 | -0.00276
LFAllSpcSCEMtlExCZ10 | Com-Iltg-dWatt-LF_OSspc | SCE | Mtl | Ex | CZ10 | 1.35 | 0.000148 | 0 | 1.51 | 0.000195 | -0.004211 | 1.35 | 0.000148 | 0 | 1.51 | 0.000195 | -0.004211 |  | LF | AllSpc | 1350 | 0.148 | 1350 | 0.148 | 1.12 | 1.32 | -0.0031193 | 1350 | 0.148 | 1350 | 0.148 | 1.12 | 1.32 | -0.00312
LFAllSpcSCEMtlExCZ13 | Com-Iltg-dWatt-LF_OSspc | SCE | Mtl | Ex | CZ13 | 1.35 | 0.000148 | 0 | 1.47 | 0.000194 | -0.0058708 | 1.35 | 0.000148 | 0 | 1.47 | 0.000194 | -0.0058708 |  | LF | AllSpc | 1350 | 0.148 | 1350 | 0.148 | 1.09 | 1.31 | -0.0043487 | 1350 | 0.148 | 1350 | 0.148 | 1.09 | 1.31 | -0.00435
LFAllSpcSCEMtlExCZ14 | Com-Iltg-dWatt-LF_OSspc | SCE | Mtl | Ex | CZ14 | 1.35 | 0.000148 | 0 | 1.46 | 0.000195 | -0.00567 | 1.35 | 0.000148 | 0 | 1.46 | 0.000195 | -0.00567 |  | LF | AllSpc | 1350 | 0.148 | 1350 | 0.148 | 1.08 | 1.32 | -0.0042 | 1350 | 0.148 | 1350 | 0.148 | 1.08 | 1.32 | -0.0042
LFAllSpcSCEMtlExCZ15 | Com-Iltg-dWatt-LF_OSspc | SCE | Mtl | Ex | CZ15 | 1.35 | 0.000148 | 0 | 1.62 | 0.000198 | -0.00175 | 1.35 | 0.000148 | 0 | 1.62 | 0.000198 | -0.00175 |  | LF | AllSpc | 1350 | 0.148 | 1350 | 0.148 | 1.2 | 1.34 | -0.0012963 | 1350 | 0.148 | 1350 | 0.148 | 1.2 | 1.34 | -0.0013
LFAllSpcSCEMtlExCZ16 | Com-Iltg-dWatt-LF_OSspc | SCE | Mtl | Ex | CZ16 | 1.35 | 0.000148 | 0 | 1.3 | 0.000187 | -0.0099108 | 1.35 | 0.000148 | 0 | 1.3 | 0.000187 | -0.0099108 |  | LF | AllSpc | 1350 | 0.148 | 1350 | 0.148 | 0.963 | 1.26 | -0.0073414 | 1350 | 0.148 | 1350 | 0.148 | 0.963 | 1.26 | -0.00734
LFAllSpcSCEMtlExIOU | Com-Iltg-dWatt-LF_OSspc | SCE | Mtl | Ex | IOU | 1.35 | 0.000148 | 0 | 1.5362 | 0.00019157 | -0.0038063 | 1.35 | 0.000148 | 0 | 1.5362 | 0.00019157 | -0.0038063 |  | LF | AllSpc | 1350 | 0.148 | 1350 | 0.148 | 1.14 | 1.29 | -0.0028195 | 1350 | 0.148 | 1350 | 0.148 | 1.14 | 1.29 | -0.00282
LFAllSpcSCEMtlNewCZ05 | Com-Iltg-dWatt-LF_OSspc | SCE | Mtl | New | CZ05 | 1.35 | 0.000148 | 0 | 1.33 | 0.000189 | -0.0105 | 1.35 | 0.000148 | 0 | 1.33 | 0.000189 | -0.0105 |  | LF | AllSpc | 1350 | 0.148 | 1350 | 0.148 | 0.985 | 1.28 | -0.0077778 | 1350 | 0.148 | 1350 | 0.148 | 0.985 | 1.28 | -0.00778
LFAllSpcSCEMtlNewCZ06 | Com-Iltg-dWatt-LF_OSspc | SCE | Mtl | New | CZ06 | 1.35 | 0.000148 | 0 | 1.49 | 0.000192 | -0.00575 | 1.35 | 0.000148 | 0 | 1.49 | 0.000192 | -0.00575 |  | LF | AllSpc | 1350 | 0.148 | 1350 | 0.148 | 1.1 | 1.3 | -0.0042593 | 1350 | 0.148 | 1350 | 0.148 | 1.1 | 1.3 | -0.00426
LFAllSpcSCEMtlNewCZ08 | Com-Iltg-dWatt-LF_OSspc | SCE | Mtl | New | CZ08 | 1.35 | 0.000148 | 0 | 1.52 | 0.000195 | -0.00477 | 1.35 | 0.000148 | 0 | 1.52 | 0.000195 | -0.00477 |  | LF | AllSpc | 1350 | 0.148 | 1350 | 0.148 | 1.13 | 1.32 | -0.0035333 | 1350 | 0.148 | 1350 | 0.148 | 1.13 | 1.32 | -0.00353
LFAllSpcSCEMtlNewCZ09 | Com-Iltg-dWatt-LF_OSspc | SCE | Mtl | New | CZ09 | 1.35 | 0.000148 | 0 | 1.51 | 0.000198 | -0.00476 | 1.35 | 0.000148 | 0 | 1.51 | 0.000198 | -0.00476 |  | LF | AllSpc | 1350 | 0.148 | 1350 | 0.148 | 1.12 | 1.34 | -0.0035259 | 1350 | 0.148 | 1350 | 0.148 | 1.12 | 1.34 | -0.00353
LFAllSpcSCEMtlNewCZ10 | Com-Iltg-dWatt-LF_OSspc | SCE | Mtl | New | CZ10 | 1.35 | 0.000148 | 0 | 1.49 | 0.000199 | -0.00583 | 1.35 | 0.000148 | 0 | 1.49 | 0.000199 | -0.00583 |  | LF | AllSpc | 1350 | 0.148 | 1350 | 0.148 | 1.1 | 1.34 | -0.0043185 | 1350 | 0.148 | 1350 | 0.148 | 1.1 | 1.34 | -0.00432
LFAllSpcSCEMtlNewCZ13 | Com-Iltg-dWatt-LF_OSspc | SCE | Mtl | New | CZ13 | 1.35 | 0.000148 | 0 | 1.44 | 0.000196 | -0.0074 | 1.35 | 0.000148 | 0 | 1.44 | 0.000196 | -0.0074 |  | LF | AllSpc | 1350 | 0.148 | 1350 | 0.148 | 1.07 | 1.32 | -0.0054815 | 1350 | 0.148 | 1350 | 0.148 | 1.07 | 1.32 | -0.00548
LFAllSpcSCEMtlNewCZ14 | Com-Iltg-dWatt-LF_OSspc | SCE | Mtl | New | CZ14 | 1.35 | 0.000148 | 0 | 1.42 | 0.000199 | -0.0076 | 1.35 | 0.000148 | 0 | 1.42 | 0.000199 | -0.0076 |  | LF | AllSpc | 1350 | 0.148 | 1350 | 0.148 | 1.05 | 1.34 | -0.0056296 | 1350 | 0.148 | 1350 | 0.148 | 1.05 | 1.34 | -0.00563
LFAllSpcSCEMtlNewCZ15 | Com-Iltg-dWatt-LF_OSspc | SCE | Mtl | New | CZ15 | 1.35 | 0.000148 | 0 | 1.61 | 0.000203 | -0.00274 | 1.35 | 0.000148 | 0 | 1.61 | 0.000203 | -0.00274 |  | LF | AllSpc | 1350 | 0.148 | 1350 | 0.148 | 1.19 | 1.37 | -0.0020296 | 1350 | 0.148 | 1350 | 0.148 | 1.19 | 1.37 | -0.00203
LFAllSpcSCEMtlNewCZ16 | Com-Iltg-dWatt-LF_OSspc | SCE | Mtl | New | CZ16 | 1.35 | 0.000148 | 0 | 1.25 | 0.000188 | -0.0118 | 1.35 | 0.000148 | 0 | 1.25 | 0.000188 | -0.0118 |  | LF | AllSpc | 1350 | 0.148 | 1350 | 0.148 | 0.926 | 1.27 | -0.0087407 | 1350 | 0.148 | 1350 | 0.148 | 0.926 | 1.27 | -0.00874
LFAllSpcSCEMtlNewIOU | Com-Iltg-dWatt-LF_OSspc | SCE | Mtl | New | IOU | 1.35 | 0.000148 | 0 | 1.5112 | 0.00019706 | -0.0051361 | 1.35 | 0.000148 | 0 | 1.5112 | 0.00019706 | -0.0051361 |  | LF | AllSpc | 1350 | 0.148 | 1350 | 0.148 | 1.12 | 1.33 | -0.0038045 | 1350 | 0.148 | 1350 | 0.148 | 1.12 | 1.33 | -0.0038
LFAllSpcSCENrsExCZ05 | Com-Iltg-dWatt-LF_OSspc | SCE | Nrs | Ex | CZ05 | 3.6004 | 0.00058008 | 0 | 3.66 | 0.00071904 | -0.056904 | 3.6004 | 0.00058008 | 0 | 3.66 | 0.00071904 | -0.056904 |  | LF | AllSpc | 3600 | 0.58 | 3600 | 0.58 | 1.02 | 1.24 | -0.015805 | 3600 | 0.58 | 3600 | 0.58 | 1.02 | 1.24 | -0.0158
LFAllSpcSCENrsExCZ06 | Com-Iltg-dWatt-LF_OSspc | SCE | Nrs | Ex | CZ06 | 3.6004 | 0.00058008 | 0 | 3.9004 | 0.00075804 | -0.037804 | 3.6004 | 0.00058008 | 0 | 3.9004 | 0.00075804 | -0.037804 |  | LF | AllSpc | 3600 | 0.58 | 3600 | 0.58 | 1.08 | 1.31 | -0.0105 | 3600 | 0.58 | 3600 | 0.58 | 1.08 | 1.31 | -0.0105
LFAllSpcSCENrsExCZ08 | Com-Iltg-dWatt-LF_OSspc | SCE | Nrs | Ex | CZ08 | 3.6004 | 0.00058008 | 0 | 3.95 | 0.00075508 | -0.036704 | 3.6004 | 0.00058008 | 0 | 3.95 | 0.00075508 | -0.036704 |  | LF | AllSpc | 3600 | 0.58 | 3600 | 0.58 | 1.1 | 1.3 | -0.010194 | 3600 | 0.58 | 3600 | 0.58 | 1.1 | 1.3 | -0.0102
LFAllSpcSCENrsExCZ09 | Com-Iltg-dWatt-LF_OSspc | SCE | Nrs | Ex | CZ09 | 3.6005 | 0.0005801 | 0 | 3.9605 | 0.0007821 | -0.037405 | 3.6005 | 0.0005801 | 0 | 3.9605 | 0.0007821 | -0.037405 |  | LF | AllSpc | 3600 | 0.58 | 3600 | 0.58 | 1.1 | 1.35 | -0.010389 | 3600 | 0.58 | 3600 | 0.58 | 1.1 | 1.35 | -0.0104
LFAllSpcSCENrsExCZ10 | Com-Iltg-dWatt-LF_OSspc | SCE | Nrs | Ex | CZ10 | 3.6008 | 0.00058016 | 0 | 3.91 | 0.00078216 | -0.037408 | 3.6008 | 0.00058016 | 0 | 3.91 | 0.00078216 | -0.037408 |  | LF | AllSpc | 3600 | 0.58 | 3600 | 0.58 | 1.09 | 1.35 | -0.010389 | 3600 | 0.58 | 3600 | 0.58 | 1.09 | 1.35 | -0.0104
LFAllSpcSCENrsExCZ13 | Com-Iltg-dWatt-LF_OSspc | SCE | Nrs | Ex | CZ13 | 3.6007 | 0.00058013 | 0 | 3.87 | 0.00077213 | -0.0436 | 3.6007 | 0.00058013 | 0 | 3.87 | 0.00077213 | -0.0436 |  | LF | AllSpc | 3600 | 0.58 | 3600 | 0.58 | 1.07 | 1.33 | -0.012109 | 3600 | 0.58 | 3600 | 0.58 | 1.07 | 1.33 | -0.0121
LFAllSpcSCENrsExCZ14 | Com-Iltg-dWatt-LF_OSspc | SCE | Nrs | Ex | CZ14 | 3.6007 | 0.00058015 | 0 | 3.88 | 0.00077007 | -0.044607 | 3.6007 | 0.00058015 | 0 | 3.88 | 0.00077007 | -0.044607 |  | LF | AllSpc | 3600 | 0.58 | 3600 | 0.58 | 1.08 | 1.33 | -0.012388 | 3600 | 0.58 | 3600 | 0.58 | 1.08 | 1.33 | -0.0124
LFAllSpcSCENrsExCZ15 | Com-Iltg-dWatt-LF_OSspc | SCE | Nrs | Ex | CZ15 | 3.6008 | 0.00058016 | 0 | 4.1808 | 0.00078716 | -0.022608 | 3.6008 | 0.00058016 | 0 | 4.1808 | 0.00078716 | -0.022608 |  | LF | AllSpc | 3600 | 0.58 | 3600 | 0.58 | 1.16 | 1.36 | -0.0062786 | 3600 | 0.58 | 3600 | 0.58 | 1.16 | 1.36 | -0.00628
LFAllSpcSCENrsExCZ16 | Com-Iltg-dWatt-LF_OSspc | SCE | Nrs | Ex | CZ16 | 3.6008 | 0.00058015 | 0 | 3.57 | 0.00073708 | -0.064415 | 3.6008 | 0.00058015 | 0 | 3.57 | 0.00073708 | -0.064415 |  | LF | AllSpc | 3600 | 0.58 | 3600 | 0.58 | 0.991 | 1.27 | -0.017889 | 3600 | 0.58 | 3600 | 0.58 | 0.991 | 1.27 | -0.0179
LFAllSpcSCENrsExIOU | Com-Iltg-dWatt-LF_OSspc | SCE | Nrs | Ex | IOU | 3.6005 | 0.0005801 | 0 | 3.9216 | 0.00076495 | -0.038131 | 3.6005 | 0.0005801 | 0 | 3.9216 | 0.00076495 | -0.038131 |  | LF | AllSpc | 3600 | 0.58 | 3600 | 0.58 | 1.09 | 1.32 | -0.01059 | 3600 | 0.58 | 3600 | 0.58 | 1.09 | 1.32 | -0.0106
LFAllSpcSCENrsNewCZ05 | Com-Iltg-dWatt-LF_OSspc | SCE | Nrs | New | CZ05 | 3.61 | 0.000582 | 0 | 3.5 | 0.00071 | -0.0649 | 3.61 | 0.000582 | 0 | 3.5 | 0.00071 | -0.0649 |  | LF | AllSpc | 3610 | 0.582 | 3610 | 0.582 | 0.97 | 1.22 | -0.017978 | 3610 | 0.582 | 3610 | 0.582 | 0.97 | 1.22 | -0.018
LFAllSpcSCENrsNewCZ06 | Com-Iltg-dWatt-LF_OSspc | SCE | Nrs | New | CZ06 | 3.61 | 0.000582 | 0 | 3.73 | 0.000745 | -0.0415 | 3.61 | 0.000582 | 0 | 3.73 | 0.000745 | -0.0415 |  | LF | AllSpc | 3610 | 0.582 | 3610 | 0.582 | 1.03 | 1.28 | -0.011496 | 3610 | 0.582 | 3610 | 0.582 | 1.03 | 1.28 | -0.0115
LFAllSpcSCENrsNewCZ08 | Com-Iltg-dWatt-LF_OSspc | SCE | Nrs | New | CZ08 | 3.61 | 0.000582 | 0 | 3.8 | 0.00075 | -0.039 | 3.61 | 0.000582 | 0 | 3.8 | 0.00075 | -0.039 |  | LF | AllSpc | 3610 | 0.582 | 3610 | 0.582 | 1.05 | 1.29 | -0.010803 | 3610 | 0.582 | 3610 | 0.582 | 1.05 | 1.29 | -0.0108
LFAllSpcSCENrsNewCZ09 | Com-Iltg-dWatt-LF_OSspc | SCE | Nrs | New | CZ09 | 3.61 | 0.000582 | 0 | 3.82 | 0.000778 | -0.0397 | 3.61 | 0.000582 | 0 | 3.82 | 0.000778 | -0.0397 |  | LF | AllSpc | 3610 | 0.582 | 3610 | 0.582 | 1.06 | 1.34 | -0.010997 | 3610 | 0.582 | 3610 | 0.582 | 1.06 | 1.34 | -0.011
LFAllSpcSCENrsNewCZ10 | Com-Iltg-dWatt-LF_OSspc | SCE | Nrs | New | CZ10 | 3.61 | 0.000582 | 0 | 3.84 | 0.000781 | -0.0368 | 3.61 | 0.000582 | 0 | 3.84 | 0.000781 | -0.0368 |  | LF | AllSpc | 3610 | 0.582 | 3610 | 0.582 | 1.06 | 1.34 | -0.010194 | 3610 | 0.582 | 3610 | 0.582 | 1.06 | 1.34 | -0.0102
LFAllSpcSCENrsNewCZ13 | Com-Iltg-dWatt-LF_OSspc | SCE | Nrs | New | CZ13 | 3.61 | 0.000582 | 0 | 3.81 | 0.000773 | -0.0473 | 3.61 | 0.000582 | 0 | 3.81 | 0.000773 | -0.0473 |  | LF | AllSpc | 3610 | 0.582 | 3610 | 0.582 | 1.06 | 1.33 | -0.013102 | 3610 | 0.582 | 3610 | 0.582 | 1.06 | 1.33 | -0.0131
LFAllSpcSCENrsNewCZ14 | Com-Iltg-dWatt-LF_OSspc | SCE | Nrs | New | CZ14 | 3.61 | 0.000582 | 0 | 3.81 | 0.000757 | -0.0487 | 3.61 | 0.000582 | 0 | 3.81 | 0.000757 | -0.0487 |  | LF | AllSpc | 3610 | 0.582 | 3610 | 0.582 | 1.06 | 1.3 | -0.01349 | 3610 | 0.582 | 3610 | 0.582 | 1.06 | 1.3 | -0.0135
LFAllSpcSCENrsNewCZ15 | Com-Iltg-dWatt-LF_OSspc | SCE | Nrs | New | CZ15 | 3.61 | 0.000582 | 0 | 4.14 | 0.000776 | -0.0224 | 3.61 | 0.000582 | 0 | 4.14 | 0.000776 | -0.0224 |  | LF | AllSpc | 3610 | 0.582 | 3610 | 0.582 | 1.15 | 1.33 | -0.006205 | 3610 | 0.582 | 3610 | 0.582 | 1.15 | 1.33 | -0.00621
LFAllSpcSCENrsNewCZ16 | Com-Iltg-dWatt-LF_OSspc | SCE | Nrs | New | CZ16 | 3.61 | 0.000582 | 0 | 3.52 | 0.000731 | -0.07 | 3.61 | 0.000582 | 0 | 3.52 | 0.000731 | -0.07 |  | LF | AllSpc | 3610 | 0.582 | 3610 | 0.582 | 0.975 | 1.26 | -0.019391 | 3610 | 0.582 | 3610 | 0.582 | 0.975 | 1.26 | -0.0194
LFAllSpcSCENrsNewIOU | Com-Iltg-dWatt-LF_OSspc | SCE | Nrs | New | IOU | 3.61 | 0.000582 | 0 | 3.8037 | 0.00076202 | -0.04022 | 3.61 | 0.000582 | 0 | 3.8037 | 0.00076202 | -0.04022 |  | LF | AllSpc | 3610 | 0.582 | 3610 | 0.582 | 1.05 | 1.31 | -0.011141 | 3610 | 0.582 | 3610 | 0.582 | 1.05 | 1.31 | -0.0111
LFAllSpcSCEOfLExCZ05 | Com-Iltg-dWatt-LF_OSspc | SCE | OfL | Ex | CZ05 | 2.11 | 0.00057598 | 0 | 2.36 | 0.00073598 | -0.0145 | 2.11 | 0.00057598 | 0 | 2.36 | 0.00073598 | -0.0145 |  | LF | AllSpc | 2110 | 0.576 | 2110 | 0.576 | 1.12 | 1.28 | -0.006872 | 2110 | 0.576 | 2110 | 0.576 | 1.12 | 1.28 | -0.00687
LFAllSpcSCEOfLExCZ06 | Com-Iltg-dWatt-LF_OSspc | SCE | OfL | Ex | CZ06 | 2.11 | 0.00057597 | 0 | 2.47 | 0.000757 | -0.00942 | 2.11 | 0.00057597 | 0 | 2.47 | 0.000757 | -0.00942 |  | LF | AllSpc | 2110 | 0.576 | 2110 | 0.576 | 1.17 | 1.31 | -0.0044645 | 2110 | 0.576 | 2110 | 0.576 | 1.17 | 1.31 | -0.00446
LFAllSpcSCEOfLExCZ08 | Com-Iltg-dWatt-LF_OSspc | SCE | OfL | Ex | CZ08 | 2.11 | 0.00057597 | 0 | 2.48 | 0.00076497 | -0.00934 | 2.11 | 0.00057597 | 0 | 2.48 | 0.00076497 | -0.00934 |  | LF | AllSpc | 2110 | 0.576 | 2110 | 0.576 | 1.18 | 1.33 | -0.0044265 | 2110 | 0.576 | 2110 | 0.576 | 1.18 | 1.33 | -0.00443
LFAllSpcSCEOfLExCZ09 | Com-Iltg-dWatt-LF_OSspc | SCE | OfL | Ex | CZ09 | 2.11 | 0.00057596 | 0 | 2.47 | 0.00077796 | -0.0109 | 2.11 | 0.00057596 | 0 | 2.47 | 0.00077796 | -0.0109 |  | LF | AllSpc | 2110 | 0.576 | 2110 | 0.576 | 1.17 | 1.35 | -0.0051659 | 2110 | 0.576 | 2110 | 0.576 | 1.17 | 1.35 | -0.00517
LFAllSpcSCEOfLExCZ10 | Com-Iltg-dWatt-LF_OSspc | SCE | OfL | Ex | CZ10 | 2.11 | 0.00057591 | 0 | 2.46 | 0.00076891 | -0.0089191 | 2.11 | 0.00057591 | 0 | 2.46 | 0.00076891 | -0.0089191 |  | LF | AllSpc | 2110 | 0.576 | 2110 | 0.576 | 1.17 | 1.34 | -0.0042271 | 2110 | 0.576 | 2110 | 0.576 | 1.17 | 1.34 | -0.00423
LFAllSpcSCEOfLExCZ13 | Com-Iltg-dWatt-LF_OSspc | SCE | OfL | Ex | CZ13 | 2.11 | 0.00057593 | 0 | 2.44 | 0.00075493 | -0.0127 | 2.11 | 0.00057593 | 0 | 2.44 | 0.00075493 | -0.0127 |  | LF | AllSpc | 2110 | 0.576 | 2110 | 0.576 | 1.16 | 1.31 | -0.006019 | 2110 | 0.576 | 2110 | 0.576 | 1.16 | 1.31 | -0.00602
LFAllSpcSCEOfLExCZ14 | Com-Iltg-dWatt-LF_OSspc | SCE | OfL | Ex | CZ14 | 2.11 | 0.00057593 | 0 | 2.43 | 0.00076993 | -0.0117 | 2.11 | 0.00057593 | 0 | 2.43 | 0.00076993 | -0.0117 |  | LF | AllSpc | 2110 | 0.576 | 2110 | 0.576 | 1.15 | 1.34 | -0.005545 | 2110 | 0.576 | 2110 | 0.576 | 1.15 | 1.34 | -0.00555
LFAllSpcSCEOfLExCZ15 | Com-Iltg-dWatt-LF_OSspc | SCE | OfL | Ex | CZ15 | 2.11 | 0.00057591 | 0 | 2.59 | 0.00076791 | -0.0055891 | 2.11 | 0.00057591 | 0 | 2.59 | 0.00076791 | -0.0055891 |  | LF | AllSpc | 2110 | 0.576 | 2110 | 0.576 | 1.23 | 1.33 | -0.0026489 | 2110 | 0.576 | 2110 | 0.576 | 1.23 | 1.33 | -0.00265
LFAllSpcSCEOfLExCZ16 | Com-Iltg-dWatt-LF_OSspc | SCE | OfL | Ex | CZ16 | 2.11 | 0.00057593 | 0 | 2.27 | 0.00073293 | -0.0213 | 2.11 | 0.00057593 | 0 | 2.27 | 0.00073293 | -0.0213 |  | LF | AllSpc | 2110 | 0.576 | 2110 | 0.576 | 1.08 | 1.27 | -0.010095 | 2110 | 0.576 | 2110 | 0.576 | 1.08 | 1.27 | -0.0101
LFAllSpcSCEOfLExIOU | Com-Iltg-dWatt-LF_OSspc | SCE | OfL | Ex | IOU | 2.11 | 0.00057596 | 0 | 2.4723 | 0.00076543 | -0.0097738 | 2.11 | 0.00057596 | 0 | 2.4723 | 0.00076543 | -0.0097738 |  | LF | AllSpc | 2110 | 0.576 | 2110 | 0.576 | 1.17 | 1.33 | -0.0046321 | 2110 | 0.576 | 2110 | 0.576 | 1.17 | 1.33 | -0.00463
LFAllSpcSCEOfLNewCZ05 | Com-Iltg-dWatt-LF_OSspc | SCE | OfL | New | CZ05 | 2.11 | 0.000575 | 0 | 2.37 | 0.000717 | -0.00655 | 2.11 | 0.000575 | 0 | 2.37 | 0.000717 | -0.00655 |  | LF | AllSpc | 2110 | 0.575 | 2110 | 0.575 | 1.12 | 1.25 | -0.0031043 | 2110 | 0.575 | 2110 | 0.575 | 1.12 | 1.25 | -0.0031
LFAllSpcSCEOfLNewCZ06 | Com-Iltg-dWatt-LF_OSspc | SCE | OfL | New | CZ06 | 2.11 | 0.000575 | 0 | 2.46 | 0.00073 | -0.00388 | 2.11 | 0.000575 | 0 | 2.46 | 0.00073 | -0.00388 |  | LF | AllSpc | 2110 | 0.575 | 2110 | 0.575 | 1.17 | 1.27 | -0.0018389 | 2110 | 0.575 | 2110 | 0.575 | 1.17 | 1.27 | -0.00184
LFAllSpcSCEOfLNewCZ08 | Com-Iltg-dWatt-LF_OSspc | SCE | OfL | New | CZ08 | 2.11 | 0.000575 | 0 | 2.47 | 0.000738 | -0.00354 | 2.11 | 0.000575 | 0 | 2.47 | 0.000738 | -0.00354 |  | LF | AllSpc | 2110 | 0.575 | 2110 | 0.575 | 1.17 | 1.28 | -0.0016777 | 2110 | 0.575 | 2110 | 0.575 | 1.17 | 1.28 | -0.00168
LFAllSpcSCEOfLNewCZ09 | Com-Iltg-dWatt-LF_OSspc | SCE | OfL | New | CZ09 | 2.11 | 0.000575 | 0 | 2.47 | 0.000757 | -0.00506 | 2.11 | 0.000575 | 0 | 2.47 | 0.000757 | -0.00506 |  | LF | AllSpc | 2110 | 0.575 | 2110 | 0.575 | 1.17 | 1.32 | -0.0023981 | 2110 | 0.575 | 2110 | 0.575 | 1.17 | 1.32 | -0.0024
LFAllSpcSCEOfLNewCZ10 | Com-Iltg-dWatt-LF_OSspc | SCE | OfL | New | CZ10 | 2.11 | 0.000575 | 0 | 2.48 | 0.00076 | -0.00398 | 2.11 | 0.000575 | 0 | 2.48 | 0.00076 | -0.00398 |  | LF | AllSpc | 2110 | 0.575 | 2110 | 0.575 | 1.18 | 1.32 | -0.0018863 | 2110 | 0.575 | 2110 | 0.575 | 1.18 | 1.32 | -0.00189
LFAllSpcSCEOfLNewCZ13 | Com-Iltg-dWatt-LF_OSspc | SCE | OfL | New | CZ13 | 2.11 | 0.000575 | 0 | 2.43 | 0.000746 | -0.0063 | 2.11 | 0.000575 | 0 | 2.43 | 0.000746 | -0.0063 |  | LF | AllSpc | 2110 | 0.575 | 2110 | 0.575 | 1.15 | 1.3 | -0.0029858 | 2110 | 0.575 | 2110 | 0.575 | 1.15 | 1.3 | -0.00299
LFAllSpcSCEOfLNewCZ14 | Com-Iltg-dWatt-LF_OSspc | SCE | OfL | New | CZ14 | 2.11 | 0.000575 | 0 | 2.45 | 0.000763 | -0.00483 | 2.11 | 0.000575 | 0 | 2.45 | 0.000763 | -0.00483 |  | LF | AllSpc | 2110 | 0.575 | 2110 | 0.575 | 1.16 | 1.33 | -0.0022891 | 2110 | 0.575 | 2110 | 0.575 | 1.16 | 1.33 | -0.00229
LFAllSpcSCEOfLNewCZ15 | Com-Iltg-dWatt-LF_OSspc | SCE | OfL | New | CZ15 | 2.11 | 0.000575 | 0 | 2.58 | 0.000759 | -0.00221 | 2.11 | 0.000575 | 0 | 2.58 | 0.000759 | -0.00221 |  | LF | AllSpc | 2110 | 0.575 | 2110 | 0.575 | 1.22 | 1.32 | -0.0010474 | 2110 | 0.575 | 2110 | 0.575 | 1.22 | 1.32 | -0.00105
LFAllSpcSCEOfLNewCZ16 | Com-Iltg-dWatt-LF_OSspc | SCE | OfL | New | CZ16 | 2.11 | 0.000575 | 0 | 2.3 | 0.000726 | -0.0145 | 2.11 | 0.000575 | 0 | 2.3 | 0.000726 | -0.0145 |  | LF | AllSpc | 2110 | 0.575 | 2110 | 0.575 | 1.09 | 1.26 | -0.006872 | 2110 | 0.575 | 2110 | 0.575 | 1.09 | 1.26 | -0.00687
LFAllSpcSCEOfLNewIOU | Com-Iltg-dWatt-LF_OSspc | SCE | OfL | New | IOU | 2.11 | 0.000575 | 0 | 2.4716 | 0.00074693 | -0.00424 | 2.11 | 0.000575 | 0 | 2.4716 | 0.00074693 | -0.00424 |  | LF | AllSpc | 2110 | 0.575 | 2110 | 0.575 | 1.17 | 1.3 | -0.0020095 | 2110 | 0.575 | 2110 | 0.575 | 1.17 | 1.3 | -0.00201
LFAllSpcSCEOfSExCZ05 | Com-Iltg-dWatt-LF_OSspc | SCE | OfS | Ex | CZ05 | 1.8706 | 0.00051406 | 0 | 2.06 | 0.00064311 | -0.0058511 | 1.8706 | 0.00051406 | 0 | 2.06 | 0.00064311 | -0.0058511 |  | LF | AllSpc | 1870 | 0.514 | 1870 | 0.514 | 1.1 | 1.25 | -0.003128 | 1870 | 0.514 | 1870 | 0.514 | 1.1 | 1.25 | -0.00313
LFAllSpcSCEOfSExCZ06 | Com-Iltg-dWatt-LF_OSspc | SCE | OfS | Ex | CZ06 | 1.8706 | 0.00051406 | 0 | 2.1505 | 0.00065111 | -0.0028505 | 1.8706 | 0.00051406 | 0 | 2.1505 | 0.00065111 | -0.0028505 |  | LF | AllSpc | 1870 | 0.514 | 1870 | 0.514 | 1.15 | 1.27 | -0.0015239 | 1870 | 0.514 | 1870 | 0.514 | 1.15 | 1.27 | -0.00152
LFAllSpcSCEOfSExCZ08 | Com-Iltg-dWatt-LF_OSspc | SCE | OfS | Ex | CZ08 | 1.8706 | 0.00051406 | 0 | 2.17 | 0.00065611 | -0.0026406 | 1.8706 | 0.00051406 | 0 | 2.17 | 0.00065611 | -0.0026406 |  | LF | AllSpc | 1870 | 0.514 | 1870 | 0.514 | 1.16 | 1.28 | -0.0014116 | 1870 | 0.514 | 1870 | 0.514 | 1.16 | 1.28 | -0.00141
LFAllSpcSCEOfSExCZ09 | Com-Iltg-dWatt-LF_OSspc | SCE | OfS | Ex | CZ09 | 1.8705 | 0.00051405 | 0 | 2.16 | 0.00066305 | -0.0032105 | 1.8705 | 0.00051405 | 0 | 2.16 | 0.00066305 | -0.0032105 |  | LF | AllSpc | 1870 | 0.514 | 1870 | 0.514 | 1.15 | 1.29 | -0.0017164 | 1870 | 0.514 | 1870 | 0.514 | 1.15 | 1.29 | -0.00172
LFAllSpcSCEOfSExCZ10 | Com-Iltg-dWatt-LF_OSspc | SCE | OfS | Ex | CZ10 | 1.8709 | 0.00051409 | 0 | 2.13 | 0.00065617 | -0.0029809 | 1.8709 | 0.00051409 | 0 | 2.13 | 0.00065617 | -0.0029809 |  | LF | AllSpc | 1870 | 0.514 | 1870 | 0.514 | 1.14 | 1.28 | -0.0015933 | 1870 | 0.514 | 1870 | 0.514 | 1.14 | 1.28 | -0.00159
LFAllSpcSCEOfSExCZ13 | Com-Iltg-dWatt-LF_OSspc | SCE | OfS | Ex | CZ13 | 1.8706 | 0.00051406 | 0 | 2.0806 | 0.00065212 | -0.0072212 | 1.8706 | 0.00051406 | 0 | 2.0806 | 0.00065212 | -0.0072212 |  | LF | AllSpc | 1870 | 0.514 | 1870 | 0.514 | 1.11 | 1.27 | -0.0038604 | 1870 | 0.514 | 1870 | 0.514 | 1.11 | 1.27 | -0.00386
LFAllSpcSCEOfSExCZ14 | Com-Iltg-dWatt-LF_OSspc | SCE | OfS | Ex | CZ14 | 1.8708 | 0.00051408 | 0 | 2.09 | 0.00066416 | -0.0055516 | 1.8708 | 0.00051408 | 0 | 2.09 | 0.00066416 | -0.0055516 |  | LF | AllSpc | 1870 | 0.514 | 1870 | 0.514 | 1.12 | 1.29 | -0.0029675 | 1870 | 0.514 | 1870 | 0.514 | 1.12 | 1.29 | -0.00297
LFAllSpcSCEOfSExCZ15 | Com-Iltg-dWatt-LF_OSspc | SCE | OfS | Ex | CZ15 | 1.8709 | 0.00051409 | 0 | 2.2609 | 0.00065517 | -0.00090926 | 1.8709 | 0.00051409 | 0 | 2.2609 | 0.00065517 | -0.00090926 |  | LF | AllSpc | 1870 | 0.514 | 1870 | 0.514 | 1.21 | 1.27 | -0.00048601 | 1870 | 0.514 | 1870 | 0.514 | 1.21 | 1.27 | -0.000486
LFAllSpcSCEOfSExCZ16 | Com-Iltg-dWatt-LF_OSspc | SCE | OfS | Ex | CZ16 | 1.8707 | 0.00051407 | 0 | 1.8907 | 0.00063907 | -0.0137 | 1.8707 | 0.00051407 | 0 | 1.8907 | 0.00063907 | -0.0137 |  | LF | AllSpc | 1870 | 0.514 | 1870 | 0.514 | 1.01 | 1.24 | -0.0073234 | 1870 | 0.514 | 1870 | 0.514 | 1.01 | 1.24 | -0.00732
LFAllSpcSCEOfSExIOU | Com-Iltg-dWatt-LF_OSspc | SCE | OfS | Ex | IOU | 1.8706 | 0.00051406 | 0 | 2.1494 | 0.00065567 | -0.0032411 | 1.8706 | 0.00051406 | 0 | 2.1494 | 0.00065567 | -0.0032411 |  | LF | AllSpc | 1870 | 0.514 | 1870 | 0.514 | 1.15 | 1.28 | -0.0017326 | 1870 | 0.514 | 1870 | 0.514 | 1.15 | 1.28 | -0.00173
LFAllSpcSCEOfSNewCZ05 | Com-Iltg-dWatt-LF_OSspc | SCE | OfS | New | CZ05 | 1.88 | 0.000515 | 0 | 1.99 | 0.000637 | -0.0048 | 1.88 | 0.000515 | 0 | 1.99 | 0.000637 | -0.0048 |  | LF | AllSpc | 1880 | 0.515 | 1880 | 0.515 | 1.06 | 1.24 | -0.0025532 | 1880 | 0.515 | 1880 | 0.515 | 1.06 | 1.24 | -0.00255
LFAllSpcSCEOfSNewCZ06 | Com-Iltg-dWatt-LF_OSspc | SCE | OfS | New | CZ06 | 1.88 | 0.000515 | 0 | 2.09 | 0.000643 | -0.00192 | 1.88 | 0.000515 | 0 | 2.09 | 0.000643 | -0.00192 |  | LF | AllSpc | 1880 | 0.515 | 1880 | 0.515 | 1.11 | 1.25 | -0.0010213 | 1880 | 0.515 | 1880 | 0.515 | 1.11 | 1.25 | -0.00102
LFAllSpcSCEOfSNewCZ08 | Com-Iltg-dWatt-LF_OSspc | SCE | OfS | New | CZ08 | 1.88 | 0.000515 | 0 | 2.11 | 0.000653 | -0.00173 | 1.88 | 0.000515 | 0 | 2.11 | 0.000653 | -0.00173 |  | LF | AllSpc | 1880 | 0.515 | 1880 | 0.515 | 1.12 | 1.27 | -0.00092021 | 1880 | 0.515 | 1880 | 0.515 | 1.12 | 1.27 | -0.00092
LFAllSpcSCEOfSNewCZ09 | Com-Iltg-dWatt-LF_OSspc | SCE | OfS | New | CZ09 | 1.88 | 0.000515 | 0 | 2.11 | 0.000669 | -0.0019 | 1.88 | 0.000515 | 0 | 2.11 | 0.000669 | -0.0019 |  | LF | AllSpc | 1880 | 0.515 | 1880 | 0.515 | 1.12 | 1.3 | -0.0010106 | 1880 | 0.515 | 1880 | 0.515 | 1.12 | 1.3 | -0.00101
LFAllSpcSCEOfSNewCZ10 | Com-Iltg-dWatt-LF_OSspc | SCE | OfS | New | CZ10 | 1.88 | 0.000515 | 0 | 2.13 | 0.000676 | -0.00137 | 1.88 | 0.000515 | 0 | 2.13 | 0.000676 | -0.00137 |  | LF | AllSpc | 1880 | 0.515 | 1880 | 0.515 | 1.13 | 1.31 | -0.00072872 | 1880 | 0.515 | 1880 | 0.515 | 1.13 | 1.31 | -0.000729
LFAllSpcSCEOfSNewCZ13 | Com-Iltg-dWatt-LF_OSspc | SCE | OfS | New | CZ13 | 1.88 | 0.000515 | 0 | 2.07 | 0.000666 | -0.00536 | 1.88 | 0.000515 | 0 | 2.07 | 0.000666 | -0.00536 |  | LF | AllSpc | 1880 | 0.515 | 1880 | 0.515 | 1.1 | 1.29 | -0.0028511 | 1880 | 0.515 | 1880 | 0.515 | 1.1 | 1.29 | -0.00285
LFAllSpcSCEOfSNewCZ14 | Com-Iltg-dWatt-LF_OSspc | SCE | OfS | New | CZ14 | 1.88 | 0.000515 | 0 | 2.08 | 0.000675 | -0.00429 | 1.88 | 0.000515 | 0 | 2.08 | 0.000675 | -0.00429 |  | LF | AllSpc | 1880 | 0.515 | 1880 | 0.515 | 1.11 | 1.31 | -0.0022819 | 1880 | 0.515 | 1880 | 0.515 | 1.11 | 1.31 | -0.00228
LFAllSpcSCEOfSNewCZ15 | Com-Iltg-dWatt-LF_OSspc | SCE | OfS | New | CZ15 | 1.88 | 0.000515 | 0 | 2.23 | 0.000684 | -0.000123 | 1.88 | 0.000515 | 0 | 2.23 | 0.000684 | -0.000123 |  | LF | AllSpc | 1880 | 0.515 | 1880 | 0.515 | 1.19 | 1.33 | -6.5426e-05 | 1880 | 0.515 | 1880 | 0.515 | 1.19 | 1.33 | -6.54e-05
LFAllSpcSCEOfSNewCZ16 | Com-Iltg-dWatt-LF_OSspc | SCE | OfS | New | CZ16 | 1.88 | 0.000515 | 0 | 1.9 | 0.000643 | -0.0124 | 1.88 | 0.000515 | 0 | 1.9 | 0.000643 | -0.0124 |  | LF | AllSpc | 1880 | 0.515 | 1880 | 0.515 | 1.01 | 1.25 | -0.0065957 | 1880 | 0.515 | 1880 | 0.515 | 1.01 | 1.25 | -0.0066
LFAllSpcSCEOfSNewIOU | Com-Iltg-dWatt-LF_OSspc | SCE | OfS | New | IOU | 1.88 | 0.000515 | 0 | 2.1144 | 0.00066319 | -0.0020122 | 1.88 | 0.000515 | 0 | 2.1144 | 0.00066319 | -0.0020122 |  | LF | AllSpc | 1880 | 0.515 | 1880 | 0.515 | 1.12 | 1.29 | -0.0010703 | 1880 | 0.515 | 1880 | 0.515 | 1.12 | 1.29 | -0.00107
LFAllSpcSCERFFExCZ05 | Com-Iltg-dWatt-LF_OSspc | SCE | RFF | Ex | CZ05 | 4.02 | 0.000691 | 0 | 4.18 | 0.000828 | -0.0414 | 4.02 | 0.000691 | 0 | 4.18 | 0.000828 | -0.0414 |  | LF | AllSpc | 4020 | 0.691 | 4020 | 0.691 | 1.04 | 1.2 | -0.010299 | 4020 | 0.691 | 4020 | 0.691 | 1.04 | 1.2 | -0.0103
LFAllSpcSCERFFExCZ06 | Com-Iltg-dWatt-LF_OSspc | SCE | RFF | Ex | CZ06 | 4.02 | 0.000691 | 0 | 4.4 | 0.000845 | -0.0226 | 4.02 | 0.000691 | 0 | 4.4 | 0.000845 | -0.0226 |  | LF | AllSpc | 4020 | 0.691 | 4020 | 0.691 | 1.09 | 1.22 | -0.0056219 | 4020 | 0.691 | 4020 | 0.691 | 1.09 | 1.22 | -0.00562
LFAllSpcSCERFFExCZ08 | Com-Iltg-dWatt-LF_OSspc | SCE | RFF | Ex | CZ08 | 4.02 | 0.000691 | 0 | 4.44 | 0.000838 | -0.02 | 4.02 | 0.000691 | 0 | 4.44 | 0.000838 | -0.02 |  | LF | AllSpc | 4020 | 0.691 | 4020 | 0.691 | 1.1 | 1.21 | -0.0049751 | 4020 | 0.691 | 4020 | 0.691 | 1.1 | 1.21 | -0.00498
LFAllSpcSCERFFExCZ09 | Com-Iltg-dWatt-LF_OSspc | SCE | RFF | Ex | CZ09 | 4.02 | 0.000691 | 0 | 4.45 | 0.000857 | -0.0207 | 4.02 | 0.000691 | 0 | 4.45 | 0.000857 | -0.0207 |  | LF | AllSpc | 4020 | 0.691 | 4020 | 0.691 | 1.11 | 1.24 | -0.0051493 | 4020 | 0.691 | 4020 | 0.691 | 1.11 | 1.24 | -0.00515
LFAllSpcSCERFFExCZ10 | Com-Iltg-dWatt-LF_OSspc | SCE | RFF | Ex | CZ10 | 4.02 | 0.000691 | 0 | 4.36 | 0.000842 | -0.0231 | 4.02 | 0.000691 | 0 | 4.36 | 0.000842 | -0.0231 |  | LF | AllSpc | 4020 | 0.691 | 4020 | 0.691 | 1.08 | 1.22 | -0.0057463 | 4020 | 0.691 | 4020 | 0.691 | 1.08 | 1.22 | -0.00575
LFAllSpcSCERFFExCZ13 | Com-Iltg-dWatt-LF_OSspc | SCE | RFF | Ex | CZ13 | 4.02 | 0.000691 | 0 | 4.36 | 0.000848 | -0.0309 | 4.02 | 0.000691 | 0 | 4.36 | 0.000848 | -0.0309 |  | LF | AllSpc | 4020 | 0.691 | 4020 | 0.691 | 1.08 | 1.23 | -0.0076866 | 4020 | 0.691 | 4020 | 0.691 | 1.08 | 1.23 | -0.00769
LFAllSpcSCERFFExCZ14 | Com-Iltg-dWatt-LF_OSspc | SCE | RFF | Ex | CZ14 | 4.02 | 0.000691 | 0 | 4.32 | 0.000856 | -0.0325 | 4.02 | 0.000691 | 0 | 4.32 | 0.000856 | -0.0325 |  | LF | AllSpc | 4020 | 0.691 | 4020 | 0.691 | 1.07 | 1.24 | -0.0080846 | 4020 | 0.691 | 4020 | 0.691 | 1.07 | 1.24 | -0.00808
LFAllSpcSCERFFExCZ15 | Com-Iltg-dWatt-LF_OSspc | SCE | RFF | Ex | CZ15 | 4.02 | 0.000691 | 0 | 4.64 | 0.000852 | -0.0106 | 4.02 | 0.000691 | 0 | 4.64 | 0.000852 | -0.0106 |  | LF | AllSpc | 4020 | 0.691 | 4020 | 0.691 | 1.15 | 1.23 | -0.0026368 | 4020 | 0.691 | 4020 | 0.691 | 1.15 | 1.23 | -0.00264
LFAllSpcSCERFFExCZ16 | Com-Iltg-dWatt-LF_OSspc | SCE | RFF | Ex | CZ16 | 4.02 | 0.000691 | 0 | 4.02 | 0.000828 | -0.0591 | 4.02 | 0.000691 | 0 | 4.02 | 0.000828 | -0.0591 |  | LF | AllSpc | 4020 | 0.691 | 4020 | 0.691 | 1 | 1.2 | -0.014701 | 4020 | 0.691 | 4020 | 0.691 | 1 | 1.2 | -0.0147
LFAllSpcSCERFFExIOU | Com-Iltg-dWatt-LF_OSspc | SCE | RFF | Ex | IOU | 4.02 | 0.000691 | 0 | 4.4072 | 0.00084476 | -0.022573 | 4.02 | 0.000691 | 0 | 4.4072 | 0.00084476 | -0.022573 |  | LF | AllSpc | 4020 | 0.691 | 4020 | 0.691 | 1.1 | 1.22 | -0.0056152 | 4020 | 0.691 | 4020 | 0.691 | 1.1 | 1.22 | -0.00562
LFAllSpcSCERFFNewCZ05 | Com-Iltg-dWatt-LF_OSspc | SCE | RFF | New | CZ05 | 4.02 | 0.000691 | 0 | 4.13 | 0.000843 | -0.0406 | 4.02 | 0.000691 | 0 | 4.13 | 0.000843 | -0.0406 |  | LF | AllSpc | 4020 | 0.691 | 4020 | 0.691 | 1.03 | 1.22 | -0.0101 | 4020 | 0.691 | 4020 | 0.691 | 1.03 | 1.22 | -0.0101
LFAllSpcSCERFFNewCZ06 | Com-Iltg-dWatt-LF_OSspc | SCE | RFF | New | CZ06 | 4.02 | 0.000691 | 0 | 4.34 | 0.000867 | -0.022 | 4.02 | 0.000691 | 0 | 4.34 | 0.000867 | -0.022 |  | LF | AllSpc | 4020 | 0.691 | 4020 | 0.691 | 1.08 | 1.25 | -0.0054726 | 4020 | 0.691 | 4020 | 0.691 | 1.08 | 1.25 | -0.00547
LFAllSpcSCERFFNewCZ08 | Com-Iltg-dWatt-LF_OSspc | SCE | RFF | New | CZ08 | 4.02 | 0.000691 | 0 | 4.41 | 0.000872 | -0.0239 | 4.02 | 0.000691 | 0 | 4.41 | 0.000872 | -0.0239 |  | LF | AllSpc | 4020 | 0.691 | 4020 | 0.691 | 1.1 | 1.26 | -0.0059453 | 4020 | 0.691 | 4020 | 0.691 | 1.1 | 1.26 | -0.00595
LFAllSpcSCERFFNewCZ09 | Com-Iltg-dWatt-LF_OSspc | SCE | RFF | New | CZ09 | 4.02 | 0.000691 | 0 | 4.44 | 0.000902 | -0.0258 | 4.02 | 0.000691 | 0 | 4.44 | 0.000902 | -0.0258 |  | LF | AllSpc | 4020 | 0.691 | 4020 | 0.691 | 1.1 | 1.31 | -0.0064179 | 4020 | 0.691 | 4020 | 0.691 | 1.1 | 1.31 | -0.00642
LFAllSpcSCERFFNewCZ10 | Com-Iltg-dWatt-LF_OSspc | SCE | RFF | New | CZ10 | 4.02 | 0.000691 | 0 | 4.46 | 0.000909 | -0.0265 | 4.02 | 0.000691 | 0 | 4.46 | 0.000909 | -0.0265 |  | LF | AllSpc | 4020 | 0.691 | 4020 | 0.691 | 1.11 | 1.32 | -0.006592 | 4020 | 0.691 | 4020 | 0.691 | 1.11 | 1.32 | -0.00659
LFAllSpcSCERFFNewCZ13 | Com-Iltg-dWatt-LF_OSspc | SCE | RFF | New | CZ13 | 4.02 | 0.000691 | 0 | 4.44 | 0.000905 | -0.0356 | 4.02 | 0.000691 | 0 | 4.44 | 0.000905 | -0.0356 |  | LF | AllSpc | 4020 | 0.691 | 4020 | 0.691 | 1.1 | 1.31 | -0.0088557 | 4020 | 0.691 | 4020 | 0.691 | 1.1 | 1.31 | -0.00886
LFAllSpcSCERFFNewCZ14 | Com-Iltg-dWatt-LF_OSspc | SCE | RFF | New | CZ14 | 4.02 | 0.000691 | 0 | 4.44 | 0.000912 | -0.0376 | 4.02 | 0.000691 | 0 | 4.44 | 0.000912 | -0.0376 |  | LF | AllSpc | 4020 | 0.691 | 4020 | 0.691 | 1.1 | 1.32 | -0.0093532 | 4020 | 0.691 | 4020 | 0.691 | 1.1 | 1.32 | -0.00935
LFAllSpcSCERFFNewCZ15 | Com-Iltg-dWatt-LF_OSspc | SCE | RFF | New | CZ15 | 4.02 | 0.000691 | 0 | 4.77 | 0.000925 | -0.013 | 4.02 | 0.000691 | 0 | 4.77 | 0.000925 | -0.013 |  | LF | AllSpc | 4020 | 0.691 | 4020 | 0.691 | 1.19 | 1.34 | -0.0032338 | 4020 | 0.691 | 4020 | 0.691 | 1.19 | 1.34 | -0.00323
LFAllSpcSCERFFNewCZ16 | Com-Iltg-dWatt-LF_OSspc | SCE | RFF | New | CZ16 | 4.02 | 0.000691 | 0 | 4.08 | 0.000864 | -0.0635 | 4.02 | 0.000691 | 0 | 4.08 | 0.000864 | -0.0635 |  | LF | AllSpc | 4020 | 0.691 | 4020 | 0.691 | 1.01 | 1.25 | -0.015796 | 4020 | 0.691 | 4020 | 0.691 | 1.01 | 1.25 | -0.0158
LFAllSpcSCERFFNewIOU | Com-Iltg-dWatt-LF_OSspc | SCE | RFF | New | IOU | 4.02 | 0.000691 | 0 | 4.4268 | 0.00089023 | -0.02567 | 4.02 | 0.000691 | 0 | 4.4268 | 0.00089023 | -0.02567 |  | LF | AllSpc | 4020 | 0.691 | 4020 | 0.691 | 1.1 | 1.29 | -0.0063854 | 4020 | 0.691 | 4020 | 0.691 | 1.1 | 1.29 | -0.00639
LFAllSpcSCERSDExCZ05 | Com-Iltg-dWatt-LF_OSspc | SCE | RSD | Ex | CZ05 | 3.87 | 0.000679 | 0 | 4.01 | 0.000835 | -0.0457 | 3.87 | 0.000679 | 0 | 4.01 | 0.000835 | -0.0457 |  | LF | AllSpc | 3870 | 0.679 | 3870 | 0.679 | 1.04 | 1.23 | -0.011809 | 3870 | 0.679 | 3870 | 0.679 | 1.04 | 1.23 | -0.0118
LFAllSpcSCERSDExCZ06 | Com-Iltg-dWatt-LF_OSspc | SCE | RSD | Ex | CZ06 | 3.87 | 0.000679 | 0 | 4.29 | 0.000843 | -0.0237 | 3.87 | 0.000679 | 0 | 4.29 | 0.000843 | -0.0237 |  | LF | AllSpc | 3870 | 0.679 | 3870 | 0.679 | 1.11 | 1.24 | -0.006124 | 3870 | 0.679 | 3870 | 0.679 | 1.11 | 1.24 | -0.00612
LFAllSpcSCERSDExCZ08 | Com-Iltg-dWatt-LF_OSspc | SCE | RSD | Ex | CZ08 | 3.87 | 0.000679 | 0 | 4.32 | 0.000818 | -0.0196 | 3.87 | 0.000679 | 0 | 4.32 | 0.000818 | -0.0196 |  | LF | AllSpc | 3870 | 0.679 | 3870 | 0.679 | 1.12 | 1.2 | -0.0050646 | 3870 | 0.679 | 3870 | 0.679 | 1.12 | 1.2 | -0.00506
LFAllSpcSCERSDExCZ09 | Com-Iltg-dWatt-LF_OSspc | SCE | RSD | Ex | CZ09 | 3.87 | 0.000679 | 0 | 4.31 | 0.000824 | -0.0222 | 3.87 | 0.000679 | 0 | 4.31 | 0.000824 | -0.0222 |  | LF | AllSpc | 3870 | 0.679 | 3870 | 0.679 | 1.11 | 1.21 | -0.0057364 | 3870 | 0.679 | 3870 | 0.679 | 1.11 | 1.21 | -0.00574
LFAllSpcSCERSDExCZ10 | Com-Iltg-dWatt-LF_OSspc | SCE | RSD | Ex | CZ10 | 3.87 | 0.000679 | 0 | 4.24 | 0.000782 | -0.0232 | 3.87 | 0.000679 | 0 | 4.24 | 0.000782 | -0.0232 |  | LF | AllSpc | 3870 | 0.679 | 3870 | 0.679 | 1.1 | 1.15 | -0.0059948 | 3870 | 0.679 | 3870 | 0.679 | 1.1 | 1.15 | -0.00599
LFAllSpcSCERSDExCZ13 | Com-Iltg-dWatt-LF_OSspc | SCE | RSD | Ex | CZ13 | 3.87 | 0.000679 | 0 | 4.18 | 0.000845 | -0.0355 | 3.87 | 0.000679 | 0 | 4.18 | 0.000845 | -0.0355 |  | LF | AllSpc | 3870 | 0.679 | 3870 | 0.679 | 1.08 | 1.24 | -0.0091731 | 3870 | 0.679 | 3870 | 0.679 | 1.08 | 1.24 | -0.00917
LFAllSpcSCERSDExCZ14 | Com-Iltg-dWatt-LF_OSspc | SCE | RSD | Ex | CZ14 | 3.87 | 0.000679 | 0 | 4.14 | 0.000785 | -0.0379 | 3.87 | 0.000679 | 0 | 4.14 | 0.000785 | -0.0379 |  | LF | AllSpc | 3870 | 0.679 | 3870 | 0.679 | 1.07 | 1.16 | -0.0097933 | 3870 | 0.679 | 3870 | 0.679 | 1.07 | 1.16 | -0.00979
LFAllSpcSCERSDExCZ15 | Com-Iltg-dWatt-LF_OSspc | SCE | RSD | Ex | CZ15 | 3.87 | 0.000679 | 0 | 4.54 | 0.000855 | -0.00929 | 3.87 | 0.000679 | 0 | 4.54 | 0.000855 | -0.00929 |  | LF | AllSpc | 3870 | 0.679 | 3870 | 0.679 | 1.17 | 1.26 | -0.0024005 | 3870 | 0.679 | 3870 | 0.679 | 1.17 | 1.26 | -0.0024
LFAllSpcSCERSDExCZ16 | Com-Iltg-dWatt-LF_OSspc | SCE | RSD | Ex | CZ16 | 3.87 | 0.000679 | 0 | 3.84 | 0.000802 | -0.0623 | 3.87 | 0.000679 | 0 | 3.84 | 0.000802 | -0.0623 |  | LF | AllSpc | 3870 | 0.679 | 3870 | 0.679 | 0.992 | 1.18 | -0.016098 | 3870 | 0.679 | 3870 | 0.679 | 0.992 | 1.18 | -0.0161
LFAllSpcSCERSDExIOU | Com-Iltg-dWatt-LF_OSspc | SCE | RSD | Ex | IOU | 3.87 | 0.000679 | 0 | 4.2822 | 0.00081675 | -0.02332 | 3.87 | 0.000679 | 0 | 4.2822 | 0.00081675 | -0.02332 |  | LF | AllSpc | 3870 | 0.679 | 3870 | 0.679 | 1.11 | 1.2 | -0.0060259 | 3870 | 0.679 | 3870 | 0.679 | 1.11 | 1.2 | -0.00603
LFAllSpcSCERSDNewCZ05 | Com-Iltg-dWatt-LF_OSspc | SCE | RSD | New | CZ05 | 3.87 | 0.000679 | 0 | 3.97 | 0.000847 | -0.0515 | 3.87 | 0.000679 | 0 | 3.97 | 0.000847 | -0.0515 |  | LF | AllSpc | 3870 | 0.679 | 3870 | 0.679 | 1.03 | 1.25 | -0.013307 | 3870 | 0.679 | 3870 | 0.679 | 1.03 | 1.25 | -0.0133
LFAllSpcSCERSDNewCZ06 | Com-Iltg-dWatt-LF_OSspc | SCE | RSD | New | CZ06 | 3.87 | 0.000679 | 0 | 4.23 | 0.000858 | -0.0287 | 3.87 | 0.000679 | 0 | 4.23 | 0.000858 | -0.0287 |  | LF | AllSpc | 3870 | 0.679 | 3870 | 0.679 | 1.09 | 1.26 | -0.007416 | 3870 | 0.679 | 3870 | 0.679 | 1.09 | 1.26 | -0.00742
LFAllSpcSCERSDNewCZ08 | Com-Iltg-dWatt-LF_OSspc | SCE | RSD | New | CZ08 | 3.87 | 0.000679 | 0 | 4.28 | 0.000862 | -0.0235 | 3.87 | 0.000679 | 0 | 4.28 | 0.000862 | -0.0235 |  | LF | AllSpc | 3870 | 0.679 | 3870 | 0.679 | 1.11 | 1.27 | -0.0060724 | 3870 | 0.679 | 3870 | 0.679 | 1.11 | 1.27 | -0.00607
LFAllSpcSCERSDNewCZ09 | Com-Iltg-dWatt-LF_OSspc | SCE | RSD | New | CZ09 | 3.87 | 0.000679 | 0 | 4.3 | 0.0009 | -0.025 | 3.87 | 0.000679 | 0 | 4.3 | 0.0009 | -0.025 |  | LF | AllSpc | 3870 | 0.679 | 3870 | 0.679 | 1.11 | 1.33 | -0.0064599 | 3870 | 0.679 | 3870 | 0.679 | 1.11 | 1.33 | -0.00646
LFAllSpcSCERSDNewCZ10 | Com-Iltg-dWatt-LF_OSspc | SCE | RSD | New | CZ10 | 3.87 | 0.000679 | 0 | 4.32 | 0.000902 | -0.0256 | 3.87 | 0.000679 | 0 | 4.32 | 0.000902 | -0.0256 |  | LF | AllSpc | 3870 | 0.679 | 3870 | 0.679 | 1.12 | 1.33 | -0.006615 | 3870 | 0.679 | 3870 | 0.679 | 1.12 | 1.33 | -0.00662
LFAllSpcSCERSDNewCZ13 | Com-Iltg-dWatt-LF_OSspc | SCE | RSD | New | CZ13 | 3.87 | 0.000679 | 0 | 4.26 | 0.000912 | -0.0395 | 3.87 | 0.000679 | 0 | 4.26 | 0.000912 | -0.0395 |  | LF | AllSpc | 3870 | 0.679 | 3870 | 0.679 | 1.1 | 1.34 | -0.010207 | 3870 | 0.679 | 3870 | 0.679 | 1.1 | 1.34 | -0.0102
LFAllSpcSCERSDNewCZ14 | Com-Iltg-dWatt-LF_OSspc | SCE | RSD | New | CZ14 | 3.87 | 0.000679 | 0 | 4.24 | 0.0009 | -0.041 | 3.87 | 0.000679 | 0 | 4.24 | 0.0009 | -0.041 |  | LF | AllSpc | 3870 | 0.679 | 3870 | 0.679 | 1.1 | 1.33 | -0.010594 | 3870 | 0.679 | 3870 | 0.679 | 1.1 | 1.33 | -0.0106
LFAllSpcSCERSDNewCZ15 | Com-Iltg-dWatt-LF_OSspc | SCE | RSD | New | CZ15 | 3.87 | 0.000679 | 0 | 4.65 | 0.000932 | -0.0115 | 3.87 | 0.000679 | 0 | 4.65 | 0.000932 | -0.0115 |  | LF | AllSpc | 3870 | 0.679 | 3870 | 0.679 | 1.2 | 1.37 | -0.0029716 | 3870 | 0.679 | 3870 | 0.679 | 1.2 | 1.37 | -0.00297
LFAllSpcSCERSDNewCZ16 | Com-Iltg-dWatt-LF_OSspc | SCE | RSD | New | CZ16 | 3.87 | 0.000679 | 0 | 3.88 | 0.000852 | -0.0488 | 3.87 | 0.000679 | 0 | 3.88 | 0.000852 | -0.0488 |  | LF | AllSpc | 3870 | 0.679 | 3870 | 0.679 | 1 | 1.25 | -0.01261 | 3870 | 0.679 | 3870 | 0.679 | 1 | 1.25 | -0.0126
LFAllSpcSCERSDNewIOU | Com-Iltg-dWatt-LF_OSspc | SCE | RSD | New | IOU | 3.87 | 0.000679 | 0 | 4.2914 | 0.00088338 | -0.026555 | 3.87 | 0.000679 | 0 | 4.2914 | 0.00088338 | -0.026555 |  | LF | AllSpc | 3870 | 0.679 | 3870 | 0.679 | 1.11 | 1.3 | -0.0068617 | 3870 | 0.679 | 3870 | 0.679 | 1.11 | 1.3 | -0.00686
LFAllSpcSCERt3ExCZ05 | Com-Iltg-dWatt-LF_OSspc | SCE | Rt3 | Ex | CZ05 | 3.34 | 0.00074919 | 0 | 3.66 | 0.00090919 | -0.014 | 3.34 | 0.00074919 | 0 | 3.66 | 0.00090919 | -0.014 |  | LF | AllSpc | 3340 | 0.749 | 3340 | 0.749 | 1.1 | 1.21 | -0.0041916 | 3340 | 0.749 | 3340 | 0.749 | 1.1 | 1.21 | -0.00419
LFAllSpcSCERt3ExCZ06 | Com-Iltg-dWatt-LF_OSspc | SCE | Rt3 | Ex | CZ06 | 3.34 | 0.0007492 | 0 | 3.8894 | 0.00091952 | -0.00334 | 3.34 | 0.0007492 | 0 | 3.8894 | 0.00091952 | -0.00334 |  | LF | AllSpc | 3340 | 0.749 | 3340 | 0.749 | 1.16 | 1.23 | -0.001 | 3340 | 0.749 | 3340 | 0.749 | 1.16 | 1.23 | -0.001
LFAllSpcSCERt3ExCZ08 | Com-Iltg-dWatt-LF_OSspc | SCE | Rt3 | Ex | CZ08 | 3.34 | 0.0007492 | 0 | 3.89 | 0.00091052 | -0.00301 | 3.34 | 0.0007492 | 0 | 3.89 | 0.00091052 | -0.00301 |  | LF | AllSpc | 3340 | 0.749 | 3340 | 0.749 | 1.16 | 1.22 | -0.0009012 | 3340 | 0.749 | 3340 | 0.749 | 1.16 | 1.22 | -0.000901
LFAllSpcSCERt3ExCZ09 | Com-Iltg-dWatt-LF_OSspc | SCE | Rt3 | Ex | CZ09 | 3.34 | 0.0007492 | 0 | 3.85 | 0.00092327 | -0.00468 | 3.34 | 0.0007492 | 0 | 3.85 | 0.00092327 | -0.00468 |  | LF | AllSpc | 3340 | 0.749 | 3340 | 0.749 | 1.15 | 1.23 | -0.0014012 | 3340 | 0.749 | 3340 | 0.749 | 1.15 | 1.23 | -0.0014
LFAllSpcSCERt3ExCZ10 | Com-Iltg-dWatt-LF_OSspc | SCE | Rt3 | Ex | CZ10 | 3.34 | 0.00074928 | 0 | 3.76 | 0.0009114 | -0.0053488 | 3.34 | 0.00074928 | 0 | 3.76 | 0.0009114 | -0.0053488 |  | LF | AllSpc | 3340 | 0.749 | 3340 | 0.749 | 1.13 | 1.22 | -0.0016014 | 3340 | 0.749 | 3340 | 0.749 | 1.13 | 1.22 | -0.0016
LFAllSpcSCERt3ExCZ13 | Com-Iltg-dWatt-LF_OSspc | SCE | Rt3 | Ex | CZ13 | 3.34 | 0.00074926 | 0 | 3.679 | 0.00092573 | -0.0177 | 3.34 | 0.00074926 | 0 | 3.679 | 0.00092573 | -0.0177 |  | LF | AllSpc | 3340 | 0.749 | 3340 | 0.749 | 1.1 | 1.24 | -0.0052994 | 3340 | 0.749 | 3340 | 0.749 | 1.1 | 1.24 | -0.0053
LFAllSpcSCERt3ExCZ14 | Com-Iltg-dWatt-LF_OSspc | SCE | Rt3 | Ex | CZ14 | 3.34 | 0.00074925 | 0 | 3.63 | 0.00092225 | -0.01879 | 3.34 | 0.00074925 | 0 | 3.63 | 0.00092225 | -0.01879 |  | LF | AllSpc | 3340 | 0.749 | 3340 | 0.749 | 1.09 | 1.23 | -0.0056257 | 3340 | 0.749 | 3340 | 0.749 | 1.09 | 1.23 | -0.00563
LFAllSpcSCERt3ExCZ15 | Com-Iltg-dWatt-LF_OSspc | SCE | Rt3 | Ex | CZ15 | 3.34 | 0.00074928 | 0 | 3.8988 | 0.0009324 | -0.00121 | 3.34 | 0.00074928 | 0 | 3.8988 | 0.0009324 | -0.00121 |  | LF | AllSpc | 3340 | 0.749 | 3340 | 0.749 | 1.17 | 1.24 | -0.00036228 | 3340 | 0.749 | 3340 | 0.749 | 1.17 | 1.24 | -0.000362
LFAllSpcSCERt3ExCZ16 | Com-Iltg-dWatt-LF_OSspc | SCE | Rt3 | Ex | CZ16 | 3.34 | 0.00074926 | 0 | 3.3 | 0.00090173 | -0.0421 | 3.34 | 0.00074926 | 0 | 3.3 | 0.00090173 | -0.0421 |  | LF | AllSpc | 3340 | 0.749 | 3340 | 0.749 | 0.988 | 1.2 | -0.012605 | 3340 | 0.749 | 3340 | 0.749 | 0.988 | 1.2 | -0.0126
LFAllSpcSCERt3ExIOU | Com-Iltg-dWatt-LF_OSspc | SCE | Rt3 | Ex | IOU | 3.34 | 0.00074922 | 0 | 3.8337 | 0.0009163 | -0.0052148 | 3.34 | 0.00074922 | 0 | 3.8337 | 0.0009163 | -0.0052148 |  | LF | AllSpc | 3340 | 0.749 | 3340 | 0.749 | 1.15 | 1.22 | -0.0015613 | 3340 | 0.749 | 3340 | 0.749 | 1.15 | 1.22 | -0.00156
LFAllSpcSCERt3NewCZ05 | Com-Iltg-dWatt-LF_OSspc | SCE | Rt3 | New | CZ05 | 3.34 | 0.000748 | 0 | 3.54 | 0.000919 | -0.0175 | 3.34 | 0.000748 | 0 | 3.54 | 0.000919 | -0.0175 |  | LF | AllSpc | 3340 | 0.748 | 3340 | 0.748 | 1.06 | 1.23 | -0.0052395 | 3340 | 0.748 | 3340 | 0.748 | 1.06 | 1.23 | -0.00524
LFAllSpcSCERt3NewCZ06 | Com-Iltg-dWatt-LF_OSspc | SCE | Rt3 | New | CZ06 | 3.34 | 0.000748 | 0 | 3.77 | 0.000927 | -0.00441 | 3.34 | 0.000748 | 0 | 3.77 | 0.000927 | -0.00441 |  | LF | AllSpc | 3340 | 0.748 | 3340 | 0.748 | 1.13 | 1.24 | -0.0013204 | 3340 | 0.748 | 3340 | 0.748 | 1.13 | 1.24 | -0.00132
LFAllSpcSCERt3NewCZ08 | Com-Iltg-dWatt-LF_OSspc | SCE | Rt3 | New | CZ08 | 3.34 | 0.000748 | 0 | 3.81 | 0.000935 | -0.00371 | 3.34 | 0.000748 | 0 | 3.81 | 0.000935 | -0.00371 |  | LF | AllSpc | 3340 | 0.748 | 3340 | 0.748 | 1.14 | 1.25 | -0.0011108 | 3340 | 0.748 | 3340 | 0.748 | 1.14 | 1.25 | -0.00111
LFAllSpcSCERt3NewCZ09 | Com-Iltg-dWatt-LF_OSspc | SCE | Rt3 | New | CZ09 | 3.34 | 0.000748 | 0 | 3.74 | 0.000896 | -0.00584 | 3.34 | 0.000748 | 0 | 3.74 | 0.000896 | -0.00584 |  | LF | AllSpc | 3340 | 0.748 | 3340 | 0.748 | 1.12 | 1.2 | -0.0017485 | 3340 | 0.748 | 3340 | 0.748 | 1.12 | 1.2 | -0.00175
LFAllSpcSCERt3NewCZ10 | Com-Iltg-dWatt-LF_OSspc | SCE | Rt3 | New | CZ10 | 3.34 | 0.000748 | 0 | 3.77 | 0.000929 | -0.00681 | 3.34 | 0.000748 | 0 | 3.77 | 0.000929 | -0.00681 |  | LF | AllSpc | 3340 | 0.748 | 3340 | 0.748 | 1.13 | 1.24 | -0.0020389 | 3340 | 0.748 | 3340 | 0.748 | 1.13 | 1.24 | -0.00204
LFAllSpcSCERt3NewCZ13 | Com-Iltg-dWatt-LF_OSspc | SCE | Rt3 | New | CZ13 | 3.34 | 0.000748 | 0 | 3.71 | 0.000971 | -0.0192 | 3.34 | 0.000748 | 0 | 3.71 | 0.000971 | -0.0192 |  | LF | AllSpc | 3340 | 0.748 | 3340 | 0.748 | 1.11 | 1.3 | -0.0057485 | 3340 | 0.748 | 3340 | 0.748 | 1.11 | 1.3 | -0.00575
LFAllSpcSCERt3NewCZ14 | Com-Iltg-dWatt-LF_OSspc | SCE | Rt3 | New | CZ14 | 3.34 | 0.000748 | 0 | 3.71 | 0.000967 | -0.0197 | 3.34 | 0.000748 | 0 | 3.71 | 0.000967 | -0.0197 |  | LF | AllSpc | 3340 | 0.748 | 3340 | 0.748 | 1.11 | 1.29 | -0.0058982 | 3340 | 0.748 | 3340 | 0.748 | 1.11 | 1.29 | -0.0059
LFAllSpcSCERt3NewCZ15 | Com-Iltg-dWatt-LF_OSspc | SCE | Rt3 | New | CZ15 | 3.34 | 0.000748 | 0 | 3.77 | 0.000882 | -0.000715 | 3.34 | 0.000748 | 0 | 3.77 | 0.000882 | -0.000715 |  | LF | AllSpc | 3340 | 0.748 | 3340 | 0.748 | 1.13 | 1.18 | -0.00021407 | 3340 | 0.748 | 3340 | 0.748 | 1.13 | 1.18 | -0.000214
LFAllSpcSCERt3NewCZ16 | Com-Iltg-dWatt-LF_OSspc | SCE | Rt3 | New | CZ16 | 3.34 | 0.000748 | 0 | 3.33 | 0.000926 | -0.0428 | 3.34 | 0.000748 | 0 | 3.33 | 0.000926 | -0.0428 |  | LF | AllSpc | 3340 | 0.748 | 3340 | 0.748 | 0.997 | 1.24 | -0.012814 | 3340 | 0.748 | 3340 | 0.748 | 0.997 | 1.24 | -0.0128
LFAllSpcSCERt3NewIOU | Com-Iltg-dWatt-LF_OSspc | SCE | Rt3 | New | IOU | 3.34 | 0.000748 | 0 | 3.7643 | 0.00092719 | -0.0068165 | 3.34 | 0.000748 | 0 | 3.7643 | 0.00092719 | -0.0068165 |  | LF | AllSpc | 3340 | 0.748 | 3340 | 0.748 | 1.13 | 1.24 | -0.0020409 | 3340 | 0.748 | 3340 | 0.748 | 1.13 | 1.24 | -0.00204
LFAllSpcSCERtLExCZ05 | Com-Iltg-dWatt-LF_OSspc | SCE | RtL | Ex | CZ05 | 4.23 | 0.00083898 | 0 | 4.5598 | 0.00102 | -0.0252 | 4.23 | 0.00083898 | 0 | 4.5598 | 0.00102 | -0.0252 |  | LF | AllSpc | 4230 | 0.839 | 4230 | 0.839 | 1.08 | 1.22 | -0.0059574 | 4230 | 0.839 | 4230 | 0.839 | 1.08 | 1.22 | -0.00596
LFAllSpcSCERtLExCZ06 | Com-Iltg-dWatt-LF_OSspc | SCE | RtL | Ex | CZ06 | 4.23 | 0.00083898 | 0 | 4.8498 | 0.00103 | -0.0098194 | 4.23 | 0.00083898 | 0 | 4.8498 | 0.00103 | -0.0098194 |  | LF | AllSpc | 4230 | 0.839 | 4230 | 0.839 | 1.15 | 1.23 | -0.0023214 | 4230 | 0.839 | 4230 | 0.839 | 1.15 | 1.23 | -0.00232
LFAllSpcSCERtLExCZ08 | Com-Iltg-dWatt-LF_OSspc | SCE | RtL | Ex | CZ08 | 4.23 | 0.00083898 | 0 | 4.86 | 0.0010398 | -0.0085094 | 4.23 | 0.00083898 | 0 | 4.86 | 0.0010398 | -0.0085094 |  | LF | AllSpc | 4230 | 0.839 | 4230 | 0.839 | 1.15 | 1.24 | -0.0020117 | 4230 | 0.839 | 4230 | 0.839 | 1.15 | 1.24 | -0.00201
LFAllSpcSCERtLExCZ09 | Com-Iltg-dWatt-LF_OSspc | SCE | RtL | Ex | CZ09 | 4.23 | 0.00083893 | 0 | 4.8193 | 0.00106 | -0.010193 | 4.23 | 0.00083893 | 0 | 4.8193 | 0.00106 | -0.010193 |  | LF | AllSpc | 4230 | 0.839 | 4230 | 0.839 | 1.14 | 1.26 | -0.0024098 | 4230 | 0.839 | 4230 | 0.839 | 1.14 | 1.26 | -0.00241
LFAllSpcSCERtLExCZ10 | Com-Iltg-dWatt-LF_OSspc | SCE | RtL | Ex | CZ10 | 4.23 | 0.00083888 | 0 | 4.7288 | 0.0010488 | -0.0113 | 4.23 | 0.00083888 | 0 | 4.7288 | 0.0010488 | -0.0113 |  | LF | AllSpc | 4230 | 0.839 | 4230 | 0.839 | 1.12 | 1.25 | -0.0026714 | 4230 | 0.839 | 4230 | 0.839 | 1.12 | 1.25 | -0.00267
LFAllSpcSCERtLExCZ13 | Com-Iltg-dWatt-LF_OSspc | SCE | RtL | Ex | CZ13 | 4.23 | 0.0008389 | 0 | 4.64 | 0.00105 | -0.0233 | 4.23 | 0.0008389 | 0 | 4.64 | 0.00105 | -0.0233 |  | LF | AllSpc | 4230 | 0.839 | 4230 | 0.839 | 1.1 | 1.25 | -0.0055083 | 4230 | 0.839 | 4230 | 0.839 | 1.1 | 1.25 | -0.00551
LFAllSpcSCERtLExCZ14 | Com-Iltg-dWatt-LF_OSspc | SCE | RtL | Ex | CZ14 | 4.23 | 0.0008389 | 0 | 4.6 | 0.00106 | -0.02389 | 4.23 | 0.0008389 | 0 | 4.6 | 0.00106 | -0.02389 |  | LF | AllSpc | 4230 | 0.839 | 4230 | 0.839 | 1.09 | 1.26 | -0.0056478 | 4230 | 0.839 | 4230 | 0.839 | 1.09 | 1.26 | -0.00565
LFAllSpcSCERtLExCZ15 | Com-Iltg-dWatt-LF_OSspc | SCE | RtL | Ex | CZ15 | 4.23 | 0.00083888 | 0 | 4.95 | 0.00106 | -0.0039688 | 4.23 | 0.00083888 | 0 | 4.95 | 0.00106 | -0.0039688 |  | LF | AllSpc | 4230 | 0.839 | 4230 | 0.839 | 1.17 | 1.26 | -0.00093825 | 4230 | 0.839 | 4230 | 0.839 | 1.17 | 1.26 | -0.000938
LFAllSpcSCERtLExCZ16 | Com-Iltg-dWatt-LF_OSspc | SCE | RtL | Ex | CZ16 | 4.23 | 0.0008389 | 0 | 4.159 | 0.00101 | -0.05419 | 4.23 | 0.0008389 | 0 | 4.159 | 0.00101 | -0.05419 |  | LF | AllSpc | 4230 | 0.839 | 4230 | 0.839 | 0.983 | 1.2 | -0.012811 | 4230 | 0.839 | 4230 | 0.839 | 0.983 | 1.2 | -0.0128
LFAllSpcSCERtLExIOU | Com-Iltg-dWatt-LF_OSspc | SCE | RtL | Ex | IOU | 4.23 | 0.00083894 | 0 | 4.802 | 0.0010437 | -0.011038 | 4.23 | 0.00083894 | 0 | 4.802 | 0.0010437 | -0.011038 |  | LF | AllSpc | 4230 | 0.839 | 4230 | 0.839 | 1.14 | 1.24 | -0.0026095 | 4230 | 0.839 | 4230 | 0.839 | 1.14 | 1.24 | -0.00261
LFAllSpcSCERtLNewCZ05 | Com-Iltg-dWatt-LF_OSspc | SCE | RtL | New | CZ05 | 4.23 | 0.000838 | 0 | 4.43 | 0.00103 | -0.0297 | 4.23 | 0.000838 | 0 | 4.43 | 0.00103 | -0.0297 |  | LF | AllSpc | 4230 | 0.838 | 4230 | 0.838 | 1.05 | 1.23 | -0.0070213 | 4230 | 0.838 | 4230 | 0.838 | 1.05 | 1.23 | -0.00702
LFAllSpcSCERtLNewCZ06 | Com-Iltg-dWatt-LF_OSspc | SCE | RtL | New | CZ06 | 4.23 | 0.000838 | 0 | 4.68 | 0.00105 | -0.0134 | 4.23 | 0.000838 | 0 | 4.68 | 0.00105 | -0.0134 |  | LF | AllSpc | 4230 | 0.838 | 4230 | 0.838 | 1.11 | 1.25 | -0.0031678 | 4230 | 0.838 | 4230 | 0.838 | 1.11 | 1.25 | -0.00317
LFAllSpcSCERtLNewCZ08 | Com-Iltg-dWatt-LF_OSspc | SCE | RtL | New | CZ08 | 4.23 | 0.000838 | 0 | 4.75 | 0.00107 | -0.0114 | 4.23 | 0.000838 | 0 | 4.75 | 0.00107 | -0.0114 |  | LF | AllSpc | 4230 | 0.838 | 4230 | 0.838 | 1.12 | 1.28 | -0.002695 | 4230 | 0.838 | 4230 | 0.838 | 1.12 | 1.28 | -0.0027
LFAllSpcSCERtLNewCZ09 | Com-Iltg-dWatt-LF_OSspc | SCE | RtL | New | CZ09 | 4.23 | 0.000838 | 0 | 4.76 | 0.0011 | -0.0114 | 4.23 | 0.000838 | 0 | 4.76 | 0.0011 | -0.0114 |  | LF | AllSpc | 4230 | 0.838 | 4230 | 0.838 | 1.13 | 1.31 | -0.002695 | 4230 | 0.838 | 4230 | 0.838 | 1.13 | 1.31 | -0.0027
LFAllSpcSCERtLNewCZ10 | Com-Iltg-dWatt-LF_OSspc | SCE | RtL | New | CZ10 | 4.23 | 0.000838 | 0 | 4.78 | 0.00111 | -0.0132 | 4.23 | 0.000838 | 0 | 4.78 | 0.00111 | -0.0132 |  | LF | AllSpc | 4230 | 0.838 | 4230 | 0.838 | 1.13 | 1.32 | -0.0031206 | 4230 | 0.838 | 4230 | 0.838 | 1.13 | 1.32 | -0.00312
LFAllSpcSCERtLNewCZ13 | Com-Iltg-dWatt-LF_OSspc | SCE | RtL | New | CZ13 | 4.23 | 0.000838 | 0 | 4.68 | 0.0011 | -0.026 | 4.23 | 0.000838 | 0 | 4.68 | 0.0011 | -0.026 |  | LF | AllSpc | 4230 | 0.838 | 4230 | 0.838 | 1.11 | 1.31 | -0.0061466 | 4230 | 0.838 | 4230 | 0.838 | 1.11 | 1.31 | -0.00615
LFAllSpcSCERtLNewCZ14 | Com-Iltg-dWatt-LF_OSspc | SCE | RtL | New | CZ14 | 4.23 | 0.000838 | 0 | 4.67 | 0.0011 | -0.0263 | 4.23 | 0.000838 | 0 | 4.67 | 0.0011 | -0.0263 |  | LF | AllSpc | 4230 | 0.838 | 4230 | 0.838 | 1.1 | 1.31 | -0.0062175 | 4230 | 0.838 | 4230 | 0.838 | 1.1 | 1.31 | -0.00622
LFAllSpcSCERtLNewCZ15 | Com-Iltg-dWatt-LF_OSspc | SCE | RtL | New | CZ15 | 4.23 | 0.000838 | 0 | 5.07 | 0.00112 | -0.004 | 4.23 | 0.000838 | 0 | 5.07 | 0.00112 | -0.004 |  | LF | AllSpc | 4230 | 0.838 | 4230 | 0.838 | 1.2 | 1.34 | -0.00094563 | 4230 | 0.838 | 4230 | 0.838 | 1.2 | 1.34 | -0.000946
LFAllSpcSCERtLNewCZ16 | Com-Iltg-dWatt-LF_OSspc | SCE | RtL | New | CZ16 | 4.23 | 0.000838 | 0 | 4.2 | 0.00104 | -0.0571 | 4.23 | 0.000838 | 0 | 4.2 | 0.00104 | -0.0571 |  | LF | AllSpc | 4230 | 0.838 | 4230 | 0.838 | 0.993 | 1.24 | -0.013499 | 4230 | 0.838 | 4230 | 0.838 | 0.993 | 1.24 | -0.0135
LFAllSpcSCERtLNewIOU | Com-Iltg-dWatt-LF_OSspc | SCE | RtL | New | IOU | 4.23 | 0.000838 | 0 | 4.7487 | 0.0010873 | -0.013872 | 4.23 | 0.000838 | 0 | 4.7487 | 0.0010873 | -0.013872 |  | LF | AllSpc | 4230 | 0.838 | 4230 | 0.838 | 1.12 | 1.3 | -0.0032793 | 4230 | 0.838 | 4230 | 0.838 | 1.12 | 1.3 | -0.00328
LFAllSpcSCERtSExCZ05 | Com-Iltg-dWatt-LF_OSspc | SCE | RtS | Ex | CZ05 | 3.3294 | 0.00086281 | 0 | 3.5798 | 0.00104 | -0.015304 | 3.3294 | 0.00086281 | 0 | 3.5798 | 0.00104 | -0.015304 |  | LF | AllSpc | 3330 | 0.863 | 3330 | 0.863 | 1.08 | 1.21 | -0.0045968 | 3330 | 0.863 | 3330 | 0.863 | 1.08 | 1.21 | -0.0046
LFAllSpcSCERtSExCZ06 | Com-Iltg-dWatt-LF_OSspc | SCE | RtS | Ex | CZ06 | 3.3294 | 0.00086281 | 0 | 3.7894 | 0.0010594 | -0.0050587 | 3.3294 | 0.00086281 | 0 | 3.7894 | 0.0010594 | -0.0050587 |  | LF | AllSpc | 3330 | 0.863 | 3330 | 0.863 | 1.14 | 1.23 | -0.0015194 | 3330 | 0.863 | 3330 | 0.863 | 1.14 | 1.23 | -0.00152
LFAllSpcSCERtSExCZ08 | Com-Iltg-dWatt-LF_OSspc | SCE | RtS | Ex | CZ08 | 3.3293 | 0.0008628 | 0 | 3.8098 | 0.0010593 | -0.0042898 | 3.3293 | 0.0008628 | 0 | 3.8098 | 0.0010593 | -0.0042898 |  | LF | AllSpc | 3330 | 0.863 | 3330 | 0.863 | 1.14 | 1.23 | -0.0012885 | 3330 | 0.863 | 3330 | 0.863 | 1.14 | 1.23 | -0.00129
LFAllSpcSCERtSExCZ09 | Com-Iltg-dWatt-LF_OSspc | SCE | RtS | Ex | CZ09 | 3.3293 | 0.0008628 | 0 | 3.7793 | 0.00107 | -0.0057587 | 3.3293 | 0.0008628 | 0 | 3.7793 | 0.00107 | -0.0057587 |  | LF | AllSpc | 3330 | 0.863 | 3330 | 0.863 | 1.14 | 1.24 | -0.0017297 | 3330 | 0.863 | 3330 | 0.863 | 1.14 | 1.24 | -0.00173
LFAllSpcSCERtSExCZ10 | Com-Iltg-dWatt-LF_OSspc | SCE | RtS | Ex | CZ10 | 3.3288 | 0.00086264 | 0 | 3.7088 | 0.0010588 | -0.0064564 | 3.3288 | 0.00086264 | 0 | 3.7088 | 0.0010588 | -0.0064564 |  | LF | AllSpc | 3330 | 0.863 | 3330 | 0.863 | 1.11 | 1.23 | -0.0019396 | 3330 | 0.863 | 3330 | 0.863 | 1.11 | 1.23 | -0.00194
LFAllSpcSCERtSExCZ13 | Com-Iltg-dWatt-LF_OSspc | SCE | RtS | Ex | CZ13 | 3.329 | 0.00086269 | 0 | 3.639 | 0.00106 | -0.0182 | 3.329 | 0.00086269 | 0 | 3.639 | 0.00106 | -0.0182 |  | LF | AllSpc | 3330 | 0.863 | 3330 | 0.863 | 1.09 | 1.23 | -0.0054672 | 3330 | 0.863 | 3330 | 0.863 | 1.09 | 1.23 | -0.00547
LFAllSpcSCERtSExCZ14 | Com-Iltg-dWatt-LF_OSspc | SCE | RtS | Ex | CZ14 | 3.329 | 0.0008627 | 0 | 3.629 | 0.001059 | -0.016 | 3.329 | 0.0008627 | 0 | 3.629 | 0.001059 | -0.016 |  | LF | AllSpc | 3330 | 0.863 | 3330 | 0.863 | 1.09 | 1.23 | -0.0048062 | 3330 | 0.863 | 3330 | 0.863 | 1.09 | 1.23 | -0.00481
LFAllSpcSCERtSExCZ15 | Com-Iltg-dWatt-LF_OSspc | SCE | RtS | Ex | CZ15 | 3.3288 | 0.00086264 | 0 | 3.8988 | 0.0010688 | -0.00138 | 3.3288 | 0.00086264 | 0 | 3.8988 | 0.0010688 | -0.00138 |  | LF | AllSpc | 3330 | 0.863 | 3330 | 0.863 | 1.17 | 1.24 | -0.00041456 | 3330 | 0.863 | 3330 | 0.863 | 1.17 | 1.24 | -0.000415
LFAllSpcSCERtSExCZ16 | Com-Iltg-dWatt-LF_OSspc | SCE | RtS | Ex | CZ16 | 3.329 | 0.00086269 | 0 | 3.309 | 0.001039 | -0.036902 | 3.329 | 0.00086269 | 0 | 3.309 | 0.001039 | -0.036902 |  | LF | AllSpc | 3330 | 0.863 | 3330 | 0.863 | 0.994 | 1.2 | -0.011085 | 3330 | 0.863 | 3330 | 0.863 | 0.994 | 1.2 | -0.0111
LFAllSpcSCERtSExIOU | Com-Iltg-dWatt-LF_OSspc | SCE | RtS | Ex | IOU | 3.3292 | 0.00086276 | 0 | 3.7638 | 0.0010609 | -0.0062609 | 3.3292 | 0.00086276 | 0 | 3.7638 | 0.0010609 | -0.0062609 |  | LF | AllSpc | 3330 | 0.863 | 3330 | 0.863 | 1.13 | 1.23 | -0.0018806 | 3330 | 0.863 | 3330 | 0.863 | 1.13 | 1.23 | -0.00188
LFAllSpcSCERtSNewCZ05 | Com-Iltg-dWatt-LF_OSspc | SCE | RtS | New | CZ05 | 3.32 | 0.00086 | 0 | 3.48 | 0.00102 | -0.0175 | 3.32 | 0.00086 | 0 | 3.48 | 0.00102 | -0.0175 |  | LF | AllSpc | 3320 | 0.86 | 3320 | 0.86 | 1.05 | 1.19 | -0.0052711 | 3320 | 0.86 | 3320 | 0.86 | 1.05 | 1.19 | -0.00527
LFAllSpcSCERtSNewCZ06 | Com-Iltg-dWatt-LF_OSspc | SCE | RtS | New | CZ06 | 3.32 | 0.00086 | 0 | 3.68 | 0.00104 | -0.00667 | 3.32 | 0.00086 | 0 | 3.68 | 0.00104 | -0.00667 |  | LF | AllSpc | 3320 | 0.86 | 3320 | 0.86 | 1.11 | 1.21 | -0.002009 | 3320 | 0.86 | 3320 | 0.86 | 1.11 | 1.21 | -0.00201
LFAllSpcSCERtSNewCZ08 | Com-Iltg-dWatt-LF_OSspc | SCE | RtS | New | CZ08 | 3.32 | 0.00086 | 0 | 3.71 | 0.00106 | -0.00561 | 3.32 | 0.00086 | 0 | 3.71 | 0.00106 | -0.00561 |  | LF | AllSpc | 3320 | 0.86 | 3320 | 0.86 | 1.12 | 1.23 | -0.0016898 | 3320 | 0.86 | 3320 | 0.86 | 1.12 | 1.23 | -0.00169
LFAllSpcSCERtSNewCZ09 | Com-Iltg-dWatt-LF_OSspc | SCE | RtS | New | CZ09 | 3.32 | 0.00086 | 0 | 3.71 | 0.00108 | -0.0068 | 3.32 | 0.00086 | 0 | 3.71 | 0.00108 | -0.0068 |  | LF | AllSpc | 3320 | 0.86 | 3320 | 0.86 | 1.12 | 1.26 | -0.0020482 | 3320 | 0.86 | 3320 | 0.86 | 1.12 | 1.26 | -0.00205
LFAllSpcSCERtSNewCZ10 | Com-Iltg-dWatt-LF_OSspc | SCE | RtS | New | CZ10 | 3.32 | 0.00086 | 0 | 3.74 | 0.0011 | -0.00697 | 3.32 | 0.00086 | 0 | 3.74 | 0.0011 | -0.00697 |  | LF | AllSpc | 3320 | 0.86 | 3320 | 0.86 | 1.13 | 1.28 | -0.0020994 | 3320 | 0.86 | 3320 | 0.86 | 1.13 | 1.28 | -0.0021
LFAllSpcSCERtSNewCZ13 | Com-Iltg-dWatt-LF_OSspc | SCE | RtS | New | CZ13 | 3.32 | 0.00086 | 0 | 3.63 | 0.00107 | -0.0186 | 3.32 | 0.00086 | 0 | 3.63 | 0.00107 | -0.0186 |  | LF | AllSpc | 3320 | 0.86 | 3320 | 0.86 | 1.09 | 1.24 | -0.0056024 | 3320 | 0.86 | 3320 | 0.86 | 1.09 | 1.24 | -0.0056
LFAllSpcSCERtSNewCZ14 | Com-Iltg-dWatt-LF_OSspc | SCE | RtS | New | CZ14 | 3.32 | 0.00086 | 0 | 3.65 | 0.00108 | -0.0168 | 3.32 | 0.00086 | 0 | 3.65 | 0.00108 | -0.0168 |  | LF | AllSpc | 3320 | 0.86 | 3320 | 0.86 | 1.1 | 1.26 | -0.0050602 | 3320 | 0.86 | 3320 | 0.86 | 1.1 | 1.26 | -0.00506
LFAllSpcSCERtSNewCZ15 | Com-Iltg-dWatt-LF_OSspc | SCE | RtS | New | CZ15 | 3.32 | 0.00086 | 0 | 3.91 | 0.0011 | -0.00124 | 3.32 | 0.00086 | 0 | 3.91 | 0.0011 | -0.00124 |  | LF | AllSpc | 3320 | 0.86 | 3320 | 0.86 | 1.18 | 1.28 | -0.00037349 | 3320 | 0.86 | 3320 | 0.86 | 1.18 | 1.28 | -0.000373
LFAllSpcSCERtSNewCZ16 | Com-Iltg-dWatt-LF_OSspc | SCE | RtS | New | CZ16 | 3.32 | 0.00086 | 0 | 3.3 | 0.00104 | -0.0391 | 3.32 | 0.00086 | 0 | 3.3 | 0.00104 | -0.0391 |  | LF | AllSpc | 3320 | 0.86 | 3320 | 0.86 | 0.994 | 1.21 | -0.011777 | 3320 | 0.86 | 3320 | 0.86 | 0.994 | 1.21 | -0.0118
LFAllSpcSCERtSNewIOU | Com-Iltg-dWatt-LF_OSspc | SCE | RtS | New | IOU | 3.32 | 0.00086 | 0 | 3.7121 | 0.0010745 | -0.0076395 | 3.32 | 0.00086 | 0 | 3.7121 | 0.0010745 | -0.0076395 |  | LF | AllSpc | 3320 | 0.86 | 3320 | 0.86 | 1.12 | 1.25 | -0.0023011 | 3320 | 0.86 | 3320 | 0.86 | 1.12 | 1.25 | -0.0023
LFAllSpcSCEs_AgrExCZ05 | Com-Iltg-dWatt-LF_OSspc | SCE | s_Agr | Ex | CZ05 | 2.638 | 0.00073 | 0 | 2.778 | 0.0008934 | -0.013166 | 2.638 | 0.00073 | 0 | 2.778 | 0.0008934 | -0.013166 |  | LF | AllSpc | 2640 | 0.73 | 2640 | 0.73 | 1.05 | 1.22 | -0.0049909 | 2640 | 0.73 | 2640 | 0.73 | 1.05 | 1.22 | -0.00499
LFAllSpcSCEs_AgrExCZ06 | Com-Iltg-dWatt-LF_OSspc | SCE | s_Agr | Ex | CZ06 | 2.638 | 0.00073 | 0 | 2.934 | 0.000883 | -0.004664 | 2.638 | 0.00073 | 0 | 2.934 | 0.000883 | -0.004664 |  | LF | AllSpc | 2640 | 0.73 | 2640 | 0.73 | 1.11 | 1.21 | -0.001768 | 2640 | 0.73 | 2640 | 0.73 | 1.11 | 1.21 | -0.00177
LFAllSpcSCEs_AgrExCZ08 | Com-Iltg-dWatt-LF_OSspc | SCE | s_Agr | Ex | CZ08 | 2.638 | 0.00073 | 0 | 2.952 | 0.0008832 | -0.00388 | 2.638 | 0.00073 | 0 | 2.952 | 0.0008832 | -0.00388 |  | LF | AllSpc | 2640 | 0.73 | 2640 | 0.73 | 1.12 | 1.21 | -0.0014708 | 2640 | 0.73 | 2640 | 0.73 | 1.12 | 1.21 | -0.00147
LFAllSpcSCEs_AgrExCZ09 | Com-Iltg-dWatt-LF_OSspc | SCE | s_Agr | Ex | CZ09 | 2.638 | 0.00073 | 0 | 2.934 | 0.0009022 | -0.005328 | 2.638 | 0.00073 | 0 | 2.934 | 0.0009022 | -0.005328 |  | LF | AllSpc | 2640 | 0.73 | 2640 | 0.73 | 1.11 | 1.24 | -0.0020197 | 2640 | 0.73 | 2640 | 0.73 | 1.11 | 1.24 | -0.00202
LFAllSpcSCEs_AgrExCZ10 | Com-Iltg-dWatt-LF_OSspc | SCE | s_Agr | Ex | CZ10 | 2.638 | 0.00073 | 0 | 2.864 | 0.0008936 | -0.005714 | 2.638 | 0.00073 | 0 | 2.864 | 0.0008936 | -0.005714 |  | LF | AllSpc | 2640 | 0.73 | 2640 | 0.73 | 1.09 | 1.22 | -0.002166 | 2640 | 0.73 | 2640 | 0.73 | 1.09 | 1.22 | -0.00217
LFAllSpcSCEs_AgrExCZ13 | Com-Iltg-dWatt-LF_OSspc | SCE | s_Agr | Ex | CZ13 | 2.638 | 0.00073 | 0 | 2.832 | 0.0008856 | -0.01368 | 2.638 | 0.00073 | 0 | 2.832 | 0.0008856 | -0.01368 |  | LF | AllSpc | 2640 | 0.73 | 2640 | 0.73 | 1.07 | 1.21 | -0.0051857 | 2640 | 0.73 | 2640 | 0.73 | 1.07 | 1.21 | -0.00519
LFAllSpcSCEs_AgrExCZ14 | Com-Iltg-dWatt-LF_OSspc | SCE | s_Agr | Ex | CZ14 | 2.638 | 0.00073 | 0 | 2.808 | 0.000892 | -0.015348 | 2.638 | 0.00073 | 0 | 2.808 | 0.000892 | -0.015348 |  | LF | AllSpc | 2640 | 0.73 | 2640 | 0.73 | 1.06 | 1.22 | -0.005818 | 2640 | 0.73 | 2640 | 0.73 | 1.06 | 1.22 | -0.00582
LFAllSpcSCEs_AgrExCZ15 | Com-Iltg-dWatt-LF_OSspc | SCE | s_Agr | Ex | CZ15 | 2.638 | 0.00073 | 0 | 3.058 | 0.0008878 | -0.0015414 | 2.638 | 0.00073 | 0 | 3.058 | 0.0008878 | -0.0015414 |  | LF | AllSpc | 2640 | 0.73 | 2640 | 0.73 | 1.16 | 1.22 | -0.00058431 | 2640 | 0.73 | 2640 | 0.73 | 1.16 | 1.22 | -0.000584
LFAllSpcSCEs_AgrExCZ16 | Com-Iltg-dWatt-LF_OSspc | SCE | s_Agr | Ex | CZ16 | 2.638 | 0.00073 | 0 | 2.608 | 0.0008724 | -0.03034 | 2.638 | 0.00073 | 0 | 2.608 | 0.0008724 | -0.03034 |  | LF | AllSpc | 2640 | 0.73 | 2640 | 0.73 | 0.989 | 1.2 | -0.011501 | 2640 | 0.73 | 2640 | 0.73 | 0.989 | 1.2 | -0.0115
LFAllSpcSCEs_AgrExIOU | Com-Iltg-dWatt-LF_OSspc | SCE | s_Agr | Ex | IOU | 2.638 | 0.00073 | 0 | 2.9206 | 0.00088814 | -0.0057031 | 2.638 | 0.00073 | 0 | 2.9206 | 0.00088814 | -0.0057031 |  | LF | AllSpc | 2640 | 0.73 | 2640 | 0.73 | 1.11 | 1.22 | -0.0021619 | 2640 | 0.73 | 2640 | 0.73 | 1.11 | 1.22 | -0.00216
LFAllSpcSCEs_CliExCZ05 | Com-Iltg-dWatt-LF_OSspc | SCE | s_Cli | Ex | CZ05 | 2.735 | 0.000547 | 0 | 2.855 | 0.0006805 | -0.031365 | 2.735 | 0.000547 | 0 | 2.855 | 0.0006805 | -0.031365 |  | LF | AllSpc | 2730 | 0.547 | 2730 | 0.547 | 1.04 | 1.24 | -0.011468 | 2730 | 0.547 | 2730 | 0.547 | 1.04 | 1.24 | -0.0115
LFAllSpcSCEs_CliExCZ06 | Com-Iltg-dWatt-LF_OSspc | SCE | s_Cli | Ex | CZ06 | 2.735 | 0.000547 | 0 | 3.025 | 0.000704 | -0.02032 | 2.735 | 0.000547 | 0 | 3.025 | 0.000704 | -0.02032 |  | LF | AllSpc | 2730 | 0.547 | 2730 | 0.547 | 1.11 | 1.29 | -0.0074296 | 2730 | 0.547 | 2730 | 0.547 | 1.11 | 1.29 | -0.00743
LFAllSpcSCEs_CliExCZ08 | Com-Iltg-dWatt-LF_OSspc | SCE | s_Cli | Ex | CZ08 | 2.735 | 0.000547 | 0 | 3.055 | 0.0007055 | -0.01967 | 2.735 | 0.000547 | 0 | 3.055 | 0.0007055 | -0.01967 |  | LF | AllSpc | 2730 | 0.547 | 2730 | 0.547 | 1.12 | 1.29 | -0.007192 | 2730 | 0.547 | 2730 | 0.547 | 1.12 | 1.29 | -0.00719
LFAllSpcSCEs_CliExCZ09 | Com-Iltg-dWatt-LF_OSspc | SCE | s_Cli | Ex | CZ09 | 2.735 | 0.000547 | 0 | 3.055 | 0.0007225 | -0.0203 | 2.735 | 0.000547 | 0 | 3.055 | 0.0007225 | -0.0203 |  | LF | AllSpc | 2730 | 0.547 | 2730 | 0.547 | 1.12 | 1.32 | -0.0074223 | 2730 | 0.547 | 2730 | 0.547 | 1.12 | 1.32 | -0.00742
LFAllSpcSCEs_CliExCZ10 | Com-Iltg-dWatt-LF_OSspc | SCE | s_Cli | Ex | CZ10 | 2.735 | 0.000547 | 0 | 3.015 | 0.000719 | -0.020185 | 2.735 | 0.000547 | 0 | 3.015 | 0.000719 | -0.020185 |  | LF | AllSpc | 2730 | 0.547 | 2730 | 0.547 | 1.1 | 1.31 | -0.0073803 | 2730 | 0.547 | 2730 | 0.547 | 1.1 | 1.31 | -0.00738
LFAllSpcSCEs_CliExCZ13 | Com-Iltg-dWatt-LF_OSspc | SCE | s_Cli | Ex | CZ13 | 2.735 | 0.000547 | 0 | 2.975 | 0.0007115 | -0.0254 | 2.735 | 0.000547 | 0 | 2.975 | 0.0007115 | -0.0254 |  | LF | AllSpc | 2730 | 0.547 | 2730 | 0.547 | 1.09 | 1.3 | -0.009287 | 2730 | 0.547 | 2730 | 0.547 | 1.09 | 1.3 | -0.00929
LFAllSpcSCEs_CliExCZ14 | Com-Iltg-dWatt-LF_OSspc | SCE | s_Cli | Ex | CZ14 | 2.735 | 0.000547 | 0 | 2.98 | 0.0007165 | -0.02507 | 2.735 | 0.000547 | 0 | 2.98 | 0.0007165 | -0.02507 |  | LF | AllSpc | 2730 | 0.547 | 2730 | 0.547 | 1.09 | 1.31 | -0.0091664 | 2730 | 0.547 | 2730 | 0.547 | 1.09 | 1.31 | -0.00917
LFAllSpcSCEs_CliExCZ15 | Com-Iltg-dWatt-LF_OSspc | SCE | s_Cli | Ex | CZ15 | 2.735 | 0.000547 | 0 | 3.215 | 0.0007205 | -0.011754 | 2.735 | 0.000547 | 0 | 3.215 | 0.0007205 | -0.011754 |  | LF | AllSpc | 2730 | 0.547 | 2730 | 0.547 | 1.18 | 1.32 | -0.0042974 | 2730 | 0.547 | 2730 | 0.547 | 1.18 | 1.32 | -0.0043
LFAllSpcSCEs_CliExCZ16 | Com-Iltg-dWatt-LF_OSspc | SCE | s_Cli | Ex | CZ16 | 2.735 | 0.000547 | 0 | 2.725 | 0.000687 | -0.03905 | 2.735 | 0.000547 | 0 | 2.725 | 0.000687 | -0.03905 |  | LF | AllSpc | 2730 | 0.547 | 2730 | 0.547 | 0.996 | 1.26 | -0.014278 | 2730 | 0.547 | 2730 | 0.547 | 0.996 | 1.26 | -0.0143
LFAllSpcSCEs_CliExIOU | Com-Iltg-dWatt-LF_OSspc | SCE | s_Cli | Ex | IOU | 2.735 | 0.000547 | 0 | 3.0317 | 0.00070999 | -0.02068 | 2.735 | 0.000547 | 0 | 3.0317 | 0.00070999 | -0.02068 |  | LF | AllSpc | 2730 | 0.547 | 2730 | 0.547 | 1.11 | 1.3 | -0.0075611 | 2730 | 0.547 | 2730 | 0.547 | 1.11 | 1.3 | -0.00756
LFAllSpcSCEs_FStExCZ05 | Com-Iltg-dWatt-LF_OSspc | SCE | s_FSt | Ex | CZ05 | 4.05 | 0.0007655 | 0 | 4.095 | 0.0009325 | -0.04825 | 4.05 | 0.0007655 | 0 | 4.095 | 0.0009325 | -0.04825 |  | LF | AllSpc | 4050 | 0.766 | 4050 | 0.766 | 1.01 | 1.22 | -0.011914 | 4050 | 0.766 | 4050 | 0.766 | 1.01 | 1.22 | -0.0119
LFAllSpcSCEs_FStExCZ06 | Com-Iltg-dWatt-LF_OSspc | SCE | s_FSt | Ex | CZ06 | 4.05 | 0.0007655 | 0 | 4.355 | 0.0009475 | -0.03328 | 4.05 | 0.0007655 | 0 | 4.355 | 0.0009475 | -0.03328 |  | LF | AllSpc | 4050 | 0.766 | 4050 | 0.766 | 1.08 | 1.24 | -0.0082173 | 4050 | 0.766 | 4050 | 0.766 | 1.08 | 1.24 | -0.00822
LFAllSpcSCEs_FStExCZ08 | Com-Iltg-dWatt-LF_OSspc | SCE | s_FSt | Ex | CZ08 | 4.05 | 0.0007655 | 0 | 4.425 | 0.000957 | -0.0298 | 4.05 | 0.0007655 | 0 | 4.425 | 0.000957 | -0.0298 |  | LF | AllSpc | 4050 | 0.766 | 4050 | 0.766 | 1.09 | 1.25 | -0.007358 | 4050 | 0.766 | 4050 | 0.766 | 1.09 | 1.25 | -0.00736
LFAllSpcSCEs_FStExCZ09 | Com-Iltg-dWatt-LF_OSspc | SCE | s_FSt | Ex | CZ09 | 4.05 | 0.0007655 | 0 | 4.41 | 0.000967 | -0.03008 | 4.05 | 0.0007655 | 0 | 4.41 | 0.000967 | -0.03008 |  | LF | AllSpc | 4050 | 0.766 | 4050 | 0.766 | 1.09 | 1.26 | -0.0074272 | 4050 | 0.766 | 4050 | 0.766 | 1.09 | 1.26 | -0.00743
LFAllSpcSCEs_FStExCZ10 | Com-Iltg-dWatt-LF_OSspc | SCE | s_FSt | Ex | CZ10 | 4.05 | 0.0007655 | 0 | 4.37 | 0.000971 | -0.02968 | 4.05 | 0.0007655 | 0 | 4.37 | 0.000971 | -0.02968 |  | LF | AllSpc | 4050 | 0.766 | 4050 | 0.766 | 1.08 | 1.27 | -0.0073284 | 4050 | 0.766 | 4050 | 0.766 | 1.08 | 1.27 | -0.00733
LFAllSpcSCEs_FStExCZ13 | Com-Iltg-dWatt-LF_OSspc | SCE | s_FSt | Ex | CZ13 | 4.05 | 0.0007655 | 0 | 4.335 | 0.000964 | -0.0363 | 4.05 | 0.0007655 | 0 | 4.335 | 0.000964 | -0.0363 |  | LF | AllSpc | 4050 | 0.766 | 4050 | 0.766 | 1.07 | 1.26 | -0.008963 | 4050 | 0.766 | 4050 | 0.766 | 1.07 | 1.26 | -0.00896
LFAllSpcSCEs_FStExCZ14 | Com-Iltg-dWatt-LF_OSspc | SCE | s_FSt | Ex | CZ14 | 4.05 | 0.0007655 | 0 | 4.32 | 0.000977 | -0.03615 | 4.05 | 0.0007655 | 0 | 4.32 | 0.000977 | -0.03615 |  | LF | AllSpc | 4050 | 0.766 | 4050 | 0.766 | 1.07 | 1.28 | -0.0089259 | 4050 | 0.766 | 4050 | 0.766 | 1.07 | 1.28 | -0.00893
LFAllSpcSCEs_FStExCZ15 | Com-Iltg-dWatt-LF_OSspc | SCE | s_FSt | Ex | CZ15 | 4.05 | 0.0007655 | 0 | 4.65 | 0.0009735 | -0.015595 | 4.05 | 0.0007655 | 0 | 4.65 | 0.0009735 | -0.015595 |  | LF | AllSpc | 4050 | 0.766 | 4050 | 0.766 | 1.15 | 1.27 | -0.0038506 | 4050 | 0.766 | 4050 | 0.766 | 1.15 | 1.27 | -0.00385
LFAllSpcSCEs_FStExCZ16 | Com-Iltg-dWatt-LF_OSspc | SCE | s_FSt | Ex | CZ16 | 4.05 | 0.0007655 | 0 | 3.945 | 0.0009355 | -0.0564 | 4.05 | 0.0007655 | 0 | 3.945 | 0.0009355 | -0.0564 |  | LF | AllSpc | 4050 | 0.766 | 4050 | 0.766 | 0.974 | 1.22 | -0.013926 | 4050 | 0.766 | 4050 | 0.766 | 0.974 | 1.22 | -0.0139
LFAllSpcSCEs_FStExIOU | Com-Iltg-dWatt-LF_OSspc | SCE | s_FSt | Ex | IOU | 4.05 | 0.0007655 | 0 | 4.3876 | 0.00096082 | -0.030993 | 4.05 | 0.0007655 | 0 | 4.3876 | 0.00096082 | -0.030993 |  | LF | AllSpc | 4050 | 0.766 | 4050 | 0.766 | 1.08 | 1.26 | -0.0076526 | 4050 | 0.766 | 4050 | 0.766 | 1.08 | 1.26 | -0.00765
LFAllSpcSCEs_IndExCZ05 | Com-Iltg-dWatt-LF_OSspc | SCE | s_Ind | Ex | CZ05 | 2.93 | 0.0007555 | 0 | 3.22 | 0.0009345 | -0.008325 | 2.93 | 0.0007555 | 0 | 3.22 | 0.0009345 | -0.008325 |  | LF | AllSpc | 2930 | 0.755 | 2930 | 0.755 | 1.1 | 1.24 | -0.0028413 | 2930 | 0.755 | 2930 | 0.755 | 1.1 | 1.24 | -0.00284
LFAllSpcSCEs_IndExCZ06 | Com-Iltg-dWatt-LF_OSspc | SCE | s_Ind | Ex | CZ06 | 2.93 | 0.0007555 | 0 | 3.35 | 0.000915 | -0.0029385 | 2.93 | 0.0007555 | 0 | 3.35 | 0.000915 | -0.0029385 |  | LF | AllSpc | 2930 | 0.755 | 2930 | 0.755 | 1.14 | 1.21 | -0.0010029 | 2930 | 0.755 | 2930 | 0.755 | 1.14 | 1.21 | -0.001
LFAllSpcSCEs_IndExCZ08 | Com-Iltg-dWatt-LF_OSspc | SCE | s_Ind | Ex | CZ08 | 2.93 | 0.0007555 | 0 | 3.365 | 0.0009325 | -0.0023495 | 2.93 | 0.0007555 | 0 | 3.365 | 0.0009325 | -0.0023495 |  | LF | AllSpc | 2930 | 0.755 | 2930 | 0.755 | 1.15 | 1.23 | -0.00080188 | 2930 | 0.755 | 2930 | 0.755 | 1.15 | 1.23 | -0.000802
LFAllSpcSCEs_IndExCZ09 | Com-Iltg-dWatt-LF_OSspc | SCE | s_Ind | Ex | CZ09 | 2.93 | 0.0007555 | 0 | 3.35 | 0.000945 | -0.003389 | 2.93 | 0.0007555 | 0 | 3.35 | 0.000945 | -0.003389 |  | LF | AllSpc | 2930 | 0.755 | 2930 | 0.755 | 1.14 | 1.25 | -0.0011567 | 2930 | 0.755 | 2930 | 0.755 | 1.14 | 1.25 | -0.00116
LFAllSpcSCEs_IndExCZ10 | Com-Iltg-dWatt-LF_OSspc | SCE | s_Ind | Ex | CZ10 | 2.93 | 0.0007555 | 0 | 3.255 | 0.000941 | -0.0037 | 2.93 | 0.0007555 | 0 | 3.255 | 0.000941 | -0.0037 |  | LF | AllSpc | 2930 | 0.755 | 2930 | 0.755 | 1.11 | 1.25 | -0.0012628 | 2930 | 0.755 | 2930 | 0.755 | 1.11 | 1.25 | -0.00126
LFAllSpcSCEs_IndExCZ13 | Com-Iltg-dWatt-LF_OSspc | SCE | s_Ind | Ex | CZ13 | 2.93 | 0.0007555 | 0 | 3.24 | 0.0009215 | -0.00872 | 2.93 | 0.0007555 | 0 | 3.24 | 0.0009215 | -0.00872 |  | LF | AllSpc | 2930 | 0.755 | 2930 | 0.755 | 1.11 | 1.22 | -0.0029761 | 2930 | 0.755 | 2930 | 0.755 | 1.11 | 1.22 | -0.00298
LFAllSpcSCEs_IndExCZ14 | Com-Iltg-dWatt-LF_OSspc | SCE | s_Ind | Ex | CZ14 | 2.93 | 0.0007555 | 0 | 3.225 | 0.0009385 | -0.01012 | 2.93 | 0.0007555 | 0 | 3.225 | 0.0009385 | -0.01012 |  | LF | AllSpc | 2930 | 0.755 | 2930 | 0.755 | 1.1 | 1.24 | -0.0034539 | 2930 | 0.755 | 2930 | 0.755 | 1.1 | 1.24 | -0.00345
LFAllSpcSCEs_IndExCZ15 | Com-Iltg-dWatt-LF_OSspc | SCE | s_Ind | Ex | CZ15 | 2.93 | 0.0007555 | 0 | 3.43 | 0.000939 | -0.00085 | 2.93 | 0.0007555 | 0 | 3.43 | 0.000939 | -0.00085 |  | LF | AllSpc | 2930 | 0.755 | 2930 | 0.755 | 1.17 | 1.24 | -0.0002901 | 2930 | 0.755 | 2930 | 0.755 | 1.17 | 1.24 | -0.00029
LFAllSpcSCEs_IndExCZ16 | Com-Iltg-dWatt-LF_OSspc | SCE | s_Ind | Ex | CZ16 | 2.93 | 0.0007555 | 0 | 3.02 | 0.000903 | -0.0214 | 2.93 | 0.0007555 | 0 | 3.02 | 0.000903 | -0.0214 |  | LF | AllSpc | 2930 | 0.755 | 2930 | 0.755 | 1.03 | 1.2 | -0.0073038 | 2930 | 0.755 | 2930 | 0.755 | 1.03 | 1.2 | -0.0073
LFAllSpcSCEs_IndExIOU | Com-Iltg-dWatt-LF_OSspc | SCE | s_Ind | Ex | IOU | 2.93 | 0.0007555 | 0 | 3.3291 | 0.00093166 | -0.0036407 | 2.93 | 0.0007555 | 0 | 3.3291 | 0.00093166 | -0.0036407 |  | LF | AllSpc | 2930 | 0.755 | 2930 | 0.755 | 1.14 | 1.23 | -0.0012426 | 2930 | 0.755 | 2930 | 0.755 | 1.14 | 1.23 | -0.00124
LFAllSpcSCEs_MiCExCZ05 | Com-Iltg-dWatt-LF_OSspc | SCE | s_MiC | Ex | CZ05 | 3.0267 | 0.00068567 | 0 | 3.22 | 0.00084 | -0.022343 | 3.0267 | 0.00068567 | 0 | 3.22 | 0.00084 | -0.022343 |  | LF | AllSpc | 3030 | 0.686 | 3030 | 0.686 | 1.06 | 1.23 | -0.0073821 | 3030 | 0.686 | 3030 | 0.686 | 1.06 | 1.23 | -0.00738
LFAllSpcSCEs_MiCExCZ06 | Com-Iltg-dWatt-LF_OSspc | SCE | s_MiC | Ex | CZ06 | 3.0267 | 0.00068567 | 0 | 3.4133 | 0.000852 | -0.010533 | 3.0267 | 0.00068567 | 0 | 3.4133 | 0.000852 | -0.010533 |  | LF | AllSpc | 3030 | 0.686 | 3030 | 0.686 | 1.13 | 1.24 | -0.0034802 | 3030 | 0.686 | 3030 | 0.686 | 1.13 | 1.24 | -0.00348
LFAllSpcSCEs_MiCExCZ08 | Com-Iltg-dWatt-LF_OSspc | SCE | s_MiC | Ex | CZ08 | 3.0267 | 0.00068567 | 0 | 3.4367 | 0.000845 | -0.0088467 | 3.0267 | 0.00068567 | 0 | 3.4367 | 0.000845 | -0.0088467 |  | LF | AllSpc | 3030 | 0.686 | 3030 | 0.686 | 1.14 | 1.23 | -0.0029229 | 3030 | 0.686 | 3030 | 0.686 | 1.14 | 1.23 | -0.00292
LFAllSpcSCEs_MiCExCZ09 | Com-Iltg-dWatt-LF_OSspc | SCE | s_MiC | Ex | CZ09 | 3.0267 | 0.00068567 | 0 | 3.4133 | 0.000853 | -0.010387 | 3.0267 | 0.00068567 | 0 | 3.4133 | 0.000853 | -0.010387 |  | LF | AllSpc | 3030 | 0.686 | 3030 | 0.686 | 1.13 | 1.24 | -0.0034317 | 3030 | 0.686 | 3030 | 0.686 | 1.13 | 1.24 | -0.00343
LFAllSpcSCEs_MiCExCZ10 | Com-Iltg-dWatt-LF_OSspc | SCE | s_MiC | Ex | CZ10 | 3.0267 | 0.00068567 | 0 | 3.36 | 0.00083333 | -0.01091 | 3.0267 | 0.00068567 | 0 | 3.36 | 0.00083333 | -0.01091 |  | LF | AllSpc | 3030 | 0.686 | 3030 | 0.686 | 1.11 | 1.22 | -0.0036046 | 3030 | 0.686 | 3030 | 0.686 | 1.11 | 1.22 | -0.0036
LFAllSpcSCEs_MiCExCZ13 | Com-Iltg-dWatt-LF_OSspc | SCE | s_MiC | Ex | CZ13 | 3.0267 | 0.00068567 | 0 | 3.3033 | 0.000853 | -0.0203 | 3.0267 | 0.00068567 | 0 | 3.3033 | 0.000853 | -0.0203 |  | LF | AllSpc | 3030 | 0.686 | 3030 | 0.686 | 1.09 | 1.24 | -0.006707 | 3030 | 0.686 | 3030 | 0.686 | 1.09 | 1.24 | -0.00671
LFAllSpcSCEs_MiCExCZ14 | Com-Iltg-dWatt-LF_OSspc | SCE | s_MiC | Ex | CZ14 | 3.0267 | 0.00068567 | 0 | 3.2867 | 0.000837 | -0.019813 | 3.0267 | 0.00068567 | 0 | 3.2867 | 0.000837 | -0.019813 |  | LF | AllSpc | 3030 | 0.686 | 3030 | 0.686 | 1.09 | 1.22 | -0.0065462 | 3030 | 0.686 | 3030 | 0.686 | 1.09 | 1.22 | -0.00655
LFAllSpcSCEs_MiCExCZ15 | Com-Iltg-dWatt-LF_OSspc | SCE | s_MiC | Ex | CZ15 | 3.0267 | 0.00068567 | 0 | 3.57 | 0.00086067 | -0.003869 | 3.0267 | 0.00068567 | 0 | 3.57 | 0.00086067 | -0.003869 |  | LF | AllSpc | 3030 | 0.686 | 3030 | 0.686 | 1.18 | 1.26 | -0.0012783 | 3030 | 0.686 | 3030 | 0.686 | 1.18 | 1.26 | -0.00128
LFAllSpcSCEs_MiCExCZ16 | Com-Iltg-dWatt-LF_OSspc | SCE | s_MiC | Ex | CZ16 | 3.0267 | 0.00068567 | 0 | 3.0133 | 0.00082733 | -0.037733 | 3.0267 | 0.00068567 | 0 | 3.0133 | 0.00082733 | -0.037733 |  | LF | AllSpc | 3030 | 0.686 | 3030 | 0.686 | 0.996 | 1.21 | -0.012467 | 3030 | 0.686 | 3030 | 0.686 | 0.996 | 1.21 | -0.0125
LFAllSpcSCEs_MiCExIOU | Com-Iltg-dWatt-LF_OSspc | SCE | s_MiC | Ex | IOU | 3.0267 | 0.00068567 | 0 | 3.4001 | 0.00084519 | -0.010949 | 3.0267 | 0.00068567 | 0 | 3.4001 | 0.00084519 | -0.010949 |  | LF | AllSpc | 3030 | 0.686 | 3030 | 0.686 | 1.12 | 1.23 | -0.0036176 | 3030 | 0.686 | 3030 | 0.686 | 1.12 | 1.23 | -0.00362
LFAllSpcSCEs_TCUExCZ05 | Com-Iltg-dWatt-LF_OSspc | SCE | s_TCU | Ex | CZ05 | 2.618 | 0.00061 | 0 | 2.684 | 0.0007332 | -0.013686 | 2.618 | 0.00061 | 0 | 2.684 | 0.0007332 | -0.013686 |  | LF | AllSpc | 2620 | 0.61 | 2620 | 0.61 | 1.03 | 1.2 | -0.0052277 | 2620 | 0.61 | 2620 | 0.61 | 1.03 | 1.2 | -0.00523
LFAllSpcSCEs_TCUExCZ06 | Com-Iltg-dWatt-LF_OSspc | SCE | s_TCU | Ex | CZ06 | 2.618 | 0.00061 | 0 | 2.826 | 0.0007414 | -0.006938 | 2.618 | 0.00061 | 0 | 2.826 | 0.0007414 | -0.006938 |  | LF | AllSpc | 2620 | 0.61 | 2620 | 0.61 | 1.08 | 1.22 | -0.0026501 | 2620 | 0.61 | 2620 | 0.61 | 1.08 | 1.22 | -0.00265
LFAllSpcSCEs_TCUExCZ08 | Com-Iltg-dWatt-LF_OSspc | SCE | s_TCU | Ex | CZ08 | 2.618 | 0.00061 | 0 | 2.844 | 0.0007434 | -0.006216 | 2.618 | 0.00061 | 0 | 2.844 | 0.0007434 | -0.006216 |  | LF | AllSpc | 2620 | 0.61 | 2620 | 0.61 | 1.09 | 1.22 | -0.0023743 | 2620 | 0.61 | 2620 | 0.61 | 1.09 | 1.22 | -0.00237
LFAllSpcSCEs_TCUExCZ09 | Com-Iltg-dWatt-LF_OSspc | SCE | s_TCU | Ex | CZ09 | 2.618 | 0.00061 | 0 | 2.834 | 0.0007546 | -0.007512 | 2.618 | 0.00061 | 0 | 2.834 | 0.0007546 | -0.007512 |  | LF | AllSpc | 2620 | 0.61 | 2620 | 0.61 | 1.08 | 1.24 | -0.0028694 | 2620 | 0.61 | 2620 | 0.61 | 1.08 | 1.24 | -0.00287
LFAllSpcSCEs_TCUExCZ10 | Com-Iltg-dWatt-LF_OSspc | SCE | s_TCU | Ex | CZ10 | 2.618 | 0.00061 | 0 | 2.806 | 0.0007474 | -0.00736 | 2.618 | 0.00061 | 0 | 2.806 | 0.0007474 | -0.00736 |  | LF | AllSpc | 2620 | 0.61 | 2620 | 0.61 | 1.07 | 1.23 | -0.0028113 | 2620 | 0.61 | 2620 | 0.61 | 1.07 | 1.23 | -0.00281
LFAllSpcSCEs_TCUExCZ13 | Com-Iltg-dWatt-LF_OSspc | SCE | s_TCU | Ex | CZ13 | 2.618 | 0.00061 | 0 | 2.778 | 0.00074 | -0.01194 | 2.618 | 0.00061 | 0 | 2.778 | 0.00074 | -0.01194 |  | LF | AllSpc | 2620 | 0.61 | 2620 | 0.61 | 1.06 | 1.21 | -0.0045607 | 2620 | 0.61 | 2620 | 0.61 | 1.06 | 1.21 | -0.00456
LFAllSpcSCEs_TCUExCZ14 | Com-Iltg-dWatt-LF_OSspc | SCE | s_TCU | Ex | CZ14 | 2.618 | 0.00061 | 0 | 2.766 | 0.0007462 | -0.012408 | 2.618 | 0.00061 | 0 | 2.766 | 0.0007462 | -0.012408 |  | LF | AllSpc | 2620 | 0.61 | 2620 | 0.61 | 1.06 | 1.22 | -0.0047395 | 2620 | 0.61 | 2620 | 0.61 | 1.06 | 1.22 | -0.00474
LFAllSpcSCEs_TCUExCZ15 | Com-Iltg-dWatt-LF_OSspc | SCE | s_TCU | Ex | CZ15 | 2.618 | 0.00061 | 0 | 2.946 | 0.0007442 | -0.0031154 | 2.618 | 0.00061 | 0 | 2.946 | 0.0007442 | -0.0031154 |  | LF | AllSpc | 2620 | 0.61 | 2620 | 0.61 | 1.13 | 1.22 | -0.00119 | 2620 | 0.61 | 2620 | 0.61 | 1.13 | 1.22 | -0.00119
LFAllSpcSCEs_TCUExCZ16 | Com-Iltg-dWatt-LF_OSspc | SCE | s_TCU | Ex | CZ16 | 2.618 | 0.00061 | 0 | 2.59 | 0.0007258 | -0.02162 | 2.618 | 0.00061 | 0 | 2.59 | 0.0007258 | -0.02162 |  | LF | AllSpc | 2620 | 0.61 | 2620 | 0.61 | 0.989 | 1.19 | -0.0082582 | 2620 | 0.61 | 2620 | 0.61 | 0.989 | 1.19 | -0.00826
LFAllSpcSCEs_TCUExIOU | Com-Iltg-dWatt-LF_OSspc | SCE | s_TCU | Ex | IOU | 2.618 | 0.00061 | 0 | 2.8277 | 0.00074512 | -0.0072703 | 2.618 | 0.00061 | 0 | 2.8277 | 0.00074512 | -0.0072703 |  | LF | AllSpc | 2620 | 0.61 | 2620 | 0.61 | 1.08 | 1.22 | -0.002777 | 2620 | 0.61 | 2620 | 0.61 | 1.08 | 1.22 | -0.00278
LFAllSpcSCESCnExCZ05 | Com-Iltg-dWatt-LF_OSspc | SCE | SCn | Ex | CZ05 | 3.14 | 0.000588 | 0 | 2.9 | 0.000743 | -0.033 | 3.14 | 0.000588 | 0 | 2.9 | 0.000743 | -0.033 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 0.924 | 1.26 | -0.01051 | 3140 | 0.588 | 3140 | 0.588 | 0.924 | 1.26 | -0.0105
LFAllSpcSCESCnExCZ06 | Com-Iltg-dWatt-LF_OSspc | SCE | SCn | Ex | CZ06 | 3.14 | 0.000588 | 0 | 3.24 | 0.00077 | -0.0173 | 3.14 | 0.000588 | 0 | 3.24 | 0.00077 | -0.0173 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 1.03 | 1.31 | -0.0055096 | 3140 | 0.588 | 3140 | 0.588 | 1.03 | 1.31 | -0.00551
LFAllSpcSCESCnExCZ08 | Com-Iltg-dWatt-LF_OSspc | SCE | SCn | Ex | CZ08 | 3.14 | 0.000588 | 0 | 3.29 | 0.000768 | -0.0149 | 3.14 | 0.000588 | 0 | 3.29 | 0.000768 | -0.0149 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 1.05 | 1.31 | -0.0047452 | 3140 | 0.588 | 3140 | 0.588 | 1.05 | 1.31 | -0.00475
LFAllSpcSCESCnExCZ09 | Com-Iltg-dWatt-LF_OSspc | SCE | SCn | Ex | CZ09 | 3.14 | 0.000588 | 0 | 3.2702 | 0.000782 | -0.0176 | 3.14 | 0.000588 | 0 | 3.2702 | 0.000782 | -0.0176 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 1.04 | 1.33 | -0.0056051 | 3140 | 0.588 | 3140 | 0.588 | 1.04 | 1.33 | -0.00561
LFAllSpcSCESCnExCZ10 | Com-Iltg-dWatt-LF_OSspc | SCE | SCn | Ex | CZ10 | 3.14 | 0.000588 | 0 | 3.26 | 0.000771 | -0.0185 | 3.14 | 0.000588 | 0 | 3.26 | 0.000771 | -0.0185 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 1.04 | 1.31 | -0.0058917 | 3140 | 0.588 | 3140 | 0.588 | 1.04 | 1.31 | -0.00589
LFAllSpcSCESCnExCZ13 | Com-Iltg-dWatt-LF_OSspc | SCE | SCn | Ex | CZ13 | 3.14 | 0.000588 | 0 | 3.21 | 0.000761 | -0.0245 | 3.14 | 0.000588 | 0 | 3.21 | 0.000761 | -0.0245 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 1.02 | 1.29 | -0.0078025 | 3140 | 0.588 | 3140 | 0.588 | 1.02 | 1.29 | -0.0078
LFAllSpcSCESCnExCZ14 | Com-Iltg-dWatt-LF_OSspc | SCE | SCn | Ex | CZ14 | 3.14 | 0.000588 | 0 | 3.18 | 0.00076 | -0.027 | 3.14 | 0.000588 | 0 | 3.18 | 0.00076 | -0.027 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 1.01 | 1.29 | -0.0085987 | 3140 | 0.588 | 3140 | 0.588 | 1.01 | 1.29 | -0.0086
LFAllSpcSCESCnExCZ15 | Com-Iltg-dWatt-LF_OSspc | SCE | SCn | Ex | CZ15 | 3.14 | 0.000588 | 0 | 3.4815 | 0.000764 | -0.00738 | 3.14 | 0.000588 | 0 | 3.4815 | 0.000764 | -0.00738 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 1.11 | 1.3 | -0.0023503 | 3140 | 0.588 | 3140 | 0.588 | 1.11 | 1.3 | -0.00235
LFAllSpcSCESCnExCZ16 | Com-Iltg-dWatt-LF_OSspc | SCE | SCn | Ex | CZ16 | 3.14 | 0.000588 | 0 | 2.87 | 0.000739 | -0.0386 | 3.14 | 0.000588 | 0 | 2.87 | 0.000739 | -0.0386 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 0.914 | 1.26 | -0.012293 | 3140 | 0.588 | 3140 | 0.588 | 0.914 | 1.26 | -0.0123
LFAllSpcSCESCnExIOU | Com-Iltg-dWatt-LF_OSspc | SCE | SCn | Ex | IOU | 3.14 | 0.000588 | 0 | 3.2679 | 0.00077033 | -0.017016 | 3.14 | 0.000588 | 0 | 3.2679 | 0.00077033 | -0.017016 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 1.04 | 1.31 | -0.0054191 | 3140 | 0.588 | 3140 | 0.588 | 1.04 | 1.31 | -0.00542
LFAllSpcSCESCnNewCZ05 | Com-Iltg-dWatt-LF_OSspc | SCE | SCn | New | CZ05 | 3.14 | 0.000588 | 0 | 2.92 | 0.000741 | -0.0348 | 3.14 | 0.000588 | 0 | 2.92 | 0.000741 | -0.0348 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 0.93 | 1.26 | -0.011083 | 3140 | 0.588 | 3140 | 0.588 | 0.93 | 1.26 | -0.0111
LFAllSpcSCESCnNewCZ06 | Com-Iltg-dWatt-LF_OSspc | SCE | SCn | New | CZ06 | 3.14 | 0.000588 | 0 | 3.14 | 0.000711 | -0.0185 | 3.14 | 0.000588 | 0 | 3.14 | 0.000711 | -0.0185 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 1 | 1.21 | -0.0058917 | 3140 | 0.588 | 3140 | 0.588 | 1 | 1.21 | -0.00589
LFAllSpcSCESCnNewCZ08 | Com-Iltg-dWatt-LF_OSspc | SCE | SCn | New | CZ08 | 3.14 | 0.000588 | 0 | 3.22 | 0.000722 | -0.0161 | 3.14 | 0.000588 | 0 | 3.22 | 0.000722 | -0.0161 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 1.03 | 1.23 | -0.0051274 | 3140 | 0.588 | 3140 | 0.588 | 1.03 | 1.23 | -0.00513
LFAllSpcSCESCnNewCZ09 | Com-Iltg-dWatt-LF_OSspc | SCE | SCn | New | CZ09 | 3.14 | 0.000588 | 0 | 3.22 | 0.000747 | -0.0173 | 3.14 | 0.000588 | 0 | 3.22 | 0.000747 | -0.0173 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 1.03 | 1.27 | -0.0055096 | 3140 | 0.588 | 3140 | 0.588 | 1.03 | 1.27 | -0.00551
LFAllSpcSCESCnNewCZ10 | Com-Iltg-dWatt-LF_OSspc | SCE | SCn | New | CZ10 | 3.14 | 0.000588 | 0 | 3.23 | 0.00074 | -0.0188 | 3.14 | 0.000588 | 0 | 3.23 | 0.00074 | -0.0188 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 1.03 | 1.26 | -0.0059873 | 3140 | 0.588 | 3140 | 0.588 | 1.03 | 1.26 | -0.00599
LFAllSpcSCESCnNewCZ13 | Com-Iltg-dWatt-LF_OSspc | SCE | SCn | New | CZ13 | 3.14 | 0.000588 | 0 | 3.13 | 0.00072 | -0.0246 | 3.14 | 0.000588 | 0 | 3.13 | 0.00072 | -0.0246 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 0.997 | 1.22 | -0.0078344 | 3140 | 0.588 | 3140 | 0.588 | 0.997 | 1.22 | -0.00783
LFAllSpcSCESCnNewCZ14 | Com-Iltg-dWatt-LF_OSspc | SCE | SCn | New | CZ14 | 3.14 | 0.000588 | 0 | 3.16 | 0.000737 | -0.0277 | 3.14 | 0.000588 | 0 | 3.16 | 0.000737 | -0.0277 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 1.01 | 1.25 | -0.0088217 | 3140 | 0.588 | 3140 | 0.588 | 1.01 | 1.25 | -0.00882
LFAllSpcSCESCnNewCZ15 | Com-Iltg-dWatt-LF_OSspc | SCE | SCn | New | CZ15 | 3.14 | 0.000588 | 0 | 3.43 | 0.000743 | -0.0059 | 3.14 | 0.000588 | 0 | 3.43 | 0.000743 | -0.0059 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 1.09 | 1.26 | -0.001879 | 3140 | 0.588 | 3140 | 0.588 | 1.09 | 1.26 | -0.00188
LFAllSpcSCESCnNewCZ16 | Com-Iltg-dWatt-LF_OSspc | SCE | SCn | New | CZ16 | 3.14 | 0.000588 | 0 | 2.85 | 0.000712 | -0.0402 | 3.14 | 0.000588 | 0 | 2.85 | 0.000712 | -0.0402 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 0.908 | 1.21 | -0.012803 | 3140 | 0.588 | 3140 | 0.588 | 0.908 | 1.21 | -0.0128
LFAllSpcSCESCnNewIOU | Com-Iltg-dWatt-LF_OSspc | SCE | SCn | New | IOU | 3.14 | 0.000588 | 0 | 3.2166 | 0.00073429 | -0.018497 | 3.14 | 0.000588 | 0 | 3.2166 | 0.00073429 | -0.018497 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 1.02 | 1.25 | -0.0058907 | 3140 | 0.588 | 3140 | 0.588 | 1.02 | 1.25 | -0.00589
LFAllSpcSCESUnExCZ05 | Com-Iltg-dWatt-LF_OSspc | SCE | SUn | Ex | CZ05 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0 | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0
LFAllSpcSCESUnExCZ06 | Com-Iltg-dWatt-LF_OSspc | SCE | SUn | Ex | CZ06 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0 | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0
LFAllSpcSCESUnExCZ08 | Com-Iltg-dWatt-LF_OSspc | SCE | SUn | Ex | CZ08 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0 | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0
LFAllSpcSCESUnExCZ09 | Com-Iltg-dWatt-LF_OSspc | SCE | SUn | Ex | CZ09 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0 | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0
LFAllSpcSCESUnExCZ10 | Com-Iltg-dWatt-LF_OSspc | SCE | SUn | Ex | CZ10 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0 | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0
LFAllSpcSCESUnExCZ13 | Com-Iltg-dWatt-LF_OSspc | SCE | SUn | Ex | CZ13 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0 | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0
LFAllSpcSCESUnExCZ14 | Com-Iltg-dWatt-LF_OSspc | SCE | SUn | Ex | CZ14 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0 | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0
LFAllSpcSCESUnExCZ15 | Com-Iltg-dWatt-LF_OSspc | SCE | SUn | Ex | CZ15 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0 | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0
LFAllSpcSCESUnExCZ16 | Com-Iltg-dWatt-LF_OSspc | SCE | SUn | Ex | CZ16 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0 | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0
LFAllSpcSCESUnExIOU | Com-Iltg-dWatt-LF_OSspc | SCE | SUn | Ex | IOU | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0 | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0
LFAllSpcSCESUnNewCZ05 | Com-Iltg-dWatt-LF_OSspc | SCE | SUn | New | CZ05 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0 | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0
LFAllSpcSCESUnNewCZ06 | Com-Iltg-dWatt-LF_OSspc | SCE | SUn | New | CZ06 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0 | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0
LFAllSpcSCESUnNewCZ08 | Com-Iltg-dWatt-LF_OSspc | SCE | SUn | New | CZ08 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0 | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0
LFAllSpcSCESUnNewCZ09 | Com-Iltg-dWatt-LF_OSspc | SCE | SUn | New | CZ09 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0 | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0
LFAllSpcSCESUnNewCZ10 | Com-Iltg-dWatt-LF_OSspc | SCE | SUn | New | CZ10 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0 | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0
LFAllSpcSCESUnNewCZ13 | Com-Iltg-dWatt-LF_OSspc | SCE | SUn | New | CZ13 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0 | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0
LFAllSpcSCESUnNewCZ14 | Com-Iltg-dWatt-LF_OSspc | SCE | SUn | New | CZ14 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0 | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0
LFAllSpcSCESUnNewCZ15 | Com-Iltg-dWatt-LF_OSspc | SCE | SUn | New | CZ15 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0 | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0
LFAllSpcSCESUnNewCZ16 | Com-Iltg-dWatt-LF_OSspc | SCE | SUn | New | CZ16 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0 | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0
LFAllSpcSCESUnNewIOU | Com-Iltg-dWatt-LF_OSspc | SCE | SUn | New | IOU | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0 | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0
LFAllSpcSCEWRfExCZ06 | Com-Iltg-dWatt-LF_OSspc | SCE | WRf | Ex | CZ06 | 3.13 | 0.000473 | 0 | 4.9493 | 0.000593 | 0 | 3.13 | 0.000473 | 0 | 4.9493 | 0.000593 | 0 |  | LF | AllSpc | 3130 | 0.473 | 3130 | 0.473 | 1.58 | 1.25 | 0 | 3130 | 0.473 | 3130 | 0.473 | 1.58 | 1.25 | 0
LFAllSpcSCEWRfExCZ08 | Com-Iltg-dWatt-LF_OSspc | SCE | WRf | Ex | CZ08 | 3.13 | 0.000473 | 0 | 5 | 0.000594 | 0 | 3.13 | 0.000473 | 0 | 5 | 0.000594 | 0 |  | LF | AllSpc | 3130 | 0.473 | 3130 | 0.473 | 1.6 | 1.26 | 0 | 3130 | 0.473 | 3130 | 0.473 | 1.6 | 1.26 | 0
LFAllSpcSCEWRfExCZ09 | Com-Iltg-dWatt-LF_OSspc | SCE | WRf | Ex | CZ09 | 3.13 | 0.000473 | 0 | 4.9693 | 0.000606 | 0 | 3.13 | 0.000473 | 0 | 4.9693 | 0.000606 | 0 |  | LF | AllSpc | 3130 | 0.473 | 3130 | 0.473 | 1.59 | 1.28 | 0 | 3130 | 0.473 | 3130 | 0.473 | 1.59 | 1.28 | 0
LFAllSpcSCEWRfExCZ10 | Com-Iltg-dWatt-LF_OSspc | SCE | WRf | Ex | CZ10 | 3.13 | 0.000473 | 0 | 4.9591 | 0.000597 | 0 | 3.13 | 0.000473 | 0 | 4.9591 | 0.000597 | 0 |  | LF | AllSpc | 3130 | 0.473 | 3130 | 0.473 | 1.58 | 1.26 | 0 | 3130 | 0.473 | 3130 | 0.473 | 1.58 | 1.26 | 0
LFAllSpcSCEWRfExCZ13 | Com-Iltg-dWatt-LF_OSspc | SCE | WRf | Ex | CZ13 | 3.13 | 0.000473 | 0 | 4.8586 | 0.000596 | 0 | 3.13 | 0.000473 | 0 | 4.8586 | 0.000596 | 0 |  | LF | AllSpc | 3130 | 0.473 | 3130 | 0.473 | 1.55 | 1.26 | 0 | 3130 | 0.473 | 3130 | 0.473 | 1.55 | 1.26 | 0
LFAllSpcSCEWRfExCZ14 | Com-Iltg-dWatt-LF_OSspc | SCE | WRf | Ex | CZ14 | 3.13 | 0.000473 | 0 | 4.7691 | 0.000594 | 0 | 3.13 | 0.000473 | 0 | 4.7691 | 0.000594 | 0 |  | LF | AllSpc | 3130 | 0.473 | 3130 | 0.473 | 1.52 | 1.26 | 0 | 3130 | 0.473 | 3130 | 0.473 | 1.52 | 1.26 | 0
LFAllSpcSCEWRfExCZ15 | Com-Iltg-dWatt-LF_OSspc | SCE | WRf | Ex | CZ15 | 3.13 | 0.000473 | 0 | 5.1 | 0.000597 | 0 | 3.13 | 0.000473 | 0 | 5.1 | 0.000597 | 0 |  | LF | AllSpc | 3130 | 0.473 | 3130 | 0.473 | 1.63 | 1.26 | 0 | 3130 | 0.473 | 3130 | 0.473 | 1.63 | 1.26 | 0
LFAllSpcSCEWRfExCZ16 | Com-Iltg-dWatt-LF_OSspc | SCE | WRf | Ex | CZ16 | 3.13 | 0.000473 | 0 | 4.33 | 0.000673 | -0.000107 | 3.13 | 0.000473 | 0 | 4.33 | 0.000673 | -0.000107 |  | LF | AllSpc | 3130 | 0.473 | 3130 | 0.473 | 1.38 | 1.42 | -3.4185e-05 | 3130 | 0.473 | 3130 | 0.473 | 1.38 | 1.42 | -3.42e-05
LFAllSpcSCEWRfExIOU | Com-Iltg-dWatt-LF_OSspc | SCE | WRf | Ex | IOU | 3.13 | 0.000473 | 0 | 4.9545 | 0.00059601 | -3.437e-07 | 3.13 | 0.000473 | 0 | 4.9545 | 0.00059601 | -3.437e-07 |  | LF | AllSpc | 3130 | 0.473 | 3130 | 0.473 | 1.58 | 1.26 | -1.0981e-07 | 3130 | 0.473 | 3130 | 0.473 | 1.58 | 1.26 | -1.1e-07
LFAllSpcSCEWRfNewCZ05 | Com-Iltg-dWatt-LF_OSspc | SCE | WRf | New | CZ05 | 3.13 | 0.000473 | 0 | 4.04 | 0.000785 | 0 | 3.13 | 0.000473 | 0 | 4.04 | 0.000785 | 0 |  | LF | AllSpc | 3130 | 0.473 | 3130 | 0.473 | 1.29 | 1.66 | 0 | 3130 | 0.473 | 3130 | 0.473 | 1.29 | 1.66 | 0
LFAllSpcSCEWRfNewCZ06 | Com-Iltg-dWatt-LF_OSspc | SCE | WRf | New | CZ06 | 3.13 | 0.000473 | 0 | 4.5 | 0.000583 | 0 | 3.13 | 0.000473 | 0 | 4.5 | 0.000583 | 0 |  | LF | AllSpc | 3130 | 0.473 | 3130 | 0.473 | 1.44 | 1.23 | 0 | 3130 | 0.473 | 3130 | 0.473 | 1.44 | 1.23 | 0
LFAllSpcSCEWRfNewCZ08 | Com-Iltg-dWatt-LF_OSspc | SCE | WRf | New | CZ08 | 3.13 | 0.000473 | 0 | 4.45 | 0.000585 | 0 | 3.13 | 0.000473 | 0 | 4.45 | 0.000585 | 0 |  | LF | AllSpc | 3130 | 0.473 | 3130 | 0.473 | 1.42 | 1.24 | 0 | 3130 | 0.473 | 3130 | 0.473 | 1.42 | 1.24 | 0
LFAllSpcSCEWRfNewCZ09 | Com-Iltg-dWatt-LF_OSspc | SCE | WRf | New | CZ09 | 3.13 | 0.000473 | 0 | 4.41 | 0.000604 | 0 | 3.13 | 0.000473 | 0 | 4.41 | 0.000604 | 0 |  | LF | AllSpc | 3130 | 0.473 | 3130 | 0.473 | 1.41 | 1.28 | 0 | 3130 | 0.473 | 3130 | 0.473 | 1.41 | 1.28 | 0
LFAllSpcSCEWRfNewCZ10 | Com-Iltg-dWatt-LF_OSspc | SCE | WRf | New | CZ10 | 3.13 | 0.000473 | 0 | 4.39 | 0.000592 | 0 | 3.13 | 0.000473 | 0 | 4.39 | 0.000592 | 0 |  | LF | AllSpc | 3130 | 0.473 | 3130 | 0.473 | 1.4 | 1.25 | 0 | 3130 | 0.473 | 3130 | 0.473 | 1.4 | 1.25 | 0
LFAllSpcSCEWRfNewCZ13 | Com-Iltg-dWatt-LF_OSspc | SCE | WRf | New | CZ13 | 3.13 | 0.000473 | 0 | 4.39 | 0.000591 | 0 | 3.13 | 0.000473 | 0 | 4.39 | 0.000591 | 0 |  | LF | AllSpc | 3130 | 0.473 | 3130 | 0.473 | 1.4 | 1.25 | 0 | 3130 | 0.473 | 3130 | 0.473 | 1.4 | 1.25 | 0
LFAllSpcSCEWRfNewCZ14 | Com-Iltg-dWatt-LF_OSspc | SCE | WRf | New | CZ14 | 3.13 | 0.000473 | 0 | 4.3 | 0.000586 | 0 | 3.13 | 0.000473 | 0 | 4.3 | 0.000586 | 0 |  | LF | AllSpc | 3130 | 0.473 | 3130 | 0.473 | 1.37 | 1.24 | 0 | 3130 | 0.473 | 3130 | 0.473 | 1.37 | 1.24 | 0
LFAllSpcSCEWRfNewCZ15 | Com-Iltg-dWatt-LF_OSspc | SCE | WRf | New | CZ15 | 3.13 | 0.000473 | 0 | 4.6 | 0.00059 | 0 | 3.13 | 0.000473 | 0 | 4.6 | 0.00059 | 0 |  | LF | AllSpc | 3130 | 0.473 | 3130 | 0.473 | 1.47 | 1.25 | 0 | 3130 | 0.473 | 3130 | 0.473 | 1.47 | 1.25 | 0
LFAllSpcSCEWRfNewCZ16 | Com-Iltg-dWatt-LF_OSspc | SCE | WRf | New | CZ16 | 3.13 | 0.000473 | 0 | 3.94 | 0.000945 | 0 | 3.13 | 0.000473 | 0 | 3.94 | 0.000945 | 0 |  | LF | AllSpc | 3130 | 0.473 | 3130 | 0.473 | 1.26 | 2 | 0 | 3130 | 0.473 | 3130 | 0.473 | 1.26 | 2 | 0
LFAllSpcSCEWRfNewIOU | Com-Iltg-dWatt-LF_OSspc | SCE | WRf | New | IOU | 3.13 | 0.000473 | 0 | 4.4275 | 0.00059112 | 0 | 3.13 | 0.000473 | 0 | 4.4275 | 0.00059112 | 0 |  | LF | AllSpc | 3130 | 0.473 | 3130 | 0.473 | 1.41 | 1.25 | 0 | 3130 | 0.473 | 3130 | 0.473 | 1.41 | 1.25 | 0
LFAllSpcSDGAsmExCZ06 | Com-Iltg-dWatt-LF_OSspc | SDG | Asm | Ex | CZ06 | 2.2209 | 0.00043191 | 0 | 2.45 | 0.00053191 | -0.012409 | 2.2209 | 0.00043191 | 0 | 2.45 | 0.00053191 | -0.012409 |  | LF | AllSpc | 2220 | 0.432 | 2220 | 0.432 | 1.1 | 1.23 | -0.0055874 | 2220 | 0.432 | 2220 | 0.432 | 1.1 | 1.23 | -0.00559
LFAllSpcSDGAsmExCZ07 | Com-Iltg-dWatt-LF_OSspc | SDG | Asm | Ex | CZ07 | 2.2209 | 0.00043191 | 0 | 2.4509 | 0.00053191 | -0.0115 | 2.2209 | 0.00043191 | 0 | 2.4509 | 0.00053191 | -0.0115 |  | LF | AllSpc | 2220 | 0.432 | 2220 | 0.432 | 1.1 | 1.23 | -0.005178 | 2220 | 0.432 | 2220 | 0.432 | 1.1 | 1.23 | -0.00518
LFAllSpcSDGAsmExCZ08 | Com-Iltg-dWatt-LF_OSspc | SDG | Asm | Ex | CZ08 | 2.2209 | 0.00043191 | 0 | 2.47 | 0.00051691 | -0.0105 | 2.2209 | 0.00043191 | 0 | 2.47 | 0.00051691 | -0.0105 |  | LF | AllSpc | 2220 | 0.432 | 2220 | 0.432 | 1.11 | 1.2 | -0.0047277 | 2220 | 0.432 | 2220 | 0.432 | 1.11 | 1.2 | -0.00473
LFAllSpcSDGAsmExCZ10 | Com-Iltg-dWatt-LF_OSspc | SDG | Asm | Ex | CZ10 | 2.2209 | 0.00043191 | 0 | 2.4409 | 0.00052281 | -0.0134 | 2.2209 | 0.00043191 | 0 | 2.4409 | 0.00052281 | -0.0134 |  | LF | AllSpc | 2220 | 0.432 | 2220 | 0.432 | 1.1 | 1.21 | -0.0060335 | 2220 | 0.432 | 2220 | 0.432 | 1.1 | 1.21 | -0.00603
LFAllSpcSDGAsmExCZ14 | Com-Iltg-dWatt-LF_OSspc | SDG | Asm | Ex | CZ14 | 2.2209 | 0.00043191 | 0 | 2.3709 | 0.00048891 | -0.0215 | 2.2209 | 0.00043191 | 0 | 2.3709 | 0.00048891 | -0.0215 |  | LF | AllSpc | 2220 | 0.432 | 2220 | 0.432 | 1.07 | 1.13 | -0.0096806 | 2220 | 0.432 | 2220 | 0.432 | 1.07 | 1.13 | -0.00968
LFAllSpcSDGAsmExCZ15 | Com-Iltg-dWatt-LF_OSspc | SDG | Asm | Ex | CZ15 | 2.2209 | 0.00043191 | 0 | 2.6909 | 0.00051691 | -0.0059319 | 2.2209 | 0.00043191 | 0 | 2.6909 | 0.00051691 | -0.0059319 |  | LF | AllSpc | 2220 | 0.432 | 2220 | 0.432 | 1.21 | 1.2 | -0.0026709 | 2220 | 0.432 | 2220 | 0.432 | 1.21 | 1.2 | -0.00267
LFAllSpcSDGAsmExIOU | Com-Iltg-dWatt-LF_OSspc | SDG | Asm | Ex | IOU | 2.2209 | 0.00043191 | 0 | 2.4482 | 0.00052839 | -0.012164 | 2.2209 | 0.00043191 | 0 | 2.4482 | 0.00052839 | -0.012164 |  | LF | AllSpc | 2220 | 0.432 | 2220 | 0.432 | 1.1 | 1.22 | -0.0054769 | 2220 | 0.432 | 2220 | 0.432 | 1.1 | 1.22 | -0.00548
LFAllSpcSDGAsmNewCZ06 | Com-Iltg-dWatt-LF_OSspc | SDG | Asm | New | CZ06 | 2.23 | 0.000431 | 0 | 2.42 | 0.000528 | -0.0152 | 2.23 | 0.000431 | 0 | 2.42 | 0.000528 | -0.0152 |  | LF | AllSpc | 2230 | 0.431 | 2230 | 0.431 | 1.09 | 1.23 | -0.0068161 | 2230 | 0.431 | 2230 | 0.431 | 1.09 | 1.23 | -0.00682
LFAllSpcSDGAsmNewCZ07 | Com-Iltg-dWatt-LF_OSspc | SDG | Asm | New | CZ07 | 2.23 | 0.000431 | 0 | 2.44 | 0.000528 | -0.0139 | 2.23 | 0.000431 | 0 | 2.44 | 0.000528 | -0.0139 |  | LF | AllSpc | 2230 | 0.431 | 2230 | 0.431 | 1.09 | 1.23 | -0.0062332 | 2230 | 0.431 | 2230 | 0.431 | 1.09 | 1.23 | -0.00623
LFAllSpcSDGAsmNewCZ08 | Com-Iltg-dWatt-LF_OSspc | SDG | Asm | New | CZ08 | 2.23 | 0.000431 | 0 | 2.45 | 0.000521 | -0.0125 | 2.23 | 0.000431 | 0 | 2.45 | 0.000521 | -0.0125 |  | LF | AllSpc | 2230 | 0.431 | 2230 | 0.431 | 1.1 | 1.21 | -0.0056054 | 2230 | 0.431 | 2230 | 0.431 | 1.1 | 1.21 | -0.00561
LFAllSpcSDGAsmNewCZ10 | Com-Iltg-dWatt-LF_OSspc | SDG | Asm | New | CZ10 | 2.23 | 0.000431 | 0 | 2.43 | 0.000534 | -0.0144 | 2.23 | 0.000431 | 0 | 2.43 | 0.000534 | -0.0144 |  | LF | AllSpc | 2230 | 0.431 | 2230 | 0.431 | 1.09 | 1.24 | -0.0064574 | 2230 | 0.431 | 2230 | 0.431 | 1.09 | 1.24 | -0.00646
LFAllSpcSDGAsmNewCZ14 | Com-Iltg-dWatt-LF_OSspc | SDG | Asm | New | CZ14 | 2.23 | 0.000431 | 0 | 2.38 | 0.000521 | -0.0229 | 2.23 | 0.000431 | 0 | 2.38 | 0.000521 | -0.0229 |  | LF | AllSpc | 2230 | 0.431 | 2230 | 0.431 | 1.07 | 1.21 | -0.010269 | 2230 | 0.431 | 2230 | 0.431 | 1.07 | 1.21 | -0.0103
LFAllSpcSDGAsmNewCZ15 | Com-Iltg-dWatt-LF_OSspc | SDG | Asm | New | CZ15 | 2.23 | 0.000431 | 0 | 2.6 | 0.000532 | -0.00666 | 2.23 | 0.000431 | 0 | 2.6 | 0.000532 | -0.00666 |  | LF | AllSpc | 2230 | 0.431 | 2230 | 0.431 | 1.17 | 1.23 | -0.0029865 | 2230 | 0.431 | 2230 | 0.431 | 1.17 | 1.23 | -0.00299
LFAllSpcSDGAsmNewIOU | Com-Iltg-dWatt-LF_OSspc | SDG | Asm | New | IOU | 2.23 | 0.000431 | 0 | 2.4364 | 0.00052963 | -0.014129 | 2.23 | 0.000431 | 0 | 2.4364 | 0.00052963 | -0.014129 |  | LF | AllSpc | 2230 | 0.431 | 2230 | 0.431 | 1.09 | 1.23 | -0.006336 | 2230 | 0.431 | 2230 | 0.431 | 1.09 | 1.23 | -0.00634
LFAllSpcSDGComExCZ06 | Com-Iltg-dWatt-LF_OSspc | SDG | Com | Ex | CZ06 | 2.8844 | 0.00060281 | 0 | 3.17 | 0.00074259 | -0.013231 | 2.8844 | 0.00060281 | 0 | 3.17 | 0.00074259 | -0.013231 |  | LF | AllSpc | 2880 | 0.603 | 2880 | 0.603 | 1.1 | 1.23 | -0.0045869 | 2880 | 0.603 | 2880 | 0.603 | 1.1 | 1.23 | -0.00459
LFAllSpcSDGComExCZ07 | Com-Iltg-dWatt-LF_OSspc | SDG | Com | Ex | CZ07 | 2.7471 | 0.0006007 | 0 | 3.0476 | 0.00073618 | -0.0092887 | 2.7471 | 0.0006007 | 0 | 3.0476 | 0.00073618 | -0.0092887 |  | LF | AllSpc | 2750 | 0.601 | 2750 | 0.601 | 1.11 | 1.23 | -0.0033812 | 2750 | 0.601 | 2750 | 0.601 | 1.11 | 1.23 | -0.00338
LFAllSpcSDGComExCZ08 | Com-Iltg-dWatt-LF_OSspc | SDG | Com | Ex | CZ08 | 3.0648 | 0.00067766 | 0 | 3.4471 | 0.00083848 | -0.010274 | 3.0648 | 0.00067766 | 0 | 3.4471 | 0.00083848 | -0.010274 |  | LF | AllSpc | 3060 | 0.678 | 3060 | 0.678 | 1.12 | 1.24 | -0.0033524 | 3060 | 0.678 | 3060 | 0.678 | 1.12 | 1.24 | -0.00335
LFAllSpcSDGComExCZ10 | Com-Iltg-dWatt-LF_OSspc | SDG | Com | Ex | CZ10 | 2.8672 | 0.00063255 | 0 | 3.1732 | 0.00079079 | -0.011421 | 2.8672 | 0.00063255 | 0 | 3.1732 | 0.00079079 | -0.011421 |  | LF | AllSpc | 2870 | 0.633 | 2870 | 0.633 | 1.11 | 1.25 | -0.0039836 | 2870 | 0.633 | 2870 | 0.633 | 1.11 | 1.25 | -0.00398
LFAllSpcSDGComExCZ14 | Com-Iltg-dWatt-LF_OSspc | SDG | Com | Ex | CZ14 | 2.4177 | 0.00055368 | 0 | 2.6276 | 0.0006937 | -0.013974 | 2.4177 | 0.00055368 | 0 | 2.6276 | 0.0006937 | -0.013974 |  | LF | AllSpc | 2420 | 0.554 | 2420 | 0.554 | 1.09 | 1.25 | -0.0057799 | 2420 | 0.554 | 2420 | 0.554 | 1.09 | 1.25 | -0.00578
LFAllSpcSDGComExCZ15 | Com-Iltg-dWatt-LF_OSspc | SDG | Com | Ex | CZ15 | 2.1849 | 0.00044328 | 0 | 2.5679 | 0.00055957 | -0.0034675 | 2.1849 | 0.00044328 | 0 | 2.5679 | 0.00055957 | -0.0034675 |  | LF | AllSpc | 2180 | 0.443 | 2180 | 0.443 | 1.18 | 1.26 | -0.001587 | 2180 | 0.443 | 2180 | 0.443 | 1.18 | 1.26 | -0.00159
LFAllSpcSDGComExIOU | Com-Iltg-dWatt-LF_OSspc | SDG | Com | Ex | IOU | 2.7857 | 0.00060981 | 0 | 3.089 | 0.00075139 | -0.0099431 | 2.7857 | 0.00060981 | 0 | 3.089 | 0.00075139 | -0.0099431 |  | LF | AllSpc | 2790 | 0.61 | 2790 | 0.61 | 1.11 | 1.23 | -0.0035694 | 2790 | 0.61 | 2790 | 0.61 | 1.11 | 1.23 | -0.00357
LFAllSpcSDGComNewCZ06 | Com-Iltg-dWatt-LF_OSspc | SDG | Com | New | CZ06 | 2.9009 | 0.00058546 | 0 | 3.1548 | 0.00071973 | -0.012703 | 2.9009 | 0.00058546 | 0 | 3.1548 | 0.00071973 | -0.012703 |  | LF | AllSpc | 2900 | 0.585 | 2900 | 0.585 | 1.09 | 1.23 | -0.0043789 | 2900 | 0.585 | 2900 | 0.585 | 1.09 | 1.23 | -0.00438
LFAllSpcSDGComNewCZ07 | Com-Iltg-dWatt-LF_OSspc | SDG | Com | New | CZ07 | 2.7534 | 0.00058748 | 0 | 3.001 | 0.00071438 | -0.0084941 | 2.7534 | 0.00058748 | 0 | 3.001 | 0.00071438 | -0.0084941 |  | LF | AllSpc | 2750 | 0.587 | 2750 | 0.587 | 1.09 | 1.22 | -0.003085 | 2750 | 0.587 | 2750 | 0.587 | 1.09 | 1.22 | -0.00309
LFAllSpcSDGComNewCZ08 | Com-Iltg-dWatt-LF_OSspc | SDG | Com | New | CZ08 | 3.1612 | 0.00069146 | 0 | 3.5154 | 0.00086626 | -0.010149 | 3.1612 | 0.00069146 | 0 | 3.5154 | 0.00086626 | -0.010149 |  | LF | AllSpc | 3160 | 0.691 | 3160 | 0.691 | 1.11 | 1.25 | -0.0032105 | 3160 | 0.691 | 3160 | 0.691 | 1.11 | 1.25 | -0.00321
LFAllSpcSDGComNewCZ10 | Com-Iltg-dWatt-LF_OSspc | SDG | Com | New | CZ10 | 2.9361 | 0.00063492 | 0 | 3.2401 | 0.00081915 | -0.011122 | 2.9361 | 0.00063492 | 0 | 3.2401 | 0.00081915 | -0.011122 |  | LF | AllSpc | 2940 | 0.635 | 2940 | 0.635 | 1.1 | 1.29 | -0.0037881 | 2940 | 0.635 | 2940 | 0.635 | 1.1 | 1.29 | -0.00379
LFAllSpcSDGComNewCZ14 | Com-Iltg-dWatt-LF_OSspc | SDG | Com | New | CZ14 | 2.4442 | 0.00053413 | 0 | 2.6586 | 0.00069282 | -0.013893 | 2.4442 | 0.00053413 | 0 | 2.6586 | 0.00069282 | -0.013893 |  | LF | AllSpc | 2440 | 0.534 | 2440 | 0.534 | 1.09 | 1.3 | -0.0056841 | 2440 | 0.534 | 2440 | 0.534 | 1.09 | 1.3 | -0.00568
LFAllSpcSDGComNewCZ15 | Com-Iltg-dWatt-LF_OSspc | SDG | Com | New | CZ15 | 2.1197 | 0.00040007 | 0 | 2.4796 | 0.00052626 | -0.0032345 | 2.1197 | 0.00040007 | 0 | 2.4796 | 0.00052626 | -0.0032345 |  | LF | AllSpc | 2120 | 0.4 | 2120 | 0.4 | 1.17 | 1.32 | -0.0015259 | 2120 | 0.4 | 2120 | 0.4 | 1.17 | 1.32 | -0.00153
LFAllSpcSDGComNewIOU | Com-Iltg-dWatt-LF_OSspc | SDG | Com | New | IOU | 2.8085 | 0.00060051 | 0 | 3.0725 | 0.00074243 | -0.0093014 | 2.8085 | 0.00060051 | 0 | 3.0725 | 0.00074243 | -0.0093014 |  | LF | AllSpc | 2810 | 0.601 | 2810 | 0.601 | 1.09 | 1.24 | -0.0033119 | 2810 | 0.601 | 2810 | 0.601 | 1.09 | 1.24 | -0.00331
LFAllSpcSDGECCExCZ06 | Com-Iltg-dWatt-LF_OSspc | SDG | ECC | Ex | CZ06 | 2.1306 | 0.00066094 | 0 | 2.4106 | 0.00083994 | -0.0123 | 2.1306 | 0.00066094 | 0 | 2.4106 | 0.00083994 | -0.0123 |  | LF | AllSpc | 2130 | 0.661 | 2130 | 0.661 | 1.13 | 1.27 | -0.0057729 | 2130 | 0.661 | 2130 | 0.661 | 1.13 | 1.27 | -0.00577
LFAllSpcSDGECCExCZ07 | Com-Iltg-dWatt-LF_OSspc | SDG | ECC | Ex | CZ07 | 2.1306 | 0.00066094 | 0 | 2.43 | 0.00083694 | -0.0103 | 2.1306 | 0.00066094 | 0 | 2.43 | 0.00083694 | -0.0103 |  | LF | AllSpc | 2130 | 0.661 | 2130 | 0.661 | 1.14 | 1.27 | -0.0048343 | 2130 | 0.661 | 2130 | 0.661 | 1.14 | 1.27 | -0.00483
LFAllSpcSDGECCExCZ08 | Com-Iltg-dWatt-LF_OSspc | SDG | ECC | Ex | CZ08 | 2.1306 | 0.00066094 | 0 | 2.4406 | 0.00083594 | -0.0112 | 2.1306 | 0.00066094 | 0 | 2.4406 | 0.00083594 | -0.0112 |  | LF | AllSpc | 2130 | 0.661 | 2130 | 0.661 | 1.15 | 1.26 | -0.0052567 | 2130 | 0.661 | 2130 | 0.661 | 1.15 | 1.26 | -0.00526
LFAllSpcSDGECCExCZ10 | Com-Iltg-dWatt-LF_OSspc | SDG | ECC | Ex | CZ10 | 2.1306 | 0.00066094 | 0 | 2.43 | 0.00085187 | -0.0133 | 2.1306 | 0.00066094 | 0 | 2.43 | 0.00085187 | -0.0133 |  | LF | AllSpc | 2130 | 0.661 | 2130 | 0.661 | 1.14 | 1.29 | -0.0062423 | 2130 | 0.661 | 2130 | 0.661 | 1.14 | 1.29 | -0.00624
LFAllSpcSDGECCExCZ14 | Com-Iltg-dWatt-LF_OSspc | SDG | ECC | Ex | CZ14 | 2.1306 | 0.00066094 | 0 | 2.38 | 0.00084494 | -0.02 | 2.1306 | 0.00066094 | 0 | 2.38 | 0.00084494 | -0.02 |  | LF | AllSpc | 2130 | 0.661 | 2130 | 0.661 | 1.12 | 1.28 | -0.0093869 | 2130 | 0.661 | 2130 | 0.661 | 1.12 | 1.28 | -0.00939
LFAllSpcSDGECCExIOU | Com-Iltg-dWatt-LF_OSspc | SDG | ECC | Ex | IOU | 2.1306 | 0.00066094 | 0 | 2.4297 | 0.0008405 | -0.011074 | 2.1306 | 0.00066094 | 0 | 2.4297 | 0.0008405 | -0.011074 |  | LF | AllSpc | 2130 | 0.661 | 2130 | 0.661 | 1.14 | 1.27 | -0.0051974 | 2130 | 0.661 | 2130 | 0.661 | 1.14 | 1.27 | -0.0052
LFAllSpcSDGECCNewCZ06 | Com-Iltg-dWatt-LF_OSspc | SDG | ECC | New | CZ06 | 2.14 | 0.00066 | 0 | 2.43 | 0.000833 | -0.0116 | 2.14 | 0.00066 | 0 | 2.43 | 0.000833 | -0.0116 |  | LF | AllSpc | 2140 | 0.66 | 2140 | 0.66 | 1.14 | 1.26 | -0.0054206 | 2140 | 0.66 | 2140 | 0.66 | 1.14 | 1.26 | -0.00542
LFAllSpcSDGECCNewCZ07 | Com-Iltg-dWatt-LF_OSspc | SDG | ECC | New | CZ07 | 2.14 | 0.00066 | 0 | 2.41 | 0.000835 | -0.00944 | 2.14 | 0.00066 | 0 | 2.41 | 0.000835 | -0.00944 |  | LF | AllSpc | 2140 | 0.66 | 2140 | 0.66 | 1.13 | 1.27 | -0.0044112 | 2140 | 0.66 | 2140 | 0.66 | 1.13 | 1.27 | -0.00441
LFAllSpcSDGECCNewCZ08 | Com-Iltg-dWatt-LF_OSspc | SDG | ECC | New | CZ08 | 2.14 | 0.00066 | 0 | 2.45 | 0.000836 | -0.00957 | 2.14 | 0.00066 | 0 | 2.45 | 0.000836 | -0.00957 |  | LF | AllSpc | 2140 | 0.66 | 2140 | 0.66 | 1.14 | 1.27 | -0.004472 | 2140 | 0.66 | 2140 | 0.66 | 1.14 | 1.27 | -0.00447
LFAllSpcSDGECCNewCZ10 | Com-Iltg-dWatt-LF_OSspc | SDG | ECC | New | CZ10 | 2.14 | 0.00066 | 0 | 2.47 | 0.000865 | -0.0112 | 2.14 | 0.00066 | 0 | 2.47 | 0.000865 | -0.0112 |  | LF | AllSpc | 2140 | 0.66 | 2140 | 0.66 | 1.15 | 1.31 | -0.0052336 | 2140 | 0.66 | 2140 | 0.66 | 1.15 | 1.31 | -0.00523
LFAllSpcSDGECCNewCZ14 | Com-Iltg-dWatt-LF_OSspc | SDG | ECC | New | CZ14 | 2.14 | 0.00066 | 0 | 2.44 | 0.000839 | -0.0185 | 2.14 | 0.00066 | 0 | 2.44 | 0.000839 | -0.0185 |  | LF | AllSpc | 2140 | 0.66 | 2140 | 0.66 | 1.14 | 1.27 | -0.0086449 | 2140 | 0.66 | 2140 | 0.66 | 1.14 | 1.27 | -0.00864
LFAllSpcSDGECCNewCZ15 | Com-Iltg-dWatt-LF_OSspc | SDG | ECC | New | CZ15 | 2.14 | 0.00066 | 0 | 2.71 | 0.00091 | -0.0041 | 2.14 | 0.00066 | 0 | 2.71 | 0.00091 | -0.0041 |  | LF | AllSpc | 2140 | 0.66 | 2140 | 0.66 | 1.27 | 1.38 | -0.0019159 | 2140 | 0.66 | 2140 | 0.66 | 1.27 | 1.38 | -0.00192
LFAllSpcSDGECCNewIOU | Com-Iltg-dWatt-LF_OSspc | SDG | ECC | New | IOU | 2.14 | 0.00066 | 0 | 2.4247 | 0.00084207 | -0.0099131 | 2.14 | 0.00066 | 0 | 2.4247 | 0.00084207 | -0.0099131 |  | LF | AllSpc | 2140 | 0.66 | 2140 | 0.66 | 1.13 | 1.28 | -0.0046323 | 2140 | 0.66 | 2140 | 0.66 | 1.13 | 1.28 | -0.00463
LFAllSpcSDGEPrExCZ06 | Com-Iltg-dWatt-LF_OSspc | SDG | EPr | Ex | CZ06 | 1.86 | 0.00053217 | 0 | 2.12 | 0.00068222 | -0.0082699 | 1.86 | 0.00053217 | 0 | 2.12 | 0.00068222 | -0.0082699 |  | LF | AllSpc | 1860 | 0.532 | 1860 | 0.532 | 1.14 | 1.28 | -0.0044462 | 1860 | 0.532 | 1860 | 0.532 | 1.14 | 1.28 | -0.00445
LFAllSpcSDGEPrExCZ07 | Com-Iltg-dWatt-LF_OSspc | SDG | EPr | Ex | CZ07 | 1.86 | 0.00053225 | 0 | 2.12 | 0.00068928 | -0.0074 | 1.86 | 0.00053225 | 0 | 2.12 | 0.00068928 | -0.0074 |  | LF | AllSpc | 1860 | 0.532 | 1860 | 0.532 | 1.14 | 1.3 | -0.0039785 | 1860 | 0.532 | 1860 | 0.532 | 1.14 | 1.3 | -0.00398
LFAllSpcSDGEPrExCZ08 | Com-Iltg-dWatt-LF_OSspc | SDG | EPr | Ex | CZ08 | 1.86 | 0.00053225 | 0 | 2.14 | 0.00068932 | -0.00686 | 1.86 | 0.00053225 | 0 | 2.14 | 0.00068932 | -0.00686 |  | LF | AllSpc | 1860 | 0.532 | 1860 | 0.532 | 1.15 | 1.3 | -0.0036882 | 1860 | 0.532 | 1860 | 0.532 | 1.15 | 1.3 | -0.00369
LFAllSpcSDGEPrExCZ10 | Com-Iltg-dWatt-LF_OSspc | SDG | EPr | Ex | CZ10 | 1.86 | 0.00053225 | 0 | 2.12 | 0.00068628 | -0.00878 | 1.86 | 0.00053225 | 0 | 2.12 | 0.00068628 | -0.00878 |  | LF | AllSpc | 1860 | 0.532 | 1860 | 0.532 | 1.14 | 1.29 | -0.0047204 | 1860 | 0.532 | 1860 | 0.532 | 1.14 | 1.29 | -0.00472
LFAllSpcSDGEPrExCZ14 | Com-Iltg-dWatt-LF_OSspc | SDG | EPr | Ex | CZ14 | 1.86 | 0.00053225 | 0 | 2.04 | 0.00068632 | -0.0149 | 1.86 | 0.00053225 | 0 | 2.04 | 0.00068632 | -0.0149 |  | LF | AllSpc | 1860 | 0.532 | 1860 | 0.532 | 1.1 | 1.29 | -0.0080108 | 1860 | 0.532 | 1860 | 0.532 | 1.1 | 1.29 | -0.00801
LFAllSpcSDGEPrExCZ15 | Com-Iltg-dWatt-LF_OSspc | SDG | EPr | Ex | CZ15 | 1.86 | 0.00053224 | 0 | 2.28 | 0.00068727 | -0.0036 | 1.86 | 0.00053224 | 0 | 2.28 | 0.00068727 | -0.0036 |  | LF | AllSpc | 1860 | 0.532 | 1860 | 0.532 | 1.23 | 1.29 | -0.0019355 | 1860 | 0.532 | 1860 | 0.532 | 1.23 | 1.29 | -0.00194
LFAllSpcSDGEPrExIOU | Com-Iltg-dWatt-LF_OSspc | SDG | EPr | Ex | IOU | 1.86 | 0.00053224 | 0 | 2.1208 | 0.00068793 | -0.0079198 | 1.86 | 0.00053224 | 0 | 2.1208 | 0.00068793 | -0.0079198 |  | LF | AllSpc | 1860 | 0.532 | 1860 | 0.532 | 1.14 | 1.29 | -0.004258 | 1860 | 0.532 | 1860 | 0.532 | 1.14 | 1.29 | -0.00426
LFAllSpcSDGEPrNewCZ06 | Com-Iltg-dWatt-LF_OSspc | SDG | EPr | New | CZ06 | 1.86 | 0.000539 | 0 | 1.93 | 0.000511 | -0.00893 | 1.86 | 0.000539 | 0 | 1.93 | 0.000511 | -0.00893 |  | LF | AllSpc | 1860 | 0.539 | 1860 | 0.539 | 1.04 | 0.948 | -0.0048011 | 1860 | 0.539 | 1860 | 0.539 | 1.04 | 0.948 | -0.0048
LFAllSpcSDGEPrNewCZ07 | Com-Iltg-dWatt-LF_OSspc | SDG | EPr | New | CZ07 | 1.86 | 0.000539 | 0 | 2.04 | 0.00072 | -0.00956 | 1.86 | 0.000539 | 0 | 2.04 | 0.00072 | -0.00956 |  | LF | AllSpc | 1860 | 0.539 | 1860 | 0.539 | 1.1 | 1.34 | -0.0051398 | 1860 | 0.539 | 1860 | 0.539 | 1.1 | 1.34 | -0.00514
LFAllSpcSDGEPrNewCZ08 | Com-Iltg-dWatt-LF_OSspc | SDG | EPr | New | CZ08 | 1.86 | 0.000539 | 0 | 2.1 | 0.000743 | -0.009 | 1.86 | 0.000539 | 0 | 2.1 | 0.000743 | -0.009 |  | LF | AllSpc | 1860 | 0.539 | 1860 | 0.539 | 1.13 | 1.38 | -0.0048387 | 1860 | 0.539 | 1860 | 0.539 | 1.13 | 1.38 | -0.00484
LFAllSpcSDGEPrNewCZ10 | Com-Iltg-dWatt-LF_OSspc | SDG | EPr | New | CZ10 | 1.86 | 0.000539 | 0 | 2.11 | 0.000782 | -0.0111 | 1.86 | 0.000539 | 0 | 2.11 | 0.000782 | -0.0111 |  | LF | AllSpc | 1860 | 0.539 | 1860 | 0.539 | 1.13 | 1.45 | -0.0059677 | 1860 | 0.539 | 1860 | 0.539 | 1.13 | 1.45 | -0.00597
LFAllSpcSDGEPrNewCZ14 | Com-Iltg-dWatt-LF_OSspc | SDG | EPr | New | CZ14 | 1.86 | 0.000539 | 0 | 2.07 | 0.000767 | -0.0181 | 1.86 | 0.000539 | 0 | 2.07 | 0.000767 | -0.0181 |  | LF | AllSpc | 1860 | 0.539 | 1860 | 0.539 | 1.11 | 1.42 | -0.0097312 | 1860 | 0.539 | 1860 | 0.539 | 1.11 | 1.42 | -0.00973
LFAllSpcSDGEPrNewCZ15 | Com-Iltg-dWatt-LF_OSspc | SDG | EPr | New | CZ15 | 1.86 | 0.000539 | 0 | 2.29 | 0.000782 | -0.00477 | 1.86 | 0.000539 | 0 | 2.29 | 0.000782 | -0.00477 |  | LF | AllSpc | 1860 | 0.539 | 1860 | 0.539 | 1.23 | 1.45 | -0.0025645 | 1860 | 0.539 | 1860 | 0.539 | 1.23 | 1.45 | -0.00256
LFAllSpcSDGEPrNewIOU | Com-Iltg-dWatt-LF_OSspc | SDG | EPr | New | IOU | 1.86 | 0.000539 | 0 | 2.0616 | 0.00073181 | -0.010065 | 1.86 | 0.000539 | 0 | 2.0616 | 0.00073181 | -0.010065 |  | LF | AllSpc | 1860 | 0.539 | 1860 | 0.539 | 1.11 | 1.36 | -0.0054116 | 1860 | 0.539 | 1860 | 0.539 | 1.11 | 1.36 | -0.00541
LFAllSpcSDGERCExCZ06 | Com-Iltg-dWatt-LF_OSspc | SDG | ERC | Ex | CZ06 | 2.19 | 0.00060129 | 0 | 2.43 | 0.00075536 | -0.0134 | 2.19 | 0.00060129 | 0 | 2.43 | 0.00075536 | -0.0134 |  | LF | AllSpc | 2190 | 0.601 | 2190 | 0.601 | 1.11 | 1.26 | -0.0061187 | 2190 | 0.601 | 2190 | 0.601 | 1.11 | 1.26 | -0.00612
LFAllSpcSDGERCExCZ07 | Com-Iltg-dWatt-LF_OSspc | SDG | ERC | Ex | CZ07 | 2.19 | 0.00060128 | 0 | 2.47 | 0.00076839 | -0.0111 | 2.19 | 0.00060128 | 0 | 2.47 | 0.00076839 | -0.0111 |  | LF | AllSpc | 2190 | 0.601 | 2190 | 0.601 | 1.13 | 1.28 | -0.0050685 | 2190 | 0.601 | 2190 | 0.601 | 1.13 | 1.28 | -0.00507
LFAllSpcSDGERCExCZ08 | Com-Iltg-dWatt-LF_OSspc | SDG | ERC | Ex | CZ08 | 2.19 | 0.00060128 | 0 | 2.43 | 0.00076335 | -0.0117 | 2.19 | 0.00060128 | 0 | 2.43 | 0.00076335 | -0.0117 |  | LF | AllSpc | 2190 | 0.601 | 2190 | 0.601 | 1.11 | 1.27 | -0.0053425 | 2190 | 0.601 | 2190 | 0.601 | 1.11 | 1.27 | -0.00534
LFAllSpcSDGERCExCZ10 | Com-Iltg-dWatt-LF_OSspc | SDG | ERC | Ex | CZ10 | 2.19 | 0.00060128 | 0 | 2.43 | 0.00076539 | -0.0139 | 2.19 | 0.00060128 | 0 | 2.43 | 0.00076539 | -0.0139 |  | LF | AllSpc | 2190 | 0.601 | 2190 | 0.601 | 1.11 | 1.27 | -0.006347 | 2190 | 0.601 | 2190 | 0.601 | 1.11 | 1.27 | -0.00635
LFAllSpcSDGERCExCZ14 | Com-Iltg-dWatt-LF_OSspc | SDG | ERC | Ex | CZ14 | 2.19 | 0.00060129 | 0 | 2.39 | 0.00077036 | -0.0183 | 2.19 | 0.00060129 | 0 | 2.39 | 0.00077036 | -0.0183 |  | LF | AllSpc | 2190 | 0.601 | 2190 | 0.601 | 1.09 | 1.28 | -0.0083562 | 2190 | 0.601 | 2190 | 0.601 | 1.09 | 1.28 | -0.00836
LFAllSpcSDGERCExCZ15 | Com-Iltg-dWatt-LF_OSspc | SDG | ERC | Ex | CZ15 | 2.19 | 0.00060127 | 0 | 2.6 | 0.00078438 | -0.00645 | 2.19 | 0.00060127 | 0 | 2.6 | 0.00078438 | -0.00645 |  | LF | AllSpc | 2190 | 0.601 | 2190 | 0.601 | 1.19 | 1.3 | -0.0029452 | 2190 | 0.601 | 2190 | 0.601 | 1.19 | 1.3 | -0.00295
LFAllSpcSDGERCExIOU | Com-Iltg-dWatt-LF_OSspc | SDG | ERC | Ex | IOU | 2.19 | 0.00060128 | 0 | 2.4524 | 0.00076656 | -0.01221 | 2.19 | 0.00060128 | 0 | 2.4524 | 0.00076656 | -0.01221 |  | LF | AllSpc | 2190 | 0.601 | 2190 | 0.601 | 1.12 | 1.27 | -0.0055754 | 2190 | 0.601 | 2190 | 0.601 | 1.12 | 1.27 | -0.00558
LFAllSpcSDGERCNewCZ06 | Com-Iltg-dWatt-LF_OSspc | SDG | ERC | New | CZ06 | 2.19 | 0.000609 | 0 | 2.53 | 0.000788 | -0.014 | 2.19 | 0.000609 | 0 | 2.53 | 0.000788 | -0.014 |  | LF | AllSpc | 2190 | 0.609 | 2190 | 0.609 | 1.16 | 1.29 | -0.0063927 | 2190 | 0.609 | 2190 | 0.609 | 1.16 | 1.29 | -0.00639
LFAllSpcSDGERCNewCZ07 | Com-Iltg-dWatt-LF_OSspc | SDG | ERC | New | CZ07 | 2.19 | 0.000609 | 0 | 2.53 | 0.000793 | -0.011 | 2.19 | 0.000609 | 0 | 2.53 | 0.000793 | -0.011 |  | LF | AllSpc | 2190 | 0.609 | 2190 | 0.609 | 1.16 | 1.3 | -0.0050228 | 2190 | 0.609 | 2190 | 0.609 | 1.16 | 1.3 | -0.00502
LFAllSpcSDGERCNewCZ08 | Com-Iltg-dWatt-LF_OSspc | SDG | ERC | New | CZ08 | 2.19 | 0.000609 | 0 | 2.57 | 0.000806 | -0.0118 | 2.19 | 0.000609 | 0 | 2.57 | 0.000806 | -0.0118 |  | LF | AllSpc | 2190 | 0.609 | 2190 | 0.609 | 1.17 | 1.32 | -0.0053881 | 2190 | 0.609 | 2190 | 0.609 | 1.17 | 1.32 | -0.00539
LFAllSpcSDGERCNewCZ10 | Com-Iltg-dWatt-LF_OSspc | SDG | ERC | New | CZ10 | 2.19 | 0.000609 | 0 | 2.58 | 0.000843 | -0.014 | 2.19 | 0.000609 | 0 | 2.58 | 0.000843 | -0.014 |  | LF | AllSpc | 2190 | 0.609 | 2190 | 0.609 | 1.18 | 1.38 | -0.0063927 | 2190 | 0.609 | 2190 | 0.609 | 1.18 | 1.38 | -0.00639
LFAllSpcSDGERCNewCZ14 | Com-Iltg-dWatt-LF_OSspc | SDG | ERC | New | CZ14 | 2.19 | 0.000609 | 0 | 2.54 | 0.00083 | -0.0204 | 2.19 | 0.000609 | 0 | 2.54 | 0.00083 | -0.0204 |  | LF | AllSpc | 2190 | 0.609 | 2190 | 0.609 | 1.16 | 1.36 | -0.0093151 | 2190 | 0.609 | 2190 | 0.609 | 1.16 | 1.36 | -0.00932
LFAllSpcSDGERCNewCZ15 | Com-Iltg-dWatt-LF_OSspc | SDG | ERC | New | CZ15 | 2.19 | 0.000609 | 0 | 2.8 | 0.000845 | -0.00695 | 2.19 | 0.000609 | 0 | 2.8 | 0.000845 | -0.00695 |  | LF | AllSpc | 2190 | 0.609 | 2190 | 0.609 | 1.28 | 1.39 | -0.0031735 | 2190 | 0.609 | 2190 | 0.609 | 1.28 | 1.39 | -0.00317
LFAllSpcSDGERCNewIOU | Com-Iltg-dWatt-LF_OSspc | SDG | ERC | New | IOU | 2.19 | 0.000609 | 0 | 2.5492 | 0.00081021 | -0.012242 | 2.19 | 0.000609 | 0 | 2.5492 | 0.00081021 | -0.012242 |  | LF | AllSpc | 2190 | 0.609 | 2190 | 0.609 | 1.16 | 1.33 | -0.0055902 | 2190 | 0.609 | 2190 | 0.609 | 1.16 | 1.33 | -0.00559
LFAllSpcSDGESeExCZ06 | Com-Iltg-dWatt-LF_OSspc | SDG | ESe | Ex | CZ06 | 1.99 | 0.00061529 | 0 | 2.24 | 0.00078532 | -0.0112 | 1.99 | 0.00061529 | 0 | 2.24 | 0.00078532 | -0.0112 |  | LF | AllSpc | 1990 | 0.615 | 1990 | 0.615 | 1.13 | 1.28 | -0.0056281 | 1990 | 0.615 | 1990 | 0.615 | 1.13 | 1.28 | -0.00563
LFAllSpcSDGESeExCZ07 | Com-Iltg-dWatt-LF_OSspc | SDG | ESe | Ex | CZ07 | 1.99 | 0.00061528 | 0 | 2.23 | 0.00077236 | -0.00983 | 1.99 | 0.00061528 | 0 | 2.23 | 0.00077236 | -0.00983 |  | LF | AllSpc | 1990 | 0.615 | 1990 | 0.615 | 1.12 | 1.26 | -0.0049397 | 1990 | 0.615 | 1990 | 0.615 | 1.12 | 1.26 | -0.00494
LFAllSpcSDGESeExCZ08 | Com-Iltg-dWatt-LF_OSspc | SDG | ESe | Ex | CZ08 | 1.99 | 0.00061528 | 0 | 2.26 | 0.00078135 | -0.00963 | 1.99 | 0.00061528 | 0 | 2.26 | 0.00078135 | -0.00963 |  | LF | AllSpc | 1990 | 0.615 | 1990 | 0.615 | 1.14 | 1.27 | -0.0048392 | 1990 | 0.615 | 1990 | 0.615 | 1.14 | 1.27 | -0.00484
LFAllSpcSDGESeExCZ10 | Com-Iltg-dWatt-LF_OSspc | SDG | ESe | Ex | CZ10 | 1.99 | 0.00061528 | 0 | 2.25 | 0.00078032 | -0.0121 | 1.99 | 0.00061528 | 0 | 2.25 | 0.00078032 | -0.0121 |  | LF | AllSpc | 1990 | 0.615 | 1990 | 0.615 | 1.13 | 1.27 | -0.0060804 | 1990 | 0.615 | 1990 | 0.615 | 1.13 | 1.27 | -0.00608
LFAllSpcSDGESeExCZ14 | Com-Iltg-dWatt-LF_OSspc | SDG | ESe | Ex | CZ14 | 1.99 | 0.00061529 | 0 | 2.17 | 0.00075732 | -0.0193 | 1.99 | 0.00061529 | 0 | 2.17 | 0.00075732 | -0.0193 |  | LF | AllSpc | 1990 | 0.615 | 1990 | 0.615 | 1.09 | 1.23 | -0.0096985 | 1990 | 0.615 | 1990 | 0.615 | 1.09 | 1.23 | -0.0097
LFAllSpcSDGESeExCZ15 | Com-Iltg-dWatt-LF_OSspc | SDG | ESe | Ex | CZ15 | 1.99 | 0.00061527 | 0 | 2.44 | 0.00077931 | -0.0053 | 1.99 | 0.00061527 | 0 | 2.44 | 0.00077931 | -0.0053 |  | LF | AllSpc | 1990 | 0.615 | 1990 | 0.615 | 1.23 | 1.27 | -0.0026633 | 1990 | 0.615 | 1990 | 0.615 | 1.23 | 1.27 | -0.00266
LFAllSpcSDGESeExIOU | Com-Iltg-dWatt-LF_OSspc | SDG | ESe | Ex | IOU | 1.99 | 0.00061528 | 0 | 2.2386 | 0.00077596 | -0.010699 | 1.99 | 0.00061528 | 0 | 2.2386 | 0.00077596 | -0.010699 |  | LF | AllSpc | 1990 | 0.615 | 1990 | 0.615 | 1.12 | 1.26 | -0.0053762 | 1990 | 0.615 | 1990 | 0.615 | 1.12 | 1.26 | -0.00538
LFAllSpcSDGESeNewCZ06 | Com-Iltg-dWatt-LF_OSspc | SDG | ESe | New | CZ06 | 1.99 | 0.000623 | 0 | 2.2 | 0.000823 | -0.0148 | 1.99 | 0.000623 | 0 | 2.2 | 0.000823 | -0.0148 |  | LF | AllSpc | 1990 | 0.623 | 1990 | 0.623 | 1.11 | 1.32 | -0.0074372 | 1990 | 0.623 | 1990 | 0.623 | 1.11 | 1.32 | -0.00744
LFAllSpcSDGESeNewCZ07 | Com-Iltg-dWatt-LF_OSspc | SDG | ESe | New | CZ07 | 1.99 | 0.000623 | 0 | 2.18 | 0.000806 | -0.0116 | 1.99 | 0.000623 | 0 | 2.18 | 0.000806 | -0.0116 |  | LF | AllSpc | 1990 | 0.623 | 1990 | 0.623 | 1.1 | 1.29 | -0.0058291 | 1990 | 0.623 | 1990 | 0.623 | 1.1 | 1.29 | -0.00583
LFAllSpcSDGESeNewCZ08 | Com-Iltg-dWatt-LF_OSspc | SDG | ESe | New | CZ08 | 1.99 | 0.000623 | 0 | 2.23 | 0.000836 | -0.0112 | 1.99 | 0.000623 | 0 | 2.23 | 0.000836 | -0.0112 |  | LF | AllSpc | 1990 | 0.623 | 1990 | 0.623 | 1.12 | 1.34 | -0.0056281 | 1990 | 0.623 | 1990 | 0.623 | 1.12 | 1.34 | -0.00563
LFAllSpcSDGESeNewCZ10 | Com-Iltg-dWatt-LF_OSspc | SDG | ESe | New | CZ10 | 1.99 | 0.000623 | 0 | 2.25 | 0.000878 | -0.0145 | 1.99 | 0.000623 | 0 | 2.25 | 0.000878 | -0.0145 |  | LF | AllSpc | 1990 | 0.623 | 1990 | 0.623 | 1.13 | 1.41 | -0.0072864 | 1990 | 0.623 | 1990 | 0.623 | 1.13 | 1.41 | -0.00729
LFAllSpcSDGESeNewCZ14 | Com-Iltg-dWatt-LF_OSspc | SDG | ESe | New | CZ14 | 1.99 | 0.000623 | 0 | 2.21 | 0.000859 | -0.0217 | 1.99 | 0.000623 | 0 | 2.21 | 0.000859 | -0.0217 |  | LF | AllSpc | 1990 | 0.623 | 1990 | 0.623 | 1.11 | 1.38 | -0.010905 | 1990 | 0.623 | 1990 | 0.623 | 1.11 | 1.38 | -0.0109
LFAllSpcSDGESeNewCZ15 | Com-Iltg-dWatt-LF_OSspc | SDG | ESe | New | CZ15 | 1.99 | 0.000623 | 0 | 2.49 | 0.000873 | -0.00624 | 1.99 | 0.000623 | 0 | 2.49 | 0.000873 | -0.00624 |  | LF | AllSpc | 1990 | 0.623 | 1990 | 0.623 | 1.25 | 1.4 | -0.0031357 | 1990 | 0.623 | 1990 | 0.623 | 1.25 | 1.4 | -0.00314
LFAllSpcSDGESeNewIOU | Com-Iltg-dWatt-LF_OSspc | SDG | ESe | New | IOU | 1.99 | 0.000623 | 0 | 2.2075 | 0.00083256 | -0.012757 | 1.99 | 0.000623 | 0 | 2.2075 | 0.00083256 | -0.012757 |  | LF | AllSpc | 1990 | 0.623 | 1990 | 0.623 | 1.11 | 1.34 | -0.0064106 | 1990 | 0.623 | 1990 | 0.623 | 1.11 | 1.34 | -0.00641
LFAllSpcSDGEUnExCZ06 | Com-Iltg-dWatt-LF_OSspc | SDG | EUn | Ex | CZ06 | 2.07 | 0.00059294 | 0 | 2.37 | 0.00074794 | -0.0088206 | 2.07 | 0.00059294 | 0 | 2.37 | 0.00074794 | -0.0088206 |  | LF | AllSpc | 2070 | 0.593 | 2070 | 0.593 | 1.14 | 1.26 | -0.0042612 | 2070 | 0.593 | 2070 | 0.593 | 1.14 | 1.26 | -0.00426
LFAllSpcSDGEUnExCZ07 | Com-Iltg-dWatt-LF_OSspc | SDG | EUn | Ex | CZ07 | 2.07 | 0.00059294 | 0 | 2.36 | 0.00074194 | -0.0076406 | 2.07 | 0.00059294 | 0 | 2.36 | 0.00074194 | -0.0076406 |  | LF | AllSpc | 2070 | 0.593 | 2070 | 0.593 | 1.14 | 1.25 | -0.0036911 | 2070 | 0.593 | 2070 | 0.593 | 1.14 | 1.25 | -0.00369
LFAllSpcSDGEUnExCZ08 | Com-Iltg-dWatt-LF_OSspc | SDG | EUn | Ex | CZ08 | 2.07 | 0.00059294 | 0 | 2.38 | 0.00074994 | -0.0084706 | 2.07 | 0.00059294 | 0 | 2.38 | 0.00074994 | -0.0084706 |  | LF | AllSpc | 2070 | 0.593 | 2070 | 0.593 | 1.15 | 1.26 | -0.0040921 | 2070 | 0.593 | 2070 | 0.593 | 1.15 | 1.26 | -0.00409
LFAllSpcSDGEUnExCZ10 | Com-Iltg-dWatt-LF_OSspc | SDG | EUn | Ex | CZ10 | 2.07 | 0.00059294 | 0 | 2.3706 | 0.00076294 | -0.0097906 | 2.07 | 0.00059294 | 0 | 2.3706 | 0.00076294 | -0.0097906 |  | LF | AllSpc | 2070 | 0.593 | 2070 | 0.593 | 1.15 | 1.29 | -0.0047298 | 2070 | 0.593 | 2070 | 0.593 | 1.15 | 1.29 | -0.00473
LFAllSpcSDGEUnExCZ14 | Com-Iltg-dWatt-LF_OSspc | SDG | EUn | Ex | CZ14 | 2.07 | 0.00059294 | 0 | 2.34 | 0.00075587 | -0.0132 | 2.07 | 0.00059294 | 0 | 2.34 | 0.00075587 | -0.0132 |  | LF | AllSpc | 2070 | 0.593 | 2070 | 0.593 | 1.13 | 1.27 | -0.0063768 | 2070 | 0.593 | 2070 | 0.593 | 1.13 | 1.27 | -0.00638
LFAllSpcSDGEUnExIOU | Com-Iltg-dWatt-LF_OSspc | SDG | EUn | Ex | IOU | 2.07 | 0.00059294 | 0 | 2.3626 | 0.00074705 | -0.0081883 | 2.07 | 0.00059294 | 0 | 2.3626 | 0.00074705 | -0.0081883 |  | LF | AllSpc | 2070 | 0.593 | 2070 | 0.593 | 1.14 | 1.26 | -0.0039557 | 2070 | 0.593 | 2070 | 0.593 | 1.14 | 1.26 | -0.00396
LFAllSpcSDGEUnNewCZ06 | Com-Iltg-dWatt-LF_OSspc | SDG | EUn | New | CZ06 | 2.07 | 0.000592 | 0 | 2.4 | 0.000748 | -0.00583 | 2.07 | 0.000592 | 0 | 2.4 | 0.000748 | -0.00583 |  | LF | AllSpc | 2070 | 0.592 | 2070 | 0.592 | 1.16 | 1.26 | -0.0028164 | 2070 | 0.592 | 2070 | 0.592 | 1.16 | 1.26 | -0.00282
LFAllSpcSDGEUnNewCZ07 | Com-Iltg-dWatt-LF_OSspc | SDG | EUn | New | CZ07 | 2.07 | 0.000592 | 0 | 2.38 | 0.000742 | -0.00478 | 2.07 | 0.000592 | 0 | 2.38 | 0.000742 | -0.00478 |  | LF | AllSpc | 2070 | 0.592 | 2070 | 0.592 | 1.15 | 1.25 | -0.0023092 | 2070 | 0.592 | 2070 | 0.592 | 1.15 | 1.25 | -0.00231
LFAllSpcSDGEUnNewCZ08 | Com-Iltg-dWatt-LF_OSspc | SDG | EUn | New | CZ08 | 2.07 | 0.000592 | 0 | 2.42 | 0.000757 | -0.00523 | 2.07 | 0.000592 | 0 | 2.42 | 0.000757 | -0.00523 |  | LF | AllSpc | 2070 | 0.592 | 2070 | 0.592 | 1.17 | 1.28 | -0.0025266 | 2070 | 0.592 | 2070 | 0.592 | 1.17 | 1.28 | -0.00253
LFAllSpcSDGEUnNewCZ10 | Com-Iltg-dWatt-LF_OSspc | SDG | EUn | New | CZ10 | 2.07 | 0.000592 | 0 | 2.44 | 0.000783 | -0.0062 | 2.07 | 0.000592 | 0 | 2.44 | 0.000783 | -0.0062 |  | LF | AllSpc | 2070 | 0.592 | 2070 | 0.592 | 1.18 | 1.32 | -0.0029952 | 2070 | 0.592 | 2070 | 0.592 | 1.18 | 1.32 | -0.003
LFAllSpcSDGEUnNewCZ14 | Com-Iltg-dWatt-LF_OSspc | SDG | EUn | New | CZ14 | 2.07 | 0.000592 | 0 | 2.39 | 0.000755 | -0.0114 | 2.07 | 0.000592 | 0 | 2.39 | 0.000755 | -0.0114 |  | LF | AllSpc | 2070 | 0.592 | 2070 | 0.592 | 1.15 | 1.28 | -0.0055072 | 2070 | 0.592 | 2070 | 0.592 | 1.15 | 1.28 | -0.00551
LFAllSpcSDGEUnNewCZ15 | Com-Iltg-dWatt-LF_OSspc | SDG | EUn | New | CZ15 | 2.07 | 0.000592 | 0 | 2.55 | 0.000788 | -0.00244 | 2.07 | 0.000592 | 0 | 2.55 | 0.000788 | -0.00244 |  | LF | AllSpc | 2070 | 0.592 | 2070 | 0.592 | 1.23 | 1.33 | -0.0011787 | 2070 | 0.592 | 2070 | 0.592 | 1.23 | 1.33 | -0.00118
LFAllSpcSDGEUnNewIOU | Com-Iltg-dWatt-LF_OSspc | SDG | EUn | New | IOU | 2.07 | 0.000592 | 0 | 2.3946 | 0.00075186 | -0.0051576 | 2.07 | 0.000592 | 0 | 2.3946 | 0.00075186 | -0.0051576 |  | LF | AllSpc | 2070 | 0.592 | 2070 | 0.592 | 1.16 | 1.27 | -0.0024916 | 2070 | 0.592 | 2070 | 0.592 | 1.16 | 1.27 | -0.00249
LFAllSpcSDGGroExCZ06 | Com-Iltg-dWatt-LF_OSspc | SDG | Gro | Ex | CZ06 | 4.7694 | 0.00066789 | 0 | 4.8194 | 0.00082089 | -0.060594 | 4.7694 | 0.00066789 | 0 | 4.8194 | 0.00082089 | -0.060594 |  | LF | AllSpc | 4770 | 0.668 | 4770 | 0.668 | 1.01 | 1.23 | -0.012705 | 4770 | 0.668 | 4770 | 0.668 | 1.01 | 1.23 | -0.0127
LFAllSpcSDGGroExCZ07 | Com-Iltg-dWatt-LF_OSspc | SDG | Gro | Ex | CZ07 | 4.7694 | 0.00066789 | 0 | 4.7543 | 0.00080089 | -0.064394 | 4.7694 | 0.00066789 | 0 | 4.7543 | 0.00080089 | -0.064394 |  | LF | AllSpc | 4770 | 0.668 | 4770 | 0.668 | 0.997 | 1.2 | -0.013501 | 4770 | 0.668 | 4770 | 0.668 | 0.997 | 1.2 | -0.0135
LFAllSpcSDGGroExCZ08 | Com-Iltg-dWatt-LF_OSspc | SDG | Gro | Ex | CZ08 | 4.7694 | 0.00066789 | 0 | 4.9294 | 0.00084089 | -0.054838 | 4.7694 | 0.00066789 | 0 | 4.9294 | 0.00084089 | -0.054838 |  | LF | AllSpc | 4770 | 0.668 | 4770 | 0.668 | 1.03 | 1.26 | -0.011498 | 4770 | 0.668 | 4770 | 0.668 | 1.03 | 1.26 | -0.0115
LFAllSpcSDGGroExCZ10 | Com-Iltg-dWatt-LF_OSspc | SDG | Gro | Ex | CZ10 | 4.7694 | 0.00066789 | 0 | 4.9994 | 0.00087589 | -0.051994 | 4.7694 | 0.00066789 | 0 | 4.9994 | 0.00087589 | -0.051994 |  | LF | AllSpc | 4770 | 0.668 | 4770 | 0.668 | 1.05 | 1.31 | -0.010902 | 4770 | 0.668 | 4770 | 0.668 | 1.05 | 1.31 | -0.0109
LFAllSpcSDGGroExCZ14 | Com-Iltg-dWatt-LF_OSspc | SDG | Gro | Ex | CZ14 | 4.7692 | 0.00066783 | 0 | 4.96 | 0.00088683 | -0.054792 | 4.7692 | 0.00066783 | 0 | 4.96 | 0.00088683 | -0.054792 |  | LF | AllSpc | 4770 | 0.668 | 4770 | 0.668 | 1.04 | 1.33 | -0.011489 | 4770 | 0.668 | 4770 | 0.668 | 1.04 | 1.33 | -0.0115
LFAllSpcSDGGroExCZ15 | Com-Iltg-dWatt-LF_OSspc | SDG | Gro | Ex | CZ15 | 4.7697 | 0.00066794 | 0 | 5.3597 | 0.00087094 | -0.0292 | 4.7697 | 0.00066794 | 0 | 5.3597 | 0.00087094 | -0.0292 |  | LF | AllSpc | 4770 | 0.668 | 4770 | 0.668 | 1.12 | 1.3 | -0.006122 | 4770 | 0.668 | 4770 | 0.668 | 1.12 | 1.3 | -0.00612
LFAllSpcSDGGroExIOU | Com-Iltg-dWatt-LF_OSspc | SDG | Gro | Ex | IOU | 4.7694 | 0.00066789 | 0 | 4.8303 | 0.00082377 | -0.0605 | 4.7694 | 0.00066789 | 0 | 4.8303 | 0.00082377 | -0.0605 |  | LF | AllSpc | 4770 | 0.668 | 4770 | 0.668 | 1.01 | 1.23 | -0.012685 | 4770 | 0.668 | 4770 | 0.668 | 1.01 | 1.23 | -0.0127
LFAllSpcSDGGroNewCZ06 | Com-Iltg-dWatt-LF_OSspc | SDG | Gro | New | CZ06 | 4.76 | 0.000666 | 0 | 5.07 | 0.00083 | -0.0448 | 4.76 | 0.000666 | 0 | 5.07 | 0.00083 | -0.0448 |  | LF | AllSpc | 4760 | 0.666 | 4760 | 0.666 | 1.07 | 1.25 | -0.0094118 | 4760 | 0.666 | 4760 | 0.666 | 1.07 | 1.25 | -0.00941
LFAllSpcSDGGroNewCZ07 | Com-Iltg-dWatt-LF_OSspc | SDG | Gro | New | CZ07 | 4.76 | 0.000666 | 0 | 5.03 | 0.000809 | -0.0448 | 4.76 | 0.000666 | 0 | 5.03 | 0.000809 | -0.0448 |  | LF | AllSpc | 4760 | 0.666 | 4760 | 0.666 | 1.06 | 1.21 | -0.0094118 | 4760 | 0.666 | 4760 | 0.666 | 1.06 | 1.21 | -0.00941
LFAllSpcSDGGroNewCZ08 | Com-Iltg-dWatt-LF_OSspc | SDG | Gro | New | CZ08 | 4.76 | 0.000666 | 0 | 5.12 | 0.00085 | -0.0395 | 4.76 | 0.000666 | 0 | 5.12 | 0.00085 | -0.0395 |  | LF | AllSpc | 4760 | 0.666 | 4760 | 0.666 | 1.08 | 1.28 | -0.0082983 | 4760 | 0.666 | 4760 | 0.666 | 1.08 | 1.28 | -0.0083
LFAllSpcSDGGroNewCZ10 | Com-Iltg-dWatt-LF_OSspc | SDG | Gro | New | CZ10 | 4.76 | 0.000666 | 0 | 5.15 | 0.000917 | -0.0422 | 4.76 | 0.000666 | 0 | 5.15 | 0.000917 | -0.0422 |  | LF | AllSpc | 4760 | 0.666 | 4760 | 0.666 | 1.08 | 1.38 | -0.0088655 | 4760 | 0.666 | 4760 | 0.666 | 1.08 | 1.38 | -0.00887
LFAllSpcSDGGroNewCZ14 | Com-Iltg-dWatt-LF_OSspc | SDG | Gro | New | CZ14 | 4.76 | 0.000666 | 0 | 5.14 | 0.000911 | -0.0505 | 4.76 | 0.000666 | 0 | 5.14 | 0.000911 | -0.0505 |  | LF | AllSpc | 4760 | 0.666 | 4760 | 0.666 | 1.08 | 1.37 | -0.010609 | 4760 | 0.666 | 4760 | 0.666 | 1.08 | 1.37 | -0.0106
LFAllSpcSDGGroNewCZ15 | Com-Iltg-dWatt-LF_OSspc | SDG | Gro | New | CZ15 | 4.76 | 0.000666 | 0 | 5.56 | 0.000921 | -0.0233 | 4.76 | 0.000666 | 0 | 5.56 | 0.000921 | -0.0233 |  | LF | AllSpc | 4760 | 0.666 | 4760 | 0.666 | 1.17 | 1.38 | -0.004895 | 4760 | 0.666 | 4760 | 0.666 | 1.17 | 1.38 | -0.0049
LFAllSpcSDGGroNewIOU | Com-Iltg-dWatt-LF_OSspc | SDG | Gro | New | IOU | 4.76 | 0.000666 | 0 | 5.0681 | 0.00084101 | -0.043963 | 4.76 | 0.000666 | 0 | 5.0681 | 0.00084101 | -0.043963 |  | LF | AllSpc | 4760 | 0.666 | 4760 | 0.666 | 1.06 | 1.26 | -0.0092359 | 4760 | 0.666 | 4760 | 0.666 | 1.06 | 1.26 | -0.00924
LFAllSpcSDGHspExCZ06 | Com-Iltg-dWatt-LF_OSspc | SDG | Hsp | Ex | CZ06 | 4.8796 | 0.00075896 | 0 | 5.5896 | 0.00094896 | -0.0251 | 4.8796 | 0.00075896 | 0 | 5.5896 | 0.00094896 | -0.0251 |  | LF | AllSpc | 4880 | 0.759 | 4880 | 0.759 | 1.15 | 1.25 | -0.0051439 | 4880 | 0.759 | 4880 | 0.759 | 1.15 | 1.25 | -0.00514
LFAllSpcSDGHspExCZ07 | Com-Iltg-dWatt-LF_OSspc | SDG | Hsp | Ex | CZ07 | 4.8796 | 0.00075896 | 0 | 5.5896 | 0.00094089 | -0.022996 | 4.8796 | 0.00075896 | 0 | 5.5896 | 0.00094089 | -0.022996 |  | LF | AllSpc | 4880 | 0.759 | 4880 | 0.759 | 1.15 | 1.24 | -0.0047127 | 4880 | 0.759 | 4880 | 0.759 | 1.15 | 1.24 | -0.00471
LFAllSpcSDGHspExCZ08 | Com-Iltg-dWatt-LF_OSspc | SDG | Hsp | Ex | CZ08 | 4.8796 | 0.00075896 | 0 | 5.6196 | 0.00094696 | -0.024796 | 4.8796 | 0.00075896 | 0 | 5.6196 | 0.00094696 | -0.024796 |  | LF | AllSpc | 4880 | 0.759 | 4880 | 0.759 | 1.15 | 1.25 | -0.0050816 | 4880 | 0.759 | 4880 | 0.759 | 1.15 | 1.25 | -0.00508
LFAllSpcSDGHspExCZ10 | Com-Iltg-dWatt-LF_OSspc | SDG | Hsp | Ex | CZ10 | 4.8796 | 0.00075896 | 0 | 5.6196 | 0.00097296 | -0.0267 | 4.8796 | 0.00075896 | 0 | 5.6196 | 0.00097296 | -0.0267 |  | LF | AllSpc | 4880 | 0.759 | 4880 | 0.759 | 1.15 | 1.28 | -0.0054718 | 4880 | 0.759 | 4880 | 0.759 | 1.15 | 1.28 | -0.00547
LFAllSpcSDGHspExCZ14 | Com-Iltg-dWatt-LF_OSspc | SDG | Hsp | Ex | CZ14 | 4.8795 | 0.00075895 | 0 | 5.5295 | 0.00096595 | -0.032795 | 4.8795 | 0.00075895 | 0 | 5.5295 | 0.00096595 | -0.032795 |  | LF | AllSpc | 4880 | 0.759 | 4880 | 0.759 | 1.13 | 1.27 | -0.006721 | 4880 | 0.759 | 4880 | 0.759 | 1.13 | 1.27 | -0.00672
LFAllSpcSDGHspExIOU | Com-Iltg-dWatt-LF_OSspc | SDG | Hsp | Ex | IOU | 4.8796 | 0.00075896 | 0 | 5.5951 | 0.00094587 | -0.023653 | 4.8796 | 0.00075896 | 0 | 5.5951 | 0.00094587 | -0.023653 |  | LF | AllSpc | 4880 | 0.759 | 4880 | 0.759 | 1.15 | 1.25 | -0.0048474 | 4880 | 0.759 | 4880 | 0.759 | 1.15 | 1.25 | -0.00485
LFAllSpcSDGHspNewCZ06 | Com-Iltg-dWatt-LF_OSspc | SDG | Hsp | New | CZ06 | 4.87 | 0.000758 | 0 | 5.36 | 0.000912 | -0.0262 | 4.87 | 0.000758 | 0 | 5.36 | 0.000912 | -0.0262 |  | LF | AllSpc | 4870 | 0.758 | 4870 | 0.758 | 1.1 | 1.2 | -0.0053799 | 4870 | 0.758 | 4870 | 0.758 | 1.1 | 1.2 | -0.00538
LFAllSpcSDGHspNewCZ07 | Com-Iltg-dWatt-LF_OSspc | SDG | Hsp | New | CZ07 | 4.87 | 0.000758 | 0 | 5.38 | 0.000905 | -0.0217 | 4.87 | 0.000758 | 0 | 5.38 | 0.000905 | -0.0217 |  | LF | AllSpc | 4870 | 0.758 | 4870 | 0.758 | 1.1 | 1.19 | -0.0044559 | 4870 | 0.758 | 4870 | 0.758 | 1.1 | 1.19 | -0.00446
LFAllSpcSDGHspNewCZ08 | Com-Iltg-dWatt-LF_OSspc | SDG | Hsp | New | CZ08 | 4.87 | 0.000758 | 0 | 5.41 | 0.000915 | -0.0245 | 4.87 | 0.000758 | 0 | 5.41 | 0.000915 | -0.0245 |  | LF | AllSpc | 4870 | 0.758 | 4870 | 0.758 | 1.11 | 1.21 | -0.0050308 | 4870 | 0.758 | 4870 | 0.758 | 1.11 | 1.21 | -0.00503
LFAllSpcSDGHspNewCZ10 | Com-Iltg-dWatt-LF_OSspc | SDG | Hsp | New | CZ10 | 4.87 | 0.000758 | 0 | 5.4 | 0.000947 | -0.0262 | 4.87 | 0.000758 | 0 | 5.4 | 0.000947 | -0.0262 |  | LF | AllSpc | 4870 | 0.758 | 4870 | 0.758 | 1.11 | 1.25 | -0.0053799 | 4870 | 0.758 | 4870 | 0.758 | 1.11 | 1.25 | -0.00538
LFAllSpcSDGHspNewCZ14 | Com-Iltg-dWatt-LF_OSspc | SDG | Hsp | New | CZ14 | 4.87 | 0.000758 | 0 | 5.33 | 0.000937 | -0.0333 | 4.87 | 0.000758 | 0 | 5.33 | 0.000937 | -0.0333 |  | LF | AllSpc | 4870 | 0.758 | 4870 | 0.758 | 1.09 | 1.24 | -0.0068378 | 4870 | 0.758 | 4870 | 0.758 | 1.09 | 1.24 | -0.00684
LFAllSpcSDGHspNewCZ15 | Com-Iltg-dWatt-LF_OSspc | SDG | Hsp | New | CZ15 | 4.87 | 0.000758 | 0 | 5.65 | 0.000955 | -0.0187 | 4.87 | 0.000758 | 0 | 5.65 | 0.000955 | -0.0187 |  | LF | AllSpc | 4870 | 0.758 | 4870 | 0.758 | 1.16 | 1.26 | -0.0038398 | 4870 | 0.758 | 4870 | 0.758 | 1.16 | 1.26 | -0.00384
LFAllSpcSDGHspNewIOU | Com-Iltg-dWatt-LF_OSspc | SDG | Hsp | New | IOU | 4.87 | 0.000758 | 0 | 5.3836 | 0.00091154 | -0.022574 | 4.87 | 0.000758 | 0 | 5.3836 | 0.00091154 | -0.022574 |  | LF | AllSpc | 4870 | 0.758 | 4870 | 0.758 | 1.11 | 1.2 | -0.0046354 | 4870 | 0.758 | 4870 | 0.758 | 1.11 | 1.2 | -0.00464
LFAllSpcSDGHtlExCZ06 | Com-Iltg-dWatt-LF_OSspc | SDG | Htl | Ex | CZ06 | 1.6321 | 0.000207 | 0 | 1.7521 | 0.000259 | -0.0040752 | 1.6321 | 0.000207 | 0 | 1.7521 | 0.000259 | -0.0040752 |  | LF | AllSpc | 1630 | 0.207 | 1630 | 0.207 | 1.07 | 1.25 | -0.0024969 | 1630 | 0.207 | 1630 | 0.207 | 1.07 | 1.25 | -0.0025
LFAllSpcSDGHtlExCZ07 | Com-Iltg-dWatt-LF_OSspc | SDG | Htl | Ex | CZ07 | 1.6321 | 0.000207 | 0 | 1.7831 | 0.000257 | -0.0032941 | 1.6321 | 0.000207 | 0 | 1.7831 | 0.000257 | -0.0032941 |  | LF | AllSpc | 1630 | 0.207 | 1630 | 0.207 | 1.09 | 1.24 | -0.0020184 | 1630 | 0.207 | 1630 | 0.207 | 1.09 | 1.24 | -0.00202
LFAllSpcSDGHtlExCZ08 | Com-Iltg-dWatt-LF_OSspc | SDG | Htl | Ex | CZ08 | 1.6321 | 0.000207 | 0 | 1.7821 | 0.000261 | -0.0036241 | 1.6321 | 0.000207 | 0 | 1.7821 | 0.000261 | -0.0036241 |  | LF | AllSpc | 1630 | 0.207 | 1630 | 0.207 | 1.09 | 1.26 | -0.0022206 | 1630 | 0.207 | 1630 | 0.207 | 1.09 | 1.26 | -0.00222
LFAllSpcSDGHtlExCZ10 | Com-Iltg-dWatt-LF_OSspc | SDG | Htl | Ex | CZ10 | 1.6321 | 0.000207 | 0 | 1.7521 | 0.0002641 | -0.0040452 | 1.6321 | 0.000207 | 0 | 1.7521 | 0.0002641 | -0.0040452 |  | LF | AllSpc | 1630 | 0.207 | 1630 | 0.207 | 1.07 | 1.28 | -0.0024786 | 1630 | 0.207 | 1630 | 0.207 | 1.07 | 1.28 | -0.00248
LFAllSpcSDGHtlExCZ14 | Com-Iltg-dWatt-LF_OSspc | SDG | Htl | Ex | CZ14 | 1.6321 | 0.000207 | 0 | 1.6721 | 0.0002651 | -0.0054273 | 1.6321 | 0.000207 | 0 | 1.6721 | 0.0002651 | -0.0054273 |  | LF | AllSpc | 1630 | 0.207 | 1630 | 0.207 | 1.02 | 1.28 | -0.0033254 | 1630 | 0.207 | 1630 | 0.207 | 1.02 | 1.28 | -0.00333
LFAllSpcSDGHtlExCZ15 | Com-Iltg-dWatt-LF_OSspc | SDG | Htl | Ex | CZ15 | 1.6321 | 0.000207 | 0 | 1.8921 | 0.000267 | -0.0023331 | 1.6321 | 0.000207 | 0 | 1.8921 | 0.000267 | -0.0023331 |  | LF | AllSpc | 1630 | 0.207 | 1630 | 0.207 | 1.16 | 1.29 | -0.0014295 | 1630 | 0.207 | 1630 | 0.207 | 1.16 | 1.29 | -0.00143
LFAllSpcSDGHtlExIOU | Com-Iltg-dWatt-LF_OSspc | SDG | Htl | Ex | IOU | 1.6321 | 0.000207 | 0 | 1.7789 | 0.00025797 | -0.0034128 | 1.6321 | 0.000207 | 0 | 1.7789 | 0.00025797 | -0.0034128 |  | LF | AllSpc | 1630 | 0.207 | 1630 | 0.207 | 1.09 | 1.25 | -0.0020911 | 1630 | 0.207 | 1630 | 0.207 | 1.09 | 1.25 | -0.00209
LFAllSpcSDGHtlNewCZ06 | Com-Iltg-dWatt-LF_OSspc | SDG | Htl | New | CZ06 | 1.65 | 0.000207 | 0 | 1.75 | 0.000266 | -0.00399 | 1.65 | 0.000207 | 0 | 1.75 | 0.000266 | -0.00399 |  | LF | AllSpc | 1650 | 0.207 | 1650 | 0.207 | 1.06 | 1.29 | -0.0024182 | 1650 | 0.207 | 1650 | 0.207 | 1.06 | 1.29 | -0.00242
LFAllSpcSDGHtlNewCZ07 | Com-Iltg-dWatt-LF_OSspc | SDG | Htl | New | CZ07 | 1.65 | 0.000207 | 0 | 1.79 | 0.000261 | -0.00265 | 1.65 | 0.000207 | 0 | 1.79 | 0.000261 | -0.00265 |  | LF | AllSpc | 1650 | 0.207 | 1650 | 0.207 | 1.08 | 1.26 | -0.0016061 | 1650 | 0.207 | 1650 | 0.207 | 1.08 | 1.26 | -0.00161
LFAllSpcSDGHtlNewCZ08 | Com-Iltg-dWatt-LF_OSspc | SDG | Htl | New | CZ08 | 1.65 | 0.000207 | 0 | 1.78 | 0.000268 | -0.00341 | 1.65 | 0.000207 | 0 | 1.78 | 0.000268 | -0.00341 |  | LF | AllSpc | 1650 | 0.207 | 1650 | 0.207 | 1.08 | 1.29 | -0.0020667 | 1650 | 0.207 | 1650 | 0.207 | 1.08 | 1.29 | -0.00207
LFAllSpcSDGHtlNewCZ10 | Com-Iltg-dWatt-LF_OSspc | SDG | Htl | New | CZ10 | 1.65 | 0.000207 | 0 | 1.75 | 0.000277 | -0.0044 | 1.65 | 0.000207 | 0 | 1.75 | 0.000277 | -0.0044 |  | LF | AllSpc | 1650 | 0.207 | 1650 | 0.207 | 1.06 | 1.34 | -0.0026667 | 1650 | 0.207 | 1650 | 0.207 | 1.06 | 1.34 | -0.00267
LFAllSpcSDGHtlNewCZ14 | Com-Iltg-dWatt-LF_OSspc | SDG | Htl | New | CZ14 | 1.65 | 0.000207 | 0 | 1.66 | 0.000275 | -0.00652 | 1.65 | 0.000207 | 0 | 1.66 | 0.000275 | -0.00652 |  | LF | AllSpc | 1650 | 0.207 | 1650 | 0.207 | 1.01 | 1.33 | -0.0039515 | 1650 | 0.207 | 1650 | 0.207 | 1.01 | 1.33 | -0.00395
LFAllSpcSDGHtlNewCZ15 | Com-Iltg-dWatt-LF_OSspc | SDG | Htl | New | CZ15 | 1.65 | 0.000207 | 0 | 1.92 | 0.00028 | -0.00232 | 1.65 | 0.000207 | 0 | 1.92 | 0.00028 | -0.00232 |  | LF | AllSpc | 1650 | 0.207 | 1650 | 0.207 | 1.16 | 1.35 | -0.0014061 | 1650 | 0.207 | 1650 | 0.207 | 1.16 | 1.35 | -0.00141
LFAllSpcSDGHtlNewIOU | Com-Iltg-dWatt-LF_OSspc | SDG | Htl | New | IOU | 1.65 | 0.000207 | 0 | 1.7845 | 0.00026312 | -0.0029149 | 1.65 | 0.000207 | 0 | 1.7845 | 0.00026312 | -0.0029149 |  | LF | AllSpc | 1650 | 0.207 | 1650 | 0.207 | 1.08 | 1.27 | -0.0017666 | 1650 | 0.207 | 1650 | 0.207 | 1.08 | 1.27 | -0.00177
LFAllSpcSDGMBTExCZ06 | Com-Iltg-dWatt-LF_OSspc | SDG | MBT | Ex | CZ06 | 3.0291 | 0.00072709 | 0 | 3.5191 | 0.000883 | -0.00079881 | 3.0291 | 0.00072709 | 0 | 3.5191 | 0.000883 | -0.00079881 |  | LF | AllSpc | 3030 | 0.727 | 3030 | 0.727 | 1.16 | 1.21 | -0.00026372 | 3030 | 0.727 | 3030 | 0.727 | 1.16 | 1.21 | -0.000264
LFAllSpcSDGMBTExCZ07 | Com-Iltg-dWatt-LF_OSspc | SDG | MBT | Ex | CZ07 | 3.0291 | 0.00072709 | 0 | 3.5391 | 0.00087309 | -0.00015591 | 3.0291 | 0.00072709 | 0 | 3.5391 | 0.00087309 | -0.00015591 |  | LF | AllSpc | 3030 | 0.727 | 3030 | 0.727 | 1.17 | 1.2 | -5.147e-05 | 3030 | 0.727 | 3030 | 0.727 | 1.17 | 1.2 | -5.15e-05
LFAllSpcSDGMBTExCZ08 | Com-Iltg-dWatt-LF_OSspc | SDG | MBT | Ex | CZ08 | 3.0291 | 0.00072709 | 0 | 3.52 | 0.00092209 | -0.00050791 | 3.0291 | 0.00072709 | 0 | 3.52 | 0.00092209 | -0.00050791 |  | LF | AllSpc | 3030 | 0.727 | 3030 | 0.727 | 1.16 | 1.27 | -0.00016768 | 3030 | 0.727 | 3030 | 0.727 | 1.16 | 1.27 | -0.000168
LFAllSpcSDGMBTExCZ10 | Com-Iltg-dWatt-LF_OSspc | SDG | MBT | Ex | CZ10 | 3.0291 | 0.00072709 | 0 | 3.5091 | 0.00094209 | -0.00104 | 3.0291 | 0.00072709 | 0 | 3.5091 | 0.00094209 | -0.00104 |  | LF | AllSpc | 3030 | 0.727 | 3030 | 0.727 | 1.16 | 1.3 | -0.00034334 | 3030 | 0.727 | 3030 | 0.727 | 1.16 | 1.3 | -0.000343
LFAllSpcSDGMBTExCZ14 | Com-Iltg-dWatt-LF_OSspc | SDG | MBT | Ex | CZ14 | 3.0291 | 0.00072709 | 0 | 3.4491 | 0.000936 | -0.0024991 | 3.0291 | 0.00072709 | 0 | 3.4491 | 0.000936 | -0.0024991 |  | LF | AllSpc | 3030 | 0.727 | 3030 | 0.727 | 1.14 | 1.29 | -0.00082503 | 3030 | 0.727 | 3030 | 0.727 | 1.14 | 1.29 | -0.000825
LFAllSpcSDGMBTExCZ15 | Com-Iltg-dWatt-LF_OSspc | SDG | MBT | Ex | CZ15 | 3.0291 | 0.00072709 | 0 | 3.6491 | 0.00094509 | 0 | 3.0291 | 0.00072709 | 0 | 3.6491 | 0.00094509 | 0 |  | LF | AllSpc | 3030 | 0.727 | 3030 | 0.727 | 1.2 | 1.3 | 0 | 3030 | 0.727 | 3030 | 0.727 | 1.2 | 1.3 | 0
LFAllSpcSDGMBTExIOU | Com-Iltg-dWatt-LF_OSspc | SDG | MBT | Ex | IOU | 3.0291 | 0.00072709 | 0 | 3.5284 | 0.00089615 | -0.00047392 | 3.0291 | 0.00072709 | 0 | 3.5284 | 0.00089615 | -0.00047392 |  | LF | AllSpc | 3030 | 0.727 | 3030 | 0.727 | 1.16 | 1.23 | -0.00015646 | 3030 | 0.727 | 3030 | 0.727 | 1.16 | 1.23 | -0.000156
LFAllSpcSDGMBTNewCZ06 | Com-Iltg-dWatt-LF_OSspc | SDG | MBT | New | CZ06 | 3.02 | 0.000728 | 0 | 3.4 | 0.000919 | -0.00104 | 3.02 | 0.000728 | 0 | 3.4 | 0.000919 | -0.00104 |  | LF | AllSpc | 3020 | 0.728 | 3020 | 0.728 | 1.13 | 1.26 | -0.00034437 | 3020 | 0.728 | 3020 | 0.728 | 1.13 | 1.26 | -0.000344
LFAllSpcSDGMBTNewCZ07 | Com-Iltg-dWatt-LF_OSspc | SDG | MBT | New | CZ07 | 3.02 | 0.000728 | 0 | 3.39 | 0.00091 | 0 | 3.02 | 0.000728 | 0 | 3.39 | 0.00091 | 0 |  | LF | AllSpc | 3020 | 0.728 | 3020 | 0.728 | 1.12 | 1.25 | 0 | 3020 | 0.728 | 3020 | 0.728 | 1.12 | 1.25 | 0
LFAllSpcSDGMBTNewCZ08 | Com-Iltg-dWatt-LF_OSspc | SDG | MBT | New | CZ08 | 3.02 | 0.000728 | 0 | 3.42 | 0.000944 | -0.000833 | 3.02 | 0.000728 | 0 | 3.42 | 0.000944 | -0.000833 |  | LF | AllSpc | 3020 | 0.728 | 3020 | 0.728 | 1.13 | 1.3 | -0.00027583 | 3020 | 0.728 | 3020 | 0.728 | 1.13 | 1.3 | -0.000276
LFAllSpcSDGMBTNewCZ10 | Com-Iltg-dWatt-LF_OSspc | SDG | MBT | New | CZ10 | 3.02 | 0.000728 | 0 | 3.42 | 0.000983 | -0.00104 | 3.02 | 0.000728 | 0 | 3.42 | 0.000983 | -0.00104 |  | LF | AllSpc | 3020 | 0.728 | 3020 | 0.728 | 1.13 | 1.35 | -0.00034437 | 3020 | 0.728 | 3020 | 0.728 | 1.13 | 1.35 | -0.000344
LFAllSpcSDGMBTNewCZ14 | Com-Iltg-dWatt-LF_OSspc | SDG | MBT | New | CZ14 | 3.02 | 0.000728 | 0 | 3.39 | 0.000971 | -0.00197 | 3.02 | 0.000728 | 0 | 3.39 | 0.000971 | -0.00197 |  | LF | AllSpc | 3020 | 0.728 | 3020 | 0.728 | 1.12 | 1.33 | -0.00065232 | 3020 | 0.728 | 3020 | 0.728 | 1.12 | 1.33 | -0.000652
LFAllSpcSDGMBTNewCZ15 | Com-Iltg-dWatt-LF_OSspc | SDG | MBT | New | CZ15 | 3.02 | 0.000728 | 0 | 3.6 | 0.000984 | 0 | 3.02 | 0.000728 | 0 | 3.6 | 0.000984 | 0 |  | LF | AllSpc | 3020 | 0.728 | 3020 | 0.728 | 1.19 | 1.35 | 0 | 3020 | 0.728 | 3020 | 0.728 | 1.19 | 1.35 | 0
LFAllSpcSDGMBTNewIOU | Com-Iltg-dWatt-LF_OSspc | SDG | MBT | New | IOU | 3.02 | 0.000728 | 0 | 3.4007 | 0.00093393 | -0.00038487 | 3.02 | 0.000728 | 0 | 3.4007 | 0.00093393 | -0.00038487 |  | LF | AllSpc | 3020 | 0.728 | 3020 | 0.728 | 1.13 | 1.28 | -0.00012744 | 3020 | 0.728 | 3020 | 0.728 | 1.13 | 1.28 | -0.000127
LFAllSpcSDGMLIExCZ06 | Com-Iltg-dWatt-LF_OSspc | SDG | MLI | Ex | CZ06 | 2.83 | 0.000784 | 0 | 3.06 | 0.00094 | -0.0059409 | 2.83 | 0.000784 | 0 | 3.06 | 0.00094 | -0.0059409 |  | LF | AllSpc | 2830 | 0.784 | 2830 | 0.784 | 1.08 | 1.2 | -0.0020993 | 2830 | 0.784 | 2830 | 0.784 | 1.08 | 1.2 | -0.0021
LFAllSpcSDGMLIExCZ07 | Com-Iltg-dWatt-LF_OSspc | SDG | MLI | Ex | CZ07 | 2.83 | 0.000784 | 0 | 3.0509 | 0.00093691 | -0.00297 | 2.83 | 0.000784 | 0 | 3.0509 | 0.00093691 | -0.00297 |  | LF | AllSpc | 2830 | 0.784 | 2830 | 0.784 | 1.08 | 1.2 | -0.0010495 | 2830 | 0.784 | 2830 | 0.784 | 1.08 | 1.2 | -0.00105
LFAllSpcSDGMLIExCZ08 | Com-Iltg-dWatt-LF_OSspc | SDG | MLI | Ex | CZ08 | 2.83 | 0.000784 | 0 | 3.09 | 0.00094 | -0.0048609 | 2.83 | 0.000784 | 0 | 3.09 | 0.00094 | -0.0048609 |  | LF | AllSpc | 2830 | 0.784 | 2830 | 0.784 | 1.09 | 1.2 | -0.0017176 | 2830 | 0.784 | 2830 | 0.784 | 1.09 | 1.2 | -0.00172
LFAllSpcSDGMLIExCZ10 | Com-Iltg-dWatt-LF_OSspc | SDG | MLI | Ex | CZ10 | 2.83 | 0.000784 | 0 | 3.08 | 0.000964 | -0.0067009 | 2.83 | 0.000784 | 0 | 3.08 | 0.000964 | -0.0067009 |  | LF | AllSpc | 2830 | 0.784 | 2830 | 0.784 | 1.09 | 1.23 | -0.0023678 | 2830 | 0.784 | 2830 | 0.784 | 1.09 | 1.23 | -0.00237
LFAllSpcSDGMLIExCZ14 | Com-Iltg-dWatt-LF_OSspc | SDG | MLI | Ex | CZ14 | 2.83 | 0.000784 | 0 | 2.99 | 0.000955 | -0.019 | 2.83 | 0.000784 | 0 | 2.99 | 0.000955 | -0.019 |  | LF | AllSpc | 2830 | 0.784 | 2830 | 0.784 | 1.06 | 1.22 | -0.0067138 | 2830 | 0.784 | 2830 | 0.784 | 1.06 | 1.22 | -0.00671
LFAllSpcSDGMLIExCZ15 | Com-Iltg-dWatt-LF_OSspc | SDG | MLI | Ex | CZ15 | 2.83 | 0.000784 | 0 | 3.31 | 0.000953 | -0.0018209 | 2.83 | 0.000784 | 0 | 3.31 | 0.000953 | -0.0018209 |  | LF | AllSpc | 2830 | 0.784 | 2830 | 0.784 | 1.17 | 1.22 | -0.00064343 | 2830 | 0.784 | 2830 | 0.784 | 1.17 | 1.22 | -0.000643
LFAllSpcSDGMLIExIOU | Com-Iltg-dWatt-LF_OSspc | SDG | MLI | Ex | IOU | 2.83 | 0.000784 | 0 | 3.061 | 0.00094551 | -0.0043854 | 2.83 | 0.000784 | 0 | 3.061 | 0.00094551 | -0.0043854 |  | LF | AllSpc | 2830 | 0.784 | 2830 | 0.784 | 1.08 | 1.21 | -0.0015496 | 2830 | 0.784 | 2830 | 0.784 | 1.08 | 1.21 | -0.00155
LFAllSpcSDGMLINewCZ06 | Com-Iltg-dWatt-LF_OSspc | SDG | MLI | New | CZ06 | 2.83 | 0.000784 | 0 | 3.04 | 0.000964 | -0.00852 | 2.83 | 0.000784 | 0 | 3.04 | 0.000964 | -0.00852 |  | LF | AllSpc | 2830 | 0.784 | 2830 | 0.784 | 1.07 | 1.23 | -0.0030106 | 2830 | 0.784 | 2830 | 0.784 | 1.07 | 1.23 | -0.00301
LFAllSpcSDGMLINewCZ07 | Com-Iltg-dWatt-LF_OSspc | SDG | MLI | New | CZ07 | 2.83 | 0.000784 | 0 | 3 | 0.000935 | -0.00436 | 2.83 | 0.000784 | 0 | 3 | 0.000935 | -0.00436 |  | LF | AllSpc | 2830 | 0.784 | 2830 | 0.784 | 1.06 | 1.19 | -0.0015406 | 2830 | 0.784 | 2830 | 0.784 | 1.06 | 1.19 | -0.00154
LFAllSpcSDGMLINewCZ08 | Com-Iltg-dWatt-LF_OSspc | SDG | MLI | New | CZ08 | 2.83 | 0.000784 | 0 | 3.09 | 0.000974 | -0.00663 | 2.83 | 0.000784 | 0 | 3.09 | 0.000974 | -0.00663 |  | LF | AllSpc | 2830 | 0.784 | 2830 | 0.784 | 1.09 | 1.24 | -0.0023428 | 2830 | 0.784 | 2830 | 0.784 | 1.09 | 1.24 | -0.00234
LFAllSpcSDGMLINewCZ10 | Com-Iltg-dWatt-LF_OSspc | SDG | MLI | New | CZ10 | 2.83 | 0.000784 | 0 | 3.13 | 0.00104 | -0.00816 | 2.83 | 0.000784 | 0 | 3.13 | 0.00104 | -0.00816 |  | LF | AllSpc | 2830 | 0.784 | 2830 | 0.784 | 1.11 | 1.33 | -0.0028834 | 2830 | 0.784 | 2830 | 0.784 | 1.11 | 1.33 | -0.00288
LFAllSpcSDGMLINewCZ14 | Com-Iltg-dWatt-LF_OSspc | SDG | MLI | New | CZ14 | 2.83 | 0.000784 | 0 | 3.08 | 0.00102 | -0.0184 | 2.83 | 0.000784 | 0 | 3.08 | 0.00102 | -0.0184 |  | LF | AllSpc | 2830 | 0.784 | 2830 | 0.784 | 1.09 | 1.3 | -0.0065018 | 2830 | 0.784 | 2830 | 0.784 | 1.09 | 1.3 | -0.0065
LFAllSpcSDGMLINewCZ15 | Com-Iltg-dWatt-LF_OSspc | SDG | MLI | New | CZ15 | 2.83 | 0.000784 | 0 | 3.34 | 0.00105 | -0.00126 | 2.83 | 0.000784 | 0 | 3.34 | 0.00105 | -0.00126 |  | LF | AllSpc | 2830 | 0.784 | 2830 | 0.784 | 1.18 | 1.34 | -0.00044523 | 2830 | 0.784 | 2830 | 0.784 | 1.18 | 1.34 | -0.000445
LFAllSpcSDGMLINewIOU | Com-Iltg-dWatt-LF_OSspc | SDG | MLI | New | IOU | 2.83 | 0.000784 | 0 | 3.0444 | 0.00096975 | -0.005818 | 2.83 | 0.000784 | 0 | 3.0444 | 0.00096975 | -0.005818 |  | LF | AllSpc | 2830 | 0.784 | 2830 | 0.784 | 1.08 | 1.24 | -0.0020558 | 2830 | 0.784 | 2830 | 0.784 | 1.08 | 1.24 | -0.00206
LFAllSpcSDGMtlExCZ06 | Com-Iltg-dWatt-LF_OSspc | SDG | Mtl | Ex | CZ06 | 1.35 | 0.000148 | 0 | 1.5 | 0.0001861 | -0.00434 | 1.35 | 0.000148 | 0 | 1.5 | 0.0001861 | -0.00434 |  | LF | AllSpc | 1350 | 0.148 | 1350 | 0.148 | 1.11 | 1.26 | -0.0032148 | 1350 | 0.148 | 1350 | 0.148 | 1.11 | 1.26 | -0.00321
LFAllSpcSDGMtlExCZ07 | Com-Iltg-dWatt-LF_OSspc | SDG | Mtl | Ex | CZ07 | 1.35 | 0.000148 | 0 | 1.54 | 0.0001851 | -0.00318 | 1.35 | 0.000148 | 0 | 1.54 | 0.0001851 | -0.00318 |  | LF | AllSpc | 1350 | 0.148 | 1350 | 0.148 | 1.14 | 1.25 | -0.0023556 | 1350 | 0.148 | 1350 | 0.148 | 1.14 | 1.25 | -0.00236
LFAllSpcSDGMtlExCZ08 | Com-Iltg-dWatt-LF_OSspc | SDG | Mtl | Ex | CZ08 | 1.35 | 0.000148 | 0 | 1.53 | 0.000189 | -0.00365 | 1.35 | 0.000148 | 0 | 1.53 | 0.000189 | -0.00365 |  | LF | AllSpc | 1350 | 0.148 | 1350 | 0.148 | 1.13 | 1.28 | -0.0027037 | 1350 | 0.148 | 1350 | 0.148 | 1.13 | 1.28 | -0.0027
LFAllSpcSDGMtlExCZ10 | Com-Iltg-dWatt-LF_OSspc | SDG | Mtl | Ex | CZ10 | 1.35 | 0.000148 | 0 | 1.51 | 0.000194 | -0.004281 | 1.35 | 0.000148 | 0 | 1.51 | 0.000194 | -0.004281 |  | LF | AllSpc | 1350 | 0.148 | 1350 | 0.148 | 1.12 | 1.31 | -0.0031711 | 1350 | 0.148 | 1350 | 0.148 | 1.12 | 1.31 | -0.00317
LFAllSpcSDGMtlExCZ14 | Com-Iltg-dWatt-LF_OSspc | SDG | Mtl | Ex | CZ14 | 1.35 | 0.000148 | 0 | 1.451 | 0.000194 | -0.005881 | 1.35 | 0.000148 | 0 | 1.451 | 0.000194 | -0.005881 |  | LF | AllSpc | 1350 | 0.148 | 1350 | 0.148 | 1.07 | 1.31 | -0.0043563 | 1350 | 0.148 | 1350 | 0.148 | 1.07 | 1.31 | -0.00436
LFAllSpcSDGMtlExCZ15 | Com-Iltg-dWatt-LF_OSspc | SDG | Mtl | Ex | CZ15 | 1.35 | 0.000148 | 0 | 1.62 | 0.000197 | -0.001801 | 1.35 | 0.000148 | 0 | 1.62 | 0.000197 | -0.001801 |  | LF | AllSpc | 1350 | 0.148 | 1350 | 0.148 | 1.2 | 1.33 | -0.0013341 | 1350 | 0.148 | 1350 | 0.148 | 1.2 | 1.33 | -0.00133
LFAllSpcSDGMtlExIOU | Com-Iltg-dWatt-LF_OSspc | SDG | Mtl | Ex | IOU | 1.35 | 0.000148 | 0 | 1.5353 | 0.00018622 | -0.003351 | 1.35 | 0.000148 | 0 | 1.5353 | 0.00018622 | -0.003351 |  | LF | AllSpc | 1350 | 0.148 | 1350 | 0.148 | 1.14 | 1.26 | -0.0024822 | 1350 | 0.148 | 1350 | 0.148 | 1.14 | 1.26 | -0.00248
LFAllSpcSDGMtlNewCZ06 | Com-Iltg-dWatt-LF_OSspc | SDG | Mtl | New | CZ06 | 1.35 | 0.000148 | 0 | 1.49 | 0.000191 | -0.00592 | 1.35 | 0.000148 | 0 | 1.49 | 0.000191 | -0.00592 |  | LF | AllSpc | 1350 | 0.148 | 1350 | 0.148 | 1.1 | 1.29 | -0.0043852 | 1350 | 0.148 | 1350 | 0.148 | 1.1 | 1.29 | -0.00439
LFAllSpcSDGMtlNewCZ07 | Com-Iltg-dWatt-LF_OSspc | SDG | Mtl | New | CZ07 | 1.35 | 0.000148 | 0 | 1.51 | 0.000186 | -0.00424 | 1.35 | 0.000148 | 0 | 1.51 | 0.000186 | -0.00424 |  | LF | AllSpc | 1350 | 0.148 | 1350 | 0.148 | 1.12 | 1.26 | -0.0031407 | 1350 | 0.148 | 1350 | 0.148 | 1.12 | 1.26 | -0.00314
LFAllSpcSDGMtlNewCZ08 | Com-Iltg-dWatt-LF_OSspc | SDG | Mtl | New | CZ08 | 1.35 | 0.000148 | 0 | 1.52 | 0.000194 | -0.00489 | 1.35 | 0.000148 | 0 | 1.52 | 0.000194 | -0.00489 |  | LF | AllSpc | 1350 | 0.148 | 1350 | 0.148 | 1.13 | 1.31 | -0.0036222 | 1350 | 0.148 | 1350 | 0.148 | 1.13 | 1.31 | -0.00362
LFAllSpcSDGMtlNewCZ10 | Com-Iltg-dWatt-LF_OSspc | SDG | Mtl | New | CZ10 | 1.35 | 0.000148 | 0 | 1.48 | 0.000198 | -0.00601 | 1.35 | 0.000148 | 0 | 1.48 | 0.000198 | -0.00601 |  | LF | AllSpc | 1350 | 0.148 | 1350 | 0.148 | 1.1 | 1.34 | -0.0044519 | 1350 | 0.148 | 1350 | 0.148 | 1.1 | 1.34 | -0.00445
LFAllSpcSDGMtlNewCZ14 | Com-Iltg-dWatt-LF_OSspc | SDG | Mtl | New | CZ14 | 1.35 | 0.000148 | 0 | 1.42 | 0.000197 | -0.00783 | 1.35 | 0.000148 | 0 | 1.42 | 0.000197 | -0.00783 |  | LF | AllSpc | 1350 | 0.148 | 1350 | 0.148 | 1.05 | 1.33 | -0.0058 | 1350 | 0.148 | 1350 | 0.148 | 1.05 | 1.33 | -0.0058
LFAllSpcSDGMtlNewCZ15 | Com-Iltg-dWatt-LF_OSspc | SDG | Mtl | New | CZ15 | 1.35 | 0.000148 | 0 | 1.6 | 0.000201 | -0.00282 | 1.35 | 0.000148 | 0 | 1.6 | 0.000201 | -0.00282 |  | LF | AllSpc | 1350 | 0.148 | 1350 | 0.148 | 1.19 | 1.36 | -0.0020889 | 1350 | 0.148 | 1350 | 0.148 | 1.19 | 1.36 | -0.00209
LFAllSpcSDGMtlNewIOU | Com-Iltg-dWatt-LF_OSspc | SDG | Mtl | New | IOU | 1.35 | 0.000148 | 0 | 1.5064 | 0.00018767 | -0.0045077 | 1.35 | 0.000148 | 0 | 1.5064 | 0.00018767 | -0.0045077 |  | LF | AllSpc | 1350 | 0.148 | 1350 | 0.148 | 1.12 | 1.27 | -0.0033391 | 1350 | 0.148 | 1350 | 0.148 | 1.12 | 1.27 | -0.00334
LFAllSpcSDGNrsExCZ06 | Com-Iltg-dWatt-LF_OSspc | SDG | Nrs | Ex | CZ06 | 3.6004 | 0.00058008 | 0 | 3.8704 | 0.00075604 | -0.037104 | 3.6004 | 0.00058008 | 0 | 3.8704 | 0.00075604 | -0.037104 |  | LF | AllSpc | 3600 | 0.58 | 3600 | 0.58 | 1.07 | 1.3 | -0.010306 | 3600 | 0.58 | 3600 | 0.58 | 1.07 | 1.3 | -0.0103
LFAllSpcSDGNrsExCZ07 | Com-Iltg-dWatt-LF_OSspc | SDG | Nrs | Ex | CZ07 | 3.6004 | 0.00058008 | 0 | 3.86 | 0.00074408 | -0.033804 | 3.6004 | 0.00058008 | 0 | 3.86 | 0.00074408 | -0.033804 |  | LF | AllSpc | 3600 | 0.58 | 3600 | 0.58 | 1.07 | 1.28 | -0.009389 | 3600 | 0.58 | 3600 | 0.58 | 1.07 | 1.28 | -0.00939
LFAllSpcSDGNrsExCZ08 | Com-Iltg-dWatt-LF_OSspc | SDG | Nrs | Ex | CZ08 | 3.6004 | 0.00058008 | 0 | 3.92 | 0.00075308 | -0.036 | 3.6004 | 0.00058008 | 0 | 3.92 | 0.00075308 | -0.036 |  | LF | AllSpc | 3600 | 0.58 | 3600 | 0.58 | 1.09 | 1.3 | -0.0099989 | 3600 | 0.58 | 3600 | 0.58 | 1.09 | 1.3 | -0.01
LFAllSpcSDGNrsExCZ10 | Com-Iltg-dWatt-LF_OSspc | SDG | Nrs | Ex | CZ10 | 3.6004 | 0.00058008 | 0 | 3.9304 | 0.00078404 | -0.0382 | 3.6004 | 0.00058008 | 0 | 3.9304 | 0.00078404 | -0.0382 |  | LF | AllSpc | 3600 | 0.58 | 3600 | 0.58 | 1.09 | 1.35 | -0.01061 | 3600 | 0.58 | 3600 | 0.58 | 1.09 | 1.35 | -0.0106
LFAllSpcSDGNrsExCZ14 | Com-Iltg-dWatt-LF_OSspc | SDG | Nrs | Ex | CZ14 | 3.6005 | 0.0005801 | 0 | 3.8805 | 0.0007691 | -0.044605 | 3.6005 | 0.0005801 | 0 | 3.8805 | 0.0007691 | -0.044605 |  | LF | AllSpc | 3600 | 0.58 | 3600 | 0.58 | 1.08 | 1.33 | -0.012389 | 3600 | 0.58 | 3600 | 0.58 | 1.08 | 1.33 | -0.0124
LFAllSpcSDGNrsExIOU | Com-Iltg-dWatt-LF_OSspc | SDG | Nrs | Ex | IOU | 3.6004 | 0.00058008 | 0 | 3.8728 | 0.0007504 | -0.034606 | 3.6004 | 0.00058008 | 0 | 3.8728 | 0.0007504 | -0.034606 |  | LF | AllSpc | 3600 | 0.58 | 3600 | 0.58 | 1.08 | 1.29 | -0.0096117 | 3600 | 0.58 | 3600 | 0.58 | 1.08 | 1.29 | -0.00961
LFAllSpcSDGNrsNewCZ06 | Com-Iltg-dWatt-LF_OSspc | SDG | Nrs | New | CZ06 | 3.61 | 0.000582 | 0 | 3.73 | 0.000744 | -0.0418 | 3.61 | 0.000582 | 0 | 3.73 | 0.000744 | -0.0418 |  | LF | AllSpc | 3610 | 0.582 | 3610 | 0.582 | 1.03 | 1.28 | -0.011579 | 3610 | 0.582 | 3610 | 0.582 | 1.03 | 1.28 | -0.0116
LFAllSpcSDGNrsNewCZ07 | Com-Iltg-dWatt-LF_OSspc | SDG | Nrs | New | CZ07 | 3.61 | 0.000582 | 0 | 3.69 | 0.000747 | -0.0397 | 3.61 | 0.000582 | 0 | 3.69 | 0.000747 | -0.0397 |  | LF | AllSpc | 3610 | 0.582 | 3610 | 0.582 | 1.02 | 1.28 | -0.010997 | 3610 | 0.582 | 3610 | 0.582 | 1.02 | 1.28 | -0.011
LFAllSpcSDGNrsNewCZ08 | Com-Iltg-dWatt-LF_OSspc | SDG | Nrs | New | CZ08 | 3.61 | 0.000582 | 0 | 3.8 | 0.000749 | -0.0393 | 3.61 | 0.000582 | 0 | 3.8 | 0.000749 | -0.0393 |  | LF | AllSpc | 3610 | 0.582 | 3610 | 0.582 | 1.05 | 1.29 | -0.010886 | 3610 | 0.582 | 3610 | 0.582 | 1.05 | 1.29 | -0.0109
LFAllSpcSDGNrsNewCZ10 | Com-Iltg-dWatt-LF_OSspc | SDG | Nrs | New | CZ10 | 3.61 | 0.000582 | 0 | 3.84 | 0.00078 | -0.0372 | 3.61 | 0.000582 | 0 | 3.84 | 0.00078 | -0.0372 |  | LF | AllSpc | 3610 | 0.582 | 3610 | 0.582 | 1.06 | 1.34 | -0.010305 | 3610 | 0.582 | 3610 | 0.582 | 1.06 | 1.34 | -0.0103
LFAllSpcSDGNrsNewCZ14 | Com-Iltg-dWatt-LF_OSspc | SDG | Nrs | New | CZ14 | 3.61 | 0.000582 | 0 | 3.81 | 0.000755 | -0.0491 | 3.61 | 0.000582 | 0 | 3.81 | 0.000755 | -0.0491 |  | LF | AllSpc | 3610 | 0.582 | 3610 | 0.582 | 1.06 | 1.3 | -0.013601 | 3610 | 0.582 | 3610 | 0.582 | 1.06 | 1.3 | -0.0136
LFAllSpcSDGNrsNewCZ15 | Com-Iltg-dWatt-LF_OSspc | SDG | Nrs | New | CZ15 | 3.61 | 0.000582 | 0 | 4.14 | 0.000774 | -0.0227 | 3.61 | 0.000582 | 0 | 4.14 | 0.000774 | -0.0227 |  | LF | AllSpc | 3610 | 0.582 | 3610 | 0.582 | 1.15 | 1.33 | -0.0062881 | 3610 | 0.582 | 3610 | 0.582 | 1.15 | 1.33 | -0.00629
LFAllSpcSDGNrsNewIOU | Com-Iltg-dWatt-LF_OSspc | SDG | Nrs | New | IOU | 3.61 | 0.000582 | 0 | 3.717 | 0.00075166 | -0.039389 | 3.61 | 0.000582 | 0 | 3.717 | 0.00075166 | -0.039389 |  | LF | AllSpc | 3610 | 0.582 | 3610 | 0.582 | 1.03 | 1.29 | -0.010911 | 3610 | 0.582 | 3610 | 0.582 | 1.03 | 1.29 | -0.0109
LFAllSpcSDGOfLExCZ06 | Com-Iltg-dWatt-LF_OSspc | SDG | OfL | Ex | CZ06 | 2.11 | 0.00057595 | 0 | 2.45 | 0.00073295 | -0.0048095 | 2.11 | 0.00057595 | 0 | 2.45 | 0.00073295 | -0.0048095 |  | LF | AllSpc | 2110 | 0.576 | 2110 | 0.576 | 1.16 | 1.27 | -0.0022794 | 2110 | 0.576 | 2110 | 0.576 | 1.16 | 1.27 | -0.00228
LFAllSpcSDGOfLExCZ07 | Com-Iltg-dWatt-LF_OSspc | SDG | OfL | Ex | CZ07 | 2.11 | 0.00057595 | 0 | 2.44 | 0.00072495 | -0.00426 | 2.11 | 0.00057595 | 0 | 2.44 | 0.00072495 | -0.00426 |  | LF | AllSpc | 2110 | 0.576 | 2110 | 0.576 | 1.16 | 1.26 | -0.002019 | 2110 | 0.576 | 2110 | 0.576 | 1.16 | 1.26 | -0.00202
LFAllSpcSDGOfLExCZ08 | Com-Iltg-dWatt-LF_OSspc | SDG | OfL | Ex | CZ08 | 2.11 | 0.00057595 | 0 | 2.46 | 0.00073995 | -0.00478 | 2.11 | 0.00057595 | 0 | 2.46 | 0.00073995 | -0.00478 |  | LF | AllSpc | 2110 | 0.576 | 2110 | 0.576 | 1.17 | 1.28 | -0.0022654 | 2110 | 0.576 | 2110 | 0.576 | 1.17 | 1.28 | -0.00227
LFAllSpcSDGOfLExCZ10 | Com-Iltg-dWatt-LF_OSspc | SDG | OfL | Ex | CZ10 | 2.11 | 0.00057595 | 0 | 2.45 | 0.00075095 | -0.00563 | 2.11 | 0.00057595 | 0 | 2.45 | 0.00075095 | -0.00563 |  | LF | AllSpc | 2110 | 0.576 | 2110 | 0.576 | 1.16 | 1.3 | -0.0026682 | 2110 | 0.576 | 2110 | 0.576 | 1.16 | 1.3 | -0.00267
LFAllSpcSDGOfLExCZ14 | Com-Iltg-dWatt-LF_OSspc | SDG | OfL | Ex | CZ14 | 2.11 | 0.00057595 | 0 | 2.42 | 0.00074695 | -0.00704 | 2.11 | 0.00057595 | 0 | 2.42 | 0.00074695 | -0.00704 |  | LF | AllSpc | 2110 | 0.576 | 2110 | 0.576 | 1.15 | 1.3 | -0.0033365 | 2110 | 0.576 | 2110 | 0.576 | 1.15 | 1.3 | -0.00334
LFAllSpcSDGOfLExCZ15 | Com-Iltg-dWatt-LF_OSspc | SDG | OfL | Ex | CZ15 | 2.11 | 0.00057595 | 0 | 2.57 | 0.00075495 | -0.00327 | 2.11 | 0.00057595 | 0 | 2.57 | 0.00075495 | -0.00327 |  | LF | AllSpc | 2110 | 0.576 | 2110 | 0.576 | 1.22 | 1.31 | -0.0015498 | 2110 | 0.576 | 2110 | 0.576 | 1.22 | 1.31 | -0.00155
LFAllSpcSDGOfLExIOU | Com-Iltg-dWatt-LF_OSspc | SDG | OfL | Ex | IOU | 2.11 | 0.00057595 | 0 | 2.4424 | 0.00073006 | -0.0045304 | 2.11 | 0.00057595 | 0 | 2.4424 | 0.00073006 | -0.0045304 |  | LF | AllSpc | 2110 | 0.576 | 2110 | 0.576 | 1.16 | 1.27 | -0.0021471 | 2110 | 0.576 | 2110 | 0.576 | 1.16 | 1.27 | -0.00215
LFAllSpcSDGOfLNewCZ06 | Com-Iltg-dWatt-LF_OSspc | SDG | OfL | New | CZ06 | 2.11 | 0.000575 | 0 | 2.45 | 0.000724 | -0.00282 | 2.11 | 0.000575 | 0 | 2.45 | 0.000724 | -0.00282 |  | LF | AllSpc | 2110 | 0.575 | 2110 | 0.575 | 1.16 | 1.26 | -0.0013365 | 2110 | 0.575 | 2110 | 0.575 | 1.16 | 1.26 | -0.00134
LFAllSpcSDGOfLNewCZ07 | Com-Iltg-dWatt-LF_OSspc | SDG | OfL | New | CZ07 | 2.11 | 0.000575 | 0 | 2.44 | 0.000713 | -0.00195 | 2.11 | 0.000575 | 0 | 2.44 | 0.000713 | -0.00195 |  | LF | AllSpc | 2110 | 0.575 | 2110 | 0.575 | 1.16 | 1.24 | -0.00092417 | 2110 | 0.575 | 2110 | 0.575 | 1.16 | 1.24 | -0.000924
LFAllSpcSDGOfLNewCZ08 | Com-Iltg-dWatt-LF_OSspc | SDG | OfL | New | CZ08 | 2.11 | 0.000575 | 0 | 2.46 | 0.000734 | -0.00251 | 2.11 | 0.000575 | 0 | 2.46 | 0.000734 | -0.00251 |  | LF | AllSpc | 2110 | 0.575 | 2110 | 0.575 | 1.17 | 1.28 | -0.0011896 | 2110 | 0.575 | 2110 | 0.575 | 1.17 | 1.28 | -0.00119
LFAllSpcSDGOfLNewCZ10 | Com-Iltg-dWatt-LF_OSspc | SDG | OfL | New | CZ10 | 2.11 | 0.000575 | 0 | 2.48 | 0.000755 | -0.00278 | 2.11 | 0.000575 | 0 | 2.48 | 0.000755 | -0.00278 |  | LF | AllSpc | 2110 | 0.575 | 2110 | 0.575 | 1.18 | 1.31 | -0.0013175 | 2110 | 0.575 | 2110 | 0.575 | 1.18 | 1.31 | -0.00132
LFAllSpcSDGOfLNewCZ14 | Com-Iltg-dWatt-LF_OSspc | SDG | OfL | New | CZ14 | 2.11 | 0.000575 | 0 | 2.44 | 0.000761 | -0.00407 | 2.11 | 0.000575 | 0 | 2.44 | 0.000761 | -0.00407 |  | LF | AllSpc | 2110 | 0.575 | 2110 | 0.575 | 1.16 | 1.32 | -0.0019289 | 2110 | 0.575 | 2110 | 0.575 | 1.16 | 1.32 | -0.00193
LFAllSpcSDGOfLNewCZ15 | Com-Iltg-dWatt-LF_OSspc | SDG | OfL | New | CZ15 | 2.11 | 0.000575 | 0 | 2.58 | 0.000756 | -0.00144 | 2.11 | 0.000575 | 0 | 2.58 | 0.000756 | -0.00144 |  | LF | AllSpc | 2110 | 0.575 | 2110 | 0.575 | 1.22 | 1.31 | -0.00068246 | 2110 | 0.575 | 2110 | 0.575 | 1.22 | 1.31 | -0.000682
LFAllSpcSDGOfLNewIOU | Com-Iltg-dWatt-LF_OSspc | SDG | OfL | New | IOU | 2.11 | 0.000575 | 0 | 2.4477 | 0.00072121 | -0.0021324 | 2.11 | 0.000575 | 0 | 2.4477 | 0.00072121 | -0.0021324 |  | LF | AllSpc | 2110 | 0.575 | 2110 | 0.575 | 1.16 | 1.25 | -0.0010106 | 2110 | 0.575 | 2110 | 0.575 | 1.16 | 1.25 | -0.00101
LFAllSpcSDGOfSExCZ06 | Com-Iltg-dWatt-LF_OSspc | SDG | OfS | Ex | CZ06 | 1.8705 | 0.00051405 | 0 | 2.1605 | 0.00064405 | -0.0014505 | 1.8705 | 0.00051405 | 0 | 2.1605 | 0.00064405 | -0.0014505 |  | LF | AllSpc | 1870 | 0.514 | 1870 | 0.514 | 1.16 | 1.25 | -0.00077546 | 1870 | 0.514 | 1870 | 0.514 | 1.16 | 1.25 | -0.000775
LFAllSpcSDGOfSExCZ07 | Com-Iltg-dWatt-LF_OSspc | SDG | OfS | Ex | CZ07 | 1.8705 | 0.00051405 | 0 | 2.1705 | 0.00063809 | -0.00041409 | 1.8705 | 0.00051405 | 0 | 2.1705 | 0.00063809 | -0.00041409 |  | LF | AllSpc | 1870 | 0.514 | 1870 | 0.514 | 1.16 | 1.24 | -0.00022138 | 1870 | 0.514 | 1870 | 0.514 | 1.16 | 1.24 | -0.000221
LFAllSpcSDGOfSExCZ08 | Com-Iltg-dWatt-LF_OSspc | SDG | OfS | Ex | CZ08 | 1.8705 | 0.00051405 | 0 | 2.18 | 0.00064809 | -0.00125 | 1.8705 | 0.00051405 | 0 | 2.18 | 0.00064809 | -0.00125 |  | LF | AllSpc | 1870 | 0.514 | 1870 | 0.514 | 1.17 | 1.26 | -0.00066828 | 1870 | 0.514 | 1870 | 0.514 | 1.17 | 1.26 | -0.000668
LFAllSpcSDGOfSExCZ10 | Com-Iltg-dWatt-LF_OSspc | SDG | OfS | Ex | CZ10 | 1.8705 | 0.00051405 | 0 | 2.1705 | 0.00065109 | -0.0018905 | 1.8705 | 0.00051405 | 0 | 2.1705 | 0.00065109 | -0.0018905 |  | LF | AllSpc | 1870 | 0.514 | 1870 | 0.514 | 1.16 | 1.27 | -0.0010107 | 1870 | 0.514 | 1870 | 0.514 | 1.16 | 1.27 | -0.00101
LFAllSpcSDGOfSExCZ14 | Com-Iltg-dWatt-LF_OSspc | SDG | OfS | Ex | CZ14 | 1.8705 | 0.00051405 | 0 | 2.1105 | 0.00065905 | -0.0046905 | 1.8705 | 0.00051405 | 0 | 2.1105 | 0.00065905 | -0.0046905 |  | LF | AllSpc | 1870 | 0.514 | 1870 | 0.514 | 1.13 | 1.28 | -0.0025076 | 1870 | 0.514 | 1870 | 0.514 | 1.13 | 1.28 | -0.00251
LFAllSpcSDGOfSExCZ15 | Com-Iltg-dWatt-LF_OSspc | SDG | OfS | Ex | CZ15 | 1.8705 | 0.00051405 | 0 | 2.3005 | 0.00064909 | -0.00038805 | 1.8705 | 0.00051405 | 0 | 2.3005 | 0.00064909 | -0.00038805 |  | LF | AllSpc | 1870 | 0.514 | 1870 | 0.514 | 1.23 | 1.26 | -0.00020746 | 1870 | 0.514 | 1870 | 0.514 | 1.23 | 1.26 | -0.000207
LFAllSpcSDGOfSExIOU | Com-Iltg-dWatt-LF_OSspc | SDG | OfS | Ex | IOU | 1.8705 | 0.00051405 | 0 | 2.1704 | 0.00064078 | -0.00072753 | 1.8705 | 0.00051405 | 0 | 2.1704 | 0.00064078 | -0.00072753 |  | LF | AllSpc | 1870 | 0.514 | 1870 | 0.514 | 1.16 | 1.25 | -0.00038895 | 1870 | 0.514 | 1870 | 0.514 | 1.16 | 1.25 | -0.000389
LFAllSpcSDGOfSNewCZ06 | Com-Iltg-dWatt-LF_OSspc | SDG | OfS | New | CZ06 | 1.88 | 0.000515 | 0 | 2.08 | 0.000636 | -0.00149 | 1.88 | 0.000515 | 0 | 2.08 | 0.000636 | -0.00149 |  | LF | AllSpc | 1880 | 0.515 | 1880 | 0.515 | 1.11 | 1.23 | -0.00079255 | 1880 | 0.515 | 1880 | 0.515 | 1.11 | 1.23 | -0.000793
LFAllSpcSDGOfSNewCZ07 | Com-Iltg-dWatt-LF_OSspc | SDG | OfS | New | CZ07 | 1.88 | 0.000515 | 0 | 2.07 | 0.000628 | -0.00034 | 1.88 | 0.000515 | 0 | 2.07 | 0.000628 | -0.00034 |  | LF | AllSpc | 1880 | 0.515 | 1880 | 0.515 | 1.1 | 1.22 | -0.00018085 | 1880 | 0.515 | 1880 | 0.515 | 1.1 | 1.22 | -0.000181
LFAllSpcSDGOfSNewCZ08 | Com-Iltg-dWatt-LF_OSspc | SDG | OfS | New | CZ08 | 1.88 | 0.000515 | 0 | 2.1 | 0.000645 | -0.00128 | 1.88 | 0.000515 | 0 | 2.1 | 0.000645 | -0.00128 |  | LF | AllSpc | 1880 | 0.515 | 1880 | 0.515 | 1.12 | 1.25 | -0.00068085 | 1880 | 0.515 | 1880 | 0.515 | 1.12 | 1.25 | -0.000681
LFAllSpcSDGOfSNewCZ10 | Com-Iltg-dWatt-LF_OSspc | SDG | OfS | New | CZ10 | 1.88 | 0.000515 | 0 | 2.12 | 0.000667 | -0.00101 | 1.88 | 0.000515 | 0 | 2.12 | 0.000667 | -0.00101 |  | LF | AllSpc | 1880 | 0.515 | 1880 | 0.515 | 1.13 | 1.3 | -0.00053723 | 1880 | 0.515 | 1880 | 0.515 | 1.13 | 1.3 | -0.000537
LFAllSpcSDGOfSNewCZ14 | Com-Iltg-dWatt-LF_OSspc | SDG | OfS | New | CZ14 | 1.88 | 0.000515 | 0 | 2.07 | 0.000666 | -0.00391 | 1.88 | 0.000515 | 0 | 2.07 | 0.000666 | -0.00391 |  | LF | AllSpc | 1880 | 0.515 | 1880 | 0.515 | 1.1 | 1.29 | -0.0020798 | 1880 | 0.515 | 1880 | 0.515 | 1.1 | 1.29 | -0.00208
LFAllSpcSDGOfSNewCZ15 | Com-Iltg-dWatt-LF_OSspc | SDG | OfS | New | CZ15 | 1.88 | 0.000515 | 0 | 2.22 | 0.000674 | 0 | 1.88 | 0.000515 | 0 | 2.22 | 0.000674 | 0 |  | LF | AllSpc | 1880 | 0.515 | 1880 | 0.515 | 1.18 | 1.31 | 0 | 1880 | 0.515 | 1880 | 0.515 | 1.18 | 1.31 | 0
LFAllSpcSDGOfSNewIOU | Com-Iltg-dWatt-LF_OSspc | SDG | OfS | New | IOU | 1.88 | 0.000515 | 0 | 2.0797 | 0.0006355 | -0.0005149 | 1.88 | 0.000515 | 0 | 2.0797 | 0.0006355 | -0.0005149 |  | LF | AllSpc | 1880 | 0.515 | 1880 | 0.515 | 1.11 | 1.23 | -0.00027389 | 1880 | 0.515 | 1880 | 0.515 | 1.11 | 1.23 | -0.000274
LFAllSpcSDGRFFExCZ06 | Com-Iltg-dWatt-LF_OSspc | SDG | RFF | Ex | CZ06 | 4.02 | 0.000691 | 0 | 4.48 | 0.000853 | -0.0231 | 4.02 | 0.000691 | 0 | 4.48 | 0.000853 | -0.0231 |  | LF | AllSpc | 4020 | 0.691 | 4020 | 0.691 | 1.11 | 1.23 | -0.0057463 | 4020 | 0.691 | 4020 | 0.691 | 1.11 | 1.23 | -0.00575
LFAllSpcSDGRFFExCZ07 | Com-Iltg-dWatt-LF_OSspc | SDG | RFF | Ex | CZ07 | 4.02 | 0.000691 | 0 | 4.49 | 0.000848 | -0.0211 | 4.02 | 0.000691 | 0 | 4.49 | 0.000848 | -0.0211 |  | LF | AllSpc | 4020 | 0.691 | 4020 | 0.691 | 1.12 | 1.23 | -0.0052488 | 4020 | 0.691 | 4020 | 0.691 | 1.12 | 1.23 | -0.00525
LFAllSpcSDGRFFExCZ08 | Com-Iltg-dWatt-LF_OSspc | SDG | RFF | Ex | CZ08 | 4.02 | 0.000691 | 0 | 4.52 | 0.000846 | -0.0205 | 4.02 | 0.000691 | 0 | 4.52 | 0.000846 | -0.0205 |  | LF | AllSpc | 4020 | 0.691 | 4020 | 0.691 | 1.12 | 1.22 | -0.0050995 | 4020 | 0.691 | 4020 | 0.691 | 1.12 | 1.22 | -0.0051
LFAllSpcSDGRFFExCZ10 | Com-Iltg-dWatt-LF_OSspc | SDG | RFF | Ex | CZ10 | 4.02 | 0.000691 | 0 | 4.52 | 0.00086 | -0.0227 | 4.02 | 0.000691 | 0 | 4.52 | 0.00086 | -0.0227 |  | LF | AllSpc | 4020 | 0.691 | 4020 | 0.691 | 1.12 | 1.24 | -0.0056468 | 4020 | 0.691 | 4020 | 0.691 | 1.12 | 1.24 | -0.00565
LFAllSpcSDGRFFExCZ14 | Com-Iltg-dWatt-LF_OSspc | SDG | RFF | Ex | CZ14 | 4.02 | 0.000691 | 0 | 4.43 | 0.000875 | -0.0323 | 4.02 | 0.000691 | 0 | 4.43 | 0.000875 | -0.0323 |  | LF | AllSpc | 4020 | 0.691 | 4020 | 0.691 | 1.1 | 1.27 | -0.0080348 | 4020 | 0.691 | 4020 | 0.691 | 1.1 | 1.27 | -0.00803
LFAllSpcSDGRFFExCZ15 | Com-Iltg-dWatt-LF_OSspc | SDG | RFF | Ex | CZ15 | 4.02 | 0.000691 | 0 | 4.8 | 0.000869 | -0.0104 | 4.02 | 0.000691 | 0 | 4.8 | 0.000869 | -0.0104 |  | LF | AllSpc | 4020 | 0.691 | 4020 | 0.691 | 1.19 | 1.26 | -0.0025871 | 4020 | 0.691 | 4020 | 0.691 | 1.19 | 1.26 | -0.00259
LFAllSpcSDGRFFExIOU | Com-Iltg-dWatt-LF_OSspc | SDG | RFF | Ex | IOU | 4.02 | 0.000691 | 0 | 4.4972 | 0.00085088 | -0.021537 | 4.02 | 0.000691 | 0 | 4.4972 | 0.00085088 | -0.021537 |  | LF | AllSpc | 4020 | 0.691 | 4020 | 0.691 | 1.12 | 1.23 | -0.0053575 | 4020 | 0.691 | 4020 | 0.691 | 1.12 | 1.23 | -0.00536
LFAllSpcSDGRFFNewCZ06 | Com-Iltg-dWatt-LF_OSspc | SDG | RFF | New | CZ06 | 4.02 | 0.000691 | 0 | 4.34 | 0.00087 | -0.0229 | 4.02 | 0.000691 | 0 | 4.34 | 0.00087 | -0.0229 |  | LF | AllSpc | 4020 | 0.691 | 4020 | 0.691 | 1.08 | 1.26 | -0.0056965 | 4020 | 0.691 | 4020 | 0.691 | 1.08 | 1.26 | -0.0057
LFAllSpcSDGRFFNewCZ07 | Com-Iltg-dWatt-LF_OSspc | SDG | RFF | New | CZ07 | 4.02 | 0.000691 | 0 | 4.31 | 0.000862 | -0.0262 | 4.02 | 0.000691 | 0 | 4.31 | 0.000862 | -0.0262 |  | LF | AllSpc | 4020 | 0.691 | 4020 | 0.691 | 1.07 | 1.25 | -0.0065174 | 4020 | 0.691 | 4020 | 0.691 | 1.07 | 1.25 | -0.00652
LFAllSpcSDGRFFNewCZ08 | Com-Iltg-dWatt-LF_OSspc | SDG | RFF | New | CZ08 | 4.02 | 0.000691 | 0 | 4.41 | 0.000875 | -0.0249 | 4.02 | 0.000691 | 0 | 4.41 | 0.000875 | -0.0249 |  | LF | AllSpc | 4020 | 0.691 | 4020 | 0.691 | 1.1 | 1.27 | -0.006194 | 4020 | 0.691 | 4020 | 0.691 | 1.1 | 1.27 | -0.00619
LFAllSpcSDGRFFNewCZ10 | Com-Iltg-dWatt-LF_OSspc | SDG | RFF | New | CZ10 | 4.02 | 0.000691 | 0 | 4.46 | 0.000913 | -0.0275 | 4.02 | 0.000691 | 0 | 4.46 | 0.000913 | -0.0275 |  | LF | AllSpc | 4020 | 0.691 | 4020 | 0.691 | 1.11 | 1.32 | -0.0068408 | 4020 | 0.691 | 4020 | 0.691 | 1.11 | 1.32 | -0.00684
LFAllSpcSDGRFFNewCZ14 | Com-Iltg-dWatt-LF_OSspc | SDG | RFF | New | CZ14 | 4.02 | 0.000691 | 0 | 4.43 | 0.000916 | -0.039 | 4.02 | 0.000691 | 0 | 4.43 | 0.000916 | -0.039 |  | LF | AllSpc | 4020 | 0.691 | 4020 | 0.691 | 1.1 | 1.33 | -0.0097015 | 4020 | 0.691 | 4020 | 0.691 | 1.1 | 1.33 | -0.0097
LFAllSpcSDGRFFNewCZ15 | Com-Iltg-dWatt-LF_OSspc | SDG | RFF | New | CZ15 | 4.02 | 0.000691 | 0 | 4.78 | 0.000929 | -0.0136 | 4.02 | 0.000691 | 0 | 4.78 | 0.000929 | -0.0136 |  | LF | AllSpc | 4020 | 0.691 | 4020 | 0.691 | 1.19 | 1.34 | -0.0033831 | 4020 | 0.691 | 4020 | 0.691 | 1.19 | 1.34 | -0.00338
LFAllSpcSDGRFFNewIOU | Com-Iltg-dWatt-LF_OSspc | SDG | RFF | New | IOU | 4.02 | 0.000691 | 0 | 4.3481 | 0.00087414 | -0.026308 | 4.02 | 0.000691 | 0 | 4.3481 | 0.00087414 | -0.026308 |  | LF | AllSpc | 4020 | 0.691 | 4020 | 0.691 | 1.08 | 1.27 | -0.0065442 | 4020 | 0.691 | 4020 | 0.691 | 1.08 | 1.27 | -0.00654
LFAllSpcSDGRSDExCZ06 | Com-Iltg-dWatt-LF_OSspc | SDG | RSD | Ex | CZ06 | 3.87 | 0.000679 | 0 | 4.35 | 0.00085 | -0.0245 | 3.87 | 0.000679 | 0 | 4.35 | 0.00085 | -0.0245 |  | LF | AllSpc | 3870 | 0.679 | 3870 | 0.679 | 1.12 | 1.25 | -0.0063307 | 3870 | 0.679 | 3870 | 0.679 | 1.12 | 1.25 | -0.00633
LFAllSpcSDGRSDExCZ07 | Com-Iltg-dWatt-LF_OSspc | SDG | RSD | Ex | CZ07 | 3.8713 | 0.00067913 | 0 | 4.3513 | 0.00086227 | -0.0225 | 3.8713 | 0.00067913 | 0 | 4.3513 | 0.00086227 | -0.0225 |  | LF | AllSpc | 3870 | 0.679 | 3870 | 0.679 | 1.12 | 1.27 | -0.0058119 | 3870 | 0.679 | 3870 | 0.679 | 1.12 | 1.27 | -0.00581
LFAllSpcSDGRSDExCZ08 | Com-Iltg-dWatt-LF_OSspc | SDG | RSD | Ex | CZ08 | 3.87 | 0.000679 | 0 | 4.38 | 0.000823 | -0.0203 | 3.87 | 0.000679 | 0 | 4.38 | 0.000823 | -0.0203 |  | LF | AllSpc | 3870 | 0.679 | 3870 | 0.679 | 1.13 | 1.21 | -0.0052455 | 3870 | 0.679 | 3870 | 0.679 | 1.13 | 1.21 | -0.00525
LFAllSpcSDGRSDExCZ10 | Com-Iltg-dWatt-LF_OSspc | SDG | RSD | Ex | CZ10 | 3.87 | 0.000679 | 0 | 4.34 | 0.000783 | -0.0239 | 3.87 | 0.000679 | 0 | 4.34 | 0.000783 | -0.0239 |  | LF | AllSpc | 3870 | 0.679 | 3870 | 0.679 | 1.12 | 1.15 | -0.0061757 | 3870 | 0.679 | 3870 | 0.679 | 1.12 | 1.15 | -0.00618
LFAllSpcSDGRSDExCZ14 | Com-Iltg-dWatt-LF_OSspc | SDG | RSD | Ex | CZ14 | 3.87 | 0.000679 | 0 | 4.2 | 0.000782 | -0.0391 | 3.87 | 0.000679 | 0 | 4.2 | 0.000782 | -0.0391 |  | LF | AllSpc | 3870 | 0.679 | 3870 | 0.679 | 1.09 | 1.15 | -0.010103 | 3870 | 0.679 | 3870 | 0.679 | 1.09 | 1.15 | -0.0101
LFAllSpcSDGRSDExCZ15 | Com-Iltg-dWatt-LF_OSspc | SDG | RSD | Ex | CZ15 | 3.87 | 0.000679 | 0 | 4.68 | 0.000873 | -0.0091 | 3.87 | 0.000679 | 0 | 4.68 | 0.000873 | -0.0091 |  | LF | AllSpc | 3870 | 0.679 | 3870 | 0.679 | 1.21 | 1.29 | -0.0023514 | 3870 | 0.679 | 3870 | 0.679 | 1.21 | 1.29 | -0.00235
LFAllSpcSDGRSDExIOU | Com-Iltg-dWatt-LF_OSspc | SDG | RSD | Ex | IOU | 3.8709 | 0.00067909 | 0 | 4.3497 | 0.00084294 | -0.022853 | 3.8709 | 0.00067909 | 0 | 4.3497 | 0.00084294 | -0.022853 |  | LF | AllSpc | 3870 | 0.679 | 3870 | 0.679 | 1.12 | 1.24 | -0.0059037 | 3870 | 0.679 | 3870 | 0.679 | 1.12 | 1.24 | -0.0059
LFAllSpcSDGRSDNewCZ06 | Com-Iltg-dWatt-LF_OSspc | SDG | RSD | New | CZ06 | 3.87 | 0.000679 | 0 | 4.22 | 0.00086 | -0.0297 | 3.87 | 0.000679 | 0 | 4.22 | 0.00086 | -0.0297 |  | LF | AllSpc | 3870 | 0.679 | 3870 | 0.679 | 1.09 | 1.27 | -0.0076744 | 3870 | 0.679 | 3870 | 0.679 | 1.09 | 1.27 | -0.00767
LFAllSpcSDGRSDNewCZ07 | Com-Iltg-dWatt-LF_OSspc | SDG | RSD | New | CZ07 | 3.87 | 0.000679 | 0 | 4.2 | 0.00087 | -0.0282 | 3.87 | 0.000679 | 0 | 4.2 | 0.00087 | -0.0282 |  | LF | AllSpc | 3870 | 0.679 | 3870 | 0.679 | 1.09 | 1.28 | -0.0072868 | 3870 | 0.679 | 3870 | 0.679 | 1.09 | 1.28 | -0.00729
LFAllSpcSDGRSDNewCZ08 | Com-Iltg-dWatt-LF_OSspc | SDG | RSD | New | CZ08 | 3.87 | 0.000679 | 0 | 4.28 | 0.000864 | -0.0244 | 3.87 | 0.000679 | 0 | 4.28 | 0.000864 | -0.0244 |  | LF | AllSpc | 3870 | 0.679 | 3870 | 0.679 | 1.11 | 1.27 | -0.0063049 | 3870 | 0.679 | 3870 | 0.679 | 1.11 | 1.27 | -0.0063
LFAllSpcSDGRSDNewCZ10 | Com-Iltg-dWatt-LF_OSspc | SDG | RSD | New | CZ10 | 3.87 | 0.000679 | 0 | 4.32 | 0.000905 | -0.0265 | 3.87 | 0.000679 | 0 | 4.32 | 0.000905 | -0.0265 |  | LF | AllSpc | 3870 | 0.679 | 3870 | 0.679 | 1.12 | 1.33 | -0.0068475 | 3870 | 0.679 | 3870 | 0.679 | 1.12 | 1.33 | -0.00685
LFAllSpcSDGRSDNewCZ14 | Com-Iltg-dWatt-LF_OSspc | SDG | RSD | New | CZ14 | 3.87 | 0.000679 | 0 | 4.22 | 0.000903 | -0.0426 | 3.87 | 0.000679 | 0 | 4.22 | 0.000903 | -0.0426 |  | LF | AllSpc | 3870 | 0.679 | 3870 | 0.679 | 1.09 | 1.33 | -0.011008 | 3870 | 0.679 | 3870 | 0.679 | 1.09 | 1.33 | -0.011
LFAllSpcSDGRSDNewCZ15 | Com-Iltg-dWatt-LF_OSspc | SDG | RSD | New | CZ15 | 3.87 | 0.000679 | 0 | 4.66 | 0.000936 | -0.0119 | 3.87 | 0.000679 | 0 | 4.66 | 0.000936 | -0.0119 |  | LF | AllSpc | 3870 | 0.679 | 3870 | 0.679 | 1.2 | 1.38 | -0.0030749 | 3870 | 0.679 | 3870 | 0.679 | 1.2 | 1.38 | -0.00307
LFAllSpcSDGRSDNewIOU | Com-Iltg-dWatt-LF_OSspc | SDG | RSD | New | IOU | 3.87 | 0.000679 | 0 | 4.2302 | 0.00087717 | -0.027792 | 3.87 | 0.000679 | 0 | 4.2302 | 0.00087717 | -0.027792 |  | LF | AllSpc | 3870 | 0.679 | 3870 | 0.679 | 1.09 | 1.29 | -0.0071814 | 3870 | 0.679 | 3870 | 0.679 | 1.09 | 1.29 | -0.00718
LFAllSpcSDGRt3ExCZ06 | Com-Iltg-dWatt-LF_OSspc | SDG | Rt3 | Ex | CZ06 | 3.34 | 0.00074923 | 0 | 3.8393 | 0.00091431 | -0.00319 | 3.34 | 0.00074923 | 0 | 3.8393 | 0.00091431 | -0.00319 |  | LF | AllSpc | 3340 | 0.749 | 3340 | 0.749 | 1.15 | 1.22 | -0.00095509 | 3340 | 0.749 | 3340 | 0.749 | 1.15 | 1.22 | -0.000955
LFAllSpcSDGRt3ExCZ07 | Com-Iltg-dWatt-LF_OSspc | SDG | Rt3 | Ex | CZ07 | 3.34 | 0.00074923 | 0 | 3.85 | 0.00090123 | -0.00138 | 3.34 | 0.00074923 | 0 | 3.85 | 0.00090123 | -0.00138 |  | LF | AllSpc | 3340 | 0.749 | 3340 | 0.749 | 1.15 | 1.2 | -0.00041317 | 3340 | 0.749 | 3340 | 0.749 | 1.15 | 1.2 | -0.000413
LFAllSpcSDGRt3ExCZ08 | Com-Iltg-dWatt-LF_OSspc | SDG | Rt3 | Ex | CZ08 | 3.34 | 0.00074923 | 0 | 3.85 | 0.00090531 | -0.00285 | 3.34 | 0.00074923 | 0 | 3.85 | 0.00090531 | -0.00285 |  | LF | AllSpc | 3340 | 0.749 | 3340 | 0.749 | 1.15 | 1.21 | -0.00085329 | 3340 | 0.749 | 3340 | 0.749 | 1.15 | 1.21 | -0.000853
LFAllSpcSDGRt3ExCZ10 | Com-Iltg-dWatt-LF_OSspc | SDG | Rt3 | Ex | CZ10 | 3.34 | 0.00074923 | 0 | 3.81 | 0.00091823 | -0.00521 | 3.34 | 0.00074923 | 0 | 3.81 | 0.00091823 | -0.00521 |  | LF | AllSpc | 3340 | 0.749 | 3340 | 0.749 | 1.14 | 1.23 | -0.0015599 | 3340 | 0.749 | 3340 | 0.749 | 1.14 | 1.23 | -0.00156
LFAllSpcSDGRt3ExCZ14 | Com-Iltg-dWatt-LF_OSspc | SDG | Rt3 | Ex | CZ14 | 3.34 | 0.00074924 | 0 | 3.64 | 0.00092424 | -0.019 | 3.34 | 0.00074924 | 0 | 3.64 | 0.00092424 | -0.019 |  | LF | AllSpc | 3340 | 0.749 | 3340 | 0.749 | 1.09 | 1.23 | -0.0056886 | 3340 | 0.749 | 3340 | 0.749 | 1.09 | 1.23 | -0.00569
LFAllSpcSDGRt3ExCZ15 | Com-Iltg-dWatt-LF_OSspc | SDG | Rt3 | Ex | CZ15 | 3.34 | 0.00074923 | 0 | 3.94 | 0.00093762 | -0.00123 | 3.34 | 0.00074923 | 0 | 3.94 | 0.00093762 | -0.00123 |  | LF | AllSpc | 3340 | 0.749 | 3340 | 0.749 | 1.18 | 1.25 | -0.00036826 | 3340 | 0.749 | 3340 | 0.749 | 1.18 | 1.25 | -0.000368
LFAllSpcSDGRt3ExIOU | Com-Iltg-dWatt-LF_OSspc | SDG | Rt3 | Ex | IOU | 3.34 | 0.00074923 | 0 | 3.8397 | 0.00090613 | -0.0024861 | 3.34 | 0.00074923 | 0 | 3.8397 | 0.00090613 | -0.0024861 |  | LF | AllSpc | 3340 | 0.749 | 3340 | 0.749 | 1.15 | 1.21 | -0.00074433 | 3340 | 0.749 | 3340 | 0.749 | 1.15 | 1.21 | -0.000744
LFAllSpcSDGRt3NewCZ06 | Com-Iltg-dWatt-LF_OSspc | SDG | Rt3 | New | CZ06 | 3.34 | 0.000748 | 0 | 3.77 | 0.000926 | -0.00451 | 3.34 | 0.000748 | 0 | 3.77 | 0.000926 | -0.00451 |  | LF | AllSpc | 3340 | 0.748 | 3340 | 0.748 | 1.13 | 1.24 | -0.0013503 | 3340 | 0.748 | 3340 | 0.748 | 1.13 | 1.24 | -0.00135
LFAllSpcSDGRt3NewCZ07 | Com-Iltg-dWatt-LF_OSspc | SDG | Rt3 | New | CZ07 | 3.34 | 0.000748 | 0 | 3.76 | 0.000908 | -0.00174 | 3.34 | 0.000748 | 0 | 3.76 | 0.000908 | -0.00174 |  | LF | AllSpc | 3340 | 0.748 | 3340 | 0.748 | 1.13 | 1.21 | -0.00052096 | 3340 | 0.748 | 3340 | 0.748 | 1.13 | 1.21 | -0.000521
LFAllSpcSDGRt3NewCZ08 | Com-Iltg-dWatt-LF_OSspc | SDG | Rt3 | New | CZ08 | 3.34 | 0.000748 | 0 | 3.81 | 0.000933 | -0.00377 | 3.34 | 0.000748 | 0 | 3.81 | 0.000933 | -0.00377 |  | LF | AllSpc | 3340 | 0.748 | 3340 | 0.748 | 1.14 | 1.25 | -0.0011287 | 3340 | 0.748 | 3340 | 0.748 | 1.14 | 1.25 | -0.00113
LFAllSpcSDGRt3NewCZ10 | Com-Iltg-dWatt-LF_OSspc | SDG | Rt3 | New | CZ10 | 3.34 | 0.000748 | 0 | 3.76 | 0.000926 | -0.00695 | 3.34 | 0.000748 | 0 | 3.76 | 0.000926 | -0.00695 |  | LF | AllSpc | 3340 | 0.748 | 3340 | 0.748 | 1.13 | 1.24 | -0.0020808 | 3340 | 0.748 | 3340 | 0.748 | 1.13 | 1.24 | -0.00208
LFAllSpcSDGRt3NewCZ14 | Com-Iltg-dWatt-LF_OSspc | SDG | Rt3 | New | CZ14 | 3.34 | 0.000748 | 0 | 3.7 | 0.000965 | -0.0203 | 3.34 | 0.000748 | 0 | 3.7 | 0.000965 | -0.0203 |  | LF | AllSpc | 3340 | 0.748 | 3340 | 0.748 | 1.11 | 1.29 | -0.0060778 | 3340 | 0.748 | 3340 | 0.748 | 1.11 | 1.29 | -0.00608
LFAllSpcSDGRt3NewCZ15 | Com-Iltg-dWatt-LF_OSspc | SDG | Rt3 | New | CZ15 | 3.34 | 0.000748 | 0 | 3.76 | 0.00088 | -0.000698 | 3.34 | 0.000748 | 0 | 3.76 | 0.00088 | -0.000698 |  | LF | AllSpc | 3340 | 0.748 | 3340 | 0.748 | 1.13 | 1.18 | -0.00020898 | 3340 | 0.748 | 3340 | 0.748 | 1.13 | 1.18 | -0.000209
LFAllSpcSDGRt3NewIOU | Com-Iltg-dWatt-LF_OSspc | SDG | Rt3 | New | IOU | 3.34 | 0.000748 | 0 | 3.7633 | 0.00091458 | -0.0032514 | 3.34 | 0.000748 | 0 | 3.7633 | 0.00091458 | -0.0032514 |  | LF | AllSpc | 3340 | 0.748 | 3340 | 0.748 | 1.13 | 1.22 | -0.00097346 | 3340 | 0.748 | 3340 | 0.748 | 1.13 | 1.22 | -0.000973
LFAllSpcSDGRtLExCZ06 | Com-Iltg-dWatt-LF_OSspc | SDG | RtL | Ex | CZ06 | 4.23 | 0.00083893 | 0 | 4.7993 | 0.00103 | -0.0101 | 4.23 | 0.00083893 | 0 | 4.7993 | 0.00103 | -0.0101 |  | LF | AllSpc | 4230 | 0.839 | 4230 | 0.839 | 1.13 | 1.23 | -0.0023877 | 4230 | 0.839 | 4230 | 0.839 | 1.13 | 1.23 | -0.00239
LFAllSpcSDGRtLExCZ07 | Com-Iltg-dWatt-LF_OSspc | SDG | RtL | Ex | CZ07 | 4.23 | 0.00083893 | 0 | 4.8293 | 0.00103 | -0.0073693 | 4.23 | 0.00083893 | 0 | 4.8293 | 0.00103 | -0.0073693 |  | LF | AllSpc | 4230 | 0.839 | 4230 | 0.839 | 1.14 | 1.23 | -0.0017421 | 4230 | 0.839 | 4230 | 0.839 | 1.14 | 1.23 | -0.00174
LFAllSpcSDGRtLExCZ08 | Com-Iltg-dWatt-LF_OSspc | SDG | RtL | Ex | CZ08 | 4.23 | 0.00083893 | 0 | 4.8193 | 0.00103 | -0.0087193 | 4.23 | 0.00083893 | 0 | 4.8193 | 0.00103 | -0.0087193 |  | LF | AllSpc | 4230 | 0.839 | 4230 | 0.839 | 1.14 | 1.23 | -0.0020613 | 4230 | 0.839 | 4230 | 0.839 | 1.14 | 1.23 | -0.00206
LFAllSpcSDGRtLExCZ10 | Com-Iltg-dWatt-LF_OSspc | SDG | RtL | Ex | CZ10 | 4.23 | 0.00083893 | 0 | 4.7793 | 0.00105 | -0.0116 | 4.23 | 0.00083893 | 0 | 4.7793 | 0.00105 | -0.0116 |  | LF | AllSpc | 4230 | 0.839 | 4230 | 0.839 | 1.13 | 1.25 | -0.0027423 | 4230 | 0.839 | 4230 | 0.839 | 1.13 | 1.25 | -0.00274
LFAllSpcSDGRtLExCZ14 | Com-Iltg-dWatt-LF_OSspc | SDG | RtL | Ex | CZ14 | 4.23 | 0.00083893 | 0 | 4.61 | 0.00106 | -0.0245 | 4.23 | 0.00083893 | 0 | 4.61 | 0.00106 | -0.0245 |  | LF | AllSpc | 4230 | 0.839 | 4230 | 0.839 | 1.09 | 1.26 | -0.005792 | 4230 | 0.839 | 4230 | 0.839 | 1.09 | 1.26 | -0.00579
LFAllSpcSDGRtLExCZ15 | Com-Iltg-dWatt-LF_OSspc | SDG | RtL | Ex | CZ15 | 4.23 | 0.00083893 | 0 | 4.99 | 0.00107 | -0.0041192 | 4.23 | 0.00083893 | 0 | 4.99 | 0.00107 | -0.0041192 |  | LF | AllSpc | 4230 | 0.839 | 4230 | 0.839 | 1.18 | 1.28 | -0.00097382 | 4230 | 0.839 | 4230 | 0.839 | 1.18 | 1.28 | -0.000974
LFAllSpcSDGRtLExIOU | Com-Iltg-dWatt-LF_OSspc | SDG | RtL | Ex | IOU | 4.23 | 0.00083893 | 0 | 4.8152 | 0.001035 | -0.0085962 | 4.23 | 0.00083893 | 0 | 4.8152 | 0.001035 | -0.0085962 |  | LF | AllSpc | 4230 | 0.839 | 4230 | 0.839 | 1.14 | 1.23 | -0.0020322 | 4230 | 0.839 | 4230 | 0.839 | 1.14 | 1.23 | -0.00203
LFAllSpcSDGRtLNewCZ06 | Com-Iltg-dWatt-LF_OSspc | SDG | RtL | New | CZ06 | 4.23 | 0.000838 | 0 | 4.68 | 0.00105 | -0.0138 | 4.23 | 0.000838 | 0 | 4.68 | 0.00105 | -0.0138 |  | LF | AllSpc | 4230 | 0.838 | 4230 | 0.838 | 1.11 | 1.25 | -0.0032624 | 4230 | 0.838 | 4230 | 0.838 | 1.11 | 1.25 | -0.00326
LFAllSpcSDGRtLNewCZ07 | Com-Iltg-dWatt-LF_OSspc | SDG | RtL | New | CZ07 | 4.23 | 0.000838 | 0 | 4.64 | 0.00101 | -0.00998 | 4.23 | 0.000838 | 0 | 4.64 | 0.00101 | -0.00998 |  | LF | AllSpc | 4230 | 0.838 | 4230 | 0.838 | 1.1 | 1.21 | -0.0023593 | 4230 | 0.838 | 4230 | 0.838 | 1.1 | 1.21 | -0.00236
LFAllSpcSDGRtLNewCZ08 | Com-Iltg-dWatt-LF_OSspc | SDG | RtL | New | CZ08 | 4.23 | 0.000838 | 0 | 4.74 | 0.00107 | -0.0118 | 4.23 | 0.000838 | 0 | 4.74 | 0.00107 | -0.0118 |  | LF | AllSpc | 4230 | 0.838 | 4230 | 0.838 | 1.12 | 1.28 | -0.0027896 | 4230 | 0.838 | 4230 | 0.838 | 1.12 | 1.28 | -0.00279
LFAllSpcSDGRtLNewCZ10 | Com-Iltg-dWatt-LF_OSspc | SDG | RtL | New | CZ10 | 4.23 | 0.000838 | 0 | 4.78 | 0.00111 | -0.0136 | 4.23 | 0.000838 | 0 | 4.78 | 0.00111 | -0.0136 |  | LF | AllSpc | 4230 | 0.838 | 4230 | 0.838 | 1.13 | 1.32 | -0.0032151 | 4230 | 0.838 | 4230 | 0.838 | 1.13 | 1.32 | -0.00322
LFAllSpcSDGRtLNewCZ14 | Com-Iltg-dWatt-LF_OSspc | SDG | RtL | New | CZ14 | 4.23 | 0.000838 | 0 | 4.67 | 0.0011 | -0.0273 | 4.23 | 0.000838 | 0 | 4.67 | 0.0011 | -0.0273 |  | LF | AllSpc | 4230 | 0.838 | 4230 | 0.838 | 1.1 | 1.31 | -0.0064539 | 4230 | 0.838 | 4230 | 0.838 | 1.1 | 1.31 | -0.00645
LFAllSpcSDGRtLNewCZ15 | Com-Iltg-dWatt-LF_OSspc | SDG | RtL | New | CZ15 | 4.23 | 0.000838 | 0 | 5.06 | 0.00112 | -0.0041 | 4.23 | 0.000838 | 0 | 5.06 | 0.00112 | -0.0041 |  | LF | AllSpc | 4230 | 0.838 | 4230 | 0.838 | 1.2 | 1.34 | -0.00096927 | 4230 | 0.838 | 4230 | 0.838 | 1.2 | 1.34 | -0.000969
LFAllSpcSDGRtLNewIOU | Com-Iltg-dWatt-LF_OSspc | SDG | RtL | New | IOU | 4.23 | 0.000838 | 0 | 4.6819 | 0.0010396 | -0.011122 | 4.23 | 0.000838 | 0 | 4.6819 | 0.0010396 | -0.011122 |  | LF | AllSpc | 4230 | 0.838 | 4230 | 0.838 | 1.11 | 1.24 | -0.0026292 | 4230 | 0.838 | 4230 | 0.838 | 1.11 | 1.24 | -0.00263
LFAllSpcSDGRtSExCZ06 | Com-Iltg-dWatt-LF_OSspc | SDG | RtS | Ex | CZ06 | 3.3293 | 0.00086278 | 0 | 3.7485 | 0.00105 | -0.0052193 | 3.3293 | 0.00086278 | 0 | 3.7485 | 0.00105 | -0.0052193 |  | LF | AllSpc | 3330 | 0.863 | 3330 | 0.863 | 1.13 | 1.22 | -0.0015677 | 3330 | 0.863 | 3330 | 0.863 | 1.13 | 1.22 | -0.00157
LFAllSpcSDGRtSExCZ07 | Com-Iltg-dWatt-LF_OSspc | SDG | RtS | Ex | CZ07 | 3.3293 | 0.00086278 | 0 | 3.7585 | 0.00103 | -0.0031093 | 3.3293 | 0.00086278 | 0 | 3.7585 | 0.00103 | -0.0031093 |  | LF | AllSpc | 3330 | 0.863 | 3330 | 0.863 | 1.13 | 1.19 | -0.00093392 | 3330 | 0.863 | 3330 | 0.863 | 1.13 | 1.19 | -0.000934
LFAllSpcSDGRtSExCZ08 | Com-Iltg-dWatt-LF_OSspc | SDG | RtS | Ex | CZ08 | 3.3293 | 0.00086278 | 0 | 3.7693 | 0.00105 | -0.0044286 | 3.3293 | 0.00086278 | 0 | 3.7693 | 0.00105 | -0.0044286 |  | LF | AllSpc | 3330 | 0.863 | 3330 | 0.863 | 1.13 | 1.22 | -0.0013302 | 3330 | 0.863 | 3330 | 0.863 | 1.13 | 1.22 | -0.00133
LFAllSpcSDGRtSExCZ10 | Com-Iltg-dWatt-LF_OSspc | SDG | RtS | Ex | CZ10 | 3.3293 | 0.00086278 | 0 | 3.7585 | 0.00106 | -0.0065186 | 3.3293 | 0.00086278 | 0 | 3.7585 | 0.00106 | -0.0065186 |  | LF | AllSpc | 3330 | 0.863 | 3330 | 0.863 | 1.13 | 1.23 | -0.0019579 | 3330 | 0.863 | 3330 | 0.863 | 1.13 | 1.23 | -0.00196
LFAllSpcSDGRtSExCZ14 | Com-Iltg-dWatt-LF_OSspc | SDG | RtS | Ex | CZ14 | 3.3293 | 0.00086278 | 0 | 3.6393 | 0.0010593 | -0.0163 | 3.3293 | 0.00086278 | 0 | 3.6393 | 0.0010593 | -0.0163 |  | LF | AllSpc | 3330 | 0.863 | 3330 | 0.863 | 1.09 | 1.23 | -0.004896 | 3330 | 0.863 | 3330 | 0.863 | 1.09 | 1.23 | -0.0049
LFAllSpcSDGRtSExCZ15 | Com-Iltg-dWatt-LF_OSspc | SDG | RtS | Ex | CZ15 | 3.3293 | 0.00086278 | 0 | 3.9485 | 0.00107 | -0.0013993 | 3.3293 | 0.00086278 | 0 | 3.9485 | 0.00107 | -0.0013993 |  | LF | AllSpc | 3330 | 0.863 | 3330 | 0.863 | 1.19 | 1.24 | -0.00042029 | 3330 | 0.863 | 3330 | 0.863 | 1.19 | 1.24 | -0.00042
LFAllSpcSDGRtSExIOU | Com-Iltg-dWatt-LF_OSspc | SDG | RtS | Ex | IOU | 3.3293 | 0.00086278 | 0 | 3.7588 | 0.0010393 | -0.0041086 | 3.3293 | 0.00086278 | 0 | 3.7588 | 0.0010393 | -0.0041086 |  | LF | AllSpc | 3330 | 0.863 | 3330 | 0.863 | 1.13 | 1.2 | -0.0012341 | 3330 | 0.863 | 3330 | 0.863 | 1.13 | 1.2 | -0.00123
LFAllSpcSDGRtSNewCZ06 | Com-Iltg-dWatt-LF_OSspc | SDG | RtS | New | CZ06 | 3.32 | 0.00086 | 0 | 3.67 | 0.00104 | -0.00687 | 3.32 | 0.00086 | 0 | 3.67 | 0.00104 | -0.00687 |  | LF | AllSpc | 3320 | 0.86 | 3320 | 0.86 | 1.11 | 1.21 | -0.0020693 | 3320 | 0.86 | 3320 | 0.86 | 1.11 | 1.21 | -0.00207
LFAllSpcSDGRtSNewCZ07 | Com-Iltg-dWatt-LF_OSspc | SDG | RtS | New | CZ07 | 3.32 | 0.00086 | 0 | 3.64 | 0.00103 | -0.00405 | 3.32 | 0.00086 | 0 | 3.64 | 0.00103 | -0.00405 |  | LF | AllSpc | 3320 | 0.86 | 3320 | 0.86 | 1.1 | 1.2 | -0.0012199 | 3320 | 0.86 | 3320 | 0.86 | 1.1 | 1.2 | -0.00122
LFAllSpcSDGRtSNewCZ08 | Com-Iltg-dWatt-LF_OSspc | SDG | RtS | New | CZ08 | 3.32 | 0.00086 | 0 | 3.71 | 0.00105 | -0.00574 | 3.32 | 0.00086 | 0 | 3.71 | 0.00105 | -0.00574 |  | LF | AllSpc | 3320 | 0.86 | 3320 | 0.86 | 1.12 | 1.22 | -0.0017289 | 3320 | 0.86 | 3320 | 0.86 | 1.12 | 1.22 | -0.00173
LFAllSpcSDGRtSNewCZ10 | Com-Iltg-dWatt-LF_OSspc | SDG | RtS | New | CZ10 | 3.32 | 0.00086 | 0 | 3.74 | 0.0011 | -0.00716 | 3.32 | 0.00086 | 0 | 3.74 | 0.0011 | -0.00716 |  | LF | AllSpc | 3320 | 0.86 | 3320 | 0.86 | 1.13 | 1.28 | -0.0021566 | 3320 | 0.86 | 3320 | 0.86 | 1.13 | 1.28 | -0.00216
LFAllSpcSDGRtSNewCZ14 | Com-Iltg-dWatt-LF_OSspc | SDG | RtS | New | CZ14 | 3.32 | 0.00086 | 0 | 3.65 | 0.00108 | -0.0173 | 3.32 | 0.00086 | 0 | 3.65 | 0.00108 | -0.0173 |  | LF | AllSpc | 3320 | 0.86 | 3320 | 0.86 | 1.1 | 1.26 | -0.0052108 | 3320 | 0.86 | 3320 | 0.86 | 1.1 | 1.26 | -0.00521
LFAllSpcSDGRtSNewCZ15 | Com-Iltg-dWatt-LF_OSspc | SDG | RtS | New | CZ15 | 3.32 | 0.00086 | 0 | 3.91 | 0.0011 | -0.00123 | 3.32 | 0.00086 | 0 | 3.91 | 0.0011 | -0.00123 |  | LF | AllSpc | 3320 | 0.86 | 3320 | 0.86 | 1.18 | 1.28 | -0.00037048 | 3320 | 0.86 | 3320 | 0.86 | 1.18 | 1.28 | -0.00037
LFAllSpcSDGRtSNewIOU | Com-Iltg-dWatt-LF_OSspc | SDG | RtS | New | IOU | 3.32 | 0.00086 | 0 | 3.6699 | 0.0010488 | -0.0050219 | 3.32 | 0.00086 | 0 | 3.6699 | 0.0010488 | -0.0050219 |  | LF | AllSpc | 3320 | 0.86 | 3320 | 0.86 | 1.11 | 1.22 | -0.0015126 | 3320 | 0.86 | 3320 | 0.86 | 1.11 | 1.22 | -0.00151
LFAllSpcSDGSCnExCZ06 | Com-Iltg-dWatt-LF_OSspc | SDG | SCn | Ex | CZ06 | 3.14 | 0.000588 | 0 | 3.22 | 0.000763 | -0.0175 | 3.14 | 0.000588 | 0 | 3.22 | 0.000763 | -0.0175 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 1.03 | 1.3 | -0.0055732 | 3140 | 0.588 | 3140 | 0.588 | 1.03 | 1.3 | -0.00557
LFAllSpcSDGSCnExCZ07 | Com-Iltg-dWatt-LF_OSspc | SDG | SCn | Ex | CZ07 | 3.14 | 0.000588 | 0 | 3.16 | 0.000769 | -0.0143 | 3.14 | 0.000588 | 0 | 3.16 | 0.000769 | -0.0143 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 1.01 | 1.31 | -0.0045541 | 3140 | 0.588 | 3140 | 0.588 | 1.01 | 1.31 | -0.00455
LFAllSpcSDGSCnExCZ08 | Com-Iltg-dWatt-LF_OSspc | SDG | SCn | Ex | CZ08 | 3.14 | 0.000588 | 0 | 3.26 | 0.000762 | -0.0149 | 3.14 | 0.000588 | 0 | 3.26 | 0.000762 | -0.0149 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 1.04 | 1.3 | -0.0047452 | 3140 | 0.588 | 3140 | 0.588 | 1.04 | 1.3 | -0.00475
LFAllSpcSDGSCnExCZ10 | Com-Iltg-dWatt-LF_OSspc | SDG | SCn | Ex | CZ10 | 3.14 | 0.000588 | 0 | 3.27 | 0.000772 | -0.0184 | 3.14 | 0.000588 | 0 | 3.27 | 0.000772 | -0.0184 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 1.04 | 1.31 | -0.0058599 | 3140 | 0.588 | 3140 | 0.588 | 1.04 | 1.31 | -0.00586
LFAllSpcSDGSCnExCZ14 | Com-Iltg-dWatt-LF_OSspc | SDG | SCn | Ex | CZ14 | 3.14 | 0.000588 | 0 | 3.17 | 0.000759 | -0.0269 | 3.14 | 0.000588 | 0 | 3.17 | 0.000759 | -0.0269 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 1.01 | 1.29 | -0.0085669 | 3140 | 0.588 | 3140 | 0.588 | 1.01 | 1.29 | -0.00857
LFAllSpcSDGSCnExCZ15 | Com-Iltg-dWatt-LF_OSspc | SDG | SCn | Ex | CZ15 | 3.14 | 0.000588 | 0 | 3.5 | 0.000759 | -0.00785 | 3.14 | 0.000588 | 0 | 3.5 | 0.000759 | -0.00785 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 1.11 | 1.29 | -0.0025 | 3140 | 0.588 | 3140 | 0.588 | 1.11 | 1.29 | -0.0025
LFAllSpcSDGSCnExIOU | Com-Iltg-dWatt-LF_OSspc | SDG | SCn | Ex | IOU | 3.14 | 0.000588 | 0 | 3.1965 | 0.0007696 | -0.015645 | 3.14 | 0.000588 | 0 | 3.1965 | 0.0007696 | -0.015645 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 1.02 | 1.31 | -0.0049825 | 3140 | 0.588 | 3140 | 0.588 | 1.02 | 1.31 | -0.00498
LFAllSpcSDGSCnNewCZ06 | Com-Iltg-dWatt-LF_OSspc | SDG | SCn | New | CZ06 | 3.14 | 0.000588 | 0 | 3.13 | 0.000708 | -0.0186 | 3.14 | 0.000588 | 0 | 3.13 | 0.000708 | -0.0186 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 0.997 | 1.2 | -0.0059236 | 3140 | 0.588 | 3140 | 0.588 | 0.997 | 1.2 | -0.00592
LFAllSpcSDGSCnNewCZ07 | Com-Iltg-dWatt-LF_OSspc | SDG | SCn | New | CZ07 | 3.14 | 0.000588 | 0 | 3.13 | 0.000724 | -0.0155 | 3.14 | 0.000588 | 0 | 3.13 | 0.000724 | -0.0155 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 0.997 | 1.23 | -0.0049363 | 3140 | 0.588 | 3140 | 0.588 | 0.997 | 1.23 | -0.00494
LFAllSpcSDGSCnNewCZ08 | Com-Iltg-dWatt-LF_OSspc | SDG | SCn | New | CZ08 | 3.14 | 0.000588 | 0 | 3.21 | 0.000719 | -0.0163 | 3.14 | 0.000588 | 0 | 3.21 | 0.000719 | -0.0163 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 1.02 | 1.22 | -0.0051911 | 3140 | 0.588 | 3140 | 0.588 | 1.02 | 1.22 | -0.00519
LFAllSpcSDGSCnNewCZ10 | Com-Iltg-dWatt-LF_OSspc | SDG | SCn | New | CZ10 | 3.14 | 0.000588 | 0 | 3.22 | 0.000736 | -0.019 | 3.14 | 0.000588 | 0 | 3.22 | 0.000736 | -0.019 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 1.03 | 1.25 | -0.006051 | 3140 | 0.588 | 3140 | 0.588 | 1.03 | 1.25 | -0.00605
LFAllSpcSDGSCnNewCZ14 | Com-Iltg-dWatt-LF_OSspc | SDG | SCn | New | CZ14 | 3.14 | 0.000588 | 0 | 3.15 | 0.000734 | -0.0278 | 3.14 | 0.000588 | 0 | 3.15 | 0.000734 | -0.0278 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 1 | 1.25 | -0.0088535 | 3140 | 0.588 | 3140 | 0.588 | 1 | 1.25 | -0.00885
LFAllSpcSDGSCnNewCZ15 | Com-Iltg-dWatt-LF_OSspc | SDG | SCn | New | CZ15 | 3.14 | 0.000588 | 0 | 3.42 | 0.00074 | -0.00593 | 3.14 | 0.000588 | 0 | 3.42 | 0.00074 | -0.00593 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 1.09 | 1.26 | -0.0018885 | 3140 | 0.588 | 3140 | 0.588 | 1.09 | 1.26 | -0.00189
LFAllSpcSDGSCnNewIOU | Com-Iltg-dWatt-LF_OSspc | SDG | SCn | New | IOU | 3.14 | 0.000588 | 0 | 3.1586 | 0.00072716 | -0.016661 | 3.14 | 0.000588 | 0 | 3.1586 | 0.00072716 | -0.016661 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 1.01 | 1.24 | -0.005306 | 3140 | 0.588 | 3140 | 0.588 | 1.01 | 1.24 | -0.00531
LFAllSpcSDGSUnExCZ06 | Com-Iltg-dWatt-LF_OSspc | SDG | SUn | Ex | CZ06 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0 | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0
LFAllSpcSDGSUnExCZ07 | Com-Iltg-dWatt-LF_OSspc | SDG | SUn | Ex | CZ07 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0 | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0
LFAllSpcSDGSUnExCZ08 | Com-Iltg-dWatt-LF_OSspc | SDG | SUn | Ex | CZ08 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0 | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0
LFAllSpcSDGSUnExCZ10 | Com-Iltg-dWatt-LF_OSspc | SDG | SUn | Ex | CZ10 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0 | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0
LFAllSpcSDGSUnExCZ14 | Com-Iltg-dWatt-LF_OSspc | SDG | SUn | Ex | CZ14 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0 | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0
LFAllSpcSDGSUnExCZ15 | Com-Iltg-dWatt-LF_OSspc | SDG | SUn | Ex | CZ15 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0 | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0
LFAllSpcSDGSUnExIOU | Com-Iltg-dWatt-LF_OSspc | SDG | SUn | Ex | IOU | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0 | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0
LFAllSpcSDGSUnNewCZ06 | Com-Iltg-dWatt-LF_OSspc | SDG | SUn | New | CZ06 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0 | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0
LFAllSpcSDGSUnNewCZ07 | Com-Iltg-dWatt-LF_OSspc | SDG | SUn | New | CZ07 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0 | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0
LFAllSpcSDGSUnNewCZ08 | Com-Iltg-dWatt-LF_OSspc | SDG | SUn | New | CZ08 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0 | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0
LFAllSpcSDGSUnNewCZ10 | Com-Iltg-dWatt-LF_OSspc | SDG | SUn | New | CZ10 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0 | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0
LFAllSpcSDGSUnNewCZ14 | Com-Iltg-dWatt-LF_OSspc | SDG | SUn | New | CZ14 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0 | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0
LFAllSpcSDGSUnNewCZ15 | Com-Iltg-dWatt-LF_OSspc | SDG | SUn | New | CZ15 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0 | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0
LFAllSpcSDGSUnNewIOU | Com-Iltg-dWatt-LF_OSspc | SDG | SUn | New | IOU | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 | 3.14 | 0.000588 | 0 |  | LF | AllSpc | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0 | 3140 | 0.588 | 3140 | 0.588 | 1 | 1 | 0
LFAllSpcSDGWRfExCZ06 | Com-Iltg-dWatt-LF_OSspc | SDG | WRf | Ex | CZ06 | 3.13 | 0.000473 | 0 | 5.0292 | 0.000592 | 0 | 3.13 | 0.000473 | 0 | 5.0292 | 0.000592 | 0 |  | LF | AllSpc | 3130 | 0.473 | 3130 | 0.473 | 1.61 | 1.25 | 0 | 3130 | 0.473 | 3130 | 0.473 | 1.61 | 1.25 | 0
LFAllSpcSDGWRfExCZ07 | Com-Iltg-dWatt-LF_OSspc | SDG | WRf | Ex | CZ07 | 3.13 | 0.000473 | 0 | 5.0592 | 0.000592 | 0 | 3.13 | 0.000473 | 0 | 5.0592 | 0.000592 | 0 |  | LF | AllSpc | 3130 | 0.473 | 3130 | 0.473 | 1.62 | 1.25 | 0 | 3130 | 0.473 | 3130 | 0.473 | 1.62 | 1.25 | 0
LFAllSpcSDGWRfExCZ10 | Com-Iltg-dWatt-LF_OSspc | SDG | WRf | Ex | CZ10 | 3.13 | 0.000473 | 0 | 4.9692 | 0.000597 | 0 | 3.13 | 0.000473 | 0 | 4.9692 | 0.000597 | 0 |  | LF | AllSpc | 3130 | 0.473 | 3130 | 0.473 | 1.59 | 1.26 | 0 | 3130 | 0.473 | 3130 | 0.473 | 1.59 | 1.26 | 0
LFAllSpcSDGWRfExIOU | Com-Iltg-dWatt-LF_OSspc | SDG | WRf | Ex | IOU | 3.13 | 0.000473 | 0 | 5.0391 | 0.0005931 | 0 | 3.13 | 0.000473 | 0 | 5.0391 | 0.0005931 | 0 |  | LF | AllSpc | 3130 | 0.473 | 3130 | 0.473 | 1.61 | 1.25 | 0 | 3130 | 0.473 | 3130 | 0.473 | 1.61 | 1.25 | 0
LFAllSpcSDGWRfNewCZ06 | Com-Iltg-dWatt-LF_OSspc | SDG | WRf | New | CZ06 | 3.13 | 0.000473 | 0 | 4.5 | 0.000583 | 0 | 3.13 | 0.000473 | 0 | 4.5 | 0.000583 | 0 |  | LF | AllSpc | 3130 | 0.473 | 3130 | 0.473 | 1.44 | 1.23 | 0 | 3130 | 0.473 | 3130 | 0.473 | 1.44 | 1.23 | 0
LFAllSpcSDGWRfNewCZ07 | Com-Iltg-dWatt-LF_OSspc | SDG | WRf | New | CZ07 | 3.13 | 0.000473 | 0 | 4.47 | 0.000583 | 0 | 3.13 | 0.000473 | 0 | 4.47 | 0.000583 | 0 |  | LF | AllSpc | 3130 | 0.473 | 3130 | 0.473 | 1.43 | 1.23 | 0 | 3130 | 0.473 | 3130 | 0.473 | 1.43 | 1.23 | 0
LFAllSpcSDGWRfNewCZ08 | Com-Iltg-dWatt-LF_OSspc | SDG | WRf | New | CZ08 | 3.13 | 0.000473 | 0 | 4.45 | 0.000585 | 0 | 3.13 | 0.000473 | 0 | 4.45 | 0.000585 | 0 |  | LF | AllSpc | 3130 | 0.473 | 3130 | 0.473 | 1.42 | 1.24 | 0 | 3130 | 0.473 | 3130 | 0.473 | 1.42 | 1.24 | 0
LFAllSpcSDGWRfNewCZ10 | Com-Iltg-dWatt-LF_OSspc | SDG | WRf | New | CZ10 | 3.13 | 0.000473 | 0 | 4.39 | 0.000592 | 0 | 3.13 | 0.000473 | 0 | 4.39 | 0.000592 | 0 |  | LF | AllSpc | 3130 | 0.473 | 3130 | 0.473 | 1.4 | 1.25 | 0 | 3130 | 0.473 | 3130 | 0.473 | 1.4 | 1.25 | 0
LFAllSpcSDGWRfNewCZ14 | Com-Iltg-dWatt-LF_OSspc | SDG | WRf | New | CZ14 | 3.13 | 0.000473 | 0 | 4.3 | 0.000586 | 0 | 3.13 | 0.000473 | 0 | 4.3 | 0.000586 | 0 |  | LF | AllSpc | 3130 | 0.473 | 3130 | 0.473 | 1.37 | 1.24 | 0 | 3130 | 0.473 | 3130 | 0.473 | 1.37 | 1.24 | 0
LFAllSpcSDGWRfNewCZ15 | Com-Iltg-dWatt-LF_OSspc | SDG | WRf | New | CZ15 | 3.13 | 0.000473 | 0 | 4.6 | 0.00059 | 0 | 3.13 | 0.000473 | 0 | 4.6 | 0.00059 | 0 |  | LF | AllSpc | 3130 | 0.473 | 3130 | 0.473 | 1.47 | 1.25 | 0 | 3130 | 0.473 | 3130 | 0.473 | 1.47 | 1.25 | 0
LFAllSpcSDGWRfNewIOU | Com-Iltg-dWatt-LF_OSspc | SDG | WRf | New | IOU | 3.13 | 0.000473 | 0 | 4.4528 | 0.00058497 | 0 | 3.13 | 0.000473 | 0 | 4.4528 | 0.00058497 | 0 |  | LF | AllSpc | 3130 | 0.473 | 3130 | 0.473 | 1.42 | 1.24 | 0 | 3130 | 0.473 | 3130 | 0.473 | 1.42 | 1.24 | 0
CFLNonePGEDMoExCZ01 | Res-Iltg-dWatt-CFL | PGE | DMo | Ex | CZ01 | 0.541 | 4.9e-05 | 0 | 0.519 | 5.05e-05 | -0.0131 | 0.541 | 4.9e-05 | 0 | 0.519 | 5.05e-05 | -0.0131 |  | CFL | None | 541 | 0.049 | 541 | 0.049 | 0.959 | 1.03 | -0.024214 | 541 | 0.049 | 541 | 0.049 | 0.959 | 1.03 | -0.0242
CFLNonePGEDMoExCZ02 | Res-Iltg-dWatt-CFL | PGE | DMo | Ex | CZ02 | 0.541 | 4.3e-05 | 0 | 0.586 | 7.64e-05 | -0.0119 | 0.541 | 4.3e-05 | 0 | 0.586 | 7.64e-05 | -0.0119 |  | CFL | None | 541 | 0.043 | 541 | 0.043 | 1.08 | 1.78 | -0.021996 | 541 | 0.043 | 541 | 0.043 | 1.08 | 1.78 | -0.022
CFLNonePGEDMoExCZ03 | Res-Iltg-dWatt-CFL | PGE | DMo | Ex | CZ03 | 0.541 | 4.3e-05 | 0 | 0.549 | 5.86e-05 | -0.0122 | 0.541 | 4.3e-05 | 0 | 0.549 | 5.86e-05 | -0.0122 |  | CFL | None | 541 | 0.043 | 541 | 0.043 | 1.01 | 1.36 | -0.022551 | 541 | 0.043 | 541 | 0.043 | 1.01 | 1.36 | -0.0226
CFLNonePGEDMoExCZ04 | Res-Iltg-dWatt-CFL | PGE | DMo | Ex | CZ04 | 0.541 | 4.3e-05 | 0 | 0.601 | 6.42e-05 | -0.00966 | 0.541 | 4.3e-05 | 0 | 0.601 | 6.42e-05 | -0.00966 |  | CFL | None | 541 | 0.043 | 541 | 0.043 | 1.11 | 1.49 | -0.017856 | 541 | 0.043 | 541 | 0.043 | 1.11 | 1.49 | -0.0179
CFLNonePGEDMoExCZ05 | Res-Iltg-dWatt-CFL | PGE | DMo | Ex | CZ05 | 0.541 | 4.7e-05 | 0 | 0.519 | 5.25e-05 | -0.0133 | 0.541 | 4.7e-05 | 0 | 0.519 | 5.25e-05 | -0.0133 |  | CFL | None | 541 | 0.047 | 541 | 0.047 | 0.959 | 1.12 | -0.024584 | 541 | 0.047 | 541 | 0.047 | 0.959 | 1.12 | -0.0246
CFLNonePGEDMoExCZ11 | Res-Iltg-dWatt-CFL | PGE | DMo | Ex | CZ11 | 0.541 | 4.4e-05 | 0 | 0.636 | 7.63e-05 | -0.0106 | 0.541 | 4.4e-05 | 0 | 0.636 | 7.63e-05 | -0.0106 |  | CFL | None | 541 | 0.044 | 541 | 0.044 | 1.18 | 1.73 | -0.019593 | 541 | 0.044 | 541 | 0.044 | 1.18 | 1.73 | -0.0196
CFLNonePGEDMoExCZ12 | Res-Iltg-dWatt-CFL | PGE | DMo | Ex | CZ12 | 0.541 | 4.5e-05 | 0 | 0.62 | 8.07e-05 | -0.0111 | 0.541 | 4.5e-05 | 0 | 0.62 | 8.07e-05 | -0.0111 |  | CFL | None | 541 | 0.045 | 541 | 0.045 | 1.15 | 1.79 | -0.020518 | 541 | 0.045 | 541 | 0.045 | 1.15 | 1.79 | -0.0205
CFLNonePGEDMoExCZ13 | Res-Iltg-dWatt-CFL | PGE | DMo | Ex | CZ13 | 0.541 | 4.5e-05 | 0 | 0.639 | 7.68e-05 | -0.0103 | 0.541 | 4.5e-05 | 0 | 0.639 | 7.68e-05 | -0.0103 |  | CFL | None | 541 | 0.045 | 541 | 0.045 | 1.18 | 1.71 | -0.019039 | 541 | 0.045 | 541 | 0.045 | 1.18 | 1.71 | -0.019
CFLNonePGEDMoExCZ16 | Res-Iltg-dWatt-CFL | PGE | DMo | Ex | CZ16 | 0.541 | 4.5e-05 | 0 | 0.555 | 6.16e-05 | -0.0131 | 0.541 | 4.5e-05 | 0 | 0.555 | 6.16e-05 | -0.0131 |  | CFL | None | 541 | 0.045 | 541 | 0.045 | 1.03 | 1.37 | -0.024214 | 541 | 0.045 | 541 | 0.045 | 1.03 | 1.37 | -0.0242
CFLNonePGEDMoExIOU | Res-Iltg-dWatt-CFL | PGE | DMo | Ex | IOU | 0.541 | 4.4e-05 | 0 | 0.606 | 7.18e-05 | -0.0112 | 0.541 | 4.4e-05 | 0 | 0.606 | 7.18e-05 | -0.0112 |  | CFL | None | 541 | 0.044 | 541 | 0.044 | 1.12 | 1.63 | -0.020702 | 541 | 0.044 | 541 | 0.044 | 1.12 | 1.63 | -0.0207
CFLNonePGEDMoNewCZ01 | Res-Iltg-dWatt-CFL | PGE | DMo | New | CZ01 | 0.541 | 4.9e-05 | 0 | 0.528 | 4.94e-05 | -0.0131 | 0.541 | 4.9e-05 | 0 | 0.528 | 4.94e-05 | -0.0131 |  | CFL | None | 541 | 0.049 | 541 | 0.049 | 0.976 | 1.01 | -0.024214 | 541 | 0.049 | 541 | 0.049 | 0.976 | 1.01 | -0.0242
CFLNonePGEDMoNewCZ02 | Res-Iltg-dWatt-CFL | PGE | DMo | New | CZ02 | 0.541 | 4.3e-05 | 0 | 0.59 | 6.63e-05 | -0.0131 | 0.541 | 4.3e-05 | 0 | 0.59 | 6.63e-05 | -0.0131 |  | CFL | None | 541 | 0.043 | 541 | 0.043 | 1.09 | 1.54 | -0.024214 | 541 | 0.043 | 541 | 0.043 | 1.09 | 1.54 | -0.0242
CFLNonePGEDMoNewCZ03 | Res-Iltg-dWatt-CFL | PGE | DMo | New | CZ03 | 0.541 | 4.3e-05 | 0 | 0.517 | 4.39e-05 | -0.0127 | 0.541 | 4.3e-05 | 0 | 0.517 | 4.39e-05 | -0.0127 |  | CFL | None | 541 | 0.043 | 541 | 0.043 | 0.956 | 1.02 | -0.023475 | 541 | 0.043 | 541 | 0.043 | 0.956 | 1.02 | -0.0235
CFLNonePGEDMoNewCZ04 | Res-Iltg-dWatt-CFL | PGE | DMo | New | CZ04 | 0.541 | 4.3e-05 | 0 | 0.579 | 5.61e-05 | -0.00975 | 0.541 | 4.3e-05 | 0 | 0.579 | 5.61e-05 | -0.00975 |  | CFL | None | 541 | 0.043 | 541 | 0.043 | 1.07 | 1.3 | -0.018022 | 541 | 0.043 | 541 | 0.043 | 1.07 | 1.3 | -0.018
CFLNonePGEDMoNewCZ05 | Res-Iltg-dWatt-CFL | PGE | DMo | New | CZ05 | 0.541 | 4.7e-05 | 0 | 0.514 | 4.78e-05 | -0.0133 | 0.541 | 4.7e-05 | 0 | 0.514 | 4.78e-05 | -0.0133 |  | CFL | None | 541 | 0.047 | 541 | 0.047 | 0.95 | 1.02 | -0.024584 | 541 | 0.047 | 541 | 0.047 | 0.95 | 1.02 | -0.0246
CFLNonePGEDMoNewCZ11 | Res-Iltg-dWatt-CFL | PGE | DMo | New | CZ11 | 0.541 | 4.4e-05 | 0 | 0.614 | 6.6e-05 | -0.0103 | 0.541 | 4.4e-05 | 0 | 0.614 | 6.6e-05 | -0.0103 |  | CFL | None | 541 | 0.044 | 541 | 0.044 | 1.13 | 1.5 | -0.019039 | 541 | 0.044 | 541 | 0.044 | 1.13 | 1.5 | -0.019
CFLNonePGEDMoNewCZ12 | Res-Iltg-dWatt-CFL | PGE | DMo | New | CZ12 | 0.541 | 4.5e-05 | 0 | 0.602 | 6.81e-05 | -0.0109 | 0.541 | 4.5e-05 | 0 | 0.602 | 6.81e-05 | -0.0109 |  | CFL | None | 541 | 0.045 | 541 | 0.045 | 1.11 | 1.51 | -0.020148 | 541 | 0.045 | 541 | 0.045 | 1.11 | 1.51 | -0.0201
CFLNonePGEDMoNewCZ13 | Res-Iltg-dWatt-CFL | PGE | DMo | New | CZ13 | 0.541 | 4.5e-05 | 0 | 0.521 | 4.53e-05 | -0.011 | 0.541 | 4.5e-05 | 0 | 0.521 | 4.53e-05 | -0.011 |  | CFL | None | 541 | 0.045 | 541 | 0.045 | 0.963 | 1.01 | -0.020333 | 541 | 0.045 | 541 | 0.045 | 0.963 | 1.01 | -0.0203
CFLNonePGEDMoNewCZ16 | Res-Iltg-dWatt-CFL | PGE | DMo | New | CZ16 | 0.541 | 4.5e-05 | 0 | 0.55 | 5.83e-05 | -0.0117 | 0.541 | 4.5e-05 | 0 | 0.55 | 5.83e-05 | -0.0117 |  | CFL | None | 541 | 0.045 | 541 | 0.045 | 1.02 | 1.3 | -0.021627 | 541 | 0.045 | 541 | 0.045 | 1.02 | 1.3 | -0.0216
CFLNonePGEDMoNewIOU | Res-Iltg-dWatt-CFL | PGE | DMo | New | IOU | 0.541 | 4.4e-05 | 0 | 0.58 | 5.97e-05 | -0.0108 | 0.541 | 4.4e-05 | 0 | 0.58 | 5.97e-05 | -0.0108 |  | CFL | None | 541 | 0.044 | 541 | 0.044 | 1.07 | 1.36 | -0.019963 | 541 | 0.044 | 541 | 0.044 | 1.07 | 1.36 | -0.02
CFLNonePGEMFmExCZ01 | Res-Iltg-dWatt-CFL | PGE | MFm | Ex | CZ01 | 0.541 | 4.9e-05 | 0 | 0.494 | 4.92e-05 | -0.0143 | 0.541 | 4.9e-05 | 0 | 0.494 | 4.92e-05 | -0.0143 |  | CFL | None | 541 | 0.049 | 541 | 0.049 | 0.913 | 1 | -0.026433 | 541 | 0.049 | 541 | 0.049 | 0.913 | 1 | -0.0264
CFLNonePGEMFmExCZ02 | Res-Iltg-dWatt-CFL | PGE | MFm | Ex | CZ02 | 0.541 | 4.3e-05 | 0 | 0.527 | 5.23e-05 | -0.0111 | 0.541 | 4.3e-05 | 0 | 0.527 | 5.23e-05 | -0.0111 |  | CFL | None | 541 | 0.043 | 541 | 0.043 | 0.974 | 1.22 | -0.020518 | 541 | 0.043 | 541 | 0.043 | 0.974 | 1.22 | -0.0205
CFLNonePGEMFmExCZ03 | Res-Iltg-dWatt-CFL | PGE | MFm | Ex | CZ03 | 0.541 | 4.3e-05 | 0 | 0.508 | 4.45e-05 | -0.013 | 0.541 | 4.3e-05 | 0 | 0.508 | 4.45e-05 | -0.013 |  | CFL | None | 541 | 0.043 | 541 | 0.043 | 0.939 | 1.03 | -0.02403 | 541 | 0.043 | 541 | 0.043 | 0.939 | 1.03 | -0.024
CFLNonePGEMFmExCZ04 | Res-Iltg-dWatt-CFL | PGE | MFm | Ex | CZ04 | 0.541 | 4.3e-05 | 0 | 0.535 | 5.28e-05 | -0.00978 | 0.541 | 4.3e-05 | 0 | 0.535 | 5.28e-05 | -0.00978 |  | CFL | None | 541 | 0.043 | 541 | 0.043 | 0.989 | 1.23 | -0.018078 | 541 | 0.043 | 541 | 0.043 | 0.989 | 1.23 | -0.0181
CFLNonePGEMFmExCZ05 | Res-Iltg-dWatt-CFL | PGE | MFm | Ex | CZ05 | 0.541 | 4.7e-05 | 0 | 0.509 | 4.87e-05 | -0.0134 | 0.541 | 4.7e-05 | 0 | 0.509 | 4.87e-05 | -0.0134 |  | CFL | None | 541 | 0.047 | 541 | 0.047 | 0.941 | 1.04 | -0.024769 | 541 | 0.047 | 541 | 0.047 | 0.941 | 1.04 | -0.0248
CFLNonePGEMFmExCZ11 | Res-Iltg-dWatt-CFL | PGE | MFm | Ex | CZ11 | 0.541 | 4.4e-05 | 0 | 0.586 | 6.62e-05 | -0.0096 | 0.541 | 4.4e-05 | 0 | 0.586 | 6.62e-05 | -0.0096 |  | CFL | None | 541 | 0.044 | 541 | 0.044 | 1.08 | 1.5 | -0.017745 | 541 | 0.044 | 541 | 0.044 | 1.08 | 1.5 | -0.0177
CFLNonePGEMFmExCZ12 | Res-Iltg-dWatt-CFL | PGE | MFm | Ex | CZ12 | 0.541 | 4.5e-05 | 0 | 0.566 | 6.75e-05 | -0.0103 | 0.541 | 4.5e-05 | 0 | 0.566 | 6.75e-05 | -0.0103 |  | CFL | None | 541 | 0.045 | 541 | 0.045 | 1.05 | 1.5 | -0.019039 | 541 | 0.045 | 541 | 0.045 | 1.05 | 1.5 | -0.019
CFLNonePGEMFmExCZ13 | Res-Iltg-dWatt-CFL | PGE | MFm | Ex | CZ13 | 0.541 | 4.5e-05 | 0 | 0.6 | 6.63e-05 | -0.00939 | 0.541 | 4.5e-05 | 0 | 0.6 | 6.63e-05 | -0.00939 |  | CFL | None | 541 | 0.045 | 541 | 0.045 | 1.11 | 1.47 | -0.017357 | 541 | 0.045 | 541 | 0.045 | 1.11 | 1.47 | -0.0174
CFLNonePGEMFmExCZ16 | Res-Iltg-dWatt-CFL | PGE | MFm | Ex | CZ16 | 0.541 | 4.5e-05 | 0 | 0.55 | 5.81e-05 | -0.0123 | 0.541 | 4.5e-05 | 0 | 0.55 | 5.81e-05 | -0.0123 |  | CFL | None | 541 | 0.045 | 541 | 0.045 | 1.02 | 1.29 | -0.022736 | 541 | 0.045 | 541 | 0.045 | 1.02 | 1.29 | -0.0227
CFLNonePGEMFmExIOU | Res-Iltg-dWatt-CFL | PGE | MFm | Ex | IOU | 0.541 | 4.4e-05 | 0 | 0.535 | 5.36e-05 | -0.0115 | 0.541 | 4.4e-05 | 0 | 0.535 | 5.36e-05 | -0.0115 |  | CFL | None | 541 | 0.044 | 541 | 0.044 | 0.989 | 1.22 | -0.021257 | 541 | 0.044 | 541 | 0.044 | 0.989 | 1.22 | -0.0213
CFLNonePGEMFmNewCZ01 | Res-Iltg-dWatt-CFL | PGE | MFm | New | CZ01 | 0.541 | 4.9e-05 | 0 | 0.501 | 4.93e-05 | -0.0137 | 0.541 | 4.9e-05 | 0 | 0.501 | 4.93e-05 | -0.0137 |  | CFL | None | 541 | 0.049 | 541 | 0.049 | 0.926 | 1.01 | -0.025323 | 541 | 0.049 | 541 | 0.049 | 0.926 | 1.01 | -0.0253
CFLNonePGEMFmNewCZ02 | Res-Iltg-dWatt-CFL | PGE | MFm | New | CZ02 | 0.541 | 4.3e-05 | 0 | 0.531 | 4.85e-05 | -0.00909 | 0.541 | 4.3e-05 | 0 | 0.531 | 4.85e-05 | -0.00909 |  | CFL | None | 541 | 0.043 | 541 | 0.043 | 0.982 | 1.13 | -0.016802 | 541 | 0.043 | 541 | 0.043 | 0.982 | 1.13 | -0.0168
CFLNonePGEMFmNewCZ03 | Res-Iltg-dWatt-CFL | PGE | MFm | New | CZ03 | 0.541 | 4.3e-05 | 0 | 0.527 | 4.45e-05 | -0.00935 | 0.541 | 4.3e-05 | 0 | 0.527 | 4.45e-05 | -0.00935 |  | CFL | None | 541 | 0.043 | 541 | 0.043 | 0.974 | 1.03 | -0.017283 | 541 | 0.043 | 541 | 0.043 | 0.974 | 1.03 | -0.0173
CFLNonePGEMFmNewCZ04 | Res-Iltg-dWatt-CFL | PGE | MFm | New | CZ04 | 0.541 | 4.3e-05 | 0 | 0.583 | 5.91e-05 | -0.00631 | 0.541 | 4.3e-05 | 0 | 0.583 | 5.91e-05 | -0.00631 |  | CFL | None | 541 | 0.043 | 541 | 0.043 | 1.08 | 1.37 | -0.011664 | 541 | 0.043 | 541 | 0.043 | 1.08 | 1.37 | -0.0117
CFLNonePGEMFmNewCZ05 | Res-Iltg-dWatt-CFL | PGE | MFm | New | CZ05 | 0.541 | 4.7e-05 | 0 | 0.542 | 5.09e-05 | -0.00723 | 0.541 | 4.7e-05 | 0 | 0.542 | 5.09e-05 | -0.00723 |  | CFL | None | 541 | 0.047 | 541 | 0.047 | 1 | 1.08 | -0.013364 | 541 | 0.047 | 541 | 0.047 | 1 | 1.08 | -0.0134
CFLNonePGEMFmNewCZ11 | Res-Iltg-dWatt-CFL | PGE | MFm | New | CZ11 | 0.541 | 4.4e-05 | 0 | 0.61 | 5.96e-05 | -0.00748 | 0.541 | 4.4e-05 | 0 | 0.61 | 5.96e-05 | -0.00748 |  | CFL | None | 541 | 0.044 | 541 | 0.044 | 1.13 | 1.35 | -0.013826 | 541 | 0.044 | 541 | 0.044 | 1.13 | 1.35 | -0.0138
CFLNonePGEMFmNewCZ12 | Res-Iltg-dWatt-CFL | PGE | MFm | New | CZ12 | 0.541 | 4.5e-05 | 0 | 0.591 | 6.28e-05 | -0.00786 | 0.541 | 4.5e-05 | 0 | 0.591 | 6.28e-05 | -0.00786 |  | CFL | None | 541 | 0.045 | 541 | 0.045 | 1.09 | 1.4 | -0.014529 | 541 | 0.045 | 541 | 0.045 | 1.09 | 1.4 | -0.0145
CFLNonePGEMFmNewCZ13 | Res-Iltg-dWatt-CFL | PGE | MFm | New | CZ13 | 0.541 | 4.5e-05 | 0 | 0.609 | 6.14e-05 | -0.0074 | 0.541 | 4.5e-05 | 0 | 0.609 | 6.14e-05 | -0.0074 |  | CFL | None | 541 | 0.045 | 541 | 0.045 | 1.13 | 1.36 | -0.013678 | 541 | 0.045 | 541 | 0.045 | 1.13 | 1.36 | -0.0137
CFLNonePGEMFmNewCZ16 | Res-Iltg-dWatt-CFL | PGE | MFm | New | CZ16 | 0.541 | 4.5e-05 | 0 | 0.542 | 5.27e-05 | -0.0116 | 0.541 | 4.5e-05 | 0 | 0.542 | 5.27e-05 | -0.0116 |  | CFL | None | 541 | 0.045 | 541 | 0.045 | 1 | 1.17 | -0.021442 | 541 | 0.045 | 541 | 0.045 | 1 | 1.17 | -0.0214
CFLNonePGEMFmNewIOU | Res-Iltg-dWatt-CFL | PGE | MFm | New | IOU | 0.541 | 4.4e-05 | 0 | 0.555 | 5.31e-05 | -0.00855 | 0.541 | 4.4e-05 | 0 | 0.555 | 5.31e-05 | -0.00855 |  | CFL | None | 541 | 0.044 | 541 | 0.044 | 1.03 | 1.21 | -0.015804 | 541 | 0.044 | 541 | 0.044 | 1.03 | 1.21 | -0.0158
CFLNonePGEResExCZ01 | Res-Iltg-dWatt-CFL | PGE | Res | Ex | CZ01 | 0.541 | 4.9e-05 | 0 | 0.51718 | 4.9385e-05 | -0.014914 | 0.541 | 4.9e-05 | 0 | 0.51718 | 4.9385e-05 | -0.014914 |  | CFL | None | 541 | 0.049 | 541 | 0.049 | 0.956 | 1.01 | -0.027567 | 541 | 0.049 | 541 | 0.049 | 0.956 | 1.01 | -0.0276
CFLNonePGEResExCZ02 | Res-Iltg-dWatt-CFL | PGE | Res | Ex | CZ02 | 0.541 | 4.3e-05 | 0 | 0.53738 | 5.7131e-05 | -0.013874 | 0.541 | 4.3e-05 | 0 | 0.53738 | 5.7131e-05 | -0.013874 |  | CFL | None | 541 | 0.043 | 541 | 0.043 | 0.993 | 1.33 | -0.025645 | 541 | 0.043 | 541 | 0.043 | 0.993 | 1.33 | -0.0256
CFLNonePGEResExCZ03 | Res-Iltg-dWatt-CFL | PGE | Res | Ex | CZ03 | 0.541 | 4.3e-05 | 0 | 0.5183 | 4.6091e-05 | -0.014675 | 0.541 | 4.3e-05 | 0 | 0.5183 | 4.6091e-05 | -0.014675 |  | CFL | None | 541 | 0.043 | 541 | 0.043 | 0.958 | 1.07 | -0.027126 | 541 | 0.043 | 541 | 0.043 | 0.958 | 1.07 | -0.0271
CFLNonePGEResExCZ04 | Res-Iltg-dWatt-CFL | PGE | Res | Ex | CZ04 | 0.541 | 4.3e-05 | 0 | 0.54626 | 5.4768e-05 | -0.011209 | 0.541 | 4.3e-05 | 0 | 0.54626 | 5.4768e-05 | -0.011209 |  | CFL | None | 541 | 0.043 | 541 | 0.043 | 1.01 | 1.27 | -0.02072 | 541 | 0.043 | 541 | 0.043 | 1.01 | 1.27 | -0.0207
CFLNonePGEResExCZ05 | Res-Iltg-dWatt-CFL | PGE | Res | Ex | CZ05 | 0.541 | 4.7e-05 | 0 | 0.52047 | 5.0072e-05 | -0.015335 | 0.541 | 4.7e-05 | 0 | 0.52047 | 5.0072e-05 | -0.015335 |  | CFL | None | 541 | 0.047 | 541 | 0.047 | 0.962 | 1.07 | -0.028345 | 541 | 0.047 | 541 | 0.047 | 0.962 | 1.07 | -0.0283
CFLNonePGEResExCZ11 | Res-Iltg-dWatt-CFL | PGE | Res | Ex | CZ11 | 0.541 | 4.4e-05 | 0 | 0.59845 | 7.2602e-05 | -0.011574 | 0.541 | 4.4e-05 | 0 | 0.59845 | 7.2602e-05 | -0.011574 |  | CFL | None | 541 | 0.044 | 541 | 0.044 | 1.11 | 1.65 | -0.021394 | 541 | 0.044 | 541 | 0.044 | 1.11 | 1.65 | -0.0214
CFLNonePGEResExCZ12 | Res-Iltg-dWatt-CFL | PGE | Res | Ex | CZ12 | 0.541 | 4.5e-05 | 0 | 0.57507 | 7.1997e-05 | -0.012277 | 0.541 | 4.5e-05 | 0 | 0.57507 | 7.1997e-05 | -0.012277 |  | CFL | None | 541 | 0.045 | 541 | 0.045 | 1.06 | 1.6 | -0.022694 | 541 | 0.045 | 541 | 0.045 | 1.06 | 1.6 | -0.0227
CFLNonePGEResExCZ13 | Res-Iltg-dWatt-CFL | PGE | Res | Ex | CZ13 | 0.541 | 4.5e-05 | 0 | 0.60347 | 7.0984e-05 | -0.011572 | 0.541 | 4.5e-05 | 0 | 0.60347 | 7.0984e-05 | -0.011572 |  | CFL | None | 541 | 0.045 | 541 | 0.045 | 1.12 | 1.58 | -0.021391 | 541 | 0.045 | 541 | 0.045 | 1.12 | 1.58 | -0.0214
CFLNonePGEResExCZ16 | Res-Iltg-dWatt-CFL | PGE | Res | Ex | CZ16 | 0.541 | 4.5e-05 | 0 | 0.54672 | 5.8772e-05 | -0.014828 | 0.541 | 4.5e-05 | 0 | 0.54672 | 5.8772e-05 | -0.014828 |  | CFL | None | 541 | 0.045 | 541 | 0.045 | 1.01 | 1.31 | -0.027408 | 541 | 0.045 | 541 | 0.045 | 1.01 | 1.31 | -0.0274
CFLNonePGEResExIOU | Res-Iltg-dWatt-CFL | PGE | Res | Ex | IOU | 0.541 | 4.4e-05 | 0 | 0.55327 | 5.939e-05 | -0.01298 | 0.541 | 4.4e-05 | 0 | 0.55327 | 5.939e-05 | -0.01298 |  | CFL | None | 541 | 0.044 | 541 | 0.044 | 1.02 | 1.35 | -0.023993 | 541 | 0.044 | 541 | 0.044 | 1.02 | 1.35 | -0.024
CFLNonePGEResNewCZ01 | Res-Iltg-dWatt-CFL | PGE | Res | New | CZ01 | 0.541 | 4.9e-05 | 0 | 0.5205 | 4.93e-05 | -0.012865 | 0.541 | 4.9e-05 | 0 | 0.5205 | 4.93e-05 | -0.012865 |  | CFL | None | 541 | 0.049 | 541 | 0.049 | 0.962 | 1.01 | -0.023779 | 541 | 0.049 | 541 | 0.049 | 0.962 | 1.01 | -0.0238
CFLNonePGEResNewCZ02 | Res-Iltg-dWatt-CFL | PGE | Res | New | CZ02 | 0.541 | 4.3e-05 | 0 | 0.54563 | 5.8847e-05 | -0.012849 | 0.541 | 4.3e-05 | 0 | 0.54563 | 5.8847e-05 | -0.012849 |  | CFL | None | 541 | 0.043 | 541 | 0.043 | 1.01 | 1.37 | -0.02375 | 541 | 0.043 | 541 | 0.043 | 1.01 | 1.37 | -0.0238
CFLNonePGEResNewCZ03 | Res-Iltg-dWatt-CFL | PGE | Res | New | CZ03 | 0.541 | 4.3e-05 | 0 | 0.53108 | 4.7177e-05 | -0.010681 | 0.541 | 4.3e-05 | 0 | 0.53108 | 4.7177e-05 | -0.010681 |  | CFL | None | 541 | 0.043 | 541 | 0.043 | 0.982 | 1.1 | -0.019743 | 541 | 0.043 | 541 | 0.043 | 0.982 | 1.1 | -0.0197
CFLNonePGEResNewCZ04 | Res-Iltg-dWatt-CFL | PGE | Res | New | CZ04 | 0.541 | 4.3e-05 | 0 | 0.57423 | 6.2594e-05 | -0.010097 | 0.541 | 4.3e-05 | 0 | 0.57423 | 6.2594e-05 | -0.010097 |  | CFL | None | 541 | 0.043 | 541 | 0.043 | 1.06 | 1.46 | -0.018664 | 541 | 0.043 | 541 | 0.043 | 1.06 | 1.46 | -0.0187
CFLNonePGEResNewCZ05 | Res-Iltg-dWatt-CFL | PGE | Res | New | CZ05 | 0.541 | 4.7e-05 | 0 | 0.53025 | 4.9999e-05 | -0.013204 | 0.541 | 4.7e-05 | 0 | 0.53025 | 4.9999e-05 | -0.013204 |  | CFL | None | 541 | 0.047 | 541 | 0.047 | 0.98 | 1.06 | -0.024407 | 541 | 0.047 | 541 | 0.047 | 0.98 | 1.06 | -0.0244
CFLNonePGEResNewCZ11 | Res-Iltg-dWatt-CFL | PGE | Res | New | CZ11 | 0.541 | 4.4e-05 | 0 | 0.59878 | 7.0329e-05 | -0.011383 | 0.541 | 4.4e-05 | 0 | 0.59878 | 7.0329e-05 | -0.011383 |  | CFL | None | 541 | 0.044 | 541 | 0.044 | 1.11 | 1.6 | -0.021041 | 541 | 0.044 | 541 | 0.044 | 1.11 | 1.6 | -0.021
CFLNonePGEResNewCZ12 | Res-Iltg-dWatt-CFL | PGE | Res | New | CZ12 | 0.541 | 4.5e-05 | 0 | 0.58044 | 6.9129e-05 | -0.011227 | 0.541 | 4.5e-05 | 0 | 0.58044 | 6.9129e-05 | -0.011227 |  | CFL | None | 541 | 0.045 | 541 | 0.045 | 1.07 | 1.54 | -0.020753 | 541 | 0.045 | 541 | 0.045 | 1.07 | 1.54 | -0.0208
CFLNonePGEResNewCZ13 | Res-Iltg-dWatt-CFL | PGE | Res | New | CZ13 | 0.541 | 4.5e-05 | 0 | 0.59889 | 6.4859e-05 | -0.012 | 0.541 | 4.5e-05 | 0 | 0.59889 | 6.4859e-05 | -0.012 |  | CFL | None | 541 | 0.045 | 541 | 0.045 | 1.11 | 1.44 | -0.022181 | 541 | 0.045 | 541 | 0.045 | 1.11 | 1.44 | -0.0222
CFLNonePGEResNewCZ16 | Res-Iltg-dWatt-CFL | PGE | Res | New | CZ16 | 0.541 | 4.5e-05 | 0 | 0.534 | 5.49e-05 | -0.0133 | 0.541 | 4.5e-05 | 0 | 0.534 | 5.49e-05 | -0.0133 |  | CFL | None | 541 | 0.045 | 541 | 0.045 | 0.987 | 1.22 | -0.024584 | 541 | 0.045 | 541 | 0.045 | 0.987 | 1.22 | -0.0246
CFLNonePGEResNewIOU | Res-Iltg-dWatt-CFL | PGE | Res | New | IOU | 0.541 | 4.4748e-05 | 0 | 0.57052 | 6.2971e-05 | -0.01133 | 0.541 | 4.4748e-05 | 0 | 0.57052 | 6.2971e-05 | -0.01133 |  | CFL | None | 541 | 0.0447 | 541 | 0.0447 | 1.05 | 1.41 | -0.020943 | 541 | 0.0447 | 541 | 0.0447 | 1.05 | 1.41 | -0.0209
CFLNonePGESFmExCZ01 | Res-Iltg-dWatt-CFL | PGE | SFm | Ex | CZ01 | 0.541 | 4.9e-05 | 0 | 0.525 | 4.94e-05 | -0.0152 | 0.541 | 4.9e-05 | 0 | 0.525 | 4.94e-05 | -0.0152 |  | CFL | None | 541 | 0.049 | 541 | 0.049 | 0.97 | 1.01 | -0.028096 | 541 | 0.049 | 541 | 0.049 | 0.97 | 1.01 | -0.0281
CFLNonePGESFmExCZ02 | Res-Iltg-dWatt-CFL | PGE | SFm | Ex | CZ02 | 0.541 | 4.3e-05 | 0 | 0.536 | 5.68e-05 | -0.0149 | 0.541 | 4.3e-05 | 0 | 0.536 | 5.68e-05 | -0.0149 |  | CFL | None | 541 | 0.043 | 541 | 0.043 | 0.991 | 1.32 | -0.027542 | 541 | 0.043 | 541 | 0.043 | 0.991 | 1.32 | -0.0275
CFLNonePGESFmExCZ03 | Res-Iltg-dWatt-CFL | PGE | SFm | Ex | CZ03 | 0.541 | 4.3e-05 | 0 | 0.526 | 4.71e-05 | -0.0161 | 0.541 | 4.3e-05 | 0 | 0.526 | 4.71e-05 | -0.0161 |  | CFL | None | 541 | 0.043 | 541 | 0.043 | 0.972 | 1.1 | -0.02976 | 541 | 0.043 | 541 | 0.043 | 0.972 | 1.1 | -0.0298
CFLNonePGESFmExCZ04 | Res-Iltg-dWatt-CFL | PGE | SFm | Ex | CZ04 | 0.541 | 4.3e-05 | 0 | 0.551 | 5.56e-05 | -0.0121 | 0.541 | 4.3e-05 | 0 | 0.551 | 5.56e-05 | -0.0121 |  | CFL | None | 541 | 0.043 | 541 | 0.043 | 1.02 | 1.29 | -0.022366 | 541 | 0.043 | 541 | 0.043 | 1.02 | 1.29 | -0.0224
CFLNonePGESFmExCZ05 | Res-Iltg-dWatt-CFL | PGE | SFm | Ex | CZ05 | 0.541 | 4.7e-05 | 0 | 0.524 | 5.01e-05 | -0.0162 | 0.541 | 4.7e-05 | 0 | 0.524 | 5.01e-05 | -0.0162 |  | CFL | None | 541 | 0.047 | 541 | 0.047 | 0.969 | 1.07 | -0.029945 | 541 | 0.047 | 541 | 0.047 | 0.969 | 1.07 | -0.0299
CFLNonePGESFmExCZ11 | Res-Iltg-dWatt-CFL | PGE | SFm | Ex | CZ11 | 0.541 | 4.4e-05 | 0 | 0.592 | 7.3e-05 | -0.0122 | 0.541 | 4.4e-05 | 0 | 0.592 | 7.3e-05 | -0.0122 |  | CFL | None | 541 | 0.044 | 541 | 0.044 | 1.09 | 1.66 | -0.022551 | 541 | 0.044 | 541 | 0.044 | 1.09 | 1.66 | -0.0226
CFLNonePGESFmExCZ12 | Res-Iltg-dWatt-CFL | PGE | SFm | Ex | CZ12 | 0.541 | 4.5e-05 | 0 | 0.576 | 7.31e-05 | -0.013 | 0.541 | 4.5e-05 | 0 | 0.576 | 7.31e-05 | -0.013 |  | CFL | None | 541 | 0.045 | 541 | 0.045 | 1.06 | 1.62 | -0.02403 | 541 | 0.045 | 541 | 0.045 | 1.06 | 1.62 | -0.024
CFLNonePGESFmExCZ13 | Res-Iltg-dWatt-CFL | PGE | SFm | Ex | CZ13 | 0.541 | 4.5e-05 | 0 | 0.601 | 7.19e-05 | -0.0124 | 0.541 | 4.5e-05 | 0 | 0.601 | 7.19e-05 | -0.0124 |  | CFL | None | 541 | 0.045 | 541 | 0.045 | 1.11 | 1.6 | -0.022921 | 541 | 0.045 | 541 | 0.045 | 1.11 | 1.6 | -0.0229
CFLNonePGESFmExCZ16 | Res-Iltg-dWatt-CFL | PGE | SFm | Ex | CZ16 | 0.541 | 4.5e-05 | 0 | 0.545 | 5.82e-05 | -0.0152 | 0.541 | 4.5e-05 | 0 | 0.545 | 5.82e-05 | -0.0152 |  | CFL | None | 541 | 0.045 | 541 | 0.045 | 1.01 | 1.29 | -0.028096 | 541 | 0.045 | 541 | 0.045 | 1.01 | 1.29 | -0.0281
CFLNonePGESFmExIOU | Res-Iltg-dWatt-CFL | PGE | SFm | Ex | IOU | 0.541 | 4.4e-05 | 0 | 0.558 | 6.12e-05 | -0.0138 | 0.541 | 4.4e-05 | 0 | 0.558 | 6.12e-05 | -0.0138 |  | CFL | None | 541 | 0.044 | 541 | 0.044 | 1.03 | 1.39 | -0.025508 | 541 | 0.044 | 541 | 0.044 | 1.03 | 1.39 | -0.0255
CFLNonePGESFmNewCZ01 | Res-Iltg-dWatt-CFL | PGE | SFm | New | CZ01 | 0.541 | 4.9e-05 | 0 | 0.529 | 4.93e-05 | -0.0125 | 0.541 | 4.9e-05 | 0 | 0.529 | 4.93e-05 | -0.0125 |  | CFL | None | 541 | 0.049 | 541 | 0.049 | 0.978 | 1.01 | -0.023105 | 541 | 0.049 | 541 | 0.049 | 0.978 | 1.01 | -0.0231
CFLNonePGESFmNewCZ02 | Res-Iltg-dWatt-CFL | PGE | SFm | New | CZ02 | 0.541 | 4.3e-05 | 0 | 0.555 | 6.75e-05 | -0.0162 | 0.541 | 4.3e-05 | 0 | 0.555 | 6.75e-05 | -0.0162 |  | CFL | None | 541 | 0.043 | 541 | 0.043 | 1.03 | 1.57 | -0.029945 | 541 | 0.043 | 541 | 0.043 | 1.03 | 1.57 | -0.0299
CFLNonePGESFmNewCZ03 | Res-Iltg-dWatt-CFL | PGE | SFm | New | CZ03 | 0.541 | 4.3e-05 | 0 | 0.535 | 4.97e-05 | -0.0119 | 0.541 | 4.3e-05 | 0 | 0.535 | 4.97e-05 | -0.0119 |  | CFL | None | 541 | 0.043 | 541 | 0.043 | 0.989 | 1.16 | -0.021996 | 541 | 0.043 | 541 | 0.043 | 0.989 | 1.16 | -0.022
CFLNonePGESFmNewCZ04 | Res-Iltg-dWatt-CFL | PGE | SFm | New | CZ04 | 0.541 | 4.3e-05 | 0 | 0.569 | 6.51e-05 | -0.0122 | 0.541 | 4.3e-05 | 0 | 0.569 | 6.51e-05 | -0.0122 |  | CFL | None | 541 | 0.043 | 541 | 0.043 | 1.05 | 1.51 | -0.022551 | 541 | 0.043 | 541 | 0.043 | 1.05 | 1.51 | -0.0226
CFLNonePGESFmNewCZ05 | Res-Iltg-dWatt-CFL | PGE | SFm | New | CZ05 | 0.541 | 4.7e-05 | 0 | 0.531 | 5.01e-05 | -0.0132 | 0.541 | 4.7e-05 | 0 | 0.531 | 5.01e-05 | -0.0132 |  | CFL | None | 541 | 0.047 | 541 | 0.047 | 0.982 | 1.07 | -0.024399 | 541 | 0.047 | 541 | 0.047 | 0.982 | 1.07 | -0.0244
CFLNonePGESFmNewCZ11 | Res-Iltg-dWatt-CFL | PGE | SFm | New | CZ11 | 0.541 | 4.4e-05 | 0 | 0.598 | 7.07e-05 | -0.0115 | 0.541 | 4.4e-05 | 0 | 0.598 | 7.07e-05 | -0.0115 |  | CFL | None | 541 | 0.044 | 541 | 0.044 | 1.11 | 1.61 | -0.021257 | 541 | 0.044 | 541 | 0.044 | 1.11 | 1.61 | -0.0213
CFLNonePGESFmNewCZ12 | Res-Iltg-dWatt-CFL | PGE | SFm | New | CZ12 | 0.541 | 4.5e-05 | 0 | 0.578 | 7.04e-05 | -0.0119 | 0.541 | 4.5e-05 | 0 | 0.578 | 7.04e-05 | -0.0119 |  | CFL | None | 541 | 0.045 | 541 | 0.045 | 1.07 | 1.56 | -0.021996 | 541 | 0.045 | 541 | 0.045 | 1.07 | 1.56 | -0.022
CFLNonePGESFmNewCZ13 | Res-Iltg-dWatt-CFL | PGE | SFm | New | CZ13 | 0.541 | 4.5e-05 | 0 | 0.6 | 6.55e-05 | -0.0123 | 0.541 | 4.5e-05 | 0 | 0.6 | 6.55e-05 | -0.0123 |  | CFL | None | 541 | 0.045 | 541 | 0.045 | 1.11 | 1.46 | -0.022736 | 541 | 0.045 | 541 | 0.045 | 1.11 | 1.46 | -0.0227
CFLNonePGESFmNewCZ16 | Res-Iltg-dWatt-CFL | PGE | SFm | New | CZ16 | 0.541 | 4.5e-05 | 0 | 0.534 | 5.49e-05 | -0.0133 | 0.541 | 4.5e-05 | 0 | 0.534 | 5.49e-05 | -0.0133 |  | CFL | None | 541 | 0.045 | 541 | 0.045 | 0.987 | 1.22 | -0.024584 | 541 | 0.045 | 541 | 0.045 | 0.987 | 1.22 | -0.0246
CFLNonePGESFmNewIOU | Res-Iltg-dWatt-CFL | PGE | SFm | New | IOU | 0.541 | 4.5e-05 | 0 | 0.575 | 6.61e-05 | -0.0122 | 0.541 | 4.5e-05 | 0 | 0.575 | 6.61e-05 | -0.0122 |  | CFL | None | 541 | 0.045 | 541 | 0.045 | 1.06 | 1.47 | -0.022551 | 541 | 0.045 | 541 | 0.045 | 1.06 | 1.47 | -0.0226
CFLNoneSCEDMoExCZ05 | Res-Iltg-dWatt-CFL | SCE | DMo | Ex | CZ05 | 0.541 | 4.7e-05 | 0 | 0.546 | 6.96e-05 | -0.0133 | 0.541 | 4.7e-05 | 0 | 0.546 | 6.96e-05 | -0.0133 |  | CFL | None | 541 | 0.047 | 541 | 0.047 | 1.01 | 1.48 | -0.024584 | 541 | 0.047 | 541 | 0.047 | 1.01 | 1.48 | -0.0246
CFLNoneSCEDMoExCZ06 | Res-Iltg-dWatt-CFL | SCE | DMo | Ex | CZ06 | 0.541 | 4.3e-05 | 0 | 0.555 | 5.02e-05 | -0.00878 | 0.541 | 4.3e-05 | 0 | 0.555 | 5.02e-05 | -0.00878 |  | CFL | None | 541 | 0.043 | 541 | 0.043 | 1.03 | 1.17 | -0.016229 | 541 | 0.043 | 541 | 0.043 | 1.03 | 1.17 | -0.0162
CFLNoneSCEDMoExCZ08 | Res-Iltg-dWatt-CFL | SCE | DMo | Ex | CZ08 | 0.541 | 4.7e-05 | 0 | 0.63 | 7.42e-05 | -0.00848 | 0.541 | 4.7e-05 | 0 | 0.63 | 7.42e-05 | -0.00848 |  | CFL | None | 541 | 0.047 | 541 | 0.047 | 1.16 | 1.58 | -0.015675 | 541 | 0.047 | 541 | 0.047 | 1.16 | 1.58 | -0.0157
CFLNoneSCEDMoExCZ09 | Res-Iltg-dWatt-CFL | SCE | DMo | Ex | CZ09 | 0.541 | 4.5e-05 | 0 | 0.641 | 7.23e-05 | -0.00891 | 0.541 | 4.5e-05 | 0 | 0.641 | 7.23e-05 | -0.00891 |  | CFL | None | 541 | 0.045 | 541 | 0.045 | 1.18 | 1.61 | -0.01647 | 541 | 0.045 | 541 | 0.045 | 1.18 | 1.61 | -0.0165
CFLNoneSCEDMoExCZ10 | Res-Iltg-dWatt-CFL | SCE | DMo | Ex | CZ10 | 0.541 | 4.3e-05 | 0 | 0.645 | 7.71e-05 | -0.00963 | 0.541 | 4.3e-05 | 0 | 0.645 | 7.71e-05 | -0.00963 |  | CFL | None | 541 | 0.043 | 541 | 0.043 | 1.19 | 1.79 | -0.0178 | 541 | 0.043 | 541 | 0.043 | 1.19 | 1.79 | -0.0178
CFLNoneSCEDMoExCZ13 | Res-Iltg-dWatt-CFL | SCE | DMo | Ex | CZ13 | 0.541 | 4.5e-05 | 0 | 0.649 | 7.95e-05 | -0.0103 | 0.541 | 4.5e-05 | 0 | 0.649 | 7.95e-05 | -0.0103 |  | CFL | None | 541 | 0.045 | 541 | 0.045 | 1.2 | 1.77 | -0.019039 | 541 | 0.045 | 541 | 0.045 | 1.2 | 1.77 | -0.019
CFLNoneSCEDMoExCZ14 | Res-Iltg-dWatt-CFL | SCE | DMo | Ex | CZ14 | 0.541 | 4.3e-05 | 0 | 0.67 | 7.63e-05 | -0.00987 | 0.541 | 4.3e-05 | 0 | 0.67 | 7.63e-05 | -0.00987 |  | CFL | None | 541 | 0.043 | 541 | 0.043 | 1.24 | 1.77 | -0.018244 | 541 | 0.043 | 541 | 0.043 | 1.24 | 1.77 | -0.0182
CFLNoneSCEDMoExCZ15 | Res-Iltg-dWatt-CFL | SCE | DMo | Ex | CZ15 | 0.541 | 4.4e-05 | 0 | 0.735 | 7.69e-05 | -0.00625 | 0.541 | 4.4e-05 | 0 | 0.735 | 7.69e-05 | -0.00625 |  | CFL | None | 541 | 0.044 | 541 | 0.044 | 1.36 | 1.75 | -0.011553 | 541 | 0.044 | 541 | 0.044 | 1.36 | 1.75 | -0.0116
CFLNoneSCEDMoExCZ16 | Res-Iltg-dWatt-CFL | SCE | DMo | Ex | CZ16 | 0.541 | 4.5e-05 | 0 | 0.585 | 7.31e-05 | -0.0131 | 0.541 | 4.5e-05 | 0 | 0.585 | 7.31e-05 | -0.0131 |  | CFL | None | 541 | 0.045 | 541 | 0.045 | 1.08 | 1.62 | -0.024214 | 541 | 0.045 | 541 | 0.045 | 1.08 | 1.62 | -0.0242
CFLNoneSCEDMoExIOU | Res-Iltg-dWatt-CFL | SCE | DMo | Ex | IOU | 0.541 | 4.4e-05 | 0 | 0.628 | 7.11e-05 | -0.00946 | 0.541 | 4.4e-05 | 0 | 0.628 | 7.11e-05 | -0.00946 |  | CFL | None | 541 | 0.044 | 541 | 0.044 | 1.16 | 1.62 | -0.017486 | 541 | 0.044 | 541 | 0.044 | 1.16 | 1.62 | -0.0175
CFLNoneSCEDMoNewCZ05 | Res-Iltg-dWatt-CFL | SCE | DMo | New | CZ05 | 0.541 | 4.7e-05 | 0 | 0.537 | 5.47e-05 | -0.0133 | 0.541 | 4.7e-05 | 0 | 0.537 | 5.47e-05 | -0.0133 |  | CFL | None | 541 | 0.047 | 541 | 0.047 | 0.993 | 1.16 | -0.024584 | 541 | 0.047 | 541 | 0.047 | 0.993 | 1.16 | -0.0246
CFLNoneSCEDMoNewCZ06 | Res-Iltg-dWatt-CFL | SCE | DMo | New | CZ06 | 0.541 | 4.3e-05 | 0 | 0.531 | 4.39e-05 | -0.0083 | 0.541 | 4.3e-05 | 0 | 0.531 | 4.39e-05 | -0.0083 |  | CFL | None | 541 | 0.043 | 541 | 0.043 | 0.982 | 1.02 | -0.015342 | 541 | 0.043 | 541 | 0.043 | 0.982 | 1.02 | -0.0153
CFLNoneSCEDMoNewCZ08 | Res-Iltg-dWatt-CFL | SCE | DMo | New | CZ08 | 0.541 | 4.7e-05 | 0 | 0.623 | 6.6e-05 | -0.00721 | 0.541 | 4.7e-05 | 0 | 0.623 | 6.6e-05 | -0.00721 |  | CFL | None | 541 | 0.047 | 541 | 0.047 | 1.15 | 1.4 | -0.013327 | 541 | 0.047 | 541 | 0.047 | 1.15 | 1.4 | -0.0133
CFLNoneSCEDMoNewCZ09 | Res-Iltg-dWatt-CFL | SCE | DMo | New | CZ09 | 0.541 | 4.5e-05 | 0 | 0.631 | 6.7e-05 | -0.00839 | 0.541 | 4.5e-05 | 0 | 0.631 | 6.7e-05 | -0.00839 |  | CFL | None | 541 | 0.045 | 541 | 0.045 | 1.17 | 1.49 | -0.015508 | 541 | 0.045 | 541 | 0.045 | 1.17 | 1.49 | -0.0155
CFLNoneSCEDMoNewCZ10 | Res-Iltg-dWatt-CFL | SCE | DMo | New | CZ10 | 0.541 | 4.3e-05 | 0 | 0.627 | 6.57e-05 | -0.00957 | 0.541 | 4.3e-05 | 0 | 0.627 | 6.57e-05 | -0.00957 |  | CFL | None | 541 | 0.043 | 541 | 0.043 | 1.16 | 1.53 | -0.017689 | 541 | 0.043 | 541 | 0.043 | 1.16 | 1.53 | -0.0177
CFLNoneSCEDMoNewCZ13 | Res-Iltg-dWatt-CFL | SCE | DMo | New | CZ13 | 0.541 | 4.5e-05 | 0 | 0.578 | 5.75e-05 | -0.0109 | 0.541 | 4.5e-05 | 0 | 0.578 | 5.75e-05 | -0.0109 |  | CFL | None | 541 | 0.045 | 541 | 0.045 | 1.07 | 1.28 | -0.020148 | 541 | 0.045 | 541 | 0.045 | 1.07 | 1.28 | -0.0201
CFLNoneSCEDMoNewCZ14 | Res-Iltg-dWatt-CFL | SCE | DMo | New | CZ14 | 0.541 | 4.3e-05 | 0 | 0.589 | 5.66e-05 | -0.0107 | 0.541 | 4.3e-05 | 0 | 0.589 | 5.66e-05 | -0.0107 |  | CFL | None | 541 | 0.043 | 541 | 0.043 | 1.09 | 1.32 | -0.019778 | 541 | 0.043 | 541 | 0.043 | 1.09 | 1.32 | -0.0198
CFLNoneSCEDMoNewCZ15 | Res-Iltg-dWatt-CFL | SCE | DMo | New | CZ15 | 0.541 | 4.4e-05 | 0 | 0.676 | 6.87e-05 | -0.0068 | 0.541 | 4.4e-05 | 0 | 0.676 | 6.87e-05 | -0.0068 |  | CFL | None | 541 | 0.044 | 541 | 0.044 | 1.25 | 1.56 | -0.012569 | 541 | 0.044 | 541 | 0.044 | 1.25 | 1.56 | -0.0126
CFLNoneSCEDMoNewCZ16 | Res-Iltg-dWatt-CFL | SCE | DMo | New | CZ16 | 0.541 | 4.5e-05 | 0 | 0.562 | 6.35e-05 | -0.0117 | 0.541 | 4.5e-05 | 0 | 0.562 | 6.35e-05 | -0.0117 |  | CFL | None | 541 | 0.045 | 541 | 0.045 | 1.04 | 1.41 | -0.021627 | 541 | 0.045 | 541 | 0.045 | 1.04 | 1.41 | -0.0216
CFLNoneSCEDMoNewIOU | Res-Iltg-dWatt-CFL | SCE | DMo | New | IOU | 0.541 | 4.4e-05 | 0 | 0.589 | 5.65e-05 | -0.00824 | 0.541 | 4.4e-05 | 0 | 0.589 | 5.65e-05 | -0.00824 |  | CFL | None | 541 | 0.044 | 541 | 0.044 | 1.09 | 1.28 | -0.015231 | 541 | 0.044 | 541 | 0.044 | 1.09 | 1.28 | -0.0152
CFLNoneSCEMFmExCZ05 | Res-Iltg-dWatt-CFL | SCE | MFm | Ex | CZ05 | 0.541 | 4.7e-05 | 0 | 0.537 | 4.73e-05 | -0.0158 | 0.541 | 4.7e-05 | 0 | 0.537 | 4.73e-05 | -0.0158 |  | CFL | None | 541 | 0.047 | 541 | 0.047 | 0.993 | 1.01 | -0.029205 | 541 | 0.047 | 541 | 0.047 | 0.993 | 1.01 | -0.0292
CFLNoneSCEMFmExCZ06 | Res-Iltg-dWatt-CFL | SCE | MFm | Ex | CZ06 | 0.541 | 4.3e-05 | 0 | 0.543 | 5.13e-05 | -0.00837 | 0.541 | 4.3e-05 | 0 | 0.543 | 5.13e-05 | -0.00837 |  | CFL | None | 541 | 0.043 | 541 | 0.043 | 1 | 1.19 | -0.015471 | 541 | 0.043 | 541 | 0.043 | 1 | 1.19 | -0.0155
CFLNoneSCEMFmExCZ08 | Res-Iltg-dWatt-CFL | SCE | MFm | Ex | CZ08 | 0.541 | 4.7e-05 | 0 | 0.566 | 5.92e-05 | -0.00772 | 0.541 | 4.7e-05 | 0 | 0.566 | 5.92e-05 | -0.00772 |  | CFL | None | 541 | 0.047 | 541 | 0.047 | 1.05 | 1.26 | -0.01427 | 541 | 0.047 | 541 | 0.047 | 1.05 | 1.26 | -0.0143
CFLNoneSCEMFmExCZ09 | Res-Iltg-dWatt-CFL | SCE | MFm | Ex | CZ09 | 0.541 | 4.5e-05 | 0 | 0.592 | 6.05e-05 | -0.00809 | 0.541 | 4.5e-05 | 0 | 0.592 | 6.05e-05 | -0.00809 |  | CFL | None | 541 | 0.045 | 541 | 0.045 | 1.09 | 1.34 | -0.014954 | 541 | 0.045 | 541 | 0.045 | 1.09 | 1.34 | -0.015
CFLNoneSCEMFmExCZ10 | Res-Iltg-dWatt-CFL | SCE | MFm | Ex | CZ10 | 0.541 | 4.3e-05 | 0 | 0.585 | 6.54e-05 | -0.00821 | 0.541 | 4.3e-05 | 0 | 0.585 | 6.54e-05 | -0.00821 |  | CFL | None | 541 | 0.043 | 541 | 0.043 | 1.08 | 1.52 | -0.015176 | 541 | 0.043 | 541 | 0.043 | 1.08 | 1.52 | -0.0152
CFLNoneSCEMFmExCZ13 | Res-Iltg-dWatt-CFL | SCE | MFm | Ex | CZ13 | 0.541 | 4.5e-05 | 0 | 0.595 | 6.48e-05 | -0.00934 | 0.541 | 4.5e-05 | 0 | 0.595 | 6.48e-05 | -0.00934 |  | CFL | None | 541 | 0.045 | 541 | 0.045 | 1.1 | 1.44 | -0.017264 | 541 | 0.045 | 541 | 0.045 | 1.1 | 1.44 | -0.0173
CFLNoneSCEMFmExCZ14 | Res-Iltg-dWatt-CFL | SCE | MFm | Ex | CZ14 | 0.541 | 4.3e-05 | 0 | 0.611 | 6.17e-05 | -0.009 | 0.541 | 4.3e-05 | 0 | 0.611 | 6.17e-05 | -0.009 |  | CFL | None | 541 | 0.043 | 541 | 0.043 | 1.13 | 1.43 | -0.016636 | 541 | 0.043 | 541 | 0.043 | 1.13 | 1.43 | -0.0166
CFLNoneSCEMFmExCZ15 | Res-Iltg-dWatt-CFL | SCE | MFm | Ex | CZ15 | 0.541 | 4.4e-05 | 0 | 0.66 | 6.4e-05 | -0.00439 | 0.541 | 4.4e-05 | 0 | 0.66 | 6.4e-05 | -0.00439 |  | CFL | None | 541 | 0.044 | 541 | 0.044 | 1.22 | 1.45 | -0.0081146 | 541 | 0.044 | 541 | 0.044 | 1.22 | 1.45 | -0.00811
CFLNoneSCEMFmExCZ16 | Res-Iltg-dWatt-CFL | SCE | MFm | Ex | CZ16 | 0.541 | 4.5e-05 | 0 | 0.551 | 5.93e-05 | -0.0123 | 0.541 | 4.5e-05 | 0 | 0.551 | 5.93e-05 | -0.0123 |  | CFL | None | 541 | 0.045 | 541 | 0.045 | 1.02 | 1.32 | -0.022736 | 541 | 0.045 | 541 | 0.045 | 1.02 | 1.32 | -0.0227
CFLNoneSCEMFmExIOU | Res-Iltg-dWatt-CFL | SCE | MFm | Ex | IOU | 0.541 | 4.5e-05 | 0 | 0.571 | 5.81e-05 | -0.00802 | 0.541 | 4.5e-05 | 0 | 0.571 | 5.81e-05 | -0.00802 |  | CFL | None | 541 | 0.045 | 541 | 0.045 | 1.06 | 1.29 | -0.014824 | 541 | 0.045 | 541 | 0.045 | 1.06 | 1.29 | -0.0148
CFLNoneSCEMFmNewCZ05 | Res-Iltg-dWatt-CFL | SCE | MFm | New | CZ05 | 0.541 | 4.7e-05 | 0 | 0.55 | 5.34e-05 | -0.00713 | 0.541 | 4.7e-05 | 0 | 0.55 | 5.34e-05 | -0.00713 |  | CFL | None | 541 | 0.047 | 541 | 0.047 | 1.02 | 1.14 | -0.013179 | 541 | 0.047 | 541 | 0.047 | 1.02 | 1.14 | -0.0132
CFLNoneSCEMFmNewCZ06 | Res-Iltg-dWatt-CFL | SCE | MFm | New | CZ06 | 0.541 | 4.3e-05 | 0 | 0.572 | 6.18e-05 | -0.00649 | 0.541 | 4.3e-05 | 0 | 0.572 | 6.18e-05 | -0.00649 |  | CFL | None | 541 | 0.043 | 541 | 0.043 | 1.06 | 1.44 | -0.011996 | 541 | 0.043 | 541 | 0.043 | 1.06 | 1.44 | -0.012
CFLNoneSCEMFmNewCZ08 | Res-Iltg-dWatt-CFL | SCE | MFm | New | CZ08 | 0.541 | 4.7e-05 | 0 | 0.609 | 6.56e-05 | -0.00481 | 0.541 | 4.7e-05 | 0 | 0.609 | 6.56e-05 | -0.00481 |  | CFL | None | 541 | 0.047 | 541 | 0.047 | 1.13 | 1.4 | -0.0088909 | 541 | 0.047 | 541 | 0.047 | 1.13 | 1.4 | -0.00889
CFLNoneSCEMFmNewCZ09 | Res-Iltg-dWatt-CFL | SCE | MFm | New | CZ09 | 0.541 | 4.5e-05 | 0 | 0.612 | 6.46e-05 | -0.00512 | 0.541 | 4.5e-05 | 0 | 0.612 | 6.46e-05 | -0.00512 |  | CFL | None | 541 | 0.045 | 541 | 0.045 | 1.13 | 1.44 | -0.009464 | 541 | 0.045 | 541 | 0.045 | 1.13 | 1.44 | -0.00946
CFLNoneSCEMFmNewCZ10 | Res-Iltg-dWatt-CFL | SCE | MFm | New | CZ10 | 0.541 | 4.3e-05 | 0 | 0.606 | 6.26e-05 | -0.00487 | 0.541 | 4.3e-05 | 0 | 0.606 | 6.26e-05 | -0.00487 |  | CFL | None | 541 | 0.043 | 541 | 0.043 | 1.12 | 1.46 | -0.0090018 | 541 | 0.043 | 541 | 0.043 | 1.12 | 1.46 | -0.009
CFLNoneSCEMFmNewCZ13 | Res-Iltg-dWatt-CFL | SCE | MFm | New | CZ13 | 0.541 | 4.5e-05 | 0 | 0.609 | 6.14e-05 | -0.0074 | 0.541 | 4.5e-05 | 0 | 0.609 | 6.14e-05 | -0.0074 |  | CFL | None | 541 | 0.045 | 541 | 0.045 | 1.13 | 1.36 | -0.013678 | 541 | 0.045 | 541 | 0.045 | 1.13 | 1.36 | -0.0137
CFLNoneSCEMFmNewCZ14 | Res-Iltg-dWatt-CFL | SCE | MFm | New | CZ14 | 0.541 | 4.3e-05 | 0 | 0.606 | 5.94e-05 | -0.00742 | 0.541 | 4.3e-05 | 0 | 0.606 | 5.94e-05 | -0.00742 |  | CFL | None | 541 | 0.043 | 541 | 0.043 | 1.12 | 1.38 | -0.013715 | 541 | 0.043 | 541 | 0.043 | 1.12 | 1.38 | -0.0137
CFLNoneSCEMFmNewCZ15 | Res-Iltg-dWatt-CFL | SCE | MFm | New | CZ15 | 0.541 | 4.4e-05 | 0 | 0.635 | 6.04e-05 | -0.00228 | 0.541 | 4.4e-05 | 0 | 0.635 | 6.04e-05 | -0.00228 |  | CFL | None | 541 | 0.044 | 541 | 0.044 | 1.17 | 1.37 | -0.0042144 | 541 | 0.044 | 541 | 0.044 | 1.17 | 1.37 | -0.00421
CFLNoneSCEMFmNewCZ16 | Res-Iltg-dWatt-CFL | SCE | MFm | New | CZ16 | 0.541 | 4.5e-05 | 0 | 0.566 | 5.78e-05 | -0.0112 | 0.541 | 4.5e-05 | 0 | 0.566 | 5.78e-05 | -0.0112 |  | CFL | None | 541 | 0.045 | 541 | 0.045 | 1.05 | 1.28 | -0.020702 | 541 | 0.045 | 541 | 0.045 | 1.05 | 1.28 | -0.0207
CFLNoneSCEMFmNewIOU | Res-Iltg-dWatt-CFL | SCE | MFm | New | IOU | 0.541 | 4.5e-05 | 0 | 0.598 | 6.4e-05 | -0.00544 | 0.541 | 4.5e-05 | 0 | 0.598 | 6.4e-05 | -0.00544 |  | CFL | None | 541 | 0.045 | 541 | 0.045 | 1.11 | 1.42 | -0.010055 | 541 | 0.045 | 541 | 0.045 | 1.11 | 1.42 | -0.0101
CFLNoneSCEResExCZ05 | Res-Iltg-dWatt-CFL | SCE | Res | Ex | CZ05 | 0.541 | 4.7e-05 | 0 | 0.52957 | 5.1089e-05 | -0.016097 | 0.541 | 4.7e-05 | 0 | 0.52957 | 5.1089e-05 | -0.016097 |  | CFL | None | 541 | 0.047 | 541 | 0.047 | 0.979 | 1.09 | -0.029755 | 541 | 0.047 | 541 | 0.047 | 0.979 | 1.09 | -0.0298
CFLNoneSCEResExCZ06 | Res-Iltg-dWatt-CFL | SCE | Res | Ex | CZ06 | 0.541 | 4.3e-05 | 0 | 0.54497 | 5.1715e-05 | -0.0096175 | 0.541 | 4.3e-05 | 0 | 0.54497 | 5.1715e-05 | -0.0096175 |  | CFL | None | 541 | 0.043 | 541 | 0.043 | 1.01 | 1.2 | -0.017777 | 541 | 0.043 | 541 | 0.043 | 1.01 | 1.2 | -0.0178
CFLNoneSCEResExCZ08 | Res-Iltg-dWatt-CFL | SCE | Res | Ex | CZ08 | 0.541 | 4.7e-05 | 0 | 0.56823 | 6.011e-05 | -0.0094112 | 0.541 | 4.7e-05 | 0 | 0.56823 | 6.011e-05 | -0.0094112 |  | CFL | None | 541 | 0.047 | 541 | 0.047 | 1.05 | 1.28 | -0.017396 | 541 | 0.047 | 541 | 0.047 | 1.05 | 1.28 | -0.0174
CFLNoneSCEResExCZ09 | Res-Iltg-dWatt-CFL | SCE | Res | Ex | CZ09 | 0.541 | 4.5e-05 | 0 | 0.59194 | 6.3563e-05 | -0.010172 | 0.541 | 4.5e-05 | 0 | 0.59194 | 6.3563e-05 | -0.010172 |  | CFL | None | 541 | 0.045 | 541 | 0.045 | 1.09 | 1.41 | -0.018802 | 541 | 0.045 | 541 | 0.045 | 1.09 | 1.41 | -0.0188
CFLNoneSCEResExCZ10 | Res-Iltg-dWatt-CFL | SCE | Res | Ex | CZ10 | 0.541 | 4.3e-05 | 0 | 0.59232 | 6.8138e-05 | -0.010998 | 0.541 | 4.3e-05 | 0 | 0.59232 | 6.8138e-05 | -0.010998 |  | CFL | None | 541 | 0.043 | 541 | 0.043 | 1.09 | 1.58 | -0.020329 | 541 | 0.043 | 541 | 0.043 | 1.09 | 1.58 | -0.0203
CFLNoneSCEResExCZ13 | Res-Iltg-dWatt-CFL | SCE | Res | Ex | CZ13 | 0.541 | 4.5e-05 | 0 | 0.60494 | 7.2184e-05 | -0.012063 | 0.541 | 4.5e-05 | 0 | 0.60494 | 7.2184e-05 | -0.012063 |  | CFL | None | 541 | 0.045 | 541 | 0.045 | 1.12 | 1.6 | -0.022297 | 541 | 0.045 | 541 | 0.045 | 1.12 | 1.6 | -0.0223
CFLNoneSCEResExCZ14 | Res-Iltg-dWatt-CFL | SCE | Res | Ex | CZ14 | 0.541 | 4.3e-05 | 0 | 0.61662 | 6.4793e-05 | -0.012706 | 0.541 | 4.3e-05 | 0 | 0.61662 | 6.4793e-05 | -0.012706 |  | CFL | None | 541 | 0.043 | 541 | 0.043 | 1.14 | 1.51 | -0.023486 | 541 | 0.043 | 541 | 0.043 | 1.14 | 1.51 | -0.0235
CFLNoneSCEResExCZ15 | Res-Iltg-dWatt-CFL | SCE | Res | Ex | CZ15 | 0.541 | 4.4e-05 | 0 | 0.66214 | 6.7995e-05 | -0.0064261 | 0.541 | 4.4e-05 | 0 | 0.66214 | 6.7995e-05 | -0.0064261 |  | CFL | None | 541 | 0.044 | 541 | 0.044 | 1.22 | 1.55 | -0.011878 | 541 | 0.044 | 541 | 0.044 | 1.22 | 1.55 | -0.0119
CFLNoneSCEResExCZ16 | Res-Iltg-dWatt-CFL | SCE | Res | Ex | CZ16 | 0.541 | 4.5e-05 | 0 | 0.55344 | 6.1149e-05 | -0.014636 | 0.541 | 4.5e-05 | 0 | 0.55344 | 6.1149e-05 | -0.014636 |  | CFL | None | 541 | 0.045 | 541 | 0.045 | 1.02 | 1.36 | -0.027054 | 541 | 0.045 | 541 | 0.045 | 1.02 | 1.36 | -0.0271
CFLNoneSCEResExIOU | Res-Iltg-dWatt-CFL | SCE | Res | Ex | IOU | 0.541 | 4.4273e-05 | 0 | 0.57937 | 6.1274e-05 | -0.010376 | 0.541 | 4.4273e-05 | 0 | 0.57937 | 6.1274e-05 | -0.010376 |  | CFL | None | 541 | 0.0443 | 541 | 0.0443 | 1.07 | 1.38 | -0.019179 | 541 | 0.0443 | 541 | 0.0443 | 1.07 | 1.38 | -0.0192
CFLNoneSCEResNewCZ05 | Res-Iltg-dWatt-CFL | SCE | Res | New | CZ05 | 0.541 | 4.7e-05 | 0 | 0.551 | 6.8e-05 | -0.0128 | 0.541 | 4.7e-05 | 0 | 0.551 | 6.8e-05 | -0.0128 |  | CFL | None | 541 | 0.047 | 541 | 0.047 | 1.02 | 1.45 | -0.02366 | 541 | 0.047 | 541 | 0.047 | 1.02 | 1.45 | -0.0237
CFLNoneSCEResNewCZ06 | Res-Iltg-dWatt-CFL | SCE | Res | New | CZ06 | 0.541 | 4.3e-05 | 0 | 0.55305 | 6.0314e-05 | -0.0089974 | 0.541 | 4.3e-05 | 0 | 0.55305 | 6.0314e-05 | -0.0089974 |  | CFL | None | 541 | 0.043 | 541 | 0.043 | 1.02 | 1.4 | -0.016631 | 541 | 0.043 | 541 | 0.043 | 1.02 | 1.4 | -0.0166
CFLNoneSCEResNewCZ08 | Res-Iltg-dWatt-CFL | SCE | Res | New | CZ08 | 0.541 | 4.7e-05 | 0 | 0.59885 | 6.4031e-05 | -0.0071212 | 0.541 | 4.7e-05 | 0 | 0.59885 | 6.4031e-05 | -0.0071212 |  | CFL | None | 541 | 0.047 | 541 | 0.047 | 1.11 | 1.36 | -0.013163 | 541 | 0.047 | 541 | 0.047 | 1.11 | 1.36 | -0.0132
CFLNoneSCEResNewCZ09 | Res-Iltg-dWatt-CFL | SCE | Res | New | CZ09 | 0.541 | 4.5e-05 | 0 | 0.60322 | 6.6454e-05 | -0.0080816 | 0.541 | 4.5e-05 | 0 | 0.60322 | 6.6454e-05 | -0.0080816 |  | CFL | None | 541 | 0.045 | 541 | 0.045 | 1.12 | 1.48 | -0.014938 | 541 | 0.045 | 541 | 0.045 | 1.12 | 1.48 | -0.0149
CFLNoneSCEResNewCZ10 | Res-Iltg-dWatt-CFL | SCE | Res | New | CZ10 | 0.541 | 4.3e-05 | 0 | 0.59936 | 6.6273e-05 | -0.010754 | 0.541 | 4.3e-05 | 0 | 0.59936 | 6.6273e-05 | -0.010754 |  | CFL | None | 541 | 0.043 | 541 | 0.043 | 1.11 | 1.54 | -0.019878 | 541 | 0.043 | 541 | 0.043 | 1.11 | 1.54 | -0.0199
CFLNoneSCEResNewCZ13 | Res-Iltg-dWatt-CFL | SCE | Res | New | CZ13 | 0.541 | 4.5e-05 | 0 | 0.60021 | 6.5406e-05 | -0.012187 | 0.541 | 4.5e-05 | 0 | 0.60021 | 6.5406e-05 | -0.012187 |  | CFL | None | 541 | 0.045 | 541 | 0.045 | 1.11 | 1.45 | -0.022528 | 541 | 0.045 | 541 | 0.045 | 1.11 | 1.45 | -0.0225
CFLNoneSCEResNewCZ14 | Res-Iltg-dWatt-CFL | SCE | Res | New | CZ14 | 0.541 | 4.3e-05 | 0 | 0.609 | 6.27e-05 | -0.0131 | 0.541 | 4.3e-05 | 0 | 0.609 | 6.27e-05 | -0.0131 |  | CFL | None | 541 | 0.043 | 541 | 0.043 | 1.13 | 1.46 | -0.024214 | 541 | 0.043 | 541 | 0.043 | 1.13 | 1.46 | -0.0242
CFLNoneSCEResNewCZ15 | Res-Iltg-dWatt-CFL | SCE | Res | New | CZ15 | 0.541 | 4.4e-05 | 0 | 0.65595 | 6.7289e-05 | -0.0070674 | 0.541 | 4.4e-05 | 0 | 0.65595 | 6.7289e-05 | -0.0070674 |  | CFL | None | 541 | 0.044 | 541 | 0.044 | 1.21 | 1.53 | -0.013064 | 541 | 0.044 | 541 | 0.044 | 1.21 | 1.53 | -0.0131
CFLNoneSCEResNewCZ16 | Res-Iltg-dWatt-CFL | SCE | Res | New | CZ16 | 0.541 | 4.5e-05 | 0 | 0.53074 | 4.8914e-05 | -0.01331 | 0.541 | 4.5e-05 | 0 | 0.53074 | 4.8914e-05 | -0.01331 |  | CFL | None | 541 | 0.045 | 541 | 0.045 | 0.981 | 1.09 | -0.024603 | 541 | 0.045 | 541 | 0.045 | 0.981 | 1.09 | -0.0246
CFLNoneSCEResNewIOU | Res-Iltg-dWatt-CFL | SCE | Res | New | IOU | 0.541 | 4.4173e-05 | 0 | 0.59055 | 6.437e-05 | -0.0095819 | 0.541 | 4.4173e-05 | 0 | 0.59055 | 6.437e-05 | -0.0095819 |  | CFL | None | 541 | 0.0442 | 541 | 0.0442 | 1.09 | 1.46 | -0.017712 | 541 | 0.0442 | 541 | 0.0442 | 1.09 | 1.46 | -0.0177
CFLNoneSCESFmExCZ05 | Res-Iltg-dWatt-CFL | SCE | SFm | Ex | CZ05 | 0.541 | 4.7e-05 | 0 | 0.527 | 5.24e-05 | -0.0162 | 0.541 | 4.7e-05 | 0 | 0.527 | 5.24e-05 | -0.0162 |  | CFL | None | 541 | 0.047 | 541 | 0.047 | 0.974 | 1.11 | -0.029945 | 541 | 0.047 | 541 | 0.047 | 0.974 | 1.11 | -0.0299
CFLNoneSCESFmExCZ06 | Res-Iltg-dWatt-CFL | SCE | SFm | Ex | CZ06 | 0.541 | 4.3e-05 | 0 | 0.546 | 5.22e-05 | -0.0108 | 0.541 | 4.3e-05 | 0 | 0.546 | 5.22e-05 | -0.0108 |  | CFL | None | 541 | 0.043 | 541 | 0.043 | 1.01 | 1.21 | -0.019963 | 541 | 0.043 | 541 | 0.043 | 1.01 | 1.21 | -0.02
CFLNoneSCESFmExCZ08 | Res-Iltg-dWatt-CFL | SCE | SFm | Ex | CZ08 | 0.541 | 4.7e-05 | 0 | 0.566 | 5.98e-05 | -0.0103 | 0.541 | 4.7e-05 | 0 | 0.566 | 5.98e-05 | -0.0103 |  | CFL | None | 541 | 0.047 | 541 | 0.047 | 1.05 | 1.27 | -0.019039 | 541 | 0.047 | 541 | 0.047 | 1.05 | 1.27 | -0.019
CFLNoneSCESFmExCZ09 | Res-Iltg-dWatt-CFL | SCE | SFm | Ex | CZ09 | 0.541 | 4.5e-05 | 0 | 0.589 | 6.43e-05 | -0.0111 | 0.541 | 4.5e-05 | 0 | 0.589 | 6.43e-05 | -0.0111 |  | CFL | None | 541 | 0.045 | 541 | 0.045 | 1.09 | 1.43 | -0.020518 | 541 | 0.045 | 541 | 0.045 | 1.09 | 1.43 | -0.0205
CFLNoneSCESFmExCZ10 | Res-Iltg-dWatt-CFL | SCE | SFm | Ex | CZ10 | 0.541 | 4.3e-05 | 0 | 0.588 | 6.76e-05 | -0.0115 | 0.541 | 4.3e-05 | 0 | 0.588 | 6.76e-05 | -0.0115 |  | CFL | None | 541 | 0.043 | 541 | 0.043 | 1.09 | 1.57 | -0.021257 | 541 | 0.043 | 541 | 0.043 | 1.09 | 1.57 | -0.0213
CFLNoneSCESFmExCZ13 | Res-Iltg-dWatt-CFL | SCE | SFm | Ex | CZ13 | 0.541 | 4.5e-05 | 0 | 0.602 | 7.21e-05 | -0.0124 | 0.541 | 4.5e-05 | 0 | 0.602 | 7.21e-05 | -0.0124 |  | CFL | None | 541 | 0.045 | 541 | 0.045 | 1.11 | 1.6 | -0.022921 | 541 | 0.045 | 541 | 0.045 | 1.11 | 1.6 | -0.0229
CFLNoneSCESFmExCZ14 | Res-Iltg-dWatt-CFL | SCE | SFm | Ex | CZ14 | 0.541 | 4.3e-05 | 0 | 0.613 | 6.42e-05 | -0.0133 | 0.541 | 4.3e-05 | 0 | 0.613 | 6.42e-05 | -0.0133 |  | CFL | None | 541 | 0.043 | 541 | 0.043 | 1.13 | 1.49 | -0.024584 | 541 | 0.043 | 541 | 0.043 | 1.13 | 1.49 | -0.0246
CFLNoneSCESFmExCZ15 | Res-Iltg-dWatt-CFL | SCE | SFm | Ex | CZ15 | 0.541 | 4.4e-05 | 0 | 0.656 | 7.07e-05 | -0.00833 | 0.541 | 4.4e-05 | 0 | 0.656 | 7.07e-05 | -0.00833 |  | CFL | None | 541 | 0.044 | 541 | 0.044 | 1.21 | 1.61 | -0.015397 | 541 | 0.044 | 541 | 0.044 | 1.21 | 1.61 | -0.0154
CFLNoneSCESFmExCZ16 | Res-Iltg-dWatt-CFL | SCE | SFm | Ex | CZ16 | 0.541 | 4.5e-05 | 0 | 0.549 | 5.96e-05 | -0.0152 | 0.541 | 4.5e-05 | 0 | 0.549 | 5.96e-05 | -0.0152 |  | CFL | None | 541 | 0.045 | 541 | 0.045 | 1.01 | 1.32 | -0.028096 | 541 | 0.045 | 541 | 0.045 | 1.01 | 1.32 | -0.0281
CFLNoneSCESFmExIOU | Res-Iltg-dWatt-CFL | SCE | SFm | Ex | IOU | 0.541 | 4.4e-05 | 0 | 0.579 | 6.18e-05 | -0.0114 | 0.541 | 4.4e-05 | 0 | 0.579 | 6.18e-05 | -0.0114 |  | CFL | None | 541 | 0.044 | 541 | 0.044 | 1.07 | 1.4 | -0.021072 | 541 | 0.044 | 541 | 0.044 | 1.07 | 1.4 | -0.0211
CFLNoneSCESFmNewCZ05 | Res-Iltg-dWatt-CFL | SCE | SFm | New | CZ05 | 0.541 | 4.7e-05 | 0 | 0.551 | 6.8e-05 | -0.0128 | 0.541 | 4.7e-05 | 0 | 0.551 | 6.8e-05 | -0.0128 |  | CFL | None | 541 | 0.047 | 541 | 0.047 | 1.02 | 1.45 | -0.02366 | 541 | 0.047 | 541 | 0.047 | 1.02 | 1.45 | -0.0237
CFLNoneSCESFmNewCZ06 | Res-Iltg-dWatt-CFL | SCE | SFm | New | CZ06 | 0.541 | 4.3e-05 | 0 | 0.549 | 6.27e-05 | -0.0102 | 0.541 | 4.3e-05 | 0 | 0.549 | 6.27e-05 | -0.0102 |  | CFL | None | 541 | 0.043 | 541 | 0.043 | 1.01 | 1.46 | -0.018854 | 541 | 0.043 | 541 | 0.043 | 1.01 | 1.46 | -0.0189
CFLNoneSCESFmNewCZ08 | Res-Iltg-dWatt-CFL | SCE | SFm | New | CZ08 | 0.541 | 4.7e-05 | 0 | 0.59 | 6.28e-05 | -0.0087 | 0.541 | 4.7e-05 | 0 | 0.59 | 6.28e-05 | -0.0087 |  | CFL | None | 541 | 0.047 | 541 | 0.047 | 1.09 | 1.34 | -0.016081 | 541 | 0.047 | 541 | 0.047 | 1.09 | 1.34 | -0.0161
CFLNoneSCESFmNewCZ09 | Res-Iltg-dWatt-CFL | SCE | SFm | New | CZ09 | 0.541 | 4.5e-05 | 0 | 0.594 | 6.74e-05 | -0.00968 | 0.541 | 4.5e-05 | 0 | 0.594 | 6.74e-05 | -0.00968 |  | CFL | None | 541 | 0.045 | 541 | 0.045 | 1.1 | 1.5 | -0.017893 | 541 | 0.045 | 541 | 0.045 | 1.1 | 1.5 | -0.0179
CFLNoneSCESFmNewCZ10 | Res-Iltg-dWatt-CFL | SCE | SFm | New | CZ10 | 0.541 | 4.3e-05 | 0 | 0.599 | 6.63e-05 | -0.0108 | 0.541 | 4.3e-05 | 0 | 0.599 | 6.63e-05 | -0.0108 |  | CFL | None | 541 | 0.043 | 541 | 0.043 | 1.11 | 1.54 | -0.019963 | 541 | 0.043 | 541 | 0.043 | 1.11 | 1.54 | -0.02
CFLNoneSCESFmNewCZ13 | Res-Iltg-dWatt-CFL | SCE | SFm | New | CZ13 | 0.541 | 4.5e-05 | 0 | 0.6 | 6.55e-05 | -0.0123 | 0.541 | 4.5e-05 | 0 | 0.6 | 6.55e-05 | -0.0123 |  | CFL | None | 541 | 0.045 | 541 | 0.045 | 1.11 | 1.46 | -0.022736 | 541 | 0.045 | 541 | 0.045 | 1.11 | 1.46 | -0.0227
CFLNoneSCESFmNewCZ14 | Res-Iltg-dWatt-CFL | SCE | SFm | New | CZ14 | 0.541 | 4.3e-05 | 0 | 0.609 | 6.27e-05 | -0.0131 | 0.541 | 4.3e-05 | 0 | 0.609 | 6.27e-05 | -0.0131 |  | CFL | None | 541 | 0.043 | 541 | 0.043 | 1.13 | 1.46 | -0.024214 | 541 | 0.043 | 541 | 0.043 | 1.13 | 1.46 | -0.0242
CFLNoneSCESFmNewCZ15 | Res-Iltg-dWatt-CFL | SCE | SFm | New | CZ15 | 0.541 | 4.4e-05 | 0 | 0.649 | 6.68e-05 | -0.00716 | 0.541 | 4.4e-05 | 0 | 0.649 | 6.68e-05 | -0.00716 |  | CFL | None | 541 | 0.044 | 541 | 0.044 | 1.2 | 1.52 | -0.013235 | 541 | 0.044 | 541 | 0.044 | 1.2 | 1.52 | -0.0132
CFLNoneSCESFmNewCZ16 | Res-Iltg-dWatt-CFL | SCE | SFm | New | CZ16 | 0.541 | 4.5e-05 | 0 | 0.529 | 4.81e-05 | -0.0134 | 0.541 | 4.5e-05 | 0 | 0.529 | 4.81e-05 | -0.0134 |  | CFL | None | 541 | 0.045 | 541 | 0.045 | 0.978 | 1.07 | -0.024769 | 541 | 0.045 | 541 | 0.045 | 0.978 | 1.07 | -0.0248
CFLNoneSCESFmNewIOU | Res-Iltg-dWatt-CFL | SCE | SFm | New | IOU | 0.541 | 4.4e-05 | 0 | 0.589 | 6.5e-05 | -0.0106 | 0.541 | 4.4e-05 | 0 | 0.589 | 6.5e-05 | -0.0106 |  | CFL | None | 541 | 0.044 | 541 | 0.044 | 1.09 | 1.48 | -0.019593 | 541 | 0.044 | 541 | 0.044 | 1.09 | 1.48 | -0.0196
CFLNoneSDGDMoExCZ06 | Res-Iltg-dWatt-CFL | SDG | DMo | Ex | CZ06 | 0.541 | 4.3e-05 | 0 | 0.58877 | 5.8188e-05 | -0.0086939 | 0.541 | 4.3e-05 | 0 | 0.58877 | 5.8188e-05 | -0.0086939 |  | CFL | None | 541 | 0.043 | 541 | 0.043 | 1.09 | 1.35 | -0.01607 | 541 | 0.043 | 541 | 0.043 | 1.09 | 1.35 | -0.0161
CFLNoneSDGDMoExCZ07 | Res-Iltg-dWatt-CFL | SDG | DMo | Ex | CZ07 | 0.541 | 4.7e-05 | 0 | 0.556 | 5.23e-05 | -0.00799 | 0.541 | 4.7e-05 | 0 | 0.556 | 5.23e-05 | -0.00799 |  | CFL | None | 541 | 0.047 | 541 | 0.047 | 1.03 | 1.11 | -0.014769 | 541 | 0.047 | 541 | 0.047 | 1.03 | 1.11 | -0.0148
CFLNoneSDGDMoExCZ08 | Res-Iltg-dWatt-CFL | SDG | DMo | Ex | CZ08 | 0.541 | 4.7e-05 | 0 | 0.607 | 6.85e-05 | -0.00806 | 0.541 | 4.7e-05 | 0 | 0.607 | 6.85e-05 | -0.00806 |  | CFL | None | 541 | 0.047 | 541 | 0.047 | 1.12 | 1.46 | -0.014898 | 541 | 0.047 | 541 | 0.047 | 1.12 | 1.46 | -0.0149
CFLNoneSDGDMoExCZ10 | Res-Iltg-dWatt-CFL | SDG | DMo | Ex | CZ10 | 0.541 | 4.3e-05 | 0 | 0.63 | 7.25e-05 | -0.00937 | 0.541 | 4.3e-05 | 0 | 0.63 | 7.25e-05 | -0.00937 |  | CFL | None | 541 | 0.043 | 541 | 0.043 | 1.16 | 1.69 | -0.01732 | 541 | 0.043 | 541 | 0.043 | 1.16 | 1.69 | -0.0173
CFLNoneSDGDMoExCZ14 | Res-Iltg-dWatt-CFL | SDG | DMo | Ex | CZ14 | 0.541 | 4.3e-05 | 0 | 0.551 | 4.95e-05 | -0.00971 | 0.541 | 4.3e-05 | 0 | 0.551 | 4.95e-05 | -0.00971 |  | CFL | None | 541 | 0.043 | 541 | 0.043 | 1.02 | 1.15 | -0.017948 | 541 | 0.043 | 541 | 0.043 | 1.02 | 1.15 | -0.0179
CFLNoneSDGDMoExCZ15 | Res-Iltg-dWatt-CFL | SDG | DMo | Ex | CZ15 | 0.541 | 4.4e-05 | 0 | 0.641 | 6.2e-05 | -0.00655 | 0.541 | 4.4e-05 | 0 | 0.641 | 6.2e-05 | -0.00655 |  | CFL | None | 541 | 0.044 | 541 | 0.044 | 1.18 | 1.41 | -0.012107 | 541 | 0.044 | 541 | 0.044 | 1.18 | 1.41 | -0.0121
CFLNoneSDGDMoExIOU | Res-Iltg-dWatt-CFL | SDG | DMo | Ex | IOU | 0.541 | 4.5e-05 | 0 | 0.592 | 6.25e-05 | -0.00865 | 0.541 | 4.5e-05 | 0 | 0.592 | 6.25e-05 | -0.00865 |  | CFL | None | 541 | 0.045 | 541 | 0.045 | 1.09 | 1.39 | -0.015989 | 541 | 0.045 | 541 | 0.045 | 1.09 | 1.39 | -0.016
CFLNoneSDGDMoNewCZ06 | Res-Iltg-dWatt-CFL | SDG | DMo | New | CZ06 | 0.541 | 4.3e-05 | 0 | 0.599 | 5.89e-05 | -0.00799 | 0.541 | 4.3e-05 | 0 | 0.599 | 5.89e-05 | -0.00799 |  | CFL | None | 541 | 0.043 | 541 | 0.043 | 1.11 | 1.37 | -0.014769 | 541 | 0.043 | 541 | 0.043 | 1.11 | 1.37 | -0.0148
CFLNoneSDGDMoNewCZ07 | Res-Iltg-dWatt-CFL | SDG | DMo | New | CZ07 | 0.541 | 4.7e-05 | 0 | 0.588 | 5.7e-05 | -0.00684 | 0.541 | 4.7e-05 | 0 | 0.588 | 5.7e-05 | -0.00684 |  | CFL | None | 541 | 0.047 | 541 | 0.047 | 1.09 | 1.21 | -0.012643 | 541 | 0.047 | 541 | 0.047 | 1.09 | 1.21 | -0.0126
CFLNoneSDGDMoNewCZ08 | Res-Iltg-dWatt-CFL | SDG | DMo | New | CZ08 | 0.541 | 4.7e-05 | 0 | 0.623 | 6.6e-05 | -0.00721 | 0.541 | 4.7e-05 | 0 | 0.623 | 6.6e-05 | -0.00721 |  | CFL | None | 541 | 0.047 | 541 | 0.047 | 1.15 | 1.4 | -0.013327 | 541 | 0.047 | 541 | 0.047 | 1.15 | 1.4 | -0.0133
CFLNoneSDGDMoNewCZ10 | Res-Iltg-dWatt-CFL | SDG | DMo | New | CZ10 | 0.541 | 4.3e-05 | 0 | 0.627 | 6.57e-05 | -0.00957 | 0.541 | 4.3e-05 | 0 | 0.627 | 6.57e-05 | -0.00957 |  | CFL | None | 541 | 0.043 | 541 | 0.043 | 1.16 | 1.53 | -0.017689 | 541 | 0.043 | 541 | 0.043 | 1.16 | 1.53 | -0.0177
CFLNoneSDGDMoNewCZ14 | Res-Iltg-dWatt-CFL | SDG | DMo | New | CZ14 | 0.541 | 4.3e-05 | 0 | 0.622 | 6.32e-05 | -0.0106 | 0.541 | 4.3e-05 | 0 | 0.622 | 6.32e-05 | -0.0106 |  | CFL | None | 541 | 0.043 | 541 | 0.043 | 1.15 | 1.47 | -0.019593 | 541 | 0.043 | 541 | 0.043 | 1.15 | 1.47 | -0.0196
CFLNoneSDGDMoNewCZ15 | Res-Iltg-dWatt-CFL | SDG | DMo | New | CZ15 | 0.541 | 4.4e-05 | 0 | 0.655 | 6.53e-05 | -0.00684 | 0.541 | 4.4e-05 | 0 | 0.655 | 6.53e-05 | -0.00684 |  | CFL | None | 541 | 0.044 | 541 | 0.044 | 1.21 | 1.48 | -0.012643 | 541 | 0.044 | 541 | 0.044 | 1.21 | 1.48 | -0.0126
CFLNoneSDGDMoNewIOU | Res-Iltg-dWatt-CFL | SDG | DMo | New | IOU | 0.541 | 4.4e-05 | 0 | 0.616 | 6.33e-05 | -0.00879 | 0.541 | 4.4e-05 | 0 | 0.616 | 6.33e-05 | -0.00879 |  | CFL | None | 541 | 0.044 | 541 | 0.044 | 1.14 | 1.44 | -0.016248 | 541 | 0.044 | 541 | 0.044 | 1.14 | 1.44 | -0.0162
CFLNoneSDGMFmExCZ06 | Res-Iltg-dWatt-CFL | SDG | MFm | Ex | CZ06 | 0.541 | 4.3e-05 | 0 | 0.545 | 5.23e-05 | -0.00847 | 0.541 | 4.3e-05 | 0 | 0.545 | 5.23e-05 | -0.00847 |  | CFL | None | 541 | 0.043 | 541 | 0.043 | 1.01 | 1.22 | -0.015656 | 541 | 0.043 | 541 | 0.043 | 1.01 | 1.22 | -0.0157
CFLNoneSDGMFmExCZ07 | Res-Iltg-dWatt-CFL | SDG | MFm | Ex | CZ07 | 0.541 | 4.7e-05 | 0 | 0.55 | 5.28e-05 | -0.00601 | 0.541 | 4.7e-05 | 0 | 0.55 | 5.28e-05 | -0.00601 |  | CFL | None | 541 | 0.047 | 541 | 0.047 | 1.02 | 1.12 | -0.011109 | 541 | 0.047 | 541 | 0.047 | 1.02 | 1.12 | -0.0111
CFLNoneSDGMFmExCZ08 | Res-Iltg-dWatt-CFL | SDG | MFm | Ex | CZ08 | 0.541 | 4.7e-05 | 0 | 0.589 | 6.39e-05 | -0.00674 | 0.541 | 4.7e-05 | 0 | 0.589 | 6.39e-05 | -0.00674 |  | CFL | None | 541 | 0.047 | 541 | 0.047 | 1.09 | 1.36 | -0.012458 | 541 | 0.047 | 541 | 0.047 | 1.09 | 1.36 | -0.0125
CFLNoneSDGMFmExCZ10 | Res-Iltg-dWatt-CFL | SDG | MFm | Ex | CZ10 | 0.541 | 4.3e-05 | 0 | 0.576 | 6.21e-05 | -0.0081 | 0.541 | 4.3e-05 | 0 | 0.576 | 6.21e-05 | -0.0081 |  | CFL | None | 541 | 0.043 | 541 | 0.043 | 1.06 | 1.44 | -0.014972 | 541 | 0.043 | 541 | 0.043 | 1.06 | 1.44 | -0.015
CFLNoneSDGMFmExCZ14 | Res-Iltg-dWatt-CFL | SDG | MFm | Ex | CZ14 | 0.541 | 4.3e-05 | 0 | 0.61 | 6.16e-05 | -0.00942 | 0.541 | 4.3e-05 | 0 | 0.61 | 6.16e-05 | -0.00942 |  | CFL | None | 541 | 0.043 | 541 | 0.043 | 1.13 | 1.43 | -0.017412 | 541 | 0.043 | 541 | 0.043 | 1.13 | 1.43 | -0.0174
CFLNoneSDGMFmExCZ15 | Res-Iltg-dWatt-CFL | SDG | MFm | Ex | CZ15 | 0.541 | 4.4e-05 | 0 | 0.663 | 6.41e-05 | -0.0045 | 0.541 | 4.4e-05 | 0 | 0.663 | 6.41e-05 | -0.0045 |  | CFL | None | 541 | 0.044 | 541 | 0.044 | 1.23 | 1.46 | -0.0083179 | 541 | 0.044 | 541 | 0.044 | 1.23 | 1.46 | -0.00832
CFLNoneSDGMFmExIOU | Res-Iltg-dWatt-CFL | SDG | MFm | Ex | IOU | 0.541 | 4.6e-05 | 0 | 0.557 | 5.55e-05 | -0.0066 | 0.541 | 4.6e-05 | 0 | 0.557 | 5.55e-05 | -0.0066 |  | CFL | None | 541 | 0.046 | 541 | 0.046 | 1.03 | 1.21 | -0.0122 | 541 | 0.046 | 541 | 0.046 | 1.03 | 1.21 | -0.0122
CFLNoneSDGMFmNewCZ06 | Res-Iltg-dWatt-CFL | SDG | MFm | New | CZ06 | 0.541 | 4.3e-05 | 0 | 0.577 | 6.39e-05 | -0.00638 | 0.541 | 4.3e-05 | 0 | 0.577 | 6.39e-05 | -0.00638 |  | CFL | None | 541 | 0.043 | 541 | 0.043 | 1.07 | 1.49 | -0.011793 | 541 | 0.043 | 541 | 0.043 | 1.07 | 1.49 | -0.0118
CFLNoneSDGMFmNewCZ07 | Res-Iltg-dWatt-CFL | SDG | MFm | New | CZ07 | 0.541 | 4.7e-05 | 0 | 0.601 | 5.8e-05 | -0.00195 | 0.541 | 4.7e-05 | 0 | 0.601 | 5.8e-05 | -0.00195 |  | CFL | None | 541 | 0.047 | 541 | 0.047 | 1.11 | 1.23 | -0.0036044 | 541 | 0.047 | 541 | 0.047 | 1.11 | 1.23 | -0.0036
CFLNoneSDGMFmNewCZ08 | Res-Iltg-dWatt-CFL | SDG | MFm | New | CZ08 | 0.541 | 4.7e-05 | 0 | 0.616 | 6.73e-05 | -0.00476 | 0.541 | 4.7e-05 | 0 | 0.616 | 6.73e-05 | -0.00476 |  | CFL | None | 541 | 0.047 | 541 | 0.047 | 1.14 | 1.43 | -0.0087985 | 541 | 0.047 | 541 | 0.047 | 1.14 | 1.43 | -0.0088
CFLNoneSDGMFmNewCZ10 | Res-Iltg-dWatt-CFL | SDG | MFm | New | CZ10 | 0.541 | 4.3e-05 | 0 | 0.555 | 4.88e-05 | -0.0052 | 0.541 | 4.3e-05 | 0 | 0.555 | 4.88e-05 | -0.0052 |  | CFL | None | 541 | 0.043 | 541 | 0.043 | 1.03 | 1.13 | -0.0096118 | 541 | 0.043 | 541 | 0.043 | 1.03 | 1.13 | -0.00961
CFLNoneSDGMFmNewCZ14 | Res-Iltg-dWatt-CFL | SDG | MFm | New | CZ14 | 0.541 | 4.3e-05 | 0 | 0.594 | 5.71e-05 | -0.0076 | 0.541 | 4.3e-05 | 0 | 0.594 | 5.71e-05 | -0.0076 |  | CFL | None | 541 | 0.043 | 541 | 0.043 | 1.1 | 1.33 | -0.014048 | 541 | 0.043 | 541 | 0.043 | 1.1 | 1.33 | -0.014
CFLNoneSDGMFmNewCZ15 | Res-Iltg-dWatt-CFL | SDG | MFm | New | CZ15 | 0.541 | 4.4e-05 | 0 | 0.623 | 5.81e-05 | -0.00233 | 0.541 | 4.4e-05 | 0 | 0.623 | 5.81e-05 | -0.00233 |  | CFL | None | 541 | 0.044 | 541 | 0.044 | 1.15 | 1.32 | -0.0043068 | 541 | 0.044 | 541 | 0.044 | 1.15 | 1.32 | -0.00431
CFLNoneSDGMFmNewIOU | Res-Iltg-dWatt-CFL | SDG | MFm | New | IOU | 0.541 | 4.6e-05 | 0 | 0.593 | 5.81e-05 | -0.00331 | 0.541 | 4.6e-05 | 0 | 0.593 | 5.81e-05 | -0.00331 |  | CFL | None | 541 | 0.046 | 541 | 0.046 | 1.1 | 1.26 | -0.0061183 | 541 | 0.046 | 541 | 0.046 | 1.1 | 1.26 | -0.00612
CFLNoneSDGResExCZ06 | Res-Iltg-dWatt-CFL | SDG | Res | Ex | CZ06 | 0.541 | 4.3e-05 | 0 | 0.54818 | 5.5877e-05 | -0.010561 | 0.541 | 4.3e-05 | 0 | 0.54818 | 5.5877e-05 | -0.010561 |  | CFL | None | 541 | 0.043 | 541 | 0.043 | 1.01 | 1.3 | -0.01952 | 541 | 0.043 | 541 | 0.043 | 1.01 | 1.3 | -0.0195
CFLNoneSDGResExCZ07 | Res-Iltg-dWatt-CFL | SDG | Res | Ex | CZ07 | 0.541 | 4.7e-05 | 0 | 0.54838 | 5.574e-05 | -0.0090383 | 0.541 | 4.7e-05 | 0 | 0.54838 | 5.574e-05 | -0.0090383 |  | CFL | None | 541 | 0.047 | 541 | 0.047 | 1.01 | 1.19 | -0.016707 | 541 | 0.047 | 541 | 0.047 | 1.01 | 1.19 | -0.0167
CFLNoneSDGResExCZ08 | Res-Iltg-dWatt-CFL | SDG | Res | Ex | CZ08 | 0.541 | 4.7e-05 | 0 | 0.58957 | 6.5504e-05 | -0.0080774 | 0.541 | 4.7e-05 | 0 | 0.58957 | 6.5504e-05 | -0.0080774 |  | CFL | None | 541 | 0.047 | 541 | 0.047 | 1.09 | 1.39 | -0.014931 | 541 | 0.047 | 541 | 0.047 | 1.09 | 1.39 | -0.0149
CFLNoneSDGResExCZ10 | Res-Iltg-dWatt-CFL | SDG | Res | Ex | CZ10 | 0.541 | 4.3e-05 | 0 | 0.5812 | 6.3173e-05 | -0.010572 | 0.541 | 4.3e-05 | 0 | 0.5812 | 6.3173e-05 | -0.010572 |  | CFL | None | 541 | 0.043 | 541 | 0.043 | 1.07 | 1.47 | -0.019542 | 541 | 0.043 | 541 | 0.043 | 1.07 | 1.47 | -0.0195
CFLNoneSDGResExCZ14 | Res-Iltg-dWatt-CFL | SDG | Res | Ex | CZ14 | 0.541 | 4.3e-05 | 0 | 0.58626 | 5.7675e-05 | -0.012005 | 0.541 | 4.3e-05 | 0 | 0.58626 | 5.7675e-05 | -0.012005 |  | CFL | None | 541 | 0.043 | 541 | 0.043 | 1.08 | 1.34 | -0.02219 | 541 | 0.043 | 541 | 0.043 | 1.08 | 1.34 | -0.0222
CFLNoneSDGResExCZ15 | Res-Iltg-dWatt-CFL | SDG | Res | Ex | CZ15 | 0.541 | 4.4e-05 | 0 | 0.65926 | 7.1204e-05 | -0.0072947 | 0.541 | 4.4e-05 | 0 | 0.65926 | 7.1204e-05 | -0.0072947 |  | CFL | None | 541 | 0.044 | 541 | 0.044 | 1.22 | 1.62 | -0.013484 | 541 | 0.044 | 541 | 0.044 | 1.22 | 1.62 | -0.0135
CFLNoneSDGResExIOU | Res-Iltg-dWatt-CFL | SDG | Res | Ex | IOU | 0.541 | 4.5309e-05 | 0 | 0.5587 | 5.7831e-05 | -0.0095247 | 0.541 | 4.5309e-05 | 0 | 0.5587 | 5.7831e-05 | -0.0095247 |  | CFL | None | 541 | 0.0453 | 541 | 0.0453 | 1.03 | 1.28 | -0.017606 | 541 | 0.0453 | 541 | 0.0453 | 1.03 | 1.28 | -0.0176
CFLNoneSDGResNewCZ06 | Res-Iltg-dWatt-CFL | SDG | Res | New | CZ06 | 0.541 | 4.3e-05 | 0 | 0.54647 | 5.8272e-05 | -0.010024 | 0.541 | 4.3e-05 | 0 | 0.54647 | 5.8272e-05 | -0.010024 |  | CFL | None | 541 | 0.043 | 541 | 0.043 | 1.01 | 1.36 | -0.018529 | 541 | 0.043 | 541 | 0.043 | 1.01 | 1.36 | -0.0185
CFLNoneSDGResNewCZ07 | Res-Iltg-dWatt-CFL | SDG | Res | New | CZ07 | 0.541 | 4.7e-05 | 0 | 0.56837 | 5.5872e-05 | -0.0075247 | 0.541 | 4.7e-05 | 0 | 0.56837 | 5.5872e-05 | -0.0075247 |  | CFL | None | 541 | 0.047 | 541 | 0.047 | 1.05 | 1.19 | -0.013909 | 541 | 0.047 | 541 | 0.047 | 1.05 | 1.19 | -0.0139
CFLNoneSDGResNewCZ08 | Res-Iltg-dWatt-CFL | SDG | Res | New | CZ08 | 0.541 | 4.7e-05 | 0 | 0.6158 | 6.7755e-05 | -0.0055083 | 0.541 | 4.7e-05 | 0 | 0.6158 | 6.7755e-05 | -0.0055083 |  | CFL | None | 541 | 0.047 | 541 | 0.047 | 1.14 | 1.44 | -0.010182 | 541 | 0.047 | 541 | 0.047 | 1.14 | 1.44 | -0.0102
CFLNoneSDGResNewCZ10 | Res-Iltg-dWatt-CFL | SDG | Res | New | CZ10 | 0.541 | 4.3e-05 | 0 | 0.59516 | 6.3743e-05 | -0.0099916 | 0.541 | 4.3e-05 | 0 | 0.59516 | 6.3743e-05 | -0.0099916 |  | CFL | None | 541 | 0.043 | 541 | 0.043 | 1.1 | 1.48 | -0.018469 | 541 | 0.043 | 541 | 0.043 | 1.1 | 1.48 | -0.0185
CFLNoneSDGResNewCZ14 | Res-Iltg-dWatt-CFL | SDG | Res | New | CZ14 | 0.541 | 4.3e-05 | 0 | 0.553 | 4.96e-05 | -0.0132 | 0.541 | 4.3e-05 | 0 | 0.553 | 4.96e-05 | -0.0132 |  | CFL | None | 541 | 0.043 | 541 | 0.043 | 1.02 | 1.15 | -0.024399 | 541 | 0.043 | 541 | 0.043 | 1.02 | 1.15 | -0.0244
CFLNoneSDGResNewIOU | Res-Iltg-dWatt-CFL | SDG | Res | New | IOU | 0.541 | 4.5156e-05 | 0 | 0.57456 | 5.9369e-05 | -0.0086149 | 0.541 | 4.5156e-05 | 0 | 0.57456 | 5.9369e-05 | -0.0086149 |  | CFL | None | 541 | 0.0452 | 541 | 0.0452 | 1.06 | 1.31 | -0.015924 | 541 | 0.0452 | 541 | 0.0452 | 1.06 | 1.31 | -0.0159
CFLNoneSDGSFmExCZ06 | Res-Iltg-dWatt-CFL | SDG | SFm | Ex | CZ06 | 0.541 | 4.3e-05 | 0 | 0.549 | 5.68e-05 | -0.0111 | 0.541 | 4.3e-05 | 0 | 0.549 | 5.68e-05 | -0.0111 |  | CFL | None | 541 | 0.043 | 541 | 0.043 | 1.01 | 1.32 | -0.020518 | 541 | 0.043 | 541 | 0.043 | 1.01 | 1.32 | -0.0205
CFLNoneSDGSFmExCZ07 | Res-Iltg-dWatt-CFL | SDG | SFm | Ex | CZ07 | 0.541 | 4.7e-05 | 0 | 0.547 | 5.76e-05 | -0.0108 | 0.541 | 4.7e-05 | 0 | 0.547 | 5.76e-05 | -0.0108 |  | CFL | None | 541 | 0.047 | 541 | 0.047 | 1.01 | 1.23 | -0.019963 | 541 | 0.047 | 541 | 0.047 | 1.01 | 1.23 | -0.02
CFLNoneSDGSFmExCZ08 | Res-Iltg-dWatt-CFL | SDG | SFm | Ex | CZ08 | 0.541 | 4.7e-05 | 0 | 0.586 | 6.75e-05 | -0.0104 | 0.541 | 4.7e-05 | 0 | 0.586 | 6.75e-05 | -0.0104 |  | CFL | None | 541 | 0.047 | 541 | 0.047 | 1.08 | 1.44 | -0.019224 | 541 | 0.047 | 541 | 0.047 | 1.08 | 1.44 | -0.0192
CFLNoneSDGSFmExCZ10 | Res-Iltg-dWatt-CFL | SDG | SFm | Ex | CZ10 | 0.541 | 4.3e-05 | 0 | 0.577 | 6.24e-05 | -0.0116 | 0.541 | 4.3e-05 | 0 | 0.577 | 6.24e-05 | -0.0116 |  | CFL | None | 541 | 0.043 | 541 | 0.043 | 1.07 | 1.45 | -0.021442 | 541 | 0.043 | 541 | 0.043 | 1.07 | 1.45 | -0.0214
CFLNoneSDGSFmExCZ14 | Res-Iltg-dWatt-CFL | SDG | SFm | Ex | CZ14 | 0.541 | 4.3e-05 | 0 | 0.59 | 5.86e-05 | -0.0124 | 0.541 | 4.3e-05 | 0 | 0.59 | 5.86e-05 | -0.0124 |  | CFL | None | 541 | 0.043 | 541 | 0.043 | 1.09 | 1.36 | -0.022921 | 541 | 0.043 | 541 | 0.043 | 1.09 | 1.36 | -0.0229
CFLNoneSDGSFmExCZ15 | Res-Iltg-dWatt-CFL | SDG | SFm | Ex | CZ15 | 0.541 | 4.4e-05 | 0 | 0.659 | 7.17e-05 | -0.00749 | 0.541 | 4.4e-05 | 0 | 0.659 | 7.17e-05 | -0.00749 |  | CFL | None | 541 | 0.044 | 541 | 0.044 | 1.22 | 1.63 | -0.013845 | 541 | 0.044 | 541 | 0.044 | 1.22 | 1.63 | -0.0138
CFLNoneSDGSFmExIOU | Res-Iltg-dWatt-CFL | SDG | SFm | Ex | IOU | 0.541 | 4.5e-05 | 0 | 0.557 | 5.86e-05 | -0.011 | 0.541 | 4.5e-05 | 0 | 0.557 | 5.86e-05 | -0.011 |  | CFL | None | 541 | 0.045 | 541 | 0.045 | 1.03 | 1.3 | -0.020333 | 541 | 0.045 | 541 | 0.045 | 1.03 | 1.3 | -0.0203
CFLNoneSDGSFmNewCZ06 | Res-Iltg-dWatt-CFL | SDG | SFm | New | CZ06 | 0.541 | 4.3e-05 | 0 | 0.545 | 5.8e-05 | -0.0102 | 0.541 | 4.3e-05 | 0 | 0.545 | 5.8e-05 | -0.0102 |  | CFL | None | 541 | 0.043 | 541 | 0.043 | 1.01 | 1.35 | -0.018854 | 541 | 0.043 | 541 | 0.043 | 1.01 | 1.35 | -0.0189
CFLNoneSDGSFmNewCZ07 | Res-Iltg-dWatt-CFL | SDG | SFm | New | CZ07 | 0.541 | 4.7e-05 | 0 | 0.558 | 5.52e-05 | -0.00922 | 0.541 | 4.7e-05 | 0 | 0.558 | 5.52e-05 | -0.00922 |  | CFL | None | 541 | 0.047 | 541 | 0.047 | 1.03 | 1.17 | -0.017043 | 541 | 0.047 | 541 | 0.047 | 1.03 | 1.17 | -0.017
CFLNoneSDGSFmNewCZ08 | Res-Iltg-dWatt-CFL | SDG | SFm | New | CZ08 | 0.541 | 4.7e-05 | 0 | 0.615 | 6.96e-05 | -0.00854 | 0.541 | 4.7e-05 | 0 | 0.615 | 6.96e-05 | -0.00854 |  | CFL | None | 541 | 0.047 | 541 | 0.047 | 1.14 | 1.48 | -0.015786 | 541 | 0.047 | 541 | 0.047 | 1.14 | 1.48 | -0.0158
CFLNoneSDGSFmNewCZ10 | Res-Iltg-dWatt-CFL | SDG | SFm | New | CZ10 | 0.541 | 4.3e-05 | 0 | 0.598 | 6.59e-05 | -0.0108 | 0.541 | 4.3e-05 | 0 | 0.598 | 6.59e-05 | -0.0108 |  | CFL | None | 541 | 0.043 | 541 | 0.043 | 1.11 | 1.53 | -0.019963 | 541 | 0.043 | 541 | 0.043 | 1.11 | 1.53 | -0.02
CFLNoneSDGSFmNewCZ14 | Res-Iltg-dWatt-CFL | SDG | SFm | New | CZ14 | 0.541 | 4.3e-05 | 0 | 0.553 | 4.96e-05 | -0.0132 | 0.541 | 4.3e-05 | 0 | 0.553 | 4.96e-05 | -0.0132 |  | CFL | None | 541 | 0.043 | 541 | 0.043 | 1.02 | 1.15 | -0.024399 | 541 | 0.043 | 541 | 0.043 | 1.02 | 1.15 | -0.0244
CFLNoneSDGSFmNewCZ15 | Res-Iltg-dWatt-CFL | SDG | SFm | New | CZ15 | 0.541 | 4.4e-05 | 0 | 0.605 | 5.83e-05 | -0.00723 | 0.541 | 4.4e-05 | 0 | 0.605 | 5.83e-05 | -0.00723 |  | CFL | None | 541 | 0.044 | 541 | 0.044 | 1.12 | 1.32 | -0.013364 | 541 | 0.044 | 541 | 0.044 | 1.12 | 1.32 | -0.0134
CFLNoneSDGSFmNewIOU | Res-Iltg-dWatt-CFL | SDG | SFm | New | IOU | 0.541 | 4.5e-05 | 0 | 0.568 | 5.95e-05 | -0.00993 | 0.541 | 4.5e-05 | 0 | 0.568 | 5.95e-05 | -0.00993 |  | CFL | None | 541 | 0.045 | 541 | 0.045 | 1.05 | 1.32 | -0.018355 | 541 | 0.045 | 541 | 0.045 | 1.05 | 1.32 | -0.0184

## DEER2016
deer2016 database tables: Energy Impacts
Round to 3 significant digits
[6 empty] | Above Pre-Existing Impacts (per delta Watt) | [5 empty] | Above Code/Standard Impacts (per delta Watt) | [7 empty] | Hours of Use and Coincident demand |  |  |  | Calculate IE from WB/EU impacts
[6 empty] | End Use Values |  |  | Whole Building Values |  |  | End Use Values |  |  | Whole Building Values |  |  |  |  | Pre-Existing Case |  | Code and Msr Cases |  | Energy | Demand | Gas
Lookup Index | EnergyImpactID | IOU | BldgType | BldgVint | BldgLoc | APreEUkWh | APreEUkW | APreEUtherm | APreWBkWh | APreWBkW | APreWBtherm | AStdEUkWh | AStdEUkW | AStdEUtherm | AStdWBkWh | AStdWBkW | AStdWBtherm | Ltg Type | OS | HOU | CDF | HOU | CDF | kWh/kWh | kW/kW | therm/kWh
CFLBldgPGEAsmExCZ01 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Asm | Ex | CZ01 | 1.21 | 0.00023 | 0 | 1.15 | 0.000267 | -0.0215 | 1.16 | 0.000221 | 0 | 1.1 | 0.000256 | -0.0206 | CFL | Bldg | 1210 | 0.23 | 1160 | 0.221 | 0.948 | 1.16 | -0.0178
CFLBldgPGEAsmExCZ02 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Asm | Ex | CZ02 | 1.21 | 0.000231 | 0 | 1.25 | 0.000271 | -0.0125 | 1.16 | 0.000221 | 0 | 1.19 | 0.000259 | -0.0119 | CFL | Bldg | 1210 | 0.231 | 1160 | 0.221 | 1.03 | 1.17 | -0.0103
CFLBldgPGEAsmExCZ03 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Asm | Ex | CZ03 | 1.21 | 0.000231 | 0 | 1.24 | 0.000271 | -0.0137 | 1.16 | 0.000221 | 0 | 1.19 | 0.000259 | -0.0131 | CFL | Bldg | 1210 | 0.231 | 1160 | 0.221 | 1.03 | 1.17 | -0.0113
CFLBldgPGEAsmExCZ04 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Asm | Ex | CZ04 | 1.21 | 0.000231 | 0 | 1.27 | 0.00027 | -0.0101 | 1.16 | 0.000221 | 0 | 1.22 | 0.000259 | -0.00969 | CFL | Bldg | 1210 | 0.231 | 1160 | 0.221 | 1.05 | 1.17 | -0.00835
CFLBldgSCGAsmExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCG | Asm | Ex | CZ05 | 1.21 | 0.00023 | 0 | 1.27 | 0.000276 | -0.0118 | 1.16 | 0.000221 | 0 | 1.22 | 0.000265 | -0.0113 | CFL | Bldg | 1210 | 0.23 | 1160 | 0.221 | 1.05 | 1.2 | -0.00974
CFLBldgPGEAsmExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Asm | Ex | CZ05 | 1.21 | 0.000231 | 0 | 1.27 | 0.000276 | -0.0118 | 1.16 | 0.000221 | 0 | 1.22 | 0.000265 | -0.0113 | CFL | Bldg | 1210 | 0.231 | 1160 | 0.221 | 1.05 | 1.2 | -0.00974
CFLBldgSCEAsmExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Asm | Ex | CZ05 | 1.21 | 0.00023 | 0 | 1.27 | 0.000276 | -0.0118 | 1.16 | 0.000221 | 0 | 1.22 | 0.000265 | -0.0113 | CFL | Bldg | 1210 | 0.23 | 1160 | 0.221 | 1.05 | 1.2 | -0.00974
CFLBldgSCGAsmExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCG | Asm | Ex | CZ06 | 1.21 | 0.00023 | 0 | 1.32 | 0.000286 | -0.00631 | 1.16 | 0.000221 | 0 | 1.27 | 0.000274 | -0.00606 | CFL | Bldg | 1210 | 0.23 | 1160 | 0.221 | 1.09 | 1.24 | -0.00522
CFLBldgSCEAsmExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Asm | Ex | CZ06 | 1.21 | 0.00023 | 0 | 1.32 | 0.000286 | -0.00631 | 1.16 | 0.000221 | 0 | 1.27 | 0.000274 | -0.00606 | CFL | Bldg | 1210 | 0.23 | 1160 | 0.221 | 1.09 | 1.24 | -0.00522
CFLBldgSDGAsmExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Asm | Ex | CZ06 | 1.21 | 0.00023 | 0 | 1.32 | 0.000286 | -0.0063 | 1.16 | 0.000221 | 0 | 1.27 | 0.000274 | -0.00606 | CFL | Bldg | 1210 | 0.23 | 1160 | 0.221 | 1.09 | 1.24 | -0.00522
CFLBldgSDGAsmExCZ07 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Asm | Ex | CZ07 | 1.21 | 0.00023 | 0 | 1.32 | 0.000285 | -0.00578 | 1.16 | 0.000221 | 0 | 1.27 | 0.000274 | -0.00556 | CFL | Bldg | 1210 | 0.23 | 1160 | 0.221 | 1.09 | 1.24 | -0.00479
CFLBldgSDGAsmExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Asm | Ex | CZ08 | 1.21 | 0.00023 | 0 | 1.33 | 0.000277 | -0.0055 | 1.16 | 0.000221 | 0 | 1.28 | 0.000266 | -0.00529 | CFL | Bldg | 1210 | 0.23 | 1160 | 0.221 | 1.1 | 1.2 | -0.00456
CFLBldgSCGAsmExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCG | Asm | Ex | CZ08 | 1.21 | 0.00023 | 0 | 1.33 | 0.000277 | -0.00551 | 1.16 | 0.000221 | 0 | 1.28 | 0.000266 | -0.00529 | CFL | Bldg | 1210 | 0.23 | 1160 | 0.221 | 1.1 | 1.2 | -0.00456
CFLBldgSCEAsmExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Asm | Ex | CZ08 | 1.21 | 0.00023 | 0 | 1.33 | 0.000277 | -0.00551 | 1.16 | 0.000221 | 0 | 1.28 | 0.000266 | -0.00529 | CFL | Bldg | 1210 | 0.23 | 1160 | 0.221 | 1.1 | 1.2 | -0.00456
CFLBldgSCEAsmExCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Asm | Ex | CZ09 | 1.21 | 0.00023 | 0 | 1.35 | 0.000286 | -0.00603 | 1.16 | 0.000221 | 0 | 1.29 | 0.000274 | -0.00579 | CFL | Bldg | 1210 | 0.23 | 1160 | 0.221 | 1.11 | 1.24 | -0.00499
CFLBldgSCGAsmExCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCG | Asm | Ex | CZ09 | 1.21 | 0.00023 | 0 | 1.35 | 0.000286 | -0.00603 | 1.16 | 0.000221 | 0 | 1.29 | 0.000274 | -0.00579 | CFL | Bldg | 1210 | 0.23 | 1160 | 0.221 | 1.11 | 1.24 | -0.00499
CFLBldgSDGAsmExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Asm | Ex | CZ10 | 1.21 | 0.00023 | 0 | 1.32 | 0.00028 | -0.00699 | 1.16 | 0.000221 | 0 | 1.27 | 0.000269 | -0.00673 | CFL | Bldg | 1210 | 0.23 | 1160 | 0.221 | 1.09 | 1.22 | -0.0058
CFLBldgSCGAsmExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCG | Asm | Ex | CZ10 | 1.2 | 0.00023 | 0 | 1.31 | 0.000279 | -0.00698 | 1.16 | 0.000221 | 0 | 1.27 | 0.000269 | -0.00673 | CFL | Bldg | 1200 | 0.23 | 1160 | 0.221 | 1.09 | 1.22 | -0.0058
CFLBldgSCEAsmExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Asm | Ex | CZ10 | 1.2 | 0.00023 | 0 | 1.31 | 0.000279 | -0.00698 | 1.16 | 0.000221 | 0 | 1.27 | 0.000269 | -0.00673 | CFL | Bldg | 1200 | 0.23 | 1160 | 0.221 | 1.09 | 1.22 | -0.0058
CFLBldgPGEAsmExCZ11 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Asm | Ex | CZ11 | 1.21 | 0.00023 | 0 | 1.28 | 0.000269 | -0.0107 | 1.16 | 0.000221 | 0 | 1.22 | 0.000258 | -0.0103 | CFL | Bldg | 1210 | 0.23 | 1160 | 0.221 | 1.05 | 1.17 | -0.00888
CFLBldgPGEAsmExCZ12 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Asm | Ex | CZ12 | 1.21 | 0.00023 | 0 | 1.26 | 0.000271 | -0.0113 | 1.16 | 0.000221 | 0 | 1.21 | 0.000261 | -0.0108 | CFL | Bldg | 1210 | 0.23 | 1160 | 0.221 | 1.04 | 1.18 | -0.00931
CFLBldgPGEAsmExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Asm | Ex | CZ13 | 1.21 | 0.00023 | 0 | 1.3 | 0.000279 | -0.0104 | 1.16 | 0.000221 | 0 | 1.25 | 0.000268 | -0.00998 | CFL | Bldg | 1210 | 0.23 | 1160 | 0.221 | 1.08 | 1.21 | -0.0086
CFLBldgSCEAsmExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Asm | Ex | CZ13 | 1.21 | 0.00023 | 0 | 1.3 | 0.000279 | -0.0104 | 1.16 | 0.000221 | 0 | 1.25 | 0.000268 | -0.00998 | CFL | Bldg | 1210 | 0.23 | 1160 | 0.221 | 1.08 | 1.21 | -0.0086
CFLBldgSCGAsmExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCG | Asm | Ex | CZ13 | 1.21 | 0.00023 | 0 | 1.3 | 0.000279 | -0.0104 | 1.16 | 0.000221 | 0 | 1.25 | 0.000268 | -0.00998 | CFL | Bldg | 1210 | 0.23 | 1160 | 0.221 | 1.08 | 1.21 | -0.0086
CFLBldgSCGAsmExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCG | Asm | Ex | CZ14 | 1.2 | 0.00023 | 0 | 1.28 | 0.000261 | -0.011 | 1.16 | 0.000221 | 0 | 1.24 | 0.000251 | -0.0106 | CFL | Bldg | 1200 | 0.23 | 1160 | 0.221 | 1.07 | 1.14 | -0.00914
CFLBldgSDGAsmExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Asm | Ex | CZ14 | 1.21 | 0.00023 | 0 | 1.29 | 0.000261 | -0.011 | 1.16 | 0.000221 | 0 | 1.24 | 0.000251 | -0.0106 | CFL | Bldg | 1210 | 0.23 | 1160 | 0.221 | 1.07 | 1.14 | -0.00914
CFLBldgSCEAsmExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Asm | Ex | CZ14 | 1.2 | 0.00023 | 0 | 1.28 | 0.000261 | -0.011 | 1.16 | 0.000221 | 0 | 1.24 | 0.000251 | -0.0106 | CFL | Bldg | 1200 | 0.23 | 1160 | 0.221 | 1.07 | 1.14 | -0.00914
CFLBldgSCEAsmExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Asm | Ex | CZ15 | 1.2 | 0.00023 | 0 | 1.5 | 0.000271 | -0.00307 | 1.16 | 0.000221 | 0 | 1.45 | 0.000261 | -0.00296 | CFL | Bldg | 1200 | 0.23 | 1160 | 0.221 | 1.25 | 1.18 | -0.00255
CFLBldgSCGAsmExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCG | Asm | Ex | CZ15 | 1.2 | 0.00023 | 0 | 1.5 | 0.000271 | -0.00307 | 1.16 | 0.000221 | 0 | 1.45 | 0.000261 | -0.00296 | CFL | Bldg | 1200 | 0.23 | 1160 | 0.221 | 1.25 | 1.18 | -0.00255
CFLBldgSDGAsmExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Asm | Ex | CZ15 | 1.21 | 0.00023 | 0 | 1.5 | 0.000272 | -0.00308 | 1.16 | 0.000221 | 0 | 1.45 | 0.000261 | -0.00296 | CFL | Bldg | 1210 | 0.23 | 1160 | 0.221 | 1.25 | 1.18 | -0.00255
CFLBldgSCGAsmExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCG | Asm | Ex | CZ16 | 1.2 | 0.00023 | 0 | 1.18 | 0.000274 | -0.0161 | 1.16 | 0.000221 | 0 | 1.14 | 0.000263 | -0.0155 | CFL | Bldg | 1200 | 0.23 | 1160 | 0.221 | 0.983 | 1.19 | -0.0134
CFLBldgSCEAsmExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Asm | Ex | CZ16 | 1.2 | 0.00023 | 0 | 1.18 | 0.000274 | -0.0161 | 1.16 | 0.000221 | 0 | 1.14 | 0.000263 | -0.0155 | CFL | Bldg | 1200 | 0.23 | 1160 | 0.221 | 0.983 | 1.19 | -0.0134
CFLBldgPGEAsmExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Asm | Ex | CZ16 | 1.21 | 0.00023 | 0 | 1.19 | 0.000274 | -0.0162 | 1.16 | 0.000221 | 0 | 1.14 | 0.000263 | -0.0155 | CFL | Bldg | 1210 | 0.23 | 1160 | 0.221 | 0.983 | 1.19 | -0.0134
CFLBldgSCEAsmExIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | Asm | Ex | IOU | 1.21 | 0.00023 | 0 | 1.33 | 0.00028 | -0.00642 | 1.16 | 0.000221 | 0 | 1.28 | 0.000269 | -0.00618 | CFL | Bldg | 1210 | 0.23 | 1160 | 0.221 | 1.1 | 1.22 | -0.00533
CFLBldgSDGAsmExIOU | Com-Iltg-dWatt-CFL_OSbldg | SDG | Asm | Ex | IOU | 1.21 | 0.00023 | 0 | 1.32 | 0.000283 | -0.0062 | 1.16 | 0.000221 | 0 | 1.27 | 0.000272 | -0.00597 | CFL | Bldg | 1210 | 0.23 | 1160 | 0.221 | 1.09 | 1.23 | -0.00515
CFLBldgPGEAsmExIOU | Com-Iltg-dWatt-CFL_OSbldg | PGE | Asm | Ex | IOU | 1.21 | 0.000231 | 0 | 1.26 | 0.000272 | -0.012 | 1.16 | 0.000221 | 0 | 1.21 | 0.000261 | -0.0115 | CFL | Bldg | 1210 | 0.231 | 1160 | 0.221 | 1.04 | 1.18 | -0.00991
CFLBldgSCGAsmExIOU | Com-Iltg-dWatt-CFL_OSbldg | SCG | Asm | Ex | IOU | 1.21 | 0.00023 | 0 | 1.33 | 0.000281 | -0.00634 | 1.16 | 0.000221 | 0 | 1.28 | 0.000269 | -0.0061 | CFL | Bldg | 1210 | 0.23 | 1160 | 0.221 | 1.1 | 1.22 | -0.00526
CFLBldgPGEAsmNewCZ01 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Asm | New | CZ01 | 1.16 | 0.000222 | 0 | 1.11 | 0.000257 | -0.0205 | 1.16 | 0.000222 | 0 | 1.11 | 0.000257 | -0.0205 | CFL | Bldg | 1160 | 0.222 | 1160 | 0.222 | 0.957 | 1.16 | -0.0177
CFLBldgPGEAsmNewCZ02 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Asm | New | CZ02 | 1.16 | 0.000222 | 0 | 1.18 | 0.00026 | -0.013 | 1.16 | 0.000222 | 0 | 1.18 | 0.00026 | -0.013 | CFL | Bldg | 1160 | 0.222 | 1160 | 0.222 | 1.02 | 1.17 | -0.0112
CFLBldgPGEAsmNewCZ03 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Asm | New | CZ03 | 1.16 | 0.000222 | 0 | 1.17 | 0.000256 | -0.0135 | 1.16 | 0.000222 | 0 | 1.17 | 0.000256 | -0.0135 | CFL | Bldg | 1160 | 0.222 | 1160 | 0.222 | 1.01 | 1.15 | -0.0116
CFLBldgPGEAsmNewCZ04 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Asm | New | CZ04 | 1.16 | 0.000222 | 0 | 1.2 | 0.00026 | -0.0106 | 1.16 | 0.000222 | 0 | 1.2 | 0.00026 | -0.0106 | CFL | Bldg | 1160 | 0.222 | 1160 | 0.222 | 1.03 | 1.17 | -0.00914
CFLBldgPGEAsmNewCZ05 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Asm | New | CZ05 | 1.16 | 0.000222 | 0 | 1.18 | 0.000253 | -0.0117 | 1.16 | 0.000222 | 0 | 1.18 | 0.000253 | -0.0117 | CFL | Bldg | 1160 | 0.222 | 1160 | 0.222 | 1.02 | 1.14 | -0.0101
CFLBldgSCEAsmNewCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Asm | New | CZ05 | 1.16 | 0.000222 | 0 | 1.2 | 0.000262 | -0.0114 | 1.16 | 0.000222 | 0 | 1.2 | 0.000262 | -0.0114 | CFL | Bldg | 1160 | 0.222 | 1160 | 0.222 | 1.03 | 1.18 | -0.00983
CFLBldgSDGAsmNewCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Asm | New | CZ06 | 1.16 | 0.000222 | 0 | 1.25 | 0.000274 | -0.00783 | 1.16 | 0.000222 | 0 | 1.25 | 0.000274 | -0.00783 | CFL | Bldg | 1160 | 0.222 | 1160 | 0.222 | 1.08 | 1.23 | -0.00675
CFLBldgSCEAsmNewCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Asm | New | CZ06 | 1.16 | 0.000222 | 0 | 1.25 | 0.000272 | -0.0073 | 1.16 | 0.000222 | 0 | 1.25 | 0.000272 | -0.0073 | CFL | Bldg | 1160 | 0.222 | 1160 | 0.222 | 1.08 | 1.23 | -0.00629
CFLBldgSDGAsmNewCZ07 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Asm | New | CZ07 | 1.16 | 0.000222 | 0 | 1.26 | 0.000273 | -0.00687 | 1.16 | 0.000222 | 0 | 1.26 | 0.000273 | -0.00687 | CFL | Bldg | 1160 | 0.222 | 1160 | 0.222 | 1.09 | 1.23 | -0.00592
CFLBldgSDGAsmNewCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Asm | New | CZ08 | 1.16 | 0.000222 | 0 | 1.27 | 0.00027 | -0.00607 | 1.16 | 0.000222 | 0 | 1.27 | 0.00027 | -0.00607 | CFL | Bldg | 1160 | 0.222 | 1160 | 0.222 | 1.09 | 1.22 | -0.00523
CFLBldgSCEAsmNewCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Asm | New | CZ08 | 1.16 | 0.000222 | 0 | 1.27 | 0.000268 | -0.00565 | 1.16 | 0.000222 | 0 | 1.27 | 0.000268 | -0.00565 | CFL | Bldg | 1160 | 0.222 | 1160 | 0.222 | 1.09 | 1.21 | -0.00487
CFLBldgSCEAsmNewCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Asm | New | CZ09 | 1.16 | 0.000222 | 0 | 1.26 | 0.000284 | -0.00679 | 1.16 | 0.000222 | 0 | 1.26 | 0.000284 | -0.00679 | CFL | Bldg | 1160 | 0.222 | 1160 | 0.222 | 1.09 | 1.28 | -0.00585
CFLBldgSCEAsmNewCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Asm | New | CZ10 | 1.16 | 0.000222 | 0 | 1.26 | 0.000275 | -0.0067 | 1.16 | 0.000222 | 0 | 1.26 | 0.000275 | -0.0067 | CFL | Bldg | 1160 | 0.222 | 1160 | 0.222 | 1.09 | 1.24 | -0.00578
CFLBldgSDGAsmNewCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Asm | New | CZ10 | 1.16 | 0.000222 | 0 | 1.26 | 0.000277 | -0.00722 | 1.16 | 0.000222 | 0 | 1.26 | 0.000277 | -0.00722 | CFL | Bldg | 1160 | 0.222 | 1160 | 0.222 | 1.09 | 1.25 | -0.00622
CFLBldgPGEAsmNewCZ11 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Asm | New | CZ11 | 1.16 | 0.000222 | 0 | 1.21 | 0.000264 | -0.0112 | 1.16 | 0.000222 | 0 | 1.21 | 0.000264 | -0.0112 | CFL | Bldg | 1160 | 0.222 | 1160 | 0.222 | 1.04 | 1.19 | -0.00966
CFLBldgPGEAsmNewCZ12 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Asm | New | CZ12 | 1.16 | 0.000222 | 0 | 1.2 | 0.000264 | -0.0118 | 1.16 | 0.000222 | 0 | 1.2 | 0.000264 | -0.0118 | CFL | Bldg | 1160 | 0.222 | 1160 | 0.222 | 1.03 | 1.19 | -0.0102
CFLBldgSCEAsmNewCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Asm | New | CZ13 | 1.16 | 0.000222 | 0 | 1.24 | 0.000277 | -0.0106 | 1.16 | 0.000222 | 0 | 1.24 | 0.000277 | -0.0106 | CFL | Bldg | 1160 | 0.222 | 1160 | 0.222 | 1.07 | 1.25 | -0.00914
CFLBldgPGEAsmNewCZ13 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Asm | New | CZ13 | 1.16 | 0.000222 | 0 | 1.21 | 0.000265 | -0.0108 | 1.16 | 0.000222 | 0 | 1.21 | 0.000265 | -0.0108 | CFL | Bldg | 1160 | 0.222 | 1160 | 0.222 | 1.04 | 1.19 | -0.00931
CFLBldgSCEAsmNewCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Asm | New | CZ14 | 1.16 | 0.000222 | 0 | 1.23 | 0.000264 | -0.0104 | 1.16 | 0.000222 | 0 | 1.23 | 0.000264 | -0.0104 | CFL | Bldg | 1160 | 0.222 | 1160 | 0.222 | 1.06 | 1.19 | -0.00897
CFLBldgSDGAsmNewCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Asm | New | CZ14 | 1.16 | 0.000222 | 0 | 1.23 | 0.000266 | -0.0112 | 1.16 | 0.000222 | 0 | 1.23 | 0.000266 | -0.0112 | CFL | Bldg | 1160 | 0.222 | 1160 | 0.222 | 1.06 | 1.2 | -0.00966
CFLBldgSCEAsmNewCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Asm | New | CZ15 | 1.16 | 0.000222 | 0 | 1.39 | 0.000277 | -0.00322 | 1.16 | 0.000222 | 0 | 1.39 | 0.000277 | -0.00322 | CFL | Bldg | 1160 | 0.222 | 1160 | 0.222 | 1.2 | 1.25 | -0.00278
CFLBldgSDGAsmNewCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Asm | New | CZ15 | 1.16 | 0.000222 | 0 | 1.4 | 0.000278 | -0.00347 | 1.16 | 0.000222 | 0 | 1.4 | 0.000278 | -0.00347 | CFL | Bldg | 1160 | 0.222 | 1160 | 0.222 | 1.21 | 1.25 | -0.00299
CFLBldgPGEAsmNewCZ16 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Asm | New | CZ16 | 1.16 | 0.000222 | 0 | 1.14 | 0.000255 | -0.0155 | 1.16 | 0.000222 | 0 | 1.14 | 0.000255 | -0.0155 | CFL | Bldg | 1160 | 0.222 | 1160 | 0.222 | 0.983 | 1.15 | -0.0134
CFLBldgSCEAsmNewCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Asm | New | CZ16 | 1.16 | 0.000222 | 0 | 1.15 | 0.000265 | -0.0154 | 1.16 | 0.000222 | 0 | 1.15 | 0.000265 | -0.0154 | CFL | Bldg | 1160 | 0.222 | 1160 | 0.222 | 0.991 | 1.19 | -0.0133
CFLBldgPGEAsmNewIOU | Com-Iltg-dWatt-CFL_OSbldg | PGE | Asm | New | IOU | 1.16 | 0.000222 | 0 | 1.23 | 0.000275 | -0.011 | 1.16 | 0.000222 | 0 | 1.23 | 0.000275 | -0.011 | CFL | Bldg | 1160 | 0.222 | 1160 | 0.222 | 1.06 | 1.24 | -0.00948
CFLBldgSCEAsmNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | Asm | New | IOU | 1.16 | 0.000222 | 0 | 1.28 | 0.000274 | -0.00677 | 1.16 | 0.000222 | 0 | 1.28 | 0.000274 | -0.00677 | CFL | Bldg | 1160 | 0.222 | 1160 | 0.222 | 1.1 | 1.23 | -0.00584
CFLBldgSDGAsmNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SDG | Asm | New | IOU | 1.16 | 0.000222 | 0 | 1.26 | 0.000274 | -0.00702 | 1.16 | 0.000222 | 0 | 1.26 | 0.000274 | -0.00702 | CFL | Bldg | 1160 | 0.222 | 1160 | 0.222 | 1.09 | 1.23 | -0.00605
CFLBldgSCGAsmNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SCG | Asm | New | IOU | 1.16 | 0.000222 | 0 | 1.28 | 0.000274 | -0.00677 | 1.16 | 0.000222 | 0 | 1.28 | 0.000274 | -0.00677 | CFL | Bldg | 1160 | 0.222 | 1160 | 0.222 | 1.1 | 1.23 | -0.00584
CFLBldgPGEComExCZ01 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Com | Ex | CZ01 | 2.21 | 0.000518 | 0 | 2.18 | 0.000604 | -0.027 | 2.12 | 0.000475 | 0 | 2.09 | 0.000552 | -0.0259 | CFL | Bldg | 2210 | 0.518 | 2120 | 0.475 | 0.986 | 1.16 | -0.0122
CFLBldgPGEComExCZ02 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Com | Ex | CZ02 | 2.28 | 0.000455 | 0 | 2.38 | 0.000561 | -0.018 | 2.21 | 0.000435 | 0 | 2.3 | 0.000536 | -0.0173 | CFL | Bldg | 2280 | 0.455 | 2210 | 0.435 | 1.04 | 1.23 | -0.00783
CFLBldgPGEComExCZ03 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Com | Ex | CZ03 | 2.17 | 0.000454 | 0 | 2.29 | 0.00056 | -0.0157 | 2.09 | 0.000429 | 0 | 2.2 | 0.000528 | -0.0151 | CFL | Bldg | 2170 | 0.454 | 2090 | 0.429 | 1.05 | 1.23 | -0.00722
CFLBldgPGEComExCZ04 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Com | Ex | CZ04 | 2.15 | 0.000496 | 0 | 2.29 | 0.00061 | -0.0128 | 2.06 | 0.000462 | 0 | 2.2 | 0.000569 | -0.0123 | CFL | Bldg | 2150 | 0.496 | 2060 | 0.462 | 1.07 | 1.23 | -0.00597
CFLBldgPGEComExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Com | Ex | CZ05 | 2.21 | 0.000502 | 0 | 2.38 | 0.000626 | -0.0169 | 2.13 | 0.000464 | 0 | 2.3 | 0.000579 | -0.0163 | CFL | Bldg | 2210 | 0.502 | 2130 | 0.464 | 1.08 | 1.25 | -0.00765
CFLBldgSCGComExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCG | Com | Ex | CZ05 | 2.82 | 0.00057 | 0 | 3.01 | 0.000708 | -0.0242 | 2.75 | 0.000549 | 0 | 2.94 | 0.000682 | -0.0236 | CFL | Bldg | 2820 | 0.57 | 2750 | 0.549 | 1.07 | 1.24 | -0.00858
CFLBldgSCEComExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Com | Ex | CZ05 | 2.82 | 0.00057 | 0 | 3.01 | 0.000708 | -0.0242 | 2.75 | 0.000549 | 0 | 2.94 | 0.000682 | -0.0236 | CFL | Bldg | 2820 | 0.57 | 2750 | 0.549 | 1.07 | 1.24 | -0.00858
CFLBldgSCGComExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCG | Com | Ex | CZ06 | 2.23 | 0.000507 | 0 | 2.48 | 0.000632 | -0.0089 | 2.15 | 0.000476 | 0 | 2.4 | 0.000593 | -0.00863 | CFL | Bldg | 2230 | 0.507 | 2150 | 0.476 | 1.12 | 1.25 | -0.00401
CFLBldgSDGComExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Com | Ex | CZ06 | 2.3 | 0.000501 | 0 | 2.51 | 0.000623 | -0.0123 | 2.23 | 0.000472 | 0 | 2.43 | 0.000587 | -0.0119 | CFL | Bldg | 2300 | 0.501 | 2230 | 0.472 | 1.09 | 1.24 | -0.00534
CFLBldgSCEComExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Com | Ex | CZ06 | 2.23 | 0.000507 | 0 | 2.49 | 0.000632 | -0.00893 | 2.16 | 0.000477 | 0 | 2.4 | 0.000594 | -0.00866 | CFL | Bldg | 2230 | 0.507 | 2160 | 0.477 | 1.11 | 1.25 | -0.00401
CFLBldgSDGComExCZ07 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Com | Ex | CZ07 | 2.21 | 0.000503 | 0 | 2.45 | 0.000622 | -0.00849 | 2.12 | 0.000467 | 0 | 2.35 | 0.000577 | -0.00825 | CFL | Bldg | 2210 | 0.503 | 2120 | 0.467 | 1.11 | 1.24 | -0.00389
CFLBldgSCGComExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCG | Com | Ex | CZ08 | 2.17 | 0.000498 | 0 | 2.41 | 0.000622 | -0.00792 | 2.09 | 0.000466 | 0 | 2.33 | 0.000582 | -0.00767 | CFL | Bldg | 2170 | 0.498 | 2090 | 0.466 | 1.11 | 1.25 | -0.00367
CFLBldgSDGComExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Com | Ex | CZ08 | 2.35 | 0.000558 | 0 | 2.63 | 0.000701 | -0.0092 | 2.28 | 0.000528 | 0 | 2.55 | 0.000662 | -0.00894 | CFL | Bldg | 2350 | 0.558 | 2280 | 0.528 | 1.12 | 1.25 | -0.00392
CFLBldgSCEComExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Com | Ex | CZ08 | 2.16 | 0.000497 | 0 | 2.4 | 0.00062 | -0.00792 | 2.09 | 0.000466 | 0 | 2.32 | 0.000581 | -0.00767 | CFL | Bldg | 2160 | 0.497 | 2090 | 0.466 | 1.11 | 1.25 | -0.00367
CFLBldgSCEComExCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Com | Ex | CZ09 | 2.19 | 0.000503 | 0 | 2.47 | 0.000647 | -0.00979 | 2.11 | 0.000472 | 0 | 2.38 | 0.000607 | -0.00943 | CFL | Bldg | 2190 | 0.503 | 2110 | 0.472 | 1.13 | 1.29 | -0.00447
CFLBldgSCGComExCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCG | Com | Ex | CZ09 | 2.2 | 0.000505 | 0 | 2.48 | 0.000652 | -0.01 | 2.12 | 0.000472 | 0 | 2.39 | 0.000608 | -0.00962 | CFL | Bldg | 2200 | 0.505 | 2120 | 0.472 | 1.13 | 1.29 | -0.00454
CFLBldgSDGComExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Com | Ex | CZ10 | 2.18 | 0.000511 | 0 | 2.41 | 0.000648 | -0.00984 | 2.11 | 0.000477 | 0 | 2.32 | 0.000606 | -0.00953 | CFL | Bldg | 2180 | 0.511 | 2110 | 0.477 | 1.1 | 1.27 | -0.00452
CFLBldgSCGComExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCG | Com | Ex | CZ10 | 2.18 | 0.000498 | 0 | 2.41 | 0.000627 | -0.00945 | 2.13 | 0.000474 | 0 | 2.34 | 0.000596 | -0.00922 | CFL | Bldg | 2180 | 0.498 | 2130 | 0.474 | 1.1 | 1.26 | -0.00433
CFLBldgSCEComExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Com | Ex | CZ10 | 2.18 | 0.000498 | 0 | 2.41 | 0.000627 | -0.00945 | 2.13 | 0.000474 | 0 | 2.34 | 0.000596 | -0.00922 | CFL | Bldg | 2180 | 0.498 | 2130 | 0.474 | 1.1 | 1.26 | -0.00433
CFLBldgPGEComExCZ11 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Com | Ex | CZ11 | 2.27 | 0.000454 | 0 | 2.43 | 0.000559 | -0.0161 | 2.2 | 0.000432 | 0 | 2.34 | 0.00053 | -0.0156 | CFL | Bldg | 2270 | 0.454 | 2200 | 0.432 | 1.06 | 1.23 | -0.00709
CFLBldgPGEComExCZ12 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Com | Ex | CZ12 | 2.25 | 0.000462 | 0 | 2.39 | 0.000569 | -0.0155 | 2.17 | 0.000441 | 0 | 2.31 | 0.000542 | -0.015 | CFL | Bldg | 2250 | 0.462 | 2170 | 0.441 | 1.06 | 1.23 | -0.00691
CFLBldgSCGComExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCG | Com | Ex | CZ13 | 2.34 | 0.00046 | 0 | 2.65 | 0.000582 | -0.0142 | 2.26 | 0.000439 | 0 | 2.56 | 0.000553 | -0.0137 | CFL | Bldg | 2340 | 0.46 | 2260 | 0.439 | 1.13 | 1.26 | -0.00606
CFLBldgSCEComExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Com | Ex | CZ13 | 2.34 | 0.00046 | 0 | 2.65 | 0.000582 | -0.0142 | 2.26 | 0.000439 | 0 | 2.56 | 0.000553 | -0.0137 | CFL | Bldg | 2340 | 0.46 | 2260 | 0.439 | 1.13 | 1.26 | -0.00606
CFLBldgPGEComExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Com | Ex | CZ13 | 2.3 | 0.000457 | 0 | 2.56 | 0.000577 | -0.0144 | 2.22 | 0.000434 | 0 | 2.47 | 0.000547 | -0.0139 | CFL | Bldg | 2300 | 0.457 | 2220 | 0.434 | 1.11 | 1.26 | -0.00626
CFLBldgSCEComExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Com | Ex | CZ14 | 2.28 | 0.000529 | 0 | 2.48 | 0.000672 | -0.0157 | 2.21 | 0.000499 | 0 | 2.4 | 0.000633 | -0.0152 | CFL | Bldg | 2280 | 0.529 | 2210 | 0.499 | 1.09 | 1.27 | -0.00688
CFLBldgSCGComExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCG | Com | Ex | CZ14 | 2.28 | 0.000529 | 0 | 2.48 | 0.000672 | -0.0157 | 2.21 | 0.000499 | 0 | 2.4 | 0.000633 | -0.0152 | CFL | Bldg | 2280 | 0.529 | 2210 | 0.499 | 1.09 | 1.27 | -0.00688
CFLBldgSDGComExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Com | Ex | CZ14 | 1.9 | 0.000441 | 0 | 2.06 | 0.000556 | -0.0111 | 1.8 | 0.000401 | 0 | 1.96 | 0.000506 | -0.0106 | CFL | Bldg | 1900 | 0.441 | 1800 | 0.401 | 1.09 | 1.26 | -0.00589
CFLBldgSCEComExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Com | Ex | CZ15 | 2.1 | 0.000464 | 0 | 2.49 | 0.000589 | -0.00398 | 2.04 | 0.000439 | 0 | 2.41 | 0.000557 | -0.00387 | CFL | Bldg | 2100 | 0.464 | 2040 | 0.439 | 1.18 | 1.27 | -0.0019
CFLBldgSDGComExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Com | Ex | CZ15 | 1.72 | 0.000344 | 0 | 2.03 | 0.000437 | -0.00286 | 1.65 | 0.000319 | 0 | 1.94 | 0.000405 | -0.00275 | CFL | Bldg | 1720 | 0.344 | 1650 | 0.319 | 1.18 | 1.27 | -0.00167
CFLBldgSCGComExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCG | Com | Ex | CZ15 | 2.1 | 0.000464 | 0 | 2.49 | 0.000589 | -0.00398 | 2.04 | 0.000439 | 0 | 2.41 | 0.000557 | -0.00387 | CFL | Bldg | 2100 | 0.464 | 2040 | 0.439 | 1.18 | 1.27 | -0.0019
CFLBldgSCEComExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Com | Ex | CZ16 | 2.14 | 0.000417 | 0 | 2.15 | 0.000509 | -0.0247 | 2.05 | 0.00039 | 0 | 2.07 | 0.000477 | -0.0237 | CFL | Bldg | 2140 | 0.417 | 2050 | 0.39 | 1.01 | 1.22 | -0.0116
CFLBldgSCGComExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCG | Com | Ex | CZ16 | 2.14 | 0.000417 | 0 | 2.15 | 0.000509 | -0.0247 | 2.05 | 0.00039 | 0 | 2.07 | 0.000477 | -0.0237 | CFL | Bldg | 2140 | 0.417 | 2050 | 0.39 | 1.01 | 1.22 | -0.0116
CFLBldgPGEComExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Com | Ex | CZ16 | 2.11 | 0.000405 | 0 | 2.09 | 0.000492 | -0.0234 | 2.04 | 0.000387 | 0 | 2.02 | 0.00047 | -0.0226 | CFL | Bldg | 2110 | 0.405 | 2040 | 0.387 | 0.99 | 1.21 | -0.0111
CFLBldgSCEComExIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | Com | Ex | IOU | 2.19 | 0.000498 | 0 | 2.44 | 0.000626 | -0.00931 | 2.12 | 0.000469 | 0 | 2.36 | 0.000589 | -0.00902 | CFL | Bldg | 2190 | 0.498 | 2120 | 0.469 | 1.11 | 1.26 | -0.00425
CFLBldgSDGComExIOU | Com-Iltg-dWatt-CFL_OSbldg | SDG | Com | Ex | IOU | 2.21 | 0.000506 | 0 | 2.44 | 0.00063 | -0.00894 | 2.13 | 0.000471 | 0 | 2.35 | 0.000586 | -0.00868 | CFL | Bldg | 2210 | 0.506 | 2130 | 0.471 | 1.1 | 1.24 | -0.00408
CFLBldgSCGComExIOU | Com-Iltg-dWatt-CFL_OSbldg | SCG | Com | Ex | IOU | 2.2 | 0.0005 | 0 | 2.45 | 0.000631 | -0.00938 | 2.12 | 0.00047 | 0 | 2.37 | 0.000593 | -0.00907 | CFL | Bldg | 2200 | 0.5 | 2120 | 0.47 | 1.12 | 1.26 | -0.00428
CFLBldgPGEComExIOU | Com-Iltg-dWatt-CFL_OSbldg | PGE | Com | Ex | IOU | 2.21 | 0.000464 | 0 | 2.36 | 0.000573 | -0.0154 | 2.13 | 0.000439 | 0 | 2.27 | 0.000542 | -0.0148 | CFL | Bldg | 2210 | 0.464 | 2130 | 0.439 | 1.07 | 1.23 | -0.00695
CFLBldgSCEComNewCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Com | New | CZ05 | 2.75 | 0.000567 | 0 | 2.83 | 0.000694 | -0.0248 | 2.75 | 0.000567 | 0 | 2.83 | 0.000694 | -0.0248 | CFL | Bldg | 2750 | 0.567 | 2750 | 0.567 | 1.03 | 1.22 | -0.00902
CFLBldgPGEComNewCZ05 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Com | New | CZ05 | 2.12 | 0.000457 | 0 | 2.19 | 0.000557 | -0.0162 | 2.12 | 0.000457 | 0 | 2.19 | 0.000557 | -0.0162 | CFL | Bldg | 2120 | 0.457 | 2120 | 0.457 | 1.03 | 1.22 | -0.00764
CFLBldgSDGComNewCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Com | New | CZ06 | 2.24 | 0.000463 | 0 | 2.42 | 0.000574 | -0.0121 | 2.24 | 0.000463 | 0 | 2.42 | 0.000574 | -0.0121 | CFL | Bldg | 2240 | 0.463 | 2240 | 0.463 | 1.08 | 1.24 | -0.0054
CFLBldgSCEComNewCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Com | New | CZ06 | 2.24 | 0.000497 | 0 | 2.45 | 0.000615 | -0.00977 | 2.24 | 0.000497 | 0 | 2.45 | 0.000615 | -0.00977 | CFL | Bldg | 2240 | 0.497 | 2240 | 0.497 | 1.09 | 1.24 | -0.00436
CFLBldgSDGComNewCZ07 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Com | New | CZ07 | 2.1 | 0.000455 | 0 | 2.28 | 0.000554 | -0.00802 | 2.1 | 0.000455 | 0 | 2.28 | 0.000554 | -0.00802 | CFL | Bldg | 2100 | 0.455 | 2100 | 0.455 | 1.09 | 1.22 | -0.00382
CFLBldgSCEComNewCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Com | New | CZ08 | 2.16 | 0.00048 | 0 | 2.37 | 0.000592 | -0.00819 | 2.16 | 0.00048 | 0 | 2.37 | 0.000592 | -0.00819 | CFL | Bldg | 2160 | 0.48 | 2160 | 0.48 | 1.1 | 1.23 | -0.00379
CFLBldgSDGComNewCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Com | New | CZ08 | 2.32 | 0.000541 | 0 | 2.54 | 0.000675 | -0.009 | 2.32 | 0.000541 | 0 | 2.54 | 0.000675 | -0.009 | CFL | Bldg | 2320 | 0.541 | 2320 | 0.541 | 1.09 | 1.25 | -0.00388
CFLBldgSCEComNewCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Com | New | CZ09 | 2.19 | 0.000486 | 0 | 2.42 | 0.000629 | -0.00909 | 2.19 | 0.000486 | 0 | 2.42 | 0.000629 | -0.00909 | CFL | Bldg | 2190 | 0.486 | 2190 | 0.486 | 1.11 | 1.29 | -0.00415
CFLBldgSCEComNewCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Com | New | CZ10 | 2.03 | 0.000452 | 0 | 2.2 | 0.000573 | -0.00855 | 2.03 | 0.000452 | 0 | 2.2 | 0.000573 | -0.00855 | CFL | Bldg | 2030 | 0.452 | 2030 | 0.452 | 1.08 | 1.27 | -0.00421
CFLBldgSDGComNewCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Com | New | CZ10 | 2.15 | 0.00048 | 0 | 2.36 | 0.000628 | -0.0098 | 2.15 | 0.00048 | 0 | 2.36 | 0.000628 | -0.0098 | CFL | Bldg | 2150 | 0.48 | 2150 | 0.48 | 1.1 | 1.31 | -0.00456
CFLBldgPGEComNewCZ11 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Com | New | CZ11 | 2.18 | 0.000432 | 0 | 2.32 | 0.000539 | -0.0151 | 2.18 | 0.000432 | 0 | 2.32 | 0.000539 | -0.0151 | CFL | Bldg | 2180 | 0.432 | 2180 | 0.432 | 1.06 | 1.25 | -0.00693
CFLBldgPGEComNewCZ12 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Com | New | CZ12 | 2.17 | 0.00044 | 0 | 2.31 | 0.000544 | -0.0144 | 2.17 | 0.00044 | 0 | 2.31 | 0.000544 | -0.0144 | CFL | Bldg | 2170 | 0.44 | 2170 | 0.44 | 1.06 | 1.24 | -0.00664
CFLBldgSCEComNewCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Com | New | CZ13 | 2.33 | 0.000456 | 0 | 2.64 | 0.000584 | -0.0136 | 2.33 | 0.000456 | 0 | 2.64 | 0.000584 | -0.0136 | CFL | Bldg | 2330 | 0.456 | 2330 | 0.456 | 1.13 | 1.28 | -0.00584
CFLBldgPGEComNewCZ13 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Com | New | CZ13 | 2.24 | 0.000442 | 0 | 2.43 | 0.000545 | -0.0137 | 2.24 | 0.000442 | 0 | 2.43 | 0.000545 | -0.0137 | CFL | Bldg | 2240 | 0.442 | 2240 | 0.442 | 1.08 | 1.23 | -0.00612
CFLBldgSCEComNewCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Com | New | CZ14 | 2.26 | 0.000505 | 0 | 2.45 | 0.000654 | -0.016 | 2.26 | 0.000505 | 0 | 2.45 | 0.000654 | -0.016 | CFL | Bldg | 2260 | 0.505 | 2260 | 0.505 | 1.08 | 1.3 | -0.00708
CFLBldgSDGComNewCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Com | New | CZ14 | 1.83 | 0.000388 | 0 | 1.98 | 0.000499 | -0.0109 | 1.83 | 0.000388 | 0 | 1.98 | 0.000499 | -0.0109 | CFL | Bldg | 1830 | 0.388 | 1830 | 0.388 | 1.08 | 1.29 | -0.00596
CFLBldgSCEComNewCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Com | New | CZ15 | 2.01 | 0.000439 | 0 | 2.37 | 0.000582 | -0.00333 | 2.01 | 0.000439 | 0 | 2.37 | 0.000582 | -0.00333 | CFL | Bldg | 2010 | 0.439 | 2010 | 0.439 | 1.18 | 1.33 | -0.00166
CFLBldgSDGComNewCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Com | New | CZ15 | 1.61 | 0.00029 | 0 | 1.9 | 0.000384 | -0.0025 | 1.61 | 0.00029 | 0 | 1.9 | 0.000384 | -0.0025 | CFL | Bldg | 1610 | 0.29 | 1610 | 0.29 | 1.18 | 1.32 | -0.00155
CFLBldgSCEComNewCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Com | New | CZ16 | 2.06 | 0.000407 | 0 | 2.06 | 0.000501 | -0.023 | 2.06 | 0.000407 | 0 | 2.06 | 0.000501 | -0.023 | CFL | Bldg | 2060 | 0.407 | 2060 | 0.407 | 1 | 1.23 | -0.0112
CFLBldgPGEComNewCZ16 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Com | New | CZ16 | 2.02 | 0.000383 | 0 | 1.95 | 0.000453 | -0.0214 | 2.02 | 0.000383 | 0 | 1.95 | 0.000453 | -0.0214 | CFL | Bldg | 2020 | 0.383 | 2020 | 0.383 | 0.965 | 1.18 | -0.0106
CFLBldgSCGComNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SCG | Com | New | IOU | 2.14 | 0.000473 | 0 | 2.35 | 0.000594 | -0.00868 | 2.14 | 0.000473 | 0 | 2.35 | 0.000594 | -0.00868 | CFL | Bldg | 2140 | 0.473 | 2140 | 0.473 | 1.1 | 1.26 | -0.00406
CFLBldgPGEComNewIOU | Com-Iltg-dWatt-CFL_OSbldg | PGE | Com | New | IOU | 2.16 | 0.000446 | 0 | 2.36 | 0.000566 | -0.0135 | 2.16 | 0.000446 | 0 | 2.36 | 0.000566 | -0.0135 | CFL | Bldg | 2160 | 0.446 | 2160 | 0.446 | 1.09 | 1.27 | -0.00625
CFLBldgSDGComNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SDG | Com | New | IOU | 2.12 | 0.000463 | 0 | 2.31 | 0.000575 | -0.0086 | 2.12 | 0.000463 | 0 | 2.31 | 0.000575 | -0.0086 | CFL | Bldg | 2120 | 0.463 | 2120 | 0.463 | 1.09 | 1.24 | -0.00406
CFLBldgSCEComNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | Com | New | IOU | 2.13 | 0.000471 | 0 | 2.33 | 0.000593 | -0.0087 | 2.13 | 0.000471 | 0 | 2.33 | 0.000593 | -0.0087 | CFL | Bldg | 2130 | 0.471 | 2130 | 0.471 | 1.09 | 1.26 | -0.00408
CFLBldgPGEECCExCZ01 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ECC | Ex | CZ01 | 1.6 | 0.000583 | 0 | 1.64 | 0.000712 | -0.0316 | 1.46 | 0.000477 | 0 | 1.5 | 0.000582 | -0.0289 | CFL | Bldg | 1600 | 0.583 | 1460 | 0.477 | 1.03 | 1.22 | -0.0198
CFLBldgPGEECCExCZ02 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ECC | Ex | CZ02 | 1.59 | 0.000377 | 0 | 1.73 | 0.000497 | -0.0193 | 1.46 | 0.00031 | 0 | 1.59 | 0.000409 | -0.0177 | CFL | Bldg | 1590 | 0.377 | 1460 | 0.31 | 1.09 | 1.32 | -0.0121
CFLBldgPGEECCExCZ03 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ECC | Ex | CZ03 | 1.59 | 0.000377 | 0 | 1.72 | 0.00047 | -0.0201 | 1.46 | 0.00031 | 0 | 1.58 | 0.000386 | -0.0184 | CFL | Bldg | 1590 | 0.377 | 1460 | 0.31 | 1.08 | 1.25 | -0.0126
CFLBldgPGEECCExCZ04 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ECC | Ex | CZ04 | 1.59 | 0.00058 | 0 | 1.76 | 0.000755 | -0.0154 | 1.46 | 0.000477 | 0 | 1.61 | 0.00062 | -0.0141 | CFL | Bldg | 1590 | 0.58 | 1460 | 0.477 | 1.1 | 1.3 | -0.00966
CFLBldgSCGECCExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCG | ECC | Ex | CZ05 | 1.59 | 0.000581 | 0 | 1.72 | 0.000718 | -0.0188 | 1.46 | 0.000477 | 0 | 1.58 | 0.00059 | -0.0172 | CFL | Bldg | 1590 | 0.581 | 1460 | 0.477 | 1.08 | 1.24 | -0.0118
CFLBldgPGEECCExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ECC | Ex | CZ05 | 1.59 | 0.00058 | 0 | 1.72 | 0.000718 | -0.0188 | 1.46 | 0.000477 | 0 | 1.58 | 0.00059 | -0.0172 | CFL | Bldg | 1590 | 0.58 | 1460 | 0.477 | 1.08 | 1.24 | -0.0118
CFLBldgSCEECCExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ECC | Ex | CZ05 | 1.59 | 0.000581 | 0 | 1.72 | 0.000718 | -0.0188 | 1.46 | 0.000477 | 0 | 1.58 | 0.00059 | -0.0172 | CFL | Bldg | 1590 | 0.581 | 1460 | 0.477 | 1.08 | 1.24 | -0.0118
CFLBldgSDGECCExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SDG | ECC | Ex | CZ06 | 1.59 | 0.000579 | 0 | 1.78 | 0.000739 | -0.00925 | 1.46 | 0.000477 | 0 | 1.64 | 0.000609 | -0.00848 | CFL | Bldg | 1590 | 0.579 | 1460 | 0.477 | 1.12 | 1.28 | -0.00581
CFLBldgSCEECCExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ECC | Ex | CZ06 | 1.59 | 0.000581 | 0 | 1.78 | 0.000741 | -0.00926 | 1.46 | 0.000477 | 0 | 1.64 | 0.000609 | -0.00848 | CFL | Bldg | 1590 | 0.581 | 1460 | 0.477 | 1.12 | 1.28 | -0.00581
CFLBldgSCGECCExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCG | ECC | Ex | CZ06 | 1.59 | 0.000581 | 0 | 1.78 | 0.000742 | -0.00926 | 1.46 | 0.000477 | 0 | 1.64 | 0.000609 | -0.00848 | CFL | Bldg | 1590 | 0.581 | 1460 | 0.477 | 1.12 | 1.28 | -0.00581
CFLBldgSDGECCExCZ07 | Com-Iltg-dWatt-CFL_OSbldg | SDG | ECC | Ex | CZ07 | 1.59 | 0.000579 | 0 | 1.8 | 0.000738 | -0.00764 | 1.46 | 0.000477 | 0 | 1.65 | 0.000608 | -0.00701 | CFL | Bldg | 1590 | 0.579 | 1460 | 0.477 | 1.13 | 1.27 | -0.0048
CFLBldgSDGECCExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SDG | ECC | Ex | CZ08 | 1.59 | 0.000579 | 0 | 1.8 | 0.000735 | -0.0083 | 1.46 | 0.000477 | 0 | 1.66 | 0.000606 | -0.00762 | CFL | Bldg | 1590 | 0.579 | 1460 | 0.477 | 1.14 | 1.27 | -0.00522
CFLBldgSCGECCExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCG | ECC | Ex | CZ08 | 1.59 | 0.000581 | 0 | 1.8 | 0.000738 | -0.00832 | 1.46 | 0.000477 | 0 | 1.66 | 0.000606 | -0.00762 | CFL | Bldg | 1590 | 0.581 | 1460 | 0.477 | 1.14 | 1.27 | -0.00522
CFLBldgSCEECCExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ECC | Ex | CZ08 | 1.59 | 0.000581 | 0 | 1.8 | 0.000737 | -0.00832 | 1.46 | 0.000477 | 0 | 1.66 | 0.000606 | -0.00762 | CFL | Bldg | 1590 | 0.581 | 1460 | 0.477 | 1.14 | 1.27 | -0.00522
CFLBldgSCEECCExCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ECC | Ex | CZ09 | 1.59 | 0.00058 | 0 | 1.83 | 0.000757 | -0.00925 | 1.46 | 0.000477 | 0 | 1.68 | 0.000622 | -0.00848 | CFL | Bldg | 1590 | 0.58 | 1460 | 0.477 | 1.15 | 1.3 | -0.00581
CFLBldgSCGECCExCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCG | ECC | Ex | CZ09 | 1.6 | 0.000582 | 0 | 1.83 | 0.00076 | -0.00927 | 1.46 | 0.000477 | 0 | 1.68 | 0.000622 | -0.00848 | CFL | Bldg | 1600 | 0.582 | 1460 | 0.477 | 1.15 | 1.3 | -0.00581
CFLBldgSCGECCExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCG | ECC | Ex | CZ10 | 1.59 | 0.000576 | 0 | 1.79 | 0.000745 | -0.00982 | 1.46 | 0.000477 | 0 | 1.65 | 0.000618 | -0.00904 | CFL | Bldg | 1590 | 0.576 | 1460 | 0.477 | 1.13 | 1.3 | -0.00619
CFLBldgSDGECCExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SDG | ECC | Ex | CZ10 | 1.59 | 0.000579 | 0 | 1.8 | 0.00075 | -0.00985 | 1.46 | 0.000477 | 0 | 1.65 | 0.000618 | -0.00904 | CFL | Bldg | 1590 | 0.579 | 1460 | 0.477 | 1.13 | 1.3 | -0.00619
CFLBldgSCEECCExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ECC | Ex | CZ10 | 1.59 | 0.000576 | 0 | 1.79 | 0.000745 | -0.00982 | 1.46 | 0.000477 | 0 | 1.65 | 0.000618 | -0.00904 | CFL | Bldg | 1590 | 0.576 | 1460 | 0.477 | 1.13 | 1.3 | -0.00619
CFLBldgPGEECCExCZ11 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ECC | Ex | CZ11 | 1.59 | 0.000376 | 0 | 1.78 | 0.000468 | -0.0177 | 1.46 | 0.00031 | 0 | 1.63 | 0.000386 | -0.0162 | CFL | Bldg | 1590 | 0.376 | 1460 | 0.31 | 1.12 | 1.25 | -0.0111
CFLBldgPGEECCExCZ12 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ECC | Ex | CZ12 | 1.59 | 0.000376 | 0 | 1.76 | 0.000473 | -0.0173 | 1.46 | 0.00031 | 0 | 1.62 | 0.00039 | -0.0159 | CFL | Bldg | 1590 | 0.376 | 1460 | 0.31 | 1.11 | 1.26 | -0.0109
CFLBldgSCGECCExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCG | ECC | Ex | CZ13 | 1.58 | 0.000371 | 0 | 1.77 | 0.000481 | -0.0139 | 1.46 | 0.00031 | 0 | 1.64 | 0.000402 | -0.0128 | CFL | Bldg | 1580 | 0.371 | 1460 | 0.31 | 1.12 | 1.3 | -0.00877
CFLBldgPGEECCExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ECC | Ex | CZ13 | 1.59 | 0.000376 | 0 | 1.78 | 0.000487 | -0.0139 | 1.46 | 0.00031 | 0 | 1.64 | 0.000402 | -0.0128 | CFL | Bldg | 1590 | 0.376 | 1460 | 0.31 | 1.12 | 1.3 | -0.00877
CFLBldgSCEECCExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ECC | Ex | CZ13 | 1.58 | 0.000371 | 0 | 1.77 | 0.000481 | -0.0139 | 1.46 | 0.00031 | 0 | 1.64 | 0.000402 | -0.0128 | CFL | Bldg | 1580 | 0.371 | 1460 | 0.31 | 1.12 | 1.3 | -0.00877
CFLBldgSDGECCExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SDG | ECC | Ex | CZ14 | 1.59 | 0.000579 | 0 | 1.76 | 0.000739 | -0.0148 | 1.46 | 0.000477 | 0 | 1.61 | 0.000609 | -0.0136 | CFL | Bldg | 1590 | 0.579 | 1460 | 0.477 | 1.1 | 1.28 | -0.00932
CFLBldgSCGECCExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCG | ECC | Ex | CZ14 | 1.59 | 0.000576 | 0 | 1.76 | 0.000735 | -0.0148 | 1.46 | 0.000477 | 0 | 1.61 | 0.000609 | -0.0136 | CFL | Bldg | 1590 | 0.576 | 1460 | 0.477 | 1.1 | 1.28 | -0.00932
CFLBldgSCEECCExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ECC | Ex | CZ14 | 1.59 | 0.000576 | 0 | 1.76 | 0.000735 | -0.0148 | 1.46 | 0.000477 | 0 | 1.61 | 0.000609 | -0.0136 | CFL | Bldg | 1590 | 0.576 | 1460 | 0.477 | 1.1 | 1.28 | -0.00932
CFLBldgSCEECCExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ECC | Ex | CZ15 | 1.59 | 0.000575 | 0 | 1.9 | 0.000727 | -0.00408 | 1.46 | 0.000477 | 0 | 1.75 | 0.000602 | -0.00375 | CFL | Bldg | 1590 | 0.575 | 1460 | 0.477 | 1.2 | 1.26 | -0.00257
CFLBldgSCGECCExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCG | ECC | Ex | CZ15 | 1.59 | 0.000575 | 0 | 1.9 | 0.000727 | -0.00408 | 1.46 | 0.000477 | 0 | 1.75 | 0.000602 | -0.00375 | CFL | Bldg | 1590 | 0.575 | 1460 | 0.477 | 1.2 | 1.26 | -0.00257
CFLBldgSCGECCExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCG | ECC | Ex | CZ16 | 1.59 | 0.000373 | 0 | 1.66 | 0.00046 | -0.0262 | 1.46 | 0.00031 | 0 | 1.52 | 0.000382 | -0.0241 | CFL | Bldg | 1590 | 0.373 | 1460 | 0.31 | 1.04 | 1.23 | -0.0165
CFLBldgPGEECCExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ECC | Ex | CZ16 | 1.59 | 0.000377 | 0 | 1.66 | 0.000464 | -0.0263 | 1.46 | 0.00031 | 0 | 1.52 | 0.000382 | -0.0241 | CFL | Bldg | 1590 | 0.377 | 1460 | 0.31 | 1.04 | 1.23 | -0.0165
CFLBldgSCEECCExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ECC | Ex | CZ16 | 1.59 | 0.000373 | 0 | 1.66 | 0.00046 | -0.0262 | 1.46 | 0.00031 | 0 | 1.52 | 0.000382 | -0.0241 | CFL | Bldg | 1590 | 0.373 | 1460 | 0.31 | 1.04 | 1.23 | -0.0165
CFLBldgSDGECCExIOU | Com-Iltg-dWatt-CFL_OSbldg | SDG | ECC | Ex | IOU | 1.59 | 0.000579 | 0 | 1.8 | 0.000741 | -0.00821 | 1.46 | 0.000477 | 0 | 1.65 | 0.00061 | -0.00753 | CFL | Bldg | 1590 | 0.579 | 1460 | 0.477 | 1.13 | 1.28 | -0.00516
CFLBldgSCEECCExIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | ECC | Ex | IOU | 1.59 | 0.00056 | 0 | 1.79 | 0.000714 | -0.0103 | 1.46 | 0.000461 | 0 | 1.65 | 0.000588 | -0.00949 | CFL | Bldg | 1590 | 0.56 | 1460 | 0.461 | 1.13 | 1.28 | -0.0065
CFLBldgSCGECCExIOU | Com-Iltg-dWatt-CFL_OSbldg | SCG | ECC | Ex | IOU | 1.59 | 0.000567 | 0 | 1.8 | 0.000727 | -0.00996 | 1.46 | 0.000466 | 0 | 1.65 | 0.000597 | -0.00914 | CFL | Bldg | 1590 | 0.567 | 1460 | 0.466 | 1.13 | 1.28 | -0.00626
CFLBldgPGEECCExIOU | Com-Iltg-dWatt-CFL_OSbldg | PGE | ECC | Ex | IOU | 1.59 | 0.000416 | 0 | 1.74 | 0.000525 | -0.0185 | 1.46 | 0.000342 | 0 | 1.6 | 0.000432 | -0.0169 | CFL | Bldg | 1590 | 0.416 | 1460 | 0.342 | 1.1 | 1.26 | -0.0116
CFLBldgPGEECCNewCZ01 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ECC | New | CZ01 | 1.46 | 0.000476 | 0 | 1.49 | 0.000556 | -0.0298 | 1.46 | 0.000476 | 0 | 1.49 | 0.000556 | -0.0298 | CFL | Bldg | 1460 | 0.476 | 1460 | 0.476 | 1.02 | 1.17 | -0.0204
CFLBldgPGEECCNewCZ02 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ECC | New | CZ02 | 1.46 | 0.000309 | 0 | 1.58 | 0.000421 | -0.0181 | 1.46 | 0.000309 | 0 | 1.58 | 0.000421 | -0.0181 | CFL | Bldg | 1460 | 0.309 | 1460 | 0.309 | 1.08 | 1.36 | -0.0124
CFLBldgPGEECCNewCZ03 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ECC | New | CZ03 | 1.46 | 0.000309 | 0 | 1.55 | 0.000405 | -0.0199 | 1.46 | 0.000309 | 0 | 1.55 | 0.000405 | -0.0199 | CFL | Bldg | 1460 | 0.309 | 1460 | 0.309 | 1.06 | 1.31 | -0.0136
CFLBldgPGEECCNewCZ04 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ECC | New | CZ04 | 1.46 | 0.000476 | 0 | 1.6 | 0.000605 | -0.0146 | 1.46 | 0.000476 | 0 | 1.6 | 0.000605 | -0.0146 | CFL | Bldg | 1460 | 0.476 | 1460 | 0.476 | 1.1 | 1.27 | -0.01
CFLBldgSCEECCNewCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ECC | New | CZ05 | 1.46 | 0.000476 | 0 | 1.55 | 0.000602 | -0.02 | 1.46 | 0.000476 | 0 | 1.55 | 0.000602 | -0.02 | CFL | Bldg | 1460 | 0.476 | 1460 | 0.476 | 1.06 | 1.26 | -0.0137
CFLBldgPGEECCNewCZ05 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ECC | New | CZ05 | 1.46 | 0.000476 | 0 | 1.55 | 0.000584 | -0.0193 | 1.46 | 0.000476 | 0 | 1.55 | 0.000584 | -0.0193 | CFL | Bldg | 1460 | 0.476 | 1460 | 0.476 | 1.06 | 1.23 | -0.0132
CFLBldgSCEECCNewCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ECC | New | CZ06 | 1.46 | 0.000476 | 0 | 1.64 | 0.000616 | -0.0104 | 1.46 | 0.000476 | 0 | 1.64 | 0.000616 | -0.0104 | CFL | Bldg | 1460 | 0.476 | 1460 | 0.476 | 1.12 | 1.29 | -0.00712
CFLBldgSDGECCNewCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SDG | ECC | New | CZ06 | 1.46 | 0.000476 | 0 | 1.64 | 0.000611 | -0.0103 | 1.46 | 0.000476 | 0 | 1.64 | 0.000611 | -0.0103 | CFL | Bldg | 1460 | 0.476 | 1460 | 0.476 | 1.12 | 1.28 | -0.00705
CFLBldgSDGECCNewCZ07 | Com-Iltg-dWatt-CFL_OSbldg | SDG | ECC | New | CZ07 | 1.46 | 0.000476 | 0 | 1.64 | 0.000615 | -0.00775 | 1.46 | 0.000476 | 0 | 1.64 | 0.000615 | -0.00775 | CFL | Bldg | 1460 | 0.476 | 1460 | 0.476 | 1.12 | 1.29 | -0.00531
CFLBldgSDGECCNewCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SDG | ECC | New | CZ08 | 1.46 | 0.000476 | 0 | 1.65 | 0.00061 | -0.00756 | 1.46 | 0.000476 | 0 | 1.65 | 0.00061 | -0.00756 | CFL | Bldg | 1460 | 0.476 | 1460 | 0.476 | 1.13 | 1.28 | -0.00518
CFLBldgSCEECCNewCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ECC | New | CZ08 | 1.46 | 0.000476 | 0 | 1.65 | 0.000616 | -0.00736 | 1.46 | 0.000476 | 0 | 1.65 | 0.000616 | -0.00736 | CFL | Bldg | 1460 | 0.476 | 1460 | 0.476 | 1.13 | 1.29 | -0.00504
CFLBldgSCEECCNewCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ECC | New | CZ09 | 1.46 | 0.000476 | 0 | 1.65 | 0.000633 | -0.00856 | 1.46 | 0.000476 | 0 | 1.65 | 0.000633 | -0.00856 | CFL | Bldg | 1460 | 0.476 | 1460 | 0.476 | 1.13 | 1.33 | -0.00586
CFLBldgSCEECCNewCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ECC | New | CZ10 | 1.46 | 0.000476 | 0 | 1.67 | 0.000639 | -0.0085 | 1.46 | 0.000476 | 0 | 1.67 | 0.000639 | -0.0085 | CFL | Bldg | 1460 | 0.476 | 1460 | 0.476 | 1.14 | 1.34 | -0.00582
CFLBldgSDGECCNewCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SDG | ECC | New | CZ10 | 1.46 | 0.000476 | 0 | 1.67 | 0.000629 | -0.0086 | 1.46 | 0.000476 | 0 | 1.67 | 0.000629 | -0.0086 | CFL | Bldg | 1460 | 0.476 | 1460 | 0.476 | 1.14 | 1.32 | -0.00589
CFLBldgPGEECCNewCZ11 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ECC | New | CZ11 | 1.46 | 0.000309 | 0 | 1.62 | 0.000413 | -0.0152 | 1.46 | 0.000309 | 0 | 1.62 | 0.000413 | -0.0152 | CFL | Bldg | 1460 | 0.309 | 1460 | 0.309 | 1.11 | 1.34 | -0.0104
CFLBldgPGEECCNewCZ12 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ECC | New | CZ12 | 1.46 | 0.000309 | 0 | 1.61 | 0.000422 | -0.0155 | 1.46 | 0.000309 | 0 | 1.61 | 0.000422 | -0.0155 | CFL | Bldg | 1460 | 0.309 | 1460 | 0.309 | 1.1 | 1.37 | -0.0106
CFLBldgSCEECCNewCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ECC | New | CZ13 | 1.46 | 0.000309 | 0 | 1.65 | 0.000434 | -0.0133 | 1.46 | 0.000309 | 0 | 1.65 | 0.000434 | -0.0133 | CFL | Bldg | 1460 | 0.309 | 1460 | 0.309 | 1.13 | 1.4 | -0.00911
CFLBldgPGEECCNewCZ13 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ECC | New | CZ13 | 1.46 | 0.000309 | 0 | 1.64 | 0.000417 | -0.0132 | 1.46 | 0.000309 | 0 | 1.64 | 0.000417 | -0.0132 | CFL | Bldg | 1460 | 0.309 | 1460 | 0.309 | 1.12 | 1.35 | -0.00904
CFLBldgSDGECCNewCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SDG | ECC | New | CZ14 | 1.46 | 0.000476 | 0 | 1.65 | 0.000609 | -0.0135 | 1.46 | 0.000476 | 0 | 1.65 | 0.000609 | -0.0135 | CFL | Bldg | 1460 | 0.476 | 1460 | 0.476 | 1.13 | 1.28 | -0.00925
CFLBldgSCEECCNewCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ECC | New | CZ14 | 1.46 | 0.000476 | 0 | 1.65 | 0.00062 | -0.0138 | 1.46 | 0.000476 | 0 | 1.65 | 0.00062 | -0.0138 | CFL | Bldg | 1460 | 0.476 | 1460 | 0.476 | 1.13 | 1.3 | -0.00945
CFLBldgSDGECCNewCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SDG | ECC | New | CZ15 | 1.46 | 0.000476 | 0 | 1.76 | 0.000624 | -0.00337 | 1.46 | 0.000476 | 0 | 1.76 | 0.000624 | -0.00337 | CFL | Bldg | 1460 | 0.476 | 1460 | 0.476 | 1.21 | 1.31 | -0.00231
CFLBldgSCEECCNewCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ECC | New | CZ15 | 1.46 | 0.000476 | 0 | 1.77 | 0.000637 | -0.00326 | 1.46 | 0.000476 | 0 | 1.77 | 0.000637 | -0.00326 | CFL | Bldg | 1460 | 0.476 | 1460 | 0.476 | 1.21 | 1.34 | -0.00223
CFLBldgSCEECCNewCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ECC | New | CZ16 | 1.46 | 0.000309 | 0 | 1.53 | 0.000416 | -0.0248 | 1.46 | 0.000309 | 0 | 1.53 | 0.000416 | -0.0248 | CFL | Bldg | 1460 | 0.309 | 1460 | 0.309 | 1.05 | 1.35 | -0.017
CFLBldgPGEECCNewCZ16 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ECC | New | CZ16 | 1.46 | 0.000309 | 0 | 1.53 | 0.0004 | -0.0242 | 1.46 | 0.000309 | 0 | 1.53 | 0.0004 | -0.0242 | CFL | Bldg | 1460 | 0.309 | 1460 | 0.309 | 1.05 | 1.29 | -0.0166
CFLBldgSCEECCNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | ECC | New | IOU | 1.46 | 0.000476 | 0 | 1.66 | 0.000616 | -0.00864 | 1.46 | 0.000476 | 0 | 1.66 | 0.000616 | -0.00864 | CFL | Bldg | 1460 | 0.476 | 1460 | 0.476 | 1.14 | 1.29 | -0.00592
CFLBldgSCGECCNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SCG | ECC | New | IOU | 1.46 | 0.000476 | 0 | 1.66 | 0.000615 | -0.00863 | 1.46 | 0.000476 | 0 | 1.66 | 0.000615 | -0.00863 | CFL | Bldg | 1460 | 0.476 | 1460 | 0.476 | 1.14 | 1.29 | -0.00591
CFLBldgPGEECCNewIOU | Com-Iltg-dWatt-CFL_OSbldg | PGE | ECC | New | IOU | 1.46 | 0.000359 | 0 | 1.62 | 0.000484 | -0.0154 | 1.46 | 0.000359 | 0 | 1.62 | 0.000484 | -0.0154 | CFL | Bldg | 1460 | 0.359 | 1460 | 0.359 | 1.11 | 1.35 | -0.0105
CFLBldgSDGECCNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SDG | ECC | New | IOU | 1.46 | 0.000476 | 0 | 1.65 | 0.000618 | -0.00799 | 1.46 | 0.000476 | 0 | 1.65 | 0.000618 | -0.00799 | CFL | Bldg | 1460 | 0.476 | 1460 | 0.476 | 1.13 | 1.3 | -0.00547
CFLBldgPGEEPrExCZ01 | Com-Iltg-dWatt-CFL_OSbldg | PGE | EPr | Ex | CZ01 | 1.29 | 0.000462 | 0 | 1.28 | 0.000549 | -0.0233 | 1.15 | 0.000377 | 0 | 1.14 | 0.000449 | -0.0207 | CFL | Bldg | 1290 | 0.462 | 1150 | 0.377 | 0.991 | 1.19 | -0.018
CFLBldgPGEEPrExCZ02 | Com-Iltg-dWatt-CFL_OSbldg | PGE | EPr | Ex | CZ02 | 1.3 | 1.47e-05 | 0 | 1.37 | 1.47e-05 | -0.014 | 1.15 | 1.2e-05 | 0 | 1.21 | 1.2e-05 | -0.0124 | CFL | Bldg | 1300 | 0.0147 | 1150 | 0.012 | 1.05 | 1 | -0.0108
CFLBldgPGEEPrExCZ03 | Com-Iltg-dWatt-CFL_OSbldg | PGE | EPr | Ex | CZ03 | 1.3 | 1.47e-05 | 0 | 1.38 | 1.47e-05 | -0.0136 | 1.15 | 1.2e-05 | 0 | 1.22 | 1.2e-05 | -0.0121 | CFL | Bldg | 1300 | 0.0147 | 1150 | 0.012 | 1.06 | 1 | -0.0105
CFLBldgPGEEPrExCZ04 | Com-Iltg-dWatt-CFL_OSbldg | PGE | EPr | Ex | CZ04 | 1.3 | 0.000462 | 0 | 1.39 | 0.000567 | -0.0108 | 1.15 | 0.000377 | 0 | 1.24 | 0.000462 | -0.00957 | CFL | Bldg | 1300 | 0.462 | 1150 | 0.377 | 1.08 | 1.23 | -0.00832
CFLBldgPGEEPrExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | PGE | EPr | Ex | CZ05 | 1.3 | 0.000462 | 0 | 1.4 | 0.000585 | -0.0118 | 1.15 | 0.000377 | 0 | 1.25 | 0.000477 | -0.0104 | CFL | Bldg | 1300 | 0.462 | 1150 | 0.377 | 1.09 | 1.27 | -0.00904
CFLBldgSCEEPrExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | EPr | Ex | CZ05 | 1.3 | 0.000463 | 0 | 1.41 | 0.000586 | -0.0118 | 1.15 | 0.000377 | 0 | 1.25 | 0.000477 | -0.0104 | CFL | Bldg | 1300 | 0.463 | 1150 | 0.377 | 1.09 | 1.27 | -0.00904
CFLBldgSCGEPrExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCG | EPr | Ex | CZ05 | 1.3 | 0.000463 | 0 | 1.41 | 0.000586 | -0.0118 | 1.15 | 0.000377 | 0 | 1.25 | 0.000477 | -0.0104 | CFL | Bldg | 1300 | 0.463 | 1150 | 0.377 | 1.09 | 1.27 | -0.00904
CFLBldgSCGEPrExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCG | EPr | Ex | CZ06 | 1.3 | 0.000463 | 0 | 1.47 | 0.00059 | -0.00604 | 1.15 | 0.000377 | 0 | 1.3 | 0.000481 | -0.00536 | CFL | Bldg | 1300 | 0.463 | 1150 | 0.377 | 1.13 | 1.28 | -0.00466
CFLBldgSDGEPrExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SDG | EPr | Ex | CZ06 | 1.29 | 0.000462 | 0 | 1.46 | 0.000589 | -0.00604 | 1.15 | 0.000377 | 0 | 1.3 | 0.000481 | -0.00536 | CFL | Bldg | 1290 | 0.462 | 1150 | 0.377 | 1.13 | 1.28 | -0.00466
CFLBldgSCEEPrExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | EPr | Ex | CZ06 | 1.3 | 0.000463 | 0 | 1.47 | 0.00059 | -0.00604 | 1.15 | 0.000377 | 0 | 1.3 | 0.000481 | -0.00536 | CFL | Bldg | 1300 | 0.463 | 1150 | 0.377 | 1.13 | 1.28 | -0.00466
CFLBldgSDGEPrExCZ07 | Com-Iltg-dWatt-CFL_OSbldg | SDG | EPr | Ex | CZ07 | 1.29 | 0.000462 | 0 | 1.46 | 0.000594 | -0.00556 | 1.15 | 0.000377 | 0 | 1.3 | 0.000485 | -0.00493 | CFL | Bldg | 1290 | 0.462 | 1150 | 0.377 | 1.13 | 1.29 | -0.00429
CFLBldgSDGEPrExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SDG | EPr | Ex | CZ08 | 1.29 | 0.000462 | 0 | 1.47 | 0.000595 | -0.00508 | 1.15 | 0.000377 | 0 | 1.31 | 0.000486 | -0.00451 | CFL | Bldg | 1290 | 0.462 | 1150 | 0.377 | 1.14 | 1.29 | -0.00392
CFLBldgSCEEPrExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | EPr | Ex | CZ08 | 1.3 | 0.000463 | 0 | 1.48 | 0.000596 | -0.00508 | 1.15 | 0.000377 | 0 | 1.31 | 0.000486 | -0.00451 | CFL | Bldg | 1300 | 0.463 | 1150 | 0.377 | 1.14 | 1.29 | -0.00392
CFLBldgSCGEPrExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCG | EPr | Ex | CZ08 | 1.3 | 0.000463 | 0 | 1.48 | 0.000596 | -0.00509 | 1.15 | 0.000377 | 0 | 1.31 | 0.000486 | -0.00451 | CFL | Bldg | 1300 | 0.463 | 1150 | 0.377 | 1.14 | 1.29 | -0.00392
CFLBldgSCGEPrExCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCG | EPr | Ex | CZ09 | 1.3 | 0.000463 | 0 | 1.5 | 0.000603 | -0.006 | 1.15 | 0.000377 | 0 | 1.33 | 0.000491 | -0.00532 | CFL | Bldg | 1300 | 0.463 | 1150 | 0.377 | 1.16 | 1.3 | -0.00463
CFLBldgSCEEPrExCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | EPr | Ex | CZ09 | 1.3 | 0.000463 | 0 | 1.5 | 0.000603 | -0.006 | 1.15 | 0.000377 | 0 | 1.33 | 0.000491 | -0.00532 | CFL | Bldg | 1300 | 0.463 | 1150 | 0.377 | 1.16 | 1.3 | -0.00463
CFLBldgSCGEPrExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCG | EPr | Ex | CZ10 | 1.29 | 0.00046 | 0 | 1.46 | 0.000586 | -0.00637 | 1.15 | 0.000377 | 0 | 1.3 | 0.000481 | -0.00567 | CFL | Bldg | 1290 | 0.46 | 1150 | 0.377 | 1.13 | 1.28 | -0.00493
CFLBldgSCEEPrExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | EPr | Ex | CZ10 | 1.29 | 0.00046 | 0 | 1.46 | 0.000586 | -0.00637 | 1.15 | 0.000377 | 0 | 1.3 | 0.000481 | -0.00567 | CFL | Bldg | 1290 | 0.46 | 1150 | 0.377 | 1.13 | 1.28 | -0.00493
CFLBldgSDGEPrExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SDG | EPr | Ex | CZ10 | 1.29 | 0.000462 | 0 | 1.46 | 0.000589 | -0.00638 | 1.15 | 0.000377 | 0 | 1.3 | 0.000481 | -0.00567 | CFL | Bldg | 1290 | 0.462 | 1150 | 0.377 | 1.13 | 1.28 | -0.00493
CFLBldgPGEEPrExCZ11 | Com-Iltg-dWatt-CFL_OSbldg | PGE | EPr | Ex | CZ11 | 1.29 | 1.46e-05 | 0 | 1.37 | 1.46e-05 | -0.0128 | 1.15 | 1.2e-05 | 0 | 1.22 | 1.2e-05 | -0.0114 | CFL | Bldg | 1290 | 0.0146 | 1150 | 0.012 | 1.06 | 1 | -0.00991
CFLBldgPGEEPrExCZ12 | Com-Iltg-dWatt-CFL_OSbldg | PGE | EPr | Ex | CZ12 | 1.29 | 1.47e-05 | 0 | 1.37 | 1.47e-05 | -0.0133 | 1.15 | 1.2e-05 | 0 | 1.22 | 1.2e-05 | -0.0118 | CFL | Bldg | 1290 | 0.0147 | 1150 | 0.012 | 1.06 | 1 | -0.0103
CFLBldgPGEEPrExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | PGE | EPr | Ex | CZ13 | 1.29 | 1.47e-05 | 0 | 1.41 | 1.47e-05 | -0.0107 | 1.15 | 1.2e-05 | 0 | 1.26 | 1.2e-05 | -0.00957 | CFL | Bldg | 1290 | 0.0147 | 1150 | 0.012 | 1.1 | 1 | -0.00832
CFLBldgSCGEPrExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCG | EPr | Ex | CZ13 | 1.29 | 1.46e-05 | 0 | 1.41 | 1.46e-05 | -0.0107 | 1.15 | 1.2e-05 | 0 | 1.26 | 1.2e-05 | -0.00957 | CFL | Bldg | 1290 | 0.0146 | 1150 | 0.012 | 1.1 | 1 | -0.00832
CFLBldgSCEEPrExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | EPr | Ex | CZ13 | 1.29 | 1.46e-05 | 0 | 1.41 | 1.46e-05 | -0.0107 | 1.15 | 1.2e-05 | 0 | 1.26 | 1.2e-05 | -0.00957 | CFL | Bldg | 1290 | 0.0146 | 1150 | 0.012 | 1.1 | 1 | -0.00832
CFLBldgSCGEPrExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCG | EPr | Ex | CZ14 | 1.29 | 0.00046 | 0 | 1.4 | 0.000588 | -0.0106 | 1.15 | 0.000377 | 0 | 1.25 | 0.000481 | -0.00944 | CFL | Bldg | 1290 | 0.46 | 1150 | 0.377 | 1.09 | 1.28 | -0.00821
CFLBldgSDGEPrExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SDG | EPr | Ex | CZ14 | 1.29 | 0.000462 | 0 | 1.4 | 0.00059 | -0.0107 | 1.15 | 0.000377 | 0 | 1.25 | 0.000481 | -0.00944 | CFL | Bldg | 1290 | 0.462 | 1150 | 0.377 | 1.09 | 1.28 | -0.00821
CFLBldgSCEEPrExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | EPr | Ex | CZ14 | 1.29 | 0.00046 | 0 | 1.4 | 0.000588 | -0.0106 | 1.15 | 0.000377 | 0 | 1.25 | 0.000481 | -0.00944 | CFL | Bldg | 1290 | 0.46 | 1150 | 0.377 | 1.09 | 1.28 | -0.00821
CFLBldgSCEEPrExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | EPr | Ex | CZ15 | 1.29 | 0.00046 | 0 | 1.57 | 0.00059 | -0.0027 | 1.15 | 0.000377 | 0 | 1.4 | 0.000484 | -0.0024 | CFL | Bldg | 1290 | 0.46 | 1150 | 0.377 | 1.22 | 1.28 | -0.00209
CFLBldgSDGEPrExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SDG | EPr | Ex | CZ15 | 1.29 | 0.000462 | 0 | 1.57 | 0.000593 | -0.00271 | 1.15 | 0.000377 | 0 | 1.4 | 0.000484 | -0.0024 | CFL | Bldg | 1290 | 0.462 | 1150 | 0.377 | 1.22 | 1.28 | -0.00209
CFLBldgSCGEPrExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCG | EPr | Ex | CZ15 | 1.29 | 0.00046 | 0 | 1.57 | 0.00059 | -0.0027 | 1.15 | 0.000377 | 0 | 1.4 | 0.000484 | -0.0024 | CFL | Bldg | 1290 | 0.46 | 1150 | 0.377 | 1.22 | 1.28 | -0.00209
CFLBldgSCEEPrExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | EPr | Ex | CZ16 | 1.29 | 1.46e-05 | 0 | 1.25 | 1.46e-05 | -0.0212 | 1.15 | 1.2e-05 | 0 | 1.11 | 1.2e-05 | -0.0189 | CFL | Bldg | 1290 | 0.0146 | 1150 | 0.012 | 0.965 | 1 | -0.0164
CFLBldgPGEEPrExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | PGE | EPr | Ex | CZ16 | 1.29 | 1.46e-05 | 0 | 1.25 | 1.46e-05 | -0.0212 | 1.15 | 1.2e-05 | 0 | 1.11 | 1.2e-05 | -0.0189 | CFL | Bldg | 1290 | 0.0146 | 1150 | 0.012 | 0.965 | 1 | -0.0164
CFLBldgSCGEPrExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCG | EPr | Ex | CZ16 | 1.29 | 1.46e-05 | 0 | 1.25 | 1.46e-05 | -0.0212 | 1.15 | 1.2e-05 | 0 | 1.11 | 1.2e-05 | -0.0189 | CFL | Bldg | 1290 | 0.0146 | 1150 | 0.012 | 0.965 | 1 | -0.0164
CFLBldgPGEEPrExIOU | Com-Iltg-dWatt-CFL_OSbldg | PGE | EPr | Ex | IOU | 1.29 | 9.34e-05 | 0 | 1.38 | 0.000112 | -0.0127 | 1.15 | 7.62e-05 | 0 | 1.23 | 9.14e-05 | -0.0113 | CFL | Bldg | 1290 | 0.0934 | 1150 | 0.0762 | 1.07 | 1.2 | -0.00983
CFLBldgSDGEPrExIOU | Com-Iltg-dWatt-CFL_OSbldg | SDG | EPr | Ex | IOU | 1.29 | 0.000462 | 0 | 1.46 | 0.000592 | -0.00586 | 1.15 | 0.000377 | 0 | 1.3 | 0.000484 | -0.0052 | CFL | Bldg | 1290 | 0.462 | 1150 | 0.377 | 1.13 | 1.28 | -0.00452
CFLBldgSCGEPrExIOU | Com-Iltg-dWatt-CFL_OSbldg | SCG | EPr | Ex | IOU | 1.29 | 0.000438 | 0 | 1.47 | 0.000564 | -0.00642 | 1.15 | 0.000358 | 0 | 1.31 | 0.00046 | -0.0057 | CFL | Bldg | 1290 | 0.438 | 1150 | 0.358 | 1.14 | 1.28 | -0.00496
CFLBldgSCEEPrExIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | EPr | Ex | IOU | 1.29 | 0.000432 | 0 | 1.46 | 0.000555 | -0.00656 | 1.15 | 0.000353 | 0 | 1.3 | 0.000453 | -0.00583 | CFL | Bldg | 1290 | 0.432 | 1150 | 0.353 | 1.13 | 1.28 | -0.00507
CFLBldgPGEEPrNewCZ01 | Com-Iltg-dWatt-CFL_OSbldg | PGE | EPr | New | CZ01 | 1.15 | 0.00038 | 0 | 1.13 | 0.000437 | -0.0245 | 1.15 | 0.00038 | 0 | 1.13 | 0.000437 | -0.0245 | CFL | Bldg | 1150 | 0.38 | 1150 | 0.38 | 0.983 | 1.15 | -0.0213
CFLBldgPGEEPrNewCZ02 | Com-Iltg-dWatt-CFL_OSbldg | PGE | EPr | New | CZ02 | 1.15 | 1.21e-05 | 0 | 1.2 | 1.21e-05 | -0.0158 | 1.15 | 1.21e-05 | 0 | 1.2 | 1.21e-05 | -0.0158 | CFL | Bldg | 1150 | 0.0121 | 1150 | 0.0121 | 1.04 | 1 | -0.0137
CFLBldgPGEEPrNewCZ03 | Com-Iltg-dWatt-CFL_OSbldg | PGE | EPr | New | CZ03 | 1.15 | 1.21e-05 | 0 | 1.18 | 1.21e-05 | -0.0149 | 1.15 | 1.21e-05 | 0 | 1.18 | 1.21e-05 | -0.0149 | CFL | Bldg | 1150 | 0.0121 | 1150 | 0.0121 | 1.03 | 1 | -0.013
CFLBldgPGEEPrNewCZ04 | Com-Iltg-dWatt-CFL_OSbldg | PGE | EPr | New | CZ04 | 1.15 | 0.00038 | 0 | 1.22 | 0.000494 | -0.0122 | 1.15 | 0.00038 | 0 | 1.22 | 0.000494 | -0.0122 | CFL | Bldg | 1150 | 0.38 | 1150 | 0.38 | 1.06 | 1.3 | -0.0106
CFLBldgSCEEPrNewCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | EPr | New | CZ05 | 1.15 | 0.00038 | 0 | 1.2 | 0.00049 | -0.0114 | 1.15 | 0.00038 | 0 | 1.2 | 0.00049 | -0.0114 | CFL | Bldg | 1150 | 0.38 | 1150 | 0.38 | 1.04 | 1.29 | -0.00991
CFLBldgPGEEPrNewCZ05 | Com-Iltg-dWatt-CFL_OSbldg | PGE | EPr | New | CZ05 | 1.15 | 0.00038 | 0 | 1.19 | 0.000469 | -0.0124 | 1.15 | 0.00038 | 0 | 1.19 | 0.000469 | -0.0124 | CFL | Bldg | 1150 | 0.38 | 1150 | 0.38 | 1.03 | 1.23 | -0.0108
CFLBldgSDGEPrNewCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SDG | EPr | New | CZ06 | 1.15 | 0.00038 | 0 | 1.26 | 0.000508 | -0.0073 | 1.15 | 0.00038 | 0 | 1.26 | 0.000508 | -0.0073 | CFL | Bldg | 1150 | 0.38 | 1150 | 0.38 | 1.1 | 1.34 | -0.00635
CFLBldgSCEEPrNewCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | EPr | New | CZ06 | 1.15 | 0.00038 | 0 | 1.27 | 0.000511 | -0.00722 | 1.15 | 0.00038 | 0 | 1.27 | 0.000511 | -0.00722 | CFL | Bldg | 1150 | 0.38 | 1150 | 0.38 | 1.1 | 1.34 | -0.00628
CFLBldgSDGEPrNewCZ07 | Com-Iltg-dWatt-CFL_OSbldg | SDG | EPr | New | CZ07 | 1.15 | 0.00038 | 0 | 1.25 | 0.000503 | -0.0068 | 1.15 | 0.00038 | 0 | 1.25 | 0.000503 | -0.0068 | CFL | Bldg | 1150 | 0.38 | 1150 | 0.38 | 1.09 | 1.32 | -0.00591
CFLBldgSDGEPrNewCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SDG | EPr | New | CZ08 | 1.15 | 0.00038 | 0 | 1.28 | 0.000522 | -0.00627 | 1.15 | 0.00038 | 0 | 1.28 | 0.000522 | -0.00627 | CFL | Bldg | 1150 | 0.38 | 1150 | 0.38 | 1.11 | 1.37 | -0.00545
CFLBldgSCEEPrNewCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | EPr | New | CZ08 | 1.15 | 0.00038 | 0 | 1.29 | 0.000526 | -0.0062 | 1.15 | 0.00038 | 0 | 1.29 | 0.000526 | -0.0062 | CFL | Bldg | 1150 | 0.38 | 1150 | 0.38 | 1.12 | 1.38 | -0.00539
CFLBldgSCEEPrNewCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | EPr | New | CZ09 | 1.15 | 0.00038 | 0 | 1.28 | 0.000537 | -0.00704 | 1.15 | 0.00038 | 0 | 1.28 | 0.000537 | -0.00704 | CFL | Bldg | 1150 | 0.38 | 1150 | 0.38 | 1.11 | 1.41 | -0.00612
CFLBldgSDGEPrNewCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SDG | EPr | New | CZ10 | 1.15 | 0.00038 | 0 | 1.28 | 0.000541 | -0.00756 | 1.15 | 0.00038 | 0 | 1.28 | 0.000541 | -0.00756 | CFL | Bldg | 1150 | 0.38 | 1150 | 0.38 | 1.11 | 1.42 | -0.00657
CFLBldgSCEEPrNewCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | EPr | New | CZ10 | 1.15 | 0.00038 | 0 | 1.29 | 0.000545 | -0.00746 | 1.15 | 0.00038 | 0 | 1.29 | 0.000545 | -0.00746 | CFL | Bldg | 1150 | 0.38 | 1150 | 0.38 | 1.12 | 1.43 | -0.00649
CFLBldgPGEEPrNewCZ11 | Com-Iltg-dWatt-CFL_OSbldg | PGE | EPr | New | CZ11 | 1.15 | 1.21e-05 | 0 | 1.23 | 1.21e-05 | -0.0138 | 1.15 | 1.21e-05 | 0 | 1.23 | 1.21e-05 | -0.0138 | CFL | Bldg | 1150 | 0.0121 | 1150 | 0.0121 | 1.07 | 1 | -0.012
CFLBldgPGEEPrNewCZ12 | Com-Iltg-dWatt-CFL_OSbldg | PGE | EPr | New | CZ12 | 1.15 | 1.21e-05 | 0 | 1.22 | 1.21e-05 | -0.0141 | 1.15 | 1.21e-05 | 0 | 1.22 | 1.21e-05 | -0.0141 | CFL | Bldg | 1150 | 0.0121 | 1150 | 0.0121 | 1.06 | 1 | -0.0123
CFLBldgSCEEPrNewCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | EPr | New | CZ13 | 1.15 | 1.21e-05 | 0 | 1.26 | 1.21e-05 | -0.0117 | 1.15 | 1.21e-05 | 0 | 1.26 | 1.21e-05 | -0.0117 | CFL | Bldg | 1150 | 0.0121 | 1150 | 0.0121 | 1.1 | 1 | -0.0102
CFLBldgPGEEPrNewCZ13 | Com-Iltg-dWatt-CFL_OSbldg | PGE | EPr | New | CZ13 | 1.15 | 1.21e-05 | 0 | 1.24 | 1.21e-05 | -0.0126 | 1.15 | 1.21e-05 | 0 | 1.24 | 1.21e-05 | -0.0126 | CFL | Bldg | 1150 | 0.0121 | 1150 | 0.0121 | 1.08 | 1 | -0.011
CFLBldgSCEEPrNewCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | EPr | New | CZ14 | 1.15 | 0.00038 | 0 | 1.26 | 0.000534 | -0.0117 | 1.15 | 0.00038 | 0 | 1.26 | 0.000534 | -0.0117 | CFL | Bldg | 1150 | 0.38 | 1150 | 0.38 | 1.1 | 1.41 | -0.0102
CFLBldgSDGEPrNewCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SDG | EPr | New | CZ14 | 1.15 | 0.00038 | 0 | 1.26 | 0.000529 | -0.0118 | 1.15 | 0.00038 | 0 | 1.26 | 0.000529 | -0.0118 | CFL | Bldg | 1150 | 0.38 | 1150 | 0.38 | 1.1 | 1.39 | -0.0103
CFLBldgSCEEPrNewCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | EPr | New | CZ15 | 1.15 | 0.00038 | 0 | 1.4 | 0.000552 | -0.00327 | 1.15 | 0.00038 | 0 | 1.4 | 0.000552 | -0.00327 | CFL | Bldg | 1150 | 0.38 | 1150 | 0.38 | 1.22 | 1.45 | -0.00284
CFLBldgSDGEPrNewCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SDG | EPr | New | CZ15 | 1.15 | 0.00038 | 0 | 1.39 | 0.000548 | -0.0033 | 1.15 | 0.00038 | 0 | 1.39 | 0.000548 | -0.0033 | CFL | Bldg | 1150 | 0.38 | 1150 | 0.38 | 1.21 | 1.44 | -0.00287
CFLBldgSCEEPrNewCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | EPr | New | CZ16 | 1.15 | 1.21e-05 | 0 | 1.13 | 1.21e-05 | -0.0168 | 1.15 | 1.21e-05 | 0 | 1.13 | 1.21e-05 | -0.0168 | CFL | Bldg | 1150 | 0.0121 | 1150 | 0.0121 | 0.983 | 1 | -0.0146
CFLBldgPGEEPrNewCZ16 | Com-Iltg-dWatt-CFL_OSbldg | PGE | EPr | New | CZ16 | 1.15 | 1.21e-05 | 0 | 1.15 | 1.21e-05 | -0.0181 | 1.15 | 1.21e-05 | 0 | 1.15 | 1.21e-05 | -0.0181 | CFL | Bldg | 1150 | 0.0121 | 1150 | 0.0121 | 1 | 1 | -0.0157
CFLBldgPGEEPrNewIOU | Com-Iltg-dWatt-CFL_OSbldg | PGE | EPr | New | IOU | 1.15 | 3.48e-05 | 0 | 1.25 | 4.16e-05 | -0.0119 | 1.15 | 3.48e-05 | 0 | 1.25 | 4.16e-05 | -0.0119 | CFL | Bldg | 1150 | 0.0348 | 1150 | 0.0348 | 1.09 | 1.2 | -0.0103
CFLBldgSCEEPrNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | EPr | New | IOU | 1.15 | 0.00038 | 0 | 1.28 | 0.00053 | -0.00741 | 1.15 | 0.00038 | 0 | 1.28 | 0.00053 | -0.00741 | CFL | Bldg | 1150 | 0.38 | 1150 | 0.38 | 1.11 | 1.39 | -0.00644
CFLBldgSCGEPrNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SCG | EPr | New | IOU | 1.15 | 0.00038 | 0 | 1.28 | 0.000529 | -0.00738 | 1.15 | 0.00038 | 0 | 1.28 | 0.000529 | -0.00738 | CFL | Bldg | 1150 | 0.38 | 1150 | 0.38 | 1.11 | 1.39 | -0.00642
CFLBldgSDGEPrNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SDG | EPr | New | IOU | 1.15 | 0.00038 | 0 | 1.26 | 0.000517 | -0.00708 | 1.15 | 0.00038 | 0 | 1.26 | 0.000517 | -0.00708 | CFL | Bldg | 1150 | 0.38 | 1150 | 0.38 | 1.1 | 1.36 | -0.00616
CFLBldgPGEERCExCZ01 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ERC | Ex | CZ01 | 1.16 | 0.000492 | 0 | 1.13 | 0.000584 | -0.0194 | 0.998 | 0.000371 | 0 | 0.969 | 0.00044 | -0.0167 | CFL | Bldg | 1160 | 0.492 | 998 | 0.371 | 0.971 | 1.19 | -0.0167
CFLBldgPGEERCExCZ02 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ERC | Ex | CZ02 | 1.16 | 1.42e-05 | 0 | 1.17 | 1.42e-05 | -0.0139 | 0.998 | 1.07e-05 | 0 | 1.01 | 1.07e-05 | -0.012 | CFL | Bldg | 1160 | 0.0142 | 998 | 0.0107 | 1.01 | 1 | -0.012
CFLBldgPGEERCExCZ03 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ERC | Ex | CZ03 | 1.17 | 1.42e-05 | 0 | 1.18 | 1.42e-05 | -0.0131 | 0.998 | 1.07e-05 | 0 | 1.01 | 1.07e-05 | -0.0112 | CFL | Bldg | 1170 | 0.0142 | 998 | 0.0107 | 1.01 | 1 | -0.0112
CFLBldgPGEERCExCZ04 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ERC | Ex | CZ04 | 1.16 | 0.000493 | 0 | 1.21 | 0.000592 | -0.0109 | 0.998 | 0.000371 | 0 | 1.04 | 0.000446 | -0.00935 | CFL | Bldg | 1160 | 0.493 | 998 | 0.371 | 1.04 | 1.2 | -0.00937
CFLBldgSCEERCExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ERC | Ex | CZ05 | 1.17 | 0.000494 | 0 | 1.22 | 0.000617 | -0.0119 | 0.998 | 0.000371 | 0 | 1.04 | 0.000464 | -0.0102 | CFL | Bldg | 1170 | 0.494 | 998 | 0.371 | 1.04 | 1.25 | -0.0102
CFLBldgSCGERCExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCG | ERC | Ex | CZ05 | 1.17 | 0.000494 | 0 | 1.22 | 0.000617 | -0.0119 | 0.998 | 0.000371 | 0 | 1.04 | 0.000464 | -0.0102 | CFL | Bldg | 1170 | 0.494 | 998 | 0.371 | 1.04 | 1.25 | -0.0102
CFLBldgPGEERCExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ERC | Ex | CZ05 | 1.16 | 0.000493 | 0 | 1.21 | 0.000616 | -0.0118 | 0.998 | 0.000371 | 0 | 1.04 | 0.000464 | -0.0102 | CFL | Bldg | 1160 | 0.493 | 998 | 0.371 | 1.04 | 1.25 | -0.0102
CFLBldgSCEERCExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ERC | Ex | CZ06 | 1.17 | 0.000494 | 0 | 1.28 | 0.000614 | -0.00718 | 0.998 | 0.000371 | 0 | 1.09 | 0.000462 | -0.00615 | CFL | Bldg | 1170 | 0.494 | 998 | 0.371 | 1.09 | 1.25 | -0.00616
CFLBldgSDGERCExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SDG | ERC | Ex | CZ06 | 1.16 | 0.000493 | 0 | 1.27 | 0.000612 | -0.00717 | 0.998 | 0.000371 | 0 | 1.09 | 0.000462 | -0.00615 | CFL | Bldg | 1160 | 0.493 | 998 | 0.371 | 1.09 | 1.25 | -0.00616
CFLBldgSCGERCExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCG | ERC | Ex | CZ06 | 1.17 | 0.000494 | 0 | 1.28 | 0.000614 | -0.00718 | 0.998 | 0.000371 | 0 | 1.09 | 0.000462 | -0.00615 | CFL | Bldg | 1170 | 0.494 | 998 | 0.371 | 1.09 | 1.25 | -0.00616
CFLBldgSDGERCExCZ07 | Com-Iltg-dWatt-CFL_OSbldg | SDG | ERC | Ex | CZ07 | 1.16 | 0.000493 | 0 | 1.3 | 0.000611 | -0.00574 | 0.998 | 0.000371 | 0 | 1.12 | 0.000461 | -0.00492 | CFL | Bldg | 1160 | 0.493 | 998 | 0.371 | 1.12 | 1.24 | -0.00493
CFLBldgSCEERCExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ERC | Ex | CZ08 | 1.17 | 0.000494 | 0 | 1.3 | 0.000621 | -0.0063 | 0.998 | 0.000371 | 0 | 1.11 | 0.000467 | -0.00539 | CFL | Bldg | 1170 | 0.494 | 998 | 0.371 | 1.11 | 1.26 | -0.0054
CFLBldgSCGERCExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCG | ERC | Ex | CZ08 | 1.17 | 0.000494 | 0 | 1.3 | 0.000621 | -0.0063 | 0.998 | 0.000371 | 0 | 1.11 | 0.000467 | -0.00539 | CFL | Bldg | 1170 | 0.494 | 998 | 0.371 | 1.11 | 1.26 | -0.0054
CFLBldgSDGERCExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SDG | ERC | Ex | CZ08 | 1.16 | 0.000493 | 0 | 1.29 | 0.000619 | -0.00629 | 0.998 | 0.000371 | 0 | 1.11 | 0.000467 | -0.00539 | CFL | Bldg | 1160 | 0.493 | 998 | 0.371 | 1.11 | 1.26 | -0.0054
CFLBldgSCGERCExCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCG | ERC | Ex | CZ09 | 1.17 | 0.000494 | 0 | 1.3 | 0.000622 | -0.00711 | 0.998 | 0.000371 | 0 | 1.11 | 0.000467 | -0.00608 | CFL | Bldg | 1170 | 0.494 | 998 | 0.371 | 1.11 | 1.26 | -0.00609
CFLBldgSCEERCExCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ERC | Ex | CZ09 | 1.17 | 0.000494 | 0 | 1.29 | 0.000622 | -0.0071 | 0.998 | 0.000371 | 0 | 1.11 | 0.000467 | -0.00608 | CFL | Bldg | 1170 | 0.494 | 998 | 0.371 | 1.11 | 1.26 | -0.00609
CFLBldgSCEERCExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ERC | Ex | CZ10 | 1.16 | 0.000489 | 0 | 1.27 | 0.000612 | -0.0073 | 0.998 | 0.000371 | 0 | 1.09 | 0.000464 | -0.00629 | CFL | Bldg | 1160 | 0.489 | 998 | 0.371 | 1.09 | 1.25 | -0.0063
CFLBldgSCGERCExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCG | ERC | Ex | CZ10 | 1.16 | 0.000489 | 0 | 1.27 | 0.000612 | -0.0073 | 0.998 | 0.000371 | 0 | 1.09 | 0.000464 | -0.00629 | CFL | Bldg | 1160 | 0.489 | 998 | 0.371 | 1.09 | 1.25 | -0.0063
CFLBldgSDGERCExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SDG | ERC | Ex | CZ10 | 1.16 | 0.000493 | 0 | 1.27 | 0.000616 | -0.00733 | 0.998 | 0.000371 | 0 | 1.09 | 0.000464 | -0.00629 | CFL | Bldg | 1160 | 0.493 | 998 | 0.371 | 1.09 | 1.25 | -0.0063
CFLBldgPGEERCExCZ11 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ERC | Ex | CZ11 | 1.16 | 1.41e-05 | 0 | 1.2 | 1.41e-05 | -0.0117 | 0.998 | 1.07e-05 | 0 | 1.03 | 1.07e-05 | -0.0101 | CFL | Bldg | 1160 | 0.0141 | 998 | 0.0107 | 1.03 | 1 | -0.0101
CFLBldgPGEERCExCZ12 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ERC | Ex | CZ12 | 1.16 | 1.41e-05 | 0 | 1.2 | 1.41e-05 | -0.0124 | 0.998 | 1.07e-05 | 0 | 1.03 | 1.07e-05 | -0.0107 | CFL | Bldg | 1160 | 0.0141 | 998 | 0.0107 | 1.03 | 1 | -0.0107
CFLBldgSCGERCExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCG | ERC | Ex | CZ13 | 1.16 | 1.41e-05 | 0 | 1.25 | 1.41e-05 | -0.0102 | 0.998 | 1.07e-05 | 0 | 1.08 | 1.07e-05 | -0.00876 | CFL | Bldg | 1160 | 0.0141 | 998 | 0.0107 | 1.08 | 1 | -0.00878
CFLBldgSCEERCExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ERC | Ex | CZ13 | 1.16 | 1.41e-05 | 0 | 1.25 | 1.41e-05 | -0.0102 | 0.998 | 1.07e-05 | 0 | 1.08 | 1.07e-05 | -0.00876 | CFL | Bldg | 1160 | 0.0141 | 998 | 0.0107 | 1.08 | 1 | -0.00878
CFLBldgPGEERCExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ERC | Ex | CZ13 | 1.16 | 1.41e-05 | 0 | 1.25 | 1.41e-05 | -0.0102 | 0.998 | 1.07e-05 | 0 | 1.08 | 1.07e-05 | -0.00876 | CFL | Bldg | 1160 | 0.0141 | 998 | 0.0107 | 1.08 | 1 | -0.00878
CFLBldgSDGERCExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SDG | ERC | Ex | CZ14 | 1.16 | 0.000492 | 0 | 1.27 | 0.000625 | -0.00971 | 0.998 | 0.000371 | 0 | 1.09 | 0.000471 | -0.00832 | CFL | Bldg | 1160 | 0.492 | 998 | 0.371 | 1.09 | 1.27 | -0.00834
CFLBldgSCEERCExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ERC | Ex | CZ14 | 1.16 | 0.00049 | 0 | 1.27 | 0.000623 | -0.00968 | 0.998 | 0.000371 | 0 | 1.09 | 0.000471 | -0.00832 | CFL | Bldg | 1160 | 0.49 | 998 | 0.371 | 1.09 | 1.27 | -0.00834
CFLBldgSCGERCExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCG | ERC | Ex | CZ14 | 1.16 | 0.00049 | 0 | 1.27 | 0.000623 | -0.00968 | 0.998 | 0.000371 | 0 | 1.09 | 0.000471 | -0.00832 | CFL | Bldg | 1160 | 0.49 | 998 | 0.371 | 1.09 | 1.27 | -0.00834
CFLBldgSDGERCExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SDG | ERC | Ex | CZ15 | 1.16 | 0.000493 | 0 | 1.37 | 0.000634 | -0.00356 | 0.998 | 0.000371 | 0 | 1.18 | 0.000478 | -0.00305 | CFL | Bldg | 1160 | 0.493 | 998 | 0.371 | 1.18 | 1.29 | -0.00306
CFLBldgSCEERCExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ERC | Ex | CZ15 | 1.16 | 0.000489 | 0 | 1.37 | 0.00063 | -0.00355 | 0.998 | 0.000371 | 0 | 1.18 | 0.000478 | -0.00305 | CFL | Bldg | 1160 | 0.489 | 998 | 0.371 | 1.18 | 1.29 | -0.00306
CFLBldgSCGERCExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCG | ERC | Ex | CZ15 | 1.16 | 0.000489 | 0 | 1.37 | 0.00063 | -0.00355 | 0.998 | 0.000371 | 0 | 1.18 | 0.000478 | -0.00305 | CFL | Bldg | 1160 | 0.489 | 998 | 0.371 | 1.18 | 1.29 | -0.00306
CFLBldgSCEERCExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ERC | Ex | CZ16 | 1.16 | 1.41e-05 | 0 | 1.15 | 1.41e-05 | -0.0172 | 0.998 | 1.07e-05 | 0 | 0.993 | 1.07e-05 | -0.0148 | CFL | Bldg | 1160 | 0.0141 | 998 | 0.0107 | 0.995 | 1 | -0.0148
CFLBldgPGEERCExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ERC | Ex | CZ16 | 1.16 | 1.41e-05 | 0 | 1.15 | 1.41e-05 | -0.0172 | 0.998 | 1.07e-05 | 0 | 0.993 | 1.07e-05 | -0.0148 | CFL | Bldg | 1160 | 0.0141 | 998 | 0.0107 | 0.995 | 1 | -0.0148
CFLBldgSCGERCExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCG | ERC | Ex | CZ16 | 1.16 | 1.41e-05 | 0 | 1.15 | 1.41e-05 | -0.0172 | 0.998 | 1.07e-05 | 0 | 0.993 | 1.07e-05 | -0.0148 | CFL | Bldg | 1160 | 0.0141 | 998 | 0.0107 | 0.995 | 1 | -0.0148
CFLBldgSCEERCExIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | ERC | Ex | IOU | 1.16 | 0.000461 | 0 | 1.28 | 0.000578 | -0.00736 | 0.998 | 0.000347 | 0 | 1.1 | 0.000436 | -0.00631 | CFL | Bldg | 1160 | 0.461 | 998 | 0.347 | 1.1 | 1.26 | -0.00632
CFLBldgSDGERCExIOU | Com-Iltg-dWatt-CFL_OSbldg | SDG | ERC | Ex | IOU | 1.16 | 0.000493 | 0 | 1.29 | 0.000614 | -0.00639 | 0.998 | 0.000371 | 0 | 1.11 | 0.000462 | -0.00548 | CFL | Bldg | 1160 | 0.493 | 998 | 0.371 | 1.11 | 1.25 | -0.00549
CFLBldgSCGERCExIOU | Com-Iltg-dWatt-CFL_OSbldg | SCG | ERC | Ex | IOU | 1.16 | 0.000468 | 0 | 1.28 | 0.000587 | -0.00728 | 0.998 | 0.000352 | 0 | 1.1 | 0.000442 | -0.00624 | CFL | Bldg | 1160 | 0.468 | 998 | 0.352 | 1.1 | 1.26 | -0.00625
CFLBldgPGEERCExIOU | Com-Iltg-dWatt-CFL_OSbldg | PGE | ERC | Ex | IOU | 1.16 | 9.84e-05 | 0 | 1.2 | 0.000116 | -0.0122 | 0.998 | 7.41e-05 | 0 | 1.03 | 8.76e-05 | -0.0105 | CFL | Bldg | 1160 | 0.0984 | 998 | 0.0741 | 1.03 | 1.18 | -0.0105
CFLBldgPGEERCNewCZ01 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ERC | New | CZ01 | 0.998 | 0.000376 | 0 | 1.03 | 0.000445 | -0.0197 | 0.998 | 0.000376 | 0 | 1.03 | 0.000445 | -0.0197 | CFL | Bldg | 998 | 0.376 | 998 | 0.376 | 1.03 | 1.18 | -0.0197
CFLBldgPGEERCNewCZ02 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ERC | New | CZ02 | 0.998 | 1.09e-05 | 0 | 1.07 | 1.09e-05 | -0.013 | 0.998 | 1.09e-05 | 0 | 1.07 | 1.09e-05 | -0.013 | CFL | Bldg | 998 | 0.0109 | 998 | 0.0109 | 1.07 | 1 | -0.013
CFLBldgPGEERCNewCZ03 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ERC | New | CZ03 | 0.998 | 1.09e-05 | 0 | 1.07 | 1.09e-05 | -0.0119 | 0.998 | 1.09e-05 | 0 | 1.07 | 1.09e-05 | -0.0119 | CFL | Bldg | 998 | 0.0109 | 998 | 0.0109 | 1.07 | 1 | -0.0119
CFLBldgPGEERCNewCZ04 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ERC | New | CZ04 | 0.998 | 0.000376 | 0 | 1.1 | 0.000475 | -0.0103 | 0.998 | 0.000376 | 0 | 1.1 | 0.000475 | -0.0103 | CFL | Bldg | 998 | 0.376 | 998 | 0.376 | 1.1 | 1.26 | -0.0103
CFLBldgPGEERCNewCZ05 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ERC | New | CZ05 | 0.998 | 0.000376 | 0 | 1.07 | 0.000482 | -0.0114 | 0.998 | 0.000376 | 0 | 1.07 | 0.000482 | -0.0114 | CFL | Bldg | 998 | 0.376 | 998 | 0.376 | 1.07 | 1.28 | -0.0114
CFLBldgSCEERCNewCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ERC | New | CZ05 | 0.998 | 0.000376 | 0 | 1.08 | 0.000506 | -0.0105 | 0.998 | 0.000376 | 0 | 1.08 | 0.000506 | -0.0105 | CFL | Bldg | 998 | 0.376 | 998 | 0.376 | 1.08 | 1.35 | -0.0105
CFLBldgSCEERCNewCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ERC | New | CZ06 | 0.998 | 0.000376 | 0 | 1.14 | 0.000484 | -0.00672 | 0.998 | 0.000376 | 0 | 1.14 | 0.000484 | -0.00672 | CFL | Bldg | 998 | 0.376 | 998 | 0.376 | 1.14 | 1.29 | -0.00673
CFLBldgSDGERCNewCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SDG | ERC | New | CZ06 | 0.998 | 0.000376 | 0 | 1.14 | 0.000481 | -0.0068 | 0.998 | 0.000376 | 0 | 1.14 | 0.000481 | -0.0068 | CFL | Bldg | 998 | 0.376 | 998 | 0.376 | 1.14 | 1.28 | -0.00681
CFLBldgSDGERCNewCZ07 | Com-Iltg-dWatt-CFL_OSbldg | SDG | ERC | New | CZ07 | 0.998 | 0.000376 | 0 | 1.14 | 0.000474 | -0.00525 | 0.998 | 0.000376 | 0 | 1.14 | 0.000474 | -0.00525 | CFL | Bldg | 998 | 0.376 | 998 | 0.376 | 1.14 | 1.26 | -0.00526
CFLBldgSDGERCNewCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SDG | ERC | New | CZ08 | 0.998 | 0.000376 | 0 | 1.15 | 0.000493 | -0.00592 | 0.998 | 0.000376 | 0 | 1.15 | 0.000493 | -0.00592 | CFL | Bldg | 998 | 0.376 | 998 | 0.376 | 1.15 | 1.31 | -0.00593
CFLBldgSCEERCNewCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ERC | New | CZ08 | 0.998 | 0.000376 | 0 | 1.16 | 0.000496 | -0.00586 | 0.998 | 0.000376 | 0 | 1.16 | 0.000496 | -0.00586 | CFL | Bldg | 998 | 0.376 | 998 | 0.376 | 1.16 | 1.32 | -0.00587
CFLBldgSCEERCNewCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ERC | New | CZ09 | 0.998 | 0.000376 | 0 | 1.16 | 0.000509 | -0.0063 | 0.998 | 0.000376 | 0 | 1.16 | 0.000509 | -0.0063 | CFL | Bldg | 998 | 0.376 | 998 | 0.376 | 1.16 | 1.35 | -0.00631
CFLBldgSDGERCNewCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SDG | ERC | New | CZ10 | 0.998 | 0.000376 | 0 | 1.16 | 0.000515 | -0.00673 | 0.998 | 0.000376 | 0 | 1.16 | 0.000515 | -0.00673 | CFL | Bldg | 998 | 0.376 | 998 | 0.376 | 1.16 | 1.37 | -0.00674
CFLBldgSCEERCNewCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ERC | New | CZ10 | 0.998 | 0.000376 | 0 | 1.16 | 0.000519 | -0.00665 | 0.998 | 0.000376 | 0 | 1.16 | 0.000519 | -0.00665 | CFL | Bldg | 998 | 0.376 | 998 | 0.376 | 1.16 | 1.38 | -0.00666
CFLBldgPGEERCNewCZ11 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ERC | New | CZ11 | 0.998 | 1.09e-05 | 0 | 1.12 | 1.09e-05 | -0.0119 | 0.998 | 1.09e-05 | 0 | 1.12 | 1.09e-05 | -0.0119 | CFL | Bldg | 998 | 0.0109 | 998 | 0.0109 | 1.12 | 1 | -0.0119
CFLBldgPGEERCNewCZ12 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ERC | New | CZ12 | 0.998 | 1.09e-05 | 0 | 1.1 | 1.09e-05 | -0.0121 | 0.998 | 1.09e-05 | 0 | 1.1 | 1.09e-05 | -0.0121 | CFL | Bldg | 998 | 0.0109 | 998 | 0.0109 | 1.1 | 1 | -0.0121
CFLBldgPGEERCNewCZ13 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ERC | New | CZ13 | 0.998 | 1.09e-05 | 0 | 1.12 | 1.09e-05 | -0.0106 | 0.998 | 1.09e-05 | 0 | 1.12 | 1.09e-05 | -0.0106 | CFL | Bldg | 998 | 0.0109 | 998 | 0.0109 | 1.12 | 1 | -0.0106
CFLBldgSCEERCNewCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ERC | New | CZ13 | 0.998 | 1.09e-05 | 0 | 1.15 | 1.09e-05 | -0.00973 | 0.998 | 1.09e-05 | 0 | 1.15 | 1.09e-05 | -0.00973 | CFL | Bldg | 998 | 0.0109 | 998 | 0.0109 | 1.15 | 1 | -0.00975
CFLBldgSCEERCNewCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ERC | New | CZ14 | 0.998 | 0.000376 | 0 | 1.15 | 0.000511 | -0.00965 | 0.998 | 0.000376 | 0 | 1.15 | 0.000511 | -0.00965 | CFL | Bldg | 998 | 0.376 | 998 | 0.376 | 1.15 | 1.36 | -0.00967
CFLBldgSDGERCNewCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SDG | ERC | New | CZ14 | 0.998 | 0.000376 | 0 | 1.14 | 0.000507 | -0.00977 | 0.998 | 0.000376 | 0 | 1.14 | 0.000507 | -0.00977 | CFL | Bldg | 998 | 0.376 | 998 | 0.376 | 1.14 | 1.35 | -0.00979
CFLBldgSCEERCNewCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ERC | New | CZ15 | 0.998 | 0.000376 | 0 | 1.27 | 0.00052 | -0.00333 | 0.998 | 0.000376 | 0 | 1.27 | 0.00052 | -0.00333 | CFL | Bldg | 998 | 0.376 | 998 | 0.376 | 1.27 | 1.38 | -0.00334
CFLBldgSDGERCNewCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SDG | ERC | New | CZ15 | 0.998 | 0.000376 | 0 | 1.26 | 0.000515 | -0.00337 | 0.998 | 0.000376 | 0 | 1.26 | 0.000515 | -0.00337 | CFL | Bldg | 998 | 0.376 | 998 | 0.376 | 1.26 | 1.37 | -0.00338
CFLBldgPGEERCNewCZ16 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ERC | New | CZ16 | 0.998 | 1.09e-05 | 0 | 1.02 | 1.09e-05 | -0.0184 | 0.998 | 1.09e-05 | 0 | 1.02 | 1.09e-05 | -0.0184 | CFL | Bldg | 998 | 0.0109 | 998 | 0.0109 | 1.02 | 1 | -0.0184
CFLBldgSCEERCNewCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ERC | New | CZ16 | 0.998 | 1.09e-05 | 0 | 1.02 | 1.09e-05 | -0.0171 | 0.998 | 1.09e-05 | 0 | 1.02 | 1.09e-05 | -0.0171 | CFL | Bldg | 998 | 0.0109 | 998 | 0.0109 | 1.02 | 1 | -0.0171
CFLBldgSDGERCNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SDG | ERC | New | IOU | 0.998 | 0.000376 | 0 | 1.15 | 0.000489 | -0.00588 | 0.998 | 0.000376 | 0 | 1.15 | 0.000489 | -0.00588 | CFL | Bldg | 998 | 0.376 | 998 | 0.376 | 1.15 | 1.3 | -0.00589
CFLBldgPGEERCNewIOU | Com-Iltg-dWatt-CFL_OSbldg | PGE | ERC | New | IOU | 0.998 | 3.34e-05 | 0 | 1.14 | 4.14e-05 | -0.0102 | 0.998 | 3.34e-05 | 0 | 1.14 | 4.14e-05 | -0.0102 | CFL | Bldg | 998 | 0.0334 | 998 | 0.0334 | 1.14 | 1.24 | -0.0102
CFLBldgSCEERCNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | ERC | New | IOU | 0.998 | 0.000376 | 0 | 1.16 | 0.000503 | -0.00669 | 0.998 | 0.000376 | 0 | 1.16 | 0.000503 | -0.00669 | CFL | Bldg | 998 | 0.376 | 998 | 0.376 | 1.16 | 1.34 | -0.0067
CFLBldgSCGERCNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SCG | ERC | New | IOU | 0.998 | 0.000376 | 0 | 1.16 | 0.000502 | -0.00666 | 0.998 | 0.000376 | 0 | 1.16 | 0.000502 | -0.00666 | CFL | Bldg | 998 | 0.376 | 998 | 0.376 | 1.16 | 1.34 | -0.00667
CFLBldgPGEESeExCZ01 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ESe | Ex | CZ01 | 1.59 | 0.000342 | 0 | 1.54 | 0.000405 | -0.0325 | 1.44 | 0.000289 | 0 | 1.4 | 0.000342 | -0.0294 | CFL | Bldg | 1590 | 0.342 | 1440 | 0.289 | 0.972 | 1.18 | -0.0204
CFLBldgPGEESeExCZ02 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ESe | Ex | CZ02 | 1.6 | 9.55e-06 | 0 | 1.66 | 9.55e-06 | -0.0204 | 1.44 | 8.09e-06 | 0 | 1.5 | 8.09e-06 | -0.0184 | CFL | Bldg | 1600 | 0.00955 | 1440 | 0.00809 | 1.04 | 1 | -0.0128
CFLBldgPGEESeExCZ03 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ESe | Ex | CZ03 | 1.6 | 9.56e-06 | 0 | 1.66 | 9.56e-06 | -0.021 | 1.44 | 8.09e-06 | 0 | 1.5 | 8.09e-06 | -0.019 | CFL | Bldg | 1600 | 0.00956 | 1440 | 0.00809 | 1.04 | 1 | -0.0132
CFLBldgPGEESeExCZ04 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ESe | Ex | CZ04 | 1.59 | 0.000342 | 0 | 1.69 | 0.000415 | -0.0162 | 1.44 | 0.000289 | 0 | 1.53 | 0.000351 | -0.0147 | CFL | Bldg | 1590 | 0.342 | 1440 | 0.289 | 1.06 | 1.21 | -0.0102
CFLBldgSCEESeExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ESe | Ex | CZ05 | 1.6 | 0.000343 | 0 | 1.69 | 0.000424 | -0.0179 | 1.44 | 0.000289 | 0 | 1.52 | 0.000358 | -0.0161 | CFL | Bldg | 1600 | 0.343 | 1440 | 0.289 | 1.06 | 1.24 | -0.0112
CFLBldgSCGESeExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCG | ESe | Ex | CZ05 | 1.6 | 0.000343 | 0 | 1.69 | 0.000424 | -0.0179 | 1.44 | 0.000289 | 0 | 1.52 | 0.000358 | -0.0161 | CFL | Bldg | 1600 | 0.343 | 1440 | 0.289 | 1.06 | 1.24 | -0.0112
CFLBldgPGEESeExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ESe | Ex | CZ05 | 1.59 | 0.000342 | 0 | 1.68 | 0.000424 | -0.0178 | 1.44 | 0.000289 | 0 | 1.52 | 0.000358 | -0.0161 | CFL | Bldg | 1590 | 0.342 | 1440 | 0.289 | 1.06 | 1.24 | -0.0112
CFLBldgSDGESeExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SDG | ESe | Ex | CZ06 | 1.59 | 0.000342 | 0 | 1.78 | 0.000435 | -0.00917 | 1.44 | 0.000289 | 0 | 1.61 | 0.000367 | -0.00828 | CFL | Bldg | 1590 | 0.342 | 1440 | 0.289 | 1.12 | 1.27 | -0.00575
CFLBldgSCEESeExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ESe | Ex | CZ06 | 1.6 | 0.000343 | 0 | 1.79 | 0.000435 | -0.00918 | 1.44 | 0.000289 | 0 | 1.61 | 0.000367 | -0.00828 | CFL | Bldg | 1600 | 0.343 | 1440 | 0.289 | 1.12 | 1.27 | -0.00575
CFLBldgSCGESeExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCG | ESe | Ex | CZ06 | 1.6 | 0.000343 | 0 | 1.79 | 0.000435 | -0.00918 | 1.44 | 0.000289 | 0 | 1.61 | 0.000367 | -0.00828 | CFL | Bldg | 1600 | 0.343 | 1440 | 0.289 | 1.12 | 1.27 | -0.00575
CFLBldgSDGESeExCZ07 | Com-Iltg-dWatt-CFL_OSbldg | SDG | ESe | Ex | CZ07 | 1.59 | 0.000342 | 0 | 1.77 | 0.000426 | -0.00808 | 1.44 | 0.000289 | 0 | 1.6 | 0.00036 | -0.0073 | CFL | Bldg | 1590 | 0.342 | 1440 | 0.289 | 1.11 | 1.25 | -0.00507
CFLBldgSDGESeExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SDG | ESe | Ex | CZ08 | 1.59 | 0.000342 | 0 | 1.79 | 0.000432 | -0.00781 | 1.44 | 0.000289 | 0 | 1.62 | 0.000365 | -0.00706 | CFL | Bldg | 1590 | 0.342 | 1440 | 0.289 | 1.13 | 1.26 | -0.0049
CFLBldgSCGESeExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCG | ESe | Ex | CZ08 | 1.6 | 0.000343 | 0 | 1.8 | 0.000432 | -0.00782 | 1.44 | 0.000289 | 0 | 1.62 | 0.000365 | -0.00706 | CFL | Bldg | 1600 | 0.343 | 1440 | 0.289 | 1.13 | 1.26 | -0.0049
CFLBldgSCEESeExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ESe | Ex | CZ08 | 1.6 | 0.000343 | 0 | 1.8 | 0.000432 | -0.00782 | 1.44 | 0.000289 | 0 | 1.62 | 0.000365 | -0.00706 | CFL | Bldg | 1600 | 0.343 | 1440 | 0.289 | 1.13 | 1.26 | -0.0049
CFLBldgSCGESeExCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCG | ESe | Ex | CZ09 | 1.6 | 0.000343 | 0 | 1.83 | 0.00044 | -0.00947 | 1.44 | 0.000289 | 0 | 1.64 | 0.000371 | -0.00854 | CFL | Bldg | 1600 | 0.343 | 1440 | 0.289 | 1.14 | 1.28 | -0.00593
CFLBldgSCEESeExCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ESe | Ex | CZ09 | 1.6 | 0.000342 | 0 | 1.82 | 0.00044 | -0.00946 | 1.44 | 0.000289 | 0 | 1.64 | 0.000371 | -0.00854 | CFL | Bldg | 1600 | 0.342 | 1440 | 0.289 | 1.14 | 1.28 | -0.00593
CFLBldgSCGESeExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCG | ESe | Ex | CZ10 | 1.59 | 0.000341 | 0 | 1.78 | 0.000428 | -0.00973 | 1.44 | 0.000289 | 0 | 1.61 | 0.000363 | -0.00881 | CFL | Bldg | 1590 | 0.341 | 1440 | 0.289 | 1.12 | 1.26 | -0.00612
CFLBldgSCEESeExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ESe | Ex | CZ10 | 1.59 | 0.000341 | 0 | 1.78 | 0.000428 | -0.00973 | 1.44 | 0.000289 | 0 | 1.61 | 0.000363 | -0.00881 | CFL | Bldg | 1590 | 0.341 | 1440 | 0.289 | 1.12 | 1.26 | -0.00612
CFLBldgSDGESeExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SDG | ESe | Ex | CZ10 | 1.59 | 0.000342 | 0 | 1.78 | 0.00043 | -0.00976 | 1.44 | 0.000289 | 0 | 1.61 | 0.000363 | -0.00881 | CFL | Bldg | 1590 | 0.342 | 1440 | 0.289 | 1.12 | 1.26 | -0.00612
CFLBldgPGEESeExCZ11 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ESe | Ex | CZ11 | 1.59 | 9.51e-06 | 0 | 1.69 | 9.51e-06 | -0.018 | 1.44 | 8.09e-06 | 0 | 1.53 | 8.09e-06 | -0.0163 | CFL | Bldg | 1590 | 0.00951 | 1440 | 0.00809 | 1.06 | 1 | -0.0113
CFLBldgPGEESeExCZ12 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ESe | Ex | CZ12 | 1.59 | 9.52e-06 | 0 | 1.68 | 9.52e-06 | -0.0188 | 1.44 | 8.09e-06 | 0 | 1.52 | 8.09e-06 | -0.017 | CFL | Bldg | 1590 | 0.00952 | 1440 | 0.00809 | 1.06 | 1 | -0.0118
CFLBldgSCEESeExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ESe | Ex | CZ13 | 1.59 | 9.5e-06 | 0 | 1.74 | 9.5e-06 | -0.0154 | 1.44 | 8.09e-06 | 0 | 1.58 | 8.09e-06 | -0.0139 | CFL | Bldg | 1590 | 0.0095 | 1440 | 0.00809 | 1.1 | 1 | -0.00965
CFLBldgSCGESeExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCG | ESe | Ex | CZ13 | 1.59 | 9.5e-06 | 0 | 1.74 | 9.5e-06 | -0.0154 | 1.44 | 8.09e-06 | 0 | 1.58 | 8.09e-06 | -0.0139 | CFL | Bldg | 1590 | 0.0095 | 1440 | 0.00809 | 1.1 | 1 | -0.00965
CFLBldgPGEESeExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ESe | Ex | CZ13 | 1.59 | 9.52e-06 | 0 | 1.74 | 9.52e-06 | -0.0154 | 1.44 | 8.09e-06 | 0 | 1.58 | 8.09e-06 | -0.0139 | CFL | Bldg | 1590 | 0.00952 | 1440 | 0.00809 | 1.1 | 1 | -0.00965
CFLBldgSCEESeExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ESe | Ex | CZ14 | 1.59 | 0.000341 | 0 | 1.73 | 0.000414 | -0.0152 | 1.44 | 0.000289 | 0 | 1.57 | 0.000351 | -0.0138 | CFL | Bldg | 1590 | 0.341 | 1440 | 0.289 | 1.09 | 1.21 | -0.00958
CFLBldgSCGESeExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCG | ESe | Ex | CZ14 | 1.59 | 0.000341 | 0 | 1.73 | 0.000414 | -0.0152 | 1.44 | 0.000289 | 0 | 1.57 | 0.000351 | -0.0138 | CFL | Bldg | 1590 | 0.341 | 1440 | 0.289 | 1.09 | 1.21 | -0.00958
CFLBldgSDGESeExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SDG | ESe | Ex | CZ14 | 1.59 | 0.000342 | 0 | 1.73 | 0.000416 | -0.0152 | 1.44 | 0.000289 | 0 | 1.57 | 0.000351 | -0.0138 | CFL | Bldg | 1590 | 0.342 | 1440 | 0.289 | 1.09 | 1.21 | -0.00958
CFLBldgSCEESeExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ESe | Ex | CZ15 | 1.59 | 0.000341 | 0 | 1.94 | 0.000428 | -0.00434 | 1.44 | 0.000289 | 0 | 1.75 | 0.000363 | -0.00393 | CFL | Bldg | 1590 | 0.341 | 1440 | 0.289 | 1.22 | 1.26 | -0.00273
CFLBldgSCGESeExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCG | ESe | Ex | CZ15 | 1.59 | 0.000341 | 0 | 1.94 | 0.000428 | -0.00434 | 1.44 | 0.000289 | 0 | 1.75 | 0.000363 | -0.00393 | CFL | Bldg | 1590 | 0.341 | 1440 | 0.289 | 1.22 | 1.26 | -0.00273
CFLBldgSDGESeExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SDG | ESe | Ex | CZ15 | 1.59 | 0.000342 | 0 | 1.94 | 0.00043 | -0.00435 | 1.44 | 0.000289 | 0 | 1.75 | 0.000363 | -0.00393 | CFL | Bldg | 1590 | 0.342 | 1440 | 0.289 | 1.22 | 1.26 | -0.00273
CFLBldgSCGESeExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCG | ESe | Ex | CZ16 | 1.59 | 9.51e-06 | 0 | 1.55 | 9.51e-06 | -0.0265 | 1.44 | 8.09e-06 | 0 | 1.4 | 8.09e-06 | -0.024 | CFL | Bldg | 1590 | 0.00951 | 1440 | 0.00809 | 0.972 | 1 | -0.0167
CFLBldgSCEESeExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ESe | Ex | CZ16 | 1.59 | 9.51e-06 | 0 | 1.55 | 9.51e-06 | -0.0265 | 1.44 | 8.09e-06 | 0 | 1.4 | 8.09e-06 | -0.024 | CFL | Bldg | 1590 | 0.00951 | 1440 | 0.00809 | 0.972 | 1 | -0.0167
CFLBldgPGEESeExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ESe | Ex | CZ16 | 1.59 | 9.52e-06 | 0 | 1.55 | 9.52e-06 | -0.0266 | 1.44 | 8.09e-06 | 0 | 1.4 | 8.09e-06 | -0.024 | CFL | Bldg | 1590 | 0.00952 | 1440 | 0.00809 | 0.972 | 1 | -0.0167
CFLBldgSCGESeExIOU | Com-Iltg-dWatt-CFL_OSbldg | SCG | ESe | Ex | IOU | 1.59 | 0.000325 | 0 | 1.79 | 0.000411 | -0.0097 | 1.44 | 0.000274 | 0 | 1.62 | 0.000347 | -0.00876 | CFL | Bldg | 1590 | 0.325 | 1440 | 0.274 | 1.13 | 1.27 | -0.00608
CFLBldgSDGESeExIOU | Com-Iltg-dWatt-CFL_OSbldg | SDG | ESe | Ex | IOU | 1.59 | 0.000342 | 0 | 1.78 | 0.000428 | -0.00872 | 1.44 | 0.000289 | 0 | 1.6 | 0.000362 | -0.00788 | CFL | Bldg | 1590 | 0.342 | 1440 | 0.289 | 1.11 | 1.25 | -0.00547
CFLBldgPGEESeExIOU | Com-Iltg-dWatt-CFL_OSbldg | PGE | ESe | Ex | IOU | 1.59 | 6.81e-05 | 0 | 1.68 | 8.09e-05 | -0.0188 | 1.44 | 5.75e-05 | 0 | 1.52 | 6.85e-05 | -0.017 | CFL | Bldg | 1590 | 0.0681 | 1440 | 0.0575 | 1.06 | 1.19 | -0.0118
CFLBldgSCEESeExIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | ESe | Ex | IOU | 1.59 | 0.00032 | 0 | 1.79 | 0.000404 | -0.00984 | 1.44 | 0.00027 | 0 | 1.61 | 0.000342 | -0.00889 | CFL | Bldg | 1590 | 0.32 | 1440 | 0.27 | 1.12 | 1.27 | -0.00617
CFLBldgPGEESeNewCZ01 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ESe | New | CZ01 | 1.44 | 0.000291 | 0 | 1.42 | 0.000335 | -0.0232 | 1.44 | 0.000291 | 0 | 1.42 | 0.000335 | -0.0232 | CFL | Bldg | 1440 | 0.291 | 1440 | 0.291 | 0.986 | 1.15 | -0.0161
CFLBldgPGEESeNewCZ02 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ESe | New | CZ02 | 1.44 | 8.14e-06 | 0 | 1.52 | 8.14e-06 | -0.0213 | 1.44 | 8.14e-06 | 0 | 1.52 | 8.14e-06 | -0.0213 | CFL | Bldg | 1440 | 0.00814 | 1440 | 0.00814 | 1.06 | 1 | -0.0148
CFLBldgPGEESeNewCZ03 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ESe | New | CZ03 | 1.44 | 8.14e-06 | 0 | 1.5 | 8.14e-06 | -0.0187 | 1.44 | 8.14e-06 | 0 | 1.5 | 8.14e-06 | -0.0187 | CFL | Bldg | 1440 | 0.00814 | 1440 | 0.00814 | 1.04 | 1 | -0.013
CFLBldgPGEESeNewCZ04 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ESe | New | CZ04 | 1.44 | 0.000291 | 0 | 1.54 | 0.000379 | -0.017 | 1.44 | 0.000291 | 0 | 1.54 | 0.000379 | -0.017 | CFL | Bldg | 1440 | 0.291 | 1440 | 0.291 | 1.07 | 1.3 | -0.0118
CFLBldgPGEESeNewCZ05 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ESe | New | CZ05 | 1.44 | 0.000291 | 0 | 1.49 | 0.000352 | -0.0163 | 1.44 | 0.000291 | 0 | 1.49 | 0.000352 | -0.0163 | CFL | Bldg | 1440 | 0.291 | 1440 | 0.291 | 1.03 | 1.21 | -0.0113
CFLBldgSCEESeNewCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ESe | New | CZ05 | 1.44 | 0.000291 | 0 | 1.5 | 0.000365 | -0.015 | 1.44 | 0.000291 | 0 | 1.5 | 0.000365 | -0.015 | CFL | Bldg | 1440 | 0.291 | 1440 | 0.291 | 1.04 | 1.25 | -0.0104
CFLBldgSCEESeNewCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ESe | New | CZ06 | 1.44 | 0.000291 | 0 | 1.59 | 0.000387 | -0.0107 | 1.44 | 0.000291 | 0 | 1.59 | 0.000387 | -0.0107 | CFL | Bldg | 1440 | 0.291 | 1440 | 0.291 | 1.1 | 1.33 | -0.00743
CFLBldgSDGESeNewCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SDG | ESe | New | CZ06 | 1.44 | 0.000291 | 0 | 1.58 | 0.000383 | -0.0107 | 1.44 | 0.000291 | 0 | 1.58 | 0.000383 | -0.0107 | CFL | Bldg | 1440 | 0.291 | 1440 | 0.291 | 1.1 | 1.32 | -0.00743
CFLBldgSDGESeNewCZ07 | Com-Iltg-dWatt-CFL_OSbldg | SDG | ESe | New | CZ07 | 1.44 | 0.000291 | 0 | 1.56 | 0.000374 | -0.00927 | 1.44 | 0.000291 | 0 | 1.56 | 0.000374 | -0.00927 | CFL | Bldg | 1440 | 0.291 | 1440 | 0.291 | 1.08 | 1.29 | -0.00644
CFLBldgSDGESeNewCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SDG | ESe | New | CZ08 | 1.44 | 0.000291 | 0 | 1.6 | 0.000387 | -0.00876 | 1.44 | 0.000291 | 0 | 1.6 | 0.000387 | -0.00876 | CFL | Bldg | 1440 | 0.291 | 1440 | 0.291 | 1.11 | 1.33 | -0.00608
CFLBldgSCEESeNewCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ESe | New | CZ08 | 1.44 | 0.000291 | 0 | 1.61 | 0.000392 | -0.00876 | 1.44 | 0.000291 | 0 | 1.61 | 0.000392 | -0.00876 | CFL | Bldg | 1440 | 0.291 | 1440 | 0.291 | 1.12 | 1.35 | -0.00608
CFLBldgSCEESeNewCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ESe | New | CZ09 | 1.44 | 0.000291 | 0 | 1.61 | 0.000405 | -0.0103 | 1.44 | 0.000291 | 0 | 1.61 | 0.000405 | -0.0103 | CFL | Bldg | 1440 | 0.291 | 1440 | 0.291 | 1.12 | 1.39 | -0.00715
CFLBldgSDGESeNewCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SDG | ESe | New | CZ10 | 1.44 | 0.000291 | 0 | 1.61 | 0.000405 | -0.011 | 1.44 | 0.000291 | 0 | 1.61 | 0.000405 | -0.011 | CFL | Bldg | 1440 | 0.291 | 1440 | 0.291 | 1.12 | 1.39 | -0.00764
CFLBldgSCEESeNewCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ESe | New | CZ10 | 1.44 | 0.000291 | 0 | 1.62 | 0.000411 | -0.011 | 1.44 | 0.000291 | 0 | 1.62 | 0.000411 | -0.011 | CFL | Bldg | 1440 | 0.291 | 1440 | 0.291 | 1.13 | 1.41 | -0.00764
CFLBldgPGEESeNewCZ11 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ESe | New | CZ11 | 1.44 | 8.14e-06 | 0 | 1.57 | 8.14e-06 | -0.0184 | 1.44 | 8.14e-06 | 0 | 1.57 | 8.14e-06 | -0.0184 | CFL | Bldg | 1440 | 0.00814 | 1440 | 0.00814 | 1.09 | 1 | -0.0128
CFLBldgPGEESeNewCZ12 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ESe | New | CZ12 | 1.44 | 8.14e-06 | 0 | 1.55 | 8.14e-06 | -0.019 | 1.44 | 8.14e-06 | 0 | 1.55 | 8.14e-06 | -0.019 | CFL | Bldg | 1440 | 0.00814 | 1440 | 0.00814 | 1.08 | 1 | -0.0132
CFLBldgPGEESeNewCZ13 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ESe | New | CZ13 | 1.44 | 8.14e-06 | 0 | 1.58 | 8.14e-06 | -0.0171 | 1.44 | 8.14e-06 | 0 | 1.58 | 8.14e-06 | -0.0171 | CFL | Bldg | 1440 | 0.00814 | 1440 | 0.00814 | 1.1 | 1 | -0.0119
CFLBldgSCEESeNewCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ESe | New | CZ13 | 1.44 | 8.14e-06 | 0 | 1.61 | 8.14e-06 | -0.0161 | 1.44 | 8.14e-06 | 0 | 1.61 | 8.14e-06 | -0.0161 | CFL | Bldg | 1440 | 0.00814 | 1440 | 0.00814 | 1.12 | 1 | -0.0112
CFLBldgSCEESeNewCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ESe | New | CZ14 | 1.44 | 0.000291 | 0 | 1.59 | 0.000402 | -0.016 | 1.44 | 0.000291 | 0 | 1.59 | 0.000402 | -0.016 | CFL | Bldg | 1440 | 0.291 | 1440 | 0.291 | 1.1 | 1.38 | -0.0111
CFLBldgSDGESeNewCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SDG | ESe | New | CZ14 | 1.44 | 0.000291 | 0 | 1.59 | 0.000398 | -0.0161 | 1.44 | 0.000291 | 0 | 1.59 | 0.000398 | -0.0161 | CFL | Bldg | 1440 | 0.291 | 1440 | 0.291 | 1.1 | 1.37 | -0.0112
CFLBldgSCEESeNewCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ESe | New | CZ15 | 1.44 | 0.000291 | 0 | 1.79 | 0.000407 | -0.0048 | 1.44 | 0.000291 | 0 | 1.79 | 0.000407 | -0.0048 | CFL | Bldg | 1440 | 0.291 | 1440 | 0.291 | 1.24 | 1.4 | -0.00333
CFLBldgSDGESeNewCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SDG | ESe | New | CZ15 | 1.44 | 0.000291 | 0 | 1.78 | 0.000403 | -0.00484 | 1.44 | 0.000291 | 0 | 1.78 | 0.000403 | -0.00484 | CFL | Bldg | 1440 | 0.291 | 1440 | 0.291 | 1.24 | 1.38 | -0.00336
CFLBldgPGEESeNewCZ16 | Com-Iltg-dWatt-CFL_OSbldg | PGE | ESe | New | CZ16 | 1.44 | 8.14e-06 | 0 | 1.44 | 8.14e-06 | -0.0213 | 1.44 | 8.14e-06 | 0 | 1.44 | 8.14e-06 | -0.0213 | CFL | Bldg | 1440 | 0.00814 | 1440 | 0.00814 | 1 | 1 | -0.0148
CFLBldgSCEESeNewCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | ESe | New | CZ16 | 1.44 | 8.14e-06 | 0 | 1.43 | 8.14e-06 | -0.02 | 1.44 | 8.14e-06 | 0 | 1.43 | 8.14e-06 | -0.02 | CFL | Bldg | 1440 | 0.00814 | 1440 | 0.00814 | 0.993 | 1 | -0.0139
CFLBldgSDGESeNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SDG | ESe | New | IOU | 1.44 | 0.000291 | 0 | 1.58 | 0.000386 | -0.00993 | 1.44 | 0.000291 | 0 | 1.58 | 0.000386 | -0.00993 | CFL | Bldg | 1440 | 0.291 | 1440 | 0.291 | 1.1 | 1.33 | -0.0069
CFLBldgSCEESeNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | ESe | New | IOU | 1.44 | 0.000291 | 0 | 1.61 | 0.000396 | -0.0106 | 1.44 | 0.000291 | 0 | 1.61 | 0.000396 | -0.0106 | CFL | Bldg | 1440 | 0.291 | 1440 | 0.291 | 1.12 | 1.36 | -0.00736
CFLBldgPGEESeNewIOU | Com-Iltg-dWatt-CFL_OSbldg | PGE | ESe | New | IOU | 1.44 | 2.56e-05 | 0 | 1.59 | 3.01e-05 | -0.0162 | 1.44 | 2.56e-05 | 0 | 1.59 | 3.01e-05 | -0.0162 | CFL | Bldg | 1440 | 0.0256 | 1440 | 0.0256 | 1.1 | 1.18 | -0.0113
CFLBldgSCGESeNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SCG | ESe | New | IOU | 1.44 | 0.000291 | 0 | 1.61 | 0.000395 | -0.0105 | 1.44 | 0.000291 | 0 | 1.61 | 0.000395 | -0.0105 | CFL | Bldg | 1440 | 0.291 | 1440 | 0.291 | 1.12 | 1.36 | -0.00729
CFLBldgPGEEUnExCZ01 | Com-Iltg-dWatt-CFL_OSbldg | PGE | EUn | Ex | CZ01 | 2.2 | 0.000692 | 0 | 2.33 | 0.000849 | -0.0233 | 2.02 | 0.00055 | 0 | 2.14 | 0.000675 | -0.0214 | CFL | Bldg | 2200 | 0.692 | 2020 | 0.55 | 1.06 | 1.23 | -0.0106
CFLBldgPGEEUnExCZ02 | Com-Iltg-dWatt-CFL_OSbldg | PGE | EUn | Ex | CZ02 | 2.2 | 0.000451 | 0 | 2.42 | 0.000559 | -0.0171 | 2.02 | 0.000361 | 0 | 2.22 | 0.000448 | -0.0157 | CFL | Bldg | 2200 | 0.451 | 2020 | 0.361 | 1.1 | 1.24 | -0.00777
CFLBldgPGEEUnExCZ03 | Com-Iltg-dWatt-CFL_OSbldg | PGE | EUn | Ex | CZ03 | 2.2 | 0.000453 | 0 | 2.41 | 0.000548 | -0.0163 | 2.02 | 0.000361 | 0 | 2.22 | 0.000437 | -0.015 | CFL | Bldg | 2200 | 0.453 | 2020 | 0.361 | 1.1 | 1.21 | -0.00743
CFLBldgPGEEUnExCZ04 | Com-Iltg-dWatt-CFL_OSbldg | PGE | EUn | Ex | CZ04 | 2.2 | 0.000688 | 0 | 2.46 | 0.000879 | -0.0132 | 2.02 | 0.00055 | 0 | 2.26 | 0.000703 | -0.0122 | CFL | Bldg | 2200 | 0.688 | 2020 | 0.55 | 1.12 | 1.28 | -0.00604
CFLBldgSCEEUnExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | EUn | Ex | CZ05 | 2.2 | 0.000689 | 0 | 2.44 | 0.000838 | -0.0156 | 2.02 | 0.00055 | 0 | 2.24 | 0.000669 | -0.0144 | CFL | Bldg | 2200 | 0.689 | 2020 | 0.55 | 1.11 | 1.22 | -0.00713
CFLBldgSCGEUnExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCG | EUn | Ex | CZ05 | 2.2 | 0.000689 | 0 | 2.44 | 0.000838 | -0.0156 | 2.02 | 0.00055 | 0 | 2.24 | 0.000669 | -0.0144 | CFL | Bldg | 2200 | 0.689 | 2020 | 0.55 | 1.11 | 1.22 | -0.00713
CFLBldgPGEEUnExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | PGE | EUn | Ex | CZ05 | 2.2 | 0.000688 | 0 | 2.44 | 0.000838 | -0.0156 | 2.02 | 0.00055 | 0 | 2.24 | 0.000669 | -0.0144 | CFL | Bldg | 2200 | 0.688 | 2020 | 0.55 | 1.11 | 1.22 | -0.00713
CFLBldgSCEEUnExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | EUn | Ex | CZ06 | 2.2 | 0.000689 | 0 | 2.51 | 0.000871 | -0.00933 | 2.02 | 0.00055 | 0 | 2.3 | 0.000695 | -0.00856 | CFL | Bldg | 2200 | 0.689 | 2020 | 0.55 | 1.14 | 1.26 | -0.00424
CFLBldgSCGEUnExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCG | EUn | Ex | CZ06 | 2.2 | 0.000689 | 0 | 2.51 | 0.000872 | -0.00933 | 2.02 | 0.00055 | 0 | 2.3 | 0.000695 | -0.00856 | CFL | Bldg | 2200 | 0.689 | 2020 | 0.55 | 1.14 | 1.26 | -0.00424
CFLBldgSDGEUnExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SDG | EUn | Ex | CZ06 | 2.2 | 0.000687 | 0 | 2.51 | 0.000868 | -0.00932 | 2.02 | 0.00055 | 0 | 2.3 | 0.000695 | -0.00856 | CFL | Bldg | 2200 | 0.687 | 2020 | 0.55 | 1.14 | 1.26 | -0.00424
CFLBldgSDGEUnExCZ07 | Com-Iltg-dWatt-CFL_OSbldg | SDG | EUn | Ex | CZ07 | 2.2 | 0.000687 | 0 | 2.5 | 0.00086 | -0.00831 | 2.02 | 0.00055 | 0 | 2.29 | 0.000689 | -0.00764 | CFL | Bldg | 2200 | 0.687 | 2020 | 0.55 | 1.13 | 1.25 | -0.00378
CFLBldgSCEEUnExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | EUn | Ex | CZ08 | 2.2 | 0.000689 | 0 | 2.52 | 0.000873 | -0.00898 | 2.02 | 0.00055 | 0 | 2.32 | 0.000697 | -0.00824 | CFL | Bldg | 2200 | 0.689 | 2020 | 0.55 | 1.15 | 1.27 | -0.00408
CFLBldgSCGEUnExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCG | EUn | Ex | CZ08 | 2.2 | 0.00069 | 0 | 2.52 | 0.000874 | -0.00899 | 2.02 | 0.00055 | 0 | 2.32 | 0.000697 | -0.00824 | CFL | Bldg | 2200 | 0.69 | 2020 | 0.55 | 1.15 | 1.27 | -0.00408
CFLBldgSDGEUnExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SDG | EUn | Ex | CZ08 | 2.2 | 0.000687 | 0 | 2.52 | 0.00087 | -0.00897 | 2.02 | 0.00055 | 0 | 2.32 | 0.000697 | -0.00824 | CFL | Bldg | 2200 | 0.687 | 2020 | 0.55 | 1.15 | 1.27 | -0.00408
CFLBldgSCGEUnExCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCG | EUn | Ex | CZ09 | 2.2 | 0.000691 | 0 | 2.54 | 0.00089 | -0.00978 | 2.02 | 0.00055 | 0 | 2.34 | 0.000708 | -0.00897 | CFL | Bldg | 2200 | 0.691 | 2020 | 0.55 | 1.16 | 1.29 | -0.00444
CFLBldgSCEEUnExCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | EUn | Ex | CZ09 | 2.2 | 0.000688 | 0 | 2.54 | 0.000886 | -0.00976 | 2.02 | 0.00055 | 0 | 2.34 | 0.000708 | -0.00897 | CFL | Bldg | 2200 | 0.688 | 2020 | 0.55 | 1.16 | 1.29 | -0.00444
CFLBldgSDGEUnExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SDG | EUn | Ex | CZ10 | 2.2 | 0.000687 | 0 | 2.52 | 0.000884 | -0.0105 | 2.02 | 0.00055 | 0 | 2.31 | 0.000708 | -0.00972 | CFL | Bldg | 2200 | 0.687 | 2020 | 0.55 | 1.14 | 1.29 | -0.00481
CFLBldgSCEEUnExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | EUn | Ex | CZ10 | 2.19 | 0.000682 | 0 | 2.51 | 0.000878 | -0.0105 | 2.02 | 0.00055 | 0 | 2.31 | 0.000708 | -0.00972 | CFL | Bldg | 2190 | 0.682 | 2020 | 0.55 | 1.14 | 1.29 | -0.00481
CFLBldgSCGEUnExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCG | EUn | Ex | CZ10 | 2.19 | 0.000682 | 0 | 2.51 | 0.000878 | -0.0105 | 2.02 | 0.00055 | 0 | 2.31 | 0.000708 | -0.00972 | CFL | Bldg | 2190 | 0.682 | 2020 | 0.55 | 1.14 | 1.29 | -0.00481
CFLBldgPGEEUnExCZ11 | Com-Iltg-dWatt-CFL_OSbldg | PGE | EUn | Ex | CZ11 | 2.2 | 0.00045 | 0 | 2.47 | 0.000568 | -0.0153 | 2.02 | 0.000361 | 0 | 2.26 | 0.000455 | -0.0141 | CFL | Bldg | 2200 | 0.45 | 2020 | 0.361 | 1.12 | 1.26 | -0.00698
CFLBldgPGEEUnExCZ12 | Com-Iltg-dWatt-CFL_OSbldg | PGE | EUn | Ex | CZ12 | 2.2 | 0.00045 | 0 | 2.46 | 0.000563 | -0.0152 | 2.02 | 0.000361 | 0 | 2.26 | 0.000452 | -0.014 | CFL | Bldg | 2200 | 0.45 | 2020 | 0.361 | 1.12 | 1.25 | -0.00693
CFLBldgSCEEUnExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | EUn | Ex | CZ13 | 2.19 | 0.000444 | 0 | 2.47 | 0.00056 | -0.012 | 2.02 | 0.000361 | 0 | 2.28 | 0.000455 | -0.0111 | CFL | Bldg | 2190 | 0.444 | 2020 | 0.361 | 1.13 | 1.26 | -0.0055
CFLBldgPGEEUnExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | PGE | EUn | Ex | CZ13 | 2.2 | 0.00045 | 0 | 2.49 | 0.000568 | -0.012 | 2.02 | 0.000361 | 0 | 2.28 | 0.000455 | -0.0111 | CFL | Bldg | 2200 | 0.45 | 2020 | 0.361 | 1.13 | 1.26 | -0.0055
CFLBldgSCGEUnExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCG | EUn | Ex | CZ13 | 2.19 | 0.000444 | 0 | 2.47 | 0.00056 | -0.012 | 2.02 | 0.000361 | 0 | 2.28 | 0.000455 | -0.0111 | CFL | Bldg | 2190 | 0.444 | 2020 | 0.361 | 1.13 | 1.26 | -0.0055
CFLBldgSCEEUnExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | EUn | Ex | CZ14 | 2.19 | 0.000683 | 0 | 2.48 | 0.000868 | -0.0146 | 2.02 | 0.00055 | 0 | 2.29 | 0.0007 | -0.0134 | CFL | Bldg | 2190 | 0.683 | 2020 | 0.55 | 1.13 | 1.27 | -0.00663
CFLBldgSDGEUnExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SDG | EUn | Ex | CZ14 | 2.2 | 0.000687 | 0 | 2.49 | 0.000873 | -0.0146 | 2.02 | 0.00055 | 0 | 2.29 | 0.0007 | -0.0134 | CFL | Bldg | 2200 | 0.687 | 2020 | 0.55 | 1.13 | 1.27 | -0.00663
CFLBldgSCGEUnExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCG | EUn | Ex | CZ14 | 2.19 | 0.000683 | 0 | 2.48 | 0.000868 | -0.0146 | 2.02 | 0.00055 | 0 | 2.29 | 0.0007 | -0.0134 | CFL | Bldg | 2190 | 0.683 | 2020 | 0.55 | 1.13 | 1.27 | -0.00663
CFLBldgSCGEUnExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCG | EUn | Ex | CZ15 | 2.19 | 0.000682 | 0 | 2.59 | 0.000866 | -0.00487 | 2.02 | 0.00055 | 0 | 2.39 | 0.000698 | -0.00448 | CFL | Bldg | 2190 | 0.682 | 2020 | 0.55 | 1.18 | 1.27 | -0.00222
CFLBldgSCEEUnExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | EUn | Ex | CZ15 | 2.19 | 0.000682 | 0 | 2.59 | 0.000866 | -0.00487 | 2.02 | 0.00055 | 0 | 2.39 | 0.000698 | -0.00448 | CFL | Bldg | 2190 | 0.682 | 2020 | 0.55 | 1.18 | 1.27 | -0.00222
CFLBldgSCGEUnExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCG | EUn | Ex | CZ16 | 2.19 | 0.000447 | 0 | 2.31 | 0.000545 | -0.0254 | 2.02 | 0.000361 | 0 | 2.13 | 0.00044 | -0.0234 | CFL | Bldg | 2190 | 0.447 | 2020 | 0.361 | 1.05 | 1.22 | -0.0116
CFLBldgSCEEUnExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | EUn | Ex | CZ16 | 2.19 | 0.000447 | 0 | 2.31 | 0.000545 | -0.0254 | 2.02 | 0.000361 | 0 | 2.13 | 0.00044 | -0.0234 | CFL | Bldg | 2190 | 0.447 | 2020 | 0.361 | 1.05 | 1.22 | -0.0116
CFLBldgPGEEUnExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | PGE | EUn | Ex | CZ16 | 2.2 | 0.000452 | 0 | 2.32 | 0.000551 | -0.0255 | 2.02 | 0.000361 | 0 | 2.13 | 0.00044 | -0.0234 | CFL | Bldg | 2200 | 0.452 | 2020 | 0.361 | 1.05 | 1.22 | -0.0116
CFLBldgPGEEUnExIOU | Com-Iltg-dWatt-CFL_OSbldg | PGE | EUn | Ex | IOU | 2.2 | 0.000497 | 0 | 2.44 | 0.000615 | -0.0155 | 2.02 | 0.000397 | 0 | 2.24 | 0.000491 | -0.0142 | CFL | Bldg | 2200 | 0.497 | 2020 | 0.397 | 1.11 | 1.24 | -0.00703
CFLBldgSCEEUnExIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | EUn | Ex | IOU | 2.2 | 0.000664 | 0 | 2.5 | 0.000843 | -0.0107 | 2.02 | 0.000532 | 0 | 2.3 | 0.000675 | -0.0098 | CFL | Bldg | 2200 | 0.664 | 2020 | 0.532 | 1.14 | 1.27 | -0.00485
CFLBldgSCGEUnExIOU | Com-Iltg-dWatt-CFL_OSbldg | SCG | EUn | Ex | IOU | 2.2 | 0.000673 | 0 | 2.51 | 0.000856 | -0.0103 | 2.02 | 0.000537 | 0 | 2.31 | 0.000684 | -0.00949 | CFL | Bldg | 2200 | 0.673 | 2020 | 0.537 | 1.14 | 1.27 | -0.0047
CFLBldgSDGEUnExIOU | Com-Iltg-dWatt-CFL_OSbldg | SDG | EUn | Ex | IOU | 2.2 | 0.000687 | 0 | 2.5 | 0.000866 | -0.00888 | 2.02 | 0.00055 | 0 | 2.3 | 0.000694 | -0.00817 | CFL | Bldg | 2200 | 0.687 | 2020 | 0.55 | 1.14 | 1.26 | -0.00404
CFLBldgPGEEUnNewCZ01 | Com-Iltg-dWatt-CFL_OSbldg | PGE | EUn | New | CZ01 | 2.02 | 0.000547 | 0 | 2.11 | 0.000642 | -0.0195 | 2.02 | 0.000547 | 0 | 2.11 | 0.000642 | -0.0195 | CFL | Bldg | 2020 | 0.547 | 2020 | 0.547 | 1.04 | 1.17 | -0.00965
CFLBldgPGEEUnNewCZ02 | Com-Iltg-dWatt-CFL_OSbldg | PGE | EUn | New | CZ02 | 2.02 | 0.000359 | 0 | 2.23 | 0.000467 | -0.0157 | 2.02 | 0.000359 | 0 | 2.23 | 0.000467 | -0.0157 | CFL | Bldg | 2020 | 0.359 | 2020 | 0.359 | 1.1 | 1.3 | -0.00777
CFLBldgPGEEUnNewCZ03 | Com-Iltg-dWatt-CFL_OSbldg | PGE | EUn | New | CZ03 | 2.02 | 0.000359 | 0 | 2.19 | 0.000453 | -0.0116 | 2.02 | 0.000359 | 0 | 2.19 | 0.000453 | -0.0116 | CFL | Bldg | 2020 | 0.359 | 2020 | 0.359 | 1.08 | 1.26 | -0.00574
CFLBldgPGEEUnNewCZ04 | Com-Iltg-dWatt-CFL_OSbldg | PGE | EUn | New | CZ04 | 2.02 | 0.000547 | 0 | 2.25 | 0.000686 | -0.0104 | 2.02 | 0.000547 | 0 | 2.25 | 0.000686 | -0.0104 | CFL | Bldg | 2020 | 0.547 | 2020 | 0.547 | 1.11 | 1.25 | -0.00515
CFLBldgSCEEUnNewCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | EUn | New | CZ05 | 2.02 | 0.000547 | 0 | 2.19 | 0.000677 | -0.0132 | 2.02 | 0.000547 | 0 | 2.19 | 0.000677 | -0.0132 | CFL | Bldg | 2020 | 0.547 | 2020 | 0.547 | 1.08 | 1.24 | -0.00653
CFLBldgPGEEUnNewCZ05 | Com-Iltg-dWatt-CFL_OSbldg | PGE | EUn | New | CZ05 | 2.02 | 0.000547 | 0 | 2.2 | 0.000659 | -0.0126 | 2.02 | 0.000547 | 0 | 2.2 | 0.000659 | -0.0126 | CFL | Bldg | 2020 | 0.547 | 2020 | 0.547 | 1.09 | 1.2 | -0.00624
CFLBldgSCEEUnNewCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | EUn | New | CZ06 | 2.02 | 0.000547 | 0 | 2.31 | 0.000694 | -0.00598 | 2.02 | 0.000547 | 0 | 2.31 | 0.000694 | -0.00598 | CFL | Bldg | 2020 | 0.547 | 2020 | 0.547 | 1.14 | 1.27 | -0.00296
CFLBldgSDGEUnNewCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SDG | EUn | New | CZ06 | 2.02 | 0.000547 | 0 | 2.33 | 0.000689 | -0.00656 | 2.02 | 0.000547 | 0 | 2.33 | 0.000689 | -0.00656 | CFL | Bldg | 2020 | 0.547 | 2020 | 0.547 | 1.15 | 1.26 | -0.00325
CFLBldgSDGEUnNewCZ07 | Com-Iltg-dWatt-CFL_OSbldg | SDG | EUn | New | CZ07 | 2.02 | 0.000547 | 0 | 2.3 | 0.000683 | -0.00586 | 2.02 | 0.000547 | 0 | 2.3 | 0.000683 | -0.00586 | CFL | Bldg | 2020 | 0.547 | 2020 | 0.547 | 1.14 | 1.25 | -0.0029
CFLBldgSCEEUnNewCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | EUn | New | CZ08 | 2.02 | 0.000547 | 0 | 2.34 | 0.000704 | -0.00529 | 2.02 | 0.000547 | 0 | 2.34 | 0.000704 | -0.00529 | CFL | Bldg | 2020 | 0.547 | 2020 | 0.547 | 1.16 | 1.29 | -0.00262
CFLBldgSDGEUnNewCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SDG | EUn | New | CZ08 | 2.02 | 0.000547 | 0 | 2.35 | 0.000696 | -0.0058 | 2.02 | 0.000547 | 0 | 2.35 | 0.000696 | -0.0058 | CFL | Bldg | 2020 | 0.547 | 2020 | 0.547 | 1.16 | 1.27 | -0.00287
CFLBldgSCEEUnNewCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | EUn | New | CZ09 | 2.02 | 0.000547 | 0 | 2.35 | 0.000727 | -0.0061 | 2.02 | 0.000547 | 0 | 2.35 | 0.000727 | -0.0061 | CFL | Bldg | 2020 | 0.547 | 2020 | 0.547 | 1.16 | 1.33 | -0.00302
CFLBldgSDGEUnNewCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SDG | EUn | New | CZ10 | 2.02 | 0.000547 | 0 | 2.37 | 0.000718 | -0.00671 | 2.02 | 0.000547 | 0 | 2.37 | 0.000718 | -0.00671 | CFL | Bldg | 2020 | 0.547 | 2020 | 0.547 | 1.17 | 1.31 | -0.00332
CFLBldgSCEEUnNewCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | EUn | New | CZ10 | 2.02 | 0.000547 | 0 | 2.35 | 0.000729 | -0.00646 | 2.02 | 0.000547 | 0 | 2.35 | 0.000729 | -0.00646 | CFL | Bldg | 2020 | 0.547 | 2020 | 0.547 | 1.16 | 1.33 | -0.0032
CFLBldgPGEEUnNewCZ11 | Com-Iltg-dWatt-CFL_OSbldg | PGE | EUn | New | CZ11 | 2.02 | 0.000359 | 0 | 2.29 | 0.000466 | -0.0117 | 2.02 | 0.000359 | 0 | 2.29 | 0.000466 | -0.0117 | CFL | Bldg | 2020 | 0.359 | 2020 | 0.359 | 1.13 | 1.3 | -0.00579
CFLBldgPGEEUnNewCZ12 | Com-Iltg-dWatt-CFL_OSbldg | PGE | EUn | New | CZ12 | 2.02 | 0.000359 | 0 | 2.28 | 0.000467 | -0.0127 | 2.02 | 0.000359 | 0 | 2.28 | 0.000467 | -0.0127 | CFL | Bldg | 2020 | 0.359 | 2020 | 0.359 | 1.13 | 1.3 | -0.00629
CFLBldgPGEEUnNewCZ13 | Com-Iltg-dWatt-CFL_OSbldg | PGE | EUn | New | CZ13 | 2.02 | 0.000359 | 0 | 2.34 | 0.000486 | -0.0132 | 2.02 | 0.000359 | 0 | 2.34 | 0.000486 | -0.0132 | CFL | Bldg | 2020 | 0.359 | 2020 | 0.359 | 1.16 | 1.35 | -0.00653
CFLBldgSCEEUnNewCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | EUn | New | CZ13 | 2.02 | 0.000359 | 0 | 2.37 | 0.000516 | -0.0132 | 2.02 | 0.000359 | 0 | 2.37 | 0.000516 | -0.0132 | CFL | Bldg | 2020 | 0.359 | 2020 | 0.359 | 1.17 | 1.44 | -0.00653
CFLBldgSCEEUnNewCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | EUn | New | CZ14 | 2.02 | 0.000547 | 0 | 2.23 | 0.000666 | -0.0108 | 2.02 | 0.000547 | 0 | 2.23 | 0.000666 | -0.0108 | CFL | Bldg | 2020 | 0.547 | 2020 | 0.547 | 1.1 | 1.22 | -0.00535
CFLBldgSDGEUnNewCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SDG | EUn | New | CZ14 | 2.02 | 0.000547 | 0 | 2.27 | 0.000664 | -0.0111 | 2.02 | 0.000547 | 0 | 2.27 | 0.000664 | -0.0111 | CFL | Bldg | 2020 | 0.547 | 2020 | 0.547 | 1.12 | 1.21 | -0.0055
CFLBldgSCEEUnNewCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | EUn | New | CZ15 | 2.02 | 0.000547 | 0 | 2.49 | 0.000741 | -0.00277 | 2.02 | 0.000547 | 0 | 2.49 | 0.000741 | -0.00277 | CFL | Bldg | 2020 | 0.547 | 2020 | 0.547 | 1.23 | 1.35 | -0.00137
CFLBldgSDGEUnNewCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SDG | EUn | New | CZ15 | 2.02 | 0.000547 | 0 | 2.47 | 0.000724 | -0.00309 | 2.02 | 0.000547 | 0 | 2.47 | 0.000724 | -0.00309 | CFL | Bldg | 2020 | 0.547 | 2020 | 0.547 | 1.22 | 1.32 | -0.00153
CFLBldgSCEEUnNewCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | EUn | New | CZ16 | 2.02 | 0.000359 | 0 | 2.13 | 0.000464 | -0.0236 | 2.02 | 0.000359 | 0 | 2.13 | 0.000464 | -0.0236 | CFL | Bldg | 2020 | 0.359 | 2020 | 0.359 | 1.05 | 1.29 | -0.0117
CFLBldgPGEEUnNewCZ16 | Com-Iltg-dWatt-CFL_OSbldg | PGE | EUn | New | CZ16 | 2.02 | 0.000359 | 0 | 2.15 | 0.000448 | -0.021 | 2.02 | 0.000359 | 0 | 2.15 | 0.000448 | -0.021 | CFL | Bldg | 2020 | 0.359 | 2020 | 0.359 | 1.06 | 1.25 | -0.0104
CFLBldgSDGEUnNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SDG | EUn | New | IOU | 2.02 | 0.000547 | 0 | 2.32 | 0.000691 | -0.00609 | 2.02 | 0.000547 | 0 | 2.32 | 0.000691 | -0.00609 | CFL | Bldg | 2020 | 0.547 | 2020 | 0.547 | 1.15 | 1.26 | -0.00301
CFLBldgSCGEUnNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SCG | EUn | New | IOU | 2.02 | 0.000547 | 0 | 2.35 | 0.000699 | -0.0064 | 2.02 | 0.000547 | 0 | 2.35 | 0.000699 | -0.0064 | CFL | Bldg | 2020 | 0.547 | 2020 | 0.547 | 1.16 | 1.28 | -0.00317
CFLBldgPGEEUnNewIOU | Com-Iltg-dWatt-CFL_OSbldg | PGE | EUn | New | IOU | 2.02 | 0.000415 | 0 | 2.31 | 0.000564 | -0.0133 | 2.02 | 0.000415 | 0 | 2.31 | 0.000564 | -0.0133 | CFL | Bldg | 2020 | 0.415 | 2020 | 0.415 | 1.14 | 1.36 | -0.00658
CFLBldgSCEEUnNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | EUn | New | IOU | 2.02 | 0.000547 | 0 | 2.35 | 0.000699 | -0.00642 | 2.02 | 0.000547 | 0 | 2.35 | 0.000699 | -0.00642 | CFL | Bldg | 2020 | 0.547 | 2020 | 0.547 | 1.16 | 1.28 | -0.00318
CFLBldgPGEGroExCZ01 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Gro | Ex | CZ01 | 4.94 | 0.000788 | 0 | 3.97 | 0.000735 | -0.0868 | 4.85 | 0.000774 | 0 | 3.9 | 0.000722 | -0.0854 | CFL | Bldg | 4940 | 0.788 | 4850 | 0.774 | 0.804 | 0.933 | -0.0176
CFLBldgPGEGroExCZ02 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Gro | Ex | CZ02 | 4.94 | 0.000788 | 0 | 4.47 | 0.00106 | -0.0676 | 4.85 | 0.000774 | 0 | 4.38 | 0.00104 | -0.0664 | CFL | Bldg | 4940 | 0.788 | 4850 | 0.774 | 0.903 | 1.34 | -0.0137
CFLBldgPGEGroExCZ03 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Gro | Ex | CZ03 | 4.94 | 0.000788 | 0 | 4.26 | 0.000995 | -0.077 | 4.85 | 0.000774 | 0 | 4.19 | 0.000977 | -0.0757 | CFL | Bldg | 4940 | 0.788 | 4850 | 0.774 | 0.864 | 1.26 | -0.0156
CFLBldgPGEGroExCZ04 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Gro | Ex | CZ04 | 4.94 | 0.000788 | 0 | 4.55 | 0.000999 | -0.0651 | 4.85 | 0.000774 | 0 | 4.47 | 0.000983 | -0.064 | CFL | Bldg | 4940 | 0.788 | 4850 | 0.774 | 0.922 | 1.27 | -0.0132
CFLBldgSCGGroExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCG | Gro | Ex | CZ05 | 4.93 | 0.000788 | 0 | 4.73 | 0.000986 | -0.0859 | 4.85 | 0.000774 | 0 | 4.65 | 0.000968 | -0.0844 | CFL | Bldg | 4930 | 0.788 | 4850 | 0.774 | 0.959 | 1.25 | -0.0174
CFLBldgPGEGroExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Gro | Ex | CZ05 | 4.94 | 0.000788 | 0 | 4.73 | 0.000986 | -0.0859 | 4.85 | 0.000774 | 0 | 4.65 | 0.000968 | -0.0844 | CFL | Bldg | 4940 | 0.788 | 4850 | 0.774 | 0.959 | 1.25 | -0.0174
CFLBldgSCEGroExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Gro | Ex | CZ05 | 4.93 | 0.000788 | 0 | 4.73 | 0.000986 | -0.0859 | 4.85 | 0.000774 | 0 | 4.65 | 0.000968 | -0.0844 | CFL | Bldg | 4930 | 0.788 | 4850 | 0.774 | 0.959 | 1.25 | -0.0174
CFLBldgSCEGroExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Gro | Ex | CZ06 | 4.93 | 0.000788 | 0 | 4.92 | 0.000973 | -0.0676 | 4.85 | 0.000774 | 0 | 4.84 | 0.000955 | -0.0664 | CFL | Bldg | 4930 | 0.788 | 4850 | 0.774 | 0.998 | 1.23 | -0.0137
CFLBldgSDGGroExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Gro | Ex | CZ06 | 4.93 | 0.000788 | 0 | 4.92 | 0.000972 | -0.0676 | 4.85 | 0.000774 | 0 | 4.84 | 0.000955 | -0.0664 | CFL | Bldg | 4930 | 0.788 | 4850 | 0.774 | 0.998 | 1.23 | -0.0137
CFLBldgSCGGroExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCG | Gro | Ex | CZ06 | 4.93 | 0.000788 | 0 | 4.92 | 0.000973 | -0.0676 | 4.85 | 0.000774 | 0 | 4.84 | 0.000955 | -0.0664 | CFL | Bldg | 4930 | 0.788 | 4850 | 0.774 | 0.998 | 1.23 | -0.0137
CFLBldgSDGGroExCZ07 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Gro | Ex | CZ07 | 4.93 | 0.000788 | 0 | 4.85 | 0.000957 | -0.0725 | 4.85 | 0.000774 | 0 | 4.77 | 0.000941 | -0.0713 | CFL | Bldg | 4930 | 0.788 | 4850 | 0.774 | 0.984 | 1.22 | -0.0147
CFLBldgSCGGroExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCG | Gro | Ex | CZ08 | 4.93 | 0.000788 | 0 | 5.03 | 0.000999 | -0.0617 | 4.85 | 0.000774 | 0 | 4.95 | 0.000981 | -0.0606 | CFL | Bldg | 4930 | 0.788 | 4850 | 0.774 | 1.02 | 1.27 | -0.0125
CFLBldgSDGGroExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Gro | Ex | CZ08 | 4.93 | 0.000788 | 0 | 5.03 | 0.000998 | -0.0617 | 4.85 | 0.000774 | 0 | 4.95 | 0.000981 | -0.0606 | CFL | Bldg | 4930 | 0.788 | 4850 | 0.774 | 1.02 | 1.27 | -0.0125
CFLBldgSCEGroExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Gro | Ex | CZ08 | 4.93 | 0.000788 | 0 | 5.03 | 0.000999 | -0.0617 | 4.85 | 0.000774 | 0 | 4.95 | 0.000981 | -0.0606 | CFL | Bldg | 4930 | 0.788 | 4850 | 0.774 | 1.02 | 1.27 | -0.0125
CFLBldgSCEGroExCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Gro | Ex | CZ09 | 4.93 | 0.000788 | 0 | 5.17 | 0.00103 | -0.0612 | 4.85 | 0.000774 | 0 | 5.09 | 0.00101 | -0.0601 | CFL | Bldg | 4930 | 0.788 | 4850 | 0.774 | 1.05 | 1.3 | -0.0124
CFLBldgSCGGroExCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCG | Gro | Ex | CZ09 | 4.93 | 0.000788 | 0 | 5.17 | 0.00103 | -0.0612 | 4.85 | 0.000774 | 0 | 5.09 | 0.00101 | -0.0601 | CFL | Bldg | 4930 | 0.788 | 4850 | 0.774 | 1.05 | 1.3 | -0.0124
CFLBldgSDGGroExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Gro | Ex | CZ10 | 4.93 | 0.000788 | 0 | 5.12 | 0.00105 | -0.0582 | 4.85 | 0.000774 | 0 | 5.04 | 0.00103 | -0.0572 | CFL | Bldg | 4930 | 0.788 | 4850 | 0.774 | 1.04 | 1.33 | -0.0118
CFLBldgSCEGroExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Gro | Ex | CZ10 | 4.93 | 0.000787 | 0 | 5.12 | 0.00105 | -0.0582 | 4.85 | 0.000774 | 0 | 5.04 | 0.00103 | -0.0572 | CFL | Bldg | 4930 | 0.787 | 4850 | 0.774 | 1.04 | 1.33 | -0.0118
CFLBldgSCGGroExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCG | Gro | Ex | CZ10 | 4.93 | 0.000787 | 0 | 5.12 | 0.00105 | -0.0582 | 4.85 | 0.000774 | 0 | 5.04 | 0.00103 | -0.0572 | CFL | Bldg | 4930 | 0.787 | 4850 | 0.774 | 1.04 | 1.33 | -0.0118
CFLBldgPGEGroExCZ11 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Gro | Ex | CZ11 | 4.93 | 0.000788 | 0 | 4.83 | 0.00105 | -0.0552 | 4.85 | 0.000774 | 0 | 4.75 | 0.00103 | -0.0543 | CFL | Bldg | 4930 | 0.788 | 4850 | 0.774 | 0.979 | 1.33 | -0.0112
CFLBldgPGEGroExCZ12 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Gro | Ex | CZ12 | 4.93 | 0.000788 | 0 | 4.69 | 0.00104 | -0.0602 | 4.85 | 0.000774 | 0 | 4.62 | 0.00102 | -0.0592 | CFL | Bldg | 4930 | 0.788 | 4850 | 0.774 | 0.953 | 1.32 | -0.0122
CFLBldgSCGGroExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCG | Gro | Ex | CZ13 | 4.93 | 0.000788 | 0 | 5.17 | 0.00104 | -0.0587 | 4.85 | 0.000774 | 0 | 5.09 | 0.00102 | -0.0577 | CFL | Bldg | 4930 | 0.788 | 4850 | 0.774 | 1.05 | 1.32 | -0.0119
CFLBldgPGEGroExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Gro | Ex | CZ13 | 4.93 | 0.000788 | 0 | 5.17 | 0.00104 | -0.0587 | 4.85 | 0.000774 | 0 | 5.09 | 0.00102 | -0.0577 | CFL | Bldg | 4930 | 0.788 | 4850 | 0.774 | 1.05 | 1.32 | -0.0119
CFLBldgSCEGroExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Gro | Ex | CZ13 | 4.93 | 0.000788 | 0 | 5.17 | 0.00104 | -0.0587 | 4.85 | 0.000774 | 0 | 5.09 | 0.00102 | -0.0577 | CFL | Bldg | 4930 | 0.788 | 4850 | 0.774 | 1.05 | 1.32 | -0.0119
CFLBldgSCGGroExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCG | Gro | Ex | CZ14 | 4.93 | 0.000787 | 0 | 5.1 | 0.00107 | -0.0587 | 4.85 | 0.000774 | 0 | 5.02 | 0.00105 | -0.0577 | CFL | Bldg | 4930 | 0.787 | 4850 | 0.774 | 1.04 | 1.36 | -0.0119
CFLBldgSCEGroExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Gro | Ex | CZ14 | 4.93 | 0.000787 | 0 | 5.1 | 0.00107 | -0.0587 | 4.85 | 0.000774 | 0 | 5.02 | 0.00105 | -0.0577 | CFL | Bldg | 4930 | 0.787 | 4850 | 0.774 | 1.04 | 1.36 | -0.0119
CFLBldgSDGGroExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Gro | Ex | CZ14 | 4.93 | 0.000788 | 0 | 5.1 | 0.00107 | -0.0587 | 4.85 | 0.000774 | 0 | 5.02 | 0.00105 | -0.0577 | CFL | Bldg | 4930 | 0.788 | 4850 | 0.774 | 1.04 | 1.36 | -0.0119
CFLBldgSCGGroExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCG | Gro | Ex | CZ15 | 4.93 | 0.000787 | 0 | 5.52 | 0.00105 | -0.0337 | 4.85 | 0.000774 | 0 | 5.43 | 0.00103 | -0.0332 | CFL | Bldg | 4930 | 0.787 | 4850 | 0.774 | 1.12 | 1.33 | -0.00685
CFLBldgSCEGroExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Gro | Ex | CZ15 | 4.93 | 0.000787 | 0 | 5.52 | 0.00105 | -0.0337 | 4.85 | 0.000774 | 0 | 5.43 | 0.00103 | -0.0332 | CFL | Bldg | 4930 | 0.787 | 4850 | 0.774 | 1.12 | 1.33 | -0.00685
CFLBldgSDGGroExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Gro | Ex | CZ15 | 4.93 | 0.000788 | 0 | 5.52 | 0.00105 | -0.0337 | 4.85 | 0.000774 | 0 | 5.43 | 0.00103 | -0.0332 | CFL | Bldg | 4930 | 0.788 | 4850 | 0.774 | 1.12 | 1.33 | -0.00685
CFLBldgPGEGroExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Gro | Ex | CZ16 | 4.93 | 0.000788 | 0 | 4.68 | 0.000993 | -0.0804 | 4.85 | 0.000774 | 0 | 4.61 | 0.000975 | -0.0791 | CFL | Bldg | 4930 | 0.788 | 4850 | 0.774 | 0.951 | 1.26 | -0.0163
CFLBldgSCEGroExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Gro | Ex | CZ16 | 4.93 | 0.000787 | 0 | 4.68 | 0.000992 | -0.0804 | 4.85 | 0.000774 | 0 | 4.61 | 0.000975 | -0.0791 | CFL | Bldg | 4930 | 0.787 | 4850 | 0.774 | 0.951 | 1.26 | -0.0163
CFLBldgSCGGroExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCG | Gro | Ex | CZ16 | 4.93 | 0.000787 | 0 | 4.68 | 0.000992 | -0.0804 | 4.85 | 0.000774 | 0 | 4.61 | 0.000975 | -0.0791 | CFL | Bldg | 4930 | 0.787 | 4850 | 0.774 | 0.951 | 1.26 | -0.0163
CFLBldgSDGGroExIOU | Com-Iltg-dWatt-CFL_OSbldg | SDG | Gro | Ex | IOU | 4.93 | 0.000788 | 0 | 4.94 | 0.000984 | -0.068 | 4.85 | 0.000774 | 0 | 4.85 | 0.000967 | -0.0668 | CFL | Bldg | 4930 | 0.788 | 4850 | 0.774 | 1 | 1.25 | -0.0138
CFLBldgSCEGroExIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | Gro | Ex | IOU | 4.93 | 0.000788 | 0 | 5.06 | 0.00101 | -0.0615 | 4.85 | 0.000774 | 0 | 4.98 | 0.000996 | -0.0604 | CFL | Bldg | 4930 | 0.788 | 4850 | 0.774 | 1.03 | 1.29 | -0.0125
CFLBldgSCGGroExIOU | Com-Iltg-dWatt-CFL_OSbldg | SCG | Gro | Ex | IOU | 4.93 | 0.000788 | 0 | 5.08 | 0.00102 | -0.0616 | 4.85 | 0.000774 | 0 | 4.99 | 0.000997 | -0.0605 | CFL | Bldg | 4930 | 0.788 | 4850 | 0.774 | 1.03 | 1.29 | -0.0125
CFLBldgPGEGroExIOU | Com-Iltg-dWatt-CFL_OSbldg | PGE | Gro | Ex | IOU | 4.93 | 0.000788 | 0 | 4.62 | 0.00102 | -0.0667 | 4.85 | 0.000774 | 0 | 4.54 | 0.001 | -0.0656 | CFL | Bldg | 4930 | 0.788 | 4850 | 0.774 | 0.936 | 1.29 | -0.0135
CFLBldgPGEGroNewCZ01 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Gro | New | CZ01 | 4.85 | 0.000772 | 0 | 4.02 | 0.000909 | -0.0907 | 4.85 | 0.000772 | 0 | 4.02 | 0.000909 | -0.0907 | CFL | Bldg | 4850 | 0.772 | 4850 | 0.772 | 0.829 | 1.18 | -0.0187
CFLBldgPGEGroNewCZ02 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Gro | New | CZ02 | 4.85 | 0.000772 | 0 | 4.56 | 0.00107 | -0.0664 | 4.85 | 0.000772 | 0 | 4.56 | 0.00107 | -0.0664 | CFL | Bldg | 4850 | 0.772 | 4850 | 0.772 | 0.94 | 1.39 | -0.0137
CFLBldgPGEGroNewCZ03 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Gro | New | CZ03 | 4.85 | 0.000772 | 0 | 4.33 | 0.00101 | -0.0747 | 4.85 | 0.000772 | 0 | 4.33 | 0.00101 | -0.0747 | CFL | Bldg | 4850 | 0.772 | 4850 | 0.772 | 0.893 | 1.31 | -0.0154
CFLBldgPGEGroNewCZ04 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Gro | New | CZ04 | 4.85 | 0.000772 | 0 | 4.69 | 0.00101 | -0.0611 | 4.85 | 0.000772 | 0 | 4.69 | 0.00101 | -0.0611 | CFL | Bldg | 4850 | 0.772 | 4850 | 0.772 | 0.967 | 1.31 | -0.0126
CFLBldgSCEGroNewCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Gro | New | CZ05 | 4.85 | 0.000772 | 0 | 4.76 | 0.000975 | -0.081 | 4.85 | 0.000772 | 0 | 4.76 | 0.000975 | -0.081 | CFL | Bldg | 4850 | 0.772 | 4850 | 0.772 | 0.981 | 1.26 | -0.0167
CFLBldgPGEGroNewCZ05 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Gro | New | CZ05 | 4.85 | 0.000772 | 0 | 4.32 | 0.000976 | -0.0742 | 4.85 | 0.000772 | 0 | 4.32 | 0.000976 | -0.0742 | CFL | Bldg | 4850 | 0.772 | 4850 | 0.772 | 0.891 | 1.26 | -0.0153
CFLBldgSDGGroNewCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Gro | New | CZ06 | 4.85 | 0.000772 | 0 | 5.07 | 0.000973 | -0.0553 | 4.85 | 0.000772 | 0 | 5.07 | 0.000973 | -0.0553 | CFL | Bldg | 4850 | 0.772 | 4850 | 0.772 | 1.05 | 1.26 | -0.0114
CFLBldgSCEGroNewCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Gro | New | CZ06 | 4.85 | 0.000772 | 0 | 5.11 | 0.00098 | -0.0577 | 4.85 | 0.000772 | 0 | 5.11 | 0.00098 | -0.0577 | CFL | Bldg | 4850 | 0.772 | 4850 | 0.772 | 1.05 | 1.27 | -0.0119
CFLBldgSDGGroNewCZ07 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Gro | New | CZ07 | 4.85 | 0.000772 | 0 | 5.02 | 0.00095 | -0.0577 | 4.85 | 0.000772 | 0 | 5.02 | 0.00095 | -0.0577 | CFL | Bldg | 4850 | 0.772 | 4850 | 0.772 | 1.04 | 1.23 | -0.0119
CFLBldgSDGGroNewCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Gro | New | CZ08 | 4.85 | 0.000772 | 0 | 5.13 | 0.00099 | -0.0483 | 4.85 | 0.000772 | 0 | 5.13 | 0.00099 | -0.0483 | CFL | Bldg | 4850 | 0.772 | 4850 | 0.772 | 1.06 | 1.28 | -0.00996
CFLBldgSCEGroNewCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Gro | New | CZ08 | 4.85 | 0.000772 | 0 | 5.17 | 0.000997 | -0.0504 | 4.85 | 0.000772 | 0 | 5.17 | 0.000997 | -0.0504 | CFL | Bldg | 4850 | 0.772 | 4850 | 0.772 | 1.07 | 1.29 | -0.0104
CFLBldgSCEGroNewCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Gro | New | CZ09 | 4.85 | 0.000772 | 0 | 5.19 | 0.00105 | -0.0533 | 4.85 | 0.000772 | 0 | 5.19 | 0.00105 | -0.0533 | CFL | Bldg | 4850 | 0.772 | 4850 | 0.772 | 1.07 | 1.36 | -0.011
CFLBldgSDGGroNewCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Gro | New | CZ10 | 4.85 | 0.000772 | 0 | 5.19 | 0.00109 | -0.0504 | 4.85 | 0.000772 | 0 | 5.19 | 0.00109 | -0.0504 | CFL | Bldg | 4850 | 0.772 | 4850 | 0.772 | 1.07 | 1.41 | -0.0104
CFLBldgSCEGroNewCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Gro | New | CZ10 | 4.85 | 0.000772 | 0 | 5.23 | 0.0011 | -0.0524 | 4.85 | 0.000772 | 0 | 5.23 | 0.0011 | -0.0524 | CFL | Bldg | 4850 | 0.772 | 4850 | 0.772 | 1.08 | 1.42 | -0.0108
CFLBldgPGEGroNewCZ11 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Gro | New | CZ11 | 4.85 | 0.000772 | 0 | 4.91 | 0.00108 | -0.0529 | 4.85 | 0.000772 | 0 | 4.91 | 0.00108 | -0.0529 | CFL | Bldg | 4850 | 0.772 | 4850 | 0.772 | 1.01 | 1.4 | -0.0109
CFLBldgPGEGroNewCZ12 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Gro | New | CZ12 | 4.85 | 0.000772 | 0 | 4.81 | 0.00108 | -0.0587 | 4.85 | 0.000772 | 0 | 4.81 | 0.00108 | -0.0587 | CFL | Bldg | 4850 | 0.772 | 4850 | 0.772 | 0.992 | 1.4 | -0.0121
CFLBldgSCEGroNewCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Gro | New | CZ13 | 4.85 | 0.000772 | 0 | 5.24 | 0.00106 | -0.0548 | 4.85 | 0.000772 | 0 | 5.24 | 0.00106 | -0.0548 | CFL | Bldg | 4850 | 0.772 | 4850 | 0.772 | 1.08 | 1.37 | -0.0113
CFLBldgPGEGroNewCZ13 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Gro | New | CZ13 | 4.85 | 0.000772 | 0 | 4.96 | 0.00105 | -0.05 | 4.85 | 0.000772 | 0 | 4.96 | 0.00105 | -0.05 | CFL | Bldg | 4850 | 0.772 | 4850 | 0.772 | 1.02 | 1.36 | -0.0103
CFLBldgSDGGroNewCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Gro | New | CZ14 | 4.85 | 0.000772 | 0 | 5.2 | 0.00106 | -0.0553 | 4.85 | 0.000772 | 0 | 5.2 | 0.00106 | -0.0553 | CFL | Bldg | 4850 | 0.772 | 4850 | 0.772 | 1.07 | 1.37 | -0.0114
CFLBldgSCEGroNewCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Gro | New | CZ14 | 4.85 | 0.000772 | 0 | 5.25 | 0.00107 | -0.0577 | 4.85 | 0.000772 | 0 | 5.25 | 0.00107 | -0.0577 | CFL | Bldg | 4850 | 0.772 | 4850 | 0.772 | 1.08 | 1.39 | -0.0119
CFLBldgSDGGroNewCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Gro | New | CZ15 | 4.85 | 0.000772 | 0 | 5.61 | 0.00108 | -0.0286 | 4.85 | 0.000772 | 0 | 5.61 | 0.00108 | -0.0286 | CFL | Bldg | 4850 | 0.772 | 4850 | 0.772 | 1.16 | 1.4 | -0.0059
CFLBldgSCEGroNewCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Gro | New | CZ15 | 4.85 | 0.000772 | 0 | 5.65 | 0.00109 | -0.0298 | 4.85 | 0.000772 | 0 | 5.65 | 0.00109 | -0.0298 | CFL | Bldg | 4850 | 0.772 | 4850 | 0.772 | 1.16 | 1.41 | -0.00614
CFLBldgPGEGroNewCZ16 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Gro | New | CZ16 | 4.85 | 0.000772 | 0 | 4.38 | 0.000982 | -0.0689 | 4.85 | 0.000772 | 0 | 4.38 | 0.000982 | -0.0689 | CFL | Bldg | 4850 | 0.772 | 4850 | 0.772 | 0.903 | 1.27 | -0.0142
CFLBldgSCEGroNewCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Gro | New | CZ16 | 4.85 | 0.000772 | 0 | 4.76 | 0.000994 | -0.0752 | 4.85 | 0.000772 | 0 | 4.76 | 0.000994 | -0.0752 | CFL | Bldg | 4850 | 0.772 | 4850 | 0.772 | 0.981 | 1.29 | -0.0155
CFLBldgSDGGroNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SDG | Gro | New | IOU | 4.85 | 0.000772 | 0 | 5.07 | 0.000991 | -0.0553 | 4.85 | 0.000772 | 0 | 5.07 | 0.000991 | -0.0553 | CFL | Bldg | 4850 | 0.772 | 4850 | 0.772 | 1.05 | 1.28 | -0.0114
CFLBldgSCEGroNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | Gro | New | IOU | 4.85 | 0.000772 | 0 | 5.17 | 0.00104 | -0.05 | 4.85 | 0.000772 | 0 | 5.17 | 0.00104 | -0.05 | CFL | Bldg | 4850 | 0.772 | 4850 | 0.772 | 1.07 | 1.35 | -0.0103
CFLBldgSCGGroNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SCG | Gro | New | IOU | 4.85 | 0.000772 | 0 | 5.17 | 0.00103 | -0.05 | 4.85 | 0.000772 | 0 | 5.17 | 0.00103 | -0.05 | CFL | Bldg | 4850 | 0.772 | 4850 | 0.772 | 1.07 | 1.33 | -0.0103
CFLBldgPGEGroNewIOU | Com-Iltg-dWatt-CFL_OSbldg | PGE | Gro | New | IOU | 4.85 | 0.000772 | 0 | 5.17 | 0.00105 | -0.0585 | 4.85 | 0.000772 | 0 | 5.17 | 0.00105 | -0.0585 | CFL | Bldg | 4850 | 0.772 | 4850 | 0.772 | 1.07 | 1.36 | -0.0121
CFLBldgPGEHspExCZ01 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Hsp | Ex | CZ01 | 5.39 | 0.000837 | 0 | 5.77 | 0.000959 | -0.0473 | 5.34 | 0.000827 | 0 | 5.72 | 0.000948 | -0.0469 | CFL | Bldg | 5390 | 0.837 | 5340 | 0.827 | 1.07 | 1.15 | -0.00878
CFLBldgPGEHspExCZ02 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Hsp | Ex | CZ02 | 5.39 | 0.000836 | 0 | 5.93 | 0.00103 | -0.037 | 5.34 | 0.000827 | 0 | 5.88 | 0.00102 | -0.0366 | CFL | Bldg | 5390 | 0.836 | 5340 | 0.827 | 1.1 | 1.23 | -0.00685
CFLBldgPGEHspExCZ03 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Hsp | Ex | CZ03 | 5.39 | 0.000837 | 0 | 5.96 | 0.001 | -0.0351 | 5.34 | 0.000827 | 0 | 5.91 | 0.000992 | -0.0348 | CFL | Bldg | 5390 | 0.837 | 5340 | 0.827 | 1.11 | 1.2 | -0.00652
CFLBldgPGEHspExCZ04 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Hsp | Ex | CZ04 | 5.39 | 0.000836 | 0 | 5.97 | 0.00102 | -0.0333 | 5.34 | 0.000827 | 0 | 5.91 | 0.00101 | -0.033 | CFL | Bldg | 5390 | 0.836 | 5340 | 0.827 | 1.11 | 1.22 | -0.00618
CFLBldgSCEHspExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Hsp | Ex | CZ05 | 5.39 | 0.000837 | 0 | 6.04 | 0.00102 | -0.0379 | 5.34 | 0.000827 | 0 | 5.99 | 0.00101 | -0.0376 | CFL | Bldg | 5390 | 0.837 | 5340 | 0.827 | 1.12 | 1.22 | -0.00704
CFLBldgPGEHspExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Hsp | Ex | CZ05 | 5.39 | 0.000836 | 0 | 6.04 | 0.00102 | -0.0379 | 5.34 | 0.000827 | 0 | 5.99 | 0.00101 | -0.0376 | CFL | Bldg | 5390 | 0.836 | 5340 | 0.827 | 1.12 | 1.22 | -0.00704
CFLBldgSCGHspExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCG | Hsp | Ex | CZ05 | 5.39 | 0.000837 | 0 | 6.04 | 0.00102 | -0.0379 | 5.34 | 0.000827 | 0 | 5.99 | 0.00101 | -0.0376 | CFL | Bldg | 5390 | 0.837 | 5340 | 0.827 | 1.12 | 1.22 | -0.00704
CFLBldgSCEHspExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Hsp | Ex | CZ06 | 5.39 | 0.000837 | 0 | 6.16 | 0.00104 | -0.0289 | 5.34 | 0.000827 | 0 | 6.1 | 0.00102 | -0.0287 | CFL | Bldg | 5390 | 0.837 | 5340 | 0.827 | 1.14 | 1.23 | -0.00537
CFLBldgSCGHspExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCG | Hsp | Ex | CZ06 | 5.39 | 0.000837 | 0 | 6.16 | 0.00104 | -0.0289 | 5.34 | 0.000827 | 0 | 6.1 | 0.00102 | -0.0287 | CFL | Bldg | 5390 | 0.837 | 5340 | 0.827 | 1.14 | 1.23 | -0.00537
CFLBldgSDGHspExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Hsp | Ex | CZ06 | 5.39 | 0.000837 | 0 | 6.16 | 0.00104 | -0.0289 | 5.34 | 0.000827 | 0 | 6.1 | 0.00102 | -0.0287 | CFL | Bldg | 5390 | 0.837 | 5340 | 0.827 | 1.14 | 1.23 | -0.00537
CFLBldgSDGHspExCZ07 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Hsp | Ex | CZ07 | 5.39 | 0.000837 | 0 | 6.16 | 0.00103 | -0.0266 | 5.34 | 0.000827 | 0 | 6.1 | 0.00101 | -0.0264 | CFL | Bldg | 5390 | 0.837 | 5340 | 0.827 | 1.14 | 1.22 | -0.00494
CFLBldgSCGHspExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCG | Hsp | Ex | CZ08 | 5.39 | 0.000837 | 0 | 6.2 | 0.00103 | -0.0285 | 5.34 | 0.000827 | 0 | 6.14 | 0.00102 | -0.0282 | CFL | Bldg | 5390 | 0.837 | 5340 | 0.827 | 1.15 | 1.23 | -0.00528
CFLBldgSCEHspExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Hsp | Ex | CZ08 | 5.39 | 0.000837 | 0 | 6.2 | 0.00103 | -0.0285 | 5.34 | 0.000827 | 0 | 6.14 | 0.00102 | -0.0282 | CFL | Bldg | 5390 | 0.837 | 5340 | 0.827 | 1.15 | 1.23 | -0.00528
CFLBldgSDGHspExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Hsp | Ex | CZ08 | 5.39 | 0.000837 | 0 | 6.2 | 0.00103 | -0.0285 | 5.34 | 0.000827 | 0 | 6.14 | 0.00102 | -0.0282 | CFL | Bldg | 5390 | 0.837 | 5340 | 0.827 | 1.15 | 1.23 | -0.00528
CFLBldgSCEHspExCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Hsp | Ex | CZ09 | 5.39 | 0.000836 | 0 | 6.3 | 0.00107 | -0.0282 | 5.34 | 0.000827 | 0 | 6.24 | 0.00106 | -0.028 | CFL | Bldg | 5390 | 0.836 | 5340 | 0.827 | 1.17 | 1.28 | -0.00524
CFLBldgSCGHspExCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCG | Hsp | Ex | CZ09 | 5.39 | 0.000837 | 0 | 6.3 | 0.00107 | -0.0282 | 5.34 | 0.000827 | 0 | 6.24 | 0.00106 | -0.028 | CFL | Bldg | 5390 | 0.837 | 5340 | 0.827 | 1.17 | 1.28 | -0.00524
CFLBldgSDGHspExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Hsp | Ex | CZ10 | 5.39 | 0.000837 | 0 | 6.19 | 0.00106 | -0.0305 | 5.34 | 0.000827 | 0 | 6.13 | 0.00105 | -0.0302 | CFL | Bldg | 5390 | 0.837 | 5340 | 0.827 | 1.15 | 1.27 | -0.00566
CFLBldgSCEHspExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Hsp | Ex | CZ10 | 5.39 | 0.000836 | 0 | 6.19 | 0.00106 | -0.0305 | 5.34 | 0.000827 | 0 | 6.13 | 0.00105 | -0.0302 | CFL | Bldg | 5390 | 0.836 | 5340 | 0.827 | 1.15 | 1.27 | -0.00566
CFLBldgSCGHspExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCG | Hsp | Ex | CZ10 | 5.39 | 0.000836 | 0 | 6.19 | 0.00106 | -0.0305 | 5.34 | 0.000827 | 0 | 6.13 | 0.00105 | -0.0302 | CFL | Bldg | 5390 | 0.836 | 5340 | 0.827 | 1.15 | 1.27 | -0.00566
CFLBldgPGEHspExCZ11 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Hsp | Ex | CZ11 | 5.39 | 0.000836 | 0 | 5.99 | 0.00104 | -0.0348 | 5.34 | 0.000827 | 0 | 5.94 | 0.00102 | -0.0345 | CFL | Bldg | 5390 | 0.836 | 5340 | 0.827 | 1.11 | 1.23 | -0.00646
CFLBldgPGEHspExCZ12 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Hsp | Ex | CZ12 | 5.39 | 0.000836 | 0 | 5.98 | 0.00103 | -0.0338 | 5.34 | 0.000827 | 0 | 5.92 | 0.00102 | -0.0335 | CFL | Bldg | 5390 | 0.836 | 5340 | 0.827 | 1.11 | 1.23 | -0.00627
CFLBldgPGEHspExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Hsp | Ex | CZ13 | 5.39 | 0.000836 | 0 | 6.1 | 0.00106 | -0.0346 | 5.34 | 0.000827 | 0 | 6.04 | 0.00104 | -0.0343 | CFL | Bldg | 5390 | 0.836 | 5340 | 0.827 | 1.13 | 1.26 | -0.00642
CFLBldgSCGHspExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCG | Hsp | Ex | CZ13 | 5.39 | 0.000836 | 0 | 6.1 | 0.00106 | -0.0346 | 5.34 | 0.000827 | 0 | 6.04 | 0.00104 | -0.0343 | CFL | Bldg | 5390 | 0.836 | 5340 | 0.827 | 1.13 | 1.26 | -0.00642
CFLBldgSCEHspExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Hsp | Ex | CZ13 | 5.39 | 0.000836 | 0 | 6.1 | 0.00106 | -0.0346 | 5.34 | 0.000827 | 0 | 6.04 | 0.00104 | -0.0343 | CFL | Bldg | 5390 | 0.836 | 5340 | 0.827 | 1.13 | 1.26 | -0.00642
CFLBldgSDGHspExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Hsp | Ex | CZ14 | 5.39 | 0.000836 | 0 | 6.11 | 0.00105 | -0.0373 | 5.34 | 0.000827 | 0 | 6.05 | 0.00104 | -0.037 | CFL | Bldg | 5390 | 0.836 | 5340 | 0.827 | 1.13 | 1.26 | -0.00693
CFLBldgSCGHspExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCG | Hsp | Ex | CZ14 | 5.39 | 0.000836 | 0 | 6.11 | 0.00105 | -0.0373 | 5.34 | 0.000827 | 0 | 6.05 | 0.00104 | -0.037 | CFL | Bldg | 5390 | 0.836 | 5340 | 0.827 | 1.13 | 1.26 | -0.00693
CFLBldgSCEHspExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Hsp | Ex | CZ14 | 5.39 | 0.000836 | 0 | 6.11 | 0.00105 | -0.0373 | 5.34 | 0.000827 | 0 | 6.05 | 0.00104 | -0.037 | CFL | Bldg | 5390 | 0.836 | 5340 | 0.827 | 1.13 | 1.26 | -0.00693
CFLBldgSCEHspExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Hsp | Ex | CZ15 | 5.39 | 0.000836 | 0 | 6.28 | 0.00105 | -0.0246 | 5.34 | 0.000827 | 0 | 6.22 | 0.00104 | -0.0244 | CFL | Bldg | 5390 | 0.836 | 5340 | 0.827 | 1.16 | 1.26 | -0.00457
CFLBldgSCGHspExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCG | Hsp | Ex | CZ15 | 5.39 | 0.000836 | 0 | 6.28 | 0.00105 | -0.0246 | 5.34 | 0.000827 | 0 | 6.22 | 0.00104 | -0.0244 | CFL | Bldg | 5390 | 0.836 | 5340 | 0.827 | 1.16 | 1.26 | -0.00457
CFLBldgPGEHspExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Hsp | Ex | CZ16 | 5.39 | 0.000836 | 0 | 5.7 | 0.00102 | -0.0509 | 5.34 | 0.000827 | 0 | 5.64 | 0.00101 | -0.0504 | CFL | Bldg | 5390 | 0.836 | 5340 | 0.827 | 1.06 | 1.22 | -0.00944
CFLBldgSCGHspExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCG | Hsp | Ex | CZ16 | 5.39 | 0.000836 | 0 | 5.7 | 0.00102 | -0.0509 | 5.34 | 0.000827 | 0 | 5.64 | 0.00101 | -0.0504 | CFL | Bldg | 5390 | 0.836 | 5340 | 0.827 | 1.06 | 1.22 | -0.00944
CFLBldgSCEHspExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Hsp | Ex | CZ16 | 5.39 | 0.000836 | 0 | 5.7 | 0.00102 | -0.0509 | 5.34 | 0.000827 | 0 | 5.64 | 0.00101 | -0.0504 | CFL | Bldg | 5390 | 0.836 | 5340 | 0.827 | 1.06 | 1.22 | -0.00944
CFLBldgPGEHspExIOU | Com-Iltg-dWatt-CFL_OSbldg | PGE | Hsp | Ex | IOU | 5.39 | 0.000836 | 0 | 5.98 | 0.00102 | -0.0349 | 5.34 | 0.000827 | 0 | 5.93 | 0.00101 | -0.0346 | CFL | Bldg | 5390 | 0.836 | 5340 | 0.827 | 1.11 | 1.22 | -0.00648
CFLBldgSCGHspExIOU | Com-Iltg-dWatt-CFL_OSbldg | SCG | Hsp | Ex | IOU | 5.39 | 0.000836 | 0 | 6.21 | 0.00105 | -0.0294 | 5.34 | 0.000827 | 0 | 6.15 | 0.00104 | -0.0291 | CFL | Bldg | 5390 | 0.836 | 5340 | 0.827 | 1.15 | 1.26 | -0.00545
CFLBldgSCEHspExIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | Hsp | Ex | IOU | 5.39 | 0.000836 | 0 | 6.18 | 0.00104 | -0.0298 | 5.34 | 0.000827 | 0 | 6.13 | 0.00103 | -0.0295 | CFL | Bldg | 5390 | 0.836 | 5340 | 0.827 | 1.15 | 1.25 | -0.00552
CFLBldgSDGHspExIOU | Com-Iltg-dWatt-CFL_OSbldg | SDG | Hsp | Ex | IOU | 5.39 | 0.000837 | 0 | 6.16 | 0.00103 | -0.0273 | 5.34 | 0.000827 | 0 | 6.11 | 0.00102 | -0.0271 | CFL | Bldg | 5390 | 0.837 | 5340 | 0.827 | 1.14 | 1.23 | -0.00507
CFLBldgPGEHspNewCZ01 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Hsp | New | CZ01 | 5.35 | 0.000827 | 0 | 5.47 | 0.000903 | -0.0498 | 5.35 | 0.000827 | 0 | 5.47 | 0.000903 | -0.0498 | CFL | Bldg | 5350 | 0.827 | 5350 | 0.827 | 1.02 | 1.09 | -0.00931
CFLBldgPGEHspNewCZ02 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Hsp | New | CZ02 | 5.35 | 0.000827 | 0 | 5.67 | 0.000989 | -0.0399 | 5.35 | 0.000827 | 0 | 5.67 | 0.000989 | -0.0399 | CFL | Bldg | 5350 | 0.827 | 5350 | 0.827 | 1.06 | 1.2 | -0.00746
CFLBldgPGEHspNewCZ03 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Hsp | New | CZ03 | 5.35 | 0.000827 | 0 | 5.64 | 0.000964 | -0.0357 | 5.35 | 0.000827 | 0 | 5.64 | 0.000964 | -0.0357 | CFL | Bldg | 5350 | 0.827 | 5350 | 0.827 | 1.05 | 1.17 | -0.00667
CFLBldgPGEHspNewCZ04 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Hsp | New | CZ04 | 5.35 | 0.000827 | 0 | 5.72 | 0.000981 | -0.0348 | 5.35 | 0.000827 | 0 | 5.72 | 0.000981 | -0.0348 | CFL | Bldg | 5350 | 0.827 | 5350 | 0.827 | 1.07 | 1.19 | -0.0065
CFLBldgPGEHspNewCZ05 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Hsp | New | CZ05 | 5.35 | 0.000827 | 0 | 5.61 | 0.000951 | -0.0402 | 5.35 | 0.000827 | 0 | 5.61 | 0.000951 | -0.0402 | CFL | Bldg | 5350 | 0.827 | 5350 | 0.827 | 1.05 | 1.15 | -0.00751
CFLBldgSCEHspNewCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Hsp | New | CZ05 | 5.35 | 0.000827 | 0 | 5.64 | 0.000977 | -0.04 | 5.35 | 0.000827 | 0 | 5.64 | 0.000977 | -0.04 | CFL | Bldg | 5350 | 0.827 | 5350 | 0.827 | 1.05 | 1.18 | -0.00748
CFLBldgSCEHspNewCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Hsp | New | CZ06 | 5.35 | 0.000827 | 0 | 5.86 | 0.000996 | -0.0307 | 5.35 | 0.000827 | 0 | 5.86 | 0.000996 | -0.0307 | CFL | Bldg | 5350 | 0.827 | 5350 | 0.827 | 1.1 | 1.2 | -0.00574
CFLBldgSDGHspNewCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Hsp | New | CZ06 | 5.35 | 0.000827 | 0 | 5.85 | 0.000988 | -0.0305 | 5.35 | 0.000827 | 0 | 5.85 | 0.000988 | -0.0305 | CFL | Bldg | 5350 | 0.827 | 5350 | 0.827 | 1.09 | 1.19 | -0.0057
CFLBldgSDGHspNewCZ07 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Hsp | New | CZ07 | 5.35 | 0.000827 | 0 | 5.87 | 0.000982 | -0.0262 | 5.35 | 0.000827 | 0 | 5.87 | 0.000982 | -0.0262 | CFL | Bldg | 5350 | 0.827 | 5350 | 0.827 | 1.1 | 1.19 | -0.0049
CFLBldgSDGHspNewCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Hsp | New | CZ08 | 5.35 | 0.000827 | 0 | 5.91 | 0.000993 | -0.0282 | 5.35 | 0.000827 | 0 | 5.91 | 0.000993 | -0.0282 | CFL | Bldg | 5350 | 0.827 | 5350 | 0.827 | 1.1 | 1.2 | -0.00527
CFLBldgSCEHspNewCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Hsp | New | CZ08 | 5.35 | 0.000827 | 0 | 5.92 | 0.001 | -0.0283 | 5.35 | 0.000827 | 0 | 5.92 | 0.001 | -0.0283 | CFL | Bldg | 5350 | 0.827 | 5350 | 0.827 | 1.11 | 1.21 | -0.00529
CFLBldgSCEHspNewCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Hsp | New | CZ09 | 5.35 | 0.000827 | 0 | 5.94 | 0.00103 | -0.0288 | 5.35 | 0.000827 | 0 | 5.94 | 0.00103 | -0.0288 | CFL | Bldg | 5350 | 0.827 | 5350 | 0.827 | 1.11 | 1.25 | -0.00538
CFLBldgSDGHspNewCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Hsp | New | CZ10 | 5.35 | 0.000827 | 0 | 5.91 | 0.00102 | -0.0318 | 5.35 | 0.000827 | 0 | 5.91 | 0.00102 | -0.0318 | CFL | Bldg | 5350 | 0.827 | 5350 | 0.827 | 1.1 | 1.23 | -0.00594
CFLBldgSCEHspNewCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Hsp | New | CZ10 | 5.35 | 0.000827 | 0 | 5.92 | 0.00103 | -0.0316 | 5.35 | 0.000827 | 0 | 5.92 | 0.00103 | -0.0316 | CFL | Bldg | 5350 | 0.827 | 5350 | 0.827 | 1.11 | 1.25 | -0.00591
CFLBldgPGEHspNewCZ11 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Hsp | New | CZ11 | 5.35 | 0.000827 | 0 | 5.79 | 0.000995 | -0.0371 | 5.35 | 0.000827 | 0 | 5.79 | 0.000995 | -0.0371 | CFL | Bldg | 5350 | 0.827 | 5350 | 0.827 | 1.08 | 1.2 | -0.00693
CFLBldgPGEHspNewCZ12 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Hsp | New | CZ12 | 5.35 | 0.000827 | 0 | 5.76 | 0.000995 | -0.0361 | 5.35 | 0.000827 | 0 | 5.76 | 0.000995 | -0.0361 | CFL | Bldg | 5350 | 0.827 | 5350 | 0.827 | 1.08 | 1.2 | -0.00675
CFLBldgPGEHspNewCZ13 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Hsp | New | CZ13 | 5.35 | 0.000827 | 0 | 5.81 | 0.000992 | -0.0352 | 5.35 | 0.000827 | 0 | 5.81 | 0.000992 | -0.0352 | CFL | Bldg | 5350 | 0.827 | 5350 | 0.827 | 1.09 | 1.2 | -0.00658
CFLBldgSCEHspNewCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Hsp | New | CZ13 | 5.35 | 0.000827 | 0 | 5.9 | 0.00103 | -0.0356 | 5.35 | 0.000827 | 0 | 5.9 | 0.00103 | -0.0356 | CFL | Bldg | 5350 | 0.827 | 5350 | 0.827 | 1.1 | 1.25 | -0.00665
CFLBldgSCEHspNewCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Hsp | New | CZ14 | 5.35 | 0.000827 | 0 | 5.83 | 0.00103 | -0.0393 | 5.35 | 0.000827 | 0 | 5.83 | 0.00103 | -0.0393 | CFL | Bldg | 5350 | 0.827 | 5350 | 0.827 | 1.09 | 1.25 | -0.00735
CFLBldgSDGHspNewCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Hsp | New | CZ14 | 5.35 | 0.000827 | 0 | 5.83 | 0.00102 | -0.0396 | 5.35 | 0.000827 | 0 | 5.83 | 0.00102 | -0.0396 | CFL | Bldg | 5350 | 0.827 | 5350 | 0.827 | 1.09 | 1.23 | -0.0074
CFLBldgSCEHspNewCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Hsp | New | CZ15 | 5.35 | 0.000827 | 0 | 6.21 | 0.00104 | -0.0255 | 5.35 | 0.000827 | 0 | 6.21 | 0.00104 | -0.0255 | CFL | Bldg | 5350 | 0.827 | 5350 | 0.827 | 1.16 | 1.26 | -0.00477
CFLBldgSDGHspNewCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Hsp | New | CZ15 | 5.35 | 0.000827 | 0 | 6.18 | 0.00103 | -0.0257 | 5.35 | 0.000827 | 0 | 6.18 | 0.00103 | -0.0257 | CFL | Bldg | 5350 | 0.827 | 5350 | 0.827 | 1.16 | 1.25 | -0.0048
CFLBldgPGEHspNewCZ16 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Hsp | New | CZ16 | 5.35 | 0.000827 | 0 | 5.41 | 0.000962 | -0.0594 | 5.35 | 0.000827 | 0 | 5.41 | 0.000962 | -0.0594 | CFL | Bldg | 5350 | 0.827 | 5350 | 0.827 | 1.01 | 1.16 | -0.0111
CFLBldgSCEHspNewCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Hsp | New | CZ16 | 5.35 | 0.000827 | 0 | 5.4 | 0.000989 | -0.0567 | 5.35 | 0.000827 | 0 | 5.4 | 0.000989 | -0.0567 | CFL | Bldg | 5350 | 0.827 | 5350 | 0.827 | 1.01 | 1.2 | -0.0106
CFLBldgSCGHspNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SCG | Hsp | New | IOU | 5.35 | 0.000827 | 0 | 5.91 | 0.001 | -0.0302 | 5.35 | 0.000827 | 0 | 5.91 | 0.001 | -0.0302 | CFL | Bldg | 5350 | 0.827 | 5350 | 0.827 | 1.1 | 1.21 | -0.00564
CFLBldgPGEHspNewIOU | Com-Iltg-dWatt-CFL_OSbldg | PGE | Hsp | New | IOU | 5.35 | 0.000827 | 0 | 5.87 | 0.00102 | -0.0363 | 5.35 | 0.000827 | 0 | 5.87 | 0.00102 | -0.0363 | CFL | Bldg | 5350 | 0.827 | 5350 | 0.827 | 1.1 | 1.23 | -0.00679
CFLBldgSCEHspNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | Hsp | New | IOU | 5.35 | 0.000827 | 0 | 5.91 | 0.001 | -0.0304 | 5.35 | 0.000827 | 0 | 5.91 | 0.001 | -0.0304 | CFL | Bldg | 5350 | 0.827 | 5350 | 0.827 | 1.1 | 1.21 | -0.00568
CFLBldgSDGHspNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SDG | Hsp | New | IOU | 5.35 | 0.000827 | 0 | 5.88 | 0.000988 | -0.0272 | 5.35 | 0.000827 | 0 | 5.88 | 0.000988 | -0.0272 | CFL | Bldg | 5350 | 0.827 | 5350 | 0.827 | 1.1 | 1.19 | -0.00508
CFLBldgPGEHtlExCZ01 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Htl | Ex | CZ01 | 1.63 | 0.000202 | 0 | 1.48 | 0.000241 | -0.00855 | 1.59 | 0.000194 | 0 | 1.44 | 0.000232 | -0.00835 | CFL | Bldg | 1630 | 0.202 | 1590 | 0.194 | 0.906 | 1.2 | -0.00525
CFLBldgPGEHtlExCZ02 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Htl | Ex | CZ02 | 1.63 | 0.000202 | 0 | 1.61 | 0.00025 | -0.00622 | 1.59 | 0.000194 | 0 | 1.57 | 0.000241 | -0.00607 | CFL | Bldg | 1630 | 0.202 | 1590 | 0.194 | 0.987 | 1.24 | -0.00382
CFLBldgPGEHtlExCZ03 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Htl | Ex | CZ03 | 1.63 | 0.000202 | 0 | 1.63 | 0.000248 | -0.006 | 1.59 | 0.000194 | 0 | 1.59 | 0.000238 | -0.00585 | CFL | Bldg | 1630 | 0.202 | 1590 | 0.194 | 1 | 1.23 | -0.00368
CFLBldgPGEHtlExCZ04 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Htl | Ex | CZ04 | 1.63 | 0.000202 | 0 | 1.67 | 0.000249 | -0.00503 | 1.59 | 0.000194 | 0 | 1.63 | 0.00024 | -0.00491 | CFL | Bldg | 1630 | 0.202 | 1590 | 0.194 | 1.03 | 1.24 | -0.00309
CFLBldgSCGHtlExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCG | Htl | Ex | CZ05 | 1.63 | 0.000202 | 0 | 1.64 | 0.000253 | -0.00489 | 1.59 | 0.000194 | 0 | 1.6 | 0.000243 | -0.00477 | CFL | Bldg | 1630 | 0.202 | 1590 | 0.194 | 1.01 | 1.25 | -0.003
CFLBldgPGEHtlExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Htl | Ex | CZ05 | 1.63 | 0.000202 | 0 | 1.64 | 0.000252 | -0.00488 | 1.59 | 0.000194 | 0 | 1.6 | 0.000243 | -0.00477 | CFL | Bldg | 1630 | 0.202 | 1590 | 0.194 | 1.01 | 1.25 | -0.003
CFLBldgSCEHtlExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Htl | Ex | CZ05 | 1.63 | 0.000202 | 0 | 1.64 | 0.000253 | -0.00489 | 1.59 | 0.000194 | 0 | 1.6 | 0.000243 | -0.00477 | CFL | Bldg | 1630 | 0.202 | 1590 | 0.194 | 1.01 | 1.25 | -0.003
CFLBldgSDGHtlExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Htl | Ex | CZ06 | 1.63 | 0.000201 | 0 | 1.77 | 0.000252 | -0.0033 | 1.59 | 0.000194 | 0 | 1.73 | 0.000243 | -0.00323 | CFL | Bldg | 1630 | 0.201 | 1590 | 0.194 | 1.09 | 1.25 | -0.00203
CFLBldgSCGHtlExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCG | Htl | Ex | CZ06 | 1.63 | 0.000202 | 0 | 1.77 | 0.000253 | -0.00331 | 1.59 | 0.000194 | 0 | 1.73 | 0.000243 | -0.00323 | CFL | Bldg | 1630 | 0.202 | 1590 | 0.194 | 1.09 | 1.25 | -0.00203
CFLBldgSCEHtlExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Htl | Ex | CZ06 | 1.63 | 0.000202 | 0 | 1.77 | 0.000253 | -0.00331 | 1.59 | 0.000194 | 0 | 1.73 | 0.000243 | -0.00323 | CFL | Bldg | 1630 | 0.202 | 1590 | 0.194 | 1.09 | 1.25 | -0.00203
CFLBldgSDGHtlExCZ07 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Htl | Ex | CZ07 | 1.63 | 0.000201 | 0 | 1.8 | 0.000249 | -0.00257 | 1.59 | 0.000194 | 0 | 1.76 | 0.000241 | -0.00251 | CFL | Bldg | 1630 | 0.201 | 1590 | 0.194 | 1.11 | 1.24 | -0.00158
CFLBldgSCEHtlExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Htl | Ex | CZ08 | 1.63 | 0.000202 | 0 | 1.8 | 0.000254 | -0.00298 | 1.59 | 0.000194 | 0 | 1.75 | 0.000244 | -0.00291 | CFL | Bldg | 1630 | 0.202 | 1590 | 0.194 | 1.1 | 1.26 | -0.00183
CFLBldgSCGHtlExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCG | Htl | Ex | CZ08 | 1.63 | 0.000202 | 0 | 1.8 | 0.000254 | -0.00298 | 1.59 | 0.000194 | 0 | 1.75 | 0.000244 | -0.00291 | CFL | Bldg | 1630 | 0.202 | 1590 | 0.194 | 1.1 | 1.26 | -0.00183
CFLBldgSDGHtlExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Htl | Ex | CZ08 | 1.63 | 0.000201 | 0 | 1.79 | 0.000253 | -0.00297 | 1.59 | 0.000194 | 0 | 1.75 | 0.000244 | -0.00291 | CFL | Bldg | 1630 | 0.201 | 1590 | 0.194 | 1.1 | 1.26 | -0.00183
CFLBldgSCEHtlExCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Htl | Ex | CZ09 | 1.63 | 0.000202 | 0 | 1.81 | 0.00026 | -0.003 | 1.59 | 0.000194 | 0 | 1.77 | 0.000251 | -0.00293 | CFL | Bldg | 1630 | 0.202 | 1590 | 0.194 | 1.11 | 1.29 | -0.00184
CFLBldgSCGHtlExCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCG | Htl | Ex | CZ09 | 1.63 | 0.000202 | 0 | 1.81 | 0.00026 | -0.003 | 1.59 | 0.000194 | 0 | 1.77 | 0.000251 | -0.00293 | CFL | Bldg | 1630 | 0.202 | 1590 | 0.194 | 1.11 | 1.29 | -0.00184
CFLBldgSCGHtlExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCG | Htl | Ex | CZ10 | 1.63 | 0.000201 | 0 | 1.77 | 0.000258 | -0.00345 | 1.59 | 0.000194 | 0 | 1.73 | 0.000249 | -0.00337 | CFL | Bldg | 1630 | 0.201 | 1590 | 0.194 | 1.09 | 1.28 | -0.00212
CFLBldgSCEHtlExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Htl | Ex | CZ10 | 1.63 | 0.000201 | 0 | 1.77 | 0.000258 | -0.00345 | 1.59 | 0.000194 | 0 | 1.73 | 0.000249 | -0.00337 | CFL | Bldg | 1630 | 0.201 | 1590 | 0.194 | 1.09 | 1.28 | -0.00212
CFLBldgSDGHtlExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Htl | Ex | CZ10 | 1.63 | 0.000201 | 0 | 1.77 | 0.000258 | -0.00345 | 1.59 | 0.000194 | 0 | 1.73 | 0.000249 | -0.00337 | CFL | Bldg | 1630 | 0.201 | 1590 | 0.194 | 1.09 | 1.28 | -0.00212
CFLBldgPGEHtlExCZ11 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Htl | Ex | CZ11 | 1.63 | 0.000201 | 0 | 1.69 | 0.000254 | -0.00543 | 1.59 | 0.000194 | 0 | 1.64 | 0.000245 | -0.00531 | CFL | Bldg | 1630 | 0.201 | 1590 | 0.194 | 1.03 | 1.26 | -0.00334
CFLBldgPGEHtlExCZ12 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Htl | Ex | CZ12 | 1.63 | 0.000201 | 0 | 1.66 | 0.000253 | -0.00553 | 1.59 | 0.000194 | 0 | 1.62 | 0.000244 | -0.00541 | CFL | Bldg | 1630 | 0.201 | 1590 | 0.194 | 1.02 | 1.26 | -0.0034
CFLBldgPGEHtlExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Htl | Ex | CZ13 | 1.63 | 0.000201 | 0 | 1.72 | 0.000258 | -0.00424 | 1.59 | 0.000194 | 0 | 1.68 | 0.000249 | -0.00415 | CFL | Bldg | 1630 | 0.201 | 1590 | 0.194 | 1.06 | 1.28 | -0.00261
CFLBldgSCEHtlExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Htl | Ex | CZ13 | 1.63 | 0.000201 | 0 | 1.72 | 0.000258 | -0.00424 | 1.59 | 0.000194 | 0 | 1.68 | 0.000249 | -0.00415 | CFL | Bldg | 1630 | 0.201 | 1590 | 0.194 | 1.06 | 1.28 | -0.00261
CFLBldgSCGHtlExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCG | Htl | Ex | CZ13 | 1.63 | 0.000201 | 0 | 1.72 | 0.000258 | -0.00424 | 1.59 | 0.000194 | 0 | 1.68 | 0.000249 | -0.00415 | CFL | Bldg | 1630 | 0.201 | 1590 | 0.194 | 1.06 | 1.28 | -0.00261
CFLBldgSCGHtlExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCG | Htl | Ex | CZ14 | 1.63 | 0.000201 | 0 | 1.7 | 0.000258 | -0.0047 | 1.59 | 0.000194 | 0 | 1.65 | 0.000248 | -0.0046 | CFL | Bldg | 1630 | 0.201 | 1590 | 0.194 | 1.04 | 1.28 | -0.00289
CFLBldgSCEHtlExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Htl | Ex | CZ14 | 1.63 | 0.000201 | 0 | 1.7 | 0.000258 | -0.0047 | 1.59 | 0.000194 | 0 | 1.65 | 0.000248 | -0.0046 | CFL | Bldg | 1630 | 0.201 | 1590 | 0.194 | 1.04 | 1.28 | -0.00289
CFLBldgSDGHtlExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Htl | Ex | CZ14 | 1.63 | 0.000201 | 0 | 1.69 | 0.000258 | -0.0047 | 1.59 | 0.000194 | 0 | 1.65 | 0.000248 | -0.0046 | CFL | Bldg | 1630 | 0.201 | 1590 | 0.194 | 1.04 | 1.28 | -0.00289
CFLBldgSCGHtlExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCG | Htl | Ex | CZ15 | 1.63 | 0.000201 | 0 | 1.89 | 0.000259 | -0.00198 | 1.59 | 0.000194 | 0 | 1.85 | 0.00025 | -0.00194 | CFL | Bldg | 1630 | 0.201 | 1590 | 0.194 | 1.16 | 1.29 | -0.00122
CFLBldgSCEHtlExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Htl | Ex | CZ15 | 1.63 | 0.000201 | 0 | 1.89 | 0.000259 | -0.00198 | 1.59 | 0.000194 | 0 | 1.85 | 0.00025 | -0.00194 | CFL | Bldg | 1630 | 0.201 | 1590 | 0.194 | 1.16 | 1.29 | -0.00122
CFLBldgSDGHtlExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Htl | Ex | CZ15 | 1.63 | 0.000201 | 0 | 1.89 | 0.000259 | -0.00198 | 1.59 | 0.000194 | 0 | 1.85 | 0.00025 | -0.00194 | CFL | Bldg | 1630 | 0.201 | 1590 | 0.194 | 1.16 | 1.29 | -0.00122
CFLBldgPGEHtlExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Htl | Ex | CZ16 | 1.63 | 0.000201 | 0 | 1.5 | 0.000253 | -0.00698 | 1.59 | 0.000194 | 0 | 1.46 | 0.000244 | -0.00682 | CFL | Bldg | 1630 | 0.201 | 1590 | 0.194 | 0.918 | 1.26 | -0.00429
CFLBldgSCEHtlExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Htl | Ex | CZ16 | 1.63 | 0.000201 | 0 | 1.5 | 0.000253 | -0.00698 | 1.59 | 0.000194 | 0 | 1.46 | 0.000244 | -0.00682 | CFL | Bldg | 1630 | 0.201 | 1590 | 0.194 | 0.918 | 1.26 | -0.00429
CFLBldgSCGHtlExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCG | Htl | Ex | CZ16 | 1.63 | 0.000201 | 0 | 1.5 | 0.000253 | -0.00698 | 1.59 | 0.000194 | 0 | 1.46 | 0.000244 | -0.00682 | CFL | Bldg | 1630 | 0.201 | 1590 | 0.194 | 0.918 | 1.26 | -0.00429
CFLBldgPGEHtlExIOU | Com-Iltg-dWatt-CFL_OSbldg | PGE | Htl | Ex | IOU | 1.63 | 0.000202 | 0 | 1.64 | 0.00025 | -0.00563 | 1.59 | 0.000194 | 0 | 1.6 | 0.000241 | -0.00549 | CFL | Bldg | 1630 | 0.202 | 1590 | 0.194 | 1.01 | 1.24 | -0.00345
CFLBldgSCGHtlExIOU | Com-Iltg-dWatt-CFL_OSbldg | SCG | Htl | Ex | IOU | 1.63 | 0.000202 | 0 | 1.79 | 0.000256 | -0.00315 | 1.59 | 0.000194 | 0 | 1.75 | 0.000247 | -0.00308 | CFL | Bldg | 1630 | 0.202 | 1590 | 0.194 | 1.1 | 1.27 | -0.00194
CFLBldgSCEHtlExIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | Htl | Ex | IOU | 1.63 | 0.000202 | 0 | 1.79 | 0.000255 | -0.00319 | 1.59 | 0.000194 | 0 | 1.74 | 0.000246 | -0.00312 | CFL | Bldg | 1630 | 0.202 | 1590 | 0.194 | 1.09 | 1.27 | -0.00196
CFLBldgSDGHtlExIOU | Com-Iltg-dWatt-CFL_OSbldg | SDG | Htl | Ex | IOU | 1.63 | 0.000201 | 0 | 1.8 | 0.00025 | -0.00271 | 1.59 | 0.000194 | 0 | 1.76 | 0.000242 | -0.00264 | CFL | Bldg | 1630 | 0.201 | 1590 | 0.194 | 1.11 | 1.25 | -0.00166
CFLBldgPGEHtlNewCZ01 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Htl | New | CZ01 | 1.58 | 0.000194 | 0 | 1.4 | 0.000231 | -0.00918 | 1.58 | 0.000194 | 0 | 1.4 | 0.000231 | -0.00918 | CFL | Bldg | 1580 | 0.194 | 1580 | 0.194 | 0.886 | 1.19 | -0.00581
CFLBldgPGEHtlNewCZ02 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Htl | New | CZ02 | 1.58 | 0.000194 | 0 | 1.54 | 0.000246 | -0.00717 | 1.58 | 0.000194 | 0 | 1.54 | 0.000246 | -0.00717 | CFL | Bldg | 1580 | 0.194 | 1580 | 0.194 | 0.975 | 1.27 | -0.00454
CFLBldgPGEHtlNewCZ03 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Htl | New | CZ03 | 1.58 | 0.000194 | 0 | 1.54 | 0.000239 | -0.00656 | 1.58 | 0.000194 | 0 | 1.54 | 0.000239 | -0.00656 | CFL | Bldg | 1580 | 0.194 | 1580 | 0.194 | 0.975 | 1.23 | -0.00415
CFLBldgPGEHtlNewCZ04 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Htl | New | CZ04 | 1.58 | 0.000194 | 0 | 1.6 | 0.000246 | -0.00566 | 1.58 | 0.000194 | 0 | 1.6 | 0.000246 | -0.00566 | CFL | Bldg | 1580 | 0.194 | 1580 | 0.194 | 1.01 | 1.27 | -0.00358
CFLBldgSCEHtlNewCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Htl | New | CZ05 | 1.58 | 0.000194 | 0 | 1.52 | 0.000246 | -0.00498 | 1.58 | 0.000194 | 0 | 1.52 | 0.000246 | -0.00498 | CFL | Bldg | 1580 | 0.194 | 1580 | 0.194 | 0.962 | 1.27 | -0.00315
CFLBldgPGEHtlNewCZ05 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Htl | New | CZ05 | 1.58 | 0.000194 | 0 | 1.53 | 0.000236 | -0.00697 | 1.58 | 0.000194 | 0 | 1.53 | 0.000236 | -0.00697 | CFL | Bldg | 1580 | 0.194 | 1580 | 0.194 | 0.968 | 1.22 | -0.00441
CFLBldgSDGHtlNewCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Htl | New | CZ06 | 1.58 | 0.000194 | 0 | 1.71 | 0.000248 | -0.00299 | 1.58 | 0.000194 | 0 | 1.71 | 0.000248 | -0.00299 | CFL | Bldg | 1580 | 0.194 | 1580 | 0.194 | 1.08 | 1.28 | -0.00189
CFLBldgSCEHtlNewCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Htl | New | CZ06 | 1.58 | 0.000194 | 0 | 1.71 | 0.000249 | -0.00273 | 1.58 | 0.000194 | 0 | 1.71 | 0.000249 | -0.00273 | CFL | Bldg | 1580 | 0.194 | 1580 | 0.194 | 1.08 | 1.28 | -0.00173
CFLBldgSDGHtlNewCZ07 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Htl | New | CZ07 | 1.58 | 0.000194 | 0 | 1.74 | 0.000243 | -0.00215 | 1.58 | 0.000194 | 0 | 1.74 | 0.000243 | -0.00215 | CFL | Bldg | 1580 | 0.194 | 1580 | 0.194 | 1.1 | 1.25 | -0.00136
CFLBldgSDGHtlNewCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Htl | New | CZ08 | 1.58 | 0.000194 | 0 | 1.73 | 0.000249 | -0.00262 | 1.58 | 0.000194 | 0 | 1.73 | 0.000249 | -0.00262 | CFL | Bldg | 1580 | 0.194 | 1580 | 0.194 | 1.09 | 1.28 | -0.00166
CFLBldgSCEHtlNewCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Htl | New | CZ08 | 1.58 | 0.000194 | 0 | 1.73 | 0.000251 | -0.0024 | 1.58 | 0.000194 | 0 | 1.73 | 0.000251 | -0.0024 | CFL | Bldg | 1580 | 0.194 | 1580 | 0.194 | 1.09 | 1.29 | -0.00152
CFLBldgSCEHtlNewCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Htl | New | CZ09 | 1.58 | 0.000194 | 0 | 1.72 | 0.000256 | -0.00273 | 1.58 | 0.000194 | 0 | 1.72 | 0.000256 | -0.00273 | CFL | Bldg | 1580 | 0.194 | 1580 | 0.194 | 1.09 | 1.32 | -0.00173
CFLBldgSDGHtlNewCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Htl | New | CZ10 | 1.58 | 0.000194 | 0 | 1.71 | 0.000262 | -0.00329 | 1.58 | 0.000194 | 0 | 1.71 | 0.000262 | -0.00329 | CFL | Bldg | 1580 | 0.194 | 1580 | 0.194 | 1.08 | 1.35 | -0.00208
CFLBldgSCEHtlNewCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Htl | New | CZ10 | 1.58 | 0.000194 | 0 | 1.71 | 0.000264 | -0.00303 | 1.58 | 0.000194 | 0 | 1.71 | 0.000264 | -0.00303 | CFL | Bldg | 1580 | 0.194 | 1580 | 0.194 | 1.08 | 1.36 | -0.00192
CFLBldgPGEHtlNewCZ11 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Htl | New | CZ11 | 1.58 | 0.000194 | 0 | 1.61 | 0.000248 | -0.00623 | 1.58 | 0.000194 | 0 | 1.61 | 0.000248 | -0.00623 | CFL | Bldg | 1580 | 0.194 | 1580 | 0.194 | 1.02 | 1.28 | -0.00394
CFLBldgPGEHtlNewCZ12 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Htl | New | CZ12 | 1.58 | 0.000194 | 0 | 1.59 | 0.000247 | -0.00629 | 1.58 | 0.000194 | 0 | 1.59 | 0.000247 | -0.00629 | CFL | Bldg | 1580 | 0.194 | 1580 | 0.194 | 1.01 | 1.27 | -0.00398
CFLBldgSCEHtlNewCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Htl | New | CZ13 | 1.58 | 0.000194 | 0 | 1.64 | 0.000257 | -0.00416 | 1.58 | 0.000194 | 0 | 1.64 | 0.000257 | -0.00416 | CFL | Bldg | 1580 | 0.194 | 1580 | 0.194 | 1.04 | 1.32 | -0.00263
CFLBldgPGEHtlNewCZ13 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Htl | New | CZ13 | 1.58 | 0.000194 | 0 | 1.63 | 0.000245 | -0.0057 | 1.58 | 0.000194 | 0 | 1.63 | 0.000245 | -0.0057 | CFL | Bldg | 1580 | 0.194 | 1580 | 0.194 | 1.03 | 1.26 | -0.00361
CFLBldgSDGHtlNewCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Htl | New | CZ14 | 1.58 | 0.000194 | 0 | 1.62 | 0.000256 | -0.00493 | 1.58 | 0.000194 | 0 | 1.62 | 0.000256 | -0.00493 | CFL | Bldg | 1580 | 0.194 | 1580 | 0.194 | 1.03 | 1.32 | -0.00312
CFLBldgSCEHtlNewCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Htl | New | CZ14 | 1.58 | 0.000194 | 0 | 1.61 | 0.000259 | -0.00457 | 1.58 | 0.000194 | 0 | 1.61 | 0.000259 | -0.00457 | CFL | Bldg | 1580 | 0.194 | 1580 | 0.194 | 1.02 | 1.34 | -0.00289
CFLBldgSCEHtlNewCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Htl | New | CZ15 | 1.58 | 0.000194 | 0 | 1.86 | 0.000263 | -0.00151 | 1.58 | 0.000194 | 0 | 1.86 | 0.000263 | -0.00151 | CFL | Bldg | 1580 | 0.194 | 1580 | 0.194 | 1.18 | 1.36 | -0.000956
CFLBldgSDGHtlNewCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Htl | New | CZ15 | 1.58 | 0.000194 | 0 | 1.85 | 0.00026 | -0.00166 | 1.58 | 0.000194 | 0 | 1.85 | 0.00026 | -0.00166 | CFL | Bldg | 1580 | 0.194 | 1580 | 0.194 | 1.17 | 1.34 | -0.00105
CFLBldgSCEHtlNewCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Htl | New | CZ16 | 1.58 | 0.000194 | 0 | 1.39 | 0.000248 | -0.00774 | 1.58 | 0.000194 | 0 | 1.39 | 0.000248 | -0.00774 | CFL | Bldg | 1580 | 0.194 | 1580 | 0.194 | 0.88 | 1.28 | -0.0049
CFLBldgPGEHtlNewCZ16 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Htl | New | CZ16 | 1.58 | 0.000194 | 0 | 1.42 | 0.000239 | -0.0103 | 1.58 | 0.000194 | 0 | 1.42 | 0.000239 | -0.0103 | CFL | Bldg | 1580 | 0.194 | 1580 | 0.194 | 0.899 | 1.23 | -0.00652
CFLBldgSCEHtlNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | Htl | New | IOU | 1.58 | 0.000194 | 0 | 1.76 | 0.000254 | -0.00263 | 1.58 | 0.000194 | 0 | 1.76 | 0.000254 | -0.00263 | CFL | Bldg | 1580 | 0.194 | 1580 | 0.194 | 1.11 | 1.31 | -0.00166
CFLBldgSCGHtlNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SCG | Htl | New | IOU | 1.58 | 0.000194 | 0 | 1.75 | 0.000254 | -0.00265 | 1.58 | 0.000194 | 0 | 1.75 | 0.000254 | -0.00265 | CFL | Bldg | 1580 | 0.194 | 1580 | 0.194 | 1.11 | 1.31 | -0.00168
CFLBldgSDGHtlNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SDG | Htl | New | IOU | 1.58 | 0.000194 | 0 | 1.74 | 0.000245 | -0.00232 | 1.58 | 0.000194 | 0 | 1.74 | 0.000245 | -0.00232 | CFL | Bldg | 1580 | 0.194 | 1580 | 0.194 | 1.1 | 1.26 | -0.00147
CFLBldgPGEHtlNewIOU | Com-Iltg-dWatt-CFL_OSbldg | PGE | Htl | New | IOU | 1.58 | 0.000194 | 0 | 1.57 | 0.000252 | -0.00482 | 1.58 | 0.000194 | 0 | 1.57 | 0.000252 | -0.00482 | CFL | Bldg | 1580 | 0.194 | 1580 | 0.194 | 0.994 | 1.3 | -0.00305
CFLBldgPGEMBTExCZ01 | Com-Iltg-dWatt-CFL_OSbldg | PGE | MBT | Ex | CZ01 | 2.06 | 0.000546 | 0 | 2.22 | 0.000644 | -0.00237 | 2 | 0.000526 | 0 | 2.16 | 0.00062 | -0.0023 | CFL | Bldg | 2060 | 0.546 | 2000 | 0.526 | 1.08 | 1.18 | -0.00115
CFLBldgPGEMBTExCZ02 | Com-Iltg-dWatt-CFL_OSbldg | PGE | MBT | Ex | CZ02 | 2.06 | 0.000546 | 0 | 2.29 | 0.000644 | -0.00119 | 2 | 0.000526 | 0 | 2.22 | 0.000621 | -0.00116 | CFL | Bldg | 2060 | 0.546 | 2000 | 0.526 | 1.11 | 1.18 | -0.00058
CFLBldgPGEMBTExCZ03 | Com-Iltg-dWatt-CFL_OSbldg | PGE | MBT | Ex | CZ03 | 2.06 | 0.000546 | 0 | 2.3 | 0.000646 | -0.00104 | 2 | 0.000526 | 0 | 2.24 | 0.000622 | -0.00101 | CFL | Bldg | 2060 | 0.546 | 2000 | 0.526 | 1.12 | 1.18 | -0.000505
CFLBldgPGEMBTExCZ04 | Com-Iltg-dWatt-CFL_OSbldg | PGE | MBT | Ex | CZ04 | 2.06 | 0.000546 | 0 | 2.3 | 0.000654 | -0.000802 | 2 | 0.000526 | 0 | 2.23 | 0.00063 | -0.00078 | CFL | Bldg | 2060 | 0.546 | 2000 | 0.526 | 1.12 | 1.2 | -0.00039
CFLBldgSCEMBTExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | MBT | Ex | CZ05 | 2.06 | 0.000546 | 0 | 2.36 | 0.000679 | -0.00087 | 2 | 0.000526 | 0 | 2.29 | 0.000654 | -0.000846 | CFL | Bldg | 2060 | 0.546 | 2000 | 0.526 | 1.15 | 1.24 | -0.000423
CFLBldgPGEMBTExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | PGE | MBT | Ex | CZ05 | 2.06 | 0.000546 | 0 | 2.36 | 0.000679 | -0.00087 | 2 | 0.000526 | 0 | 2.29 | 0.000654 | -0.000846 | CFL | Bldg | 2060 | 0.546 | 2000 | 0.526 | 1.15 | 1.24 | -0.000423
CFLBldgSCGMBTExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCG | MBT | Ex | CZ05 | 2.06 | 0.000546 | 0 | 2.36 | 0.000679 | -0.00087 | 2 | 0.000526 | 0 | 2.29 | 0.000654 | -0.000846 | CFL | Bldg | 2060 | 0.546 | 2000 | 0.526 | 1.15 | 1.24 | -0.000423
CFLBldgSCEMBTExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | MBT | Ex | CZ06 | 2.06 | 0.000546 | 0 | 2.39 | 0.000656 | -0.00038 | 2 | 0.000526 | 0 | 2.32 | 0.000632 | -0.00037 | CFL | Bldg | 2060 | 0.546 | 2000 | 0.526 | 1.16 | 1.2 | -0.000185
CFLBldgSCGMBTExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCG | MBT | Ex | CZ06 | 2.06 | 0.000546 | 0 | 2.39 | 0.000656 | -0.00038 | 2 | 0.000526 | 0 | 2.32 | 0.000632 | -0.00037 | CFL | Bldg | 2060 | 0.546 | 2000 | 0.526 | 1.16 | 1.2 | -0.000185
CFLBldgSDGMBTExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SDG | MBT | Ex | CZ06 | 2.05 | 0.000545 | 0 | 2.38 | 0.000655 | -0.00038 | 2 | 0.000526 | 0 | 2.32 | 0.000632 | -0.00037 | CFL | Bldg | 2050 | 0.545 | 2000 | 0.526 | 1.16 | 1.2 | -0.000185
CFLBldgSDGMBTExCZ07 | Com-Iltg-dWatt-CFL_OSbldg | SDG | MBT | Ex | CZ07 | 2.05 | 0.000545 | 0 | 2.38 | 0.000648 | -0.000103 | 2 | 0.000526 | 0 | 2.32 | 0.000625 | -0.0001 | CFL | Bldg | 2050 | 0.545 | 2000 | 0.526 | 1.16 | 1.19 | -5e-05
CFLBldgSDGMBTExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SDG | MBT | Ex | CZ08 | 2.05 | 0.000545 | 0 | 2.38 | 0.000684 | -0.000246 | 2 | 0.000526 | 0 | 2.32 | 0.00066 | -0.00024 | CFL | Bldg | 2050 | 0.545 | 2000 | 0.526 | 1.16 | 1.25 | -0.00012
CFLBldgSCEMBTExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | MBT | Ex | CZ08 | 2.06 | 0.000546 | 0 | 2.39 | 0.000685 | -0.000247 | 2 | 0.000526 | 0 | 2.32 | 0.00066 | -0.00024 | CFL | Bldg | 2060 | 0.546 | 2000 | 0.526 | 1.16 | 1.25 | -0.00012
CFLBldgSCGMBTExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCG | MBT | Ex | CZ08 | 2.06 | 0.000546 | 0 | 2.39 | 0.000685 | -0.000247 | 2 | 0.000526 | 0 | 2.32 | 0.00066 | -0.00024 | CFL | Bldg | 2060 | 0.546 | 2000 | 0.526 | 1.16 | 1.25 | -0.00012
CFLBldgSCGMBTExCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCG | MBT | Ex | CZ09 | 2.06 | 0.000546 | 0 | 2.42 | 0.000689 | -0.000578 | 2 | 0.000526 | 0 | 2.35 | 0.000664 | -0.000562 | CFL | Bldg | 2060 | 0.546 | 2000 | 0.526 | 1.18 | 1.26 | -0.000281
CFLBldgSCEMBTExCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | MBT | Ex | CZ09 | 2.06 | 0.000546 | 0 | 2.42 | 0.000689 | -0.000578 | 2 | 0.000526 | 0 | 2.35 | 0.000664 | -0.000562 | CFL | Bldg | 2060 | 0.546 | 2000 | 0.526 | 1.18 | 1.26 | -0.000281
CFLBldgSCEMBTExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | MBT | Ex | CZ10 | 2.05 | 0.000544 | 0 | 2.37 | 0.000697 | -0.000664 | 2 | 0.000526 | 0 | 2.31 | 0.000674 | -0.000648 | CFL | Bldg | 2050 | 0.544 | 2000 | 0.526 | 1.16 | 1.28 | -0.000324
CFLBldgSDGMBTExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SDG | MBT | Ex | CZ10 | 2.05 | 0.000545 | 0 | 2.37 | 0.000699 | -0.000665 | 2 | 0.000526 | 0 | 2.31 | 0.000674 | -0.000648 | CFL | Bldg | 2050 | 0.545 | 2000 | 0.526 | 1.16 | 1.28 | -0.000324
CFLBldgSCGMBTExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCG | MBT | Ex | CZ10 | 2.05 | 0.000544 | 0 | 2.37 | 0.000697 | -0.000664 | 2 | 0.000526 | 0 | 2.31 | 0.000674 | -0.000648 | CFL | Bldg | 2050 | 0.544 | 2000 | 0.526 | 1.16 | 1.28 | -0.000324
CFLBldgPGEMBTExCZ11 | Com-Iltg-dWatt-CFL_OSbldg | PGE | MBT | Ex | CZ11 | 2.06 | 0.000546 | 0 | 2.3 | 0.000657 | -0.00128 | 2 | 0.000526 | 0 | 2.23 | 0.000633 | -0.00124 | CFL | Bldg | 2060 | 0.546 | 2000 | 0.526 | 1.12 | 1.2 | -0.00062
CFLBldgPGEMBTExCZ12 | Com-Iltg-dWatt-CFL_OSbldg | PGE | MBT | Ex | CZ12 | 2.06 | 0.000546 | 0 | 2.29 | 0.00064 | -0.00126 | 2 | 0.000526 | 0 | 2.22 | 0.000616 | -0.00122 | CFL | Bldg | 2060 | 0.546 | 2000 | 0.526 | 1.11 | 1.17 | -0.00061
CFLBldgPGEMBTExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | PGE | MBT | Ex | CZ13 | 2.06 | 0.000546 | 0 | 2.35 | 0.000666 | -0.00135 | 2 | 0.000526 | 0 | 2.28 | 0.000642 | -0.00131 | CFL | Bldg | 2060 | 0.546 | 2000 | 0.526 | 1.14 | 1.22 | -0.000655
CFLBldgSCEMBTExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | MBT | Ex | CZ13 | 2.05 | 0.000545 | 0 | 2.34 | 0.000666 | -0.00135 | 2 | 0.000526 | 0 | 2.28 | 0.000642 | -0.00131 | CFL | Bldg | 2050 | 0.545 | 2000 | 0.526 | 1.14 | 1.22 | -0.000655
CFLBldgSCGMBTExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCG | MBT | Ex | CZ13 | 2.05 | 0.000545 | 0 | 2.34 | 0.000666 | -0.00135 | 2 | 0.000526 | 0 | 2.28 | 0.000642 | -0.00131 | CFL | Bldg | 2050 | 0.545 | 2000 | 0.526 | 1.14 | 1.22 | -0.000655
CFLBldgSCEMBTExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | MBT | Ex | CZ14 | 2.05 | 0.000545 | 0 | 2.34 | 0.000692 | -0.00159 | 2 | 0.000526 | 0 | 2.28 | 0.000669 | -0.00155 | CFL | Bldg | 2050 | 0.545 | 2000 | 0.526 | 1.14 | 1.27 | -0.000775
CFLBldgSDGMBTExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SDG | MBT | Ex | CZ14 | 2.05 | 0.000545 | 0 | 2.34 | 0.000693 | -0.00159 | 2 | 0.000526 | 0 | 2.28 | 0.000669 | -0.00155 | CFL | Bldg | 2050 | 0.545 | 2000 | 0.526 | 1.14 | 1.27 | -0.000775
CFLBldgSCGMBTExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCG | MBT | Ex | CZ14 | 2.05 | 0.000545 | 0 | 2.34 | 0.000692 | -0.00159 | 2 | 0.000526 | 0 | 2.28 | 0.000669 | -0.00155 | CFL | Bldg | 2050 | 0.545 | 2000 | 0.526 | 1.14 | 1.27 | -0.000775
CFLBldgSCGMBTExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCG | MBT | Ex | CZ15 | 2.05 | 0.000544 | 0 | 2.47 | 0.000698 | 0 | 2 | 0.000526 | 0 | 2.41 | 0.000675 | 0 | CFL | Bldg | 2050 | 0.544 | 2000 | 0.526 | 1.21 | 1.28 | 0
CFLBldgSCEMBTExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | MBT | Ex | CZ15 | 2.05 | 0.000544 | 0 | 2.47 | 0.000698 | 0 | 2 | 0.000526 | 0 | 2.41 | 0.000675 | 0 | CFL | Bldg | 2050 | 0.544 | 2000 | 0.526 | 1.21 | 1.28 | 0
CFLBldgSDGMBTExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SDG | MBT | Ex | CZ15 | 2.05 | 0.000545 | 0 | 2.47 | 0.0007 | 0 | 2 | 0.000526 | 0 | 2.41 | 0.000675 | 0 | CFL | Bldg | 2050 | 0.545 | 2000 | 0.526 | 1.21 | 1.28 | 0
CFLBldgPGEMBTExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | PGE | MBT | Ex | CZ16 | 2.06 | 0.000546 | 0 | 2.21 | 0.00065 | -0.00545 | 2 | 0.000526 | 0 | 2.14 | 0.000626 | -0.0053 | CFL | Bldg | 2060 | 0.546 | 2000 | 0.526 | 1.07 | 1.19 | -0.00265
CFLBldgSCGMBTExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCG | MBT | Ex | CZ16 | 2.05 | 0.000545 | 0 | 2.2 | 0.000648 | -0.00544 | 2 | 0.000526 | 0 | 2.14 | 0.000626 | -0.0053 | CFL | Bldg | 2050 | 0.545 | 2000 | 0.526 | 1.07 | 1.19 | -0.00265
CFLBldgSCEMBTExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | MBT | Ex | CZ16 | 2.05 | 0.000545 | 0 | 2.2 | 0.000648 | -0.00544 | 2 | 0.000526 | 0 | 2.14 | 0.000626 | -0.0053 | CFL | Bldg | 2050 | 0.545 | 2000 | 0.526 | 1.07 | 1.19 | -0.00265
CFLBldgSCGMBTExIOU | Com-Iltg-dWatt-CFL_OSbldg | SCG | MBT | Ex | IOU | 2.06 | 0.000545 | 0 | 2.39 | 0.000681 | -0.000559 | 2 | 0.000526 | 0 | 2.33 | 0.000657 | -0.000544 | CFL | Bldg | 2060 | 0.545 | 2000 | 0.526 | 1.17 | 1.25 | -0.000272
CFLBldgSDGMBTExIOU | Com-Iltg-dWatt-CFL_OSbldg | SDG | MBT | Ex | IOU | 2.05 | 0.000545 | 0 | 2.38 | 0.000665 | -0.000299 | 2 | 0.000526 | 0 | 2.32 | 0.000641 | -0.000291 | CFL | Bldg | 2050 | 0.545 | 2000 | 0.526 | 1.16 | 1.22 | -0.000146
CFLBldgSCEMBTExIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | MBT | Ex | IOU | 2.06 | 0.000545 | 0 | 2.39 | 0.000681 | -0.000572 | 2 | 0.000526 | 0 | 2.32 | 0.000657 | -0.000557 | CFL | Bldg | 2060 | 0.545 | 2000 | 0.526 | 1.16 | 1.25 | -0.000279
CFLBldgPGEMBTExIOU | Com-Iltg-dWatt-CFL_OSbldg | PGE | MBT | Ex | IOU | 2.06 | 0.000546 | 0 | 2.3 | 0.00065 | -0.00115 | 2 | 0.000526 | 0 | 2.24 | 0.000626 | -0.00112 | CFL | Bldg | 2060 | 0.546 | 2000 | 0.526 | 1.12 | 1.19 | -0.00056
CFLBldgPGEMBTNewCZ01 | Com-Iltg-dWatt-CFL_OSbldg | PGE | MBT | New | CZ01 | 2 | 0.000526 | 0 | 2.05 | 0.000595 | -0.00222 | 2 | 0.000526 | 0 | 2.05 | 0.000595 | -0.00222 | CFL | Bldg | 2000 | 0.526 | 2000 | 0.526 | 1.03 | 1.13 | -0.00111
CFLBldgPGEMBTNewCZ02 | Com-Iltg-dWatt-CFL_OSbldg | PGE | MBT | New | CZ02 | 2 | 0.000526 | 0 | 2.13 | 0.000646 | -0.00105 | 2 | 0.000526 | 0 | 2.13 | 0.000646 | -0.00105 | CFL | Bldg | 2000 | 0.526 | 2000 | 0.526 | 1.07 | 1.23 | -0.000525
CFLBldgPGEMBTNewCZ03 | Com-Iltg-dWatt-CFL_OSbldg | PGE | MBT | New | CZ03 | 2 | 0.000526 | 0 | 2.12 | 0.000626 | -0.000994 | 2 | 0.000526 | 0 | 2.12 | 0.000626 | -0.000994 | CFL | Bldg | 2000 | 0.526 | 2000 | 0.526 | 1.06 | 1.19 | -0.000497
CFLBldgPGEMBTNewCZ04 | Com-Iltg-dWatt-CFL_OSbldg | PGE | MBT | New | CZ04 | 2 | 0.000526 | 0 | 2.15 | 0.00064 | -0.000794 | 2 | 0.000526 | 0 | 2.15 | 0.00064 | -0.000794 | CFL | Bldg | 2000 | 0.526 | 2000 | 0.526 | 1.08 | 1.22 | -0.000397
CFLBldgSCEMBTNewCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | MBT | New | CZ05 | 2 | 0.000526 | 0 | 2.15 | 0.00065 | -0.000686 | 2 | 0.000526 | 0 | 2.15 | 0.00065 | -0.000686 | CFL | Bldg | 2000 | 0.526 | 2000 | 0.526 | 1.08 | 1.24 | -0.000343
CFLBldgPGEMBTNewCZ05 | Com-Iltg-dWatt-CFL_OSbldg | PGE | MBT | New | CZ05 | 2 | 0.000526 | 0 | 2.12 | 0.000623 | -0.00053 | 2 | 0.000526 | 0 | 2.12 | 0.000623 | -0.00053 | CFL | Bldg | 2000 | 0.526 | 2000 | 0.526 | 1.06 | 1.18 | -0.000265
CFLBldgSCEMBTNewCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | MBT | New | CZ06 | 2 | 0.000526 | 0 | 2.24 | 0.000653 | -0.000656 | 2 | 0.000526 | 0 | 2.24 | 0.000653 | -0.000656 | CFL | Bldg | 2000 | 0.526 | 2000 | 0.526 | 1.12 | 1.24 | -0.000328
CFLBldgSDGMBTNewCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SDG | MBT | New | CZ06 | 2 | 0.000526 | 0 | 2.24 | 0.000658 | -0.000678 | 2 | 0.000526 | 0 | 2.24 | 0.000658 | -0.000678 | CFL | Bldg | 2000 | 0.526 | 2000 | 0.526 | 1.12 | 1.25 | -0.000339
CFLBldgSDGMBTNewCZ07 | Com-Iltg-dWatt-CFL_OSbldg | SDG | MBT | New | CZ07 | 2 | 0.000526 | 0 | 2.23 | 0.000652 | 0 | 2 | 0.000526 | 0 | 2.23 | 0.000652 | 0 | CFL | Bldg | 2000 | 0.526 | 2000 | 0.526 | 1.12 | 1.24 | 0
CFLBldgSCEMBTNewCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | MBT | New | CZ08 | 2 | 0.000526 | 0 | 2.25 | 0.00067 | -0.000526 | 2 | 0.000526 | 0 | 2.25 | 0.00067 | -0.000526 | CFL | Bldg | 2000 | 0.526 | 2000 | 0.526 | 1.13 | 1.27 | -0.000263
CFLBldgSDGMBTNewCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SDG | MBT | New | CZ08 | 2 | 0.000526 | 0 | 2.25 | 0.000675 | -0.000542 | 2 | 0.000526 | 0 | 2.25 | 0.000675 | -0.000542 | CFL | Bldg | 2000 | 0.526 | 2000 | 0.526 | 1.13 | 1.28 | -0.000271
CFLBldgSCEMBTNewCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | MBT | New | CZ09 | 2 | 0.000526 | 0 | 2.24 | 0.000685 | -0.000618 | 2 | 0.000526 | 0 | 2.24 | 0.000685 | -0.000618 | CFL | Bldg | 2000 | 0.526 | 2000 | 0.526 | 1.12 | 1.3 | -0.000309
CFLBldgSDGMBTNewCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SDG | MBT | New | CZ10 | 2 | 0.000526 | 0 | 2.26 | 0.000702 | -0.000672 | 2 | 0.000526 | 0 | 2.26 | 0.000702 | -0.000672 | CFL | Bldg | 2000 | 0.526 | 2000 | 0.526 | 1.13 | 1.33 | -0.000336
CFLBldgSCEMBTNewCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | MBT | New | CZ10 | 2 | 0.000526 | 0 | 2.25 | 0.000696 | -0.000652 | 2 | 0.000526 | 0 | 2.25 | 0.000696 | -0.000652 | CFL | Bldg | 2000 | 0.526 | 2000 | 0.526 | 1.13 | 1.32 | -0.000326
CFLBldgPGEMBTNewCZ11 | Com-Iltg-dWatt-CFL_OSbldg | PGE | MBT | New | CZ11 | 2 | 0.000526 | 0 | 2.18 | 0.000652 | -0.0011 | 2 | 0.000526 | 0 | 2.18 | 0.000652 | -0.0011 | CFL | Bldg | 2000 | 0.526 | 2000 | 0.526 | 1.09 | 1.24 | -0.00055
CFLBldgPGEMBTNewCZ12 | Com-Iltg-dWatt-CFL_OSbldg | PGE | MBT | New | CZ12 | 2 | 0.000526 | 0 | 2.16 | 0.000647 | -0.000952 | 2 | 0.000526 | 0 | 2.16 | 0.000647 | -0.000952 | CFL | Bldg | 2000 | 0.526 | 2000 | 0.526 | 1.08 | 1.23 | -0.000476
CFLBldgPGEMBTNewCZ13 | Com-Iltg-dWatt-CFL_OSbldg | PGE | MBT | New | CZ13 | 2 | 0.000526 | 0 | 2.18 | 0.000645 | -0.000886 | 2 | 0.000526 | 0 | 2.18 | 0.000645 | -0.000886 | CFL | Bldg | 2000 | 0.526 | 2000 | 0.526 | 1.09 | 1.23 | -0.000443
CFLBldgSCEMBTNewCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | MBT | New | CZ13 | 2 | 0.000526 | 0 | 2.23 | 0.000677 | -0.00115 | 2 | 0.000526 | 0 | 2.23 | 0.000677 | -0.00115 | CFL | Bldg | 2000 | 0.526 | 2000 | 0.526 | 1.12 | 1.29 | -0.000575
CFLBldgSDGMBTNewCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SDG | MBT | New | CZ14 | 2 | 0.000526 | 0 | 2.24 | 0.000693 | -0.00131 | 2 | 0.000526 | 0 | 2.24 | 0.000693 | -0.00131 | CFL | Bldg | 2000 | 0.526 | 2000 | 0.526 | 1.12 | 1.32 | -0.000655
CFLBldgSCEMBTNewCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | MBT | New | CZ14 | 2 | 0.000526 | 0 | 2.23 | 0.000687 | -0.00126 | 2 | 0.000526 | 0 | 2.23 | 0.000687 | -0.00126 | CFL | Bldg | 2000 | 0.526 | 2000 | 0.526 | 1.12 | 1.31 | -0.00063
CFLBldgSDGMBTNewCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SDG | MBT | New | CZ15 | 2 | 0.000526 | 0 | 2.38 | 0.000703 | 0 | 2 | 0.000526 | 0 | 2.38 | 0.000703 | 0 | CFL | Bldg | 2000 | 0.526 | 2000 | 0.526 | 1.19 | 1.34 | 0
CFLBldgSCEMBTNewCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | MBT | New | CZ15 | 2 | 0.000526 | 0 | 2.37 | 0.000696 | 0 | 2 | 0.000526 | 0 | 2.37 | 0.000696 | 0 | CFL | Bldg | 2000 | 0.526 | 2000 | 0.526 | 1.19 | 1.32 | 0
CFLBldgPGEMBTNewCZ16 | Com-Iltg-dWatt-CFL_OSbldg | PGE | MBT | New | CZ16 | 2 | 0.000526 | 0 | 2.09 | 0.000624 | -0.00412 | 2 | 0.000526 | 0 | 2.09 | 0.000624 | -0.00412 | CFL | Bldg | 2000 | 0.526 | 2000 | 0.526 | 1.05 | 1.19 | -0.00206
CFLBldgSCEMBTNewCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | MBT | New | CZ16 | 2 | 0.000526 | 0 | 2.11 | 0.00065 | -0.0043 | 2 | 0.000526 | 0 | 2.11 | 0.00065 | -0.0043 | CFL | Bldg | 2000 | 0.526 | 2000 | 0.526 | 1.06 | 1.24 | -0.00215
CFLBldgSDGMBTNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SDG | MBT | New | IOU | 2 | 0.000526 | 0 | 2.24 | 0.000668 | -0.000249 | 2 | 0.000526 | 0 | 2.24 | 0.000668 | -0.000249 | CFL | Bldg | 2000 | 0.526 | 2000 | 0.526 | 1.12 | 1.27 | -0.000125
CFLBldgPGEMBTNewIOU | Com-Iltg-dWatt-CFL_OSbldg | PGE | MBT | New | IOU | 2 | 0.000526 | 0 | 2.21 | 0.000672 | -0.00131 | 2 | 0.000526 | 0 | 2.21 | 0.000672 | -0.00131 | CFL | Bldg | 2000 | 0.526 | 2000 | 0.526 | 1.11 | 1.28 | -0.000655
CFLBldgSCEMBTNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | MBT | New | IOU | 2 | 0.000526 | 0 | 2.27 | 0.000686 | -0.000589 | 2 | 0.000526 | 0 | 2.27 | 0.000686 | -0.000589 | CFL | Bldg | 2000 | 0.526 | 2000 | 0.526 | 1.14 | 1.3 | -0.000295
CFLBldgSCGMBTNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SCG | MBT | New | IOU | 2 | 0.000526 | 0 | 2.27 | 0.000686 | -0.000589 | 2 | 0.000526 | 0 | 2.27 | 0.000686 | -0.000589 | CFL | Bldg | 2000 | 0.526 | 2000 | 0.526 | 1.14 | 1.3 | -0.000295
CFLBldgPGEMLIExCZ01 | Com-Iltg-dWatt-CFL_OSbldg | PGE | MLI | Ex | CZ01 | 2.26 | 0.000515 | 0 | 2.2 | 0.000586 | -0.026 | 2.26 | 0.000514 | 0 | 2.2 | 0.000585 | -0.026 | CFL | Bldg | 2260 | 0.515 | 2260 | 0.514 | 0.973 | 1.14 | -0.0115
CFLBldgPGEMLIExCZ02 | Com-Iltg-dWatt-CFL_OSbldg | PGE | MLI | Ex | CZ02 | 2.26 | 0.000515 | 0 | 2.36 | 0.000597 | -0.0129 | 2.26 | 0.000514 | 0 | 2.36 | 0.000596 | -0.0129 | CFL | Bldg | 2260 | 0.515 | 2260 | 0.514 | 1.04 | 1.16 | -0.00571
CFLBldgPGEMLIExCZ03 | Com-Iltg-dWatt-CFL_OSbldg | PGE | MLI | Ex | CZ03 | 2.26 | 0.000515 | 0 | 2.35 | 0.000597 | -0.0119 | 2.26 | 0.000514 | 0 | 2.35 | 0.000596 | -0.0119 | CFL | Bldg | 2260 | 0.515 | 2260 | 0.514 | 1.04 | 1.16 | -0.00527
CFLBldgPGEMLIExCZ04 | Com-Iltg-dWatt-CFL_OSbldg | PGE | MLI | Ex | CZ04 | 2.26 | 0.000515 | 0 | 2.38 | 0.000595 | -0.00963 | 2.26 | 0.000514 | 0 | 2.38 | 0.000594 | -0.00963 | CFL | Bldg | 2260 | 0.515 | 2260 | 0.514 | 1.05 | 1.16 | -0.00426
CFLBldgPGEMLIExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | PGE | MLI | Ex | CZ05 | 2.26 | 0.000515 | 0 | 2.38 | 0.000623 | -0.011 | 2.26 | 0.000514 | 0 | 2.38 | 0.000622 | -0.011 | CFL | Bldg | 2260 | 0.515 | 2260 | 0.514 | 1.05 | 1.21 | -0.00487
CFLBldgSCEMLIExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | MLI | Ex | CZ05 | 2.26 | 0.000515 | 0 | 2.38 | 0.000623 | -0.011 | 2.26 | 0.000514 | 0 | 2.38 | 0.000622 | -0.011 | CFL | Bldg | 2260 | 0.515 | 2260 | 0.514 | 1.05 | 1.21 | -0.00487
CFLBldgSCGMLIExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCG | MLI | Ex | CZ05 | 2.26 | 0.000515 | 0 | 2.38 | 0.000623 | -0.011 | 2.26 | 0.000514 | 0 | 2.38 | 0.000622 | -0.011 | CFL | Bldg | 2260 | 0.515 | 2260 | 0.514 | 1.05 | 1.21 | -0.00487
CFLBldgSCGMLIExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCG | MLI | Ex | CZ06 | 2.26 | 0.000515 | 0 | 2.45 | 0.000611 | -0.00486 | 2.26 | 0.000514 | 0 | 2.45 | 0.00061 | -0.00486 | CFL | Bldg | 2260 | 0.515 | 2260 | 0.514 | 1.08 | 1.19 | -0.00215
CFLBldgSCEMLIExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | MLI | Ex | CZ06 | 2.26 | 0.000515 | 0 | 2.45 | 0.000611 | -0.00486 | 2.26 | 0.000514 | 0 | 2.45 | 0.00061 | -0.00486 | CFL | Bldg | 2260 | 0.515 | 2260 | 0.514 | 1.08 | 1.19 | -0.00215
CFLBldgSDGMLIExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SDG | MLI | Ex | CZ06 | 2.26 | 0.000515 | 0 | 2.45 | 0.000611 | -0.00486 | 2.26 | 0.000514 | 0 | 2.45 | 0.00061 | -0.00486 | CFL | Bldg | 2260 | 0.515 | 2260 | 0.514 | 1.08 | 1.19 | -0.00215
CFLBldgSDGMLIExCZ07 | Com-Iltg-dWatt-CFL_OSbldg | SDG | MLI | Ex | CZ07 | 2.26 | 0.000515 | 0 | 2.44 | 0.00061 | -0.00251 | 2.26 | 0.000514 | 0 | 2.44 | 0.000609 | -0.00251 | CFL | Bldg | 2260 | 0.515 | 2260 | 0.514 | 1.08 | 1.18 | -0.00111
CFLBldgSCEMLIExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | MLI | Ex | CZ08 | 2.26 | 0.000515 | 0 | 2.47 | 0.00061 | -0.004 | 2.26 | 0.000514 | 0 | 2.47 | 0.000609 | -0.004 | CFL | Bldg | 2260 | 0.515 | 2260 | 0.514 | 1.09 | 1.18 | -0.00177
CFLBldgSCGMLIExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCG | MLI | Ex | CZ08 | 2.26 | 0.000515 | 0 | 2.47 | 0.00061 | -0.004 | 2.26 | 0.000514 | 0 | 2.47 | 0.000609 | -0.004 | CFL | Bldg | 2260 | 0.515 | 2260 | 0.514 | 1.09 | 1.18 | -0.00177
CFLBldgSDGMLIExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SDG | MLI | Ex | CZ08 | 2.26 | 0.000515 | 0 | 2.47 | 0.00061 | -0.004 | 2.26 | 0.000514 | 0 | 2.47 | 0.000609 | -0.004 | CFL | Bldg | 2260 | 0.515 | 2260 | 0.514 | 1.09 | 1.18 | -0.00177
CFLBldgSCEMLIExCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | MLI | Ex | CZ09 | 2.26 | 0.000515 | 0 | 2.51 | 0.000625 | -0.00427 | 2.26 | 0.000514 | 0 | 2.51 | 0.000623 | -0.00427 | CFL | Bldg | 2260 | 0.515 | 2260 | 0.514 | 1.11 | 1.21 | -0.00189
CFLBldgSCGMLIExCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCG | MLI | Ex | CZ09 | 2.26 | 0.000515 | 0 | 2.51 | 0.000625 | -0.00427 | 2.26 | 0.000514 | 0 | 2.51 | 0.000623 | -0.00427 | CFL | Bldg | 2260 | 0.515 | 2260 | 0.514 | 1.11 | 1.21 | -0.00189
CFLBldgSDGMLIExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SDG | MLI | Ex | CZ10 | 2.26 | 0.000515 | 0 | 2.47 | 0.000626 | -0.00545 | 2.26 | 0.000514 | 0 | 2.47 | 0.000625 | -0.00545 | CFL | Bldg | 2260 | 0.515 | 2260 | 0.514 | 1.09 | 1.22 | -0.00241
CFLBldgSCGMLIExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCG | MLI | Ex | CZ10 | 2.26 | 0.000515 | 0 | 2.47 | 0.000626 | -0.00545 | 2.26 | 0.000514 | 0 | 2.47 | 0.000625 | -0.00545 | CFL | Bldg | 2260 | 0.515 | 2260 | 0.514 | 1.09 | 1.22 | -0.00241
CFLBldgSCEMLIExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | MLI | Ex | CZ10 | 2.26 | 0.000515 | 0 | 2.47 | 0.000626 | -0.00545 | 2.26 | 0.000514 | 0 | 2.47 | 0.000625 | -0.00545 | CFL | Bldg | 2260 | 0.515 | 2260 | 0.514 | 1.09 | 1.22 | -0.00241
CFLBldgPGEMLIExCZ11 | Com-Iltg-dWatt-CFL_OSbldg | PGE | MLI | Ex | CZ11 | 2.26 | 0.000515 | 0 | 2.36 | 0.000596 | -0.0135 | 2.26 | 0.000514 | 0 | 2.36 | 0.000595 | -0.0135 | CFL | Bldg | 2260 | 0.515 | 2260 | 0.514 | 1.04 | 1.16 | -0.00597
CFLBldgPGEMLIExCZ12 | Com-Iltg-dWatt-CFL_OSbldg | PGE | MLI | Ex | CZ12 | 2.26 | 0.000515 | 0 | 2.36 | 0.0006 | -0.013 | 2.26 | 0.000514 | 0 | 2.36 | 0.000599 | -0.013 | CFL | Bldg | 2260 | 0.515 | 2260 | 0.514 | 1.04 | 1.17 | -0.00575
CFLBldgSCEMLIExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | MLI | Ex | CZ13 | 2.26 | 0.000515 | 0 | 2.42 | 0.000612 | -0.0122 | 2.26 | 0.000514 | 0 | 2.42 | 0.000611 | -0.0122 | CFL | Bldg | 2260 | 0.515 | 2260 | 0.514 | 1.07 | 1.19 | -0.0054
CFLBldgPGEMLIExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | PGE | MLI | Ex | CZ13 | 2.26 | 0.000515 | 0 | 2.42 | 0.000612 | -0.0122 | 2.26 | 0.000514 | 0 | 2.42 | 0.000611 | -0.0122 | CFL | Bldg | 2260 | 0.515 | 2260 | 0.514 | 1.07 | 1.19 | -0.0054
CFLBldgSCGMLIExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCG | MLI | Ex | CZ13 | 2.26 | 0.000515 | 0 | 2.42 | 0.000612 | -0.0122 | 2.26 | 0.000514 | 0 | 2.42 | 0.000611 | -0.0122 | CFL | Bldg | 2260 | 0.515 | 2260 | 0.514 | 1.07 | 1.19 | -0.0054
CFLBldgSDGMLIExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SDG | MLI | Ex | CZ14 | 2.26 | 0.000515 | 0 | 2.39 | 0.000619 | -0.0151 | 2.26 | 0.000514 | 0 | 2.39 | 0.000617 | -0.0151 | CFL | Bldg | 2260 | 0.515 | 2260 | 0.514 | 1.06 | 1.2 | -0.00668
CFLBldgSCGMLIExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCG | MLI | Ex | CZ14 | 2.26 | 0.000515 | 0 | 2.39 | 0.000619 | -0.0151 | 2.26 | 0.000514 | 0 | 2.39 | 0.000617 | -0.0151 | CFL | Bldg | 2260 | 0.515 | 2260 | 0.514 | 1.06 | 1.2 | -0.00668
CFLBldgSCEMLIExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | MLI | Ex | CZ14 | 2.26 | 0.000515 | 0 | 2.39 | 0.000619 | -0.0151 | 2.26 | 0.000514 | 0 | 2.39 | 0.000617 | -0.0151 | CFL | Bldg | 2260 | 0.515 | 2260 | 0.514 | 1.06 | 1.2 | -0.00668
CFLBldgSDGMLIExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SDG | MLI | Ex | CZ15 | 2.26 | 0.000515 | 0 | 2.65 | 0.000617 | -0.00142 | 2.26 | 0.000514 | 0 | 2.65 | 0.000616 | -0.00142 | CFL | Bldg | 2260 | 0.515 | 2260 | 0.514 | 1.17 | 1.2 | -0.000628
CFLBldgSCEMLIExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | MLI | Ex | CZ15 | 2.26 | 0.000515 | 0 | 2.65 | 0.000617 | -0.00142 | 2.26 | 0.000514 | 0 | 2.65 | 0.000616 | -0.00142 | CFL | Bldg | 2260 | 0.515 | 2260 | 0.514 | 1.17 | 1.2 | -0.000628
CFLBldgSCGMLIExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCG | MLI | Ex | CZ15 | 2.26 | 0.000515 | 0 | 2.65 | 0.000617 | -0.00142 | 2.26 | 0.000514 | 0 | 2.65 | 0.000616 | -0.00142 | CFL | Bldg | 2260 | 0.515 | 2260 | 0.514 | 1.17 | 1.2 | -0.000628
CFLBldgSCEMLIExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | MLI | Ex | CZ16 | 2.26 | 0.000515 | 0 | 2.23 | 0.000606 | -0.0273 | 2.26 | 0.000514 | 0 | 2.23 | 0.000605 | -0.0273 | CFL | Bldg | 2260 | 0.515 | 2260 | 0.514 | 0.987 | 1.18 | -0.0121
CFLBldgSCGMLIExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCG | MLI | Ex | CZ16 | 2.26 | 0.000515 | 0 | 2.23 | 0.000606 | -0.0273 | 2.26 | 0.000514 | 0 | 2.23 | 0.000605 | -0.0273 | CFL | Bldg | 2260 | 0.515 | 2260 | 0.514 | 0.987 | 1.18 | -0.0121
CFLBldgPGEMLIExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | PGE | MLI | Ex | CZ16 | 2.26 | 0.000515 | 0 | 2.23 | 0.000606 | -0.0273 | 2.26 | 0.000514 | 0 | 2.23 | 0.000605 | -0.0273 | CFL | Bldg | 2260 | 0.515 | 2260 | 0.514 | 0.987 | 1.18 | -0.0121
CFLBldgPGEMLIExIOU | Com-Iltg-dWatt-CFL_OSbldg | PGE | MLI | Ex | IOU | 2.26 | 0.000515 | 0 | 2.37 | 0.0006 | -0.0121 | 2.26 | 0.000514 | 0 | 2.37 | 0.000599 | -0.0121 | CFL | Bldg | 2260 | 0.515 | 2260 | 0.514 | 1.05 | 1.17 | -0.00535
CFLBldgSDGMLIExIOU | Com-Iltg-dWatt-CFL_OSbldg | SDG | MLI | Ex | IOU | 2.26 | 0.000515 | 0 | 2.45 | 0.000615 | -0.00362 | 2.26 | 0.000514 | 0 | 2.45 | 0.000614 | -0.00362 | CFL | Bldg | 2260 | 0.515 | 2260 | 0.514 | 1.08 | 1.19 | -0.0016
CFLBldgSCGMLIExIOU | Com-Iltg-dWatt-CFL_OSbldg | SCG | MLI | Ex | IOU | 2.26 | 0.000515 | 0 | 2.48 | 0.000617 | -0.00524 | 2.26 | 0.000514 | 0 | 2.48 | 0.000615 | -0.00524 | CFL | Bldg | 2260 | 0.515 | 2260 | 0.514 | 1.1 | 1.2 | -0.00232
CFLBldgSCEMLIExIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | MLI | Ex | IOU | 2.26 | 0.000515 | 0 | 2.47 | 0.000616 | -0.00545 | 2.26 | 0.000514 | 0 | 2.47 | 0.000615 | -0.00545 | CFL | Bldg | 2260 | 0.515 | 2260 | 0.514 | 1.09 | 1.2 | -0.00241
CFLBldgPGEMLINewCZ01 | Com-Iltg-dWatt-CFL_OSbldg | PGE | MLI | New | CZ01 | 2.26 | 0.000513 | 0 | 2.14 | 0.000558 | -0.0346 | 2.26 | 0.000513 | 0 | 2.14 | 0.000558 | -0.0346 | CFL | Bldg | 2260 | 0.513 | 2260 | 0.513 | 0.947 | 1.09 | -0.0153
CFLBldgPGEMLINewCZ02 | Com-Iltg-dWatt-CFL_OSbldg | PGE | MLI | New | CZ02 | 2.26 | 0.000513 | 0 | 2.28 | 0.000591 | -0.0191 | 2.26 | 0.000513 | 0 | 2.28 | 0.000591 | -0.0191 | CFL | Bldg | 2260 | 0.513 | 2260 | 0.513 | 1.01 | 1.15 | -0.00845
CFLBldgPGEMLINewCZ03 | Com-Iltg-dWatt-CFL_OSbldg | PGE | MLI | New | CZ03 | 2.26 | 0.000513 | 0 | 2.24 | 0.000598 | -0.0187 | 2.26 | 0.000513 | 0 | 2.24 | 0.000598 | -0.0187 | CFL | Bldg | 2260 | 0.513 | 2260 | 0.513 | 0.991 | 1.17 | -0.00827
CFLBldgPGEMLINewCZ04 | Com-Iltg-dWatt-CFL_OSbldg | PGE | MLI | New | CZ04 | 2.26 | 0.000513 | 0 | 2.31 | 0.00059 | -0.0151 | 2.26 | 0.000513 | 0 | 2.31 | 0.00059 | -0.0151 | CFL | Bldg | 2260 | 0.513 | 2260 | 0.513 | 1.02 | 1.15 | -0.00668
CFLBldgSCEMLINewCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | MLI | New | CZ05 | 2.26 | 0.000513 | 0 | 2.25 | 0.00061 | -0.0181 | 2.26 | 0.000513 | 0 | 2.25 | 0.00061 | -0.0181 | CFL | Bldg | 2260 | 0.513 | 2260 | 0.513 | 0.996 | 1.19 | -0.00801
CFLBldgPGEMLINewCZ05 | Com-Iltg-dWatt-CFL_OSbldg | PGE | MLI | New | CZ05 | 2.26 | 0.000513 | 0 | 2.24 | 0.000588 | -0.0183 | 2.26 | 0.000513 | 0 | 2.24 | 0.000588 | -0.0183 | CFL | Bldg | 2260 | 0.513 | 2260 | 0.513 | 0.991 | 1.15 | -0.0081
CFLBldgSDGMLINewCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SDG | MLI | New | CZ06 | 2.26 | 0.000513 | 0 | 2.38 | 0.000602 | -0.00877 | 2.26 | 0.000513 | 0 | 2.38 | 0.000602 | -0.00877 | CFL | Bldg | 2260 | 0.513 | 2260 | 0.513 | 1.05 | 1.17 | -0.00388
CFLBldgSCEMLINewCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | MLI | New | CZ06 | 2.26 | 0.000513 | 0 | 2.37 | 0.000599 | -0.00816 | 2.26 | 0.000513 | 0 | 2.37 | 0.000599 | -0.00816 | CFL | Bldg | 2260 | 0.513 | 2260 | 0.513 | 1.05 | 1.17 | -0.00361
CFLBldgSDGMLINewCZ07 | Com-Iltg-dWatt-CFL_OSbldg | SDG | MLI | New | CZ07 | 2.26 | 0.000513 | 0 | 2.36 | 0.000601 | -0.00511 | 2.26 | 0.000513 | 0 | 2.36 | 0.000601 | -0.00511 | CFL | Bldg | 2260 | 0.513 | 2260 | 0.513 | 1.04 | 1.17 | -0.00226
CFLBldgSDGMLINewCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SDG | MLI | New | CZ08 | 2.26 | 0.000513 | 0 | 2.42 | 0.000606 | -0.00705 | 2.26 | 0.000513 | 0 | 2.42 | 0.000606 | -0.00705 | CFL | Bldg | 2260 | 0.513 | 2260 | 0.513 | 1.07 | 1.18 | -0.00312
CFLBldgSCEMLINewCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | MLI | New | CZ08 | 2.26 | 0.000513 | 0 | 2.41 | 0.000603 | -0.00658 | 2.26 | 0.000513 | 0 | 2.41 | 0.000603 | -0.00658 | CFL | Bldg | 2260 | 0.513 | 2260 | 0.513 | 1.07 | 1.18 | -0.00291
CFLBldgSCEMLINewCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | MLI | New | CZ09 | 2.26 | 0.000513 | 0 | 2.47 | 0.000659 | -0.00757 | 2.26 | 0.000513 | 0 | 2.47 | 0.000659 | -0.00757 | CFL | Bldg | 2260 | 0.513 | 2260 | 0.513 | 1.09 | 1.28 | -0.00335
CFLBldgSDGMLINewCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SDG | MLI | New | CZ10 | 2.26 | 0.000513 | 0 | 2.5 | 0.000676 | -0.00886 | 2.26 | 0.000513 | 0 | 2.5 | 0.000676 | -0.00886 | CFL | Bldg | 2260 | 0.513 | 2260 | 0.513 | 1.11 | 1.32 | -0.00392
CFLBldgSCEMLINewCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | MLI | New | CZ10 | 2.26 | 0.000513 | 0 | 2.49 | 0.00067 | -0.00827 | 2.26 | 0.000513 | 0 | 2.49 | 0.00067 | -0.00827 | CFL | Bldg | 2260 | 0.513 | 2260 | 0.513 | 1.1 | 1.31 | -0.00366
CFLBldgPGEMLINewCZ11 | Com-Iltg-dWatt-CFL_OSbldg | PGE | MLI | New | CZ11 | 2.26 | 0.000513 | 0 | 2.37 | 0.000613 | -0.016 | 2.26 | 0.000513 | 0 | 2.37 | 0.000613 | -0.016 | CFL | Bldg | 2260 | 0.513 | 2260 | 0.513 | 1.05 | 1.19 | -0.00708
CFLBldgPGEMLINewCZ12 | Com-Iltg-dWatt-CFL_OSbldg | PGE | MLI | New | CZ12 | 2.26 | 0.000513 | 0 | 2.33 | 0.000605 | -0.0175 | 2.26 | 0.000513 | 0 | 2.33 | 0.000605 | -0.0175 | CFL | Bldg | 2260 | 0.513 | 2260 | 0.513 | 1.03 | 1.18 | -0.00774
CFLBldgSCEMLINewCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | MLI | New | CZ13 | 2.26 | 0.000513 | 0 | 2.43 | 0.000645 | -0.015 | 2.26 | 0.000513 | 0 | 2.43 | 0.000645 | -0.015 | CFL | Bldg | 2260 | 0.513 | 2260 | 0.513 | 1.08 | 1.26 | -0.00664
CFLBldgPGEMLINewCZ13 | Com-Iltg-dWatt-CFL_OSbldg | PGE | MLI | New | CZ13 | 2.26 | 0.000513 | 0 | 2.39 | 0.000617 | -0.0151 | 2.26 | 0.000513 | 0 | 2.39 | 0.000617 | -0.0151 | CFL | Bldg | 2260 | 0.513 | 2260 | 0.513 | 1.06 | 1.2 | -0.00668
CFLBldgSDGMLINewCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SDG | MLI | New | CZ14 | 2.26 | 0.000513 | 0 | 2.4 | 0.00063 | -0.0174 | 2.26 | 0.000513 | 0 | 2.4 | 0.00063 | -0.0174 | CFL | Bldg | 2260 | 0.513 | 2260 | 0.513 | 1.06 | 1.23 | -0.0077
CFLBldgSCEMLINewCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | MLI | New | CZ14 | 2.26 | 0.000513 | 0 | 2.39 | 0.000626 | -0.0163 | 2.26 | 0.000513 | 0 | 2.39 | 0.000626 | -0.0163 | CFL | Bldg | 2260 | 0.513 | 2260 | 0.513 | 1.06 | 1.22 | -0.00721
CFLBldgSCEMLINewCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | MLI | New | CZ15 | 2.26 | 0.000513 | 0 | 2.65 | 0.000681 | -0.00139 | 2.26 | 0.000513 | 0 | 2.65 | 0.000681 | -0.00139 | CFL | Bldg | 2260 | 0.513 | 2260 | 0.513 | 1.17 | 1.33 | -0.000615
CFLBldgSDGMLINewCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SDG | MLI | New | CZ15 | 2.26 | 0.000513 | 0 | 2.67 | 0.000687 | -0.00148 | 2.26 | 0.000513 | 0 | 2.67 | 0.000687 | -0.00148 | CFL | Bldg | 2260 | 0.513 | 2260 | 0.513 | 1.18 | 1.34 | -0.000655
CFLBldgPGEMLINewCZ16 | Com-Iltg-dWatt-CFL_OSbldg | PGE | MLI | New | CZ16 | 2.26 | 0.000513 | 0 | 2.21 | 0.000583 | -0.0294 | 2.26 | 0.000513 | 0 | 2.21 | 0.000583 | -0.0294 | CFL | Bldg | 2260 | 0.513 | 2260 | 0.513 | 0.978 | 1.14 | -0.013
CFLBldgSCEMLINewCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | MLI | New | CZ16 | 2.26 | 0.000513 | 0 | 2.23 | 0.000603 | -0.0289 | 2.26 | 0.000513 | 0 | 2.23 | 0.000603 | -0.0289 | CFL | Bldg | 2260 | 0.513 | 2260 | 0.513 | 0.987 | 1.18 | -0.0128
CFLBldgSCGMLINewIOU | Com-Iltg-dWatt-CFL_OSbldg | SCG | MLI | New | IOU | 2.26 | 0.000513 | 0 | 2.47 | 0.000641 | -0.0079 | 2.26 | 0.000513 | 0 | 2.47 | 0.000641 | -0.0079 | CFL | Bldg | 2260 | 0.513 | 2260 | 0.513 | 1.09 | 1.25 | -0.0035
CFLBldgSCEMLINewIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | MLI | New | IOU | 2.26 | 0.000513 | 0 | 2.47 | 0.000643 | -0.00791 | 2.26 | 0.000513 | 0 | 2.47 | 0.000643 | -0.00791 | CFL | Bldg | 2260 | 0.513 | 2260 | 0.513 | 1.09 | 1.25 | -0.0035
CFLBldgPGEMLINewIOU | Com-Iltg-dWatt-CFL_OSbldg | PGE | MLI | New | IOU | 2.26 | 0.000513 | 0 | 2.4 | 0.000639 | -0.0162 | 2.26 | 0.000513 | 0 | 2.4 | 0.000639 | -0.0162 | CFL | Bldg | 2260 | 0.513 | 2260 | 0.513 | 1.06 | 1.25 | -0.00717
CFLBldgSDGMLINewIOU | Com-Iltg-dWatt-CFL_OSbldg | SDG | MLI | New | IOU | 2.26 | 0.000513 | 0 | 2.41 | 0.000624 | -0.00651 | 2.26 | 0.000513 | 0 | 2.41 | 0.000624 | -0.00651 | CFL | Bldg | 2260 | 0.513 | 2260 | 0.513 | 1.07 | 1.22 | -0.00288
CFLBldgPGEMtlExCZ01 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Mtl | Ex | CZ01 | 0.993 | 8.51e-05 | 0 | 0.979 | 0.000102 | -0.00856 | 0.94 | 8e-05 | 0 | 0.927 | 9.52e-05 | -0.0081 | CFL | Bldg | 993 | 0.0851 | 940 | 0.08 | 0.986 | 1.19 | -0.00862
CFLBldgPGEMtlExCZ02 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Mtl | Ex | CZ02 | 0.993 | 8.51e-05 | 0 | 1.04 | 0.000105 | -0.00567 | 0.94 | 8e-05 | 0 | 0.979 | 9.88e-05 | -0.00537 | CFL | Bldg | 993 | 0.0851 | 940 | 0.08 | 1.04 | 1.24 | -0.00571
CFLBldgPGEMtlExCZ03 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Mtl | Ex | CZ03 | 0.994 | 8.52e-05 | 0 | 1.05 | 0.000103 | -0.00551 | 0.94 | 8e-05 | 0 | 0.99 | 9.66e-05 | -0.00521 | CFL | Bldg | 994 | 0.0852 | 940 | 0.08 | 1.05 | 1.21 | -0.00554
CFLBldgPGEMtlExCZ04 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Mtl | Ex | CZ04 | 0.993 | 8.51e-05 | 0 | 1.06 | 0.000104 | -0.00454 | 0.94 | 8e-05 | 0 | 1 | 9.78e-05 | -0.00431 | CFL | Bldg | 993 | 0.0851 | 940 | 0.08 | 1.06 | 1.22 | -0.00459
CFLBldgSCGMtlExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCG | Mtl | Ex | CZ05 | 0.994 | 8.52e-05 | 0 | 1.06 | 0.000107 | -0.00475 | 0.94 | 8e-05 | 0 | 1 | 0.0001 | -0.00449 | CFL | Bldg | 994 | 0.0852 | 940 | 0.08 | 1.06 | 1.25 | -0.00478
CFLBldgPGEMtlExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Mtl | Ex | CZ05 | 0.993 | 8.51e-05 | 0 | 1.06 | 0.000107 | -0.00474 | 0.94 | 8e-05 | 0 | 1 | 0.0001 | -0.00449 | CFL | Bldg | 993 | 0.0851 | 940 | 0.08 | 1.06 | 1.25 | -0.00478
CFLBldgSCEMtlExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Mtl | Ex | CZ05 | 0.994 | 8.52e-05 | 0 | 1.06 | 0.000107 | -0.00475 | 0.94 | 8e-05 | 0 | 1 | 0.0001 | -0.00449 | CFL | Bldg | 994 | 0.0852 | 940 | 0.08 | 1.06 | 1.25 | -0.00478
CFLBldgSCEMtlExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Mtl | Ex | CZ06 | 0.994 | 8.52e-05 | 0 | 1.13 | 0.000107 | -0.00264 | 0.94 | 8e-05 | 0 | 1.06 | 0.0001 | -0.0025 | CFL | Bldg | 994 | 0.0852 | 940 | 0.08 | 1.13 | 1.25 | -0.00266
CFLBldgSDGMtlExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Mtl | Ex | CZ06 | 0.99 | 8.48e-05 | 0 | 1.12 | 0.000106 | -0.00263 | 0.94 | 8e-05 | 0 | 1.06 | 0.0001 | -0.0025 | CFL | Bldg | 990 | 0.0848 | 940 | 0.08 | 1.13 | 1.25 | -0.00266
CFLBldgSCGMtlExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCG | Mtl | Ex | CZ06 | 0.994 | 8.52e-05 | 0 | 1.13 | 0.000107 | -0.00264 | 0.94 | 8e-05 | 0 | 1.06 | 0.0001 | -0.0025 | CFL | Bldg | 994 | 0.0852 | 940 | 0.08 | 1.13 | 1.25 | -0.00266
CFLBldgSDGMtlExCZ07 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Mtl | Ex | CZ07 | 0.99 | 8.48e-05 | 0 | 1.14 | 0.000105 | -0.00187 | 0.94 | 8e-05 | 0 | 1.08 | 9.98e-05 | -0.00178 | CFL | Bldg | 990 | 0.0848 | 940 | 0.08 | 1.15 | 1.25 | -0.00189
CFLBldgSCGMtlExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCG | Mtl | Ex | CZ08 | 0.993 | 8.52e-05 | 0 | 1.14 | 0.000108 | -0.0022 | 0.94 | 8e-05 | 0 | 1.08 | 0.000102 | -0.00209 | CFL | Bldg | 993 | 0.0852 | 940 | 0.08 | 1.15 | 1.28 | -0.00222
CFLBldgSDGMtlExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Mtl | Ex | CZ08 | 0.99 | 8.48e-05 | 0 | 1.13 | 0.000107 | -0.0022 | 0.94 | 8e-05 | 0 | 1.08 | 0.000102 | -0.00209 | CFL | Bldg | 990 | 0.0848 | 940 | 0.08 | 1.15 | 1.28 | -0.00222
CFLBldgSCEMtlExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Mtl | Ex | CZ08 | 0.994 | 8.52e-05 | 0 | 1.14 | 0.000108 | -0.00221 | 0.94 | 8e-05 | 0 | 1.08 | 0.000102 | -0.00209 | CFL | Bldg | 994 | 0.0852 | 940 | 0.08 | 1.15 | 1.28 | -0.00222
CFLBldgSCGMtlExCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCG | Mtl | Ex | CZ09 | 0.993 | 8.51e-05 | 0 | 1.15 | 0.000112 | -0.00231 | 0.94 | 8e-05 | 0 | 1.09 | 0.000105 | -0.00219 | CFL | Bldg | 993 | 0.0851 | 940 | 0.08 | 1.16 | 1.31 | -0.00233
CFLBldgSCEMtlExCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Mtl | Ex | CZ09 | 0.993 | 8.51e-05 | 0 | 1.15 | 0.000112 | -0.00231 | 0.94 | 8e-05 | 0 | 1.09 | 0.000105 | -0.00219 | CFL | Bldg | 993 | 0.0851 | 940 | 0.08 | 1.16 | 1.31 | -0.00233
CFLBldgSCEMtlExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Mtl | Ex | CZ10 | 0.99 | 8.48e-05 | 0 | 1.12 | 0.000111 | -0.00262 | 0.94 | 8e-05 | 0 | 1.07 | 0.000105 | -0.00249 | CFL | Bldg | 990 | 0.0848 | 940 | 0.08 | 1.14 | 1.31 | -0.00265
CFLBldgSDGMtlExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Mtl | Ex | CZ10 | 0.99 | 8.48e-05 | 0 | 1.12 | 0.000111 | -0.00262 | 0.94 | 8e-05 | 0 | 1.07 | 0.000105 | -0.00249 | CFL | Bldg | 990 | 0.0848 | 940 | 0.08 | 1.14 | 1.31 | -0.00265
CFLBldgSCGMtlExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCG | Mtl | Ex | CZ10 | 0.99 | 8.48e-05 | 0 | 1.12 | 0.000111 | -0.00262 | 0.94 | 8e-05 | 0 | 1.07 | 0.000105 | -0.00249 | CFL | Bldg | 990 | 0.0848 | 940 | 0.08 | 1.14 | 1.31 | -0.00265
CFLBldgPGEMtlExCZ11 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Mtl | Ex | CZ11 | 0.992 | 8.5e-05 | 0 | 1.07 | 0.000106 | -0.00477 | 0.94 | 8e-05 | 0 | 1.01 | 9.96e-05 | -0.00452 | CFL | Bldg | 992 | 0.085 | 940 | 0.08 | 1.07 | 1.25 | -0.00481
CFLBldgPGEMtlExCZ12 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Mtl | Ex | CZ12 | 0.992 | 8.5e-05 | 0 | 1.06 | 0.000106 | -0.00504 | 0.94 | 8e-05 | 0 | 1 | 9.96e-05 | -0.00478 | CFL | Bldg | 992 | 0.085 | 940 | 0.08 | 1.06 | 1.25 | -0.00509
CFLBldgPGEMtlExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Mtl | Ex | CZ13 | 0.992 | 8.5e-05 | 0 | 1.11 | 0.000112 | -0.00367 | 0.94 | 8e-05 | 0 | 1.05 | 0.000105 | -0.00347 | CFL | Bldg | 992 | 0.085 | 940 | 0.08 | 1.12 | 1.31 | -0.00369
CFLBldgSCEMtlExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Mtl | Ex | CZ13 | 0.992 | 8.5e-05 | 0 | 1.11 | 0.000111 | -0.00366 | 0.94 | 8e-05 | 0 | 1.05 | 0.000105 | -0.00347 | CFL | Bldg | 992 | 0.085 | 940 | 0.08 | 1.12 | 1.31 | -0.00369
CFLBldgSCGMtlExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCG | Mtl | Ex | CZ13 | 0.992 | 8.5e-05 | 0 | 1.11 | 0.000111 | -0.00366 | 0.94 | 8e-05 | 0 | 1.05 | 0.000105 | -0.00347 | CFL | Bldg | 992 | 0.085 | 940 | 0.08 | 1.12 | 1.31 | -0.00369
CFLBldgSDGMtlExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Mtl | Ex | CZ14 | 0.99 | 8.48e-05 | 0 | 1.09 | 0.00011 | -0.0037 | 0.94 | 8e-05 | 0 | 1.03 | 0.000104 | -0.00351 | CFL | Bldg | 990 | 0.0848 | 940 | 0.08 | 1.1 | 1.3 | -0.00373
CFLBldgSCEMtlExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Mtl | Ex | CZ14 | 0.991 | 8.49e-05 | 0 | 1.09 | 0.00011 | -0.0037 | 0.94 | 8e-05 | 0 | 1.03 | 0.000104 | -0.00351 | CFL | Bldg | 991 | 0.0849 | 940 | 0.08 | 1.1 | 1.3 | -0.00373
CFLBldgSCGMtlExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCG | Mtl | Ex | CZ14 | 0.991 | 8.49e-05 | 0 | 1.09 | 0.00011 | -0.0037 | 0.94 | 8e-05 | 0 | 1.03 | 0.000104 | -0.00351 | CFL | Bldg | 991 | 0.0849 | 940 | 0.08 | 1.1 | 1.3 | -0.00373
CFLBldgSCGMtlExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCG | Mtl | Ex | CZ15 | 0.99 | 8.48e-05 | 0 | 1.19 | 0.000112 | -0.00107 | 0.94 | 8e-05 | 0 | 1.13 | 0.000106 | -0.00102 | CFL | Bldg | 990 | 0.0848 | 940 | 0.08 | 1.2 | 1.33 | -0.00109
CFLBldgSDGMtlExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Mtl | Ex | CZ15 | 0.99 | 8.48e-05 | 0 | 1.19 | 0.000112 | -0.00107 | 0.94 | 8e-05 | 0 | 1.13 | 0.000106 | -0.00102 | CFL | Bldg | 990 | 0.0848 | 940 | 0.08 | 1.2 | 1.33 | -0.00109
CFLBldgSCEMtlExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Mtl | Ex | CZ15 | 0.99 | 8.48e-05 | 0 | 1.19 | 0.000112 | -0.00107 | 0.94 | 8e-05 | 0 | 1.13 | 0.000106 | -0.00102 | CFL | Bldg | 990 | 0.0848 | 940 | 0.08 | 1.2 | 1.33 | -0.00109
CFLBldgPGEMtlExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Mtl | Ex | CZ16 | 0.992 | 8.51e-05 | 0 | 0.987 | 0.000107 | -0.0063 | 0.94 | 8e-05 | 0 | 0.935 | 0.000101 | -0.00597 | CFL | Bldg | 992 | 0.0851 | 940 | 0.08 | 0.995 | 1.26 | -0.00635
CFLBldgSCEMtlExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Mtl | Ex | CZ16 | 0.991 | 8.49e-05 | 0 | 0.986 | 0.000106 | -0.00629 | 0.94 | 8e-05 | 0 | 0.935 | 0.000101 | -0.00597 | CFL | Bldg | 991 | 0.0849 | 940 | 0.08 | 0.995 | 1.26 | -0.00635
CFLBldgSCGMtlExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCG | Mtl | Ex | CZ16 | 0.991 | 8.49e-05 | 0 | 0.986 | 0.000106 | -0.00629 | 0.94 | 8e-05 | 0 | 0.935 | 0.000101 | -0.00597 | CFL | Bldg | 991 | 0.0849 | 940 | 0.08 | 0.995 | 1.26 | -0.00635
CFLBldgPGEMtlExIOU | Com-Iltg-dWatt-CFL_OSbldg | PGE | Mtl | Ex | IOU | 0.993 | 8.51e-05 | 0 | 1.05 | 0.000105 | -0.00515 | 0.94 | 8e-05 | 0 | 0.997 | 9.84e-05 | -0.00487 | CFL | Bldg | 993 | 0.0851 | 940 | 0.08 | 1.06 | 1.23 | -0.00518
CFLBldgSCEMtlExIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | Mtl | Ex | IOU | 0.993 | 8.51e-05 | 0 | 1.14 | 0.000109 | -0.00245 | 0.94 | 8e-05 | 0 | 1.07 | 0.000103 | -0.00232 | CFL | Bldg | 993 | 0.0851 | 940 | 0.08 | 1.14 | 1.29 | -0.00247
CFLBldgSCGMtlExIOU | Com-Iltg-dWatt-CFL_OSbldg | SCG | Mtl | Ex | IOU | 0.993 | 8.51e-05 | 0 | 1.14 | 0.000109 | -0.00242 | 0.94 | 8e-05 | 0 | 1.08 | 0.000103 | -0.00229 | CFL | Bldg | 993 | 0.0851 | 940 | 0.08 | 1.15 | 1.29 | -0.00244
CFLBldgSDGMtlExIOU | Com-Iltg-dWatt-CFL_OSbldg | SDG | Mtl | Ex | IOU | 0.99 | 8.48e-05 | 0 | 1.14 | 0.000106 | -0.00199 | 0.94 | 8e-05 | 0 | 1.08 | 0.0001 | -0.00189 | CFL | Bldg | 990 | 0.0848 | 940 | 0.08 | 1.15 | 1.25 | -0.00201
CFLBldgPGEMtlNewCZ01 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Mtl | New | CZ01 | 0.94 | 8e-05 | 0 | 0.888 | 9.51e-05 | -0.0104 | 0.94 | 8e-05 | 0 | 0.888 | 9.51e-05 | -0.0104 | CFL | Bldg | 940 | 0.08 | 940 | 0.08 | 0.945 | 1.19 | -0.0111
CFLBldgPGEMtlNewCZ02 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Mtl | New | CZ02 | 0.94 | 8e-05 | 0 | 0.962 | 0.000101 | -0.00704 | 0.94 | 8e-05 | 0 | 0.962 | 0.000101 | -0.00704 | CFL | Bldg | 940 | 0.08 | 940 | 0.08 | 1.02 | 1.26 | -0.00749
CFLBldgPGEMtlNewCZ03 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Mtl | New | CZ03 | 0.94 | 8e-05 | 0 | 0.969 | 9.79e-05 | -0.00662 | 0.94 | 8e-05 | 0 | 0.969 | 9.79e-05 | -0.00662 | CFL | Bldg | 940 | 0.08 | 940 | 0.08 | 1.03 | 1.22 | -0.00704
CFLBldgPGEMtlNewCZ04 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Mtl | New | CZ04 | 0.94 | 8e-05 | 0 | 0.993 | 0.0001 | -0.00557 | 0.94 | 8e-05 | 0 | 0.993 | 0.0001 | -0.00557 | CFL | Bldg | 940 | 0.08 | 940 | 0.08 | 1.06 | 1.25 | -0.00593
CFLBldgPGEMtlNewCZ05 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Mtl | New | CZ05 | 0.94 | 8e-05 | 0 | 0.953 | 9.7e-05 | -0.00743 | 0.94 | 8e-05 | 0 | 0.953 | 9.7e-05 | -0.00743 | CFL | Bldg | 940 | 0.08 | 940 | 0.08 | 1.01 | 1.21 | -0.0079
CFLBldgSCEMtlNewCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Mtl | New | CZ05 | 0.94 | 8e-05 | 0 | 0.968 | 0.000101 | -0.00603 | 0.94 | 8e-05 | 0 | 0.968 | 0.000101 | -0.00603 | CFL | Bldg | 940 | 0.08 | 940 | 0.08 | 1.03 | 1.26 | -0.00641
CFLBldgSDGMtlNewCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Mtl | New | CZ06 | 0.94 | 8e-05 | 0 | 1.06 | 0.000103 | -0.00329 | 0.94 | 8e-05 | 0 | 1.06 | 0.000103 | -0.00329 | CFL | Bldg | 940 | 0.08 | 940 | 0.08 | 1.13 | 1.29 | -0.0035
CFLBldgSCEMtlNewCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Mtl | New | CZ06 | 0.94 | 8e-05 | 0 | 1.06 | 0.000103 | -0.0032 | 0.94 | 8e-05 | 0 | 1.06 | 0.000103 | -0.0032 | CFL | Bldg | 940 | 0.08 | 940 | 0.08 | 1.13 | 1.29 | -0.0034
CFLBldgSDGMtlNewCZ07 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Mtl | New | CZ07 | 0.94 | 8e-05 | 0 | 1.08 | 0.000101 | -0.00227 | 0.94 | 8e-05 | 0 | 1.08 | 0.000101 | -0.00227 | CFL | Bldg | 940 | 0.08 | 940 | 0.08 | 1.15 | 1.26 | -0.00241
CFLBldgSCEMtlNewCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Mtl | New | CZ08 | 0.94 | 8e-05 | 0 | 1.08 | 0.000105 | -0.00266 | 0.94 | 8e-05 | 0 | 1.08 | 0.000105 | -0.00266 | CFL | Bldg | 940 | 0.08 | 940 | 0.08 | 1.15 | 1.31 | -0.00283
CFLBldgSDGMtlNewCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Mtl | New | CZ08 | 0.94 | 8e-05 | 0 | 1.07 | 0.000104 | -0.00274 | 0.94 | 8e-05 | 0 | 1.07 | 0.000104 | -0.00274 | CFL | Bldg | 940 | 0.08 | 940 | 0.08 | 1.14 | 1.3 | -0.00291
CFLBldgSCEMtlNewCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Mtl | New | CZ09 | 0.94 | 8e-05 | 0 | 1.08 | 0.000108 | -0.00268 | 0.94 | 8e-05 | 0 | 1.08 | 0.000108 | -0.00268 | CFL | Bldg | 940 | 0.08 | 940 | 0.08 | 1.15 | 1.35 | -0.00285
CFLBldgSCEMtlNewCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Mtl | New | CZ10 | 0.94 | 8e-05 | 0 | 1.06 | 0.000108 | -0.00332 | 0.94 | 8e-05 | 0 | 1.06 | 0.000108 | -0.00332 | CFL | Bldg | 940 | 0.08 | 940 | 0.08 | 1.13 | 1.35 | -0.00353
CFLBldgSDGMtlNewCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Mtl | New | CZ10 | 0.94 | 8e-05 | 0 | 1.06 | 0.000107 | -0.00344 | 0.94 | 8e-05 | 0 | 1.06 | 0.000107 | -0.00344 | CFL | Bldg | 940 | 0.08 | 940 | 0.08 | 1.13 | 1.34 | -0.00366
CFLBldgPGEMtlNewCZ11 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Mtl | New | CZ11 | 0.94 | 8e-05 | 0 | 1 | 0.000102 | -0.00564 | 0.94 | 8e-05 | 0 | 1 | 0.000102 | -0.00564 | CFL | Bldg | 940 | 0.08 | 940 | 0.08 | 1.06 | 1.28 | -0.006
CFLBldgPGEMtlNewCZ12 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Mtl | New | CZ12 | 0.94 | 8e-05 | 0 | 0.993 | 0.000102 | -0.00589 | 0.94 | 8e-05 | 0 | 0.993 | 0.000102 | -0.00589 | CFL | Bldg | 940 | 0.08 | 940 | 0.08 | 1.06 | 1.28 | -0.00627
CFLBldgPGEMtlNewCZ13 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Mtl | New | CZ13 | 0.94 | 8e-05 | 0 | 1.01 | 0.000101 | -0.0053 | 0.94 | 8e-05 | 0 | 1.01 | 0.000101 | -0.0053 | CFL | Bldg | 940 | 0.08 | 940 | 0.08 | 1.07 | 1.26 | -0.00564
CFLBldgSCEMtlNewCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Mtl | New | CZ13 | 0.94 | 8e-05 | 0 | 1.03 | 0.000107 | -0.00429 | 0.94 | 8e-05 | 0 | 1.03 | 0.000107 | -0.00429 | CFL | Bldg | 940 | 0.08 | 940 | 0.08 | 1.1 | 1.34 | -0.00456
CFLBldgSDGMtlNewCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Mtl | New | CZ14 | 0.94 | 8e-05 | 0 | 1.02 | 0.000107 | -0.00461 | 0.94 | 8e-05 | 0 | 1.02 | 0.000107 | -0.00461 | CFL | Bldg | 940 | 0.08 | 940 | 0.08 | 1.09 | 1.34 | -0.0049
CFLBldgSCEMtlNewCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Mtl | New | CZ14 | 0.94 | 8e-05 | 0 | 1.02 | 0.000108 | -0.00446 | 0.94 | 8e-05 | 0 | 1.02 | 0.000108 | -0.00446 | CFL | Bldg | 940 | 0.08 | 940 | 0.08 | 1.09 | 1.35 | -0.00474
CFLBldgSDGMtlNewCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Mtl | New | CZ15 | 0.94 | 8e-05 | 0 | 1.13 | 0.00011 | -0.00158 | 0.94 | 8e-05 | 0 | 1.13 | 0.00011 | -0.00158 | CFL | Bldg | 940 | 0.08 | 940 | 0.08 | 1.2 | 1.38 | -0.00168
CFLBldgSCEMtlNewCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Mtl | New | CZ15 | 0.94 | 8e-05 | 0 | 1.14 | 0.000111 | -0.00154 | 0.94 | 8e-05 | 0 | 1.14 | 0.000111 | -0.00154 | CFL | Bldg | 940 | 0.08 | 940 | 0.08 | 1.21 | 1.39 | -0.00164
CFLBldgSCEMtlNewCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Mtl | New | CZ16 | 0.94 | 8e-05 | 0 | 0.91 | 0.000102 | -0.00694 | 0.94 | 8e-05 | 0 | 0.91 | 0.000102 | -0.00694 | CFL | Bldg | 940 | 0.08 | 940 | 0.08 | 0.968 | 1.28 | -0.00738
CFLBldgPGEMtlNewCZ16 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Mtl | New | CZ16 | 0.94 | 8e-05 | 0 | 0.905 | 9.76e-05 | -0.00831 | 0.94 | 8e-05 | 0 | 0.905 | 9.76e-05 | -0.00831 | CFL | Bldg | 940 | 0.08 | 940 | 0.08 | 0.963 | 1.22 | -0.00884
CFLBldgSCGMtlNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SCG | Mtl | New | IOU | 0.94 | 8e-05 | 0 | 1.08 | 0.000106 | -0.00274 | 0.94 | 8e-05 | 0 | 1.08 | 0.000106 | -0.00274 | CFL | Bldg | 940 | 0.08 | 940 | 0.08 | 1.15 | 1.33 | -0.00291
CFLBldgPGEMtlNewIOU | Com-Iltg-dWatt-CFL_OSbldg | PGE | Mtl | New | IOU | 0.94 | 8e-05 | 0 | 0.995 | 0.000104 | -0.00519 | 0.94 | 8e-05 | 0 | 0.995 | 0.000104 | -0.00519 | CFL | Bldg | 940 | 0.08 | 940 | 0.08 | 1.06 | 1.3 | -0.00552
CFLBldgSCEMtlNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | Mtl | New | IOU | 0.94 | 8e-05 | 0 | 1.08 | 0.000106 | -0.00271 | 0.94 | 8e-05 | 0 | 1.08 | 0.000106 | -0.00271 | CFL | Bldg | 940 | 0.08 | 940 | 0.08 | 1.15 | 1.33 | -0.00288
CFLBldgSDGMtlNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SDG | Mtl | New | IOU | 0.94 | 8e-05 | 0 | 1.08 | 0.000102 | -0.00245 | 0.94 | 8e-05 | 0 | 1.08 | 0.000102 | -0.00245 | CFL | Bldg | 940 | 0.08 | 940 | 0.08 | 1.15 | 1.28 | -0.00261
CFLBldgPGENrsExCZ01 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Nrs | Ex | CZ01 | 3.47 | 0.000493 | 0 | 3.41 | 0.000563 | -0.07 | 3.38 | 0.000477 | 0 | 3.32 | 0.000545 | -0.0683 | CFL | Bldg | 3470 | 0.493 | 3380 | 0.477 | 0.982 | 1.14 | -0.0202
CFLBldgPGENrsExCZ02 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Nrs | Ex | CZ02 | 3.47 | 0.000493 | 0 | 3.59 | 0.000619 | -0.0506 | 3.38 | 0.000477 | 0 | 3.5 | 0.000599 | -0.0493 | CFL | Bldg | 3470 | 0.493 | 3380 | 0.477 | 1.04 | 1.26 | -0.0146
CFLBldgPGENrsExCZ03 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Nrs | Ex | CZ03 | 3.47 | 0.000493 | 0 | 3.56 | 0.000601 | -0.0513 | 3.38 | 0.000477 | 0 | 3.46 | 0.000581 | -0.05 | CFL | Bldg | 3470 | 0.493 | 3380 | 0.477 | 1.02 | 1.22 | -0.0148
CFLBldgPGENrsExCZ04 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Nrs | Ex | CZ04 | 3.47 | 0.000493 | 0 | 3.64 | 0.000615 | -0.0433 | 3.38 | 0.000477 | 0 | 3.55 | 0.000594 | -0.0423 | CFL | Bldg | 3470 | 0.493 | 3380 | 0.477 | 1.05 | 1.25 | -0.0125
CFLBldgSCGNrsExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCG | Nrs | Ex | CZ05 | 3.47 | 0.000493 | 0 | 3.55 | 0.000608 | -0.0506 | 3.38 | 0.000477 | 0 | 3.45 | 0.000588 | -0.0493 | CFL | Bldg | 3470 | 0.493 | 3380 | 0.477 | 1.02 | 1.23 | -0.0146
CFLBldgSCENrsExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Nrs | Ex | CZ05 | 3.47 | 0.000493 | 0 | 3.55 | 0.000608 | -0.0506 | 3.38 | 0.000477 | 0 | 3.45 | 0.000588 | -0.0493 | CFL | Bldg | 3470 | 0.493 | 3380 | 0.477 | 1.02 | 1.23 | -0.0146
CFLBldgPGENrsExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Nrs | Ex | CZ05 | 3.47 | 0.000493 | 0 | 3.54 | 0.000608 | -0.0506 | 3.38 | 0.000477 | 0 | 3.45 | 0.000588 | -0.0493 | CFL | Bldg | 3470 | 0.493 | 3380 | 0.477 | 1.02 | 1.23 | -0.0146
CFLBldgSCENrsExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Nrs | Ex | CZ06 | 3.47 | 0.000493 | 0 | 3.74 | 0.000636 | -0.0329 | 3.38 | 0.000477 | 0 | 3.65 | 0.000615 | -0.032 | CFL | Bldg | 3470 | 0.493 | 3380 | 0.477 | 1.08 | 1.29 | -0.00947
CFLBldgSCGNrsExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCG | Nrs | Ex | CZ06 | 3.47 | 0.000493 | 0 | 3.74 | 0.000636 | -0.0329 | 3.38 | 0.000477 | 0 | 3.65 | 0.000615 | -0.032 | CFL | Bldg | 3470 | 0.493 | 3380 | 0.477 | 1.08 | 1.29 | -0.00947
CFLBldgSDGNrsExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Nrs | Ex | CZ06 | 3.47 | 0.000493 | 0 | 3.74 | 0.000636 | -0.0329 | 3.38 | 0.000477 | 0 | 3.65 | 0.000615 | -0.032 | CFL | Bldg | 3470 | 0.493 | 3380 | 0.477 | 1.08 | 1.29 | -0.00947
CFLBldgSDGNrsExCZ07 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Nrs | Ex | CZ07 | 3.47 | 0.000493 | 0 | 3.74 | 0.000625 | -0.0291 | 3.38 | 0.000477 | 0 | 3.64 | 0.000605 | -0.0284 | CFL | Bldg | 3470 | 0.493 | 3380 | 0.477 | 1.08 | 1.27 | -0.0084
CFLBldgSCGNrsExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCG | Nrs | Ex | CZ08 | 3.47 | 0.000493 | 0 | 3.78 | 0.000639 | -0.0317 | 3.38 | 0.000477 | 0 | 3.68 | 0.000618 | -0.0309 | CFL | Bldg | 3470 | 0.493 | 3380 | 0.477 | 1.09 | 1.3 | -0.00914
CFLBldgSDGNrsExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Nrs | Ex | CZ08 | 3.47 | 0.000493 | 0 | 3.78 | 0.000639 | -0.0317 | 3.38 | 0.000477 | 0 | 3.68 | 0.000618 | -0.0309 | CFL | Bldg | 3470 | 0.493 | 3380 | 0.477 | 1.09 | 1.3 | -0.00914
CFLBldgSCENrsExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Nrs | Ex | CZ08 | 3.47 | 0.000493 | 0 | 3.78 | 0.000639 | -0.0317 | 3.38 | 0.000477 | 0 | 3.68 | 0.000618 | -0.0309 | CFL | Bldg | 3470 | 0.493 | 3380 | 0.477 | 1.09 | 1.3 | -0.00914
CFLBldgSCENrsExCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Nrs | Ex | CZ09 | 3.47 | 0.000493 | 0 | 3.82 | 0.000659 | -0.0331 | 3.38 | 0.000477 | 0 | 3.73 | 0.000637 | -0.0322 | CFL | Bldg | 3470 | 0.493 | 3380 | 0.477 | 1.1 | 1.34 | -0.00953
CFLBldgSCGNrsExCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCG | Nrs | Ex | CZ09 | 3.47 | 0.000493 | 0 | 3.83 | 0.000659 | -0.0331 | 3.38 | 0.000477 | 0 | 3.73 | 0.000637 | -0.0322 | CFL | Bldg | 3470 | 0.493 | 3380 | 0.477 | 1.1 | 1.34 | -0.00953
CFLBldgSCENrsExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Nrs | Ex | CZ10 | 3.46 | 0.000493 | 0 | 3.79 | 0.000658 | -0.0337 | 3.38 | 0.000477 | 0 | 3.7 | 0.000638 | -0.033 | CFL | Bldg | 3460 | 0.493 | 3380 | 0.477 | 1.09 | 1.34 | -0.00976
CFLBldgSCGNrsExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCG | Nrs | Ex | CZ10 | 3.46 | 0.000493 | 0 | 3.79 | 0.000658 | -0.0337 | 3.38 | 0.000477 | 0 | 3.7 | 0.000638 | -0.033 | CFL | Bldg | 3460 | 0.493 | 3380 | 0.477 | 1.09 | 1.34 | -0.00976
CFLBldgSDGNrsExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Nrs | Ex | CZ10 | 3.47 | 0.000493 | 0 | 3.8 | 0.000659 | -0.0338 | 3.38 | 0.000477 | 0 | 3.7 | 0.000638 | -0.033 | CFL | Bldg | 3470 | 0.493 | 3380 | 0.477 | 1.09 | 1.34 | -0.00976
CFLBldgPGENrsExCZ11 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Nrs | Ex | CZ11 | 3.46 | 0.000493 | 0 | 3.69 | 0.000624 | -0.0419 | 3.38 | 0.000477 | 0 | 3.6 | 0.000604 | -0.0409 | CFL | Bldg | 3460 | 0.493 | 3380 | 0.477 | 1.07 | 1.27 | -0.0121
CFLBldgPGENrsExCZ12 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Nrs | Ex | CZ12 | 3.46 | 0.000493 | 0 | 3.65 | 0.000621 | -0.044 | 3.38 | 0.000477 | 0 | 3.57 | 0.000601 | -0.0429 | CFL | Bldg | 3460 | 0.493 | 3380 | 0.477 | 1.06 | 1.26 | -0.0127
CFLBldgPGENrsExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Nrs | Ex | CZ13 | 3.46 | 0.000493 | 0 | 3.73 | 0.000651 | -0.0381 | 3.38 | 0.000477 | 0 | 3.64 | 0.00063 | -0.0372 | CFL | Bldg | 3460 | 0.493 | 3380 | 0.477 | 1.08 | 1.32 | -0.011
CFLBldgSCENrsExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Nrs | Ex | CZ13 | 3.46 | 0.000493 | 0 | 3.73 | 0.000651 | -0.0381 | 3.38 | 0.000477 | 0 | 3.64 | 0.00063 | -0.0372 | CFL | Bldg | 3460 | 0.493 | 3380 | 0.477 | 1.08 | 1.32 | -0.011
CFLBldgSCGNrsExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCG | Nrs | Ex | CZ13 | 3.46 | 0.000493 | 0 | 3.73 | 0.000651 | -0.0381 | 3.38 | 0.000477 | 0 | 3.64 | 0.00063 | -0.0372 | CFL | Bldg | 3460 | 0.493 | 3380 | 0.477 | 1.08 | 1.32 | -0.011
CFLBldgSCENrsExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Nrs | Ex | CZ14 | 3.46 | 0.000493 | 0 | 3.74 | 0.000651 | -0.0395 | 3.38 | 0.000477 | 0 | 3.66 | 0.000631 | -0.0385 | CFL | Bldg | 3460 | 0.493 | 3380 | 0.477 | 1.08 | 1.32 | -0.0114
CFLBldgSDGNrsExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Nrs | Ex | CZ14 | 3.47 | 0.000493 | 0 | 3.75 | 0.000652 | -0.0395 | 3.38 | 0.000477 | 0 | 3.66 | 0.000631 | -0.0385 | CFL | Bldg | 3470 | 0.493 | 3380 | 0.477 | 1.08 | 1.32 | -0.0114
CFLBldgSCGNrsExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCG | Nrs | Ex | CZ14 | 3.46 | 0.000493 | 0 | 3.74 | 0.000651 | -0.0395 | 3.38 | 0.000477 | 0 | 3.66 | 0.000631 | -0.0385 | CFL | Bldg | 3460 | 0.493 | 3380 | 0.477 | 1.08 | 1.32 | -0.0114
CFLBldgSCGNrsExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCG | Nrs | Ex | CZ15 | 3.46 | 0.000493 | 0 | 3.98 | 0.000655 | -0.0195 | 3.38 | 0.000477 | 0 | 3.89 | 0.000634 | -0.019 | CFL | Bldg | 3460 | 0.493 | 3380 | 0.477 | 1.15 | 1.33 | -0.00562
CFLBldgSCENrsExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Nrs | Ex | CZ15 | 3.46 | 0.000493 | 0 | 3.98 | 0.000655 | -0.0195 | 3.38 | 0.000477 | 0 | 3.89 | 0.000634 | -0.019 | CFL | Bldg | 3460 | 0.493 | 3380 | 0.477 | 1.15 | 1.33 | -0.00562
CFLBldgSCGNrsExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCG | Nrs | Ex | CZ16 | 3.46 | 0.000493 | 0 | 3.45 | 0.000621 | -0.0575 | 3.38 | 0.000477 | 0 | 3.37 | 0.000602 | -0.0561 | CFL | Bldg | 3460 | 0.493 | 3380 | 0.477 | 0.997 | 1.26 | -0.0166
CFLBldgSCENrsExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Nrs | Ex | CZ16 | 3.46 | 0.000493 | 0 | 3.45 | 0.000621 | -0.0575 | 3.38 | 0.000477 | 0 | 3.37 | 0.000602 | -0.0561 | CFL | Bldg | 3460 | 0.493 | 3380 | 0.477 | 0.997 | 1.26 | -0.0166
CFLBldgPGENrsExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Nrs | Ex | CZ16 | 3.47 | 0.000493 | 0 | 3.46 | 0.000622 | -0.0575 | 3.38 | 0.000477 | 0 | 3.37 | 0.000602 | -0.0561 | CFL | Bldg | 3470 | 0.493 | 3380 | 0.477 | 0.997 | 1.26 | -0.0166
CFLBldgPGENrsExIOU | Com-Iltg-dWatt-CFL_OSbldg | PGE | Nrs | Ex | IOU | 3.47 | 0.000493 | 0 | 3.63 | 0.000618 | -0.046 | 3.38 | 0.000477 | 0 | 3.54 | 0.000598 | -0.0449 | CFL | Bldg | 3470 | 0.493 | 3380 | 0.477 | 1.05 | 1.25 | -0.0133
CFLBldgSCENrsExIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | Nrs | Ex | IOU | 3.47 | 0.000493 | 0 | 3.77 | 0.000644 | -0.0334 | 3.38 | 0.000477 | 0 | 3.68 | 0.000623 | -0.0326 | CFL | Bldg | 3470 | 0.493 | 3380 | 0.477 | 1.09 | 1.31 | -0.00964
CFLBldgSCGNrsExIOU | Com-Iltg-dWatt-CFL_OSbldg | SCG | Nrs | Ex | IOU | 3.47 | 0.000493 | 0 | 3.78 | 0.000647 | -0.0332 | 3.38 | 0.000477 | 0 | 3.69 | 0.000626 | -0.0324 | CFL | Bldg | 3470 | 0.493 | 3380 | 0.477 | 1.09 | 1.31 | -0.00959
CFLBldgSDGNrsExIOU | Com-Iltg-dWatt-CFL_OSbldg | SDG | Nrs | Ex | IOU | 3.47 | 0.000493 | 0 | 3.75 | 0.000631 | -0.0299 | 3.38 | 0.000477 | 0 | 3.65 | 0.00061 | -0.0293 | CFL | Bldg | 3470 | 0.493 | 3380 | 0.477 | 1.08 | 1.28 | -0.00867
CFLBldgPGENrsNewCZ01 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Nrs | New | CZ01 | 3.39 | 0.000478 | 0 | 3.22 | 0.000522 | -0.0746 | 3.39 | 0.000478 | 0 | 3.22 | 0.000522 | -0.0746 | CFL | Bldg | 3390 | 0.478 | 3390 | 0.478 | 0.95 | 1.09 | -0.022
CFLBldgPGENrsNewCZ02 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Nrs | New | CZ02 | 3.39 | 0.000478 | 0 | 3.39 | 0.000598 | -0.0525 | 3.39 | 0.000478 | 0 | 3.39 | 0.000598 | -0.0525 | CFL | Bldg | 3390 | 0.478 | 3390 | 0.478 | 1 | 1.25 | -0.0155
CFLBldgPGENrsNewCZ03 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Nrs | New | CZ03 | 3.39 | 0.000478 | 0 | 3.34 | 0.000587 | -0.0549 | 3.39 | 0.000478 | 0 | 3.34 | 0.000587 | -0.0549 | CFL | Bldg | 3390 | 0.478 | 3390 | 0.478 | 0.985 | 1.23 | -0.0162
CFLBldgPGENrsNewCZ04 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Nrs | New | CZ04 | 3.39 | 0.000478 | 0 | 3.48 | 0.000598 | -0.0444 | 3.39 | 0.000478 | 0 | 3.48 | 0.000598 | -0.0444 | CFL | Bldg | 3390 | 0.478 | 3390 | 0.478 | 1.03 | 1.25 | -0.0131
CFLBldgPGENrsNewCZ05 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Nrs | New | CZ05 | 3.39 | 0.000478 | 0 | 3.34 | 0.000566 | -0.057 | 3.39 | 0.000478 | 0 | 3.34 | 0.000566 | -0.057 | CFL | Bldg | 3390 | 0.478 | 3390 | 0.478 | 0.985 | 1.18 | -0.0168
CFLBldgSCENrsNewCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Nrs | New | CZ05 | 3.39 | 0.000478 | 0 | 3.32 | 0.000582 | -0.0553 | 3.39 | 0.000478 | 0 | 3.32 | 0.000582 | -0.0553 | CFL | Bldg | 3390 | 0.478 | 3390 | 0.478 | 0.979 | 1.22 | -0.0163
CFLBldgSDGNrsNewCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Nrs | New | CZ06 | 3.39 | 0.000478 | 0 | 3.53 | 0.000607 | -0.0342 | 3.39 | 0.000478 | 0 | 3.53 | 0.000607 | -0.0342 | CFL | Bldg | 3390 | 0.478 | 3390 | 0.478 | 1.04 | 1.27 | -0.0101
CFLBldgSCENrsNewCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Nrs | New | CZ06 | 3.39 | 0.000478 | 0 | 3.53 | 0.000608 | -0.0339 | 3.39 | 0.000478 | 0 | 3.53 | 0.000608 | -0.0339 | CFL | Bldg | 3390 | 0.478 | 3390 | 0.478 | 1.04 | 1.27 | -0.01
CFLBldgSDGNrsNewCZ07 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Nrs | New | CZ07 | 3.39 | 0.000478 | 0 | 3.51 | 0.000607 | -0.032 | 3.39 | 0.000478 | 0 | 3.51 | 0.000607 | -0.032 | CFL | Bldg | 3390 | 0.478 | 3390 | 0.478 | 1.04 | 1.27 | -0.00944
CFLBldgSDGNrsNewCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Nrs | New | CZ08 | 3.39 | 0.000478 | 0 | 3.59 | 0.000609 | -0.0327 | 3.39 | 0.000478 | 0 | 3.59 | 0.000609 | -0.0327 | CFL | Bldg | 3390 | 0.478 | 3390 | 0.478 | 1.06 | 1.27 | -0.00965
CFLBldgSCENrsNewCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Nrs | New | CZ08 | 3.39 | 0.000478 | 0 | 3.59 | 0.000611 | -0.0323 | 3.39 | 0.000478 | 0 | 3.59 | 0.000611 | -0.0323 | CFL | Bldg | 3390 | 0.478 | 3390 | 0.478 | 1.06 | 1.28 | -0.00953
CFLBldgSCENrsNewCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Nrs | New | CZ09 | 3.39 | 0.000478 | 0 | 3.61 | 0.000633 | -0.0326 | 3.39 | 0.000478 | 0 | 3.61 | 0.000633 | -0.0326 | CFL | Bldg | 3390 | 0.478 | 3390 | 0.478 | 1.06 | 1.32 | -0.00962
CFLBldgSDGNrsNewCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Nrs | New | CZ10 | 3.39 | 0.000478 | 0 | 3.63 | 0.000634 | -0.0336 | 3.39 | 0.000478 | 0 | 3.63 | 0.000634 | -0.0336 | CFL | Bldg | 3390 | 0.478 | 3390 | 0.478 | 1.07 | 1.33 | -0.00991
CFLBldgSCENrsNewCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Nrs | New | CZ10 | 3.39 | 0.000478 | 0 | 3.63 | 0.000635 | -0.0333 | 3.39 | 0.000478 | 0 | 3.63 | 0.000635 | -0.0333 | CFL | Bldg | 3390 | 0.478 | 3390 | 0.478 | 1.07 | 1.33 | -0.00982
CFLBldgPGENrsNewCZ11 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Nrs | New | CZ11 | 3.39 | 0.000478 | 0 | 3.56 | 0.000606 | -0.0424 | 3.39 | 0.000478 | 0 | 3.56 | 0.000606 | -0.0424 | CFL | Bldg | 3390 | 0.478 | 3390 | 0.478 | 1.05 | 1.27 | -0.0125
CFLBldgPGENrsNewCZ12 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Nrs | New | CZ12 | 3.39 | 0.000478 | 0 | 3.51 | 0.000607 | -0.0444 | 3.39 | 0.000478 | 0 | 3.51 | 0.000607 | -0.0444 | CFL | Bldg | 3390 | 0.478 | 3390 | 0.478 | 1.04 | 1.27 | -0.0131
CFLBldgSCENrsNewCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Nrs | New | CZ13 | 3.39 | 0.000478 | 0 | 3.6 | 0.000629 | -0.0393 | 3.39 | 0.000478 | 0 | 3.6 | 0.000629 | -0.0393 | CFL | Bldg | 3390 | 0.478 | 3390 | 0.478 | 1.06 | 1.32 | -0.0116
CFLBldgPGENrsNewCZ13 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Nrs | New | CZ13 | 3.39 | 0.000478 | 0 | 3.57 | 0.000606 | -0.0403 | 3.39 | 0.000478 | 0 | 3.57 | 0.000606 | -0.0403 | CFL | Bldg | 3390 | 0.478 | 3390 | 0.478 | 1.05 | 1.27 | -0.0119
CFLBldgSCENrsNewCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Nrs | New | CZ14 | 3.39 | 0.000478 | 0 | 3.6 | 0.000619 | -0.041 | 3.39 | 0.000478 | 0 | 3.6 | 0.000619 | -0.041 | CFL | Bldg | 3390 | 0.478 | 3390 | 0.478 | 1.06 | 1.29 | -0.0121
CFLBldgSDGNrsNewCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Nrs | New | CZ14 | 3.39 | 0.000478 | 0 | 3.6 | 0.000616 | -0.0414 | 3.39 | 0.000478 | 0 | 3.6 | 0.000616 | -0.0414 | CFL | Bldg | 3390 | 0.478 | 3390 | 0.478 | 1.06 | 1.29 | -0.0122
CFLBldgSDGNrsNewCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Nrs | New | CZ15 | 3.39 | 0.000478 | 0 | 3.9 | 0.000633 | -0.0161 | 3.39 | 0.000478 | 0 | 3.9 | 0.000633 | -0.0161 | CFL | Bldg | 3390 | 0.478 | 3390 | 0.478 | 1.15 | 1.32 | -0.00475
CFLBldgSCENrsNewCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Nrs | New | CZ15 | 3.39 | 0.000478 | 0 | 3.9 | 0.000635 | -0.0159 | 3.39 | 0.000478 | 0 | 3.9 | 0.000635 | -0.0159 | CFL | Bldg | 3390 | 0.478 | 3390 | 0.478 | 1.15 | 1.33 | -0.00469
CFLBldgPGENrsNewCZ16 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Nrs | New | CZ16 | 3.39 | 0.000478 | 0 | 3.34 | 0.000579 | -0.0627 | 3.39 | 0.000478 | 0 | 3.34 | 0.000579 | -0.0627 | CFL | Bldg | 3390 | 0.478 | 3390 | 0.478 | 0.985 | 1.21 | -0.0185
CFLBldgSCENrsNewCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Nrs | New | CZ16 | 3.39 | 0.000478 | 0 | 3.33 | 0.000598 | -0.061 | 3.39 | 0.000478 | 0 | 3.33 | 0.000598 | -0.061 | CFL | Bldg | 3390 | 0.478 | 3390 | 0.478 | 0.982 | 1.25 | -0.018
CFLBldgSCGNrsNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SCG | Nrs | New | IOU | 3.39 | 0.000478 | 0 | 3.6 | 0.000617 | -0.0328 | 3.39 | 0.000478 | 0 | 3.6 | 0.000617 | -0.0328 | CFL | Bldg | 3390 | 0.478 | 3390 | 0.478 | 1.06 | 1.29 | -0.00968
CFLBldgPGENrsNewIOU | Com-Iltg-dWatt-CFL_OSbldg | PGE | Nrs | New | IOU | 3.39 | 0.000478 | 0 | 3.57 | 0.000624 | -0.0411 | 3.39 | 0.000478 | 0 | 3.57 | 0.000624 | -0.0411 | CFL | Bldg | 3390 | 0.478 | 3390 | 0.478 | 1.05 | 1.31 | -0.0121
CFLBldgSCENrsNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | Nrs | New | IOU | 3.39 | 0.000478 | 0 | 3.61 | 0.000618 | -0.0327 | 3.39 | 0.000478 | 0 | 3.61 | 0.000618 | -0.0327 | CFL | Bldg | 3390 | 0.478 | 3390 | 0.478 | 1.06 | 1.29 | -0.00965
CFLBldgSDGNrsNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SDG | Nrs | New | IOU | 3.39 | 0.000478 | 0 | 3.53 | 0.000611 | -0.0323 | 3.39 | 0.000478 | 0 | 3.53 | 0.000611 | -0.0323 | CFL | Bldg | 3390 | 0.478 | 3390 | 0.478 | 1.04 | 1.28 | -0.00953
CFLBldgPGEOfLExCZ01 | Com-Iltg-dWatt-CFL_OSbldg | PGE | OfL | Ex | CZ01 | 2.1 | 0.000506 | 0 | 2.24 | 0.000642 | -0.0195 | 1.96 | 0.000458 | 0 | 2.09 | 0.000581 | -0.0182 | CFL | Bldg | 2100 | 0.506 | 1960 | 0.458 | 1.07 | 1.27 | -0.00929
CFLBldgPGEOfLExCZ02 | Com-Iltg-dWatt-CFL_OSbldg | PGE | OfL | Ex | CZ02 | 2.1 | 0.000505 | 0 | 2.31 | 0.000675 | -0.0145 | 1.96 | 0.000458 | 0 | 2.15 | 0.000612 | -0.0136 | CFL | Bldg | 2100 | 0.505 | 1960 | 0.458 | 1.1 | 1.34 | -0.00694
CFLBldgPGEOfLExCZ03 | Com-Iltg-dWatt-CFL_OSbldg | PGE | OfL | Ex | CZ03 | 2.1 | 0.000506 | 0 | 2.3 | 0.000658 | -0.0135 | 1.96 | 0.000458 | 0 | 2.15 | 0.000596 | -0.0125 | CFL | Bldg | 2100 | 0.506 | 1960 | 0.458 | 1.1 | 1.3 | -0.00638
CFLBldgPGEOfLExCZ04 | Com-Iltg-dWatt-CFL_OSbldg | PGE | OfL | Ex | CZ04 | 2.1 | 0.000505 | 0 | 2.33 | 0.00066 | -0.0122 | 1.96 | 0.000458 | 0 | 2.17 | 0.000599 | -0.0114 | CFL | Bldg | 2100 | 0.505 | 1960 | 0.458 | 1.11 | 1.31 | -0.00582
CFLBldgSCGOfLExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCG | OfL | Ex | CZ05 | 2.11 | 0.000507 | 0 | 2.34 | 0.000655 | -0.0146 | 1.96 | 0.000458 | 0 | 2.17 | 0.000593 | -0.0136 | CFL | Bldg | 2110 | 0.507 | 1960 | 0.458 | 1.11 | 1.29 | -0.00694
CFLBldgSCEOfLExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | OfL | Ex | CZ05 | 2.11 | 0.000507 | 0 | 2.34 | 0.000655 | -0.0146 | 1.96 | 0.000458 | 0 | 2.17 | 0.000593 | -0.0136 | CFL | Bldg | 2110 | 0.507 | 1960 | 0.458 | 1.11 | 1.29 | -0.00694
CFLBldgPGEOfLExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | PGE | OfL | Ex | CZ05 | 2.1 | 0.000505 | 0 | 2.33 | 0.000653 | -0.0145 | 1.96 | 0.000458 | 0 | 2.17 | 0.000593 | -0.0136 | CFL | Bldg | 2100 | 0.505 | 1960 | 0.458 | 1.11 | 1.29 | -0.00694
CFLBldgSDGOfLExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SDG | OfL | Ex | CZ06 | 2.1 | 0.000505 | 0 | 2.41 | 0.000645 | -0.00504 | 1.96 | 0.000458 | 0 | 2.25 | 0.000584 | -0.0047 | CFL | Bldg | 2100 | 0.505 | 1960 | 0.458 | 1.15 | 1.28 | -0.0024
CFLBldgSCGOfLExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCG | OfL | Ex | CZ06 | 2.11 | 0.000506 | 0 | 2.41 | 0.000646 | -0.00505 | 1.96 | 0.000458 | 0 | 2.25 | 0.000584 | -0.0047 | CFL | Bldg | 2110 | 0.506 | 1960 | 0.458 | 1.15 | 1.28 | -0.0024
CFLBldgSCEOfLExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | OfL | Ex | CZ06 | 2.11 | 0.000507 | 0 | 2.42 | 0.000646 | -0.00505 | 1.96 | 0.000458 | 0 | 2.25 | 0.000584 | -0.0047 | CFL | Bldg | 2110 | 0.507 | 1960 | 0.458 | 1.15 | 1.28 | -0.0024
CFLBldgSDGOfLExCZ07 | Com-Iltg-dWatt-CFL_OSbldg | SDG | OfL | Ex | CZ07 | 2.1 | 0.000505 | 0 | 2.41 | 0.000636 | -0.00433 | 1.96 | 0.000458 | 0 | 2.24 | 0.000576 | -0.00404 | CFL | Bldg | 2100 | 0.505 | 1960 | 0.458 | 1.14 | 1.26 | -0.00206
CFLBldgSDGOfLExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SDG | OfL | Ex | CZ08 | 2.1 | 0.000505 | 0 | 2.42 | 0.000657 | -0.0049 | 1.96 | 0.000458 | 0 | 2.26 | 0.000596 | -0.00457 | CFL | Bldg | 2100 | 0.505 | 1960 | 0.458 | 1.15 | 1.3 | -0.00233
CFLBldgSCEOfLExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | OfL | Ex | CZ08 | 2.11 | 0.000507 | 0 | 2.43 | 0.000659 | -0.00491 | 1.96 | 0.000458 | 0 | 2.26 | 0.000596 | -0.00457 | CFL | Bldg | 2110 | 0.507 | 1960 | 0.458 | 1.15 | 1.3 | -0.00233
CFLBldgSCGOfLExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCG | OfL | Ex | CZ08 | 2.11 | 0.000506 | 0 | 2.42 | 0.000659 | -0.00491 | 1.96 | 0.000458 | 0 | 2.26 | 0.000596 | -0.00457 | CFL | Bldg | 2110 | 0.506 | 1960 | 0.458 | 1.15 | 1.3 | -0.00233
CFLBldgSCGOfLExCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCG | OfL | Ex | CZ09 | 2.1 | 0.000506 | 0 | 2.43 | 0.000688 | -0.0107 | 1.96 | 0.000458 | 0 | 2.27 | 0.000622 | -0.00996 | CFL | Bldg | 2100 | 0.506 | 1960 | 0.458 | 1.16 | 1.36 | -0.00508
CFLBldgSCEOfLExCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | OfL | Ex | CZ09 | 2.1 | 0.000506 | 0 | 2.43 | 0.000687 | -0.0107 | 1.96 | 0.000458 | 0 | 2.27 | 0.000622 | -0.00996 | CFL | Bldg | 2100 | 0.506 | 1960 | 0.458 | 1.16 | 1.36 | -0.00508
CFLBldgSCGOfLExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCG | OfL | Ex | CZ10 | 2.1 | 0.000503 | 0 | 2.41 | 0.00066 | -0.00557 | 1.96 | 0.000458 | 0 | 2.25 | 0.000601 | -0.00521 | CFL | Bldg | 2100 | 0.503 | 1960 | 0.458 | 1.15 | 1.31 | -0.00266
CFLBldgSCEOfLExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | OfL | Ex | CZ10 | 2.1 | 0.000503 | 0 | 2.41 | 0.00066 | -0.00557 | 1.96 | 0.000458 | 0 | 2.25 | 0.000601 | -0.00521 | CFL | Bldg | 2100 | 0.503 | 1960 | 0.458 | 1.15 | 1.31 | -0.00266
CFLBldgSDGOfLExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SDG | OfL | Ex | CZ10 | 2.1 | 0.000505 | 0 | 2.42 | 0.000662 | -0.00559 | 1.96 | 0.000458 | 0 | 2.25 | 0.000601 | -0.00521 | CFL | Bldg | 2100 | 0.505 | 1960 | 0.458 | 1.15 | 1.31 | -0.00266
CFLBldgPGEOfLExCZ11 | Com-Iltg-dWatt-CFL_OSbldg | PGE | OfL | Ex | CZ11 | 2.1 | 0.000504 | 0 | 2.36 | 0.000673 | -0.0139 | 1.96 | 0.000458 | 0 | 2.2 | 0.000611 | -0.013 | CFL | Bldg | 2100 | 0.504 | 1960 | 0.458 | 1.12 | 1.33 | -0.00663
CFLBldgPGEOfLExCZ12 | Com-Iltg-dWatt-CFL_OSbldg | PGE | OfL | Ex | CZ12 | 2.1 | 0.000504 | 0 | 2.33 | 0.000667 | -0.0133 | 1.96 | 0.000458 | 0 | 2.17 | 0.000605 | -0.0125 | CFL | Bldg | 2100 | 0.504 | 1960 | 0.458 | 1.11 | 1.32 | -0.00638
CFLBldgPGEOfLExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | PGE | OfL | Ex | CZ13 | 2.1 | 0.000504 | 0 | 2.42 | 0.000667 | -0.0126 | 1.96 | 0.000458 | 0 | 2.25 | 0.000605 | -0.0118 | CFL | Bldg | 2100 | 0.504 | 1960 | 0.458 | 1.15 | 1.32 | -0.00602
CFLBldgSCEOfLExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | OfL | Ex | CZ13 | 2.1 | 0.000504 | 0 | 2.42 | 0.000667 | -0.0126 | 1.96 | 0.000458 | 0 | 2.25 | 0.000605 | -0.0118 | CFL | Bldg | 2100 | 0.504 | 1960 | 0.458 | 1.15 | 1.32 | -0.00602
CFLBldgSCGOfLExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCG | OfL | Ex | CZ13 | 2.1 | 0.000504 | 0 | 2.42 | 0.000667 | -0.0126 | 1.96 | 0.000458 | 0 | 2.25 | 0.000605 | -0.0118 | CFL | Bldg | 2100 | 0.504 | 1960 | 0.458 | 1.15 | 1.32 | -0.00602
CFLBldgSCGOfLExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCG | OfL | Ex | CZ14 | 2.1 | 0.000504 | 0 | 2.38 | 0.000651 | -0.0077 | 1.96 | 0.000458 | 0 | 2.22 | 0.000591 | -0.00719 | CFL | Bldg | 2100 | 0.504 | 1960 | 0.458 | 1.13 | 1.29 | -0.00367
CFLBldgSCEOfLExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | OfL | Ex | CZ14 | 2.1 | 0.000504 | 0 | 2.38 | 0.000651 | -0.0077 | 1.96 | 0.000458 | 0 | 2.22 | 0.000591 | -0.00719 | CFL | Bldg | 2100 | 0.504 | 1960 | 0.458 | 1.13 | 1.29 | -0.00367
CFLBldgSDGOfLExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SDG | OfL | Ex | CZ14 | 2.1 | 0.000505 | 0 | 2.38 | 0.000652 | -0.00771 | 1.96 | 0.000458 | 0 | 2.22 | 0.000591 | -0.00719 | CFL | Bldg | 2100 | 0.505 | 1960 | 0.458 | 1.13 | 1.29 | -0.00367
CFLBldgSCGOfLExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCG | OfL | Ex | CZ15 | 2.1 | 0.000503 | 0 | 2.55 | 0.000663 | -0.00323 | 1.96 | 0.000458 | 0 | 2.39 | 0.000603 | -0.00302 | CFL | Bldg | 2100 | 0.503 | 1960 | 0.458 | 1.22 | 1.32 | -0.00154
CFLBldgSDGOfLExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SDG | OfL | Ex | CZ15 | 2.1 | 0.000505 | 0 | 2.56 | 0.000665 | -0.00324 | 1.96 | 0.000458 | 0 | 2.39 | 0.000603 | -0.00302 | CFL | Bldg | 2100 | 0.505 | 1960 | 0.458 | 1.22 | 1.32 | -0.00154
CFLBldgSCEOfLExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | OfL | Ex | CZ15 | 2.1 | 0.000503 | 0 | 2.55 | 0.000663 | -0.00323 | 1.96 | 0.000458 | 0 | 2.39 | 0.000603 | -0.00302 | CFL | Bldg | 2100 | 0.503 | 1960 | 0.458 | 1.22 | 1.32 | -0.00154
CFLBldgPGEOfLExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | PGE | OfL | Ex | CZ16 | 2.1 | 0.000505 | 0 | 2.22 | 0.000641 | -0.0223 | 1.96 | 0.000458 | 0 | 2.08 | 0.000581 | -0.0208 | CFL | Bldg | 2100 | 0.505 | 1960 | 0.458 | 1.06 | 1.27 | -0.0106
CFLBldgSCEOfLExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | OfL | Ex | CZ16 | 2.1 | 0.000505 | 0 | 2.22 | 0.000641 | -0.0223 | 1.96 | 0.000458 | 0 | 2.08 | 0.000581 | -0.0208 | CFL | Bldg | 2100 | 0.505 | 1960 | 0.458 | 1.06 | 1.27 | -0.0106
CFLBldgSCGOfLExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCG | OfL | Ex | CZ16 | 2.1 | 0.000505 | 0 | 2.22 | 0.000641 | -0.0223 | 1.96 | 0.000458 | 0 | 2.08 | 0.000581 | -0.0208 | CFL | Bldg | 2100 | 0.505 | 1960 | 0.458 | 1.06 | 1.27 | -0.0106
CFLBldgSCGOfLExIOU | Com-Iltg-dWatt-CFL_OSbldg | SCG | OfL | Ex | IOU | 2.1 | 0.000506 | 0 | 2.43 | 0.000667 | -0.00738 | 1.96 | 0.000458 | 0 | 2.26 | 0.000604 | -0.00688 | CFL | Bldg | 2100 | 0.506 | 1960 | 0.458 | 1.15 | 1.32 | -0.00351
CFLBldgSDGOfLExIOU | Com-Iltg-dWatt-CFL_OSbldg | SDG | OfL | Ex | IOU | 2.1 | 0.000505 | 0 | 2.41 | 0.000641 | -0.00459 | 1.96 | 0.000458 | 0 | 2.24 | 0.000581 | -0.00428 | CFL | Bldg | 2100 | 0.505 | 1960 | 0.458 | 1.14 | 1.27 | -0.00218
CFLBldgPGEOfLExIOU | Com-Iltg-dWatt-CFL_OSbldg | PGE | OfL | Ex | IOU | 2.1 | 0.000505 | 0 | 2.32 | 0.000661 | -0.0132 | 1.96 | 0.000458 | 0 | 2.16 | 0.000599 | -0.0123 | CFL | Bldg | 2100 | 0.505 | 1960 | 0.458 | 1.1 | 1.31 | -0.00628
CFLBldgSCEOfLExIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | OfL | Ex | IOU | 2.1 | 0.000506 | 0 | 2.42 | 0.000661 | -0.0065 | 1.96 | 0.000458 | 0 | 2.26 | 0.000598 | -0.00606 | CFL | Bldg | 2100 | 0.506 | 1960 | 0.458 | 1.15 | 1.31 | -0.00309
CFLBldgPGEOfLNewCZ01 | Com-Iltg-dWatt-CFL_OSbldg | PGE | OfL | New | CZ01 | 1.96 | 0.000458 | 0 | 2.08 | 0.000557 | -0.0119 | 1.96 | 0.000458 | 0 | 2.08 | 0.000557 | -0.0119 | CFL | Bldg | 1960 | 0.458 | 1960 | 0.458 | 1.06 | 1.22 | -0.00607
CFLBldgPGEOfLNewCZ02 | Com-Iltg-dWatt-CFL_OSbldg | PGE | OfL | New | CZ02 | 1.96 | 0.000458 | 0 | 2.17 | 0.000567 | -0.00788 | 1.96 | 0.000458 | 0 | 2.17 | 0.000567 | -0.00788 | CFL | Bldg | 1960 | 0.458 | 1960 | 0.458 | 1.11 | 1.24 | -0.00402
CFLBldgPGEOfLNewCZ03 | Com-Iltg-dWatt-CFL_OSbldg | PGE | OfL | New | CZ03 | 1.96 | 0.000458 | 0 | 2.15 | 0.000566 | -0.00778 | 1.96 | 0.000458 | 0 | 2.15 | 0.000566 | -0.00778 | CFL | Bldg | 1960 | 0.458 | 1960 | 0.458 | 1.1 | 1.24 | -0.00397
CFLBldgPGEOfLNewCZ04 | Com-Iltg-dWatt-CFL_OSbldg | PGE | OfL | New | CZ04 | 1.96 | 0.000458 | 0 | 2.18 | 0.000568 | -0.00717 | 1.96 | 0.000458 | 0 | 2.18 | 0.000568 | -0.00717 | CFL | Bldg | 1960 | 0.458 | 1960 | 0.458 | 1.11 | 1.24 | -0.00366
CFLBldgPGEOfLNewCZ05 | Com-Iltg-dWatt-CFL_OSbldg | PGE | OfL | New | CZ05 | 1.96 | 0.000458 | 0 | 2.14 | 0.000554 | -0.00619 | 1.96 | 0.000458 | 0 | 2.14 | 0.000554 | -0.00619 | CFL | Bldg | 1960 | 0.458 | 1960 | 0.458 | 1.09 | 1.21 | -0.00316
CFLBldgSCEOfLNewCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | OfL | New | CZ05 | 1.96 | 0.000458 | 0 | 2.17 | 0.000568 | -0.00637 | 1.96 | 0.000458 | 0 | 2.17 | 0.000568 | -0.00637 | CFL | Bldg | 1960 | 0.458 | 1960 | 0.458 | 1.11 | 1.24 | -0.00325
CFLBldgSCEOfLNewCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | OfL | New | CZ06 | 1.96 | 0.000458 | 0 | 2.25 | 0.000578 | -0.00425 | 1.96 | 0.000458 | 0 | 2.25 | 0.000578 | -0.00425 | CFL | Bldg | 1960 | 0.458 | 1960 | 0.458 | 1.15 | 1.26 | -0.00217
CFLBldgSDGOfLNewCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SDG | OfL | New | CZ06 | 1.96 | 0.000458 | 0 | 2.25 | 0.00057 | -0.00319 | 1.96 | 0.000458 | 0 | 2.25 | 0.00057 | -0.00319 | CFL | Bldg | 1960 | 0.458 | 1960 | 0.458 | 1.15 | 1.24 | -0.00163
CFLBldgSDGOfLNewCZ07 | Com-Iltg-dWatt-CFL_OSbldg | SDG | OfL | New | CZ07 | 1.96 | 0.000458 | 0 | 2.24 | 0.000563 | -0.00259 | 1.96 | 0.000458 | 0 | 2.24 | 0.000563 | -0.00259 | CFL | Bldg | 1960 | 0.458 | 1960 | 0.458 | 1.14 | 1.23 | -0.00132
CFLBldgSDGOfLNewCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SDG | OfL | New | CZ08 | 1.96 | 0.000458 | 0 | 2.25 | 0.000578 | -0.00265 | 1.96 | 0.000458 | 0 | 2.25 | 0.000578 | -0.00265 | CFL | Bldg | 1960 | 0.458 | 1960 | 0.458 | 1.15 | 1.26 | -0.00135
CFLBldgSCEOfLNewCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | OfL | New | CZ08 | 1.96 | 0.000458 | 0 | 2.26 | 0.000585 | -0.0037 | 1.96 | 0.000458 | 0 | 2.26 | 0.000585 | -0.0037 | CFL | Bldg | 1960 | 0.458 | 1960 | 0.458 | 1.15 | 1.28 | -0.00189
CFLBldgSCEOfLNewCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | OfL | New | CZ09 | 1.96 | 0.000458 | 0 | 2.26 | 0.000602 | -0.00517 | 1.96 | 0.000458 | 0 | 2.26 | 0.000602 | -0.00517 | CFL | Bldg | 1960 | 0.458 | 1960 | 0.458 | 1.15 | 1.31 | -0.00264
CFLBldgSCEOfLNewCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | OfL | New | CZ10 | 1.96 | 0.000458 | 0 | 2.27 | 0.000605 | -0.00449 | 1.96 | 0.000458 | 0 | 2.27 | 0.000605 | -0.00449 | CFL | Bldg | 1960 | 0.458 | 1960 | 0.458 | 1.16 | 1.32 | -0.00229
CFLBldgSDGOfLNewCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SDG | OfL | New | CZ10 | 1.96 | 0.000458 | 0 | 2.26 | 0.000596 | -0.00325 | 1.96 | 0.000458 | 0 | 2.26 | 0.000596 | -0.00325 | CFL | Bldg | 1960 | 0.458 | 1960 | 0.458 | 1.15 | 1.3 | -0.00166
CFLBldgPGEOfLNewCZ11 | Com-Iltg-dWatt-CFL_OSbldg | PGE | OfL | New | CZ11 | 1.96 | 0.000458 | 0 | 2.19 | 0.000573 | -0.00678 | 1.96 | 0.000458 | 0 | 2.19 | 0.000573 | -0.00678 | CFL | Bldg | 1960 | 0.458 | 1960 | 0.458 | 1.12 | 1.25 | -0.00346
CFLBldgPGEOfLNewCZ12 | Com-Iltg-dWatt-CFL_OSbldg | PGE | OfL | New | CZ12 | 1.96 | 0.000458 | 0 | 2.18 | 0.000571 | -0.00762 | 1.96 | 0.000458 | 0 | 2.18 | 0.000571 | -0.00762 | CFL | Bldg | 1960 | 0.458 | 1960 | 0.458 | 1.11 | 1.25 | -0.00389
CFLBldgSCEOfLNewCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | OfL | New | CZ13 | 1.96 | 0.000458 | 0 | 2.23 | 0.000589 | -0.00668 | 1.96 | 0.000458 | 0 | 2.23 | 0.000589 | -0.00668 | CFL | Bldg | 1960 | 0.458 | 1960 | 0.458 | 1.14 | 1.29 | -0.00341
CFLBldgPGEOfLNewCZ13 | Com-Iltg-dWatt-CFL_OSbldg | PGE | OfL | New | CZ13 | 1.96 | 0.000458 | 0 | 2.2 | 0.000572 | -0.00664 | 1.96 | 0.000458 | 0 | 2.2 | 0.000572 | -0.00664 | CFL | Bldg | 1960 | 0.458 | 1960 | 0.458 | 1.12 | 1.25 | -0.00339
CFLBldgSDGOfLNewCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SDG | OfL | New | CZ14 | 1.96 | 0.000458 | 0 | 2.23 | 0.000606 | -0.00512 | 1.96 | 0.000458 | 0 | 2.23 | 0.000606 | -0.00512 | CFL | Bldg | 1960 | 0.458 | 1960 | 0.458 | 1.14 | 1.32 | -0.00261
CFLBldgSCEOfLNewCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | OfL | New | CZ14 | 1.96 | 0.000458 | 0 | 2.24 | 0.000611 | -0.0059 | 1.96 | 0.000458 | 0 | 2.24 | 0.000611 | -0.0059 | CFL | Bldg | 1960 | 0.458 | 1960 | 0.458 | 1.14 | 1.33 | -0.00301
CFLBldgSDGOfLNewCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SDG | OfL | New | CZ15 | 1.96 | 0.000458 | 0 | 2.35 | 0.000593 | -0.00154 | 1.96 | 0.000458 | 0 | 2.35 | 0.000593 | -0.00154 | CFL | Bldg | 1960 | 0.458 | 1960 | 0.458 | 1.2 | 1.29 | -0.000786
CFLBldgSCEOfLNewCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | OfL | New | CZ15 | 1.96 | 0.000458 | 0 | 2.36 | 0.000599 | -0.00218 | 1.96 | 0.000458 | 0 | 2.36 | 0.000599 | -0.00218 | CFL | Bldg | 1960 | 0.458 | 1960 | 0.458 | 1.2 | 1.31 | -0.00111
CFLBldgSCEOfLNewCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | OfL | New | CZ16 | 1.96 | 0.000458 | 0 | 2.11 | 0.000574 | -0.0163 | 1.96 | 0.000458 | 0 | 2.11 | 0.000574 | -0.0163 | CFL | Bldg | 1960 | 0.458 | 1960 | 0.458 | 1.08 | 1.25 | -0.00832
CFLBldgPGEOfLNewCZ16 | Com-Iltg-dWatt-CFL_OSbldg | PGE | OfL | New | CZ16 | 1.96 | 0.000458 | 0 | 2.09 | 0.000562 | -0.0166 | 1.96 | 0.000458 | 0 | 2.09 | 0.000562 | -0.0166 | CFL | Bldg | 1960 | 0.458 | 1960 | 0.458 | 1.07 | 1.23 | -0.00847
CFLBldgPGEOfLNewIOU | Com-Iltg-dWatt-CFL_OSbldg | PGE | OfL | New | IOU | 1.96 | 0.000458 | 0 | 2.22 | 0.000586 | -0.00683 | 1.96 | 0.000458 | 0 | 2.22 | 0.000586 | -0.00683 | CFL | Bldg | 1960 | 0.458 | 1960 | 0.458 | 1.13 | 1.28 | -0.00348
CFLBldgSDGOfLNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SDG | OfL | New | IOU | 1.96 | 0.000458 | 0 | 2.24 | 0.000569 | -0.00273 | 1.96 | 0.000458 | 0 | 2.24 | 0.000569 | -0.00273 | CFL | Bldg | 1960 | 0.458 | 1960 | 0.458 | 1.14 | 1.24 | -0.00139
CFLBldgSCGOfLNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SCG | OfL | New | IOU | 1.96 | 0.000458 | 0 | 2.26 | 0.000581 | -0.00296 | 1.96 | 0.000458 | 0 | 2.26 | 0.000581 | -0.00296 | CFL | Bldg | 1960 | 0.458 | 1960 | 0.458 | 1.15 | 1.27 | -0.00151
CFLBldgSCEOfLNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | OfL | New | IOU | 1.96 | 0.000458 | 0 | 2.26 | 0.000583 | -0.003 | 1.96 | 0.000458 | 0 | 2.26 | 0.000583 | -0.003 | CFL | Bldg | 1960 | 0.458 | 1960 | 0.458 | 1.15 | 1.27 | -0.00153
CFLBldgPGEOfSExCZ01 | Com-Iltg-dWatt-CFL_OSbldg | PGE | OfS | Ex | CZ01 | 1.63 | 0.000508 | 0 | 1.64 | 0.000602 | -0.0101 | 1.38 | 0.0004 | 0 | 1.39 | 0.000474 | -0.00861 | CFL | Bldg | 1630 | 0.508 | 1380 | 0.4 | 1.01 | 1.19 | -0.00624
CFLBldgPGEOfSExCZ02 | Com-Iltg-dWatt-CFL_OSbldg | PGE | OfS | Ex | CZ02 | 1.63 | 0.000507 | 0 | 1.7 | 0.000618 | -0.00658 | 1.38 | 0.0004 | 0 | 1.45 | 0.000488 | -0.00559 | CFL | Bldg | 1630 | 0.507 | 1380 | 0.4 | 1.05 | 1.22 | -0.00405
CFLBldgPGEOfSExCZ03 | Com-Iltg-dWatt-CFL_OSbldg | PGE | OfS | Ex | CZ03 | 1.63 | 0.000507 | 0 | 1.7 | 0.000618 | -0.00561 | 1.38 | 0.0004 | 0 | 1.44 | 0.000488 | -0.00476 | CFL | Bldg | 1630 | 0.507 | 1380 | 0.4 | 1.04 | 1.22 | -0.00345
CFLBldgPGEOfSExCZ04 | Com-Iltg-dWatt-CFL_OSbldg | PGE | OfS | Ex | CZ04 | 1.62 | 0.000506 | 0 | 1.73 | 0.00062 | -0.0045 | 1.38 | 0.0004 | 0 | 1.47 | 0.00049 | -0.00382 | CFL | Bldg | 1620 | 0.506 | 1380 | 0.4 | 1.07 | 1.23 | -0.00277
CFLBldgPGEOfSExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | PGE | OfS | Ex | CZ05 | 1.62 | 0.000506 | 0 | 1.76 | 0.000636 | -0.00508 | 1.38 | 0.0004 | 0 | 1.5 | 0.000502 | -0.00432 | CFL | Bldg | 1620 | 0.506 | 1380 | 0.4 | 1.09 | 1.26 | -0.00313
CFLBldgSCEOfSExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | OfS | Ex | CZ05 | 1.63 | 0.000507 | 0 | 1.76 | 0.000636 | -0.00509 | 1.38 | 0.0004 | 0 | 1.5 | 0.000502 | -0.00432 | CFL | Bldg | 1630 | 0.507 | 1380 | 0.4 | 1.09 | 1.26 | -0.00313
CFLBldgSCGOfSExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCG | OfS | Ex | CZ05 | 1.63 | 0.000507 | 0 | 1.76 | 0.000636 | -0.00509 | 1.38 | 0.0004 | 0 | 1.5 | 0.000502 | -0.00432 | CFL | Bldg | 1630 | 0.507 | 1380 | 0.4 | 1.09 | 1.26 | -0.00313
CFLBldgSDGOfSExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SDG | OfS | Ex | CZ06 | 1.63 | 0.000508 | 0 | 1.87 | 0.000639 | -0.00131 | 1.38 | 0.0004 | 0 | 1.58 | 0.000504 | -0.00111 | CFL | Bldg | 1630 | 0.508 | 1380 | 0.4 | 1.14 | 1.26 | -0.000804
CFLBldgSCGOfSExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCG | OfS | Ex | CZ06 | 1.63 | 0.000507 | 0 | 1.86 | 0.000638 | -0.00131 | 1.38 | 0.0004 | 0 | 1.58 | 0.000504 | -0.00111 | CFL | Bldg | 1630 | 0.507 | 1380 | 0.4 | 1.14 | 1.26 | -0.000804
CFLBldgSCEOfSExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | OfS | Ex | CZ06 | 1.63 | 0.000507 | 0 | 1.86 | 0.000638 | -0.00131 | 1.38 | 0.0004 | 0 | 1.58 | 0.000504 | -0.00111 | CFL | Bldg | 1630 | 0.507 | 1380 | 0.4 | 1.14 | 1.26 | -0.000804
CFLBldgSDGOfSExCZ07 | Com-Iltg-dWatt-CFL_OSbldg | SDG | OfS | Ex | CZ07 | 1.63 | 0.000508 | 0 | 1.87 | 0.000632 | -0.000356 | 1.38 | 0.0004 | 0 | 1.58 | 0.000498 | -0.000302 | CFL | Bldg | 1630 | 0.508 | 1380 | 0.4 | 1.14 | 1.25 | -0.000219
CFLBldgSCEOfSExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | OfS | Ex | CZ08 | 1.63 | 0.000507 | 0 | 1.87 | 0.000642 | -0.00111 | 1.38 | 0.0004 | 0 | 1.59 | 0.000507 | -0.000941 | CFL | Bldg | 1630 | 0.507 | 1380 | 0.4 | 1.15 | 1.27 | -0.000682
CFLBldgSCGOfSExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCG | OfS | Ex | CZ08 | 1.63 | 0.000507 | 0 | 1.87 | 0.000642 | -0.00111 | 1.38 | 0.0004 | 0 | 1.59 | 0.000507 | -0.000941 | CFL | Bldg | 1630 | 0.507 | 1380 | 0.4 | 1.15 | 1.27 | -0.000682
CFLBldgSDGOfSExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SDG | OfS | Ex | CZ08 | 1.63 | 0.000508 | 0 | 1.88 | 0.000643 | -0.00111 | 1.38 | 0.0004 | 0 | 1.59 | 0.000507 | -0.000941 | CFL | Bldg | 1630 | 0.508 | 1380 | 0.4 | 1.15 | 1.27 | -0.000682
CFLBldgSCGOfSExCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCG | OfS | Ex | CZ09 | 1.63 | 0.000508 | 0 | 1.86 | 0.000657 | -0.00277 | 1.38 | 0.0004 | 0 | 1.57 | 0.000518 | -0.00235 | CFL | Bldg | 1630 | 0.508 | 1380 | 0.4 | 1.14 | 1.3 | -0.0017
CFLBldgSCEOfSExCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | OfS | Ex | CZ09 | 1.63 | 0.000507 | 0 | 1.85 | 0.000656 | -0.00277 | 1.38 | 0.0004 | 0 | 1.57 | 0.000518 | -0.00235 | CFL | Bldg | 1630 | 0.507 | 1380 | 0.4 | 1.14 | 1.3 | -0.0017
CFLBldgSCGOfSExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCG | OfS | Ex | CZ10 | 1.62 | 0.000503 | 0 | 1.85 | 0.00064 | -0.00169 | 1.38 | 0.0004 | 0 | 1.58 | 0.000509 | -0.00144 | CFL | Bldg | 1620 | 0.503 | 1380 | 0.4 | 1.14 | 1.27 | -0.00104
CFLBldgSDGOfSExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SDG | OfS | Ex | CZ10 | 1.63 | 0.000508 | 0 | 1.87 | 0.000646 | -0.0017 | 1.38 | 0.0004 | 0 | 1.58 | 0.000509 | -0.00144 | CFL | Bldg | 1630 | 0.508 | 1380 | 0.4 | 1.14 | 1.27 | -0.00104
CFLBldgSCEOfSExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | OfS | Ex | CZ10 | 1.62 | 0.000503 | 0 | 1.85 | 0.00064 | -0.00169 | 1.38 | 0.0004 | 0 | 1.58 | 0.000509 | -0.00144 | CFL | Bldg | 1620 | 0.503 | 1380 | 0.4 | 1.14 | 1.27 | -0.00104
CFLBldgPGEOfSExCZ11 | Com-Iltg-dWatt-CFL_OSbldg | PGE | OfS | Ex | CZ11 | 1.63 | 0.000507 | 0 | 1.73 | 0.000619 | -0.00691 | 1.38 | 0.0004 | 0 | 1.47 | 0.000489 | -0.00586 | CFL | Bldg | 1630 | 0.507 | 1380 | 0.4 | 1.07 | 1.22 | -0.00425
CFLBldgPGEOfSExCZ12 | Com-Iltg-dWatt-CFL_OSbldg | PGE | OfS | Ex | CZ12 | 1.62 | 0.000506 | 0 | 1.72 | 0.00062 | -0.00671 | 1.38 | 0.0004 | 0 | 1.46 | 0.00049 | -0.0057 | CFL | Bldg | 1620 | 0.506 | 1380 | 0.4 | 1.06 | 1.23 | -0.00413
CFLBldgSCGOfSExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCG | OfS | Ex | CZ13 | 1.62 | 0.000506 | 0 | 1.79 | 0.000646 | -0.00609 | 1.38 | 0.0004 | 0 | 1.52 | 0.00051 | -0.00517 | CFL | Bldg | 1620 | 0.506 | 1380 | 0.4 | 1.1 | 1.28 | -0.00375
CFLBldgSCEOfSExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | OfS | Ex | CZ13 | 1.62 | 0.000506 | 0 | 1.79 | 0.000646 | -0.00609 | 1.38 | 0.0004 | 0 | 1.52 | 0.00051 | -0.00517 | CFL | Bldg | 1620 | 0.506 | 1380 | 0.4 | 1.1 | 1.28 | -0.00375
CFLBldgPGEOfSExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | PGE | OfS | Ex | CZ13 | 1.62 | 0.000506 | 0 | 1.79 | 0.000646 | -0.00609 | 1.38 | 0.0004 | 0 | 1.52 | 0.00051 | -0.00517 | CFL | Bldg | 1620 | 0.506 | 1380 | 0.4 | 1.1 | 1.28 | -0.00375
CFLBldgSCEOfSExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | OfS | Ex | CZ14 | 1.62 | 0.000504 | 0 | 1.81 | 0.000649 | -0.0041 | 1.38 | 0.0004 | 0 | 1.54 | 0.000515 | -0.00349 | CFL | Bldg | 1620 | 0.504 | 1380 | 0.4 | 1.12 | 1.29 | -0.00253
CFLBldgSDGOfSExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SDG | OfS | Ex | CZ14 | 1.63 | 0.000508 | 0 | 1.82 | 0.000653 | -0.00412 | 1.38 | 0.0004 | 0 | 1.54 | 0.000515 | -0.00349 | CFL | Bldg | 1630 | 0.508 | 1380 | 0.4 | 1.12 | 1.29 | -0.00253
CFLBldgSCGOfSExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCG | OfS | Ex | CZ14 | 1.62 | 0.000504 | 0 | 1.81 | 0.000649 | -0.0041 | 1.38 | 0.0004 | 0 | 1.54 | 0.000515 | -0.00349 | CFL | Bldg | 1620 | 0.504 | 1380 | 0.4 | 1.12 | 1.29 | -0.00253
CFLBldgSCGOfSExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCG | OfS | Ex | CZ15 | 1.62 | 0.000503 | 0 | 1.98 | 0.000634 | -0.000354 | 1.38 | 0.0004 | 0 | 1.69 | 0.000504 | -0.000302 | CFL | Bldg | 1620 | 0.503 | 1380 | 0.4 | 1.22 | 1.26 | -0.000219
CFLBldgSCEOfSExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | OfS | Ex | CZ15 | 1.62 | 0.000503 | 0 | 1.98 | 0.000634 | -0.000354 | 1.38 | 0.0004 | 0 | 1.69 | 0.000504 | -0.000302 | CFL | Bldg | 1620 | 0.503 | 1380 | 0.4 | 1.22 | 1.26 | -0.000219
CFLBldgSDGOfSExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SDG | OfS | Ex | CZ15 | 1.63 | 0.000508 | 0 | 2 | 0.000639 | -0.000356 | 1.38 | 0.0004 | 0 | 1.69 | 0.000504 | -0.000302 | CFL | Bldg | 1630 | 0.508 | 1380 | 0.4 | 1.22 | 1.26 | -0.000219
CFLBldgSCEOfSExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | OfS | Ex | CZ16 | 1.62 | 0.000505 | 0 | 1.63 | 0.000632 | -0.0115 | 1.38 | 0.0004 | 0 | 1.39 | 0.0005 | -0.00978 | CFL | Bldg | 1620 | 0.505 | 1380 | 0.4 | 1.01 | 1.25 | -0.00709
CFLBldgPGEOfSExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | PGE | OfS | Ex | CZ16 | 1.63 | 0.000507 | 0 | 1.64 | 0.000635 | -0.0115 | 1.38 | 0.0004 | 0 | 1.39 | 0.0005 | -0.00978 | CFL | Bldg | 1630 | 0.507 | 1380 | 0.4 | 1.01 | 1.25 | -0.00709
CFLBldgSCGOfSExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCG | OfS | Ex | CZ16 | 1.62 | 0.000505 | 0 | 1.63 | 0.000632 | -0.0115 | 1.38 | 0.0004 | 0 | 1.39 | 0.0005 | -0.00978 | CFL | Bldg | 1620 | 0.505 | 1380 | 0.4 | 1.01 | 1.25 | -0.00709
CFLBldgSDGOfSExIOU | Com-Iltg-dWatt-CFL_OSbldg | SDG | OfS | Ex | IOU | 1.63 | 0.000508 | 0 | 1.87 | 0.000635 | -0.000641 | 1.38 | 0.0004 | 0 | 1.58 | 0.0005 | -0.000543 | CFL | Bldg | 1630 | 0.508 | 1380 | 0.4 | 1.14 | 1.25 | -0.000393
CFLBldgPGEOfSExIOU | Com-Iltg-dWatt-CFL_OSbldg | PGE | OfS | Ex | IOU | 1.62 | 0.000506 | 0 | 1.73 | 0.000625 | -0.00599 | 1.38 | 0.0004 | 0 | 1.47 | 0.000493 | -0.00508 | CFL | Bldg | 1620 | 0.506 | 1380 | 0.4 | 1.07 | 1.23 | -0.00368
CFLBldgSCEOfSExIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | OfS | Ex | IOU | 1.62 | 0.000506 | 0 | 1.86 | 0.000643 | -0.00198 | 1.38 | 0.0004 | 0 | 1.58 | 0.000508 | -0.00168 | CFL | Bldg | 1620 | 0.506 | 1380 | 0.4 | 1.14 | 1.27 | -0.00122
CFLBldgSCGOfSExIOU | Com-Iltg-dWatt-CFL_OSbldg | SCG | OfS | Ex | IOU | 1.62 | 0.000506 | 0 | 1.86 | 0.000645 | -0.00206 | 1.38 | 0.0004 | 0 | 1.58 | 0.00051 | -0.00175 | CFL | Bldg | 1620 | 0.506 | 1380 | 0.4 | 1.14 | 1.28 | -0.00127
CFLBldgPGEOfSNewCZ01 | Com-Iltg-dWatt-CFL_OSbldg | PGE | OfS | New | CZ01 | 1.38 | 0.0004 | 0 | 1.36 | 0.00047 | -0.00798 | 1.38 | 0.0004 | 0 | 1.36 | 0.00047 | -0.00798 | CFL | Bldg | 1380 | 0.4 | 1380 | 0.4 | 0.986 | 1.18 | -0.00578
CFLBldgPGEOfSNewCZ02 | Com-Iltg-dWatt-CFL_OSbldg | PGE | OfS | New | CZ02 | 1.38 | 0.0004 | 0 | 1.44 | 0.000498 | -0.00429 | 1.38 | 0.0004 | 0 | 1.44 | 0.000498 | -0.00429 | CFL | Bldg | 1380 | 0.4 | 1380 | 0.4 | 1.04 | 1.25 | -0.00311
CFLBldgPGEOfSNewCZ03 | Com-Iltg-dWatt-CFL_OSbldg | PGE | OfS | New | CZ03 | 1.38 | 0.0004 | 0 | 1.42 | 0.000486 | -0.00468 | 1.38 | 0.0004 | 0 | 1.42 | 0.000486 | -0.00468 | CFL | Bldg | 1380 | 0.4 | 1380 | 0.4 | 1.03 | 1.22 | -0.00339
CFLBldgPGEOfSNewCZ04 | Com-Iltg-dWatt-CFL_OSbldg | PGE | OfS | New | CZ04 | 1.38 | 0.0004 | 0 | 1.46 | 0.000495 | -0.00342 | 1.38 | 0.0004 | 0 | 1.46 | 0.000495 | -0.00342 | CFL | Bldg | 1380 | 0.4 | 1380 | 0.4 | 1.06 | 1.24 | -0.00248
CFLBldgPGEOfSNewCZ05 | Com-Iltg-dWatt-CFL_OSbldg | PGE | OfS | New | CZ05 | 1.38 | 0.0004 | 0 | 1.43 | 0.000478 | -0.00371 | 1.38 | 0.0004 | 0 | 1.43 | 0.000478 | -0.00371 | CFL | Bldg | 1380 | 0.4 | 1380 | 0.4 | 1.04 | 1.2 | -0.00269
CFLBldgSCEOfSNewCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | OfS | New | CZ05 | 1.38 | 0.0004 | 0 | 1.44 | 0.000495 | -0.00391 | 1.38 | 0.0004 | 0 | 1.44 | 0.000495 | -0.00391 | CFL | Bldg | 1380 | 0.4 | 1380 | 0.4 | 1.04 | 1.24 | -0.00283
CFLBldgSDGOfSNewCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SDG | OfS | New | CZ06 | 1.38 | 0.0004 | 0 | 1.51 | 0.000496 | -0.00122 | 1.38 | 0.0004 | 0 | 1.51 | 0.000496 | -0.00122 | CFL | Bldg | 1380 | 0.4 | 1380 | 0.4 | 1.09 | 1.24 | -0.000884
CFLBldgSCEOfSNewCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | OfS | New | CZ06 | 1.38 | 0.0004 | 0 | 1.52 | 0.000502 | -0.00157 | 1.38 | 0.0004 | 0 | 1.52 | 0.000502 | -0.00157 | CFL | Bldg | 1380 | 0.4 | 1380 | 0.4 | 1.1 | 1.26 | -0.00114
CFLBldgSDGOfSNewCZ07 | Com-Iltg-dWatt-CFL_OSbldg | SDG | OfS | New | CZ07 | 1.38 | 0.0004 | 0 | 1.51 | 0.000489 | -0.000286 | 1.38 | 0.0004 | 0 | 1.51 | 0.000489 | -0.000286 | CFL | Bldg | 1380 | 0.4 | 1380 | 0.4 | 1.09 | 1.22 | -0.000207
CFLBldgSCEOfSNewCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | OfS | New | CZ08 | 1.38 | 0.0004 | 0 | 1.53 | 0.000508 | -0.00139 | 1.38 | 0.0004 | 0 | 1.53 | 0.000508 | -0.00139 | CFL | Bldg | 1380 | 0.4 | 1380 | 0.4 | 1.11 | 1.27 | -0.00101
CFLBldgSDGOfSNewCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SDG | OfS | New | CZ08 | 1.38 | 0.0004 | 0 | 1.52 | 0.000501 | -0.00103 | 1.38 | 0.0004 | 0 | 1.52 | 0.000501 | -0.00103 | CFL | Bldg | 1380 | 0.4 | 1380 | 0.4 | 1.1 | 1.25 | -0.000746
CFLBldgSCEOfSNewCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | OfS | New | CZ09 | 1.38 | 0.0004 | 0 | 1.53 | 0.000521 | -0.00157 | 1.38 | 0.0004 | 0 | 1.53 | 0.000521 | -0.00157 | CFL | Bldg | 1380 | 0.4 | 1380 | 0.4 | 1.11 | 1.3 | -0.00114
CFLBldgSDGOfSNewCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SDG | OfS | New | CZ10 | 1.38 | 0.0004 | 0 | 1.54 | 0.000519 | -0.000816 | 1.38 | 0.0004 | 0 | 1.54 | 0.000519 | -0.000816 | CFL | Bldg | 1380 | 0.4 | 1380 | 0.4 | 1.12 | 1.3 | -0.000591
CFLBldgSCEOfSNewCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | OfS | New | CZ10 | 1.38 | 0.0004 | 0 | 1.55 | 0.000527 | -0.00111 | 1.38 | 0.0004 | 0 | 1.55 | 0.000527 | -0.00111 | CFL | Bldg | 1380 | 0.4 | 1380 | 0.4 | 1.12 | 1.32 | -0.000804
CFLBldgPGEOfSNewCZ11 | Com-Iltg-dWatt-CFL_OSbldg | PGE | OfS | New | CZ11 | 1.38 | 0.0004 | 0 | 1.47 | 0.000502 | -0.00475 | 1.38 | 0.0004 | 0 | 1.47 | 0.000502 | -0.00475 | CFL | Bldg | 1380 | 0.4 | 1380 | 0.4 | 1.07 | 1.26 | -0.00344
CFLBldgPGEOfSNewCZ12 | Com-Iltg-dWatt-CFL_OSbldg | PGE | OfS | New | CZ12 | 1.38 | 0.0004 | 0 | 1.46 | 0.0005 | -0.0046 | 1.38 | 0.0004 | 0 | 1.46 | 0.0005 | -0.0046 | CFL | Bldg | 1380 | 0.4 | 1380 | 0.4 | 1.06 | 1.25 | -0.00333
CFLBldgSCEOfSNewCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | OfS | New | CZ13 | 1.38 | 0.0004 | 0 | 1.5 | 0.000518 | -0.00414 | 1.38 | 0.0004 | 0 | 1.5 | 0.000518 | -0.00414 | CFL | Bldg | 1380 | 0.4 | 1380 | 0.4 | 1.09 | 1.3 | -0.003
CFLBldgPGEOfSNewCZ13 | Com-Iltg-dWatt-CFL_OSbldg | PGE | OfS | New | CZ13 | 1.38 | 0.0004 | 0 | 1.47 | 0.000497 | -0.00437 | 1.38 | 0.0004 | 0 | 1.47 | 0.000497 | -0.00437 | CFL | Bldg | 1380 | 0.4 | 1380 | 0.4 | 1.07 | 1.24 | -0.00317
CFLBldgSCEOfSNewCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | OfS | New | CZ14 | 1.38 | 0.0004 | 0 | 1.51 | 0.000527 | -0.00345 | 1.38 | 0.0004 | 0 | 1.51 | 0.000527 | -0.00345 | CFL | Bldg | 1380 | 0.4 | 1380 | 0.4 | 1.09 | 1.32 | -0.0025
CFLBldgSDGOfSNewCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SDG | OfS | New | CZ14 | 1.38 | 0.0004 | 0 | 1.5 | 0.000519 | -0.00312 | 1.38 | 0.0004 | 0 | 1.5 | 0.000519 | -0.00312 | CFL | Bldg | 1380 | 0.4 | 1380 | 0.4 | 1.09 | 1.3 | -0.00226
CFLBldgSCEOfSNewCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | OfS | New | CZ15 | 1.38 | 0.0004 | 0 | 1.62 | 0.000533 | -0.000103 | 1.38 | 0.0004 | 0 | 1.62 | 0.000533 | -0.000103 | CFL | Bldg | 1380 | 0.4 | 1380 | 0.4 | 1.17 | 1.33 | -7.46e-05
CFLBldgSDGOfSNewCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SDG | OfS | New | CZ15 | 1.38 | 0.0004 | 0 | 1.61 | 0.000525 | 0 | 1.38 | 0.0004 | 0 | 1.61 | 0.000525 | 0 | CFL | Bldg | 1380 | 0.4 | 1380 | 0.4 | 1.17 | 1.31 | 0
CFLBldgSCEOfSNewCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | OfS | New | CZ16 | 1.38 | 0.0004 | 0 | 1.38 | 0.000502 | -0.00922 | 1.38 | 0.0004 | 0 | 1.38 | 0.000502 | -0.00922 | CFL | Bldg | 1380 | 0.4 | 1380 | 0.4 | 1 | 1.26 | -0.00668
CFLBldgPGEOfSNewCZ16 | Com-Iltg-dWatt-CFL_OSbldg | PGE | OfS | New | CZ16 | 1.38 | 0.0004 | 0 | 1.37 | 0.000484 | -0.00992 | 1.38 | 0.0004 | 0 | 1.37 | 0.000484 | -0.00992 | CFL | Bldg | 1380 | 0.4 | 1380 | 0.4 | 0.993 | 1.21 | -0.00719
CFLBldgSCEOfSNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | OfS | New | IOU | 1.38 | 0.0004 | 0 | 1.53 | 0.000509 | -0.000994 | 1.38 | 0.0004 | 0 | 1.53 | 0.000509 | -0.000994 | CFL | Bldg | 1380 | 0.4 | 1380 | 0.4 | 1.11 | 1.27 | -0.00072
CFLBldgSDGOfSNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SDG | OfS | New | IOU | 1.38 | 0.0004 | 0 | 1.52 | 0.000495 | -0.000425 | 1.38 | 0.0004 | 0 | 1.52 | 0.000495 | -0.000425 | CFL | Bldg | 1380 | 0.4 | 1380 | 0.4 | 1.1 | 1.24 | -0.000308
CFLBldgSCGOfSNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SCG | OfS | New | IOU | 1.38 | 0.0004 | 0 | 1.53 | 0.000509 | -0.001 | 1.38 | 0.0004 | 0 | 1.53 | 0.000509 | -0.001 | CFL | Bldg | 1380 | 0.4 | 1380 | 0.4 | 1.11 | 1.27 | -0.000725
CFLBldgPGEOfSNewIOU | Com-Iltg-dWatt-CFL_OSbldg | PGE | OfS | New | IOU | 1.38 | 0.0004 | 0 | 1.49 | 0.000516 | -0.00429 | 1.38 | 0.0004 | 0 | 1.49 | 0.000516 | -0.00429 | CFL | Bldg | 1380 | 0.4 | 1380 | 0.4 | 1.08 | 1.29 | -0.00311
CFLBldgPGERFFExCZ01 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RFF | Ex | CZ01 | 3.72 | 0.00067 | 0 | 3.63 | 0.000761 | -0.0439 | 3.72 | 0.00067 | 0 | 3.63 | 0.000761 | -0.0439 | CFL | Bldg | 3720 | 0.67 | 3720 | 0.67 | 0.976 | 1.14 | -0.0118
CFLBldgPGERFFExCZ02 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RFF | Ex | CZ02 | 3.72 | 0.00067 | 0 | 3.84 | 0.000778 | -0.0285 | 3.72 | 0.00067 | 0 | 3.84 | 0.000778 | -0.0285 | CFL | Bldg | 3720 | 0.67 | 3720 | 0.67 | 1.03 | 1.16 | -0.00766
CFLBldgPGERFFExCZ03 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RFF | Ex | CZ03 | 3.72 | 0.00067 | 0 | 3.8 | 0.000773 | -0.0302 | 3.72 | 0.00067 | 0 | 3.8 | 0.000773 | -0.0302 | CFL | Bldg | 3720 | 0.67 | 3720 | 0.67 | 1.02 | 1.15 | -0.00812
CFLBldgPGERFFExCZ04 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RFF | Ex | CZ04 | 3.72 | 0.00067 | 0 | 3.9 | 0.000777 | -0.024 | 3.72 | 0.00067 | 0 | 3.9 | 0.000777 | -0.024 | CFL | Bldg | 3720 | 0.67 | 3720 | 0.67 | 1.05 | 1.16 | -0.00645
CFLBldgSCGRFFExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCG | RFF | Ex | CZ05 | 3.72 | 0.00067 | 0 | 3.87 | 0.000793 | -0.0347 | 3.72 | 0.00067 | 0 | 3.87 | 0.000793 | -0.0347 | CFL | Bldg | 3720 | 0.67 | 3720 | 0.67 | 1.04 | 1.18 | -0.00933
CFLBldgSCERFFExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RFF | Ex | CZ05 | 3.72 | 0.00067 | 0 | 3.87 | 0.000793 | -0.0347 | 3.72 | 0.00067 | 0 | 3.87 | 0.000793 | -0.0347 | CFL | Bldg | 3720 | 0.67 | 3720 | 0.67 | 1.04 | 1.18 | -0.00933
CFLBldgPGERFFExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RFF | Ex | CZ05 | 3.72 | 0.00067 | 0 | 3.87 | 0.000793 | -0.0347 | 3.72 | 0.00067 | 0 | 3.87 | 0.000793 | -0.0347 | CFL | Bldg | 3720 | 0.67 | 3720 | 0.67 | 1.04 | 1.18 | -0.00933
CFLBldgSCGRFFExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCG | RFF | Ex | CZ06 | 3.72 | 0.00067 | 0 | 4.13 | 0.000818 | -0.0199 | 3.72 | 0.00067 | 0 | 4.13 | 0.000818 | -0.0199 | CFL | Bldg | 3720 | 0.67 | 3720 | 0.67 | 1.11 | 1.22 | -0.00535
CFLBldgSCERFFExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RFF | Ex | CZ06 | 3.72 | 0.00067 | 0 | 4.13 | 0.000818 | -0.0199 | 3.72 | 0.00067 | 0 | 4.13 | 0.000818 | -0.0199 | CFL | Bldg | 3720 | 0.67 | 3720 | 0.67 | 1.11 | 1.22 | -0.00535
CFLBldgSDGRFFExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SDG | RFF | Ex | CZ06 | 3.72 | 0.00067 | 0 | 4.13 | 0.000818 | -0.0199 | 3.72 | 0.00067 | 0 | 4.13 | 0.000818 | -0.0199 | CFL | Bldg | 3720 | 0.67 | 3720 | 0.67 | 1.11 | 1.22 | -0.00535
CFLBldgSDGRFFExCZ07 | Com-Iltg-dWatt-CFL_OSbldg | SDG | RFF | Ex | CZ07 | 3.72 | 0.00067 | 0 | 4.14 | 0.000812 | -0.0179 | 3.72 | 0.00067 | 0 | 4.14 | 0.000812 | -0.0179 | CFL | Bldg | 3720 | 0.67 | 3720 | 0.67 | 1.11 | 1.21 | -0.00481
CFLBldgSDGRFFExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SDG | RFF | Ex | CZ08 | 3.72 | 0.00067 | 0 | 4.16 | 0.000811 | -0.0175 | 3.72 | 0.00067 | 0 | 4.16 | 0.000811 | -0.0175 | CFL | Bldg | 3720 | 0.67 | 3720 | 0.67 | 1.12 | 1.21 | -0.0047
CFLBldgSCERFFExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RFF | Ex | CZ08 | 3.72 | 0.00067 | 0 | 4.16 | 0.000811 | -0.0175 | 3.72 | 0.00067 | 0 | 4.16 | 0.000811 | -0.0175 | CFL | Bldg | 3720 | 0.67 | 3720 | 0.67 | 1.12 | 1.21 | -0.0047
CFLBldgSCGRFFExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCG | RFF | Ex | CZ08 | 3.72 | 0.00067 | 0 | 4.16 | 0.000811 | -0.0175 | 3.72 | 0.00067 | 0 | 4.16 | 0.000811 | -0.0175 | CFL | Bldg | 3720 | 0.67 | 3720 | 0.67 | 1.12 | 1.21 | -0.0047
CFLBldgSCGRFFExCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCG | RFF | Ex | CZ09 | 3.72 | 0.00067 | 0 | 4.1 | 0.000821 | -0.0179 | 3.72 | 0.00067 | 0 | 4.1 | 0.000821 | -0.0179 | CFL | Bldg | 3720 | 0.67 | 3720 | 0.67 | 1.1 | 1.23 | -0.00481
CFLBldgSCERFFExCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RFF | Ex | CZ09 | 3.72 | 0.00067 | 0 | 4.1 | 0.000821 | -0.0179 | 3.72 | 0.00067 | 0 | 4.1 | 0.000821 | -0.0179 | CFL | Bldg | 3720 | 0.67 | 3720 | 0.67 | 1.1 | 1.23 | -0.00481
CFLBldgSDGRFFExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SDG | RFF | Ex | CZ10 | 3.72 | 0.00067 | 0 | 4.17 | 0.000825 | -0.0195 | 3.72 | 0.00067 | 0 | 4.17 | 0.000825 | -0.0195 | CFL | Bldg | 3720 | 0.67 | 3720 | 0.67 | 1.12 | 1.23 | -0.00524
CFLBldgSCERFFExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RFF | Ex | CZ10 | 3.72 | 0.00067 | 0 | 4.17 | 0.000825 | -0.0195 | 3.72 | 0.00067 | 0 | 4.17 | 0.000825 | -0.0195 | CFL | Bldg | 3720 | 0.67 | 3720 | 0.67 | 1.12 | 1.23 | -0.00524
CFLBldgSCGRFFExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCG | RFF | Ex | CZ10 | 3.72 | 0.00067 | 0 | 4.17 | 0.000825 | -0.0195 | 3.72 | 0.00067 | 0 | 4.17 | 0.000825 | -0.0195 | CFL | Bldg | 3720 | 0.67 | 3720 | 0.67 | 1.12 | 1.23 | -0.00524
CFLBldgPGERFFExCZ11 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RFF | Ex | CZ11 | 3.72 | 0.00067 | 0 | 3.92 | 0.000793 | -0.0235 | 3.72 | 0.00067 | 0 | 3.92 | 0.000793 | -0.0235 | CFL | Bldg | 3720 | 0.67 | 3720 | 0.67 | 1.05 | 1.18 | -0.00632
CFLBldgPGERFFExCZ12 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RFF | Ex | CZ12 | 3.72 | 0.00067 | 0 | 3.9 | 0.000785 | -0.0246 | 3.72 | 0.00067 | 0 | 3.9 | 0.000785 | -0.0246 | CFL | Bldg | 3720 | 0.67 | 3720 | 0.67 | 1.05 | 1.17 | -0.00661
CFLBldgSCGRFFExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCG | RFF | Ex | CZ13 | 3.72 | 0.00067 | 0 | 4.02 | 0.000813 | -0.0262 | 3.72 | 0.00067 | 0 | 4.02 | 0.000813 | -0.0262 | CFL | Bldg | 3720 | 0.67 | 3720 | 0.67 | 1.08 | 1.21 | -0.00704
CFLBldgSCERFFExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RFF | Ex | CZ13 | 3.72 | 0.00067 | 0 | 4.02 | 0.000813 | -0.0262 | 3.72 | 0.00067 | 0 | 4.02 | 0.000813 | -0.0262 | CFL | Bldg | 3720 | 0.67 | 3720 | 0.67 | 1.08 | 1.21 | -0.00704
CFLBldgPGERFFExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RFF | Ex | CZ13 | 3.72 | 0.00067 | 0 | 4.02 | 0.000813 | -0.0262 | 3.72 | 0.00067 | 0 | 4.02 | 0.000813 | -0.0262 | CFL | Bldg | 3720 | 0.67 | 3720 | 0.67 | 1.08 | 1.21 | -0.00704
CFLBldgSCERFFExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RFF | Ex | CZ14 | 3.72 | 0.00067 | 0 | 4.1 | 0.00084 | -0.0275 | 3.72 | 0.00067 | 0 | 4.1 | 0.00084 | -0.0275 | CFL | Bldg | 3720 | 0.67 | 3720 | 0.67 | 1.1 | 1.25 | -0.00739
CFLBldgSDGRFFExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SDG | RFF | Ex | CZ14 | 3.72 | 0.00067 | 0 | 4.1 | 0.00084 | -0.0275 | 3.72 | 0.00067 | 0 | 4.1 | 0.00084 | -0.0275 | CFL | Bldg | 3720 | 0.67 | 3720 | 0.67 | 1.1 | 1.25 | -0.00739
CFLBldgSCGRFFExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCG | RFF | Ex | CZ14 | 3.72 | 0.00067 | 0 | 4.1 | 0.00084 | -0.0275 | 3.72 | 0.00067 | 0 | 4.1 | 0.00084 | -0.0275 | CFL | Bldg | 3720 | 0.67 | 3720 | 0.67 | 1.1 | 1.25 | -0.00739
CFLBldgSDGRFFExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SDG | RFF | Ex | CZ15 | 3.72 | 0.00067 | 0 | 4.42 | 0.000833 | -0.00904 | 3.72 | 0.00067 | 0 | 4.42 | 0.000833 | -0.00904 | CFL | Bldg | 3720 | 0.67 | 3720 | 0.67 | 1.19 | 1.24 | -0.00243
CFLBldgSCERFFExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RFF | Ex | CZ15 | 3.72 | 0.00067 | 0 | 4.42 | 0.000833 | -0.00904 | 3.72 | 0.00067 | 0 | 4.42 | 0.000833 | -0.00904 | CFL | Bldg | 3720 | 0.67 | 3720 | 0.67 | 1.19 | 1.24 | -0.00243
CFLBldgSCGRFFExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCG | RFF | Ex | CZ15 | 3.72 | 0.00067 | 0 | 4.42 | 0.000833 | -0.00904 | 3.72 | 0.00067 | 0 | 4.42 | 0.000833 | -0.00904 | CFL | Bldg | 3720 | 0.67 | 3720 | 0.67 | 1.19 | 1.24 | -0.00243
CFLBldgPGERFFExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RFF | Ex | CZ16 | 3.72 | 0.00067 | 0 | 3.72 | 0.000795 | -0.0502 | 3.72 | 0.00067 | 0 | 3.72 | 0.000795 | -0.0502 | CFL | Bldg | 3720 | 0.67 | 3720 | 0.67 | 1 | 1.19 | -0.0135
CFLBldgSCERFFExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RFF | Ex | CZ16 | 3.72 | 0.00067 | 0 | 3.72 | 0.000795 | -0.0502 | 3.72 | 0.00067 | 0 | 3.72 | 0.000795 | -0.0502 | CFL | Bldg | 3720 | 0.67 | 3720 | 0.67 | 1 | 1.19 | -0.0135
CFLBldgSCGRFFExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCG | RFF | Ex | CZ16 | 3.72 | 0.00067 | 0 | 3.72 | 0.000795 | -0.0502 | 3.72 | 0.00067 | 0 | 3.72 | 0.000795 | -0.0502 | CFL | Bldg | 3720 | 0.67 | 3720 | 0.67 | 1 | 1.19 | -0.0135
CFLBldgSCGRFFExIOU | Com-Iltg-dWatt-CFL_OSbldg | SCG | RFF | Ex | IOU | 3.72 | 0.00067 | 0 | 4.14 | 0.000819 | -0.0192 | 3.72 | 0.00067 | 0 | 4.14 | 0.000819 | -0.0192 | CFL | Bldg | 3720 | 0.67 | 3720 | 0.67 | 1.11 | 1.22 | -0.00516
CFLBldgPGERFFExIOU | Com-Iltg-dWatt-CFL_OSbldg | PGE | RFF | Ex | IOU | 3.72 | 0.00067 | 0 | 3.88 | 0.000784 | -0.0276 | 3.72 | 0.00067 | 0 | 3.88 | 0.000784 | -0.0276 | CFL | Bldg | 3720 | 0.67 | 3720 | 0.67 | 1.04 | 1.17 | -0.00742
CFLBldgSCERFFExIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | RFF | Ex | IOU | 3.72 | 0.00067 | 0 | 4.14 | 0.000819 | -0.0195 | 3.72 | 0.00067 | 0 | 4.14 | 0.000819 | -0.0195 | CFL | Bldg | 3720 | 0.67 | 3720 | 0.67 | 1.11 | 1.22 | -0.00524
CFLBldgSDGRFFExIOU | Com-Iltg-dWatt-CFL_OSbldg | SDG | RFF | Ex | IOU | 3.72 | 0.00067 | 0 | 4.15 | 0.000815 | -0.0183 | 3.72 | 0.00067 | 0 | 4.15 | 0.000815 | -0.0183 | CFL | Bldg | 3720 | 0.67 | 3720 | 0.67 | 1.12 | 1.22 | -0.00492
CFLBldgPGERFFNewCZ01 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RFF | New | CZ01 | 3.72 | 0.00067 | 0 | 3.5 | 0.000729 | -0.0461 | 3.72 | 0.00067 | 0 | 3.5 | 0.000729 | -0.0461 | CFL | Bldg | 3720 | 0.67 | 3720 | 0.67 | 0.941 | 1.09 | -0.0124
CFLBldgPGERFFNewCZ02 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RFF | New | CZ02 | 3.72 | 0.00067 | 0 | 3.76 | 0.000808 | -0.0338 | 3.72 | 0.00067 | 0 | 3.76 | 0.000808 | -0.0338 | CFL | Bldg | 3720 | 0.67 | 3720 | 0.67 | 1.01 | 1.21 | -0.00909
CFLBldgPGERFFNewCZ03 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RFF | New | CZ03 | 3.72 | 0.00067 | 0 | 3.68 | 0.000784 | -0.0344 | 3.72 | 0.00067 | 0 | 3.68 | 0.000784 | -0.0344 | CFL | Bldg | 3720 | 0.67 | 3720 | 0.67 | 0.989 | 1.17 | -0.00925
CFLBldgPGERFFNewCZ04 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RFF | New | CZ04 | 3.72 | 0.00067 | 0 | 3.82 | 0.000799 | -0.0285 | 3.72 | 0.00067 | 0 | 3.82 | 0.000799 | -0.0285 | CFL | Bldg | 3720 | 0.67 | 3720 | 0.67 | 1.03 | 1.19 | -0.00766
CFLBldgPGERFFNewCZ05 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RFF | New | CZ05 | 3.72 | 0.00067 | 0 | 3.68 | 0.000773 | -0.0305 | 3.72 | 0.00067 | 0 | 3.68 | 0.000773 | -0.0305 | CFL | Bldg | 3720 | 0.67 | 3720 | 0.67 | 0.989 | 1.15 | -0.0082
CFLBldgSCERFFNewCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RFF | New | CZ05 | 3.72 | 0.00067 | 0 | 3.81 | 0.000805 | -0.0337 | 3.72 | 0.00067 | 0 | 3.81 | 0.000805 | -0.0337 | CFL | Bldg | 3720 | 0.67 | 3720 | 0.67 | 1.02 | 1.2 | -0.00906
CFLBldgSDGRFFNewCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SDG | RFF | New | CZ06 | 3.72 | 0.00067 | 0 | 3.99 | 0.000831 | -0.0209 | 3.72 | 0.00067 | 0 | 3.99 | 0.000831 | -0.0209 | CFL | Bldg | 3720 | 0.67 | 3720 | 0.67 | 1.07 | 1.24 | -0.00562
CFLBldgSCERFFNewCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RFF | New | CZ06 | 3.72 | 0.00067 | 0 | 4 | 0.000829 | -0.0201 | 3.72 | 0.00067 | 0 | 4 | 0.000829 | -0.0201 | CFL | Bldg | 3720 | 0.67 | 3720 | 0.67 | 1.08 | 1.24 | -0.0054
CFLBldgSDGRFFNewCZ07 | Com-Iltg-dWatt-CFL_OSbldg | SDG | RFF | New | CZ07 | 3.72 | 0.00067 | 0 | 3.97 | 0.000823 | -0.0221 | 3.72 | 0.00067 | 0 | 3.97 | 0.000823 | -0.0221 | CFL | Bldg | 3720 | 0.67 | 3720 | 0.67 | 1.07 | 1.23 | -0.00594
CFLBldgSDGRFFNewCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SDG | RFF | New | CZ08 | 3.72 | 0.00067 | 0 | 4 | 0.000806 | -0.0205 | 3.72 | 0.00067 | 0 | 4 | 0.000806 | -0.0205 | CFL | Bldg | 3720 | 0.67 | 3720 | 0.67 | 1.08 | 1.2 | -0.00551
CFLBldgSCERFFNewCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RFF | New | CZ08 | 3.72 | 0.00067 | 0 | 4 | 0.000804 | -0.0197 | 3.72 | 0.00067 | 0 | 4 | 0.000804 | -0.0197 | CFL | Bldg | 3720 | 0.67 | 3720 | 0.67 | 1.08 | 1.2 | -0.0053
CFLBldgSCERFFNewCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RFF | New | CZ09 | 3.72 | 0.00067 | 0 | 4.08 | 0.00086 | -0.022 | 3.72 | 0.00067 | 0 | 4.08 | 0.00086 | -0.022 | CFL | Bldg | 3720 | 0.67 | 3720 | 0.67 | 1.1 | 1.28 | -0.00591
CFLBldgSDGRFFNewCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SDG | RFF | New | CZ10 | 3.72 | 0.00067 | 0 | 4.09 | 0.000869 | -0.0238 | 3.72 | 0.00067 | 0 | 4.09 | 0.000869 | -0.0238 | CFL | Bldg | 3720 | 0.67 | 3720 | 0.67 | 1.1 | 1.3 | -0.0064
CFLBldgSCERFFNewCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RFF | New | CZ10 | 3.72 | 0.00067 | 0 | 4.1 | 0.000866 | -0.0229 | 3.72 | 0.00067 | 0 | 4.1 | 0.000866 | -0.0229 | CFL | Bldg | 3720 | 0.67 | 3720 | 0.67 | 1.1 | 1.29 | -0.00616
CFLBldgPGERFFNewCZ11 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RFF | New | CZ11 | 3.72 | 0.00067 | 0 | 3.91 | 0.000826 | -0.0257 | 3.72 | 0.00067 | 0 | 3.91 | 0.000826 | -0.0257 | CFL | Bldg | 3720 | 0.67 | 3720 | 0.67 | 1.05 | 1.23 | -0.00691
CFLBldgPGERFFNewCZ12 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RFF | New | CZ12 | 3.72 | 0.00067 | 0 | 3.87 | 0.000817 | -0.0302 | 3.72 | 0.00067 | 0 | 3.87 | 0.000817 | -0.0302 | CFL | Bldg | 3720 | 0.67 | 3720 | 0.67 | 1.04 | 1.22 | -0.00812
CFLBldgSCERFFNewCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RFF | New | CZ13 | 3.72 | 0.00067 | 0 | 4.08 | 0.000863 | -0.03 | 3.72 | 0.00067 | 0 | 4.08 | 0.000863 | -0.03 | CFL | Bldg | 3720 | 0.67 | 3720 | 0.67 | 1.1 | 1.29 | -0.00806
CFLBldgPGERFFNewCZ13 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RFF | New | CZ13 | 3.72 | 0.00067 | 0 | 3.92 | 0.000816 | -0.0268 | 3.72 | 0.00067 | 0 | 3.92 | 0.000816 | -0.0268 | CFL | Bldg | 3720 | 0.67 | 3720 | 0.67 | 1.05 | 1.22 | -0.0072
CFLBldgSDGRFFNewCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SDG | RFF | New | CZ14 | 3.72 | 0.00067 | 0 | 4.07 | 0.000874 | -0.0332 | 3.72 | 0.00067 | 0 | 4.07 | 0.000874 | -0.0332 | CFL | Bldg | 3720 | 0.67 | 3720 | 0.67 | 1.09 | 1.3 | -0.00892
CFLBldgSCERFFNewCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RFF | New | CZ14 | 3.72 | 0.00067 | 0 | 4.08 | 0.000871 | -0.0319 | 3.72 | 0.00067 | 0 | 4.08 | 0.000871 | -0.0319 | CFL | Bldg | 3720 | 0.67 | 3720 | 0.67 | 1.1 | 1.3 | -0.00858
CFLBldgSCERFFNewCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RFF | New | CZ15 | 3.72 | 0.00067 | 0 | 4.37 | 0.000882 | -0.0114 | 3.72 | 0.00067 | 0 | 4.37 | 0.000882 | -0.0114 | CFL | Bldg | 3720 | 0.67 | 3720 | 0.67 | 1.17 | 1.32 | -0.00306
CFLBldgSDGRFFNewCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SDG | RFF | New | CZ15 | 3.72 | 0.00067 | 0 | 4.38 | 0.000885 | -0.0118 | 3.72 | 0.00067 | 0 | 4.38 | 0.000885 | -0.0118 | CFL | Bldg | 3720 | 0.67 | 3720 | 0.67 | 1.18 | 1.32 | -0.00317
CFLBldgSCERFFNewCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RFF | New | CZ16 | 3.72 | 0.00067 | 0 | 3.77 | 0.000827 | -0.0539 | 3.72 | 0.00067 | 0 | 3.77 | 0.000827 | -0.0539 | CFL | Bldg | 3720 | 0.67 | 3720 | 0.67 | 1.01 | 1.23 | -0.0145
CFLBldgPGERFFNewCZ16 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RFF | New | CZ16 | 3.72 | 0.00067 | 0 | 3.62 | 0.000789 | -0.0476 | 3.72 | 0.00067 | 0 | 3.62 | 0.000789 | -0.0476 | CFL | Bldg | 3720 | 0.67 | 3720 | 0.67 | 0.973 | 1.18 | -0.0128
CFLBldgPGERFFNewIOU | Com-Iltg-dWatt-CFL_OSbldg | PGE | RFF | New | IOU | 3.72 | 0.00067 | 0 | 4.03 | 0.000853 | -0.0319 | 3.72 | 0.00067 | 0 | 4.03 | 0.000853 | -0.0319 | CFL | Bldg | 3720 | 0.67 | 3720 | 0.67 | 1.08 | 1.27 | -0.00858
CFLBldgSCGRFFNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SCG | RFF | New | IOU | 3.72 | 0.00067 | 0 | 4.05 | 0.000841 | -0.0219 | 3.72 | 0.00067 | 0 | 4.05 | 0.000841 | -0.0219 | CFL | Bldg | 3720 | 0.67 | 3720 | 0.67 | 1.09 | 1.26 | -0.00589
CFLBldgSDGRFFNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SDG | RFF | New | IOU | 3.72 | 0.00067 | 0 | 4 | 0.000833 | -0.0224 | 3.72 | 0.00067 | 0 | 4 | 0.000833 | -0.0224 | CFL | Bldg | 3720 | 0.67 | 3720 | 0.67 | 1.08 | 1.24 | -0.00602
CFLBldgSCERFFNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | RFF | New | IOU | 3.72 | 0.00067 | 0 | 4.06 | 0.000843 | -0.0219 | 3.72 | 0.00067 | 0 | 4.06 | 0.000843 | -0.0219 | CFL | Bldg | 3720 | 0.67 | 3720 | 0.67 | 1.09 | 1.26 | -0.00589
CFLBldgPGERSDExCZ01 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RSD | Ex | CZ01 | 3.68 | 0.000616 | 0 | 3.53 | 0.000722 | -0.046 | 3.68 | 0.000616 | 0 | 3.53 | 0.000722 | -0.046 | CFL | Bldg | 3680 | 0.616 | 3680 | 0.616 | 0.959 | 1.17 | -0.0125
CFLBldgPGERSDExCZ02 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RSD | Ex | CZ02 | 3.68 | 0.000616 | 0 | 3.82 | 0.000722 | -0.027 | 3.68 | 0.000616 | 0 | 3.82 | 0.000722 | -0.027 | CFL | Bldg | 3680 | 0.616 | 3680 | 0.616 | 1.04 | 1.17 | -0.00734
CFLBldgPGERSDExCZ03 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RSD | Ex | CZ03 | 3.68 | 0.000616 | 0 | 3.76 | 0.000723 | -0.0302 | 3.68 | 0.000616 | 0 | 3.76 | 0.000723 | -0.0302 | CFL | Bldg | 3680 | 0.616 | 3680 | 0.616 | 1.02 | 1.17 | -0.00821
CFLBldgPGERSDExCZ04 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RSD | Ex | CZ04 | 3.68 | 0.000616 | 0 | 3.88 | 0.000725 | -0.0224 | 3.68 | 0.000616 | 0 | 3.88 | 0.000725 | -0.0224 | CFL | Bldg | 3680 | 0.616 | 3680 | 0.616 | 1.05 | 1.18 | -0.00609
CFLBldgSCERSDExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RSD | Ex | CZ05 | 3.68 | 0.000616 | 0 | 3.87 | 0.000749 | -0.0331 | 3.68 | 0.000616 | 0 | 3.87 | 0.000749 | -0.0331 | CFL | Bldg | 3680 | 0.616 | 3680 | 0.616 | 1.05 | 1.22 | -0.00899
CFLBldgPGERSDExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RSD | Ex | CZ05 | 3.68 | 0.000616 | 0 | 3.87 | 0.000749 | -0.0331 | 3.68 | 0.000616 | 0 | 3.87 | 0.000749 | -0.0331 | CFL | Bldg | 3680 | 0.616 | 3680 | 0.616 | 1.05 | 1.22 | -0.00899
CFLBldgSCGRSDExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCG | RSD | Ex | CZ05 | 3.68 | 0.000616 | 0 | 3.87 | 0.000749 | -0.0331 | 3.68 | 0.000616 | 0 | 3.87 | 0.000749 | -0.0331 | CFL | Bldg | 3680 | 0.616 | 3680 | 0.616 | 1.05 | 1.22 | -0.00899
CFLBldgSCERSDExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RSD | Ex | CZ06 | 3.68 | 0.000616 | 0 | 4.16 | 0.000765 | -0.0176 | 3.68 | 0.000616 | 0 | 4.16 | 0.000765 | -0.0176 | CFL | Bldg | 3680 | 0.616 | 3680 | 0.616 | 1.13 | 1.24 | -0.00478
CFLBldgSDGRSDExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SDG | RSD | Ex | CZ06 | 3.68 | 0.000616 | 0 | 4.16 | 0.000765 | -0.0176 | 3.68 | 0.000616 | 0 | 4.16 | 0.000765 | -0.0176 | CFL | Bldg | 3680 | 0.616 | 3680 | 0.616 | 1.13 | 1.24 | -0.00478
CFLBldgSCGRSDExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCG | RSD | Ex | CZ06 | 3.68 | 0.000616 | 0 | 4.16 | 0.000765 | -0.0176 | 3.68 | 0.000616 | 0 | 4.16 | 0.000765 | -0.0176 | CFL | Bldg | 3680 | 0.616 | 3680 | 0.616 | 1.13 | 1.24 | -0.00478
CFLBldgSDGRSDExCZ07 | Com-Iltg-dWatt-CFL_OSbldg | SDG | RSD | Ex | CZ07 | 3.68 | 0.000616 | 0 | 4.16 | 0.000769 | -0.0153 | 3.68 | 0.000616 | 0 | 4.16 | 0.000769 | -0.0153 | CFL | Bldg | 3680 | 0.616 | 3680 | 0.616 | 1.13 | 1.25 | -0.00416
CFLBldgSCERSDExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RSD | Ex | CZ08 | 3.68 | 0.000616 | 0 | 4.19 | 0.000747 | -0.0149 | 3.68 | 0.000616 | 0 | 4.19 | 0.000747 | -0.0149 | CFL | Bldg | 3680 | 0.616 | 3680 | 0.616 | 1.14 | 1.21 | -0.00405
CFLBldgSDGRSDExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SDG | RSD | Ex | CZ08 | 3.68 | 0.000616 | 0 | 4.19 | 0.000747 | -0.0149 | 3.68 | 0.000616 | 0 | 4.19 | 0.000747 | -0.0149 | CFL | Bldg | 3680 | 0.616 | 3680 | 0.616 | 1.14 | 1.21 | -0.00405
CFLBldgSCGRSDExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCG | RSD | Ex | CZ08 | 3.68 | 0.000616 | 0 | 4.19 | 0.000747 | -0.0149 | 3.68 | 0.000616 | 0 | 4.19 | 0.000747 | -0.0149 | CFL | Bldg | 3680 | 0.616 | 3680 | 0.616 | 1.14 | 1.21 | -0.00405
CFLBldgSCERSDExCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RSD | Ex | CZ09 | 3.68 | 0.000616 | 0 | 4.12 | 0.000752 | -0.0164 | 3.68 | 0.000616 | 0 | 4.12 | 0.000752 | -0.0164 | CFL | Bldg | 3680 | 0.616 | 3680 | 0.616 | 1.12 | 1.22 | -0.00446
CFLBldgSCGRSDExCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCG | RSD | Ex | CZ09 | 3.68 | 0.000616 | 0 | 4.12 | 0.000752 | -0.0164 | 3.68 | 0.000616 | 0 | 4.12 | 0.000752 | -0.0164 | CFL | Bldg | 3680 | 0.616 | 3680 | 0.616 | 1.12 | 1.22 | -0.00446
CFLBldgSCGRSDExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCG | RSD | Ex | CZ10 | 3.68 | 0.000616 | 0 | 4.17 | 0.000738 | -0.0176 | 3.68 | 0.000616 | 0 | 4.17 | 0.000738 | -0.0176 | CFL | Bldg | 3680 | 0.616 | 3680 | 0.616 | 1.13 | 1.2 | -0.00478
CFLBldgSDGRSDExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SDG | RSD | Ex | CZ10 | 3.68 | 0.000616 | 0 | 4.17 | 0.000738 | -0.0176 | 3.68 | 0.000616 | 0 | 4.17 | 0.000738 | -0.0176 | CFL | Bldg | 3680 | 0.616 | 3680 | 0.616 | 1.13 | 1.2 | -0.00478
CFLBldgSCERSDExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RSD | Ex | CZ10 | 3.68 | 0.000616 | 0 | 4.17 | 0.000738 | -0.0176 | 3.68 | 0.000616 | 0 | 4.17 | 0.000738 | -0.0176 | CFL | Bldg | 3680 | 0.616 | 3680 | 0.616 | 1.13 | 1.2 | -0.00478
CFLBldgPGERSDExCZ11 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RSD | Ex | CZ11 | 3.68 | 0.000616 | 0 | 3.9 | 0.000729 | -0.0233 | 3.68 | 0.000616 | 0 | 3.9 | 0.000729 | -0.0233 | CFL | Bldg | 3680 | 0.616 | 3680 | 0.616 | 1.06 | 1.18 | -0.00633
CFLBldgPGERSDExCZ12 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RSD | Ex | CZ12 | 3.68 | 0.000616 | 0 | 3.86 | 0.000706 | -0.0241 | 3.68 | 0.000616 | 0 | 3.86 | 0.000706 | -0.0241 | CFL | Bldg | 3680 | 0.616 | 3680 | 0.616 | 1.05 | 1.15 | -0.00655
CFLBldgPGERSDExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RSD | Ex | CZ13 | 3.68 | 0.000616 | 0 | 4.03 | 0.000758 | -0.0255 | 3.68 | 0.000616 | 0 | 4.03 | 0.000758 | -0.0255 | CFL | Bldg | 3680 | 0.616 | 3680 | 0.616 | 1.1 | 1.23 | -0.00693
CFLBldgSCGRSDExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCG | RSD | Ex | CZ13 | 3.68 | 0.000616 | 0 | 4.03 | 0.000758 | -0.0255 | 3.68 | 0.000616 | 0 | 4.03 | 0.000758 | -0.0255 | CFL | Bldg | 3680 | 0.616 | 3680 | 0.616 | 1.1 | 1.23 | -0.00693
CFLBldgSCERSDExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RSD | Ex | CZ13 | 3.68 | 0.000616 | 0 | 4.03 | 0.000758 | -0.0255 | 3.68 | 0.000616 | 0 | 4.03 | 0.000758 | -0.0255 | CFL | Bldg | 3680 | 0.616 | 3680 | 0.616 | 1.1 | 1.23 | -0.00693
CFLBldgSCERSDExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RSD | Ex | CZ14 | 3.68 | 0.000616 | 0 | 4.07 | 0.000739 | -0.0273 | 3.68 | 0.000616 | 0 | 4.07 | 0.000739 | -0.0273 | CFL | Bldg | 3680 | 0.616 | 3680 | 0.616 | 1.11 | 1.2 | -0.00742
CFLBldgSCGRSDExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCG | RSD | Ex | CZ14 | 3.68 | 0.000616 | 0 | 4.07 | 0.000739 | -0.0273 | 3.68 | 0.000616 | 0 | 4.07 | 0.000739 | -0.0273 | CFL | Bldg | 3680 | 0.616 | 3680 | 0.616 | 1.11 | 1.2 | -0.00742
CFLBldgSDGRSDExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SDG | RSD | Ex | CZ14 | 3.68 | 0.000616 | 0 | 4.07 | 0.000739 | -0.0273 | 3.68 | 0.000616 | 0 | 4.07 | 0.000739 | -0.0273 | CFL | Bldg | 3680 | 0.616 | 3680 | 0.616 | 1.11 | 1.2 | -0.00742
CFLBldgSDGRSDExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SDG | RSD | Ex | CZ15 | 3.68 | 0.000616 | 0 | 4.48 | 0.000786 | -0.00651 | 3.68 | 0.000616 | 0 | 4.48 | 0.000786 | -0.00651 | CFL | Bldg | 3680 | 0.616 | 3680 | 0.616 | 1.22 | 1.28 | -0.00177
CFLBldgSCGRSDExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCG | RSD | Ex | CZ15 | 3.68 | 0.000616 | 0 | 4.48 | 0.000786 | -0.00651 | 3.68 | 0.000616 | 0 | 4.48 | 0.000786 | -0.00651 | CFL | Bldg | 3680 | 0.616 | 3680 | 0.616 | 1.22 | 1.28 | -0.00177
CFLBldgSCERSDExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RSD | Ex | CZ15 | 3.68 | 0.000616 | 0 | 4.48 | 0.000786 | -0.00651 | 3.68 | 0.000616 | 0 | 4.48 | 0.000786 | -0.00651 | CFL | Bldg | 3680 | 0.616 | 3680 | 0.616 | 1.22 | 1.28 | -0.00177
CFLBldgPGERSDExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RSD | Ex | CZ16 | 3.68 | 0.000616 | 0 | 3.7 | 0.00073 | -0.0471 | 3.68 | 0.000616 | 0 | 3.7 | 0.00073 | -0.0471 | CFL | Bldg | 3680 | 0.616 | 3680 | 0.616 | 1.01 | 1.19 | -0.0128
CFLBldgSCERSDExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RSD | Ex | CZ16 | 3.68 | 0.000616 | 0 | 3.7 | 0.00073 | -0.0471 | 3.68 | 0.000616 | 0 | 3.7 | 0.00073 | -0.0471 | CFL | Bldg | 3680 | 0.616 | 3680 | 0.616 | 1.01 | 1.19 | -0.0128
CFLBldgSCGRSDExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCG | RSD | Ex | CZ16 | 3.68 | 0.000616 | 0 | 3.7 | 0.00073 | -0.0471 | 3.68 | 0.000616 | 0 | 3.7 | 0.00073 | -0.0471 | CFL | Bldg | 3680 | 0.616 | 3680 | 0.616 | 1.01 | 1.19 | -0.0128
CFLBldgPGERSDExIOU | Com-Iltg-dWatt-CFL_OSbldg | PGE | RSD | Ex | IOU | 3.68 | 0.000616 | 0 | 3.85 | 0.000726 | -0.027 | 3.68 | 0.000616 | 0 | 3.85 | 0.000726 | -0.027 | CFL | Bldg | 3680 | 0.616 | 3680 | 0.616 | 1.05 | 1.18 | -0.00734
CFLBldgSDGRSDExIOU | Com-Iltg-dWatt-CFL_OSbldg | SDG | RSD | Ex | IOU | 3.68 | 0.000616 | 0 | 4.16 | 0.000761 | -0.0159 | 3.68 | 0.000616 | 0 | 4.16 | 0.000761 | -0.0159 | CFL | Bldg | 3680 | 0.616 | 3680 | 0.616 | 1.13 | 1.24 | -0.00432
CFLBldgSCGRSDExIOU | Com-Iltg-dWatt-CFL_OSbldg | SCG | RSD | Ex | IOU | 3.68 | 0.000616 | 0 | 4.16 | 0.000751 | -0.0172 | 3.68 | 0.000616 | 0 | 4.16 | 0.000751 | -0.0172 | CFL | Bldg | 3680 | 0.616 | 3680 | 0.616 | 1.13 | 1.22 | -0.00467
CFLBldgSCERSDExIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | RSD | Ex | IOU | 3.68 | 0.000616 | 0 | 4.16 | 0.000751 | -0.0174 | 3.68 | 0.000616 | 0 | 4.16 | 0.000751 | -0.0174 | CFL | Bldg | 3680 | 0.616 | 3680 | 0.616 | 1.13 | 1.22 | -0.00473
CFLBldgPGERSDNewCZ01 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RSD | New | CZ01 | 3.68 | 0.000616 | 0 | 3.51 | 0.0007 | -0.0111 | 3.68 | 0.000616 | 0 | 3.51 | 0.0007 | -0.0111 | CFL | Bldg | 3680 | 0.616 | 3680 | 0.616 | 0.954 | 1.14 | -0.00302
CFLBldgPGERSDNewCZ02 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RSD | New | CZ02 | 3.68 | 0.000616 | 0 | 3.77 | 0.00075 | -0.03 | 3.68 | 0.000616 | 0 | 3.77 | 0.00075 | -0.03 | CFL | Bldg | 3680 | 0.616 | 3680 | 0.616 | 1.02 | 1.22 | -0.00815
CFLBldgPGERSDNewCZ03 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RSD | New | CZ03 | 3.68 | 0.000616 | 0 | 3.66 | 0.000715 | -0.0375 | 3.68 | 0.000616 | 0 | 3.66 | 0.000715 | -0.0375 | CFL | Bldg | 3680 | 0.616 | 3680 | 0.616 | 0.995 | 1.16 | -0.0102
CFLBldgPGERSDNewCZ04 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RSD | New | CZ04 | 3.68 | 0.000616 | 0 | 3.84 | 0.00075 | -0.0251 | 3.68 | 0.000616 | 0 | 3.84 | 0.00075 | -0.0251 | CFL | Bldg | 3680 | 0.616 | 3680 | 0.616 | 1.04 | 1.22 | -0.00682
CFLBldgSCERSDNewCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RSD | New | CZ05 | 3.68 | 0.000616 | 0 | 3.81 | 0.000756 | -0.036 | 3.68 | 0.000616 | 0 | 3.81 | 0.000756 | -0.036 | CFL | Bldg | 3680 | 0.616 | 3680 | 0.616 | 1.04 | 1.23 | -0.00978
CFLBldgPGERSDNewCZ05 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RSD | New | CZ05 | 3.68 | 0.000616 | 0 | 3.69 | 0.000722 | -0.0322 | 3.68 | 0.000616 | 0 | 3.69 | 0.000722 | -0.0322 | CFL | Bldg | 3680 | 0.616 | 3680 | 0.616 | 1 | 1.17 | -0.00875
CFLBldgSDGRSDNewCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SDG | RSD | New | CZ06 | 3.68 | 0.000616 | 0 | 4.03 | 0.000771 | -0.0211 | 3.68 | 0.000616 | 0 | 4.03 | 0.000771 | -0.0211 | CFL | Bldg | 3680 | 0.616 | 3680 | 0.616 | 1.1 | 1.25 | -0.00573
CFLBldgSCERSDNewCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RSD | New | CZ06 | 3.68 | 0.000616 | 0 | 4.03 | 0.000769 | -0.0203 | 3.68 | 0.000616 | 0 | 4.03 | 0.000769 | -0.0203 | CFL | Bldg | 3680 | 0.616 | 3680 | 0.616 | 1.1 | 1.25 | -0.00552
CFLBldgSDGRSDNewCZ07 | Com-Iltg-dWatt-CFL_OSbldg | SDG | RSD | New | CZ07 | 3.68 | 0.000616 | 0 | 4 | 0.000774 | -0.0194 | 3.68 | 0.000616 | 0 | 4 | 0.000774 | -0.0194 | CFL | Bldg | 3680 | 0.616 | 3680 | 0.616 | 1.09 | 1.26 | -0.00527
CFLBldgSCERSDNewCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RSD | New | CZ08 | 3.68 | 0.000616 | 0 | 3.96 | 0.00067 | -0.0169 | 3.68 | 0.000616 | 0 | 3.96 | 0.00067 | -0.0169 | CFL | Bldg | 3680 | 0.616 | 3680 | 0.616 | 1.08 | 1.09 | -0.00459
CFLBldgSDGRSDNewCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SDG | RSD | New | CZ08 | 3.68 | 0.000616 | 0 | 3.95 | 0.000671 | -0.0175 | 3.68 | 0.000616 | 0 | 3.95 | 0.000671 | -0.0175 | CFL | Bldg | 3680 | 0.616 | 3680 | 0.616 | 1.07 | 1.09 | -0.00476
CFLBldgSCERSDNewCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RSD | New | CZ09 | 3.68 | 0.000616 | 0 | 4.1 | 0.000807 | -0.0188 | 3.68 | 0.000616 | 0 | 4.1 | 0.000807 | -0.0188 | CFL | Bldg | 3680 | 0.616 | 3680 | 0.616 | 1.11 | 1.31 | -0.00511
CFLBldgSCERSDNewCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RSD | New | CZ10 | 3.68 | 0.000616 | 0 | 4.11 | 0.000807 | -0.0192 | 3.68 | 0.000616 | 0 | 4.11 | 0.000807 | -0.0192 | CFL | Bldg | 3680 | 0.616 | 3680 | 0.616 | 1.12 | 1.31 | -0.00522
CFLBldgSDGRSDNewCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SDG | RSD | New | CZ10 | 3.68 | 0.000616 | 0 | 4.11 | 0.00081 | -0.0199 | 3.68 | 0.000616 | 0 | 4.11 | 0.00081 | -0.0199 | CFL | Bldg | 3680 | 0.616 | 3680 | 0.616 | 1.12 | 1.31 | -0.00541
CFLBldgPGERSDNewCZ11 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RSD | New | CZ11 | 3.68 | 0.000616 | 0 | 3.89 | 0.000766 | -0.0258 | 3.68 | 0.000616 | 0 | 3.89 | 0.000766 | -0.0258 | CFL | Bldg | 3680 | 0.616 | 3680 | 0.616 | 1.06 | 1.24 | -0.00701
CFLBldgPGERSDNewCZ12 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RSD | New | CZ12 | 3.68 | 0.000616 | 0 | 3.83 | 0.000738 | -0.026 | 3.68 | 0.000616 | 0 | 3.83 | 0.000738 | -0.026 | CFL | Bldg | 3680 | 0.616 | 3680 | 0.616 | 1.04 | 1.2 | -0.00707
CFLBldgSCERSDNewCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RSD | New | CZ13 | 3.68 | 0.000616 | 0 | 4.07 | 0.000811 | -0.0278 | 3.68 | 0.000616 | 0 | 4.07 | 0.000811 | -0.0278 | CFL | Bldg | 3680 | 0.616 | 3680 | 0.616 | 1.11 | 1.32 | -0.00755
CFLBldgPGERSDNewCZ13 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RSD | New | CZ13 | 3.68 | 0.000616 | 0 | 3.9 | 0.000764 | -0.0247 | 3.68 | 0.000616 | 0 | 3.9 | 0.000764 | -0.0247 | CFL | Bldg | 3680 | 0.616 | 3680 | 0.616 | 1.06 | 1.24 | -0.00671
CFLBldgSDGRSDNewCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SDG | RSD | New | CZ14 | 3.68 | 0.000616 | 0 | 4.05 | 0.000808 | -0.0296 | 3.68 | 0.000616 | 0 | 4.05 | 0.000808 | -0.0296 | CFL | Bldg | 3680 | 0.616 | 3680 | 0.616 | 1.1 | 1.31 | -0.00804
CFLBldgSCERSDNewCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RSD | New | CZ14 | 3.68 | 0.000616 | 0 | 4.06 | 0.000805 | -0.0286 | 3.68 | 0.000616 | 0 | 4.06 | 0.000805 | -0.0286 | CFL | Bldg | 3680 | 0.616 | 3680 | 0.616 | 1.1 | 1.31 | -0.00777
CFLBldgSCERSDNewCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RSD | New | CZ15 | 3.68 | 0.000616 | 0 | 4.41 | 0.000832 | -0.00832 | 3.68 | 0.000616 | 0 | 4.41 | 0.000832 | -0.00832 | CFL | Bldg | 3680 | 0.616 | 3680 | 0.616 | 1.2 | 1.35 | -0.00226
CFLBldgSDGRSDNewCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SDG | RSD | New | CZ15 | 3.68 | 0.000616 | 0 | 4.42 | 0.000835 | -0.00861 | 3.68 | 0.000616 | 0 | 4.42 | 0.000835 | -0.00861 | CFL | Bldg | 3680 | 0.616 | 3680 | 0.616 | 1.2 | 1.36 | -0.00234
CFLBldgPGERSDNewCZ16 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RSD | New | CZ16 | 3.68 | 0.000616 | 0 | 3.57 | 0.000726 | -0.0345 | 3.68 | 0.000616 | 0 | 3.57 | 0.000726 | -0.0345 | CFL | Bldg | 3680 | 0.616 | 3680 | 0.616 | 0.97 | 1.18 | -0.00938
CFLBldgSCERSDNewCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RSD | New | CZ16 | 3.68 | 0.000616 | 0 | 3.73 | 0.000762 | -0.039 | 3.68 | 0.000616 | 0 | 3.73 | 0.000762 | -0.039 | CFL | Bldg | 3680 | 0.616 | 3680 | 0.616 | 1.01 | 1.24 | -0.0106
CFLBldgSCGRSDNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SCG | RSD | New | IOU | 3.68 | 0.000616 | 0 | 4.06 | 0.000758 | -0.0194 | 3.68 | 0.000616 | 0 | 4.06 | 0.000758 | -0.0194 | CFL | Bldg | 3680 | 0.616 | 3680 | 0.616 | 1.1 | 1.23 | -0.00527
CFLBldgSCERSDNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | RSD | New | IOU | 3.68 | 0.000616 | 0 | 4.06 | 0.000762 | -0.0194 | 3.68 | 0.000616 | 0 | 4.06 | 0.000762 | -0.0194 | CFL | Bldg | 3680 | 0.616 | 3680 | 0.616 | 1.1 | 1.24 | -0.00527
CFLBldgPGERSDNewIOU | Com-Iltg-dWatt-CFL_OSbldg | PGE | RSD | New | IOU | 3.68 | 0.000616 | 0 | 4.02 | 0.000801 | -0.0295 | 3.68 | 0.000616 | 0 | 4.02 | 0.000801 | -0.0295 | CFL | Bldg | 3680 | 0.616 | 3680 | 0.616 | 1.09 | 1.3 | -0.00802
CFLBldgSDGRSDNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SDG | RSD | New | IOU | 3.68 | 0.000616 | 0 | 4.02 | 0.000779 | -0.0195 | 3.68 | 0.000616 | 0 | 4.02 | 0.000779 | -0.0195 | CFL | Bldg | 3680 | 0.616 | 3680 | 0.616 | 1.09 | 1.26 | -0.0053
CFLBldgPGERt3ExCZ01 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Rt3 | Ex | CZ01 | 1.89 | 0.00061 | 0 | 1.81 | 0.000756 | -0.0278 | 1.89 | 0.000607 | 0 | 1.81 | 0.000752 | -0.0278 | CFL | Bldg | 1890 | 0.61 | 1890 | 0.607 | 0.958 | 1.24 | -0.0147
CFLBldgPGERt3ExCZ02 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Rt3 | Ex | CZ02 | 1.89 | 0.00061 | 0 | 1.99 | 0.000742 | -0.0141 | 1.89 | 0.000607 | 0 | 1.99 | 0.000738 | -0.0141 | CFL | Bldg | 1890 | 0.61 | 1890 | 0.607 | 1.05 | 1.22 | -0.00746
CFLBldgPGERt3ExCZ03 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Rt3 | Ex | CZ03 | 1.89 | 0.00061 | 0 | 2 | 0.000746 | -0.0135 | 1.89 | 0.000607 | 0 | 2 | 0.000742 | -0.0135 | CFL | Bldg | 1890 | 0.61 | 1890 | 0.607 | 1.06 | 1.22 | -0.00714
CFLBldgPGERt3ExCZ04 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Rt3 | Ex | CZ04 | 1.89 | 0.00061 | 0 | 2.03 | 0.000745 | -0.00932 | 1.89 | 0.000607 | 0 | 2.03 | 0.000742 | -0.00932 | CFL | Bldg | 1890 | 0.61 | 1890 | 0.607 | 1.07 | 1.22 | -0.00493
CFLBldgPGERt3ExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Rt3 | Ex | CZ05 | 1.89 | 0.00061 | 0 | 2.03 | 0.00077 | -0.0106 | 1.89 | 0.000607 | 0 | 2.03 | 0.000767 | -0.0106 | CFL | Bldg | 1890 | 0.61 | 1890 | 0.607 | 1.07 | 1.26 | -0.00561
CFLBldgSCGRt3ExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCG | Rt3 | Ex | CZ05 | 1.89 | 0.00061 | 0 | 2.03 | 0.00077 | -0.0106 | 1.89 | 0.000607 | 0 | 2.03 | 0.000767 | -0.0106 | CFL | Bldg | 1890 | 0.61 | 1890 | 0.607 | 1.07 | 1.26 | -0.00561
CFLBldgSCERt3ExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Rt3 | Ex | CZ05 | 1.89 | 0.00061 | 0 | 2.03 | 0.00077 | -0.0106 | 1.89 | 0.000607 | 0 | 2.03 | 0.000767 | -0.0106 | CFL | Bldg | 1890 | 0.61 | 1890 | 0.607 | 1.07 | 1.26 | -0.00561
CFLBldgSCGRt3ExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCG | Rt3 | Ex | CZ06 | 1.89 | 0.00061 | 0 | 2.15 | 0.000766 | -0.00272 | 1.89 | 0.000607 | 0 | 2.15 | 0.000762 | -0.00272 | CFL | Bldg | 1890 | 0.61 | 1890 | 0.607 | 1.14 | 1.26 | -0.00144
CFLBldgSCERt3ExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Rt3 | Ex | CZ06 | 1.89 | 0.00061 | 0 | 2.15 | 0.000766 | -0.00272 | 1.89 | 0.000607 | 0 | 2.15 | 0.000762 | -0.00272 | CFL | Bldg | 1890 | 0.61 | 1890 | 0.607 | 1.14 | 1.26 | -0.00144
CFLBldgSDGRt3ExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Rt3 | Ex | CZ06 | 1.89 | 0.00061 | 0 | 2.15 | 0.000766 | -0.00272 | 1.89 | 0.000607 | 0 | 2.15 | 0.000762 | -0.00272 | CFL | Bldg | 1890 | 0.61 | 1890 | 0.607 | 1.14 | 1.26 | -0.00144
CFLBldgSDGRt3ExCZ07 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Rt3 | Ex | CZ07 | 1.89 | 0.00061 | 0 | 2.16 | 0.000752 | -0.00125 | 1.89 | 0.000607 | 0 | 2.16 | 0.000748 | -0.00125 | CFL | Bldg | 1890 | 0.61 | 1890 | 0.607 | 1.14 | 1.23 | -0.000661
CFLBldgSDGRt3ExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Rt3 | Ex | CZ08 | 1.89 | 0.00061 | 0 | 2.16 | 0.000755 | -0.00236 | 1.89 | 0.000607 | 0 | 2.16 | 0.000751 | -0.00236 | CFL | Bldg | 1890 | 0.61 | 1890 | 0.607 | 1.14 | 1.24 | -0.00125
CFLBldgSCERt3ExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Rt3 | Ex | CZ08 | 1.89 | 0.00061 | 0 | 2.16 | 0.000755 | -0.00236 | 1.89 | 0.000607 | 0 | 2.16 | 0.000751 | -0.00236 | CFL | Bldg | 1890 | 0.61 | 1890 | 0.607 | 1.14 | 1.24 | -0.00125
CFLBldgSCGRt3ExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCG | Rt3 | Ex | CZ08 | 1.89 | 0.00061 | 0 | 2.16 | 0.000755 | -0.00236 | 1.89 | 0.000607 | 0 | 2.16 | 0.000751 | -0.00236 | CFL | Bldg | 1890 | 0.61 | 1890 | 0.607 | 1.14 | 1.24 | -0.00125
CFLBldgSCERt3ExCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Rt3 | Ex | CZ09 | 1.89 | 0.00061 | 0 | 2.15 | 0.00077 | -0.00369 | 1.89 | 0.000607 | 0 | 2.15 | 0.000766 | -0.00369 | CFL | Bldg | 1890 | 0.61 | 1890 | 0.607 | 1.14 | 1.26 | -0.00195
CFLBldgSCGRt3ExCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCG | Rt3 | Ex | CZ09 | 1.89 | 0.00061 | 0 | 2.15 | 0.00077 | -0.00369 | 1.89 | 0.000607 | 0 | 2.15 | 0.000766 | -0.00369 | CFL | Bldg | 1890 | 0.61 | 1890 | 0.607 | 1.14 | 1.26 | -0.00195
CFLBldgSCERt3ExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Rt3 | Ex | CZ10 | 1.89 | 0.00061 | 0 | 2.13 | 0.000764 | -0.00416 | 1.89 | 0.000607 | 0 | 2.13 | 0.000761 | -0.00416 | CFL | Bldg | 1890 | 0.61 | 1890 | 0.607 | 1.13 | 1.25 | -0.0022
CFLBldgSCGRt3ExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCG | Rt3 | Ex | CZ10 | 1.89 | 0.00061 | 0 | 2.13 | 0.000764 | -0.00416 | 1.89 | 0.000607 | 0 | 2.13 | 0.000761 | -0.00416 | CFL | Bldg | 1890 | 0.61 | 1890 | 0.607 | 1.13 | 1.25 | -0.0022
CFLBldgSDGRt3ExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Rt3 | Ex | CZ10 | 1.89 | 0.00061 | 0 | 2.13 | 0.000764 | -0.00416 | 1.89 | 0.000607 | 0 | 2.13 | 0.000761 | -0.00416 | CFL | Bldg | 1890 | 0.61 | 1890 | 0.607 | 1.13 | 1.25 | -0.0022
CFLBldgPGERt3ExCZ11 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Rt3 | Ex | CZ11 | 1.89 | 0.00061 | 0 | 2 | 0.000748 | -0.0134 | 1.89 | 0.000607 | 0 | 2 | 0.000744 | -0.0134 | CFL | Bldg | 1890 | 0.61 | 1890 | 0.607 | 1.06 | 1.23 | -0.00709
CFLBldgPGERt3ExCZ12 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Rt3 | Ex | CZ12 | 1.89 | 0.00061 | 0 | 2 | 0.000752 | -0.013 | 1.89 | 0.000607 | 0 | 2 | 0.000748 | -0.013 | CFL | Bldg | 1890 | 0.61 | 1890 | 0.607 | 1.06 | 1.23 | -0.00688
CFLBldgSCGRt3ExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCG | Rt3 | Ex | CZ13 | 1.89 | 0.00061 | 0 | 2.05 | 0.000777 | -0.0118 | 1.89 | 0.000607 | 0 | 2.05 | 0.000773 | -0.0118 | CFL | Bldg | 1890 | 0.61 | 1890 | 0.607 | 1.08 | 1.27 | -0.00624
CFLBldgSCERt3ExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Rt3 | Ex | CZ13 | 1.89 | 0.00061 | 0 | 2.05 | 0.000777 | -0.0118 | 1.89 | 0.000607 | 0 | 2.05 | 0.000773 | -0.0118 | CFL | Bldg | 1890 | 0.61 | 1890 | 0.607 | 1.08 | 1.27 | -0.00624
CFLBldgPGERt3ExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Rt3 | Ex | CZ13 | 1.89 | 0.00061 | 0 | 2.05 | 0.000777 | -0.0118 | 1.89 | 0.000607 | 0 | 2.05 | 0.000773 | -0.0118 | CFL | Bldg | 1890 | 0.61 | 1890 | 0.607 | 1.08 | 1.27 | -0.00624
CFLBldgSDGRt3ExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Rt3 | Ex | CZ14 | 1.89 | 0.00061 | 0 | 2.03 | 0.00077 | -0.0128 | 1.89 | 0.000607 | 0 | 2.03 | 0.000767 | -0.0128 | CFL | Bldg | 1890 | 0.61 | 1890 | 0.607 | 1.07 | 1.26 | -0.00677
CFLBldgSCGRt3ExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCG | Rt3 | Ex | CZ14 | 1.89 | 0.00061 | 0 | 2.03 | 0.00077 | -0.0128 | 1.89 | 0.000607 | 0 | 2.03 | 0.000767 | -0.0128 | CFL | Bldg | 1890 | 0.61 | 1890 | 0.607 | 1.07 | 1.26 | -0.00677
CFLBldgSCERt3ExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Rt3 | Ex | CZ14 | 1.89 | 0.00061 | 0 | 2.03 | 0.00077 | -0.0128 | 1.89 | 0.000607 | 0 | 2.03 | 0.000767 | -0.0128 | CFL | Bldg | 1890 | 0.61 | 1890 | 0.607 | 1.07 | 1.26 | -0.00677
CFLBldgSCGRt3ExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCG | Rt3 | Ex | CZ15 | 1.89 | 0.00061 | 0 | 2.2 | 0.000785 | -0.00106 | 1.89 | 0.000607 | 0 | 2.2 | 0.000781 | -0.00106 | CFL | Bldg | 1890 | 0.61 | 1890 | 0.607 | 1.16 | 1.29 | -0.000561
CFLBldgSCERt3ExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Rt3 | Ex | CZ15 | 1.89 | 0.00061 | 0 | 2.2 | 0.000785 | -0.00106 | 1.89 | 0.000607 | 0 | 2.2 | 0.000781 | -0.00106 | CFL | Bldg | 1890 | 0.61 | 1890 | 0.607 | 1.16 | 1.29 | -0.000561
CFLBldgSDGRt3ExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Rt3 | Ex | CZ15 | 1.89 | 0.00061 | 0 | 2.2 | 0.000785 | -0.00106 | 1.89 | 0.000607 | 0 | 2.2 | 0.000781 | -0.00106 | CFL | Bldg | 1890 | 0.61 | 1890 | 0.607 | 1.16 | 1.29 | -0.000561
CFLBldgSCERt3ExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Rt3 | Ex | CZ16 | 1.89 | 0.00061 | 0 | 1.85 | 0.000755 | -0.0244 | 1.89 | 0.000607 | 0 | 1.85 | 0.000751 | -0.0244 | CFL | Bldg | 1890 | 0.61 | 1890 | 0.607 | 0.979 | 1.24 | -0.0129
CFLBldgSCGRt3ExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCG | Rt3 | Ex | CZ16 | 1.89 | 0.00061 | 0 | 1.85 | 0.000755 | -0.0244 | 1.89 | 0.000607 | 0 | 1.85 | 0.000751 | -0.0244 | CFL | Bldg | 1890 | 0.61 | 1890 | 0.607 | 0.979 | 1.24 | -0.0129
CFLBldgPGERt3ExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Rt3 | Ex | CZ16 | 1.89 | 0.00061 | 0 | 1.85 | 0.000755 | -0.0244 | 1.89 | 0.000607 | 0 | 1.85 | 0.000751 | -0.0244 | CFL | Bldg | 1890 | 0.61 | 1890 | 0.607 | 0.979 | 1.24 | -0.0129
CFLBldgSCERt3ExIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | Rt3 | Ex | IOU | 1.89 | 0.00061 | 0 | 2.14 | 0.000764 | -0.0039 | 1.89 | 0.000607 | 0 | 2.14 | 0.00076 | -0.0039 | CFL | Bldg | 1890 | 0.61 | 1890 | 0.607 | 1.13 | 1.25 | -0.00206
CFLBldgSDGRt3ExIOU | Com-Iltg-dWatt-CFL_OSbldg | SDG | Rt3 | Ex | IOU | 1.89 | 0.00061 | 0 | 2.15 | 0.000755 | -0.00209 | 1.89 | 0.000607 | 0 | 2.15 | 0.000752 | -0.00209 | CFL | Bldg | 1890 | 0.61 | 1890 | 0.607 | 1.14 | 1.24 | -0.00111
CFLBldgPGERt3ExIOU | Com-Iltg-dWatt-CFL_OSbldg | PGE | Rt3 | Ex | IOU | 1.89 | 0.00061 | 0 | 2.01 | 0.000752 | -0.0127 | 1.89 | 0.000607 | 0 | 2.01 | 0.000748 | -0.0127 | CFL | Bldg | 1890 | 0.61 | 1890 | 0.607 | 1.06 | 1.23 | -0.00672
CFLBldgSCGRt3ExIOU | Com-Iltg-dWatt-CFL_OSbldg | SCG | Rt3 | Ex | IOU | 1.89 | 0.00061 | 0 | 2.14 | 0.000764 | -0.00379 | 1.89 | 0.000607 | 0 | 2.14 | 0.000761 | -0.00379 | CFL | Bldg | 1890 | 0.61 | 1890 | 0.607 | 1.13 | 1.25 | -0.00201
CFLBldgPGERt3NewCZ01 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Rt3 | New | CZ01 | 1.89 | 0.000607 | 0 | 1.78 | 0.00074 | -0.0306 | 1.89 | 0.000607 | 0 | 1.78 | 0.00074 | -0.0306 | CFL | Bldg | 1890 | 0.607 | 1890 | 0.607 | 0.942 | 1.22 | -0.0162
CFLBldgPGERt3NewCZ02 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Rt3 | New | CZ02 | 1.89 | 0.000607 | 0 | 1.93 | 0.000721 | -0.0165 | 1.89 | 0.000607 | 0 | 1.93 | 0.000721 | -0.0165 | CFL | Bldg | 1890 | 0.607 | 1890 | 0.607 | 1.02 | 1.19 | -0.00873
CFLBldgPGERt3NewCZ03 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Rt3 | New | CZ03 | 1.89 | 0.000607 | 0 | 1.92 | 0.000727 | -0.0168 | 1.89 | 0.000607 | 0 | 1.92 | 0.000727 | -0.0168 | CFL | Bldg | 1890 | 0.607 | 1890 | 0.607 | 1.02 | 1.2 | -0.00889
CFLBldgPGERt3NewCZ04 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Rt3 | New | CZ04 | 1.89 | 0.000607 | 0 | 1.97 | 0.000731 | -0.012 | 1.89 | 0.000607 | 0 | 1.97 | 0.000731 | -0.012 | CFL | Bldg | 1890 | 0.607 | 1890 | 0.607 | 1.04 | 1.2 | -0.00635
CFLBldgPGERt3NewCZ05 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Rt3 | New | CZ05 | 1.89 | 0.000607 | 0 | 1.93 | 0.000723 | -0.0139 | 1.89 | 0.000607 | 0 | 1.93 | 0.000723 | -0.0139 | CFL | Bldg | 1890 | 0.607 | 1890 | 0.607 | 1.02 | 1.19 | -0.00735
CFLBldgSCERt3NewCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Rt3 | New | CZ05 | 1.89 | 0.000607 | 0 | 1.96 | 0.00075 | -0.0131 | 1.89 | 0.000607 | 0 | 1.96 | 0.00075 | -0.0131 | CFL | Bldg | 1890 | 0.607 | 1890 | 0.607 | 1.04 | 1.24 | -0.00693
CFLBldgSCERt3NewCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Rt3 | New | CZ06 | 1.89 | 0.000607 | 0 | 2.1 | 0.000743 | -0.00395 | 1.89 | 0.000607 | 0 | 2.1 | 0.000743 | -0.00395 | CFL | Bldg | 1890 | 0.607 | 1890 | 0.607 | 1.11 | 1.22 | -0.00209
CFLBldgSDGRt3NewCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Rt3 | New | CZ06 | 1.89 | 0.000607 | 0 | 2.09 | 0.000742 | -0.00404 | 1.89 | 0.000607 | 0 | 2.09 | 0.000742 | -0.00404 | CFL | Bldg | 1890 | 0.607 | 1890 | 0.607 | 1.11 | 1.22 | -0.00214
CFLBldgSDGRt3NewCZ07 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Rt3 | New | CZ07 | 1.89 | 0.000607 | 0 | 2.11 | 0.000718 | -0.00193 | 1.89 | 0.000607 | 0 | 2.11 | 0.000718 | -0.00193 | CFL | Bldg | 1890 | 0.607 | 1890 | 0.607 | 1.12 | 1.18 | -0.00102
CFLBldgSCERt3NewCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Rt3 | New | CZ08 | 1.89 | 0.000607 | 0 | 2.11 | 0.000733 | -0.00323 | 1.89 | 0.000607 | 0 | 2.11 | 0.000733 | -0.00323 | CFL | Bldg | 1890 | 0.607 | 1890 | 0.607 | 1.12 | 1.21 | -0.00171
CFLBldgSDGRt3NewCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Rt3 | New | CZ08 | 1.89 | 0.000607 | 0 | 2.11 | 0.000731 | -0.00329 | 1.89 | 0.000607 | 0 | 2.11 | 0.000731 | -0.00329 | CFL | Bldg | 1890 | 0.607 | 1890 | 0.607 | 1.12 | 1.2 | -0.00174
CFLBldgSCERt3NewCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Rt3 | New | CZ09 | 1.89 | 0.000607 | 0 | 2.09 | 0.00075 | -0.00486 | 1.89 | 0.000607 | 0 | 2.09 | 0.00075 | -0.00486 | CFL | Bldg | 1890 | 0.607 | 1890 | 0.607 | 1.11 | 1.24 | -0.00257
CFLBldgSCERt3NewCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Rt3 | New | CZ10 | 1.89 | 0.000607 | 0 | 2.09 | 0.000758 | -0.00559 | 1.89 | 0.000607 | 0 | 2.09 | 0.000758 | -0.00559 | CFL | Bldg | 1890 | 0.607 | 1890 | 0.607 | 1.11 | 1.25 | -0.00296
CFLBldgSDGRt3NewCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Rt3 | New | CZ10 | 1.89 | 0.000607 | 0 | 2.09 | 0.000756 | -0.00571 | 1.89 | 0.000607 | 0 | 2.09 | 0.000756 | -0.00571 | CFL | Bldg | 1890 | 0.607 | 1890 | 0.607 | 1.11 | 1.25 | -0.00302
CFLBldgPGERt3NewCZ11 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Rt3 | New | CZ11 | 1.89 | 0.000607 | 0 | 1.98 | 0.000748 | -0.0142 | 1.89 | 0.000607 | 0 | 1.98 | 0.000748 | -0.0142 | CFL | Bldg | 1890 | 0.607 | 1890 | 0.607 | 1.05 | 1.23 | -0.00751
CFLBldgPGERt3NewCZ12 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Rt3 | New | CZ12 | 1.89 | 0.000607 | 0 | 1.97 | 0.000745 | -0.0152 | 1.89 | 0.000607 | 0 | 1.97 | 0.000745 | -0.0152 | CFL | Bldg | 1890 | 0.607 | 1890 | 0.607 | 1.04 | 1.23 | -0.00804
CFLBldgSCERt3NewCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Rt3 | New | CZ13 | 1.89 | 0.000607 | 0 | 2.03 | 0.000771 | -0.0129 | 1.89 | 0.000607 | 0 | 2.03 | 0.000771 | -0.0129 | CFL | Bldg | 1890 | 0.607 | 1890 | 0.607 | 1.07 | 1.27 | -0.00683
CFLBldgPGERt3NewCZ13 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Rt3 | New | CZ13 | 1.89 | 0.000607 | 0 | 1.99 | 0.00074 | -0.0137 | 1.89 | 0.000607 | 0 | 1.99 | 0.00074 | -0.0137 | CFL | Bldg | 1890 | 0.607 | 1890 | 0.607 | 1.05 | 1.22 | -0.00725
CFLBldgSDGRt3NewCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Rt3 | New | CZ14 | 1.89 | 0.000607 | 0 | 2.02 | 0.00076 | -0.0138 | 1.89 | 0.000607 | 0 | 2.02 | 0.00076 | -0.0138 | CFL | Bldg | 1890 | 0.607 | 1890 | 0.607 | 1.07 | 1.25 | -0.0073
CFLBldgSCERt3NewCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Rt3 | New | CZ14 | 1.89 | 0.000607 | 0 | 2.02 | 0.000762 | -0.0134 | 1.89 | 0.000607 | 0 | 2.02 | 0.000762 | -0.0134 | CFL | Bldg | 1890 | 0.607 | 1890 | 0.607 | 1.07 | 1.26 | -0.00709
CFLBldgSDGRt3NewCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SDG | Rt3 | New | CZ15 | 1.89 | 0.000607 | 0 | 2.2 | 0.000809 | -0.000858 | 1.89 | 0.000607 | 0 | 2.2 | 0.000809 | -0.000858 | CFL | Bldg | 1890 | 0.607 | 1890 | 0.607 | 1.16 | 1.33 | -0.000454
CFLBldgSCERt3NewCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Rt3 | New | CZ15 | 1.89 | 0.000607 | 0 | 2.21 | 0.000811 | -0.000856 | 1.89 | 0.000607 | 0 | 2.21 | 0.000811 | -0.000856 | CFL | Bldg | 1890 | 0.607 | 1890 | 0.607 | 1.17 | 1.34 | -0.000453
CFLBldgPGERt3NewCZ16 | Com-Iltg-dWatt-CFL_OSbldg | PGE | Rt3 | New | CZ16 | 1.89 | 0.000607 | 0 | 1.8 | 0.000668 | -0.0248 | 1.89 | 0.000607 | 0 | 1.8 | 0.000668 | -0.0248 | CFL | Bldg | 1890 | 0.607 | 1890 | 0.607 | 0.952 | 1.1 | -0.0131
CFLBldgSCERt3NewCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | Rt3 | New | CZ16 | 1.89 | 0.000607 | 0 | 1.83 | 0.000685 | -0.0232 | 1.89 | 0.000607 | 0 | 1.83 | 0.000685 | -0.0232 | CFL | Bldg | 1890 | 0.607 | 1890 | 0.607 | 0.968 | 1.13 | -0.0123
CFLBldgPGERt3NewIOU | Com-Iltg-dWatt-CFL_OSbldg | PGE | Rt3 | New | IOU | 1.89 | 0.000607 | 0 | 2.02 | 0.000767 | -0.0131 | 1.89 | 0.000607 | 0 | 2.02 | 0.000767 | -0.0131 | CFL | Bldg | 1890 | 0.607 | 1890 | 0.607 | 1.07 | 1.26 | -0.00693
CFLBldgSCERt3NewIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | Rt3 | New | IOU | 1.89 | 0.000607 | 0 | 2.1 | 0.000749 | -0.00492 | 1.89 | 0.000607 | 0 | 2.1 | 0.000749 | -0.00492 | CFL | Bldg | 1890 | 0.607 | 1890 | 0.607 | 1.11 | 1.23 | -0.0026
CFLBldgSDGRt3NewIOU | Com-Iltg-dWatt-CFL_OSbldg | SDG | Rt3 | New | IOU | 1.89 | 0.000607 | 0 | 2.1 | 0.000729 | -0.00302 | 1.89 | 0.000607 | 0 | 2.1 | 0.000729 | -0.00302 | CFL | Bldg | 1890 | 0.607 | 1890 | 0.607 | 1.11 | 1.2 | -0.0016
CFLBldgSCGRt3NewIOU | Com-Iltg-dWatt-CFL_OSbldg | SCG | Rt3 | New | IOU | 1.89 | 0.000607 | 0 | 2.1 | 0.000748 | -0.00483 | 1.89 | 0.000607 | 0 | 2.1 | 0.000748 | -0.00483 | CFL | Bldg | 1890 | 0.607 | 1890 | 0.607 | 1.11 | 1.23 | -0.00256
CFLBldgPGERtLExCZ01 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RtL | Ex | CZ01 | 2.94 | 0.000804 | 0 | 2.85 | 0.000979 | -0.0397 | 2.94 | 0.000801 | 0 | 2.85 | 0.000976 | -0.0397 | CFL | Bldg | 2940 | 0.804 | 2940 | 0.801 | 0.969 | 1.22 | -0.0135
CFLBldgPGERtLExCZ02 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RtL | Ex | CZ02 | 2.94 | 0.000804 | 0 | 3.09 | 0.000977 | -0.0206 | 2.94 | 0.000801 | 0 | 3.09 | 0.000973 | -0.0206 | CFL | Bldg | 2940 | 0.804 | 2940 | 0.801 | 1.05 | 1.21 | -0.00701
CFLBldgPGERtLExCZ03 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RtL | Ex | CZ03 | 2.94 | 0.000804 | 0 | 3.11 | 0.000972 | -0.0194 | 2.94 | 0.000801 | 0 | 3.11 | 0.000968 | -0.0194 | CFL | Bldg | 2940 | 0.804 | 2940 | 0.801 | 1.06 | 1.21 | -0.0066
CFLBldgPGERtLExCZ04 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RtL | Ex | CZ04 | 2.94 | 0.000804 | 0 | 3.15 | 0.000978 | -0.0145 | 2.94 | 0.000801 | 0 | 3.15 | 0.000974 | -0.0145 | CFL | Bldg | 2940 | 0.804 | 2940 | 0.801 | 1.07 | 1.22 | -0.00493
CFLBldgSCERtLExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RtL | Ex | CZ05 | 2.94 | 0.000804 | 0 | 3.15 | 0.001 | -0.0176 | 2.94 | 0.000801 | 0 | 3.15 | 0.000998 | -0.0176 | CFL | Bldg | 2940 | 0.804 | 2940 | 0.801 | 1.07 | 1.25 | -0.00599
CFLBldgSCGRtLExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCG | RtL | Ex | CZ05 | 2.94 | 0.000804 | 0 | 3.15 | 0.001 | -0.0176 | 2.94 | 0.000801 | 0 | 3.15 | 0.000998 | -0.0176 | CFL | Bldg | 2940 | 0.804 | 2940 | 0.801 | 1.07 | 1.25 | -0.00599
CFLBldgPGERtLExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RtL | Ex | CZ05 | 2.94 | 0.000804 | 0 | 3.15 | 0.001 | -0.0176 | 2.94 | 0.000801 | 0 | 3.15 | 0.000998 | -0.0176 | CFL | Bldg | 2940 | 0.804 | 2940 | 0.801 | 1.07 | 1.25 | -0.00599
CFLBldgSCGRtLExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCG | RtL | Ex | CZ06 | 2.94 | 0.000804 | 0 | 3.31 | 0.00101 | -0.00726 | 2.94 | 0.000801 | 0 | 3.31 | 0.00101 | -0.00726 | CFL | Bldg | 2940 | 0.804 | 2940 | 0.801 | 1.13 | 1.26 | -0.00247
CFLBldgSCERtLExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RtL | Ex | CZ06 | 2.94 | 0.000804 | 0 | 3.31 | 0.00101 | -0.00726 | 2.94 | 0.000801 | 0 | 3.31 | 0.00101 | -0.00726 | CFL | Bldg | 2940 | 0.804 | 2940 | 0.801 | 1.13 | 1.26 | -0.00247
CFLBldgSDGRtLExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SDG | RtL | Ex | CZ06 | 2.94 | 0.000804 | 0 | 3.31 | 0.00101 | -0.00726 | 2.94 | 0.000801 | 0 | 3.31 | 0.00101 | -0.00726 | CFL | Bldg | 2940 | 0.804 | 2940 | 0.801 | 1.13 | 1.26 | -0.00247
CFLBldgSDGRtLExCZ07 | Com-Iltg-dWatt-CFL_OSbldg | SDG | RtL | Ex | CZ07 | 2.94 | 0.000804 | 0 | 3.33 | 0.00101 | -0.0052 | 2.94 | 0.000801 | 0 | 3.33 | 0.00101 | -0.0052 | CFL | Bldg | 2940 | 0.804 | 2940 | 0.801 | 1.13 | 1.26 | -0.00177
CFLBldgSDGRtLExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SDG | RtL | Ex | CZ08 | 2.94 | 0.000804 | 0 | 3.32 | 0.00102 | -0.00623 | 2.94 | 0.000801 | 0 | 3.32 | 0.00101 | -0.00623 | CFL | Bldg | 2940 | 0.804 | 2940 | 0.801 | 1.13 | 1.26 | -0.00212
CFLBldgSCERtLExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RtL | Ex | CZ08 | 2.94 | 0.000804 | 0 | 3.32 | 0.00102 | -0.00623 | 2.94 | 0.000801 | 0 | 3.32 | 0.00101 | -0.00623 | CFL | Bldg | 2940 | 0.804 | 2940 | 0.801 | 1.13 | 1.26 | -0.00212
CFLBldgSCGRtLExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCG | RtL | Ex | CZ08 | 2.94 | 0.000804 | 0 | 3.32 | 0.00102 | -0.00623 | 2.94 | 0.000801 | 0 | 3.32 | 0.00101 | -0.00623 | CFL | Bldg | 2940 | 0.804 | 2940 | 0.801 | 1.13 | 1.26 | -0.00212
CFLBldgSCERtLExCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RtL | Ex | CZ09 | 2.94 | 0.000804 | 0 | 3.32 | 0.00104 | -0.00735 | 2.94 | 0.000801 | 0 | 3.32 | 0.00104 | -0.00735 | CFL | Bldg | 2940 | 0.804 | 2940 | 0.801 | 1.13 | 1.3 | -0.0025
CFLBldgSCGRtLExCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCG | RtL | Ex | CZ09 | 2.94 | 0.000804 | 0 | 3.32 | 0.00104 | -0.00735 | 2.94 | 0.000801 | 0 | 3.32 | 0.00104 | -0.00735 | CFL | Bldg | 2940 | 0.804 | 2940 | 0.801 | 1.13 | 1.3 | -0.0025
CFLBldgSCERtLExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RtL | Ex | CZ10 | 2.94 | 0.000804 | 0 | 3.3 | 0.00103 | -0.00832 | 2.94 | 0.000801 | 0 | 3.3 | 0.00103 | -0.00832 | CFL | Bldg | 2940 | 0.804 | 2940 | 0.801 | 1.12 | 1.29 | -0.00283
CFLBldgSCGRtLExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCG | RtL | Ex | CZ10 | 2.94 | 0.000804 | 0 | 3.3 | 0.00103 | -0.00832 | 2.94 | 0.000801 | 0 | 3.3 | 0.00103 | -0.00832 | CFL | Bldg | 2940 | 0.804 | 2940 | 0.801 | 1.12 | 1.29 | -0.00283
CFLBldgSDGRtLExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SDG | RtL | Ex | CZ10 | 2.94 | 0.000804 | 0 | 3.3 | 0.00103 | -0.00832 | 2.94 | 0.000801 | 0 | 3.3 | 0.00103 | -0.00832 | CFL | Bldg | 2940 | 0.804 | 2940 | 0.801 | 1.12 | 1.29 | -0.00283
CFLBldgPGERtLExCZ11 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RtL | Ex | CZ11 | 2.94 | 0.000804 | 0 | 3.11 | 0.000987 | -0.0196 | 2.94 | 0.000801 | 0 | 3.11 | 0.000983 | -0.0196 | CFL | Bldg | 2940 | 0.804 | 2940 | 0.801 | 1.06 | 1.23 | -0.00667
CFLBldgPGERtLExCZ12 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RtL | Ex | CZ12 | 2.94 | 0.000804 | 0 | 3.11 | 0.000995 | -0.018 | 2.94 | 0.000801 | 0 | 3.11 | 0.000992 | -0.018 | CFL | Bldg | 2940 | 0.804 | 2940 | 0.801 | 1.06 | 1.24 | -0.00612
CFLBldgSCERtLExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RtL | Ex | CZ13 | 2.94 | 0.000804 | 0 | 3.21 | 0.00104 | -0.0161 | 2.94 | 0.000801 | 0 | 3.21 | 0.00103 | -0.0161 | CFL | Bldg | 2940 | 0.804 | 2940 | 0.801 | 1.09 | 1.29 | -0.00548
CFLBldgSCGRtLExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCG | RtL | Ex | CZ13 | 2.94 | 0.000804 | 0 | 3.21 | 0.00104 | -0.0161 | 2.94 | 0.000801 | 0 | 3.21 | 0.00103 | -0.0161 | CFL | Bldg | 2940 | 0.804 | 2940 | 0.801 | 1.09 | 1.29 | -0.00548
CFLBldgPGERtLExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RtL | Ex | CZ13 | 2.94 | 0.000804 | 0 | 3.21 | 0.00104 | -0.0161 | 2.94 | 0.000801 | 0 | 3.21 | 0.00103 | -0.0161 | CFL | Bldg | 2940 | 0.804 | 2940 | 0.801 | 1.09 | 1.29 | -0.00548
CFLBldgSDGRtLExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SDG | RtL | Ex | CZ14 | 2.94 | 0.000804 | 0 | 3.19 | 0.00105 | -0.017 | 2.94 | 0.000801 | 0 | 3.19 | 0.00104 | -0.017 | CFL | Bldg | 2940 | 0.804 | 2940 | 0.801 | 1.09 | 1.3 | -0.00578
CFLBldgSCGRtLExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCG | RtL | Ex | CZ14 | 2.94 | 0.000804 | 0 | 3.19 | 0.00105 | -0.017 | 2.94 | 0.000801 | 0 | 3.19 | 0.00104 | -0.017 | CFL | Bldg | 2940 | 0.804 | 2940 | 0.801 | 1.09 | 1.3 | -0.00578
CFLBldgSCERtLExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RtL | Ex | CZ14 | 2.94 | 0.000804 | 0 | 3.19 | 0.00105 | -0.017 | 2.94 | 0.000801 | 0 | 3.19 | 0.00104 | -0.017 | CFL | Bldg | 2940 | 0.804 | 2940 | 0.801 | 1.09 | 1.3 | -0.00578
CFLBldgSDGRtLExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SDG | RtL | Ex | CZ15 | 2.94 | 0.000804 | 0 | 3.44 | 0.00105 | -0.00297 | 2.94 | 0.000801 | 0 | 3.44 | 0.00105 | -0.00297 | CFL | Bldg | 2940 | 0.804 | 2940 | 0.801 | 1.17 | 1.31 | -0.00101
CFLBldgSCERtLExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RtL | Ex | CZ15 | 2.94 | 0.000804 | 0 | 3.44 | 0.00105 | -0.00297 | 2.94 | 0.000801 | 0 | 3.44 | 0.00105 | -0.00297 | CFL | Bldg | 2940 | 0.804 | 2940 | 0.801 | 1.17 | 1.31 | -0.00101
CFLBldgSCGRtLExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCG | RtL | Ex | CZ15 | 2.94 | 0.000804 | 0 | 3.44 | 0.00105 | -0.00297 | 2.94 | 0.000801 | 0 | 3.44 | 0.00105 | -0.00297 | CFL | Bldg | 2940 | 0.804 | 2940 | 0.801 | 1.17 | 1.31 | -0.00101
CFLBldgSCERtLExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RtL | Ex | CZ16 | 2.94 | 0.000804 | 0 | 2.88 | 0.000988 | -0.0368 | 2.94 | 0.000801 | 0 | 2.88 | 0.000984 | -0.0368 | CFL | Bldg | 2940 | 0.804 | 2940 | 0.801 | 0.98 | 1.23 | -0.0125
CFLBldgPGERtLExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RtL | Ex | CZ16 | 2.94 | 0.000804 | 0 | 2.88 | 0.000988 | -0.0368 | 2.94 | 0.000801 | 0 | 2.88 | 0.000984 | -0.0368 | CFL | Bldg | 2940 | 0.804 | 2940 | 0.801 | 0.98 | 1.23 | -0.0125
CFLBldgSCGRtLExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCG | RtL | Ex | CZ16 | 2.94 | 0.000804 | 0 | 2.88 | 0.000988 | -0.0368 | 2.94 | 0.000801 | 0 | 2.88 | 0.000984 | -0.0368 | CFL | Bldg | 2940 | 0.804 | 2940 | 0.801 | 0.98 | 1.23 | -0.0125
CFLBldgSCERtLExIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | RtL | Ex | IOU | 2.94 | 0.000804 | 0 | 3.3 | 0.00102 | -0.00802 | 2.94 | 0.000801 | 0 | 3.3 | 0.00102 | -0.00802 | CFL | Bldg | 2940 | 0.804 | 2940 | 0.801 | 1.12 | 1.27 | -0.00273
CFLBldgSDGRtLExIOU | Com-Iltg-dWatt-CFL_OSbldg | SDG | RtL | Ex | IOU | 2.94 | 0.000804 | 0 | 3.32 | 0.00102 | -0.00611 | 2.94 | 0.000801 | 0 | 3.32 | 0.00101 | -0.00611 | CFL | Bldg | 2940 | 0.804 | 2940 | 0.801 | 1.13 | 1.26 | -0.00208
CFLBldgSCGRtLExIOU | Com-Iltg-dWatt-CFL_OSbldg | SCG | RtL | Ex | IOU | 2.94 | 0.000804 | 0 | 3.31 | 0.00103 | -0.00784 | 2.94 | 0.000801 | 0 | 3.31 | 0.00102 | -0.00784 | CFL | Bldg | 2940 | 0.804 | 2940 | 0.801 | 1.13 | 1.27 | -0.00267
CFLBldgPGERtLExIOU | Com-Iltg-dWatt-CFL_OSbldg | PGE | RtL | Ex | IOU | 2.94 | 0.000804 | 0 | 3.13 | 0.00099 | -0.0182 | 2.94 | 0.000801 | 0 | 3.13 | 0.000985 | -0.0182 | CFL | Bldg | 2940 | 0.804 | 2940 | 0.801 | 1.06 | 1.23 | -0.00619
CFLBldgPGERtLNewCZ01 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RtL | New | CZ01 | 2.93 | 0.000801 | 0 | 2.82 | 0.000956 | -0.044 | 2.93 | 0.000801 | 0 | 2.82 | 0.000956 | -0.044 | CFL | Bldg | 2930 | 0.801 | 2930 | 0.801 | 0.962 | 1.19 | -0.015
CFLBldgPGERtLNewCZ02 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RtL | New | CZ02 | 2.93 | 0.000801 | 0 | 3.04 | 0.00102 | -0.0234 | 2.93 | 0.000801 | 0 | 3.04 | 0.00102 | -0.0234 | CFL | Bldg | 2930 | 0.801 | 2930 | 0.801 | 1.04 | 1.27 | -0.00799
CFLBldgPGERtLNewCZ03 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RtL | New | CZ03 | 2.93 | 0.000801 | 0 | 3.01 | 0.00099 | -0.0219 | 2.93 | 0.000801 | 0 | 3.01 | 0.00099 | -0.0219 | CFL | Bldg | 2930 | 0.801 | 2930 | 0.801 | 1.03 | 1.24 | -0.00747
CFLBldgPGERtLNewCZ04 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RtL | New | CZ04 | 2.93 | 0.000801 | 0 | 3.11 | 0.00101 | -0.0166 | 2.93 | 0.000801 | 0 | 3.11 | 0.00101 | -0.0166 | CFL | Bldg | 2930 | 0.801 | 2930 | 0.801 | 1.06 | 1.26 | -0.00567
CFLBldgSCERtLNewCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RtL | New | CZ05 | 2.93 | 0.000801 | 0 | 3.05 | 0.001 | -0.0209 | 2.93 | 0.000801 | 0 | 3.05 | 0.001 | -0.0209 | CFL | Bldg | 2930 | 0.801 | 2930 | 0.801 | 1.04 | 1.25 | -0.00713
CFLBldgPGERtLNewCZ05 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RtL | New | CZ05 | 2.93 | 0.000801 | 0 | 3.01 | 0.000967 | -0.0227 | 2.93 | 0.000801 | 0 | 3.01 | 0.000967 | -0.0227 | CFL | Bldg | 2930 | 0.801 | 2930 | 0.801 | 1.03 | 1.21 | -0.00775
CFLBldgSDGRtLNewCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SDG | RtL | New | CZ06 | 2.93 | 0.000801 | 0 | 3.21 | 0.00102 | -0.01 | 2.93 | 0.000801 | 0 | 3.21 | 0.00102 | -0.01 | CFL | Bldg | 2930 | 0.801 | 2930 | 0.801 | 1.1 | 1.27 | -0.00341
CFLBldgSCERtLNewCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RtL | New | CZ06 | 2.93 | 0.000801 | 0 | 3.21 | 0.00102 | -0.00973 | 2.93 | 0.000801 | 0 | 3.21 | 0.00102 | -0.00973 | CFL | Bldg | 2930 | 0.801 | 2930 | 0.801 | 1.1 | 1.27 | -0.00332
CFLBldgSDGRtLNewCZ07 | Com-Iltg-dWatt-CFL_OSbldg | SDG | RtL | New | CZ07 | 2.93 | 0.000801 | 0 | 3.2 | 0.000981 | -0.00718 | 2.93 | 0.000801 | 0 | 3.2 | 0.000981 | -0.00718 | CFL | Bldg | 2930 | 0.801 | 2930 | 0.801 | 1.09 | 1.22 | -0.00245
CFLBldgSDGRtLNewCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SDG | RtL | New | CZ08 | 2.93 | 0.000801 | 0 | 3.25 | 0.00103 | -0.00847 | 2.93 | 0.000801 | 0 | 3.25 | 0.00103 | -0.00847 | CFL | Bldg | 2930 | 0.801 | 2930 | 0.801 | 1.11 | 1.29 | -0.00289
CFLBldgSCERtLNewCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RtL | New | CZ08 | 2.93 | 0.000801 | 0 | 3.25 | 0.00103 | -0.00823 | 2.93 | 0.000801 | 0 | 3.25 | 0.00103 | -0.00823 | CFL | Bldg | 2930 | 0.801 | 2930 | 0.801 | 1.11 | 1.29 | -0.00281
CFLBldgSCERtLNewCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RtL | New | CZ09 | 2.93 | 0.000801 | 0 | 3.26 | 0.00108 | -0.00815 | 2.93 | 0.000801 | 0 | 3.26 | 0.00108 | -0.00815 | CFL | Bldg | 2930 | 0.801 | 2930 | 0.801 | 1.11 | 1.35 | -0.00278
CFLBldgSDGRtLNewCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SDG | RtL | New | CZ10 | 2.93 | 0.000801 | 0 | 3.27 | 0.00109 | -0.00976 | 2.93 | 0.000801 | 0 | 3.27 | 0.00109 | -0.00976 | CFL | Bldg | 2930 | 0.801 | 2930 | 0.801 | 1.12 | 1.36 | -0.00333
CFLBldgSCERtLNewCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RtL | New | CZ10 | 2.93 | 0.000801 | 0 | 3.28 | 0.00109 | -0.00949 | 2.93 | 0.000801 | 0 | 3.28 | 0.00109 | -0.00949 | CFL | Bldg | 2930 | 0.801 | 2930 | 0.801 | 1.12 | 1.36 | -0.00324
CFLBldgPGERtLNewCZ11 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RtL | New | CZ11 | 2.93 | 0.000801 | 0 | 3.13 | 0.00102 | -0.0209 | 2.93 | 0.000801 | 0 | 3.13 | 0.00102 | -0.0209 | CFL | Bldg | 2930 | 0.801 | 2930 | 0.801 | 1.07 | 1.27 | -0.00713
CFLBldgPGERtLNewCZ12 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RtL | New | CZ12 | 2.93 | 0.000801 | 0 | 3.11 | 0.00103 | -0.0205 | 2.93 | 0.000801 | 0 | 3.11 | 0.00103 | -0.0205 | CFL | Bldg | 2930 | 0.801 | 2930 | 0.801 | 1.06 | 1.29 | -0.007
CFLBldgPGERtLNewCZ13 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RtL | New | CZ13 | 2.93 | 0.000801 | 0 | 3.15 | 0.00103 | -0.0195 | 2.93 | 0.000801 | 0 | 3.15 | 0.00103 | -0.0195 | CFL | Bldg | 2930 | 0.801 | 2930 | 0.801 | 1.08 | 1.29 | -0.00666
CFLBldgSCERtLNewCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RtL | New | CZ13 | 2.93 | 0.000801 | 0 | 3.21 | 0.00108 | -0.018 | 2.93 | 0.000801 | 0 | 3.21 | 0.00108 | -0.018 | CFL | Bldg | 2930 | 0.801 | 2930 | 0.801 | 1.1 | 1.35 | -0.00614
CFLBldgSCERtLNewCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RtL | New | CZ14 | 2.93 | 0.000801 | 0 | 3.2 | 0.00108 | -0.0184 | 2.93 | 0.000801 | 0 | 3.2 | 0.00108 | -0.0184 | CFL | Bldg | 2930 | 0.801 | 2930 | 0.801 | 1.09 | 1.35 | -0.00628
CFLBldgSDGRtLNewCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SDG | RtL | New | CZ14 | 2.93 | 0.000801 | 0 | 3.2 | 0.00108 | -0.019 | 2.93 | 0.000801 | 0 | 3.2 | 0.00108 | -0.019 | CFL | Bldg | 2930 | 0.801 | 2930 | 0.801 | 1.09 | 1.35 | -0.00648
CFLBldgSCERtLNewCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RtL | New | CZ15 | 2.93 | 0.000801 | 0 | 3.47 | 0.0011 | -0.00279 | 2.93 | 0.000801 | 0 | 3.47 | 0.0011 | -0.00279 | CFL | Bldg | 2930 | 0.801 | 2930 | 0.801 | 1.18 | 1.37 | -0.000952
CFLBldgSDGRtLNewCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SDG | RtL | New | CZ15 | 2.93 | 0.000801 | 0 | 3.46 | 0.0011 | -0.00286 | 2.93 | 0.000801 | 0 | 3.46 | 0.0011 | -0.00286 | CFL | Bldg | 2930 | 0.801 | 2930 | 0.801 | 1.18 | 1.37 | -0.000976
CFLBldgPGERtLNewCZ16 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RtL | New | CZ16 | 2.93 | 0.000801 | 0 | 2.87 | 0.000979 | -0.041 | 2.93 | 0.000801 | 0 | 2.87 | 0.000979 | -0.041 | CFL | Bldg | 2930 | 0.801 | 2930 | 0.801 | 0.98 | 1.22 | -0.014
CFLBldgSCERtLNewCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RtL | New | CZ16 | 2.93 | 0.000801 | 0 | 2.9 | 0.00102 | -0.0381 | 2.93 | 0.000801 | 0 | 2.9 | 0.00102 | -0.0381 | CFL | Bldg | 2930 | 0.801 | 2930 | 0.801 | 0.99 | 1.27 | -0.013
CFLBldgSCGRtLNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SCG | RtL | New | IOU | 2.93 | 0.000801 | 0 | 3.26 | 0.00106 | -0.00962 | 2.93 | 0.000801 | 0 | 3.26 | 0.00106 | -0.00962 | CFL | Bldg | 2930 | 0.801 | 2930 | 0.801 | 1.11 | 1.32 | -0.00328
CFLBldgSDGRtLNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SDG | RtL | New | IOU | 2.93 | 0.000801 | 0 | 3.22 | 0.00101 | -0.008 | 2.93 | 0.000801 | 0 | 3.22 | 0.00101 | -0.008 | CFL | Bldg | 2930 | 0.801 | 2930 | 0.801 | 1.1 | 1.26 | -0.00273
CFLBldgSCERtLNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | RtL | New | IOU | 2.93 | 0.000801 | 0 | 3.26 | 0.00106 | -0.00966 | 2.93 | 0.000801 | 0 | 3.26 | 0.00106 | -0.00966 | CFL | Bldg | 2930 | 0.801 | 2930 | 0.801 | 1.11 | 1.32 | -0.0033
CFLBldgPGERtLNewIOU | Com-Iltg-dWatt-CFL_OSbldg | PGE | RtL | New | IOU | 2.93 | 0.000801 | 0 | 3.19 | 0.00107 | -0.0186 | 2.93 | 0.000801 | 0 | 3.19 | 0.00107 | -0.0186 | CFL | Bldg | 2930 | 0.801 | 2930 | 0.801 | 1.09 | 1.34 | -0.00635
CFLBldgPGERtSExCZ01 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RtS | Ex | CZ01 | 2.26 | 0.000529 | 0 | 2.19 | 0.000625 | -0.0271 | 2.26 | 0.000529 | 0 | 2.19 | 0.000625 | -0.0271 | CFL | Bldg | 2260 | 0.529 | 2260 | 0.529 | 0.969 | 1.18 | -0.012
CFLBldgPGERtSExCZ02 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RtS | Ex | CZ02 | 2.26 | 0.000529 | 0 | 2.35 | 0.000631 | -0.0148 | 2.26 | 0.000529 | 0 | 2.35 | 0.000631 | -0.0148 | CFL | Bldg | 2260 | 0.529 | 2260 | 0.529 | 1.04 | 1.19 | -0.00655
CFLBldgPGERtSExCZ03 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RtS | Ex | CZ03 | 2.26 | 0.000529 | 0 | 2.36 | 0.000641 | -0.014 | 2.26 | 0.000529 | 0 | 2.36 | 0.000641 | -0.014 | CFL | Bldg | 2260 | 0.529 | 2260 | 0.529 | 1.04 | 1.21 | -0.00619
CFLBldgPGERtSExCZ04 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RtS | Ex | CZ04 | 2.26 | 0.000529 | 0 | 2.4 | 0.000641 | -0.0105 | 2.26 | 0.000529 | 0 | 2.4 | 0.000641 | -0.0105 | CFL | Bldg | 2260 | 0.529 | 2260 | 0.529 | 1.06 | 1.21 | -0.00465
CFLBldgPGERtSExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RtS | Ex | CZ05 | 2.26 | 0.000529 | 0 | 2.39 | 0.000658 | -0.0118 | 2.26 | 0.000529 | 0 | 2.39 | 0.000658 | -0.0118 | CFL | Bldg | 2260 | 0.529 | 2260 | 0.529 | 1.06 | 1.24 | -0.00522
CFLBldgSCGRtSExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCG | RtS | Ex | CZ05 | 2.26 | 0.000529 | 0 | 2.39 | 0.000658 | -0.0118 | 2.26 | 0.000529 | 0 | 2.39 | 0.000658 | -0.0118 | CFL | Bldg | 2260 | 0.529 | 2260 | 0.529 | 1.06 | 1.24 | -0.00522
CFLBldgSCERtSExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RtS | Ex | CZ05 | 2.26 | 0.000529 | 0 | 2.39 | 0.000658 | -0.0118 | 2.26 | 0.000529 | 0 | 2.39 | 0.000658 | -0.0118 | CFL | Bldg | 2260 | 0.529 | 2260 | 0.529 | 1.06 | 1.24 | -0.00522
CFLBldgSDGRtSExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SDG | RtS | Ex | CZ06 | 2.26 | 0.000529 | 0 | 2.5 | 0.000662 | -0.00447 | 2.26 | 0.000529 | 0 | 2.5 | 0.000662 | -0.00447 | CFL | Bldg | 2260 | 0.529 | 2260 | 0.529 | 1.11 | 1.25 | -0.00198
CFLBldgSCGRtSExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCG | RtS | Ex | CZ06 | 2.26 | 0.000529 | 0 | 2.5 | 0.000662 | -0.00447 | 2.26 | 0.000529 | 0 | 2.5 | 0.000662 | -0.00447 | CFL | Bldg | 2260 | 0.529 | 2260 | 0.529 | 1.11 | 1.25 | -0.00198
CFLBldgSCERtSExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RtS | Ex | CZ06 | 2.26 | 0.000529 | 0 | 2.5 | 0.000662 | -0.00447 | 2.26 | 0.000529 | 0 | 2.5 | 0.000662 | -0.00447 | CFL | Bldg | 2260 | 0.529 | 2260 | 0.529 | 1.11 | 1.25 | -0.00198
CFLBldgSDGRtSExCZ07 | Com-Iltg-dWatt-CFL_OSbldg | SDG | RtS | Ex | CZ07 | 2.26 | 0.000529 | 0 | 2.51 | 0.000647 | -0.00276 | 2.26 | 0.000529 | 0 | 2.51 | 0.000647 | -0.00276 | CFL | Bldg | 2260 | 0.529 | 2260 | 0.529 | 1.11 | 1.22 | -0.00122
CFLBldgSDGRtSExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SDG | RtS | Ex | CZ08 | 2.26 | 0.000529 | 0 | 2.52 | 0.000663 | -0.0038 | 2.26 | 0.000529 | 0 | 2.52 | 0.000663 | -0.0038 | CFL | Bldg | 2260 | 0.529 | 2260 | 0.529 | 1.12 | 1.25 | -0.00168
CFLBldgSCGRtSExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCG | RtS | Ex | CZ08 | 2.26 | 0.000529 | 0 | 2.52 | 0.000663 | -0.0038 | 2.26 | 0.000529 | 0 | 2.52 | 0.000663 | -0.0038 | CFL | Bldg | 2260 | 0.529 | 2260 | 0.529 | 1.12 | 1.25 | -0.00168
CFLBldgSCERtSExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RtS | Ex | CZ08 | 2.26 | 0.000529 | 0 | 2.52 | 0.000663 | -0.0038 | 2.26 | 0.000529 | 0 | 2.52 | 0.000663 | -0.0038 | CFL | Bldg | 2260 | 0.529 | 2260 | 0.529 | 1.12 | 1.25 | -0.00168
CFLBldgSCGRtSExCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCG | RtS | Ex | CZ09 | 2.26 | 0.000529 | 0 | 2.52 | 0.000676 | -0.0047 | 2.26 | 0.000529 | 0 | 2.52 | 0.000676 | -0.0047 | CFL | Bldg | 2260 | 0.529 | 2260 | 0.529 | 1.12 | 1.28 | -0.00208
CFLBldgSCERtSExCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RtS | Ex | CZ09 | 2.26 | 0.000529 | 0 | 2.52 | 0.000676 | -0.0047 | 2.26 | 0.000529 | 0 | 2.52 | 0.000676 | -0.0047 | CFL | Bldg | 2260 | 0.529 | 2260 | 0.529 | 1.12 | 1.28 | -0.00208
CFLBldgSDGRtSExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SDG | RtS | Ex | CZ10 | 2.26 | 0.000529 | 0 | 2.51 | 0.000669 | -0.00529 | 2.26 | 0.000529 | 0 | 2.51 | 0.000669 | -0.00529 | CFL | Bldg | 2260 | 0.529 | 2260 | 0.529 | 1.11 | 1.26 | -0.00234
CFLBldgSCGRtSExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCG | RtS | Ex | CZ10 | 2.26 | 0.000529 | 0 | 2.51 | 0.000669 | -0.00529 | 2.26 | 0.000529 | 0 | 2.51 | 0.000669 | -0.00529 | CFL | Bldg | 2260 | 0.529 | 2260 | 0.529 | 1.11 | 1.26 | -0.00234
CFLBldgSCERtSExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RtS | Ex | CZ10 | 2.26 | 0.000529 | 0 | 2.51 | 0.000669 | -0.00529 | 2.26 | 0.000529 | 0 | 2.51 | 0.000669 | -0.00529 | CFL | Bldg | 2260 | 0.529 | 2260 | 0.529 | 1.11 | 1.26 | -0.00234
CFLBldgPGERtSExCZ11 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RtS | Ex | CZ11 | 2.26 | 0.000529 | 0 | 2.37 | 0.000647 | -0.014 | 2.26 | 0.000529 | 0 | 2.37 | 0.000647 | -0.014 | CFL | Bldg | 2260 | 0.529 | 2260 | 0.529 | 1.05 | 1.22 | -0.00619
CFLBldgPGERtSExCZ12 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RtS | Ex | CZ12 | 2.26 | 0.000529 | 0 | 2.37 | 0.000638 | -0.0144 | 2.26 | 0.000529 | 0 | 2.37 | 0.000638 | -0.0144 | CFL | Bldg | 2260 | 0.529 | 2260 | 0.529 | 1.05 | 1.21 | -0.00637
CFLBldgSCERtSExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RtS | Ex | CZ13 | 2.26 | 0.000529 | 0 | 2.43 | 0.000671 | -0.0125 | 2.26 | 0.000529 | 0 | 2.43 | 0.000671 | -0.0125 | CFL | Bldg | 2260 | 0.529 | 2260 | 0.529 | 1.08 | 1.27 | -0.00553
CFLBldgPGERtSExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RtS | Ex | CZ13 | 2.26 | 0.000529 | 0 | 2.43 | 0.000671 | -0.0125 | 2.26 | 0.000529 | 0 | 2.43 | 0.000671 | -0.0125 | CFL | Bldg | 2260 | 0.529 | 2260 | 0.529 | 1.08 | 1.27 | -0.00553
CFLBldgSCGRtSExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCG | RtS | Ex | CZ13 | 2.26 | 0.000529 | 0 | 2.43 | 0.000671 | -0.0125 | 2.26 | 0.000529 | 0 | 2.43 | 0.000671 | -0.0125 | CFL | Bldg | 2260 | 0.529 | 2260 | 0.529 | 1.08 | 1.27 | -0.00553
CFLBldgSCGRtSExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCG | RtS | Ex | CZ14 | 2.26 | 0.000529 | 0 | 2.44 | 0.000668 | -0.0116 | 2.26 | 0.000529 | 0 | 2.44 | 0.000668 | -0.0116 | CFL | Bldg | 2260 | 0.529 | 2260 | 0.529 | 1.08 | 1.26 | -0.00513
CFLBldgSDGRtSExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SDG | RtS | Ex | CZ14 | 2.26 | 0.000529 | 0 | 2.44 | 0.000668 | -0.0116 | 2.26 | 0.000529 | 0 | 2.44 | 0.000668 | -0.0116 | CFL | Bldg | 2260 | 0.529 | 2260 | 0.529 | 1.08 | 1.26 | -0.00513
CFLBldgSCERtSExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RtS | Ex | CZ14 | 2.26 | 0.000529 | 0 | 2.44 | 0.000668 | -0.0116 | 2.26 | 0.000529 | 0 | 2.44 | 0.000668 | -0.0116 | CFL | Bldg | 2260 | 0.529 | 2260 | 0.529 | 1.08 | 1.26 | -0.00513
CFLBldgSCGRtSExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCG | RtS | Ex | CZ15 | 2.26 | 0.000529 | 0 | 2.68 | 0.000658 | -0.00137 | 2.26 | 0.000529 | 0 | 2.68 | 0.000658 | -0.00137 | CFL | Bldg | 2260 | 0.529 | 2260 | 0.529 | 1.19 | 1.24 | -0.000606
CFLBldgSDGRtSExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SDG | RtS | Ex | CZ15 | 2.26 | 0.000529 | 0 | 2.68 | 0.000658 | -0.00137 | 2.26 | 0.000529 | 0 | 2.68 | 0.000658 | -0.00137 | CFL | Bldg | 2260 | 0.529 | 2260 | 0.529 | 1.19 | 1.24 | -0.000606
CFLBldgSCERtSExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RtS | Ex | CZ15 | 2.26 | 0.000529 | 0 | 2.68 | 0.000658 | -0.00137 | 2.26 | 0.000529 | 0 | 2.68 | 0.000658 | -0.00137 | CFL | Bldg | 2260 | 0.529 | 2260 | 0.529 | 1.19 | 1.24 | -0.000606
CFLBldgSCERtSExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RtS | Ex | CZ16 | 2.26 | 0.000529 | 0 | 2.23 | 0.000653 | -0.024 | 2.26 | 0.000529 | 0 | 2.23 | 0.000653 | -0.024 | CFL | Bldg | 2260 | 0.529 | 2260 | 0.529 | 0.987 | 1.23 | -0.0106
CFLBldgPGERtSExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RtS | Ex | CZ16 | 2.26 | 0.000529 | 0 | 2.23 | 0.000653 | -0.024 | 2.26 | 0.000529 | 0 | 2.23 | 0.000653 | -0.024 | CFL | Bldg | 2260 | 0.529 | 2260 | 0.529 | 0.987 | 1.23 | -0.0106
CFLBldgSCGRtSExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCG | RtS | Ex | CZ16 | 2.26 | 0.000529 | 0 | 2.23 | 0.000653 | -0.024 | 2.26 | 0.000529 | 0 | 2.23 | 0.000653 | -0.024 | CFL | Bldg | 2260 | 0.529 | 2260 | 0.529 | 0.987 | 1.23 | -0.0106
CFLBldgSCERtSExIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | RtS | Ex | IOU | 2.26 | 0.000529 | 0 | 2.51 | 0.000666 | -0.00511 | 2.26 | 0.000529 | 0 | 2.51 | 0.000666 | -0.00511 | CFL | Bldg | 2260 | 0.529 | 2260 | 0.529 | 1.11 | 1.26 | -0.00226
CFLBldgPGERtSExIOU | Com-Iltg-dWatt-CFL_OSbldg | PGE | RtS | Ex | IOU | 2.26 | 0.000529 | 0 | 2.38 | 0.000644 | -0.0136 | 2.26 | 0.000529 | 0 | 2.38 | 0.000644 | -0.0136 | CFL | Bldg | 2260 | 0.529 | 2260 | 0.529 | 1.05 | 1.22 | -0.00602
CFLBldgSDGRtSExIOU | Com-Iltg-dWatt-CFL_OSbldg | SDG | RtS | Ex | IOU | 2.26 | 0.000529 | 0 | 2.51 | 0.000654 | -0.00351 | 2.26 | 0.000529 | 0 | 2.51 | 0.000654 | -0.00351 | CFL | Bldg | 2260 | 0.529 | 2260 | 0.529 | 1.11 | 1.24 | -0.00155
CFLBldgSCGRtSExIOU | Com-Iltg-dWatt-CFL_OSbldg | SCG | RtS | Ex | IOU | 2.26 | 0.000529 | 0 | 2.51 | 0.000667 | -0.00499 | 2.26 | 0.000529 | 0 | 2.51 | 0.000667 | -0.00499 | CFL | Bldg | 2260 | 0.529 | 2260 | 0.529 | 1.11 | 1.26 | -0.00221
CFLBldgPGERtSNewCZ01 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RtS | New | CZ01 | 2.26 | 0.000529 | 0 | 2.17 | 0.000616 | -0.0303 | 2.26 | 0.000529 | 0 | 2.17 | 0.000616 | -0.0303 | CFL | Bldg | 2260 | 0.529 | 2260 | 0.529 | 0.96 | 1.16 | -0.0134
CFLBldgPGERtSNewCZ02 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RtS | New | CZ02 | 2.26 | 0.000529 | 0 | 2.33 | 0.000646 | -0.0163 | 2.26 | 0.000529 | 0 | 2.33 | 0.000646 | -0.0163 | CFL | Bldg | 2260 | 0.529 | 2260 | 0.529 | 1.03 | 1.22 | -0.00721
CFLBldgPGERtSNewCZ03 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RtS | New | CZ03 | 2.26 | 0.000529 | 0 | 2.29 | 0.000634 | -0.0156 | 2.26 | 0.000529 | 0 | 2.29 | 0.000634 | -0.0156 | CFL | Bldg | 2260 | 0.529 | 2260 | 0.529 | 1.01 | 1.2 | -0.0069
CFLBldgPGERtSNewCZ04 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RtS | New | CZ04 | 2.26 | 0.000529 | 0 | 2.36 | 0.00064 | -0.0117 | 2.26 | 0.000529 | 0 | 2.36 | 0.00064 | -0.0117 | CFL | Bldg | 2260 | 0.529 | 2260 | 0.529 | 1.04 | 1.21 | -0.00518
CFLBldgSCERtSNewCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RtS | New | CZ05 | 2.26 | 0.000529 | 0 | 2.32 | 0.000643 | -0.0132 | 2.26 | 0.000529 | 0 | 2.32 | 0.000643 | -0.0132 | CFL | Bldg | 2260 | 0.529 | 2260 | 0.529 | 1.03 | 1.22 | -0.00584
CFLBldgPGERtSNewCZ05 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RtS | New | CZ05 | 2.26 | 0.000529 | 0 | 2.31 | 0.000623 | -0.0139 | 2.26 | 0.000529 | 0 | 2.31 | 0.000623 | -0.0139 | CFL | Bldg | 2260 | 0.529 | 2260 | 0.529 | 1.02 | 1.18 | -0.00615
CFLBldgSDGRtSNewCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SDG | RtS | New | CZ06 | 2.26 | 0.000529 | 0 | 2.44 | 0.000651 | -0.00563 | 2.26 | 0.000529 | 0 | 2.44 | 0.000651 | -0.00563 | CFL | Bldg | 2260 | 0.529 | 2260 | 0.529 | 1.08 | 1.23 | -0.00249
CFLBldgSCERtSNewCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RtS | New | CZ06 | 2.26 | 0.000529 | 0 | 2.44 | 0.000652 | -0.00551 | 2.26 | 0.000529 | 0 | 2.44 | 0.000652 | -0.00551 | CFL | Bldg | 2260 | 0.529 | 2260 | 0.529 | 1.08 | 1.23 | -0.00244
CFLBldgSDGRtSNewCZ07 | Com-Iltg-dWatt-CFL_OSbldg | SDG | RtS | New | CZ07 | 2.26 | 0.000529 | 0 | 2.43 | 0.000643 | -0.00344 | 2.26 | 0.000529 | 0 | 2.43 | 0.000643 | -0.00344 | CFL | Bldg | 2260 | 0.529 | 2260 | 0.529 | 1.08 | 1.22 | -0.00152
CFLBldgSCERtSNewCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RtS | New | CZ08 | 2.26 | 0.000529 | 0 | 2.47 | 0.000659 | -0.00461 | 2.26 | 0.000529 | 0 | 2.47 | 0.000659 | -0.00461 | CFL | Bldg | 2260 | 0.529 | 2260 | 0.529 | 1.09 | 1.25 | -0.00204
CFLBldgSDGRtSNewCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SDG | RtS | New | CZ08 | 2.26 | 0.000529 | 0 | 2.46 | 0.000658 | -0.0047 | 2.26 | 0.000529 | 0 | 2.46 | 0.000658 | -0.0047 | CFL | Bldg | 2260 | 0.529 | 2260 | 0.529 | 1.09 | 1.24 | -0.00208
CFLBldgSCERtSNewCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RtS | New | CZ09 | 2.26 | 0.000529 | 0 | 2.46 | 0.000676 | -0.00531 | 2.26 | 0.000529 | 0 | 2.46 | 0.000676 | -0.00531 | CFL | Bldg | 2260 | 0.529 | 2260 | 0.529 | 1.09 | 1.28 | -0.00235
CFLBldgSDGRtSNewCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SDG | RtS | New | CZ10 | 2.26 | 0.000529 | 0 | 2.48 | 0.000686 | -0.00563 | 2.26 | 0.000529 | 0 | 2.48 | 0.000686 | -0.00563 | CFL | Bldg | 2260 | 0.529 | 2260 | 0.529 | 1.1 | 1.3 | -0.00249
CFLBldgSCERtSNewCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RtS | New | CZ10 | 2.26 | 0.000529 | 0 | 2.48 | 0.000687 | -0.00551 | 2.26 | 0.000529 | 0 | 2.48 | 0.000687 | -0.00551 | CFL | Bldg | 2260 | 0.529 | 2260 | 0.529 | 1.1 | 1.3 | -0.00244
CFLBldgPGERtSNewCZ11 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RtS | New | CZ11 | 2.26 | 0.000529 | 0 | 2.38 | 0.000658 | -0.0141 | 2.26 | 0.000529 | 0 | 2.38 | 0.000658 | -0.0141 | CFL | Bldg | 2260 | 0.529 | 2260 | 0.529 | 1.05 | 1.24 | -0.00624
CFLBldgPGERtSNewCZ12 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RtS | New | CZ12 | 2.26 | 0.000529 | 0 | 2.37 | 0.000652 | -0.0151 | 2.26 | 0.000529 | 0 | 2.37 | 0.000652 | -0.0151 | CFL | Bldg | 2260 | 0.529 | 2260 | 0.529 | 1.05 | 1.23 | -0.00668
CFLBldgPGERtSNewCZ13 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RtS | New | CZ13 | 2.26 | 0.000529 | 0 | 2.39 | 0.000651 | -0.0137 | 2.26 | 0.000529 | 0 | 2.39 | 0.000651 | -0.0137 | CFL | Bldg | 2260 | 0.529 | 2260 | 0.529 | 1.06 | 1.23 | -0.00606
CFLBldgSCERtSNewCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RtS | New | CZ13 | 2.26 | 0.000529 | 0 | 2.42 | 0.000677 | -0.0129 | 2.26 | 0.000529 | 0 | 2.42 | 0.000677 | -0.0129 | CFL | Bldg | 2260 | 0.529 | 2260 | 0.529 | 1.07 | 1.28 | -0.00571
CFLBldgSDGRtSNewCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SDG | RtS | New | CZ14 | 2.26 | 0.000529 | 0 | 2.43 | 0.000677 | -0.0124 | 2.26 | 0.000529 | 0 | 2.43 | 0.000677 | -0.0124 | CFL | Bldg | 2260 | 0.529 | 2260 | 0.529 | 1.08 | 1.28 | -0.00549
CFLBldgSCERtSNewCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RtS | New | CZ14 | 2.26 | 0.000529 | 0 | 2.43 | 0.000678 | -0.012 | 2.26 | 0.000529 | 0 | 2.43 | 0.000678 | -0.012 | CFL | Bldg | 2260 | 0.529 | 2260 | 0.529 | 1.08 | 1.28 | -0.00531
CFLBldgSDGRtSNewCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SDG | RtS | New | CZ15 | 2.26 | 0.000529 | 0 | 2.6 | 0.000696 | -0.00109 | 2.26 | 0.000529 | 0 | 2.6 | 0.000696 | -0.00109 | CFL | Bldg | 2260 | 0.529 | 2260 | 0.529 | 1.15 | 1.32 | -0.000482
CFLBldgSCERtSNewCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RtS | New | CZ15 | 2.26 | 0.000529 | 0 | 2.6 | 0.000697 | -0.0011 | 2.26 | 0.000529 | 0 | 2.6 | 0.000697 | -0.0011 | CFL | Bldg | 2260 | 0.529 | 2260 | 0.529 | 1.15 | 1.32 | -0.000487
CFLBldgSCERtSNewCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | RtS | New | CZ16 | 2.26 | 0.000529 | 0 | 2.22 | 0.00065 | -0.0255 | 2.26 | 0.000529 | 0 | 2.22 | 0.00065 | -0.0255 | CFL | Bldg | 2260 | 0.529 | 2260 | 0.529 | 0.982 | 1.23 | -0.0113
CFLBldgPGERtSNewCZ16 | Com-Iltg-dWatt-CFL_OSbldg | PGE | RtS | New | CZ16 | 2.26 | 0.000529 | 0 | 2.21 | 0.000628 | -0.0271 | 2.26 | 0.000529 | 0 | 2.21 | 0.000628 | -0.0271 | CFL | Bldg | 2260 | 0.529 | 2260 | 0.529 | 0.978 | 1.19 | -0.012
CFLBldgSCGRtSNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SCG | RtS | New | IOU | 2.26 | 0.000529 | 0 | 2.47 | 0.00067 | -0.00552 | 2.26 | 0.000529 | 0 | 2.47 | 0.00067 | -0.00552 | CFL | Bldg | 2260 | 0.529 | 2260 | 0.529 | 1.09 | 1.27 | -0.00244
CFLBldgPGERtSNewIOU | Com-Iltg-dWatt-CFL_OSbldg | PGE | RtS | New | IOU | 2.26 | 0.000529 | 0 | 2.41 | 0.000673 | -0.0131 | 2.26 | 0.000529 | 0 | 2.41 | 0.000673 | -0.0131 | CFL | Bldg | 2260 | 0.529 | 2260 | 0.529 | 1.07 | 1.27 | -0.0058
CFLBldgSCERtSNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | RtS | New | IOU | 2.26 | 0.000529 | 0 | 2.47 | 0.000671 | -0.00555 | 2.26 | 0.000529 | 0 | 2.47 | 0.000671 | -0.00555 | CFL | Bldg | 2260 | 0.529 | 2260 | 0.529 | 1.09 | 1.27 | -0.00246
CFLBldgSDGRtSNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SDG | RtS | New | IOU | 2.26 | 0.000529 | 0 | 2.44 | 0.000655 | -0.00414 | 2.26 | 0.000529 | 0 | 2.44 | 0.000655 | -0.00414 | CFL | Bldg | 2260 | 0.529 | 2260 | 0.529 | 1.08 | 1.24 | -0.00183
CFLBldgSCEs_AgrExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_Agr | Ex | CZ05 | 2.13 | 0.000513 | 0 | 2.26 | 0.000626 | -0.00982 | 2.08 | 0.000491 | 0 | 2.2 | 0.000598 | -0.00966 | CFL | Bldg | 2130 | 0.513 | 2080 | 0.491 | 1.06 | 1.22 | -0.00464
CFLBldgSCEs_AgrExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_Agr | Ex | CZ06 | 2.13 | 0.000513 | 0 | 2.33 | 0.000616 | -0.00415 | 2.08 | 0.000491 | 0 | 2.28 | 0.000589 | -0.00411 | CFL | Bldg | 2130 | 0.513 | 2080 | 0.491 | 1.1 | 1.2 | -0.00198
CFLBldgSCEs_AgrExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_Agr | Ex | CZ08 | 2.13 | 0.000513 | 0 | 2.35 | 0.000616 | -0.00342 | 2.08 | 0.000491 | 0 | 2.29 | 0.000589 | -0.00339 | CFL | Bldg | 2130 | 0.513 | 2080 | 0.491 | 1.1 | 1.2 | -0.00163
CFLBldgSCEs_AgrExCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_Agr | Ex | CZ09 | 2.13 | 0.000513 | 0 | 2.38 | 0.000631 | -0.00397 | 2.08 | 0.000491 | 0 | 2.32 | 0.000602 | -0.00389 | CFL | Bldg | 2130 | 0.513 | 2080 | 0.491 | 1.12 | 1.23 | -0.00187
CFLBldgSCEs_AgrExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_Agr | Ex | CZ10 | 2.13 | 0.000513 | 0 | 2.35 | 0.000629 | -0.0047 | 2.08 | 0.000491 | 0 | 2.29 | 0.000602 | -0.00465 | CFL | Bldg | 2130 | 0.513 | 2080 | 0.491 | 1.1 | 1.23 | -0.00224
CFLBldgSCEs_AgrExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_Agr | Ex | CZ13 | 2.13 | 0.000513 | 0 | 2.29 | 0.000619 | -0.011 | 2.08 | 0.000491 | 0 | 2.24 | 0.000591 | -0.0108 | CFL | Bldg | 2130 | 0.513 | 2080 | 0.491 | 1.08 | 1.2 | -0.00519
CFLBldgSCEs_AgrExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_Agr | Ex | CZ14 | 2.13 | 0.000513 | 0 | 2.27 | 0.000625 | -0.0129 | 2.08 | 0.000491 | 0 | 2.22 | 0.000597 | -0.0128 | CFL | Bldg | 2130 | 0.513 | 2080 | 0.491 | 1.07 | 1.22 | -0.00615
CFLBldgSCEs_AgrExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_Agr | Ex | CZ15 | 2.13 | 0.000513 | 0 | 2.52 | 0.00062 | -0.00121 | 2.08 | 0.000491 | 0 | 2.46 | 0.000594 | -0.0012 | CFL | Bldg | 2130 | 0.513 | 2080 | 0.491 | 1.18 | 1.21 | -0.000577
CFLBldgSCEs_AgrExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_Agr | Ex | CZ16 | 2.13 | 0.000513 | 0 | 2.11 | 0.000611 | -0.0241 | 2.08 | 0.000491 | 0 | 2.06 | 0.000584 | -0.0238 | CFL | Bldg | 2130 | 0.513 | 2080 | 0.491 | 0.99 | 1.19 | -0.0114
CFLBldgSCEs_AgrExIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_Agr | Ex | IOU | 2.13 | 0.000513 | 0 | 2.35 | 0.000621 | -0.00476 | 2.08 | 0.000491 | 0 | 2.29 | 0.000593 | -0.0047 | CFL | Bldg | 2130 | 0.513 | 2080 | 0.491 | 1.1 | 1.21 | -0.00226
CFLBldgSCEs_CliExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_Cli | Ex | CZ05 | 2.55 | 0.0005 | 0 | 2.66 | 0.000622 | -0.0279 | 2.38 | 0.000439 | 0 | 2.48 | 0.000545 | -0.0268 | CFL | Bldg | 2550 | 0.5 | 2380 | 0.439 | 1.04 | 1.24 | -0.0113
CFLBldgSCEs_CliExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_Cli | Ex | CZ06 | 2.55 | 0.0005 | 0 | 2.8 | 0.000637 | -0.0171 | 2.38 | 0.000439 | 0 | 2.62 | 0.00056 | -0.0166 | CFL | Bldg | 2550 | 0.5 | 2380 | 0.439 | 1.1 | 1.28 | -0.00697
CFLBldgSCEs_CliExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_Cli | Ex | CZ08 | 2.55 | 0.0005 | 0 | 2.82 | 0.000641 | -0.0164 | 2.38 | 0.000439 | 0 | 2.64 | 0.000563 | -0.0159 | CFL | Bldg | 2550 | 0.5 | 2380 | 0.439 | 1.11 | 1.28 | -0.00668
CFLBldgSCEs_CliExCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_Cli | Ex | CZ09 | 2.55 | 0.0005 | 0 | 2.84 | 0.000657 | -0.0179 | 2.38 | 0.000439 | 0 | 2.65 | 0.000578 | -0.0173 | CFL | Bldg | 2550 | 0.5 | 2380 | 0.439 | 1.11 | 1.32 | -0.00727
CFLBldgSCEs_CliExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_Cli | Ex | CZ10 | 2.54 | 0.000498 | 0 | 2.82 | 0.000649 | -0.0177 | 2.38 | 0.000439 | 0 | 2.64 | 0.000574 | -0.0172 | CFL | Bldg | 2540 | 0.498 | 2380 | 0.439 | 1.11 | 1.31 | -0.00723
CFLBldgSCEs_CliExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_Cli | Ex | CZ13 | 2.54 | 0.0005 | 0 | 2.76 | 0.000648 | -0.0221 | 2.38 | 0.000439 | 0 | 2.58 | 0.00057 | -0.0212 | CFL | Bldg | 2540 | 0.5 | 2380 | 0.439 | 1.08 | 1.3 | -0.00891
CFLBldgSCEs_CliExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_Cli | Ex | CZ14 | 2.54 | 0.000498 | 0 | 2.78 | 0.00065 | -0.0218 | 2.38 | 0.000439 | 0 | 2.6 | 0.000573 | -0.021 | CFL | Bldg | 2540 | 0.498 | 2380 | 0.439 | 1.09 | 1.31 | -0.00882
CFLBldgSCEs_CliExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_Cli | Ex | CZ15 | 2.54 | 0.000498 | 0 | 2.98 | 0.000644 | -0.00991 | 2.38 | 0.000439 | 0 | 2.79 | 0.000569 | -0.00965 | CFL | Bldg | 2540 | 0.498 | 2380 | 0.439 | 1.17 | 1.3 | -0.00405
CFLBldgSCEs_CliExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_Cli | Ex | CZ16 | 2.54 | 0.000499 | 0 | 2.54 | 0.000627 | -0.0345 | 2.38 | 0.000439 | 0 | 2.38 | 0.000551 | -0.0329 | CFL | Bldg | 2540 | 0.499 | 2380 | 0.439 | 1 | 1.26 | -0.0138
CFLBldgSCEs_CliExIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_Cli | Ex | IOU | 2.54 | 0.000499 | 0 | 2.81 | 0.000643 | -0.0177 | 2.38 | 0.000439 | 0 | 2.63 | 0.000566 | -0.0171 | CFL | Bldg | 2540 | 0.499 | 2380 | 0.439 | 1.11 | 1.29 | -0.00718
CFLBldgSCEs_FStExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_FSt | Ex | CZ05 | 3.6 | 0.000659 | 0 | 3.56 | 0.000822 | -0.0489 | 3.56 | 0.000652 | 0 | 3.52 | 0.000813 | -0.0481 | CFL | Bldg | 3600 | 0.659 | 3560 | 0.652 | 0.989 | 1.25 | -0.0135
CFLBldgSCEs_FStExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_FSt | Ex | CZ06 | 3.6 | 0.000659 | 0 | 3.71 | 0.000817 | -0.036 | 3.56 | 0.000652 | 0 | 3.67 | 0.000809 | -0.0354 | CFL | Bldg | 3600 | 0.659 | 3560 | 0.652 | 1.03 | 1.24 | -0.00994
CFLBldgSCEs_FStExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_FSt | Ex | CZ08 | 3.6 | 0.000659 | 0 | 3.78 | 0.000831 | -0.0328 | 3.56 | 0.000652 | 0 | 3.74 | 0.000822 | -0.0322 | CFL | Bldg | 3600 | 0.659 | 3560 | 0.652 | 1.05 | 1.26 | -0.00904
CFLBldgSCEs_FStExCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_FSt | Ex | CZ09 | 3.6 | 0.000659 | 0 | 3.85 | 0.000852 | -0.033 | 3.56 | 0.000652 | 0 | 3.81 | 0.000843 | -0.0324 | CFL | Bldg | 3600 | 0.659 | 3560 | 0.652 | 1.07 | 1.29 | -0.0091
CFLBldgSCEs_FStExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_FSt | Ex | CZ10 | 3.59 | 0.000658 | 0 | 3.81 | 0.000858 | -0.0317 | 3.56 | 0.000652 | 0 | 3.78 | 0.00085 | -0.0312 | CFL | Bldg | 3590 | 0.658 | 3560 | 0.652 | 1.06 | 1.3 | -0.00876
CFLBldgSCEs_FStExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_FSt | Ex | CZ13 | 3.6 | 0.000658 | 0 | 3.8 | 0.000855 | -0.0356 | 3.56 | 0.000652 | 0 | 3.76 | 0.000846 | -0.0351 | CFL | Bldg | 3600 | 0.658 | 3560 | 0.652 | 1.06 | 1.3 | -0.00986
CFLBldgSCEs_FStExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_FSt | Ex | CZ14 | 3.6 | 0.000658 | 0 | 3.77 | 0.000868 | -0.0351 | 3.56 | 0.000652 | 0 | 3.73 | 0.000859 | -0.0347 | CFL | Bldg | 3600 | 0.658 | 3560 | 0.652 | 1.05 | 1.32 | -0.00975
CFLBldgSCEs_FStExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_FSt | Ex | CZ15 | 3.59 | 0.000658 | 0 | 4.1 | 0.000853 | -0.0176 | 3.56 | 0.000652 | 0 | 4.06 | 0.000844 | -0.0173 | CFL | Bldg | 3590 | 0.658 | 3560 | 0.652 | 1.14 | 1.29 | -0.00486
CFLBldgSCEs_FStExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_FSt | Ex | CZ16 | 3.6 | 0.000658 | 0 | 3.46 | 0.000823 | -0.0522 | 3.56 | 0.000652 | 0 | 3.42 | 0.000814 | -0.0516 | CFL | Bldg | 3600 | 0.658 | 3560 | 0.652 | 0.961 | 1.25 | -0.0145
CFLBldgSCEs_FStExIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_FSt | Ex | IOU | 3.6 | 0.000658 | 0 | 3.79 | 0.00084 | -0.0333 | 3.56 | 0.000652 | 0 | 3.74 | 0.000831 | -0.0328 | CFL | Bldg | 3600 | 0.658 | 3560 | 0.652 | 1.05 | 1.27 | -0.00921
CFLBldgSCEs_IndExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_Ind | Ex | CZ05 | 2.16 | 0.00053 | 0 | 2.37 | 0.000651 | -0.00593 | 2.13 | 0.00052 | 0 | 2.34 | 0.000638 | -0.00592 | CFL | Bldg | 2160 | 0.53 | 2130 | 0.52 | 1.1 | 1.23 | -0.00278
CFLBldgSCEs_IndExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_Ind | Ex | CZ06 | 2.16 | 0.00053 | 0 | 2.42 | 0.000633 | -0.00262 | 2.13 | 0.00052 | 0 | 2.39 | 0.000621 | -0.00262 | CFL | Bldg | 2160 | 0.53 | 2130 | 0.52 | 1.12 | 1.19 | -0.00123
CFLBldgSCEs_IndExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_Ind | Ex | CZ08 | 2.16 | 0.00053 | 0 | 2.43 | 0.000647 | -0.00212 | 2.13 | 0.00052 | 0 | 2.4 | 0.000635 | -0.00212 | CFL | Bldg | 2160 | 0.53 | 2130 | 0.52 | 1.13 | 1.22 | -0.000995
CFLBldgSCEs_IndExCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_Ind | Ex | CZ09 | 2.16 | 0.00053 | 0 | 2.46 | 0.000657 | -0.00242 | 2.13 | 0.00052 | 0 | 2.43 | 0.000644 | -0.00242 | CFL | Bldg | 2160 | 0.53 | 2130 | 0.52 | 1.14 | 1.24 | -0.00114
CFLBldgSCEs_IndExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_Ind | Ex | CZ10 | 2.16 | 0.000529 | 0 | 2.42 | 0.000662 | -0.00306 | 2.13 | 0.00052 | 0 | 2.39 | 0.00065 | -0.00305 | CFL | Bldg | 2160 | 0.529 | 2130 | 0.52 | 1.12 | 1.25 | -0.00143
CFLBldgSCEs_IndExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_Ind | Ex | CZ13 | 2.16 | 0.00053 | 0 | 2.38 | 0.000639 | -0.00677 | 2.13 | 0.00052 | 0 | 2.35 | 0.000627 | -0.00676 | CFL | Bldg | 2160 | 0.53 | 2130 | 0.52 | 1.1 | 1.21 | -0.00317
CFLBldgSCEs_IndExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_Ind | Ex | CZ14 | 2.16 | 0.00053 | 0 | 2.37 | 0.000656 | -0.00834 | 2.13 | 0.00052 | 0 | 2.34 | 0.000643 | -0.00833 | CFL | Bldg | 2160 | 0.53 | 2130 | 0.52 | 1.1 | 1.24 | -0.00391
CFLBldgSCEs_IndExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_Ind | Ex | CZ15 | 2.16 | 0.000529 | 0 | 2.56 | 0.000658 | -0.00071 | 2.13 | 0.00052 | 0 | 2.53 | 0.000646 | -0.00071 | CFL | Bldg | 2160 | 0.529 | 2130 | 0.52 | 1.19 | 1.24 | -0.000333
CFLBldgSCEs_IndExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_Ind | Ex | CZ16 | 2.16 | 0.00053 | 0 | 2.22 | 0.000627 | -0.0164 | 2.13 | 0.00052 | 0 | 2.19 | 0.000616 | -0.0163 | CFL | Bldg | 2160 | 0.53 | 2130 | 0.52 | 1.03 | 1.18 | -0.00765
CFLBldgSCEs_IndExIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_Ind | Ex | IOU | 2.16 | 0.00053 | 0 | 2.43 | 0.000648 | -0.00301 | 2.13 | 0.00052 | 0 | 2.4 | 0.000636 | -0.003 | CFL | Bldg | 2160 | 0.53 | 2130 | 0.52 | 1.13 | 1.22 | -0.00141
CFLBldgSCEs_MiCExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_MiC | Ex | CZ05 | 2.52 | 0.000551 | 0 | 2.67 | 0.000681 | -0.0167 | 2.44 | 0.000515 | 0 | 2.59 | 0.000636 | -0.0164 | CFL | Bldg | 2520 | 0.551 | 2440 | 0.515 | 1.06 | 1.23 | -0.00672
CFLBldgSCEs_MiCExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_MiC | Ex | CZ06 | 2.52 | 0.000551 | 0 | 2.84 | 0.000688 | -0.00779 | 2.44 | 0.000515 | 0 | 2.75 | 0.000644 | -0.00773 | CFL | Bldg | 2520 | 0.551 | 2440 | 0.515 | 1.13 | 1.25 | -0.00317
CFLBldgSCEs_MiCExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_MiC | Ex | CZ08 | 2.52 | 0.000551 | 0 | 2.86 | 0.000684 | -0.0066 | 2.44 | 0.000515 | 0 | 2.77 | 0.000639 | -0.00655 | CFL | Bldg | 2520 | 0.551 | 2440 | 0.515 | 1.14 | 1.24 | -0.00268
CFLBldgSCEs_MiCExCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_MiC | Ex | CZ09 | 2.52 | 0.000551 | 0 | 2.83 | 0.000695 | -0.00796 | 2.44 | 0.000515 | 0 | 2.74 | 0.000649 | -0.00782 | CFL | Bldg | 2520 | 0.551 | 2440 | 0.515 | 1.12 | 1.26 | -0.0032
CFLBldgSCEs_MiCExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_MiC | Ex | CZ10 | 2.52 | 0.000549 | 0 | 2.84 | 0.000682 | -0.00819 | 2.44 | 0.000515 | 0 | 2.75 | 0.000639 | -0.00811 | CFL | Bldg | 2520 | 0.549 | 2440 | 0.515 | 1.13 | 1.24 | -0.00332
CFLBldgSCEs_MiCExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_MiC | Ex | CZ13 | 2.52 | 0.00055 | 0 | 2.75 | 0.000692 | -0.0147 | 2.44 | 0.000515 | 0 | 2.66 | 0.000646 | -0.0144 | CFL | Bldg | 2520 | 0.55 | 2440 | 0.515 | 1.09 | 1.25 | -0.0059
CFLBldgSCEs_MiCExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_MiC | Ex | CZ14 | 2.52 | 0.00055 | 0 | 2.77 | 0.000685 | -0.0143 | 2.44 | 0.000515 | 0 | 2.68 | 0.000641 | -0.0141 | CFL | Bldg | 2520 | 0.55 | 2440 | 0.515 | 1.1 | 1.24 | -0.00578
CFLBldgSCEs_MiCExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_MiC | Ex | CZ15 | 2.52 | 0.000549 | 0 | 3.05 | 0.000693 | -0.00274 | 2.44 | 0.000515 | 0 | 2.95 | 0.000649 | -0.00273 | CFL | Bldg | 2520 | 0.549 | 2440 | 0.515 | 1.21 | 1.26 | -0.00112
CFLBldgSCEs_MiCExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_MiC | Ex | CZ16 | 2.52 | 0.00055 | 0 | 2.52 | 0.000672 | -0.0275 | 2.44 | 0.000515 | 0 | 2.44 | 0.000628 | -0.027 | CFL | Bldg | 2520 | 0.55 | 2440 | 0.515 | 1 | 1.22 | -0.0111
CFLBldgSCEs_MiCExIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_MiC | Ex | IOU | 2.52 | 0.00055 | 0 | 2.84 | 0.000687 | -0.00817 | 2.44 | 0.000515 | 0 | 2.75 | 0.000642 | -0.00807 | CFL | Bldg | 2520 | 0.55 | 2440 | 0.515 | 1.13 | 1.25 | -0.00331
CFLBldgSCEs_TCUExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_TCU | Ex | CZ05 | 1.88 | 0.000454 | 0 | 1.95 | 0.000556 | -0.0102 | 1.79 | 0.000417 | 0 | 1.85 | 0.00051 | -0.0098 | CFL | Bldg | 1880 | 0.454 | 1790 | 0.417 | 1.03 | 1.22 | -0.00547
CFLBldgSCEs_TCUExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_TCU | Ex | CZ06 | 1.88 | 0.000454 | 0 | 2.04 | 0.000556 | -0.00436 | 1.79 | 0.000417 | 0 | 1.94 | 0.00051 | -0.00423 | CFL | Bldg | 1880 | 0.454 | 1790 | 0.417 | 1.08 | 1.22 | -0.00236
CFLBldgSCEs_TCUExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_TCU | Ex | CZ08 | 1.88 | 0.000454 | 0 | 2.05 | 0.000558 | -0.00382 | 1.79 | 0.000417 | 0 | 1.95 | 0.000512 | -0.00369 | CFL | Bldg | 1880 | 0.454 | 1790 | 0.417 | 1.09 | 1.23 | -0.00206
CFLBldgSCEs_TCUExCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_TCU | Ex | CZ09 | 1.88 | 0.000453 | 0 | 2.06 | 0.000573 | -0.00574 | 1.79 | 0.000417 | 0 | 1.96 | 0.000526 | -0.00548 | CFL | Bldg | 1880 | 0.453 | 1790 | 0.417 | 1.09 | 1.26 | -0.00306
CFLBldgSCEs_TCUExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_TCU | Ex | CZ10 | 1.87 | 0.000451 | 0 | 2.04 | 0.000562 | -0.00485 | 1.79 | 0.000417 | 0 | 1.95 | 0.000519 | -0.0047 | CFL | Bldg | 1870 | 0.451 | 1790 | 0.417 | 1.09 | 1.24 | -0.00263
CFLBldgSCEs_TCUExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_TCU | Ex | CZ13 | 1.88 | 0.000452 | 0 | 2.01 | 0.000561 | -0.00932 | 1.79 | 0.000417 | 0 | 1.92 | 0.000515 | -0.00893 | CFL | Bldg | 1880 | 0.452 | 1790 | 0.417 | 1.07 | 1.24 | -0.00499
CFLBldgSCEs_TCUExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_TCU | Ex | CZ14 | 1.87 | 0.000452 | 0 | 2 | 0.000559 | -0.00879 | 1.79 | 0.000417 | 0 | 1.91 | 0.000514 | -0.00854 | CFL | Bldg | 1870 | 0.452 | 1790 | 0.417 | 1.07 | 1.23 | -0.00477
CFLBldgSCEs_TCUExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_TCU | Ex | CZ15 | 1.87 | 0.000451 | 0 | 2.16 | 0.000557 | -0.00196 | 1.79 | 0.000417 | 0 | 2.06 | 0.000514 | -0.0019 | CFL | Bldg | 1870 | 0.451 | 1790 | 0.417 | 1.15 | 1.23 | -0.00106
CFLBldgSCEs_TCUExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_TCU | Ex | CZ16 | 1.87 | 0.000452 | 0 | 1.86 | 0.000547 | -0.0172 | 1.79 | 0.000417 | 0 | 1.78 | 0.000504 | -0.0165 | CFL | Bldg | 1870 | 0.452 | 1790 | 0.417 | 0.994 | 1.21 | -0.00922
CFLBldgSCEs_TCUExIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | s_TCU | Ex | IOU | 1.88 | 0.000453 | 0 | 2.05 | 0.000561 | -0.00489 | 1.79 | 0.000417 | 0 | 1.95 | 0.000515 | -0.00471 | CFL | Bldg | 1880 | 0.453 | 1790 | 0.417 | 1.09 | 1.24 | -0.00263
CFLBldgPGESCnExCZ01 | Com-Iltg-dWatt-CFL_OSbldg | PGE | SCn | Ex | CZ01 | 2.04 | 0.0005 | 0 | 1.73 | 0.0005 | -0.0343 | 2.01 | 0.000482 | 0 | 1.7 | 0.000482 | -0.0338 | CFL | Bldg | 2040 | 0.5 | 2010 | 0.482 | 0.846 | 1 | -0.0168
CFLBldgPGESCnExCZ02 | Com-Iltg-dWatt-CFL_OSbldg | PGE | SCn | Ex | CZ02 | 2.04 | 0.0005 | 0 | 1.95 | 0.000624 | -0.0182 | 2.01 | 0.000482 | 0 | 1.92 | 0.000601 | -0.0179 | CFL | Bldg | 2040 | 0.5 | 2010 | 0.482 | 0.955 | 1.25 | -0.00891
CFLBldgPGESCnExCZ03 | Com-Iltg-dWatt-CFL_OSbldg | PGE | SCn | Ex | CZ03 | 2.04 | 0.0005 | 0 | 1.89 | 0.00066 | -0.0199 | 2.01 | 0.000482 | 0 | 1.86 | 0.000636 | -0.0196 | CFL | Bldg | 2040 | 0.5 | 2010 | 0.482 | 0.925 | 1.32 | -0.00975
CFLBldgPGESCnExCZ04 | Com-Iltg-dWatt-CFL_OSbldg | PGE | SCn | Ex | CZ04 | 2.04 | 0.0005 | 0 | 2 | 0.000624 | -0.0159 | 2.01 | 0.000482 | 0 | 1.97 | 0.000602 | -0.0157 | CFL | Bldg | 2040 | 0.5 | 2010 | 0.482 | 0.98 | 1.25 | -0.00781
CFLBldgSCGSCnExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCG | SCn | Ex | CZ05 | 2.04 | 0.0005 | 0 | 1.9 | 0.000626 | -0.0204 | 2.01 | 0.000482 | 0 | 1.87 | 0.000603 | -0.0201 | CFL | Bldg | 2040 | 0.5 | 2010 | 0.482 | 0.93 | 1.25 | -0.01
CFLBldgSCESCnExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | SCn | Ex | CZ05 | 2.04 | 0.0005 | 0 | 1.9 | 0.000626 | -0.0204 | 2.01 | 0.000482 | 0 | 1.87 | 0.000603 | -0.0201 | CFL | Bldg | 2040 | 0.5 | 2010 | 0.482 | 0.93 | 1.25 | -0.01
CFLBldgPGESCnExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | PGE | SCn | Ex | CZ05 | 2.04 | 0.0005 | 0 | 1.9 | 0.000626 | -0.0204 | 2.01 | 0.000482 | 0 | 1.87 | 0.000603 | -0.0201 | CFL | Bldg | 2040 | 0.5 | 2010 | 0.482 | 0.93 | 1.25 | -0.01
CFLBldgSDGSCnExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SDG | SCn | Ex | CZ06 | 2.04 | 0.0005 | 0 | 2.09 | 0.000642 | -0.0106 | 2.01 | 0.000482 | 0 | 2.06 | 0.00062 | -0.0105 | CFL | Bldg | 2040 | 0.5 | 2010 | 0.482 | 1.02 | 1.29 | -0.00522
CFLBldgSCGSCnExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCG | SCn | Ex | CZ06 | 2.04 | 0.0005 | 0 | 2.09 | 0.000643 | -0.0106 | 2.01 | 0.000482 | 0 | 2.06 | 0.00062 | -0.0105 | CFL | Bldg | 2040 | 0.5 | 2010 | 0.482 | 1.02 | 1.29 | -0.00522
CFLBldgSCESCnExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | SCn | Ex | CZ06 | 2.04 | 0.0005 | 0 | 2.09 | 0.000643 | -0.0106 | 2.01 | 0.000482 | 0 | 2.06 | 0.00062 | -0.0105 | CFL | Bldg | 2040 | 0.5 | 2010 | 0.482 | 1.02 | 1.29 | -0.00522
CFLBldgSDGSCnExCZ07 | Com-Iltg-dWatt-CFL_OSbldg | SDG | SCn | Ex | CZ07 | 2.04 | 0.0005 | 0 | 2.06 | 0.000646 | -0.00854 | 2.01 | 0.000482 | 0 | 2.03 | 0.000623 | -0.00842 | CFL | Bldg | 2040 | 0.5 | 2010 | 0.482 | 1.01 | 1.29 | -0.00419
CFLBldgSCESCnExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | SCn | Ex | CZ08 | 2.04 | 0.0005 | 0 | 2.13 | 0.000642 | -0.00909 | 2.01 | 0.000482 | 0 | 2.09 | 0.000619 | -0.00896 | CFL | Bldg | 2040 | 0.5 | 2010 | 0.482 | 1.04 | 1.28 | -0.00446
CFLBldgSCGSCnExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCG | SCn | Ex | CZ08 | 2.04 | 0.0005 | 0 | 2.13 | 0.000642 | -0.00909 | 2.01 | 0.000482 | 0 | 2.09 | 0.000619 | -0.00896 | CFL | Bldg | 2040 | 0.5 | 2010 | 0.482 | 1.04 | 1.28 | -0.00446
CFLBldgSDGSCnExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SDG | SCn | Ex | CZ08 | 2.04 | 0.0005 | 0 | 2.13 | 0.000641 | -0.00909 | 2.01 | 0.000482 | 0 | 2.09 | 0.000619 | -0.00896 | CFL | Bldg | 2040 | 0.5 | 2010 | 0.482 | 1.04 | 1.28 | -0.00446
CFLBldgSCGSCnExCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCG | SCn | Ex | CZ09 | 2.04 | 0.0005 | 0 | 2.13 | 0.000658 | -0.011 | 2.01 | 0.000482 | 0 | 2.1 | 0.000635 | -0.0108 | CFL | Bldg | 2040 | 0.5 | 2010 | 0.482 | 1.04 | 1.32 | -0.00537
CFLBldgSCESCnExCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | SCn | Ex | CZ09 | 2.04 | 0.0005 | 0 | 2.13 | 0.000658 | -0.011 | 2.01 | 0.000482 | 0 | 2.1 | 0.000635 | -0.0108 | CFL | Bldg | 2040 | 0.5 | 2010 | 0.482 | 1.04 | 1.32 | -0.00537
CFLBldgSCESCnExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | SCn | Ex | CZ10 | 2.03 | 0.000497 | 0 | 2.12 | 0.000646 | -0.0116 | 2.01 | 0.000482 | 0 | 2.1 | 0.000627 | -0.0114 | CFL | Bldg | 2030 | 0.497 | 2010 | 0.482 | 1.04 | 1.3 | -0.00567
CFLBldgSDGSCnExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SDG | SCn | Ex | CZ10 | 2.04 | 0.0005 | 0 | 2.13 | 0.000649 | -0.0116 | 2.01 | 0.000482 | 0 | 2.1 | 0.000627 | -0.0114 | CFL | Bldg | 2040 | 0.5 | 2010 | 0.482 | 1.04 | 1.3 | -0.00567
CFLBldgSCGSCnExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCG | SCn | Ex | CZ10 | 2.03 | 0.000497 | 0 | 2.12 | 0.000646 | -0.0116 | 2.01 | 0.000482 | 0 | 2.1 | 0.000627 | -0.0114 | CFL | Bldg | 2030 | 0.497 | 2010 | 0.482 | 1.04 | 1.3 | -0.00567
CFLBldgPGESCnExCZ11 | Com-Iltg-dWatt-CFL_OSbldg | PGE | SCn | Ex | CZ11 | 2.04 | 0.000499 | 0 | 2 | 0.000607 | -0.0169 | 2.01 | 0.000482 | 0 | 1.97 | 0.000586 | -0.0166 | CFL | Bldg | 2040 | 0.499 | 2010 | 0.482 | 0.98 | 1.22 | -0.00826
CFLBldgPGESCnExCZ12 | Com-Iltg-dWatt-CFL_OSbldg | PGE | SCn | Ex | CZ12 | 2.04 | 0.000499 | 0 | 2.01 | 0.000615 | -0.017 | 2.01 | 0.000482 | 0 | 1.98 | 0.000594 | -0.0167 | CFL | Bldg | 2040 | 0.499 | 2010 | 0.482 | 0.985 | 1.23 | -0.00831
CFLBldgPGESCnExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | PGE | SCn | Ex | CZ13 | 2.04 | 0.000499 | 0 | 2.08 | 0.000641 | -0.0157 | 2.01 | 0.000482 | 0 | 2.05 | 0.000619 | -0.0155 | CFL | Bldg | 2040 | 0.499 | 2010 | 0.482 | 1.02 | 1.28 | -0.00771
CFLBldgSCESCnExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | SCn | Ex | CZ13 | 2.04 | 0.000498 | 0 | 2.08 | 0.000639 | -0.0157 | 2.01 | 0.000482 | 0 | 2.05 | 0.000619 | -0.0155 | CFL | Bldg | 2040 | 0.498 | 2010 | 0.482 | 1.02 | 1.28 | -0.00771
CFLBldgSCGSCnExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCG | SCn | Ex | CZ13 | 2.04 | 0.000498 | 0 | 2.08 | 0.000639 | -0.0157 | 2.01 | 0.000482 | 0 | 2.05 | 0.000619 | -0.0155 | CFL | Bldg | 2040 | 0.498 | 2010 | 0.482 | 1.02 | 1.28 | -0.00771
CFLBldgSCGSCnExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCG | SCn | Ex | CZ14 | 2.04 | 0.000498 | 0 | 2.07 | 0.000636 | -0.0171 | 2.01 | 0.000482 | 0 | 2.04 | 0.000616 | -0.0169 | CFL | Bldg | 2040 | 0.498 | 2010 | 0.482 | 1.01 | 1.28 | -0.00841
CFLBldgSDGSCnExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SDG | SCn | Ex | CZ14 | 2.04 | 0.0005 | 0 | 2.07 | 0.000638 | -0.0171 | 2.01 | 0.000482 | 0 | 2.04 | 0.000616 | -0.0169 | CFL | Bldg | 2040 | 0.5 | 2010 | 0.482 | 1.01 | 1.28 | -0.00841
CFLBldgSCESCnExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | SCn | Ex | CZ14 | 2.04 | 0.000498 | 0 | 2.07 | 0.000636 | -0.0171 | 2.01 | 0.000482 | 0 | 2.04 | 0.000616 | -0.0169 | CFL | Bldg | 2040 | 0.498 | 2010 | 0.482 | 1.01 | 1.28 | -0.00841
CFLBldgSDGSCnExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SDG | SCn | Ex | CZ15 | 2.04 | 0.0005 | 0 | 2.28 | 0.000638 | -0.00481 | 2.01 | 0.000482 | 0 | 2.25 | 0.000616 | -0.00474 | CFL | Bldg | 2040 | 0.5 | 2010 | 0.482 | 1.12 | 1.28 | -0.00236
CFLBldgSCESCnExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | SCn | Ex | CZ15 | 2.03 | 0.000497 | 0 | 2.27 | 0.000635 | -0.0048 | 2.01 | 0.000482 | 0 | 2.25 | 0.000616 | -0.00474 | CFL | Bldg | 2030 | 0.497 | 2010 | 0.482 | 1.12 | 1.28 | -0.00236
CFLBldgSCGSCnExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCG | SCn | Ex | CZ15 | 2.03 | 0.000497 | 0 | 2.27 | 0.000635 | -0.0048 | 2.01 | 0.000482 | 0 | 2.25 | 0.000616 | -0.00474 | CFL | Bldg | 2030 | 0.497 | 2010 | 0.482 | 1.12 | 1.28 | -0.00236
CFLBldgPGESCnExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | PGE | SCn | Ex | CZ16 | 2.04 | 0.000499 | 0 | 1.86 | 0.000623 | -0.0249 | 2.01 | 0.000482 | 0 | 1.84 | 0.000601 | -0.0245 | CFL | Bldg | 2040 | 0.499 | 2010 | 0.482 | 0.915 | 1.25 | -0.0122
CFLBldgSCESCnExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | SCn | Ex | CZ16 | 2.03 | 0.000497 | 0 | 1.86 | 0.00062 | -0.0248 | 2.01 | 0.000482 | 0 | 1.84 | 0.000601 | -0.0245 | CFL | Bldg | 2030 | 0.497 | 2010 | 0.482 | 0.915 | 1.25 | -0.0122
CFLBldgSCGSCnExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCG | SCn | Ex | CZ16 | 2.03 | 0.000497 | 0 | 1.86 | 0.00062 | -0.0248 | 2.01 | 0.000482 | 0 | 1.84 | 0.000601 | -0.0245 | CFL | Bldg | 2030 | 0.497 | 2010 | 0.482 | 0.915 | 1.25 | -0.0122
CFLBldgSDGSCnExIOU | Com-Iltg-dWatt-CFL_OSbldg | SDG | SCn | Ex | IOU | 2.04 | 0.0005 | 0 | 2.08 | 0.000647 | -0.00953 | 2.01 | 0.000482 | 0 | 2.05 | 0.000624 | -0.00939 | CFL | Bldg | 2040 | 0.5 | 2010 | 0.482 | 1.02 | 1.29 | -0.00467
CFLBldgPGESCnExIOU | Com-Iltg-dWatt-CFL_OSbldg | PGE | SCn | Ex | IOU | 2.04 | 0.0005 | 0 | 1.97 | 0.000634 | -0.018 | 2.01 | 0.000482 | 0 | 1.94 | 0.000612 | -0.0177 | CFL | Bldg | 2040 | 0.5 | 2010 | 0.482 | 0.965 | 1.27 | -0.00881
CFLBldgSCGSCnExIOU | Com-Iltg-dWatt-CFL_OSbldg | SCG | SCn | Ex | IOU | 2.04 | 0.000499 | 0 | 2.12 | 0.000647 | -0.0105 | 2.01 | 0.000482 | 0 | 2.09 | 0.000625 | -0.0104 | CFL | Bldg | 2040 | 0.499 | 2010 | 0.482 | 1.04 | 1.3 | -0.00517
CFLBldgSCESCnExIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | SCn | Ex | IOU | 2.04 | 0.000499 | 0 | 2.12 | 0.000645 | -0.0105 | 2.01 | 0.000482 | 0 | 2.09 | 0.000623 | -0.0104 | CFL | Bldg | 2040 | 0.499 | 2010 | 0.482 | 1.04 | 1.29 | -0.00517
CFLBldgPGESCnNewCZ01 | Com-Iltg-dWatt-CFL_OSbldg | PGE | SCn | New | CZ01 | 2.01 | 0.000482 | 0 | 1.72 | 0.000482 | -0.0364 | 2.01 | 0.000482 | 0 | 1.72 | 0.000482 | -0.0364 | CFL | Bldg | 2010 | 0.482 | 2010 | 0.482 | 0.856 | 1 | -0.0181
CFLBldgPGESCnNewCZ02 | Com-Iltg-dWatt-CFL_OSbldg | PGE | SCn | New | CZ02 | 2.01 | 0.000482 | 0 | 1.92 | 0.000584 | -0.019 | 2.01 | 0.000482 | 0 | 1.92 | 0.000584 | -0.019 | CFL | Bldg | 2010 | 0.482 | 2010 | 0.482 | 0.955 | 1.21 | -0.00945
CFLBldgPGESCnNewCZ03 | Com-Iltg-dWatt-CFL_OSbldg | PGE | SCn | New | CZ03 | 2.01 | 0.000482 | 0 | 1.86 | 0.000603 | -0.0213 | 2.01 | 0.000482 | 0 | 1.86 | 0.000603 | -0.0213 | CFL | Bldg | 2010 | 0.482 | 2010 | 0.482 | 0.925 | 1.25 | -0.0106
CFLBldgPGESCnNewCZ04 | Com-Iltg-dWatt-CFL_OSbldg | PGE | SCn | New | CZ04 | 2.01 | 0.000482 | 0 | 1.96 | 0.000579 | -0.0169 | 2.01 | 0.000482 | 0 | 1.96 | 0.000579 | -0.0169 | CFL | Bldg | 2010 | 0.482 | 2010 | 0.482 | 0.975 | 1.2 | -0.00841
CFLBldgSCESCnNewCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | SCn | New | CZ05 | 2.01 | 0.000482 | 0 | 1.87 | 0.000605 | -0.0221 | 2.01 | 0.000482 | 0 | 1.87 | 0.000605 | -0.0221 | CFL | Bldg | 2010 | 0.482 | 2010 | 0.482 | 0.93 | 1.26 | -0.011
CFLBldgPGESCnNewCZ05 | Com-Iltg-dWatt-CFL_OSbldg | PGE | SCn | New | CZ05 | 2.01 | 0.000482 | 0 | 1.84 | 0.000576 | -0.0215 | 2.01 | 0.000482 | 0 | 1.84 | 0.000576 | -0.0215 | CFL | Bldg | 2010 | 0.482 | 2010 | 0.482 | 0.915 | 1.2 | -0.0107
CFLBldgSCESCnNewCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | SCn | New | CZ06 | 2.01 | 0.000482 | 0 | 2.01 | 0.00058 | -0.0118 | 2.01 | 0.000482 | 0 | 2.01 | 0.00058 | -0.0118 | CFL | Bldg | 2010 | 0.482 | 2010 | 0.482 | 1 | 1.2 | -0.00587
CFLBldgSDGSCnNewCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SDG | SCn | New | CZ06 | 2.01 | 0.000482 | 0 | 2.01 | 0.000577 | -0.0119 | 2.01 | 0.000482 | 0 | 2.01 | 0.000577 | -0.0119 | CFL | Bldg | 2010 | 0.482 | 2010 | 0.482 | 1 | 1.2 | -0.00592
CFLBldgSDGSCnNewCZ07 | Com-Iltg-dWatt-CFL_OSbldg | SDG | SCn | New | CZ07 | 2.01 | 0.000482 | 0 | 2 | 0.000589 | -0.00983 | 2.01 | 0.000482 | 0 | 2 | 0.000589 | -0.00983 | CFL | Bldg | 2010 | 0.482 | 2010 | 0.482 | 0.995 | 1.22 | -0.00489
CFLBldgSDGSCnNewCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SDG | SCn | New | CZ08 | 2.01 | 0.000482 | 0 | 2.05 | 0.000586 | -0.0103 | 2.01 | 0.000482 | 0 | 2.05 | 0.000586 | -0.0103 | CFL | Bldg | 2010 | 0.482 | 2010 | 0.482 | 1.02 | 1.22 | -0.00512
CFLBldgSCESCnNewCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | SCn | New | CZ08 | 2.01 | 0.000482 | 0 | 2.06 | 0.000588 | -0.0102 | 2.01 | 0.000482 | 0 | 2.06 | 0.000588 | -0.0102 | CFL | Bldg | 2010 | 0.482 | 2010 | 0.482 | 1.02 | 1.22 | -0.00507
CFLBldgSCESCnNewCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | SCn | New | CZ09 | 2.01 | 0.000482 | 0 | 2.06 | 0.000608 | -0.011 | 2.01 | 0.000482 | 0 | 2.06 | 0.000608 | -0.011 | CFL | Bldg | 2010 | 0.482 | 2010 | 0.482 | 1.02 | 1.26 | -0.00547
CFLBldgSCESCnNewCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | SCn | New | CZ10 | 2.01 | 0.000482 | 0 | 2.07 | 0.000603 | -0.012 | 2.01 | 0.000482 | 0 | 2.07 | 0.000603 | -0.012 | CFL | Bldg | 2010 | 0.482 | 2010 | 0.482 | 1.03 | 1.25 | -0.00597
CFLBldgSDGSCnNewCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SDG | SCn | New | CZ10 | 2.01 | 0.000482 | 0 | 2.06 | 0.0006 | -0.0121 | 2.01 | 0.000482 | 0 | 2.06 | 0.0006 | -0.0121 | CFL | Bldg | 2010 | 0.482 | 2010 | 0.482 | 1.02 | 1.24 | -0.00602
CFLBldgPGESCnNewCZ11 | Com-Iltg-dWatt-CFL_OSbldg | PGE | SCn | New | CZ11 | 2.01 | 0.000482 | 0 | 1.96 | 0.000573 | -0.0174 | 2.01 | 0.000482 | 0 | 1.96 | 0.000573 | -0.0174 | CFL | Bldg | 2010 | 0.482 | 2010 | 0.482 | 0.975 | 1.19 | -0.00866
CFLBldgPGESCnNewCZ12 | Com-Iltg-dWatt-CFL_OSbldg | PGE | SCn | New | CZ12 | 2.01 | 0.000482 | 0 | 1.96 | 0.000576 | -0.0176 | 2.01 | 0.000482 | 0 | 1.96 | 0.000576 | -0.0176 | CFL | Bldg | 2010 | 0.482 | 2010 | 0.482 | 0.975 | 1.2 | -0.00876
CFLBldgSCESCnNewCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | SCn | New | CZ13 | 2.01 | 0.000482 | 0 | 2.01 | 0.000587 | -0.0158 | 2.01 | 0.000482 | 0 | 2.01 | 0.000587 | -0.0158 | CFL | Bldg | 2010 | 0.482 | 2010 | 0.482 | 1 | 1.22 | -0.00786
CFLBldgPGESCnNewCZ13 | Com-Iltg-dWatt-CFL_OSbldg | PGE | SCn | New | CZ13 | 2.01 | 0.000482 | 0 | 1.95 | 0.000561 | -0.0153 | 2.01 | 0.000482 | 0 | 1.95 | 0.000561 | -0.0153 | CFL | Bldg | 2010 | 0.482 | 2010 | 0.482 | 0.97 | 1.16 | -0.00761
CFLBldgSCESCnNewCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | SCn | New | CZ14 | 2.01 | 0.000482 | 0 | 2.03 | 0.0006 | -0.0177 | 2.01 | 0.000482 | 0 | 2.03 | 0.0006 | -0.0177 | CFL | Bldg | 2010 | 0.482 | 2010 | 0.482 | 1.01 | 1.24 | -0.00881
CFLBldgSDGSCnNewCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SDG | SCn | New | CZ14 | 2.01 | 0.000482 | 0 | 2.02 | 0.000597 | -0.0178 | 2.01 | 0.000482 | 0 | 2.02 | 0.000597 | -0.0178 | CFL | Bldg | 2010 | 0.482 | 2010 | 0.482 | 1 | 1.24 | -0.00886
CFLBldgSCESCnNewCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | SCn | New | CZ15 | 2.01 | 0.000482 | 0 | 2.19 | 0.000605 | -0.00374 | 2.01 | 0.000482 | 0 | 2.19 | 0.000605 | -0.00374 | CFL | Bldg | 2010 | 0.482 | 2010 | 0.482 | 1.09 | 1.26 | -0.00186
CFLBldgSDGSCnNewCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SDG | SCn | New | CZ15 | 2.01 | 0.000482 | 0 | 2.19 | 0.000602 | -0.00376 | 2.01 | 0.000482 | 0 | 2.19 | 0.000602 | -0.00376 | CFL | Bldg | 2010 | 0.482 | 2010 | 0.482 | 1.09 | 1.25 | -0.00187
CFLBldgSCESCnNewCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | SCn | New | CZ16 | 2.01 | 0.000482 | 0 | 1.82 | 0.00058 | -0.0255 | 2.01 | 0.000482 | 0 | 1.82 | 0.00058 | -0.0255 | CFL | Bldg | 2010 | 0.482 | 2010 | 0.482 | 0.905 | 1.2 | -0.0127
CFLBldgPGESCnNewCZ16 | Com-Iltg-dWatt-CFL_OSbldg | PGE | SCn | New | CZ16 | 2.01 | 0.000482 | 0 | 1.78 | 0.000557 | -0.0247 | 2.01 | 0.000482 | 0 | 1.78 | 0.000557 | -0.0247 | CFL | Bldg | 2010 | 0.482 | 2010 | 0.482 | 0.886 | 1.16 | -0.0123
CFLBldgSDGSCnNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SDG | SCn | New | IOU | 2.01 | 0.000482 | 0 | 2.02 | 0.000592 | -0.0106 | 2.01 | 0.000482 | 0 | 2.02 | 0.000592 | -0.0106 | CFL | Bldg | 2010 | 0.482 | 2010 | 0.482 | 1 | 1.23 | -0.00527
CFLBldgPGESCnNewIOU | Com-Iltg-dWatt-CFL_OSbldg | PGE | SCn | New | IOU | 2.01 | 0.000482 | 0 | 2 | 0.000587 | -0.0164 | 2.01 | 0.000482 | 0 | 2 | 0.000587 | -0.0164 | CFL | Bldg | 2010 | 0.482 | 2010 | 0.482 | 0.995 | 1.22 | -0.00816
CFLBldgSCESCnNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | SCn | New | IOU | 2.01 | 0.000482 | 0 | 2.06 | 0.000595 | -0.0117 | 2.01 | 0.000482 | 0 | 2.06 | 0.000595 | -0.0117 | CFL | Bldg | 2010 | 0.482 | 2010 | 0.482 | 1.02 | 1.23 | -0.00582
CFLBldgSCGSCnNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SCG | SCn | New | IOU | 2.01 | 0.000482 | 0 | 2.05 | 0.000595 | -0.0116 | 2.01 | 0.000482 | 0 | 2.05 | 0.000595 | -0.0116 | CFL | Bldg | 2010 | 0.482 | 2010 | 0.482 | 1.02 | 1.23 | -0.00577
CFLBldgPGESUnExCZ01 | Com-Iltg-dWatt-CFL_OSbldg | PGE | SUn | Ex | CZ01 | 1.36 | 0.000239 | 0 | 1.36 | 0.000239 | 0 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | CFL | Bldg | 1360 | 0.239 | 1340 | 0.231 | 1 | 1 | 0
CFLBldgPGESUnExCZ02 | Com-Iltg-dWatt-CFL_OSbldg | PGE | SUn | Ex | CZ02 | 1.36 | 0.00024 | 0 | 1.36 | 0.00024 | 0 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | CFL | Bldg | 1360 | 0.24 | 1340 | 0.231 | 1 | 1 | 0
CFLBldgPGESUnExCZ03 | Com-Iltg-dWatt-CFL_OSbldg | PGE | SUn | Ex | CZ03 | 1.36 | 0.00024 | 0 | 1.36 | 0.00024 | 0 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | CFL | Bldg | 1360 | 0.24 | 1340 | 0.231 | 1 | 1 | 0
CFLBldgPGESUnExCZ04 | Com-Iltg-dWatt-CFL_OSbldg | PGE | SUn | Ex | CZ04 | 1.36 | 0.00024 | 0 | 1.36 | 0.00024 | 0 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | CFL | Bldg | 1360 | 0.24 | 1340 | 0.231 | 1 | 1 | 0
CFLBldgSCESUnExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | SUn | Ex | CZ05 | 1.36 | 0.000239 | 0 | 1.36 | 0.000239 | 0 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | CFL | Bldg | 1360 | 0.239 | 1340 | 0.231 | 1 | 1 | 0
CFLBldgSCGSUnExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCG | SUn | Ex | CZ05 | 1.36 | 0.000239 | 0 | 1.36 | 0.000239 | 0 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | CFL | Bldg | 1360 | 0.239 | 1340 | 0.231 | 1 | 1 | 0
CFLBldgPGESUnExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | PGE | SUn | Ex | CZ05 | 1.36 | 0.00024 | 0 | 1.36 | 0.00024 | 0 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | CFL | Bldg | 1360 | 0.24 | 1340 | 0.231 | 1 | 1 | 0
CFLBldgSCGSUnExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCG | SUn | Ex | CZ06 | 1.36 | 0.000239 | 0 | 1.36 | 0.000239 | 0 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | CFL | Bldg | 1360 | 0.239 | 1340 | 0.231 | 1 | 1 | 0
CFLBldgSDGSUnExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SDG | SUn | Ex | CZ06 | 1.36 | 0.000239 | 0 | 1.36 | 0.000239 | 0 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | CFL | Bldg | 1360 | 0.239 | 1340 | 0.231 | 1 | 1 | 0
CFLBldgSCESUnExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | SUn | Ex | CZ06 | 1.36 | 0.000239 | 0 | 1.36 | 0.000239 | 0 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | CFL | Bldg | 1360 | 0.239 | 1340 | 0.231 | 1 | 1 | 0
CFLBldgSDGSUnExCZ07 | Com-Iltg-dWatt-CFL_OSbldg | SDG | SUn | Ex | CZ07 | 1.36 | 0.000239 | 0 | 1.36 | 0.000239 | 0 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | CFL | Bldg | 1360 | 0.239 | 1340 | 0.231 | 1 | 1 | 0
CFLBldgSCGSUnExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCG | SUn | Ex | CZ08 | 1.36 | 0.000239 | 0 | 1.36 | 0.000239 | 0 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | CFL | Bldg | 1360 | 0.239 | 1340 | 0.231 | 1 | 1 | 0
CFLBldgSDGSUnExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SDG | SUn | Ex | CZ08 | 1.36 | 0.000239 | 0 | 1.36 | 0.000239 | 0 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | CFL | Bldg | 1360 | 0.239 | 1340 | 0.231 | 1 | 1 | 0
CFLBldgSCESUnExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | SUn | Ex | CZ08 | 1.36 | 0.000239 | 0 | 1.36 | 0.000239 | 0 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | CFL | Bldg | 1360 | 0.239 | 1340 | 0.231 | 1 | 1 | 0
CFLBldgSCGSUnExCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCG | SUn | Ex | CZ09 | 1.36 | 0.000239 | 0 | 1.36 | 0.000239 | 0 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | CFL | Bldg | 1360 | 0.239 | 1340 | 0.231 | 1 | 1 | 0
CFLBldgSCESUnExCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | SUn | Ex | CZ09 | 1.36 | 0.000239 | 0 | 1.36 | 0.000239 | 0 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | CFL | Bldg | 1360 | 0.239 | 1340 | 0.231 | 1 | 1 | 0
CFLBldgSDGSUnExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SDG | SUn | Ex | CZ10 | 1.36 | 0.000239 | 0 | 1.36 | 0.000239 | 0 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | CFL | Bldg | 1360 | 0.239 | 1340 | 0.231 | 1 | 1 | 0
CFLBldgSCGSUnExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCG | SUn | Ex | CZ10 | 1.36 | 0.000238 | 0 | 1.36 | 0.000238 | 0 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | CFL | Bldg | 1360 | 0.238 | 1340 | 0.231 | 1 | 1 | 0
CFLBldgSCESUnExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | SUn | Ex | CZ10 | 1.36 | 0.000238 | 0 | 1.36 | 0.000238 | 0 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | CFL | Bldg | 1360 | 0.238 | 1340 | 0.231 | 1 | 1 | 0
CFLBldgPGESUnExCZ11 | Com-Iltg-dWatt-CFL_OSbldg | PGE | SUn | Ex | CZ11 | 1.36 | 0.000239 | 0 | 1.36 | 0.000239 | 0 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | CFL | Bldg | 1360 | 0.239 | 1340 | 0.231 | 1 | 1 | 0
CFLBldgPGESUnExCZ12 | Com-Iltg-dWatt-CFL_OSbldg | PGE | SUn | Ex | CZ12 | 1.36 | 0.000239 | 0 | 1.36 | 0.000239 | 0 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | CFL | Bldg | 1360 | 0.239 | 1340 | 0.231 | 1 | 1 | 0
CFLBldgPGESUnExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | PGE | SUn | Ex | CZ13 | 1.36 | 0.000239 | 0 | 1.36 | 0.000239 | 0 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | CFL | Bldg | 1360 | 0.239 | 1340 | 0.231 | 1 | 1 | 0
CFLBldgSCGSUnExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCG | SUn | Ex | CZ13 | 1.36 | 0.000239 | 0 | 1.36 | 0.000239 | 0 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | CFL | Bldg | 1360 | 0.239 | 1340 | 0.231 | 1 | 1 | 0
CFLBldgSCESUnExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | SUn | Ex | CZ13 | 1.36 | 0.000239 | 0 | 1.36 | 0.000239 | 0 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | CFL | Bldg | 1360 | 0.239 | 1340 | 0.231 | 1 | 1 | 0
CFLBldgSDGSUnExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SDG | SUn | Ex | CZ14 | 1.36 | 0.000239 | 0 | 1.36 | 0.000239 | 0 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | CFL | Bldg | 1360 | 0.239 | 1340 | 0.231 | 1 | 1 | 0
CFLBldgSCESUnExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | SUn | Ex | CZ14 | 1.36 | 0.000239 | 0 | 1.36 | 0.000239 | 0 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | CFL | Bldg | 1360 | 0.239 | 1340 | 0.231 | 1 | 1 | 0
CFLBldgSCGSUnExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCG | SUn | Ex | CZ14 | 1.36 | 0.000239 | 0 | 1.36 | 0.000239 | 0 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | CFL | Bldg | 1360 | 0.239 | 1340 | 0.231 | 1 | 1 | 0
CFLBldgSDGSUnExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SDG | SUn | Ex | CZ15 | 1.36 | 0.000239 | 0 | 1.36 | 0.000239 | 0 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | CFL | Bldg | 1360 | 0.239 | 1340 | 0.231 | 1 | 1 | 0
CFLBldgSCESUnExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | SUn | Ex | CZ15 | 1.36 | 0.000238 | 0 | 1.36 | 0.000238 | 0 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | CFL | Bldg | 1360 | 0.238 | 1340 | 0.231 | 1 | 1 | 0
CFLBldgSCGSUnExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCG | SUn | Ex | CZ15 | 1.36 | 0.000238 | 0 | 1.36 | 0.000238 | 0 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | CFL | Bldg | 1360 | 0.238 | 1340 | 0.231 | 1 | 1 | 0
CFLBldgSCGSUnExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCG | SUn | Ex | CZ16 | 1.36 | 0.000238 | 0 | 1.36 | 0.000238 | 0 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | CFL | Bldg | 1360 | 0.238 | 1340 | 0.231 | 1 | 1 | 0
CFLBldgSCESUnExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | SUn | Ex | CZ16 | 1.36 | 0.000238 | 0 | 1.36 | 0.000238 | 0 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | CFL | Bldg | 1360 | 0.238 | 1340 | 0.231 | 1 | 1 | 0
CFLBldgPGESUnExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | PGE | SUn | Ex | CZ16 | 1.36 | 0.000239 | 0 | 1.36 | 0.000239 | 0 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | CFL | Bldg | 1360 | 0.239 | 1340 | 0.231 | 1 | 1 | 0
CFLBldgSDGSUnExIOU | Com-Iltg-dWatt-CFL_OSbldg | SDG | SUn | Ex | IOU | 1.36 | 0.000239 | 0 | 1.36 | 0.000239 | 0 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | CFL | Bldg | 1360 | 0.239 | 1340 | 0.231 | 1 | 1 | 0
CFLBldgPGESUnExIOU | Com-Iltg-dWatt-CFL_OSbldg | PGE | SUn | Ex | IOU | 1.36 | 0.000239 | 0 | 1.36 | 0.000239 | 0 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | CFL | Bldg | 1360 | 0.239 | 1340 | 0.231 | 1 | 1 | 0
CFLBldgSCGSUnExIOU | Com-Iltg-dWatt-CFL_OSbldg | SCG | SUn | Ex | IOU | 1.36 | 0.000239 | 0 | 1.36 | 0.000239 | 0 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | CFL | Bldg | 1360 | 0.239 | 1340 | 0.231 | 1 | 1 | 0
CFLBldgSCESUnExIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | SUn | Ex | IOU | 1.36 | 0.000239 | 0 | 1.36 | 0.000239 | 0 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | CFL | Bldg | 1360 | 0.239 | 1340 | 0.231 | 1 | 1 | 0
CFLBldgPGESUnNewCZ01 | Com-Iltg-dWatt-CFL_OSbldg | PGE | SUn | New | CZ01 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | CFL | Bldg | 1340 | 0.231 | 1340 | 0.231 | 1 | 1 | 0
CFLBldgPGESUnNewCZ02 | Com-Iltg-dWatt-CFL_OSbldg | PGE | SUn | New | CZ02 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | CFL | Bldg | 1340 | 0.231 | 1340 | 0.231 | 1 | 1 | 0
CFLBldgPGESUnNewCZ03 | Com-Iltg-dWatt-CFL_OSbldg | PGE | SUn | New | CZ03 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | CFL | Bldg | 1340 | 0.231 | 1340 | 0.231 | 1 | 1 | 0
CFLBldgPGESUnNewCZ04 | Com-Iltg-dWatt-CFL_OSbldg | PGE | SUn | New | CZ04 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | CFL | Bldg | 1340 | 0.231 | 1340 | 0.231 | 1 | 1 | 0
CFLBldgSCESUnNewCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | SUn | New | CZ05 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | CFL | Bldg | 1340 | 0.231 | 1340 | 0.231 | 1 | 1 | 0
CFLBldgPGESUnNewCZ05 | Com-Iltg-dWatt-CFL_OSbldg | PGE | SUn | New | CZ05 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | CFL | Bldg | 1340 | 0.231 | 1340 | 0.231 | 1 | 1 | 0
CFLBldgSDGSUnNewCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SDG | SUn | New | CZ06 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | CFL | Bldg | 1340 | 0.231 | 1340 | 0.231 | 1 | 1 | 0
CFLBldgSCESUnNewCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | SUn | New | CZ06 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | CFL | Bldg | 1340 | 0.231 | 1340 | 0.231 | 1 | 1 | 0
CFLBldgSDGSUnNewCZ07 | Com-Iltg-dWatt-CFL_OSbldg | SDG | SUn | New | CZ07 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | CFL | Bldg | 1340 | 0.231 | 1340 | 0.231 | 1 | 1 | 0
CFLBldgSCESUnNewCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | SUn | New | CZ08 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | CFL | Bldg | 1340 | 0.231 | 1340 | 0.231 | 1 | 1 | 0
CFLBldgSDGSUnNewCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SDG | SUn | New | CZ08 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | CFL | Bldg | 1340 | 0.231 | 1340 | 0.231 | 1 | 1 | 0
CFLBldgSCESUnNewCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | SUn | New | CZ09 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | CFL | Bldg | 1340 | 0.231 | 1340 | 0.231 | 1 | 1 | 0
CFLBldgSCESUnNewCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | SUn | New | CZ10 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | CFL | Bldg | 1340 | 0.231 | 1340 | 0.231 | 1 | 1 | 0
CFLBldgSDGSUnNewCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SDG | SUn | New | CZ10 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | CFL | Bldg | 1340 | 0.231 | 1340 | 0.231 | 1 | 1 | 0
CFLBldgPGESUnNewCZ11 | Com-Iltg-dWatt-CFL_OSbldg | PGE | SUn | New | CZ11 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | CFL | Bldg | 1340 | 0.231 | 1340 | 0.231 | 1 | 1 | 0
CFLBldgPGESUnNewCZ12 | Com-Iltg-dWatt-CFL_OSbldg | PGE | SUn | New | CZ12 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | CFL | Bldg | 1340 | 0.231 | 1340 | 0.231 | 1 | 1 | 0
CFLBldgSCESUnNewCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | SUn | New | CZ13 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | CFL | Bldg | 1340 | 0.231 | 1340 | 0.231 | 1 | 1 | 0
CFLBldgPGESUnNewCZ13 | Com-Iltg-dWatt-CFL_OSbldg | PGE | SUn | New | CZ13 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | CFL | Bldg | 1340 | 0.231 | 1340 | 0.231 | 1 | 1 | 0
CFLBldgSCESUnNewCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | SUn | New | CZ14 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | CFL | Bldg | 1340 | 0.231 | 1340 | 0.231 | 1 | 1 | 0
CFLBldgSDGSUnNewCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SDG | SUn | New | CZ14 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | CFL | Bldg | 1340 | 0.231 | 1340 | 0.231 | 1 | 1 | 0
CFLBldgSCESUnNewCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | SUn | New | CZ15 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | CFL | Bldg | 1340 | 0.231 | 1340 | 0.231 | 1 | 1 | 0
CFLBldgSDGSUnNewCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SDG | SUn | New | CZ15 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | CFL | Bldg | 1340 | 0.231 | 1340 | 0.231 | 1 | 1 | 0
CFLBldgPGESUnNewCZ16 | Com-Iltg-dWatt-CFL_OSbldg | PGE | SUn | New | CZ16 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | CFL | Bldg | 1340 | 0.231 | 1340 | 0.231 | 1 | 1 | 0
CFLBldgSCESUnNewCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | SUn | New | CZ16 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | CFL | Bldg | 1340 | 0.231 | 1340 | 0.231 | 1 | 1 | 0
CFLBldgSCGSUnNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SCG | SUn | New | IOU | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | CFL | Bldg | 1340 | 0.231 | 1340 | 0.231 | 1 | 1 | 0
CFLBldgSDGSUnNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SDG | SUn | New | IOU | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | CFL | Bldg | 1340 | 0.231 | 1340 | 0.231 | 1 | 1 | 0
CFLBldgSCESUnNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | SUn | New | IOU | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | CFL | Bldg | 1340 | 0.231 | 1340 | 0.231 | 1 | 1 | 0
CFLBldgPGESUnNewIOU | Com-Iltg-dWatt-CFL_OSbldg | PGE | SUn | New | IOU | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | 1.34 | 0.000231 | 0 | CFL | Bldg | 1340 | 0.231 | 1340 | 0.231 | 1 | 1 | 0
CFLBldgPGEWRfExCZ01 | Com-Iltg-dWatt-CFL_OSbldg | PGE | WRf | Ex | CZ01 | 4.77 | 0.000573 | 0 | 7.62 | 0.000809 | 0 | 4.64 | 0.00055 | 0 | 7.41 | 0.000775 | 0 | CFL | Bldg | 4770 | 0.573 | 4640 | 0.55 | 1.6 | 1.41 | 0
CFLBldgPGEWRfExCZ02 | Com-Iltg-dWatt-CFL_OSbldg | PGE | WRf | Ex | CZ02 | 4.77 | 0.000574 | 0 | 7.74 | 0.000728 | 0 | 4.64 | 0.00055 | 0 | 7.52 | 0.000698 | 0 | CFL | Bldg | 4770 | 0.574 | 4640 | 0.55 | 1.62 | 1.27 | 0
CFLBldgPGEWRfExCZ03 | Com-Iltg-dWatt-CFL_OSbldg | PGE | WRf | Ex | CZ03 | 4.77 | 0.000574 | 0 | 7.72 | 0.000759 | 0 | 4.64 | 0.00055 | 0 | 7.5 | 0.000728 | 0 | CFL | Bldg | 4770 | 0.574 | 4640 | 0.55 | 1.62 | 1.32 | 0
CFLBldgPGEWRfExCZ04 | Com-Iltg-dWatt-CFL_OSbldg | PGE | WRf | Ex | CZ04 | 4.77 | 0.000574 | 0 | 7.73 | 0.000732 | 0 | 4.64 | 0.00055 | 0 | 7.52 | 0.000702 | 0 | CFL | Bldg | 4770 | 0.574 | 4640 | 0.55 | 1.62 | 1.28 | 0
CFLBldgPGEWRfExCZ05 | Com-Iltg-dWatt-CFL_OSbldg | PGE | WRf | Ex | CZ05 | 4.77 | 0.000574 | 0 | 7.3 | 0.000881 | 0 | 4.64 | 0.00055 | 0 | 7.09 | 0.000844 | 0 | CFL | Bldg | 4770 | 0.574 | 4640 | 0.55 | 1.53 | 1.53 | 0
CFLBldgSDGWRfExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SDG | WRf | Ex | CZ06 | 4.77 | 0.000573 | 0 | 7.5 | 0.000718 | 0 | 4.64 | 0.00055 | 0 | 7.3 | 0.00069 | 0 | CFL | Bldg | 4770 | 0.573 | 4640 | 0.55 | 1.57 | 1.25 | 0
CFLBldgSCEWRfExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | WRf | Ex | CZ06 | 4.77 | 0.000573 | 0 | 7.5 | 0.000719 | 0 | 4.64 | 0.00055 | 0 | 7.3 | 0.00069 | 0 | CFL | Bldg | 4770 | 0.573 | 4640 | 0.55 | 1.57 | 1.25 | 0
CFLBldgSCGWRfExCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCG | WRf | Ex | CZ06 | 4.77 | 0.000573 | 0 | 7.5 | 0.000719 | 0 | 4.64 | 0.00055 | 0 | 7.3 | 0.00069 | 0 | CFL | Bldg | 4770 | 0.573 | 4640 | 0.55 | 1.57 | 1.25 | 0
CFLBldgSDGWRfExCZ07 | Com-Iltg-dWatt-CFL_OSbldg | SDG | WRf | Ex | CZ07 | 4.77 | 0.000573 | 0 | 7.46 | 0.000719 | 0 | 4.64 | 0.00055 | 0 | 7.26 | 0.00069 | 0 | CFL | Bldg | 4770 | 0.573 | 4640 | 0.55 | 1.56 | 1.25 | 0
CFLBldgSCGWRfExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCG | WRf | Ex | CZ08 | 4.77 | 0.000573 | 0 | 7.44 | 0.000715 | 0 | 4.64 | 0.00055 | 0 | 7.24 | 0.000686 | 0 | CFL | Bldg | 4770 | 0.573 | 4640 | 0.55 | 1.56 | 1.25 | 0
CFLBldgSCEWRfExCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | WRf | Ex | CZ08 | 4.77 | 0.000573 | 0 | 7.44 | 0.000715 | 0 | 4.64 | 0.00055 | 0 | 7.24 | 0.000686 | 0 | CFL | Bldg | 4770 | 0.573 | 4640 | 0.55 | 1.56 | 1.25 | 0
CFLBldgSCGWRfExCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCG | WRf | Ex | CZ09 | 4.77 | 0.000573 | 0 | 7.63 | 0.000739 | 0 | 4.64 | 0.00055 | 0 | 7.42 | 0.000708 | 0 | CFL | Bldg | 4770 | 0.573 | 4640 | 0.55 | 1.6 | 1.29 | 0
CFLBldgSCEWRfExCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | WRf | Ex | CZ09 | 4.77 | 0.000573 | 0 | 7.63 | 0.000739 | 0 | 4.64 | 0.00055 | 0 | 7.42 | 0.000708 | 0 | CFL | Bldg | 4770 | 0.573 | 4640 | 0.55 | 1.6 | 1.29 | 0
CFLBldgSDGWRfExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SDG | WRf | Ex | CZ10 | 4.77 | 0.000573 | 0 | 7.69 | 0.000724 | 0 | 4.64 | 0.00055 | 0 | 7.48 | 0.000696 | 0 | CFL | Bldg | 4770 | 0.573 | 4640 | 0.55 | 1.61 | 1.27 | 0
CFLBldgSCGWRfExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCG | WRf | Ex | CZ10 | 4.77 | 0.000573 | 0 | 7.69 | 0.000724 | 0 | 4.64 | 0.00055 | 0 | 7.48 | 0.000696 | 0 | CFL | Bldg | 4770 | 0.573 | 4640 | 0.55 | 1.61 | 1.27 | 0
CFLBldgSCEWRfExCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | WRf | Ex | CZ10 | 4.77 | 0.000573 | 0 | 7.69 | 0.000724 | 0 | 4.64 | 0.00055 | 0 | 7.48 | 0.000696 | 0 | CFL | Bldg | 4770 | 0.573 | 4640 | 0.55 | 1.61 | 1.27 | 0
CFLBldgPGEWRfExCZ11 | Com-Iltg-dWatt-CFL_OSbldg | PGE | WRf | Ex | CZ11 | 4.77 | 0.000572 | 0 | 7.69 | 0.000749 | 0 | 4.64 | 0.00055 | 0 | 7.48 | 0.000719 | 0 | CFL | Bldg | 4770 | 0.572 | 4640 | 0.55 | 1.61 | 1.31 | 0
CFLBldgPGEWRfExCZ12 | Com-Iltg-dWatt-CFL_OSbldg | PGE | WRf | Ex | CZ12 | 4.76 | 0.000572 | 0 | 7.63 | 0.000733 | 0 | 4.64 | 0.00055 | 0 | 7.44 | 0.000705 | 0 | CFL | Bldg | 4760 | 0.572 | 4640 | 0.55 | 1.6 | 1.28 | 0
CFLBldgSCEWRfExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | WRf | Ex | CZ13 | 4.76 | 0.000572 | 0 | 7.68 | 0.000721 | 0 | 4.64 | 0.00055 | 0 | 7.48 | 0.000694 | 0 | CFL | Bldg | 4760 | 0.572 | 4640 | 0.55 | 1.61 | 1.26 | 0
CFLBldgPGEWRfExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | PGE | WRf | Ex | CZ13 | 4.77 | 0.000573 | 0 | 7.69 | 0.000722 | 0 | 4.64 | 0.00055 | 0 | 7.48 | 0.000694 | 0 | CFL | Bldg | 4770 | 0.573 | 4640 | 0.55 | 1.61 | 1.26 | 0
CFLBldgSCGWRfExCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCG | WRf | Ex | CZ13 | 4.76 | 0.000572 | 0 | 7.68 | 0.000721 | 0 | 4.64 | 0.00055 | 0 | 7.48 | 0.000694 | 0 | CFL | Bldg | 4760 | 0.572 | 4640 | 0.55 | 1.61 | 1.26 | 0
CFLBldgSCGWRfExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCG | WRf | Ex | CZ14 | 4.77 | 0.000573 | 0 | 7.27 | 0.000715 | 0 | 4.64 | 0.00055 | 0 | 7.08 | 0.000687 | 0 | CFL | Bldg | 4770 | 0.573 | 4640 | 0.55 | 1.53 | 1.25 | 0
CFLBldgSCEWRfExCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | WRf | Ex | CZ14 | 4.77 | 0.000573 | 0 | 7.27 | 0.000715 | 0 | 4.64 | 0.00055 | 0 | 7.08 | 0.000687 | 0 | CFL | Bldg | 4770 | 0.573 | 4640 | 0.55 | 1.53 | 1.25 | 0
CFLBldgSCEWRfExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | WRf | Ex | CZ15 | 4.77 | 0.000573 | 0 | 7.67 | 0.00072 | 0 | 4.64 | 0.00055 | 0 | 7.47 | 0.000691 | 0 | CFL | Bldg | 4770 | 0.573 | 4640 | 0.55 | 1.61 | 1.26 | 0
CFLBldgSCGWRfExCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCG | WRf | Ex | CZ15 | 4.77 | 0.000573 | 0 | 7.67 | 0.00072 | 0 | 4.64 | 0.00055 | 0 | 7.47 | 0.000691 | 0 | CFL | Bldg | 4770 | 0.573 | 4640 | 0.55 | 1.61 | 1.26 | 0
CFLBldgSCGWRfExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCG | WRf | Ex | CZ16 | 4.76 | 0.000572 | 0 | 6.93 | 0.00081 | 0 | 4.64 | 0.00055 | 0 | 6.76 | 0.00078 | 0 | CFL | Bldg | 4760 | 0.572 | 4640 | 0.55 | 1.46 | 1.42 | 0
CFLBldgPGEWRfExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | PGE | WRf | Ex | CZ16 | 4.77 | 0.000573 | 0 | 6.94 | 0.000812 | 0 | 4.64 | 0.00055 | 0 | 6.76 | 0.00078 | 0 | CFL | Bldg | 4770 | 0.573 | 4640 | 0.55 | 1.46 | 1.42 | 0
CFLBldgSCEWRfExCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | WRf | Ex | CZ16 | 4.76 | 0.000572 | 0 | 6.93 | 0.00081 | 0 | 4.64 | 0.00055 | 0 | 6.76 | 0.00078 | 0 | CFL | Bldg | 4760 | 0.572 | 4640 | 0.55 | 1.46 | 1.42 | 0
CFLBldgSDGWRfExIOU | Com-Iltg-dWatt-CFL_OSbldg | SDG | WRf | Ex | IOU | 4.77 | 0.000573 | 0 | 7.51 | 0.000721 | 0 | 4.64 | 0.00055 | 0 | 7.31 | 0.000691 | 0 | CFL | Bldg | 4770 | 0.573 | 4640 | 0.55 | 1.58 | 1.26 | 0
CFLBldgSCGWRfExIOU | Com-Iltg-dWatt-CFL_OSbldg | SCG | WRf | Ex | IOU | 4.77 | 0.000573 | 0 | 7.56 | 0.000723 | 0 | 4.64 | 0.00055 | 0 | 7.36 | 0.000694 | 0 | CFL | Bldg | 4770 | 0.573 | 4640 | 0.55 | 1.59 | 1.26 | 0
CFLBldgSCEWRfExIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | WRf | Ex | IOU | 4.77 | 0.000573 | 0 | 7.56 | 0.000721 | 0 | 4.64 | 0.00055 | 0 | 7.35 | 0.000692 | 0 | CFL | Bldg | 4770 | 0.573 | 4640 | 0.55 | 1.58 | 1.26 | 0
CFLBldgPGEWRfExIOU | Com-Iltg-dWatt-CFL_OSbldg | PGE | WRf | Ex | IOU | 4.77 | 0.000573 | 0 | 7.68 | 0.000745 | 0 | 4.64 | 0.00055 | 0 | 7.47 | 0.000715 | 0 | CFL | Bldg | 4770 | 0.573 | 4640 | 0.55 | 1.61 | 1.3 | 0
CFLBldgPGEWRfNewCZ01 | Com-Iltg-dWatt-CFL_OSbldg | PGE | WRf | New | CZ01 | 4.65 | 0.000551 | 0 | 6.17 | 0.0011 | 0 | 4.65 | 0.000551 | 0 | 6.17 | 0.0011 | 0 | CFL | Bldg | 4650 | 0.551 | 4650 | 0.551 | 1.33 | 2 | 0
CFLBldgPGEWRfNewCZ02 | Com-Iltg-dWatt-CFL_OSbldg | PGE | WRf | New | CZ02 | 4.65 | 0.000551 | 0 | 6.53 | 0.000745 | 0 | 4.65 | 0.000551 | 0 | 6.53 | 0.000745 | 0 | CFL | Bldg | 4650 | 0.551 | 4650 | 0.551 | 1.4 | 1.35 | 0
CFLBldgPGEWRfNewCZ03 | Com-Iltg-dWatt-CFL_OSbldg | PGE | WRf | New | CZ03 | 4.65 | 0.000551 | 0 | 6.6 | 0.0011 | 0 | 4.65 | 0.000551 | 0 | 6.6 | 0.0011 | 0 | CFL | Bldg | 4650 | 0.551 | 4650 | 0.551 | 1.42 | 2 | 0
CFLBldgPGEWRfNewCZ04 | Com-Iltg-dWatt-CFL_OSbldg | PGE | WRf | New | CZ04 | 4.65 | 0.000551 | 0 | 6.71 | 0.000808 | 0 | 4.65 | 0.000551 | 0 | 6.71 | 0.000808 | 0 | CFL | Bldg | 4650 | 0.551 | 4650 | 0.551 | 1.44 | 1.47 | 0
CFLBldgPGEWRfNewCZ05 | Com-Iltg-dWatt-CFL_OSbldg | PGE | WRf | New | CZ05 | 4.65 | 0.000551 | 0 | 6.54 | 0.0011 | 0 | 4.65 | 0.000551 | 0 | 6.54 | 0.0011 | 0 | CFL | Bldg | 4650 | 0.551 | 4650 | 0.551 | 1.41 | 2 | 0
CFLBldgSCEWRfNewCZ05 | Com-Iltg-dWatt-CFL_OSbldg | SCE | WRf | New | CZ05 | 4.65 | 0.000551 | 0 | 6.54 | 0.0011 | 0 | 4.65 | 0.000551 | 0 | 6.54 | 0.0011 | 0 | CFL | Bldg | 4650 | 0.551 | 4650 | 0.551 | 1.41 | 2 | 0
CFLBldgSCEWRfNewCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SCE | WRf | New | CZ06 | 4.65 | 0.000551 | 0 | 7.05 | 0.000679 | 0 | 4.65 | 0.000551 | 0 | 7.05 | 0.000679 | 0 | CFL | Bldg | 4650 | 0.551 | 4650 | 0.551 | 1.52 | 1.23 | 0
CFLBldgSDGWRfNewCZ06 | Com-Iltg-dWatt-CFL_OSbldg | SDG | WRf | New | CZ06 | 4.65 | 0.000551 | 0 | 7.05 | 0.000679 | 0 | 4.65 | 0.000551 | 0 | 7.05 | 0.000679 | 0 | CFL | Bldg | 4650 | 0.551 | 4650 | 0.551 | 1.52 | 1.23 | 0
CFLBldgSDGWRfNewCZ07 | Com-Iltg-dWatt-CFL_OSbldg | SDG | WRf | New | CZ07 | 4.65 | 0.000551 | 0 | 7.11 | 0.00068 | 0 | 4.65 | 0.000551 | 0 | 7.11 | 0.00068 | 0 | CFL | Bldg | 4650 | 0.551 | 4650 | 0.551 | 1.53 | 1.23 | 0
CFLBldgSDGWRfNewCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SDG | WRf | New | CZ08 | 4.65 | 0.000551 | 0 | 7.01 | 0.00068 | 0 | 4.65 | 0.000551 | 0 | 7.01 | 0.00068 | 0 | CFL | Bldg | 4650 | 0.551 | 4650 | 0.551 | 1.51 | 1.23 | 0
CFLBldgSCEWRfNewCZ08 | Com-Iltg-dWatt-CFL_OSbldg | SCE | WRf | New | CZ08 | 4.65 | 0.000551 | 0 | 7.01 | 0.00068 | 0 | 4.65 | 0.000551 | 0 | 7.01 | 0.00068 | 0 | CFL | Bldg | 4650 | 0.551 | 4650 | 0.551 | 1.51 | 1.23 | 0
CFLBldgSCEWRfNewCZ09 | Com-Iltg-dWatt-CFL_OSbldg | SCE | WRf | New | CZ09 | 4.65 | 0.000551 | 0 | 6.86 | 0.000707 | 0 | 4.65 | 0.000551 | 0 | 6.86 | 0.000707 | 0 | CFL | Bldg | 4650 | 0.551 | 4650 | 0.551 | 1.48 | 1.28 | 0
CFLBldgSDGWRfNewCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SDG | WRf | New | CZ10 | 4.65 | 0.000551 | 0 | 6.84 | 0.000689 | 0 | 4.65 | 0.000551 | 0 | 6.84 | 0.000689 | 0 | CFL | Bldg | 4650 | 0.551 | 4650 | 0.551 | 1.47 | 1.25 | 0
CFLBldgSCEWRfNewCZ10 | Com-Iltg-dWatt-CFL_OSbldg | SCE | WRf | New | CZ10 | 4.65 | 0.000551 | 0 | 6.84 | 0.000689 | 0 | 4.65 | 0.000551 | 0 | 6.84 | 0.000689 | 0 | CFL | Bldg | 4650 | 0.551 | 4650 | 0.551 | 1.47 | 1.25 | 0
CFLBldgPGEWRfNewCZ11 | Com-Iltg-dWatt-CFL_OSbldg | PGE | WRf | New | CZ11 | 4.65 | 0.000551 | 0 | 6.7 | 0.00087 | 0 | 4.65 | 0.000551 | 0 | 6.7 | 0.00087 | 0 | CFL | Bldg | 4650 | 0.551 | 4650 | 0.551 | 1.44 | 1.58 | 0
CFLBldgPGEWRfNewCZ12 | Com-Iltg-dWatt-CFL_OSbldg | PGE | WRf | New | CZ12 | 4.65 | 0.000551 | 0 | 6.67 | 0.000754 | 0 | 4.65 | 0.000551 | 0 | 6.67 | 0.000754 | 0 | CFL | Bldg | 4650 | 0.551 | 4650 | 0.551 | 1.43 | 1.37 | 0
CFLBldgPGEWRfNewCZ13 | Com-Iltg-dWatt-CFL_OSbldg | PGE | WRf | New | CZ13 | 4.65 | 0.000551 | 0 | 6.82 | 0.000689 | 0 | 4.65 | 0.000551 | 0 | 6.82 | 0.000689 | 0 | CFL | Bldg | 4650 | 0.551 | 4650 | 0.551 | 1.47 | 1.25 | 0
CFLBldgSCEWRfNewCZ13 | Com-Iltg-dWatt-CFL_OSbldg | SCE | WRf | New | CZ13 | 4.65 | 0.000551 | 0 | 6.82 | 0.000689 | 0 | 4.65 | 0.000551 | 0 | 6.82 | 0.000689 | 0 | CFL | Bldg | 4650 | 0.551 | 4650 | 0.551 | 1.47 | 1.25 | 0
CFLBldgSDGWRfNewCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SDG | WRf | New | CZ14 | 4.65 | 0.000551 | 0 | 6.58 | 0.000683 | 0 | 4.65 | 0.000551 | 0 | 6.58 | 0.000683 | 0 | CFL | Bldg | 4650 | 0.551 | 4650 | 0.551 | 1.42 | 1.24 | 0
CFLBldgSCEWRfNewCZ14 | Com-Iltg-dWatt-CFL_OSbldg | SCE | WRf | New | CZ14 | 4.65 | 0.000551 | 0 | 6.58 | 0.000683 | 0 | 4.65 | 0.000551 | 0 | 6.58 | 0.000683 | 0 | CFL | Bldg | 4650 | 0.551 | 4650 | 0.551 | 1.42 | 1.24 | 0
CFLBldgSDGWRfNewCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SDG | WRf | New | CZ15 | 4.65 | 0.000551 | 0 | 7.07 | 0.000687 | 0 | 4.65 | 0.000551 | 0 | 7.07 | 0.000687 | 0 | CFL | Bldg | 4650 | 0.551 | 4650 | 0.551 | 1.52 | 1.25 | 0
CFLBldgSCEWRfNewCZ15 | Com-Iltg-dWatt-CFL_OSbldg | SCE | WRf | New | CZ15 | 4.65 | 0.000551 | 0 | 7.07 | 0.000687 | 0 | 4.65 | 0.000551 | 0 | 7.07 | 0.000687 | 0 | CFL | Bldg | 4650 | 0.551 | 4650 | 0.551 | 1.52 | 1.25 | 0
CFLBldgPGEWRfNewCZ16 | Com-Iltg-dWatt-CFL_OSbldg | PGE | WRf | New | CZ16 | 4.65 | 0.000551 | 0 | 6.12 | 0.0011 | 0 | 4.65 | 0.000551 | 0 | 6.12 | 0.0011 | 0 | CFL | Bldg | 4650 | 0.551 | 4650 | 0.551 | 1.32 | 2 | 0
CFLBldgSCEWRfNewCZ16 | Com-Iltg-dWatt-CFL_OSbldg | SCE | WRf | New | CZ16 | 4.65 | 0.000551 | 0 | 6.12 | 0.0011 | 0 | 4.65 | 0.000551 | 0 | 6.12 | 0.0011 | 0 | CFL | Bldg | 4650 | 0.551 | 4650 | 0.551 | 1.32 | 2 | 0
CFLBldgSCEWRfNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SCE | WRf | New | IOU | 4.65 | 0.000551 | 0 | 6.97 | 0.000683 | 0 | 4.65 | 0.000551 | 0 | 6.97 | 0.000683 | 0 | CFL | Bldg | 4650 | 0.551 | 4650 | 0.551 | 1.5 | 1.24 | 0
CFLBldgSCGWRfNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SCG | WRf | New | IOU | 4.65 | 0.000551 | 0 | 6.97 | 0.000682 | 0 | 4.65 | 0.000551 | 0 | 6.97 | 0.000682 | 0 | CFL | Bldg | 4650 | 0.551 | 4650 | 0.551 | 1.5 | 1.24 | 0
CFLBldgPGEWRfNewIOU | Com-Iltg-dWatt-CFL_OSbldg | PGE | WRf | New | IOU | 4.65 | 0.000551 | 0 | 6.8 | 0.000717 | 0 | 4.65 | 0.000551 | 0 | 6.8 | 0.000717 | 0 | CFL | Bldg | 4650 | 0.551 | 4650 | 0.551 | 1.46 | 1.3 | 0
CFLBldgSDGWRfNewIOU | Com-Iltg-dWatt-CFL_OSbldg | SDG | WRf | New | IOU | 4.65 | 0.000551 | 0 | 7.05 | 0.000682 | 0 | 4.65 | 0.000551 | 0 | 7.05 | 0.000682 | 0 | CFL | Bldg | 4650 | 0.551 | 4650 | 0.551 | 1.52 | 1.24 | 0
CFLNonePGEAsmExCZ01 | Com-Iltg-dWatt-CFL_OSnone | PGE | Asm | Ex | CZ01 | 1.18 | 0.000226 | 0 | 1.12 | 0.000262 | -0.021 | 1.18 | 0.000226 | 0 | 1.12 | 0.000262 | -0.021 | CFL | None | 1180 | 0.226 | 1180 | 0.226 | 0.949 | 1.16 | -0.0178
CFLNonePGEAsmExCZ02 | Com-Iltg-dWatt-CFL_OSnone | PGE | Asm | Ex | CZ02 | 1.18 | 0.000226 | 0 | 1.22 | 0.000265 | -0.0122 | 1.18 | 0.000226 | 0 | 1.22 | 0.000265 | -0.0122 | CFL | None | 1180 | 0.226 | 1180 | 0.226 | 1.03 | 1.17 | -0.0103
CFLNonePGEAsmExCZ03 | Com-Iltg-dWatt-CFL_OSnone | PGE | Asm | Ex | CZ03 | 1.18 | 0.000226 | 0 | 1.21 | 0.000265 | -0.0133 | 1.18 | 0.000226 | 0 | 1.21 | 0.000265 | -0.0133 | CFL | None | 1180 | 0.226 | 1180 | 0.226 | 1.03 | 1.17 | -0.0113
CFLNonePGEAsmExCZ04 | Com-Iltg-dWatt-CFL_OSnone | PGE | Asm | Ex | CZ04 | 1.18 | 0.000226 | 0 | 1.24 | 0.000264 | -0.00985 | 1.18 | 0.000226 | 0 | 1.24 | 0.000264 | -0.00985 | CFL | None | 1180 | 0.226 | 1180 | 0.226 | 1.05 | 1.17 | -0.00835
CFLNoneSCEAsmExCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | Asm | Ex | CZ05 | 1.18 | 0.000226 | 0 | 1.24 | 0.000271 | -0.0115 | 1.18 | 0.000226 | 0 | 1.24 | 0.000271 | -0.0115 | CFL | None | 1180 | 0.226 | 1180 | 0.226 | 1.05 | 1.2 | -0.00975
CFLNonePGEAsmExCZ05 | Com-Iltg-dWatt-CFL_OSnone | PGE | Asm | Ex | CZ05 | 1.18 | 0.000226 | 0 | 1.24 | 0.000271 | -0.0115 | 1.18 | 0.000226 | 0 | 1.24 | 0.000271 | -0.0115 | CFL | None | 1180 | 0.226 | 1180 | 0.226 | 1.05 | 1.2 | -0.00975
CFLNoneSCGAsmExCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCG | Asm | Ex | CZ05 | 1.18 | 0.000226 | 0 | 1.24 | 0.000271 | -0.0115 | 1.18 | 0.000226 | 0 | 1.24 | 0.000271 | -0.0115 | CFL | None | 1180 | 0.226 | 1180 | 0.226 | 1.05 | 1.2 | -0.00975
CFLNoneSCEAsmExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | Asm | Ex | CZ06 | 1.18 | 0.000226 | 0 | 1.29 | 0.000281 | -0.00616 | 1.18 | 0.000226 | 0 | 1.29 | 0.000281 | -0.00616 | CFL | None | 1180 | 0.226 | 1180 | 0.226 | 1.09 | 1.24 | -0.00522
CFLNoneSDGAsmExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SDG | Asm | Ex | CZ06 | 1.18 | 0.000226 | 0 | 1.29 | 0.000281 | -0.00616 | 1.18 | 0.000226 | 0 | 1.29 | 0.000281 | -0.00616 | CFL | None | 1180 | 0.226 | 1180 | 0.226 | 1.09 | 1.24 | -0.00522
CFLNoneSCGAsmExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCG | Asm | Ex | CZ06 | 1.18 | 0.000226 | 0 | 1.29 | 0.000281 | -0.00616 | 1.18 | 0.000226 | 0 | 1.29 | 0.000281 | -0.00616 | CFL | None | 1180 | 0.226 | 1180 | 0.226 | 1.09 | 1.24 | -0.00522
CFLNoneSDGAsmExCZ07 | Com-Iltg-dWatt-CFL_OSnone | SDG | Asm | Ex | CZ07 | 1.18 | 0.000226 | 0 | 1.3 | 0.00028 | -0.00565 | 1.18 | 0.000226 | 0 | 1.3 | 0.00028 | -0.00565 | CFL | None | 1180 | 0.226 | 1180 | 0.226 | 1.1 | 1.24 | -0.00479
CFLNoneSDGAsmExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SDG | Asm | Ex | CZ08 | 1.18 | 0.000226 | 0 | 1.3 | 0.000272 | -0.00538 | 1.18 | 0.000226 | 0 | 1.3 | 0.000272 | -0.00538 | CFL | None | 1180 | 0.226 | 1180 | 0.226 | 1.1 | 1.2 | -0.00456
CFLNoneSCEAsmExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | Asm | Ex | CZ08 | 1.18 | 0.000226 | 0 | 1.3 | 0.000272 | -0.00538 | 1.18 | 0.000226 | 0 | 1.3 | 0.000272 | -0.00538 | CFL | None | 1180 | 0.226 | 1180 | 0.226 | 1.1 | 1.2 | -0.00456
CFLNoneSCGAsmExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCG | Asm | Ex | CZ08 | 1.18 | 0.000226 | 0 | 1.3 | 0.000272 | -0.00538 | 1.18 | 0.000226 | 0 | 1.3 | 0.000272 | -0.00538 | CFL | None | 1180 | 0.226 | 1180 | 0.226 | 1.1 | 1.2 | -0.00456
CFLNoneSCGAsmExCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCG | Asm | Ex | CZ09 | 1.18 | 0.000226 | 0 | 1.31 | 0.000281 | -0.00589 | 1.18 | 0.000226 | 0 | 1.31 | 0.000281 | -0.00589 | CFL | None | 1180 | 0.226 | 1180 | 0.226 | 1.11 | 1.24 | -0.00499
CFLNoneSCEAsmExCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | Asm | Ex | CZ09 | 1.18 | 0.000226 | 0 | 1.31 | 0.000281 | -0.00589 | 1.18 | 0.000226 | 0 | 1.31 | 0.000281 | -0.00589 | CFL | None | 1180 | 0.226 | 1180 | 0.226 | 1.11 | 1.24 | -0.00499
CFLNoneSDGAsmExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SDG | Asm | Ex | CZ10 | 1.18 | 0.000226 | 0 | 1.29 | 0.000275 | -0.00684 | 1.18 | 0.000226 | 0 | 1.29 | 0.000275 | -0.00684 | CFL | None | 1180 | 0.226 | 1180 | 0.226 | 1.09 | 1.22 | -0.0058
CFLNoneSCGAsmExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCG | Asm | Ex | CZ10 | 1.18 | 0.000226 | 0 | 1.29 | 0.000275 | -0.00684 | 1.18 | 0.000226 | 0 | 1.29 | 0.000275 | -0.00684 | CFL | None | 1180 | 0.226 | 1180 | 0.226 | 1.09 | 1.22 | -0.0058
CFLNoneSCEAsmExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | Asm | Ex | CZ10 | 1.18 | 0.000226 | 0 | 1.29 | 0.000275 | -0.00684 | 1.18 | 0.000226 | 0 | 1.29 | 0.000275 | -0.00684 | CFL | None | 1180 | 0.226 | 1180 | 0.226 | 1.09 | 1.22 | -0.0058
CFLNonePGEAsmExCZ11 | Com-Iltg-dWatt-CFL_OSnone | PGE | Asm | Ex | CZ11 | 1.18 | 0.000226 | 0 | 1.24 | 0.000264 | -0.0105 | 1.18 | 0.000226 | 0 | 1.24 | 0.000264 | -0.0105 | CFL | None | 1180 | 0.226 | 1180 | 0.226 | 1.05 | 1.17 | -0.0089
CFLNonePGEAsmExCZ12 | Com-Iltg-dWatt-CFL_OSnone | PGE | Asm | Ex | CZ12 | 1.18 | 0.000226 | 0 | 1.23 | 0.000266 | -0.011 | 1.18 | 0.000226 | 0 | 1.23 | 0.000266 | -0.011 | CFL | None | 1180 | 0.226 | 1180 | 0.226 | 1.04 | 1.18 | -0.00932
CFLNoneSCGAsmExCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCG | Asm | Ex | CZ13 | 1.18 | 0.000226 | 0 | 1.27 | 0.000274 | -0.0101 | 1.18 | 0.000226 | 0 | 1.27 | 0.000274 | -0.0101 | CFL | None | 1180 | 0.226 | 1180 | 0.226 | 1.08 | 1.21 | -0.00856
CFLNoneSCEAsmExCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | Asm | Ex | CZ13 | 1.18 | 0.000226 | 0 | 1.27 | 0.000274 | -0.0101 | 1.18 | 0.000226 | 0 | 1.27 | 0.000274 | -0.0101 | CFL | None | 1180 | 0.226 | 1180 | 0.226 | 1.08 | 1.21 | -0.00856
CFLNonePGEAsmExCZ13 | Com-Iltg-dWatt-CFL_OSnone | PGE | Asm | Ex | CZ13 | 1.18 | 0.000226 | 0 | 1.27 | 0.000274 | -0.0101 | 1.18 | 0.000226 | 0 | 1.27 | 0.000274 | -0.0101 | CFL | None | 1180 | 0.226 | 1180 | 0.226 | 1.08 | 1.21 | -0.00856
CFLNoneSCEAsmExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | Asm | Ex | CZ14 | 1.18 | 0.000226 | 0 | 1.26 | 0.000257 | -0.0107 | 1.18 | 0.000226 | 0 | 1.26 | 0.000257 | -0.0107 | CFL | None | 1180 | 0.226 | 1180 | 0.226 | 1.07 | 1.14 | -0.00907
CFLNoneSCGAsmExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCG | Asm | Ex | CZ14 | 1.18 | 0.000226 | 0 | 1.26 | 0.000257 | -0.0107 | 1.18 | 0.000226 | 0 | 1.26 | 0.000257 | -0.0107 | CFL | None | 1180 | 0.226 | 1180 | 0.226 | 1.07 | 1.14 | -0.00907
CFLNoneSDGAsmExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SDG | Asm | Ex | CZ14 | 1.18 | 0.000226 | 0 | 1.26 | 0.000257 | -0.0107 | 1.18 | 0.000226 | 0 | 1.26 | 0.000257 | -0.0107 | CFL | None | 1180 | 0.226 | 1180 | 0.226 | 1.07 | 1.14 | -0.00907
CFLNoneSCGAsmExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCG | Asm | Ex | CZ15 | 1.18 | 0.000226 | 0 | 1.48 | 0.000267 | -0.00301 | 1.18 | 0.000226 | 0 | 1.48 | 0.000267 | -0.00301 | CFL | None | 1180 | 0.226 | 1180 | 0.226 | 1.25 | 1.18 | -0.00255
CFLNoneSDGAsmExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SDG | Asm | Ex | CZ15 | 1.18 | 0.000226 | 0 | 1.48 | 0.000267 | -0.00301 | 1.18 | 0.000226 | 0 | 1.48 | 0.000267 | -0.00301 | CFL | None | 1180 | 0.226 | 1180 | 0.226 | 1.25 | 1.18 | -0.00255
CFLNoneSCEAsmExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | Asm | Ex | CZ15 | 1.18 | 0.000226 | 0 | 1.48 | 0.000267 | -0.00301 | 1.18 | 0.000226 | 0 | 1.48 | 0.000267 | -0.00301 | CFL | None | 1180 | 0.226 | 1180 | 0.226 | 1.25 | 1.18 | -0.00255
CFLNoneSCGAsmExCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCG | Asm | Ex | CZ16 | 1.18 | 0.000226 | 0 | 1.16 | 0.000269 | -0.0158 | 1.18 | 0.000226 | 0 | 1.16 | 0.000269 | -0.0158 | CFL | None | 1180 | 0.226 | 1180 | 0.226 | 0.983 | 1.19 | -0.0134
CFLNoneSCEAsmExCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | Asm | Ex | CZ16 | 1.18 | 0.000226 | 0 | 1.16 | 0.000269 | -0.0158 | 1.18 | 0.000226 | 0 | 1.16 | 0.000269 | -0.0158 | CFL | None | 1180 | 0.226 | 1180 | 0.226 | 0.983 | 1.19 | -0.0134
CFLNonePGEAsmExCZ16 | Com-Iltg-dWatt-CFL_OSnone | PGE | Asm | Ex | CZ16 | 1.18 | 0.000226 | 0 | 1.16 | 0.000269 | -0.0158 | 1.18 | 0.000226 | 0 | 1.16 | 0.000269 | -0.0158 | CFL | None | 1180 | 0.226 | 1180 | 0.226 | 0.983 | 1.19 | -0.0134
CFLNonePGEAsmExIOU | Com-Iltg-dWatt-CFL_OSnone | PGE | Asm | Ex | IOU | 1.18 | 0.000226 | 0 | 1.23 | 0.000266 | -0.0117 | 1.18 | 0.000226 | 0 | 1.23 | 0.000266 | -0.0117 | CFL | None | 1180 | 0.226 | 1180 | 0.226 | 1.04 | 1.18 | -0.00992
CFLNoneSCEAsmExIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | Asm | Ex | IOU | 1.18 | 0.000226 | 0 | 1.3 | 0.000275 | -0.00628 | 1.18 | 0.000226 | 0 | 1.3 | 0.000275 | -0.00628 | CFL | None | 1180 | 0.226 | 1180 | 0.226 | 1.1 | 1.22 | -0.00532
CFLNoneSCGAsmExIOU | Com-Iltg-dWatt-CFL_OSnone | SCG | Asm | Ex | IOU | 1.18 | 0.000226 | 0 | 1.3 | 0.000276 | -0.0062 | 1.18 | 0.000226 | 0 | 1.3 | 0.000276 | -0.0062 | CFL | None | 1180 | 0.226 | 1180 | 0.226 | 1.1 | 1.22 | -0.00525
CFLNoneSDGAsmExIOU | Com-Iltg-dWatt-CFL_OSnone | SDG | Asm | Ex | IOU | 1.18 | 0.000226 | 0 | 1.3 | 0.000278 | -0.00606 | 1.18 | 0.000226 | 0 | 1.3 | 0.000278 | -0.00606 | CFL | None | 1180 | 0.226 | 1180 | 0.226 | 1.1 | 1.23 | -0.00514
CFLNonePGEAsmNewCZ01 | Com-Iltg-dWatt-CFL_OSnone | PGE | Asm | New | CZ01 | 1.18 | 0.000226 | 0 | 1.13 | 0.000261 | -0.0209 | 1.18 | 0.000226 | 0 | 1.13 | 0.000261 | -0.0209 | CFL | None | 1180 | 0.226 | 1180 | 0.226 | 0.958 | 1.15 | -0.0177
CFLNonePGEAsmNewCZ02 | Com-Iltg-dWatt-CFL_OSnone | PGE | Asm | New | CZ02 | 1.18 | 0.000226 | 0 | 1.2 | 0.000265 | -0.0132 | 1.18 | 0.000226 | 0 | 1.2 | 0.000265 | -0.0132 | CFL | None | 1180 | 0.226 | 1180 | 0.226 | 1.02 | 1.17 | -0.0112
CFLNonePGEAsmNewCZ03 | Com-Iltg-dWatt-CFL_OSnone | PGE | Asm | New | CZ03 | 1.18 | 0.000226 | 0 | 1.19 | 0.000261 | -0.0137 | 1.18 | 0.000226 | 0 | 1.19 | 0.000261 | -0.0137 | CFL | None | 1180 | 0.226 | 1180 | 0.226 | 1.01 | 1.15 | -0.0116
CFLNonePGEAsmNewCZ04 | Com-Iltg-dWatt-CFL_OSnone | PGE | Asm | New | CZ04 | 1.18 | 0.000226 | 0 | 1.22 | 0.000265 | -0.0108 | 1.18 | 0.000226 | 0 | 1.22 | 0.000265 | -0.0108 | CFL | None | 1180 | 0.226 | 1180 | 0.226 | 1.03 | 1.17 | -0.00915
CFLNonePGEAsmNewCZ05 | Com-Iltg-dWatt-CFL_OSnone | PGE | Asm | New | CZ05 | 1.18 | 0.000226 | 0 | 1.2 | 0.000258 | -0.0119 | 1.18 | 0.000226 | 0 | 1.2 | 0.000258 | -0.0119 | CFL | None | 1180 | 0.226 | 1180 | 0.226 | 1.02 | 1.14 | -0.0101
CFLNoneSCEAsmNewCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | Asm | New | CZ05 | 1.18 | 0.000226 | 0 | 1.22 | 0.000267 | -0.0116 | 1.18 | 0.000226 | 0 | 1.22 | 0.000267 | -0.0116 | CFL | None | 1180 | 0.226 | 1180 | 0.226 | 1.03 | 1.18 | -0.00983
CFLNoneSCEAsmNewCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | Asm | New | CZ06 | 1.18 | 0.000226 | 0 | 1.27 | 0.000277 | -0.00742 | 1.18 | 0.000226 | 0 | 1.27 | 0.000277 | -0.00742 | CFL | None | 1180 | 0.226 | 1180 | 0.226 | 1.08 | 1.23 | -0.00629
CFLNoneSDGAsmNewCZ06 | Com-Iltg-dWatt-CFL_OSnone | SDG | Asm | New | CZ06 | 1.18 | 0.000226 | 0 | 1.27 | 0.000279 | -0.00796 | 1.18 | 0.000226 | 0 | 1.27 | 0.000279 | -0.00796 | CFL | None | 1180 | 0.226 | 1180 | 0.226 | 1.08 | 1.23 | -0.00675
CFLNoneSDGAsmNewCZ07 | Com-Iltg-dWatt-CFL_OSnone | SDG | Asm | New | CZ07 | 1.18 | 0.000226 | 0 | 1.28 | 0.000278 | -0.00699 | 1.18 | 0.000226 | 0 | 1.28 | 0.000278 | -0.00699 | CFL | None | 1180 | 0.226 | 1180 | 0.226 | 1.08 | 1.23 | -0.00592
CFLNoneSCEAsmNewCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | Asm | New | CZ08 | 1.18 | 0.000226 | 0 | 1.29 | 0.000273 | -0.00575 | 1.18 | 0.000226 | 0 | 1.29 | 0.000273 | -0.00575 | CFL | None | 1180 | 0.226 | 1180 | 0.226 | 1.09 | 1.21 | -0.00487
CFLNoneSDGAsmNewCZ08 | Com-Iltg-dWatt-CFL_OSnone | SDG | Asm | New | CZ08 | 1.18 | 0.000226 | 0 | 1.29 | 0.000275 | -0.00617 | 1.18 | 0.000226 | 0 | 1.29 | 0.000275 | -0.00617 | CFL | None | 1180 | 0.226 | 1180 | 0.226 | 1.09 | 1.22 | -0.00523
CFLNoneSCEAsmNewCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | Asm | New | CZ09 | 1.18 | 0.000226 | 0 | 1.29 | 0.000289 | -0.0069 | 1.18 | 0.000226 | 0 | 1.29 | 0.000289 | -0.0069 | CFL | None | 1180 | 0.226 | 1180 | 0.226 | 1.09 | 1.28 | -0.00585
CFLNoneSDGAsmNewCZ10 | Com-Iltg-dWatt-CFL_OSnone | SDG | Asm | New | CZ10 | 1.18 | 0.000226 | 0 | 1.28 | 0.000282 | -0.00734 | 1.18 | 0.000226 | 0 | 1.28 | 0.000282 | -0.00734 | CFL | None | 1180 | 0.226 | 1180 | 0.226 | 1.08 | 1.25 | -0.00622
CFLNoneSCEAsmNewCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | Asm | New | CZ10 | 1.18 | 0.000226 | 0 | 1.28 | 0.00028 | -0.00682 | 1.18 | 0.000226 | 0 | 1.28 | 0.00028 | -0.00682 | CFL | None | 1180 | 0.226 | 1180 | 0.226 | 1.08 | 1.24 | -0.00578
CFLNonePGEAsmNewCZ11 | Com-Iltg-dWatt-CFL_OSnone | PGE | Asm | New | CZ11 | 1.18 | 0.000226 | 0 | 1.23 | 0.000269 | -0.0114 | 1.18 | 0.000226 | 0 | 1.23 | 0.000269 | -0.0114 | CFL | None | 1180 | 0.226 | 1180 | 0.226 | 1.04 | 1.19 | -0.00966
CFLNonePGEAsmNewCZ12 | Com-Iltg-dWatt-CFL_OSnone | PGE | Asm | New | CZ12 | 1.18 | 0.000226 | 0 | 1.22 | 0.000268 | -0.012 | 1.18 | 0.000226 | 0 | 1.22 | 0.000268 | -0.012 | CFL | None | 1180 | 0.226 | 1180 | 0.226 | 1.03 | 1.19 | -0.0102
CFLNonePGEAsmNewCZ13 | Com-Iltg-dWatt-CFL_OSnone | PGE | Asm | New | CZ13 | 1.18 | 0.000226 | 0 | 1.23 | 0.00027 | -0.0109 | 1.18 | 0.000226 | 0 | 1.23 | 0.00027 | -0.0109 | CFL | None | 1180 | 0.226 | 1180 | 0.226 | 1.04 | 1.19 | -0.00924
CFLNoneSCEAsmNewCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | Asm | New | CZ13 | 1.18 | 0.000226 | 0 | 1.26 | 0.000282 | -0.0108 | 1.18 | 0.000226 | 0 | 1.26 | 0.000282 | -0.0108 | CFL | None | 1180 | 0.226 | 1180 | 0.226 | 1.07 | 1.25 | -0.00915
CFLNoneSCEAsmNewCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | Asm | New | CZ14 | 1.18 | 0.000226 | 0 | 1.25 | 0.000269 | -0.0106 | 1.18 | 0.000226 | 0 | 1.25 | 0.000269 | -0.0106 | CFL | None | 1180 | 0.226 | 1180 | 0.226 | 1.06 | 1.19 | -0.00898
CFLNoneSDGAsmNewCZ14 | Com-Iltg-dWatt-CFL_OSnone | SDG | Asm | New | CZ14 | 1.18 | 0.000226 | 0 | 1.25 | 0.00027 | -0.0114 | 1.18 | 0.000226 | 0 | 1.25 | 0.00027 | -0.0114 | CFL | None | 1180 | 0.226 | 1180 | 0.226 | 1.06 | 1.19 | -0.00966
CFLNoneSCEAsmNewCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | Asm | New | CZ15 | 1.18 | 0.000226 | 0 | 1.41 | 0.000282 | -0.00328 | 1.18 | 0.000226 | 0 | 1.41 | 0.000282 | -0.00328 | CFL | None | 1180 | 0.226 | 1180 | 0.226 | 1.19 | 1.25 | -0.00278
CFLNoneSDGAsmNewCZ15 | Com-Iltg-dWatt-CFL_OSnone | SDG | Asm | New | CZ15 | 1.18 | 0.000226 | 0 | 1.42 | 0.000283 | -0.00353 | 1.18 | 0.000226 | 0 | 1.42 | 0.000283 | -0.00353 | CFL | None | 1180 | 0.226 | 1180 | 0.226 | 1.2 | 1.25 | -0.00299
CFLNoneSCEAsmNewCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | Asm | New | CZ16 | 1.18 | 0.000226 | 0 | 1.17 | 0.000269 | -0.0157 | 1.18 | 0.000226 | 0 | 1.17 | 0.000269 | -0.0157 | CFL | None | 1180 | 0.226 | 1180 | 0.226 | 0.992 | 1.19 | -0.0133
CFLNonePGEAsmNewCZ16 | Com-Iltg-dWatt-CFL_OSnone | PGE | Asm | New | CZ16 | 1.18 | 0.000226 | 0 | 1.16 | 0.00026 | -0.0158 | 1.18 | 0.000226 | 0 | 1.16 | 0.00026 | -0.0158 | CFL | None | 1180 | 0.226 | 1180 | 0.226 | 0.983 | 1.15 | -0.0134
CFLNoneSCGAsmNewIOU | Com-Iltg-dWatt-CFL_OSnone | SCG | Asm | New | IOU | 1.18 | 0.000226 | 0 | 1.3 | 0.000279 | -0.00688 | 1.18 | 0.000226 | 0 | 1.3 | 0.000279 | -0.00688 | CFL | None | 1180 | 0.226 | 1180 | 0.226 | 1.1 | 1.23 | -0.00583
CFLNoneSCEAsmNewIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | Asm | New | IOU | 1.18 | 0.000226 | 0 | 1.3 | 0.000279 | -0.00689 | 1.18 | 0.000226 | 0 | 1.3 | 0.000279 | -0.00689 | CFL | None | 1180 | 0.226 | 1180 | 0.226 | 1.1 | 1.23 | -0.00584
CFLNonePGEAsmNewIOU | Com-Iltg-dWatt-CFL_OSnone | PGE | Asm | New | IOU | 1.18 | 0.000226 | 0 | 1.25 | 0.00028 | -0.0112 | 1.18 | 0.000226 | 0 | 1.25 | 0.00028 | -0.0112 | CFL | None | 1180 | 0.226 | 1180 | 0.226 | 1.06 | 1.24 | -0.00949
CFLNoneSDGAsmNewIOU | Com-Iltg-dWatt-CFL_OSnone | SDG | Asm | New | IOU | 1.18 | 0.000226 | 0 | 1.28 | 0.000279 | -0.00714 | 1.18 | 0.000226 | 0 | 1.28 | 0.000279 | -0.00714 | CFL | None | 1180 | 0.226 | 1180 | 0.226 | 1.08 | 1.23 | -0.00605
CFLNonePGEComExCZ01 | Com-Iltg-dWatt-CFL_OSnone | PGE | Com | Ex | CZ01 | 2.17 | 0.000497 | 0 | 2.14 | 0.000579 | -0.0265 | 2.17 | 0.000497 | 0 | 2.14 | 0.000579 | -0.0265 | CFL | None | 2170 | 0.497 | 2170 | 0.497 | 0.986 | 1.16 | -0.0122
CFLNonePGEComExCZ02 | Com-Iltg-dWatt-CFL_OSnone | PGE | Com | Ex | CZ02 | 2.25 | 0.000446 | 0 | 2.34 | 0.000549 | -0.0177 | 2.25 | 0.000446 | 0 | 2.34 | 0.000549 | -0.0177 | CFL | None | 2250 | 0.446 | 2250 | 0.446 | 1.04 | 1.23 | -0.00787
CFLNonePGEComExCZ03 | Com-Iltg-dWatt-CFL_OSnone | PGE | Com | Ex | CZ03 | 2.13 | 0.000442 | 0 | 2.25 | 0.000545 | -0.0154 | 2.13 | 0.000442 | 0 | 2.25 | 0.000545 | -0.0154 | CFL | None | 2130 | 0.442 | 2130 | 0.442 | 1.06 | 1.23 | -0.00723
CFLNonePGEComExCZ04 | Com-Iltg-dWatt-CFL_OSnone | PGE | Com | Ex | CZ04 | 2.11 | 0.00048 | 0 | 2.25 | 0.000591 | -0.0126 | 2.11 | 0.00048 | 0 | 2.25 | 0.000591 | -0.0126 | CFL | None | 2110 | 0.48 | 2110 | 0.48 | 1.07 | 1.23 | -0.00597
CFLNonePGEComExCZ05 | Com-Iltg-dWatt-CFL_OSnone | PGE | Com | Ex | CZ05 | 2.18 | 0.000484 | 0 | 2.34 | 0.000603 | -0.0166 | 2.18 | 0.000484 | 0 | 2.34 | 0.000603 | -0.0166 | CFL | None | 2180 | 0.484 | 2180 | 0.484 | 1.07 | 1.25 | -0.00761
CFLNoneSCEComExCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | Com | Ex | CZ05 | 2.79 | 0.000559 | 0 | 2.98 | 0.000695 | -0.0239 | 2.79 | 0.000559 | 0 | 2.98 | 0.000695 | -0.0239 | CFL | None | 2790 | 0.559 | 2790 | 0.559 | 1.07 | 1.24 | -0.00857
CFLNoneSCGComExCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCG | Com | Ex | CZ05 | 2.79 | 0.000559 | 0 | 2.98 | 0.000695 | -0.0239 | 2.79 | 0.000559 | 0 | 2.98 | 0.000695 | -0.0239 | CFL | None | 2790 | 0.559 | 2790 | 0.559 | 1.07 | 1.24 | -0.00857
CFLNoneSCEComExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | Com | Ex | CZ06 | 2.2 | 0.000493 | 0 | 2.45 | 0.000614 | -0.00881 | 2.2 | 0.000493 | 0 | 2.45 | 0.000614 | -0.00881 | CFL | None | 2200 | 0.493 | 2200 | 0.493 | 1.11 | 1.25 | -0.004
CFLNoneSDGComExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SDG | Com | Ex | CZ06 | 2.27 | 0.000487 | 0 | 2.47 | 0.000606 | -0.0121 | 2.27 | 0.000487 | 0 | 2.47 | 0.000606 | -0.0121 | CFL | None | 2270 | 0.487 | 2270 | 0.487 | 1.09 | 1.24 | -0.00533
CFLNoneSCGComExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCG | Com | Ex | CZ06 | 2.19 | 0.000492 | 0 | 2.44 | 0.000613 | -0.00878 | 2.19 | 0.000492 | 0 | 2.44 | 0.000613 | -0.00878 | CFL | None | 2190 | 0.492 | 2190 | 0.492 | 1.11 | 1.25 | -0.00401
CFLNoneSDGComExCZ07 | Com-Iltg-dWatt-CFL_OSnone | SDG | Com | Ex | CZ07 | 2.17 | 0.000486 | 0 | 2.4 | 0.000601 | -0.00838 | 2.17 | 0.000486 | 0 | 2.4 | 0.000601 | -0.00838 | CFL | None | 2170 | 0.486 | 2170 | 0.486 | 1.11 | 1.24 | -0.00386
CFLNoneSDGComExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SDG | Com | Ex | CZ08 | 2.32 | 0.000544 | 0 | 2.59 | 0.000682 | -0.00909 | 2.32 | 0.000544 | 0 | 2.59 | 0.000682 | -0.00909 | CFL | None | 2320 | 0.544 | 2320 | 0.544 | 1.12 | 1.25 | -0.00392
CFLNoneSCGComExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCG | Com | Ex | CZ08 | 2.13 | 0.000483 | 0 | 2.37 | 0.000603 | -0.00781 | 2.13 | 0.000483 | 0 | 2.37 | 0.000603 | -0.00781 | CFL | None | 2130 | 0.483 | 2130 | 0.483 | 1.11 | 1.25 | -0.00367
CFLNoneSCEComExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | Com | Ex | CZ08 | 2.13 | 0.000482 | 0 | 2.37 | 0.000601 | -0.00781 | 2.13 | 0.000482 | 0 | 2.37 | 0.000601 | -0.00781 | CFL | None | 2130 | 0.482 | 2130 | 0.482 | 1.11 | 1.25 | -0.00367
CFLNoneSCEComExCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | Com | Ex | CZ09 | 2.16 | 0.000488 | 0 | 2.43 | 0.000628 | -0.00964 | 2.16 | 0.000488 | 0 | 2.43 | 0.000628 | -0.00964 | CFL | None | 2160 | 0.488 | 2160 | 0.488 | 1.13 | 1.29 | -0.00446
CFLNoneSCGComExCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCG | Com | Ex | CZ09 | 2.17 | 0.000489 | 0 | 2.44 | 0.000631 | -0.00985 | 2.17 | 0.000489 | 0 | 2.44 | 0.000631 | -0.00985 | CFL | None | 2170 | 0.489 | 2170 | 0.489 | 1.12 | 1.29 | -0.00454
CFLNoneSDGComExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SDG | Com | Ex | CZ10 | 2.15 | 0.000495 | 0 | 2.37 | 0.000628 | -0.0097 | 2.15 | 0.000495 | 0 | 2.37 | 0.000628 | -0.0097 | CFL | None | 2150 | 0.495 | 2150 | 0.495 | 1.1 | 1.27 | -0.00451
CFLNoneSCGComExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCG | Com | Ex | CZ10 | 2.16 | 0.000488 | 0 | 2.38 | 0.000613 | -0.00935 | 2.16 | 0.000488 | 0 | 2.38 | 0.000613 | -0.00935 | CFL | None | 2160 | 0.488 | 2160 | 0.488 | 1.1 | 1.26 | -0.00433
CFLNoneSCEComExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | Com | Ex | CZ10 | 2.16 | 0.000488 | 0 | 2.38 | 0.000613 | -0.00935 | 2.16 | 0.000488 | 0 | 2.38 | 0.000613 | -0.00935 | CFL | None | 2160 | 0.488 | 2160 | 0.488 | 1.1 | 1.26 | -0.00433
CFLNonePGEComExCZ11 | Com-Iltg-dWatt-CFL_OSnone | PGE | Com | Ex | CZ11 | 2.24 | 0.000444 | 0 | 2.39 | 0.000546 | -0.0159 | 2.24 | 0.000444 | 0 | 2.39 | 0.000546 | -0.0159 | CFL | None | 2240 | 0.444 | 2240 | 0.444 | 1.07 | 1.23 | -0.0071
CFLNonePGEComExCZ12 | Com-Iltg-dWatt-CFL_OSnone | PGE | Com | Ex | CZ12 | 2.22 | 0.000452 | 0 | 2.35 | 0.000557 | -0.0153 | 2.22 | 0.000452 | 0 | 2.35 | 0.000557 | -0.0153 | CFL | None | 2220 | 0.452 | 2220 | 0.452 | 1.06 | 1.23 | -0.00689
CFLNonePGEComExCZ13 | Com-Iltg-dWatt-CFL_OSnone | PGE | Com | Ex | CZ13 | 2.26 | 0.000446 | 0 | 2.52 | 0.000563 | -0.0142 | 2.26 | 0.000446 | 0 | 2.52 | 0.000563 | -0.0142 | CFL | None | 2260 | 0.446 | 2260 | 0.446 | 1.12 | 1.26 | -0.00628
CFLNoneSCGComExCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCG | Com | Ex | CZ13 | 2.3 | 0.000451 | 0 | 2.61 | 0.000568 | -0.014 | 2.3 | 0.000451 | 0 | 2.61 | 0.000568 | -0.014 | CFL | None | 2300 | 0.451 | 2300 | 0.451 | 1.13 | 1.26 | -0.00609
CFLNoneSCEComExCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | Com | Ex | CZ13 | 2.3 | 0.000451 | 0 | 2.61 | 0.000568 | -0.014 | 2.3 | 0.000451 | 0 | 2.61 | 0.000568 | -0.014 | CFL | None | 2300 | 0.451 | 2300 | 0.451 | 1.13 | 1.26 | -0.00609
CFLNoneSCEComExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | Com | Ex | CZ14 | 2.25 | 0.000515 | 0 | 2.44 | 0.000654 | -0.0155 | 2.25 | 0.000515 | 0 | 2.44 | 0.000654 | -0.0155 | CFL | None | 2250 | 0.515 | 2250 | 0.515 | 1.08 | 1.27 | -0.00689
CFLNoneSCGComExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCG | Com | Ex | CZ14 | 2.25 | 0.000515 | 0 | 2.44 | 0.000654 | -0.0155 | 2.25 | 0.000515 | 0 | 2.44 | 0.000654 | -0.0155 | CFL | None | 2250 | 0.515 | 2250 | 0.515 | 1.08 | 1.27 | -0.00689
CFLNoneSDGComExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SDG | Com | Ex | CZ14 | 1.85 | 0.000422 | 0 | 2.01 | 0.000532 | -0.0108 | 1.85 | 0.000422 | 0 | 2.01 | 0.000532 | -0.0108 | CFL | None | 1850 | 0.422 | 1850 | 0.422 | 1.09 | 1.26 | -0.00584
CFLNoneSCGComExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCG | Com | Ex | CZ15 | 2.07 | 0.000453 | 0 | 2.46 | 0.000574 | -0.00393 | 2.07 | 0.000453 | 0 | 2.46 | 0.000574 | -0.00393 | CFL | None | 2070 | 0.453 | 2070 | 0.453 | 1.19 | 1.27 | -0.0019
CFLNoneSDGComExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SDG | Com | Ex | CZ15 | 1.68 | 0.000332 | 0 | 1.99 | 0.000422 | -0.00281 | 1.68 | 0.000332 | 0 | 1.99 | 0.000422 | -0.00281 | CFL | None | 1680 | 0.332 | 1680 | 0.332 | 1.18 | 1.27 | -0.00167
CFLNoneSCEComExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | Com | Ex | CZ15 | 2.07 | 0.000453 | 0 | 2.46 | 0.000574 | -0.00393 | 2.07 | 0.000453 | 0 | 2.46 | 0.000574 | -0.00393 | CFL | None | 2070 | 0.453 | 2070 | 0.453 | 1.19 | 1.27 | -0.0019
CFLNonePGEComExCZ16 | Com-Iltg-dWatt-CFL_OSnone | PGE | Com | Ex | CZ16 | 2.08 | 0.000396 | 0 | 2.06 | 0.000481 | -0.023 | 2.08 | 0.000396 | 0 | 2.06 | 0.000481 | -0.023 | CFL | None | 2080 | 0.396 | 2080 | 0.396 | 0.99 | 1.21 | -0.0111
CFLNoneSCEComExCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | Com | Ex | CZ16 | 2.1 | 0.000405 | 0 | 2.11 | 0.000494 | -0.0243 | 2.1 | 0.000405 | 0 | 2.11 | 0.000494 | -0.0243 | CFL | None | 2100 | 0.405 | 2100 | 0.405 | 1 | 1.22 | -0.0116
CFLNoneSCGComExCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCG | Com | Ex | CZ16 | 2.1 | 0.000405 | 0 | 2.11 | 0.000494 | -0.0243 | 2.1 | 0.000405 | 0 | 2.11 | 0.000494 | -0.0243 | CFL | None | 2100 | 0.405 | 2100 | 0.405 | 1 | 1.22 | -0.0116
CFLNoneSDGComExIOU | Com-Iltg-dWatt-CFL_OSnone | SDG | Com | Ex | IOU | 2.17 | 0.000489 | 0 | 2.4 | 0.000609 | -0.00883 | 2.17 | 0.000489 | 0 | 2.4 | 0.000609 | -0.00883 | CFL | None | 2170 | 0.489 | 2170 | 0.489 | 1.11 | 1.25 | -0.00407
CFLNonePGEComExIOU | Com-Iltg-dWatt-CFL_OSnone | PGE | Com | Ex | IOU | 2.18 | 0.000452 | 0 | 2.32 | 0.000558 | -0.0152 | 2.18 | 0.000452 | 0 | 2.32 | 0.000558 | -0.0152 | CFL | None | 2180 | 0.452 | 2180 | 0.452 | 1.06 | 1.23 | -0.00697
CFLNoneSCEComExIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | Com | Ex | IOU | 2.16 | 0.000485 | 0 | 2.41 | 0.000609 | -0.00918 | 2.16 | 0.000485 | 0 | 2.41 | 0.000609 | -0.00918 | CFL | None | 2160 | 0.485 | 2160 | 0.485 | 1.12 | 1.26 | -0.00425
CFLNoneSCGComExIOU | Com-Iltg-dWatt-CFL_OSnone | SCG | Com | Ex | IOU | 2.16 | 0.000486 | 0 | 2.41 | 0.000613 | -0.00925 | 2.16 | 0.000486 | 0 | 2.41 | 0.000613 | -0.00925 | CFL | None | 2160 | 0.486 | 2160 | 0.486 | 1.12 | 1.26 | -0.00428
CFLNoneSCEComNewCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | Com | New | CZ05 | 2.78 | 0.000575 | 0 | 2.86 | 0.000705 | -0.025 | 2.78 | 0.000575 | 0 | 2.86 | 0.000705 | -0.025 | CFL | None | 2780 | 0.575 | 2780 | 0.575 | 1.03 | 1.23 | -0.00899
CFLNonePGEComNewCZ05 | Com-Iltg-dWatt-CFL_OSnone | PGE | Com | New | CZ05 | 2.17 | 0.000477 | 0 | 2.24 | 0.000581 | -0.0165 | 2.17 | 0.000477 | 0 | 2.24 | 0.000581 | -0.0165 | CFL | None | 2170 | 0.477 | 2170 | 0.477 | 1.03 | 1.22 | -0.0076
CFLNoneSDGComNewCZ06 | Com-Iltg-dWatt-CFL_OSnone | SDG | Com | New | CZ06 | 2.28 | 0.000474 | 0 | 2.46 | 0.000588 | -0.0123 | 2.28 | 0.000474 | 0 | 2.46 | 0.000588 | -0.0123 | CFL | None | 2280 | 0.474 | 2280 | 0.474 | 1.08 | 1.24 | -0.00539
CFLNoneSCEComNewCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | Com | New | CZ06 | 2.28 | 0.00051 | 0 | 2.49 | 0.000631 | -0.00989 | 2.28 | 0.00051 | 0 | 2.49 | 0.000631 | -0.00989 | CFL | None | 2280 | 0.51 | 2280 | 0.51 | 1.09 | 1.24 | -0.00434
CFLNoneSDGComNewCZ07 | Com-Iltg-dWatt-CFL_OSnone | SDG | Com | New | CZ07 | 2.14 | 0.00047 | 0 | 2.32 | 0.000573 | -0.00813 | 2.14 | 0.00047 | 0 | 2.32 | 0.000573 | -0.00813 | CFL | None | 2140 | 0.47 | 2140 | 0.47 | 1.08 | 1.22 | -0.0038
CFLNoneSCEComNewCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | Com | New | CZ08 | 2.2 | 0.000493 | 0 | 2.4 | 0.000609 | -0.0083 | 2.2 | 0.000493 | 0 | 2.4 | 0.000609 | -0.0083 | CFL | None | 2200 | 0.493 | 2200 | 0.493 | 1.09 | 1.24 | -0.00377
CFLNoneSDGComNewCZ08 | Com-Iltg-dWatt-CFL_OSnone | SDG | Com | New | CZ08 | 2.35 | 0.000553 | 0 | 2.57 | 0.00069 | -0.00911 | 2.35 | 0.000553 | 0 | 2.57 | 0.00069 | -0.00911 | CFL | None | 2350 | 0.553 | 2350 | 0.553 | 1.09 | 1.25 | -0.00388
CFLNoneSCEComNewCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | Com | New | CZ09 | 2.23 | 0.000499 | 0 | 2.46 | 0.000647 | -0.00922 | 2.23 | 0.000499 | 0 | 2.46 | 0.000647 | -0.00922 | CFL | None | 2230 | 0.499 | 2230 | 0.499 | 1.1 | 1.3 | -0.00413
CFLNoneSCEComNewCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | Com | New | CZ10 | 2.06 | 0.000462 | 0 | 2.22 | 0.000586 | -0.00864 | 2.06 | 0.000462 | 0 | 2.22 | 0.000586 | -0.00864 | CFL | None | 2060 | 0.462 | 2060 | 0.462 | 1.08 | 1.27 | -0.00419
CFLNoneSDGComNewCZ10 | Com-Iltg-dWatt-CFL_OSnone | SDG | Com | New | CZ10 | 2.18 | 0.000494 | 0 | 2.4 | 0.000646 | -0.00994 | 2.18 | 0.000494 | 0 | 2.4 | 0.000646 | -0.00994 | CFL | None | 2180 | 0.494 | 2180 | 0.494 | 1.1 | 1.31 | -0.00456
CFLNonePGEComNewCZ11 | Com-Iltg-dWatt-CFL_OSnone | PGE | Com | New | CZ11 | 2.22 | 0.000444 | 0 | 2.36 | 0.000553 | -0.0154 | 2.22 | 0.000444 | 0 | 2.36 | 0.000553 | -0.0154 | CFL | None | 2220 | 0.444 | 2220 | 0.444 | 1.06 | 1.25 | -0.00694
CFLNonePGEComNewCZ12 | Com-Iltg-dWatt-CFL_OSnone | PGE | Com | New | CZ12 | 2.21 | 0.000452 | 0 | 2.35 | 0.000559 | -0.0147 | 2.21 | 0.000452 | 0 | 2.35 | 0.000559 | -0.0147 | CFL | None | 2210 | 0.452 | 2210 | 0.452 | 1.06 | 1.24 | -0.00665
CFLNoneSCEComNewCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | Com | New | CZ13 | 2.37 | 0.000467 | 0 | 2.69 | 0.000598 | -0.0138 | 2.37 | 0.000467 | 0 | 2.69 | 0.000598 | -0.0138 | CFL | None | 2370 | 0.467 | 2370 | 0.467 | 1.14 | 1.28 | -0.00582
CFLNonePGEComNewCZ13 | Com-Iltg-dWatt-CFL_OSnone | PGE | Com | New | CZ13 | 2.28 | 0.000454 | 0 | 2.48 | 0.000559 | -0.0139 | 2.28 | 0.000454 | 0 | 2.48 | 0.000559 | -0.0139 | CFL | None | 2280 | 0.454 | 2280 | 0.454 | 1.09 | 1.23 | -0.0061
CFLNoneSCEComNewCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | Com | New | CZ14 | 2.29 | 0.000518 | 0 | 2.48 | 0.000672 | -0.0162 | 2.29 | 0.000518 | 0 | 2.48 | 0.000672 | -0.0162 | CFL | None | 2290 | 0.518 | 2290 | 0.518 | 1.08 | 1.3 | -0.00707
CFLNoneSDGComNewCZ14 | Com-Iltg-dWatt-CFL_OSnone | SDG | Com | New | CZ14 | 1.87 | 0.000402 | 0 | 2.02 | 0.000519 | -0.0111 | 1.87 | 0.000402 | 0 | 2.02 | 0.000519 | -0.0111 | CFL | None | 1870 | 0.402 | 1870 | 0.402 | 1.08 | 1.29 | -0.00594
CFLNoneSDGComNewCZ15 | Com-Iltg-dWatt-CFL_OSnone | SDG | Com | New | CZ15 | 1.65 | 0.000298 | 0 | 1.94 | 0.000395 | -0.00255 | 1.65 | 0.000298 | 0 | 1.94 | 0.000395 | -0.00255 | CFL | None | 1650 | 0.298 | 1650 | 0.298 | 1.18 | 1.33 | -0.00155
CFLNoneSCEComNewCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | Com | New | CZ15 | 2.04 | 0.00045 | 0 | 2.4 | 0.000597 | -0.00337 | 2.04 | 0.00045 | 0 | 2.4 | 0.000597 | -0.00337 | CFL | None | 2040 | 0.45 | 2040 | 0.45 | 1.18 | 1.33 | -0.00165
CFLNoneSCEComNewCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | Com | New | CZ16 | 2.1 | 0.00042 | 0 | 2.11 | 0.000519 | -0.0235 | 2.1 | 0.00042 | 0 | 2.11 | 0.000519 | -0.0235 | CFL | None | 2100 | 0.42 | 2100 | 0.42 | 1 | 1.24 | -0.0112
CFLNonePGEComNewCZ16 | Com-Iltg-dWatt-CFL_OSnone | PGE | Com | New | CZ16 | 2.05 | 0.000392 | 0 | 1.98 | 0.000464 | -0.0218 | 2.05 | 0.000392 | 0 | 1.98 | 0.000464 | -0.0218 | CFL | None | 2050 | 0.392 | 2050 | 0.392 | 0.966 | 1.18 | -0.0106
CFLNoneSCEComNewIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | Com | New | IOU | 2.16 | 0.000483 | 0 | 2.37 | 0.000608 | -0.00881 | 2.16 | 0.000483 | 0 | 2.37 | 0.000608 | -0.00881 | CFL | None | 2160 | 0.483 | 2160 | 0.483 | 1.1 | 1.26 | -0.00408
CFLNonePGEComNewIOU | Com-Iltg-dWatt-CFL_OSnone | PGE | Com | New | IOU | 2.21 | 0.000459 | 0 | 2.41 | 0.000583 | -0.0137 | 2.21 | 0.000459 | 0 | 2.41 | 0.000583 | -0.0137 | CFL | None | 2210 | 0.459 | 2210 | 0.459 | 1.09 | 1.27 | -0.0062
CFLNoneSCGComNewIOU | Com-Iltg-dWatt-CFL_OSnone | SCG | Com | New | IOU | 2.17 | 0.000485 | 0 | 2.38 | 0.00061 | -0.00879 | 2.17 | 0.000485 | 0 | 2.38 | 0.00061 | -0.00879 | CFL | None | 2170 | 0.485 | 2170 | 0.485 | 1.1 | 1.26 | -0.00405
CFLNoneSDGComNewIOU | Com-Iltg-dWatt-CFL_OSnone | SDG | Com | New | IOU | 2.16 | 0.000477 | 0 | 2.35 | 0.000593 | -0.00871 | 2.16 | 0.000477 | 0 | 2.35 | 0.000593 | -0.00871 | CFL | None | 2160 | 0.477 | 2160 | 0.477 | 1.09 | 1.24 | -0.00403
CFLNonePGEECCExCZ01 | Com-Iltg-dWatt-CFL_OSnone | PGE | ECC | Ex | CZ01 | 1.53 | 0.000532 | 0 | 1.57 | 0.00065 | -0.0303 | 1.53 | 0.000532 | 0 | 1.57 | 0.00065 | -0.0303 | CFL | None | 1530 | 0.532 | 1530 | 0.532 | 1.03 | 1.22 | -0.0198
CFLNonePGEECCExCZ02 | Com-Iltg-dWatt-CFL_OSnone | PGE | ECC | Ex | CZ02 | 1.53 | 0.000345 | 0 | 1.66 | 0.000455 | -0.0185 | 1.53 | 0.000345 | 0 | 1.66 | 0.000455 | -0.0185 | CFL | None | 1530 | 0.345 | 1530 | 0.345 | 1.08 | 1.32 | -0.0121
CFLNonePGEECCExCZ03 | Com-Iltg-dWatt-CFL_OSnone | PGE | ECC | Ex | CZ03 | 1.53 | 0.000345 | 0 | 1.65 | 0.00043 | -0.0193 | 1.53 | 0.000345 | 0 | 1.65 | 0.00043 | -0.0193 | CFL | None | 1530 | 0.345 | 1530 | 0.345 | 1.08 | 1.25 | -0.0126
CFLNonePGEECCExCZ04 | Com-Iltg-dWatt-CFL_OSnone | PGE | ECC | Ex | CZ04 | 1.53 | 0.000532 | 0 | 1.69 | 0.000692 | -0.0148 | 1.53 | 0.000532 | 0 | 1.69 | 0.000692 | -0.0148 | CFL | None | 1530 | 0.532 | 1530 | 0.532 | 1.1 | 1.3 | -0.00967
CFLNoneSCEECCExCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | ECC | Ex | CZ05 | 1.53 | 0.000532 | 0 | 1.65 | 0.000658 | -0.0181 | 1.53 | 0.000532 | 0 | 1.65 | 0.000658 | -0.0181 | CFL | None | 1530 | 0.532 | 1530 | 0.532 | 1.08 | 1.24 | -0.0118
CFLNoneSCGECCExCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCG | ECC | Ex | CZ05 | 1.53 | 0.000532 | 0 | 1.65 | 0.000658 | -0.0181 | 1.53 | 0.000532 | 0 | 1.65 | 0.000658 | -0.0181 | CFL | None | 1530 | 0.532 | 1530 | 0.532 | 1.08 | 1.24 | -0.0118
CFLNonePGEECCExCZ05 | Com-Iltg-dWatt-CFL_OSnone | PGE | ECC | Ex | CZ05 | 1.53 | 0.000532 | 0 | 1.65 | 0.000658 | -0.0181 | 1.53 | 0.000532 | 0 | 1.65 | 0.000658 | -0.0181 | CFL | None | 1530 | 0.532 | 1530 | 0.532 | 1.08 | 1.24 | -0.0118
CFLNoneSCGECCExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCG | ECC | Ex | CZ06 | 1.53 | 0.000532 | 0 | 1.71 | 0.000679 | -0.00889 | 1.53 | 0.000532 | 0 | 1.71 | 0.000679 | -0.00889 | CFL | None | 1530 | 0.532 | 1530 | 0.532 | 1.12 | 1.28 | -0.00581
CFLNoneSCEECCExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | ECC | Ex | CZ06 | 1.53 | 0.000532 | 0 | 1.71 | 0.000679 | -0.00889 | 1.53 | 0.000532 | 0 | 1.71 | 0.000679 | -0.00889 | CFL | None | 1530 | 0.532 | 1530 | 0.532 | 1.12 | 1.28 | -0.00581
CFLNoneSDGECCExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SDG | ECC | Ex | CZ06 | 1.53 | 0.000532 | 0 | 1.71 | 0.000679 | -0.00889 | 1.53 | 0.000532 | 0 | 1.71 | 0.000679 | -0.00889 | CFL | None | 1530 | 0.532 | 1530 | 0.532 | 1.12 | 1.28 | -0.00581
CFLNoneSDGECCExCZ07 | Com-Iltg-dWatt-CFL_OSnone | SDG | ECC | Ex | CZ07 | 1.53 | 0.000532 | 0 | 1.73 | 0.000678 | -0.00734 | 1.53 | 0.000532 | 0 | 1.73 | 0.000678 | -0.00734 | CFL | None | 1530 | 0.532 | 1530 | 0.532 | 1.13 | 1.27 | -0.0048
CFLNoneSCGECCExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCG | ECC | Ex | CZ08 | 1.53 | 0.000532 | 0 | 1.74 | 0.000676 | -0.00799 | 1.53 | 0.000532 | 0 | 1.74 | 0.000676 | -0.00799 | CFL | None | 1530 | 0.532 | 1530 | 0.532 | 1.14 | 1.27 | -0.00522
CFLNoneSCEECCExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | ECC | Ex | CZ08 | 1.53 | 0.000532 | 0 | 1.74 | 0.000676 | -0.00799 | 1.53 | 0.000532 | 0 | 1.74 | 0.000676 | -0.00799 | CFL | None | 1530 | 0.532 | 1530 | 0.532 | 1.14 | 1.27 | -0.00522
CFLNoneSDGECCExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SDG | ECC | Ex | CZ08 | 1.53 | 0.000532 | 0 | 1.74 | 0.000676 | -0.00799 | 1.53 | 0.000532 | 0 | 1.74 | 0.000676 | -0.00799 | CFL | None | 1530 | 0.532 | 1530 | 0.532 | 1.14 | 1.27 | -0.00522
CFLNoneSCGECCExCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCG | ECC | Ex | CZ09 | 1.53 | 0.000532 | 0 | 1.76 | 0.000694 | -0.00889 | 1.53 | 0.000532 | 0 | 1.76 | 0.000694 | -0.00889 | CFL | None | 1530 | 0.532 | 1530 | 0.532 | 1.15 | 1.3 | -0.00581
CFLNoneSCEECCExCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | ECC | Ex | CZ09 | 1.53 | 0.000532 | 0 | 1.76 | 0.000694 | -0.00889 | 1.53 | 0.000532 | 0 | 1.76 | 0.000694 | -0.00889 | CFL | None | 1530 | 0.532 | 1530 | 0.532 | 1.15 | 1.3 | -0.00581
CFLNoneSDGECCExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SDG | ECC | Ex | CZ10 | 1.53 | 0.000532 | 0 | 1.73 | 0.000689 | -0.00947 | 1.53 | 0.000532 | 0 | 1.73 | 0.000689 | -0.00947 | CFL | None | 1530 | 0.532 | 1530 | 0.532 | 1.13 | 1.3 | -0.00619
CFLNoneSCGECCExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCG | ECC | Ex | CZ10 | 1.53 | 0.000532 | 0 | 1.73 | 0.000689 | -0.00947 | 1.53 | 0.000532 | 0 | 1.73 | 0.000689 | -0.00947 | CFL | None | 1530 | 0.532 | 1530 | 0.532 | 1.13 | 1.3 | -0.00619
CFLNoneSCEECCExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | ECC | Ex | CZ10 | 1.53 | 0.000532 | 0 | 1.73 | 0.000689 | -0.00947 | 1.53 | 0.000532 | 0 | 1.73 | 0.000689 | -0.00947 | CFL | None | 1530 | 0.532 | 1530 | 0.532 | 1.13 | 1.3 | -0.00619
CFLNonePGEECCExCZ11 | Com-Iltg-dWatt-CFL_OSnone | PGE | ECC | Ex | CZ11 | 1.53 | 0.000345 | 0 | 1.71 | 0.00043 | -0.017 | 1.53 | 0.000345 | 0 | 1.71 | 0.00043 | -0.017 | CFL | None | 1530 | 0.345 | 1530 | 0.345 | 1.12 | 1.25 | -0.0111
CFLNonePGEECCExCZ12 | Com-Iltg-dWatt-CFL_OSnone | PGE | ECC | Ex | CZ12 | 1.53 | 0.000345 | 0 | 1.7 | 0.000434 | -0.0167 | 1.53 | 0.000345 | 0 | 1.7 | 0.000434 | -0.0167 | CFL | None | 1530 | 0.345 | 1530 | 0.345 | 1.11 | 1.26 | -0.0109
CFLNonePGEECCExCZ13 | Com-Iltg-dWatt-CFL_OSnone | PGE | ECC | Ex | CZ13 | 1.53 | 0.000345 | 0 | 1.72 | 0.000447 | -0.0134 | 1.53 | 0.000345 | 0 | 1.72 | 0.000447 | -0.0134 | CFL | None | 1530 | 0.345 | 1530 | 0.345 | 1.12 | 1.3 | -0.00876
CFLNoneSCGECCExCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCG | ECC | Ex | CZ13 | 1.53 | 0.000345 | 0 | 1.72 | 0.000447 | -0.0134 | 1.53 | 0.000345 | 0 | 1.72 | 0.000447 | -0.0134 | CFL | None | 1530 | 0.345 | 1530 | 0.345 | 1.12 | 1.3 | -0.00876
CFLNoneSCEECCExCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | ECC | Ex | CZ13 | 1.53 | 0.000345 | 0 | 1.72 | 0.000447 | -0.0134 | 1.53 | 0.000345 | 0 | 1.72 | 0.000447 | -0.0134 | CFL | None | 1530 | 0.345 | 1530 | 0.345 | 1.12 | 1.3 | -0.00876
CFLNoneSDGECCExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SDG | ECC | Ex | CZ14 | 1.53 | 0.000532 | 0 | 1.69 | 0.000679 | -0.0143 | 1.53 | 0.000532 | 0 | 1.69 | 0.000679 | -0.0143 | CFL | None | 1530 | 0.532 | 1530 | 0.532 | 1.1 | 1.28 | -0.00935
CFLNoneSCEECCExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | ECC | Ex | CZ14 | 1.53 | 0.000532 | 0 | 1.69 | 0.000679 | -0.0143 | 1.53 | 0.000532 | 0 | 1.69 | 0.000679 | -0.0143 | CFL | None | 1530 | 0.532 | 1530 | 0.532 | 1.1 | 1.28 | -0.00935
CFLNoneSCGECCExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCG | ECC | Ex | CZ14 | 1.53 | 0.000532 | 0 | 1.69 | 0.000679 | -0.0143 | 1.53 | 0.000532 | 0 | 1.69 | 0.000679 | -0.0143 | CFL | None | 1530 | 0.532 | 1530 | 0.532 | 1.1 | 1.28 | -0.00935
CFLNoneSCGECCExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCG | ECC | Ex | CZ15 | 1.53 | 0.000532 | 0 | 1.83 | 0.000672 | -0.00393 | 1.53 | 0.000532 | 0 | 1.83 | 0.000672 | -0.00393 | CFL | None | 1530 | 0.532 | 1530 | 0.532 | 1.2 | 1.26 | -0.00257
CFLNoneSCEECCExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | ECC | Ex | CZ15 | 1.53 | 0.000532 | 0 | 1.83 | 0.000672 | -0.00393 | 1.53 | 0.000532 | 0 | 1.83 | 0.000672 | -0.00393 | CFL | None | 1530 | 0.532 | 1530 | 0.532 | 1.2 | 1.26 | -0.00257
CFLNoneSCGECCExCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCG | ECC | Ex | CZ16 | 1.53 | 0.000345 | 0 | 1.59 | 0.000425 | -0.0252 | 1.53 | 0.000345 | 0 | 1.59 | 0.000425 | -0.0252 | CFL | None | 1530 | 0.345 | 1530 | 0.345 | 1.04 | 1.23 | -0.0165
CFLNoneSCEECCExCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | ECC | Ex | CZ16 | 1.53 | 0.000345 | 0 | 1.59 | 0.000425 | -0.0252 | 1.53 | 0.000345 | 0 | 1.59 | 0.000425 | -0.0252 | CFL | None | 1530 | 0.345 | 1530 | 0.345 | 1.04 | 1.23 | -0.0165
CFLNonePGEECCExCZ16 | Com-Iltg-dWatt-CFL_OSnone | PGE | ECC | Ex | CZ16 | 1.53 | 0.000345 | 0 | 1.59 | 0.000425 | -0.0252 | 1.53 | 0.000345 | 0 | 1.59 | 0.000425 | -0.0252 | CFL | None | 1530 | 0.345 | 1530 | 0.345 | 1.04 | 1.23 | -0.0165
CFLNoneSCEECCExIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | ECC | Ex | IOU | 1.53 | 0.000514 | 0 | 1.72 | 0.000656 | -0.00995 | 1.53 | 0.000514 | 0 | 1.72 | 0.000656 | -0.00995 | CFL | None | 1530 | 0.514 | 1530 | 0.514 | 1.12 | 1.28 | -0.0065
CFLNoneSDGECCExIOU | Com-Iltg-dWatt-CFL_OSnone | SDG | ECC | Ex | IOU | 1.53 | 0.000532 | 0 | 1.73 | 0.000681 | -0.00789 | 1.53 | 0.000532 | 0 | 1.73 | 0.000681 | -0.00789 | CFL | None | 1530 | 0.532 | 1530 | 0.532 | 1.13 | 1.28 | -0.00516
CFLNonePGEECCExIOU | Com-Iltg-dWatt-CFL_OSnone | PGE | ECC | Ex | IOU | 1.53 | 0.000381 | 0 | 1.67 | 0.000481 | -0.0177 | 1.53 | 0.000381 | 0 | 1.67 | 0.000481 | -0.0177 | CFL | None | 1530 | 0.381 | 1530 | 0.381 | 1.09 | 1.26 | -0.0116
CFLNoneSCGECCExIOU | Com-Iltg-dWatt-CFL_OSnone | SCG | ECC | Ex | IOU | 1.53 | 0.00052 | 0 | 1.73 | 0.000666 | -0.00958 | 1.53 | 0.00052 | 0 | 1.73 | 0.000666 | -0.00958 | CFL | None | 1530 | 0.52 | 1530 | 0.52 | 1.13 | 1.28 | -0.00626
CFLNonePGEECCNewCZ01 | Com-Iltg-dWatt-CFL_OSnone | PGE | ECC | New | CZ01 | 1.53 | 0.000532 | 0 | 1.56 | 0.000621 | -0.0312 | 1.53 | 0.000532 | 0 | 1.56 | 0.000621 | -0.0312 | CFL | None | 1530 | 0.532 | 1530 | 0.532 | 1.02 | 1.17 | -0.0204
CFLNonePGEECCNewCZ02 | Com-Iltg-dWatt-CFL_OSnone | PGE | ECC | New | CZ02 | 1.53 | 0.000345 | 0 | 1.65 | 0.00047 | -0.019 | 1.53 | 0.000345 | 0 | 1.65 | 0.00047 | -0.019 | CFL | None | 1530 | 0.345 | 1530 | 0.345 | 1.08 | 1.36 | -0.0124
CFLNonePGEECCNewCZ03 | Com-Iltg-dWatt-CFL_OSnone | PGE | ECC | New | CZ03 | 1.53 | 0.000345 | 0 | 1.62 | 0.000452 | -0.0208 | 1.53 | 0.000345 | 0 | 1.62 | 0.000452 | -0.0208 | CFL | None | 1530 | 0.345 | 1530 | 0.345 | 1.06 | 1.31 | -0.0136
CFLNonePGEECCNewCZ04 | Com-Iltg-dWatt-CFL_OSnone | PGE | ECC | New | CZ04 | 1.53 | 0.000532 | 0 | 1.67 | 0.000676 | -0.0153 | 1.53 | 0.000532 | 0 | 1.67 | 0.000676 | -0.0153 | CFL | None | 1530 | 0.532 | 1530 | 0.532 | 1.09 | 1.27 | -0.01
CFLNoneSCEECCNewCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | ECC | New | CZ05 | 1.53 | 0.000532 | 0 | 1.63 | 0.000673 | -0.021 | 1.53 | 0.000532 | 0 | 1.63 | 0.000673 | -0.021 | CFL | None | 1530 | 0.532 | 1530 | 0.532 | 1.07 | 1.27 | -0.0137
CFLNonePGEECCNewCZ05 | Com-Iltg-dWatt-CFL_OSnone | PGE | ECC | New | CZ05 | 1.53 | 0.000532 | 0 | 1.63 | 0.000653 | -0.0202 | 1.53 | 0.000532 | 0 | 1.63 | 0.000653 | -0.0202 | CFL | None | 1530 | 0.532 | 1530 | 0.532 | 1.07 | 1.23 | -0.0132
CFLNoneSDGECCNewCZ06 | Com-Iltg-dWatt-CFL_OSnone | SDG | ECC | New | CZ06 | 1.53 | 0.000532 | 0 | 1.72 | 0.000683 | -0.0108 | 1.53 | 0.000532 | 0 | 1.72 | 0.000683 | -0.0108 | CFL | None | 1530 | 0.532 | 1530 | 0.532 | 1.12 | 1.28 | -0.00706
CFLNoneSCEECCNewCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | ECC | New | CZ06 | 1.53 | 0.000532 | 0 | 1.72 | 0.000688 | -0.0109 | 1.53 | 0.000532 | 0 | 1.72 | 0.000688 | -0.0109 | CFL | None | 1530 | 0.532 | 1530 | 0.532 | 1.12 | 1.29 | -0.00712
CFLNoneSDGECCNewCZ07 | Com-Iltg-dWatt-CFL_OSnone | SDG | ECC | New | CZ07 | 1.53 | 0.000532 | 0 | 1.72 | 0.000688 | -0.00812 | 1.53 | 0.000532 | 0 | 1.72 | 0.000688 | -0.00812 | CFL | None | 1530 | 0.532 | 1530 | 0.532 | 1.12 | 1.29 | -0.00531
CFLNoneSCEECCNewCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | ECC | New | CZ08 | 1.53 | 0.000532 | 0 | 1.73 | 0.000688 | -0.00771 | 1.53 | 0.000532 | 0 | 1.73 | 0.000688 | -0.00771 | CFL | None | 1530 | 0.532 | 1530 | 0.532 | 1.13 | 1.29 | -0.00504
CFLNoneSDGECCNewCZ08 | Com-Iltg-dWatt-CFL_OSnone | SDG | ECC | New | CZ08 | 1.53 | 0.000532 | 0 | 1.73 | 0.000682 | -0.00793 | 1.53 | 0.000532 | 0 | 1.73 | 0.000682 | -0.00793 | CFL | None | 1530 | 0.532 | 1530 | 0.532 | 1.13 | 1.28 | -0.00518
CFLNoneSCEECCNewCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | ECC | New | CZ09 | 1.53 | 0.000532 | 0 | 1.73 | 0.000707 | -0.00897 | 1.53 | 0.000532 | 0 | 1.73 | 0.000707 | -0.00897 | CFL | None | 1530 | 0.532 | 1530 | 0.532 | 1.13 | 1.33 | -0.00586
CFLNoneSDGECCNewCZ10 | Com-Iltg-dWatt-CFL_OSnone | SDG | ECC | New | CZ10 | 1.53 | 0.000532 | 0 | 1.75 | 0.000703 | -0.00901 | 1.53 | 0.000532 | 0 | 1.75 | 0.000703 | -0.00901 | CFL | None | 1530 | 0.532 | 1530 | 0.532 | 1.14 | 1.32 | -0.00589
CFLNoneSCEECCNewCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | ECC | New | CZ10 | 1.53 | 0.000532 | 0 | 1.75 | 0.000714 | -0.0089 | 1.53 | 0.000532 | 0 | 1.75 | 0.000714 | -0.0089 | CFL | None | 1530 | 0.532 | 1530 | 0.532 | 1.14 | 1.34 | -0.00582
CFLNonePGEECCNewCZ11 | Com-Iltg-dWatt-CFL_OSnone | PGE | ECC | New | CZ11 | 1.53 | 0.000345 | 0 | 1.7 | 0.000461 | -0.0159 | 1.53 | 0.000345 | 0 | 1.7 | 0.000461 | -0.0159 | CFL | None | 1530 | 0.345 | 1530 | 0.345 | 1.11 | 1.34 | -0.0104
CFLNonePGEECCNewCZ12 | Com-Iltg-dWatt-CFL_OSnone | PGE | ECC | New | CZ12 | 1.53 | 0.000345 | 0 | 1.69 | 0.000471 | -0.0162 | 1.53 | 0.000345 | 0 | 1.69 | 0.000471 | -0.0162 | CFL | None | 1530 | 0.345 | 1530 | 0.345 | 1.1 | 1.37 | -0.0106
CFLNoneSCEECCNewCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | ECC | New | CZ13 | 1.53 | 0.000345 | 0 | 1.73 | 0.000485 | -0.0139 | 1.53 | 0.000345 | 0 | 1.73 | 0.000485 | -0.0139 | CFL | None | 1530 | 0.345 | 1530 | 0.345 | 1.13 | 1.41 | -0.00908
CFLNonePGEECCNewCZ13 | Com-Iltg-dWatt-CFL_OSnone | PGE | ECC | New | CZ13 | 1.53 | 0.000345 | 0 | 1.72 | 0.000466 | -0.0139 | 1.53 | 0.000345 | 0 | 1.72 | 0.000466 | -0.0139 | CFL | None | 1530 | 0.345 | 1530 | 0.345 | 1.12 | 1.35 | -0.00908
CFLNoneSCEECCNewCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | ECC | New | CZ14 | 1.53 | 0.000532 | 0 | 1.72 | 0.000693 | -0.0145 | 1.53 | 0.000532 | 0 | 1.72 | 0.000693 | -0.0145 | CFL | None | 1530 | 0.532 | 1530 | 0.532 | 1.12 | 1.3 | -0.00948
CFLNoneSDGECCNewCZ14 | Com-Iltg-dWatt-CFL_OSnone | SDG | ECC | New | CZ14 | 1.53 | 0.000532 | 0 | 1.73 | 0.000681 | -0.0142 | 1.53 | 0.000532 | 0 | 1.73 | 0.000681 | -0.0142 | CFL | None | 1530 | 0.532 | 1530 | 0.532 | 1.13 | 1.28 | -0.00928
CFLNoneSCEECCNewCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | ECC | New | CZ15 | 1.53 | 0.000532 | 0 | 1.86 | 0.000712 | -0.00341 | 1.53 | 0.000532 | 0 | 1.86 | 0.000712 | -0.00341 | CFL | None | 1530 | 0.532 | 1530 | 0.532 | 1.22 | 1.34 | -0.00223
CFLNoneSDGECCNewCZ15 | Com-Iltg-dWatt-CFL_OSnone | SDG | ECC | New | CZ15 | 1.53 | 0.000532 | 0 | 1.85 | 0.000697 | -0.00353 | 1.53 | 0.000532 | 0 | 1.85 | 0.000697 | -0.00353 | CFL | None | 1530 | 0.532 | 1530 | 0.532 | 1.21 | 1.31 | -0.00231
CFLNoneSCEECCNewCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | ECC | New | CZ16 | 1.53 | 0.000345 | 0 | 1.6 | 0.000464 | -0.026 | 1.53 | 0.000345 | 0 | 1.6 | 0.000464 | -0.026 | CFL | None | 1530 | 0.345 | 1530 | 0.345 | 1.05 | 1.34 | -0.017
CFLNonePGEECCNewCZ16 | Com-Iltg-dWatt-CFL_OSnone | PGE | ECC | New | CZ16 | 1.53 | 0.000345 | 0 | 1.61 | 0.000447 | -0.0254 | 1.53 | 0.000345 | 0 | 1.61 | 0.000447 | -0.0254 | CFL | None | 1530 | 0.345 | 1530 | 0.345 | 1.05 | 1.3 | -0.0166
CFLNoneSCEECCNewIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | ECC | New | IOU | 1.53 | 0.000532 | 0 | 1.74 | 0.000688 | -0.00906 | 1.53 | 0.000532 | 0 | 1.74 | 0.000688 | -0.00906 | CFL | None | 1530 | 0.532 | 1530 | 0.532 | 1.14 | 1.29 | -0.00592
CFLNoneSCGECCNewIOU | Com-Iltg-dWatt-CFL_OSnone | SCG | ECC | New | IOU | 1.53 | 0.000532 | 0 | 1.74 | 0.000688 | -0.00905 | 1.53 | 0.000532 | 0 | 1.74 | 0.000688 | -0.00905 | CFL | None | 1530 | 0.532 | 1530 | 0.532 | 1.14 | 1.29 | -0.00592
CFLNonePGEECCNewIOU | Com-Iltg-dWatt-CFL_OSnone | PGE | ECC | New | IOU | 1.53 | 0.000401 | 0 | 1.7 | 0.000541 | -0.0162 | 1.53 | 0.000401 | 0 | 1.7 | 0.000541 | -0.0162 | CFL | None | 1530 | 0.401 | 1530 | 0.401 | 1.11 | 1.35 | -0.0106
CFLNoneSDGECCNewIOU | Com-Iltg-dWatt-CFL_OSnone | SDG | ECC | New | IOU | 1.53 | 0.000532 | 0 | 1.73 | 0.000691 | -0.00837 | 1.53 | 0.000532 | 0 | 1.73 | 0.000691 | -0.00837 | CFL | None | 1530 | 0.532 | 1530 | 0.532 | 1.13 | 1.3 | -0.00547
CFLNonePGEEPrExCZ01 | Com-Iltg-dWatt-CFL_OSnone | PGE | EPr | Ex | CZ01 | 1.23 | 0.000421 | 0 | 1.22 | 0.000501 | -0.0221 | 1.23 | 0.000421 | 0 | 1.22 | 0.000501 | -0.0221 | CFL | None | 1230 | 0.421 | 1230 | 0.421 | 0.992 | 1.19 | -0.018
CFLNonePGEEPrExCZ02 | Com-Iltg-dWatt-CFL_OSnone | PGE | EPr | Ex | CZ02 | 1.23 | 1.34e-05 | 0 | 1.29 | 1.34e-05 | -0.0133 | 1.23 | 1.34e-05 | 0 | 1.29 | 1.34e-05 | -0.0133 | CFL | None | 1230 | 0.0134 | 1230 | 0.0134 | 1.05 | 1 | -0.0108
CFLNonePGEEPrExCZ03 | Com-Iltg-dWatt-CFL_OSnone | PGE | EPr | Ex | CZ03 | 1.23 | 1.34e-05 | 0 | 1.31 | 1.34e-05 | -0.0129 | 1.23 | 1.34e-05 | 0 | 1.31 | 1.34e-05 | -0.0129 | CFL | None | 1230 | 0.0134 | 1230 | 0.0134 | 1.07 | 1 | -0.0105
CFLNonePGEEPrExCZ04 | Com-Iltg-dWatt-CFL_OSnone | PGE | EPr | Ex | CZ04 | 1.23 | 0.000421 | 0 | 1.32 | 0.000516 | -0.0102 | 1.23 | 0.000421 | 0 | 1.32 | 0.000516 | -0.0102 | CFL | None | 1230 | 0.421 | 1230 | 0.421 | 1.07 | 1.23 | -0.00829
CFLNoneSCGEPrExCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCG | EPr | Ex | CZ05 | 1.23 | 0.000421 | 0 | 1.34 | 0.000533 | -0.0112 | 1.23 | 0.000421 | 0 | 1.34 | 0.000533 | -0.0112 | CFL | None | 1230 | 0.421 | 1230 | 0.421 | 1.09 | 1.27 | -0.00911
CFLNonePGEEPrExCZ05 | Com-Iltg-dWatt-CFL_OSnone | PGE | EPr | Ex | CZ05 | 1.23 | 0.000421 | 0 | 1.34 | 0.000533 | -0.0112 | 1.23 | 0.000421 | 0 | 1.34 | 0.000533 | -0.0112 | CFL | None | 1230 | 0.421 | 1230 | 0.421 | 1.09 | 1.27 | -0.00911
CFLNoneSCEEPrExCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | EPr | Ex | CZ05 | 1.23 | 0.000421 | 0 | 1.34 | 0.000533 | -0.0112 | 1.23 | 0.000421 | 0 | 1.34 | 0.000533 | -0.0112 | CFL | None | 1230 | 0.421 | 1230 | 0.421 | 1.09 | 1.27 | -0.00911
CFLNoneSDGEPrExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SDG | EPr | Ex | CZ06 | 1.23 | 0.000421 | 0 | 1.39 | 0.000537 | -0.00573 | 1.23 | 0.000421 | 0 | 1.39 | 0.000537 | -0.00573 | CFL | None | 1230 | 0.421 | 1230 | 0.421 | 1.13 | 1.28 | -0.00466
CFLNoneSCEEPrExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | EPr | Ex | CZ06 | 1.23 | 0.000421 | 0 | 1.39 | 0.000537 | -0.00573 | 1.23 | 0.000421 | 0 | 1.39 | 0.000537 | -0.00573 | CFL | None | 1230 | 0.421 | 1230 | 0.421 | 1.13 | 1.28 | -0.00466
CFLNoneSCGEPrExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCG | EPr | Ex | CZ06 | 1.23 | 0.000421 | 0 | 1.39 | 0.000537 | -0.00573 | 1.23 | 0.000421 | 0 | 1.39 | 0.000537 | -0.00573 | CFL | None | 1230 | 0.421 | 1230 | 0.421 | 1.13 | 1.28 | -0.00466
CFLNoneSDGEPrExCZ07 | Com-Iltg-dWatt-CFL_OSnone | SDG | EPr | Ex | CZ07 | 1.23 | 0.000421 | 0 | 1.39 | 0.000542 | -0.00528 | 1.23 | 0.000421 | 0 | 1.39 | 0.000542 | -0.00528 | CFL | None | 1230 | 0.421 | 1230 | 0.421 | 1.13 | 1.29 | -0.00429
CFLNoneSCEEPrExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | EPr | Ex | CZ08 | 1.23 | 0.000421 | 0 | 1.4 | 0.000542 | -0.00482 | 1.23 | 0.000421 | 0 | 1.4 | 0.000542 | -0.00482 | CFL | None | 1230 | 0.421 | 1230 | 0.421 | 1.14 | 1.29 | -0.00392
CFLNoneSCGEPrExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCG | EPr | Ex | CZ08 | 1.23 | 0.000421 | 0 | 1.4 | 0.000542 | -0.00482 | 1.23 | 0.000421 | 0 | 1.4 | 0.000542 | -0.00482 | CFL | None | 1230 | 0.421 | 1230 | 0.421 | 1.14 | 1.29 | -0.00392
CFLNoneSDGEPrExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SDG | EPr | Ex | CZ08 | 1.23 | 0.000421 | 0 | 1.4 | 0.000542 | -0.00482 | 1.23 | 0.000421 | 0 | 1.4 | 0.000542 | -0.00482 | CFL | None | 1230 | 0.421 | 1230 | 0.421 | 1.14 | 1.29 | -0.00392
CFLNoneSCGEPrExCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCG | EPr | Ex | CZ09 | 1.23 | 0.000421 | 0 | 1.42 | 0.000549 | -0.00569 | 1.23 | 0.000421 | 0 | 1.42 | 0.000549 | -0.00569 | CFL | None | 1230 | 0.421 | 1230 | 0.421 | 1.15 | 1.3 | -0.00463
CFLNoneSCEEPrExCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | EPr | Ex | CZ09 | 1.23 | 0.000421 | 0 | 1.42 | 0.000549 | -0.00569 | 1.23 | 0.000421 | 0 | 1.42 | 0.000549 | -0.00569 | CFL | None | 1230 | 0.421 | 1230 | 0.421 | 1.15 | 1.3 | -0.00463
CFLNoneSCEEPrExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | EPr | Ex | CZ10 | 1.23 | 0.000421 | 0 | 1.39 | 0.000537 | -0.00606 | 1.23 | 0.000421 | 0 | 1.39 | 0.000537 | -0.00606 | CFL | None | 1230 | 0.421 | 1230 | 0.421 | 1.13 | 1.28 | -0.00493
CFLNoneSCGEPrExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCG | EPr | Ex | CZ10 | 1.23 | 0.000421 | 0 | 1.39 | 0.000537 | -0.00606 | 1.23 | 0.000421 | 0 | 1.39 | 0.000537 | -0.00606 | CFL | None | 1230 | 0.421 | 1230 | 0.421 | 1.13 | 1.28 | -0.00493
CFLNoneSDGEPrExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SDG | EPr | Ex | CZ10 | 1.23 | 0.000421 | 0 | 1.39 | 0.000537 | -0.00606 | 1.23 | 0.000421 | 0 | 1.39 | 0.000537 | -0.00606 | CFL | None | 1230 | 0.421 | 1230 | 0.421 | 1.13 | 1.28 | -0.00493
CFLNonePGEEPrExCZ11 | Com-Iltg-dWatt-CFL_OSnone | PGE | EPr | Ex | CZ11 | 1.23 | 1.34e-05 | 0 | 1.3 | 1.34e-05 | -0.0122 | 1.23 | 1.34e-05 | 0 | 1.3 | 1.34e-05 | -0.0122 | CFL | None | 1230 | 0.0134 | 1230 | 0.0134 | 1.06 | 1 | -0.00992
CFLNonePGEEPrExCZ12 | Com-Iltg-dWatt-CFL_OSnone | PGE | EPr | Ex | CZ12 | 1.23 | 1.34e-05 | 0 | 1.3 | 1.34e-05 | -0.0127 | 1.23 | 1.34e-05 | 0 | 1.3 | 1.34e-05 | -0.0127 | CFL | None | 1230 | 0.0134 | 1230 | 0.0134 | 1.06 | 1 | -0.0103
CFLNoneSCGEPrExCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCG | EPr | Ex | CZ13 | 1.23 | 1.34e-05 | 0 | 1.34 | 1.34e-05 | -0.0102 | 1.23 | 1.34e-05 | 0 | 1.34 | 1.34e-05 | -0.0102 | CFL | None | 1230 | 0.0134 | 1230 | 0.0134 | 1.09 | 1 | -0.00829
CFLNonePGEEPrExCZ13 | Com-Iltg-dWatt-CFL_OSnone | PGE | EPr | Ex | CZ13 | 1.23 | 1.34e-05 | 0 | 1.34 | 1.34e-05 | -0.0102 | 1.23 | 1.34e-05 | 0 | 1.34 | 1.34e-05 | -0.0102 | CFL | None | 1230 | 0.0134 | 1230 | 0.0134 | 1.09 | 1 | -0.00829
CFLNoneSCEEPrExCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | EPr | Ex | CZ13 | 1.23 | 1.34e-05 | 0 | 1.34 | 1.34e-05 | -0.0102 | 1.23 | 1.34e-05 | 0 | 1.34 | 1.34e-05 | -0.0102 | CFL | None | 1230 | 0.0134 | 1230 | 0.0134 | 1.09 | 1 | -0.00829
CFLNoneSDGEPrExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SDG | EPr | Ex | CZ14 | 1.23 | 0.000421 | 0 | 1.34 | 0.000538 | -0.0101 | 1.23 | 0.000421 | 0 | 1.34 | 0.000538 | -0.0101 | CFL | None | 1230 | 0.421 | 1230 | 0.421 | 1.09 | 1.28 | -0.00821
CFLNoneSCGEPrExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCG | EPr | Ex | CZ14 | 1.23 | 0.000421 | 0 | 1.34 | 0.000538 | -0.0101 | 1.23 | 0.000421 | 0 | 1.34 | 0.000538 | -0.0101 | CFL | None | 1230 | 0.421 | 1230 | 0.421 | 1.09 | 1.28 | -0.00821
CFLNoneSCEEPrExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | EPr | Ex | CZ14 | 1.23 | 0.000421 | 0 | 1.34 | 0.000538 | -0.0101 | 1.23 | 0.000421 | 0 | 1.34 | 0.000538 | -0.0101 | CFL | None | 1230 | 0.421 | 1230 | 0.421 | 1.09 | 1.28 | -0.00821
CFLNoneSDGEPrExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SDG | EPr | Ex | CZ15 | 1.23 | 0.000421 | 0 | 1.49 | 0.00054 | -0.00257 | 1.23 | 0.000421 | 0 | 1.49 | 0.00054 | -0.00257 | CFL | None | 1230 | 0.421 | 1230 | 0.421 | 1.21 | 1.28 | -0.00209
CFLNoneSCEEPrExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | EPr | Ex | CZ15 | 1.23 | 0.000421 | 0 | 1.49 | 0.00054 | -0.00257 | 1.23 | 0.000421 | 0 | 1.49 | 0.00054 | -0.00257 | CFL | None | 1230 | 0.421 | 1230 | 0.421 | 1.21 | 1.28 | -0.00209
CFLNoneSCGEPrExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCG | EPr | Ex | CZ15 | 1.23 | 0.000421 | 0 | 1.49 | 0.00054 | -0.00257 | 1.23 | 0.000421 | 0 | 1.49 | 0.00054 | -0.00257 | CFL | None | 1230 | 0.421 | 1230 | 0.421 | 1.21 | 1.28 | -0.00209
CFLNoneSCGEPrExCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCG | EPr | Ex | CZ16 | 1.23 | 1.34e-05 | 0 | 1.19 | 1.34e-05 | -0.0202 | 1.23 | 1.34e-05 | 0 | 1.19 | 1.34e-05 | -0.0202 | CFL | None | 1230 | 0.0134 | 1230 | 0.0134 | 0.967 | 1 | -0.0164
CFLNonePGEEPrExCZ16 | Com-Iltg-dWatt-CFL_OSnone | PGE | EPr | Ex | CZ16 | 1.23 | 1.34e-05 | 0 | 1.19 | 1.34e-05 | -0.0202 | 1.23 | 1.34e-05 | 0 | 1.19 | 1.34e-05 | -0.0202 | CFL | None | 1230 | 0.0134 | 1230 | 0.0134 | 0.967 | 1 | -0.0164
CFLNoneSCEEPrExCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | EPr | Ex | CZ16 | 1.23 | 1.34e-05 | 0 | 1.19 | 1.34e-05 | -0.0202 | 1.23 | 1.34e-05 | 0 | 1.19 | 1.34e-05 | -0.0202 | CFL | None | 1230 | 0.0134 | 1230 | 0.0134 | 0.967 | 1 | -0.0164
CFLNoneSCGEPrExIOU | Com-Iltg-dWatt-CFL_OSnone | SCG | EPr | Ex | IOU | 1.23 | 0.000399 | 0 | 1.39 | 0.000514 | -0.00609 | 1.23 | 0.000399 | 0 | 1.39 | 0.000514 | -0.00609 | CFL | None | 1230 | 0.399 | 1230 | 0.399 | 1.13 | 1.29 | -0.00495
CFLNoneSCEEPrExIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | EPr | Ex | IOU | 1.23 | 0.000394 | 0 | 1.39 | 0.000506 | -0.00623 | 1.23 | 0.000394 | 0 | 1.39 | 0.000506 | -0.00623 | CFL | None | 1230 | 0.394 | 1230 | 0.394 | 1.13 | 1.28 | -0.00507
CFLNonePGEEPrExIOU | Com-Iltg-dWatt-CFL_OSnone | PGE | EPr | Ex | IOU | 1.23 | 8.51e-05 | 0 | 1.31 | 0.000102 | -0.0121 | 1.23 | 8.51e-05 | 0 | 1.31 | 0.000102 | -0.0121 | CFL | None | 1230 | 0.0851 | 1230 | 0.0851 | 1.07 | 1.2 | -0.00984
CFLNoneSDGEPrExIOU | Com-Iltg-dWatt-CFL_OSnone | SDG | EPr | Ex | IOU | 1.23 | 0.000421 | 0 | 1.39 | 0.00054 | -0.00557 | 1.23 | 0.000421 | 0 | 1.39 | 0.00054 | -0.00557 | CFL | None | 1230 | 0.421 | 1230 | 0.421 | 1.13 | 1.28 | -0.00453
CFLNonePGEEPrNewCZ01 | Com-Iltg-dWatt-CFL_OSnone | PGE | EPr | New | CZ01 | 1.23 | 0.000421 | 0 | 1.21 | 0.000485 | -0.0262 | 1.23 | 0.000421 | 0 | 1.21 | 0.000485 | -0.0262 | CFL | None | 1230 | 0.421 | 1230 | 0.421 | 0.984 | 1.15 | -0.0213
CFLNonePGEEPrNewCZ02 | Com-Iltg-dWatt-CFL_OSnone | PGE | EPr | New | CZ02 | 1.23 | 1.34e-05 | 0 | 1.28 | 1.34e-05 | -0.0169 | 1.23 | 1.34e-05 | 0 | 1.28 | 1.34e-05 | -0.0169 | CFL | None | 1230 | 0.0134 | 1230 | 0.0134 | 1.04 | 1 | -0.0137
CFLNonePGEEPrNewCZ03 | Com-Iltg-dWatt-CFL_OSnone | PGE | EPr | New | CZ03 | 1.23 | 1.34e-05 | 0 | 1.27 | 1.34e-05 | -0.016 | 1.23 | 1.34e-05 | 0 | 1.27 | 1.34e-05 | -0.016 | CFL | None | 1230 | 0.0134 | 1230 | 0.0134 | 1.03 | 1 | -0.013
CFLNonePGEEPrNewCZ04 | Com-Iltg-dWatt-CFL_OSnone | PGE | EPr | New | CZ04 | 1.23 | 0.000421 | 0 | 1.31 | 0.000547 | -0.013 | 1.23 | 0.000421 | 0 | 1.31 | 0.000547 | -0.013 | CFL | None | 1230 | 0.421 | 1230 | 0.421 | 1.07 | 1.3 | -0.0106
CFLNonePGEEPrNewCZ05 | Com-Iltg-dWatt-CFL_OSnone | PGE | EPr | New | CZ05 | 1.23 | 0.000421 | 0 | 1.28 | 0.00052 | -0.0133 | 1.23 | 0.000421 | 0 | 1.28 | 0.00052 | -0.0133 | CFL | None | 1230 | 0.421 | 1230 | 0.421 | 1.04 | 1.24 | -0.0108
CFLNoneSCEEPrNewCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | EPr | New | CZ05 | 1.23 | 0.000421 | 0 | 1.28 | 0.000543 | -0.0122 | 1.23 | 0.000421 | 0 | 1.28 | 0.000543 | -0.0122 | CFL | None | 1230 | 0.421 | 1230 | 0.421 | 1.04 | 1.29 | -0.00992
CFLNoneSCEEPrNewCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | EPr | New | CZ06 | 1.23 | 0.000421 | 0 | 1.35 | 0.000567 | -0.00772 | 1.23 | 0.000421 | 0 | 1.35 | 0.000567 | -0.00772 | CFL | None | 1230 | 0.421 | 1230 | 0.421 | 1.1 | 1.35 | -0.00628
CFLNoneSDGEPrNewCZ06 | Com-Iltg-dWatt-CFL_OSnone | SDG | EPr | New | CZ06 | 1.23 | 0.000421 | 0 | 1.35 | 0.000563 | -0.00781 | 1.23 | 0.000421 | 0 | 1.35 | 0.000563 | -0.00781 | CFL | None | 1230 | 0.421 | 1230 | 0.421 | 1.1 | 1.34 | -0.00635
CFLNoneSDGEPrNewCZ07 | Com-Iltg-dWatt-CFL_OSnone | SDG | EPr | New | CZ07 | 1.23 | 0.000421 | 0 | 1.33 | 0.000557 | -0.00727 | 1.23 | 0.000421 | 0 | 1.33 | 0.000557 | -0.00727 | CFL | None | 1230 | 0.421 | 1230 | 0.421 | 1.08 | 1.32 | -0.00591
CFLNoneSDGEPrNewCZ08 | Com-Iltg-dWatt-CFL_OSnone | SDG | EPr | New | CZ08 | 1.23 | 0.000421 | 0 | 1.37 | 0.000578 | -0.0067 | 1.23 | 0.000421 | 0 | 1.37 | 0.000578 | -0.0067 | CFL | None | 1230 | 0.421 | 1230 | 0.421 | 1.11 | 1.37 | -0.00545
CFLNoneSCEEPrNewCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | EPr | New | CZ08 | 1.23 | 0.000421 | 0 | 1.38 | 0.000583 | -0.00663 | 1.23 | 0.000421 | 0 | 1.38 | 0.000583 | -0.00663 | CFL | None | 1230 | 0.421 | 1230 | 0.421 | 1.12 | 1.38 | -0.00539
CFLNoneSCEEPrNewCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | EPr | New | CZ09 | 1.23 | 0.000421 | 0 | 1.37 | 0.000594 | -0.00753 | 1.23 | 0.000421 | 0 | 1.37 | 0.000594 | -0.00753 | CFL | None | 1230 | 0.421 | 1230 | 0.421 | 1.11 | 1.41 | -0.00612
CFLNoneSDGEPrNewCZ10 | Com-Iltg-dWatt-CFL_OSnone | SDG | EPr | New | CZ10 | 1.23 | 0.000421 | 0 | 1.37 | 0.000599 | -0.00808 | 1.23 | 0.000421 | 0 | 1.37 | 0.000599 | -0.00808 | CFL | None | 1230 | 0.421 | 1230 | 0.421 | 1.11 | 1.42 | -0.00657
CFLNoneSCEEPrNewCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | EPr | New | CZ10 | 1.23 | 0.000421 | 0 | 1.38 | 0.000604 | -0.00798 | 1.23 | 0.000421 | 0 | 1.38 | 0.000604 | -0.00798 | CFL | None | 1230 | 0.421 | 1230 | 0.421 | 1.12 | 1.43 | -0.00649
CFLNonePGEEPrNewCZ11 | Com-Iltg-dWatt-CFL_OSnone | PGE | EPr | New | CZ11 | 1.23 | 1.34e-05 | 0 | 1.32 | 1.34e-05 | -0.0148 | 1.23 | 1.34e-05 | 0 | 1.32 | 1.34e-05 | -0.0148 | CFL | None | 1230 | 0.0134 | 1230 | 0.0134 | 1.07 | 1 | -0.012
CFLNonePGEEPrNewCZ12 | Com-Iltg-dWatt-CFL_OSnone | PGE | EPr | New | CZ12 | 1.23 | 1.34e-05 | 0 | 1.31 | 1.34e-05 | -0.0151 | 1.23 | 1.34e-05 | 0 | 1.31 | 1.34e-05 | -0.0151 | CFL | None | 1230 | 0.0134 | 1230 | 0.0134 | 1.07 | 1 | -0.0123
CFLNonePGEEPrNewCZ13 | Com-Iltg-dWatt-CFL_OSnone | PGE | EPr | New | CZ13 | 1.23 | 1.34e-05 | 0 | 1.33 | 1.34e-05 | -0.0135 | 1.23 | 1.34e-05 | 0 | 1.33 | 1.34e-05 | -0.0135 | CFL | None | 1230 | 0.0134 | 1230 | 0.0134 | 1.08 | 1 | -0.011
CFLNoneSCEEPrNewCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | EPr | New | CZ13 | 1.23 | 1.34e-05 | 0 | 1.35 | 1.34e-05 | -0.0125 | 1.23 | 1.34e-05 | 0 | 1.35 | 1.34e-05 | -0.0125 | CFL | None | 1230 | 0.0134 | 1230 | 0.0134 | 1.1 | 1 | -0.0102
CFLNoneSDGEPrNewCZ14 | Com-Iltg-dWatt-CFL_OSnone | SDG | EPr | New | CZ14 | 1.23 | 0.000421 | 0 | 1.35 | 0.000586 | -0.0127 | 1.23 | 0.000421 | 0 | 1.35 | 0.000586 | -0.0127 | CFL | None | 1230 | 0.421 | 1230 | 0.421 | 1.1 | 1.39 | -0.0103
CFLNoneSCEEPrNewCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | EPr | New | CZ14 | 1.23 | 0.000421 | 0 | 1.35 | 0.000591 | -0.0125 | 1.23 | 0.000421 | 0 | 1.35 | 0.000591 | -0.0125 | CFL | None | 1230 | 0.421 | 1230 | 0.421 | 1.1 | 1.4 | -0.0102
CFLNoneSDGEPrNewCZ15 | Com-Iltg-dWatt-CFL_OSnone | SDG | EPr | New | CZ15 | 1.23 | 0.000421 | 0 | 1.49 | 0.000607 | -0.00353 | 1.23 | 0.000421 | 0 | 1.49 | 0.000607 | -0.00353 | CFL | None | 1230 | 0.421 | 1230 | 0.421 | 1.21 | 1.44 | -0.00287
CFLNoneSCEEPrNewCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | EPr | New | CZ15 | 1.23 | 0.000421 | 0 | 1.5 | 0.000612 | -0.00349 | 1.23 | 0.000421 | 0 | 1.5 | 0.000612 | -0.00349 | CFL | None | 1230 | 0.421 | 1230 | 0.421 | 1.22 | 1.45 | -0.00284
CFLNonePGEEPrNewCZ16 | Com-Iltg-dWatt-CFL_OSnone | PGE | EPr | New | CZ16 | 1.23 | 1.34e-05 | 0 | 1.23 | 1.34e-05 | -0.0193 | 1.23 | 1.34e-05 | 0 | 1.23 | 1.34e-05 | -0.0193 | CFL | None | 1230 | 0.0134 | 1230 | 0.0134 | 1 | 1 | -0.0157
CFLNoneSCEEPrNewCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | EPr | New | CZ16 | 1.23 | 1.34e-05 | 0 | 1.21 | 1.34e-05 | -0.018 | 1.23 | 1.34e-05 | 0 | 1.21 | 1.34e-05 | -0.018 | CFL | None | 1230 | 0.0134 | 1230 | 0.0134 | 0.984 | 1 | -0.0146
CFLNoneSCEEPrNewIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | EPr | New | IOU | 1.23 | 0.000421 | 0 | 1.37 | 0.000587 | -0.00793 | 1.23 | 0.000421 | 0 | 1.37 | 0.000587 | -0.00793 | CFL | None | 1230 | 0.421 | 1230 | 0.421 | 1.11 | 1.39 | -0.00645
CFLNoneSDGEPrNewIOU | Com-Iltg-dWatt-CFL_OSnone | SDG | EPr | New | IOU | 1.23 | 0.000421 | 0 | 1.35 | 0.000573 | -0.00757 | 1.23 | 0.000421 | 0 | 1.35 | 0.000573 | -0.00757 | CFL | None | 1230 | 0.421 | 1230 | 0.421 | 1.1 | 1.36 | -0.00615
CFLNoneSCGEPrNewIOU | Com-Iltg-dWatt-CFL_OSnone | SCG | EPr | New | IOU | 1.23 | 0.000421 | 0 | 1.37 | 0.000586 | -0.0079 | 1.23 | 0.000421 | 0 | 1.37 | 0.000586 | -0.0079 | CFL | None | 1230 | 0.421 | 1230 | 0.421 | 1.11 | 1.39 | -0.00642
CFLNonePGEEPrNewIOU | Com-Iltg-dWatt-CFL_OSnone | PGE | EPr | New | IOU | 1.23 | 3.85e-05 | 0 | 1.34 | 4.61e-05 | -0.0128 | 1.23 | 3.85e-05 | 0 | 1.34 | 4.61e-05 | -0.0128 | CFL | None | 1230 | 0.0385 | 1230 | 0.0385 | 1.09 | 1.2 | -0.0104
CFLNonePGEERCExCZ01 | Com-Iltg-dWatt-CFL_OSnone | PGE | ERC | Ex | CZ01 | 1.09 | 0.000434 | 0 | 1.06 | 0.000515 | -0.0182 | 1.09 | 0.000434 | 0 | 1.06 | 0.000515 | -0.0182 | CFL | None | 1090 | 0.434 | 1090 | 0.434 | 0.972 | 1.19 | -0.0167
CFLNonePGEERCExCZ02 | Com-Iltg-dWatt-CFL_OSnone | PGE | ERC | Ex | CZ02 | 1.09 | 1.25e-05 | 0 | 1.1 | 1.25e-05 | -0.0131 | 1.09 | 1.25e-05 | 0 | 1.1 | 1.25e-05 | -0.0131 | CFL | None | 1090 | 0.0125 | 1090 | 0.0125 | 1.01 | 1 | -0.012
CFLNonePGEERCExCZ03 | Com-Iltg-dWatt-CFL_OSnone | PGE | ERC | Ex | CZ03 | 1.09 | 1.25e-05 | 0 | 1.1 | 1.25e-05 | -0.0122 | 1.09 | 1.25e-05 | 0 | 1.1 | 1.25e-05 | -0.0122 | CFL | None | 1090 | 0.0125 | 1090 | 0.0125 | 1.01 | 1 | -0.0112
CFLNonePGEERCExCZ04 | Com-Iltg-dWatt-CFL_OSnone | PGE | ERC | Ex | CZ04 | 1.09 | 0.000434 | 0 | 1.13 | 0.000521 | -0.0102 | 1.09 | 0.000434 | 0 | 1.13 | 0.000521 | -0.0102 | CFL | None | 1090 | 0.434 | 1090 | 0.434 | 1.04 | 1.2 | -0.00936
CFLNoneSCEERCExCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | ERC | Ex | CZ05 | 1.09 | 0.000434 | 0 | 1.13 | 0.000542 | -0.0111 | 1.09 | 0.000434 | 0 | 1.13 | 0.000542 | -0.0111 | CFL | None | 1090 | 0.434 | 1090 | 0.434 | 1.04 | 1.25 | -0.0102
CFLNonePGEERCExCZ05 | Com-Iltg-dWatt-CFL_OSnone | PGE | ERC | Ex | CZ05 | 1.09 | 0.000434 | 0 | 1.13 | 0.000542 | -0.0111 | 1.09 | 0.000434 | 0 | 1.13 | 0.000542 | -0.0111 | CFL | None | 1090 | 0.434 | 1090 | 0.434 | 1.04 | 1.25 | -0.0102
CFLNoneSCGERCExCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCG | ERC | Ex | CZ05 | 1.09 | 0.000434 | 0 | 1.13 | 0.000542 | -0.0111 | 1.09 | 0.000434 | 0 | 1.13 | 0.000542 | -0.0111 | CFL | None | 1090 | 0.434 | 1090 | 0.434 | 1.04 | 1.25 | -0.0102
CFLNoneSCGERCExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCG | ERC | Ex | CZ06 | 1.09 | 0.000434 | 0 | 1.19 | 0.00054 | -0.00671 | 1.09 | 0.000434 | 0 | 1.19 | 0.00054 | -0.00671 | CFL | None | 1090 | 0.434 | 1090 | 0.434 | 1.09 | 1.24 | -0.00616
CFLNoneSDGERCExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SDG | ERC | Ex | CZ06 | 1.09 | 0.000434 | 0 | 1.19 | 0.00054 | -0.00671 | 1.09 | 0.000434 | 0 | 1.19 | 0.00054 | -0.00671 | CFL | None | 1090 | 0.434 | 1090 | 0.434 | 1.09 | 1.24 | -0.00616
CFLNoneSCEERCExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | ERC | Ex | CZ06 | 1.09 | 0.000434 | 0 | 1.19 | 0.00054 | -0.00671 | 1.09 | 0.000434 | 0 | 1.19 | 0.00054 | -0.00671 | CFL | None | 1090 | 0.434 | 1090 | 0.434 | 1.09 | 1.24 | -0.00616
CFLNoneSDGERCExCZ07 | Com-Iltg-dWatt-CFL_OSnone | SDG | ERC | Ex | CZ07 | 1.09 | 0.000434 | 0 | 1.22 | 0.000539 | -0.00537 | 1.09 | 0.000434 | 0 | 1.22 | 0.000539 | -0.00537 | CFL | None | 1090 | 0.434 | 1090 | 0.434 | 1.12 | 1.24 | -0.00493
CFLNoneSDGERCExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SDG | ERC | Ex | CZ08 | 1.09 | 0.000434 | 0 | 1.21 | 0.000546 | -0.00589 | 1.09 | 0.000434 | 0 | 1.21 | 0.000546 | -0.00589 | CFL | None | 1090 | 0.434 | 1090 | 0.434 | 1.11 | 1.26 | -0.0054
CFLNoneSCEERCExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | ERC | Ex | CZ08 | 1.09 | 0.000434 | 0 | 1.21 | 0.000546 | -0.00589 | 1.09 | 0.000434 | 0 | 1.21 | 0.000546 | -0.00589 | CFL | None | 1090 | 0.434 | 1090 | 0.434 | 1.11 | 1.26 | -0.0054
CFLNoneSCGERCExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCG | ERC | Ex | CZ08 | 1.09 | 0.000434 | 0 | 1.21 | 0.000546 | -0.00589 | 1.09 | 0.000434 | 0 | 1.21 | 0.000546 | -0.00589 | CFL | None | 1090 | 0.434 | 1090 | 0.434 | 1.11 | 1.26 | -0.0054
CFLNoneSCGERCExCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCG | ERC | Ex | CZ09 | 1.09 | 0.000434 | 0 | 1.21 | 0.000547 | -0.00664 | 1.09 | 0.000434 | 0 | 1.21 | 0.000547 | -0.00664 | CFL | None | 1090 | 0.434 | 1090 | 0.434 | 1.11 | 1.26 | -0.00609
CFLNoneSCEERCExCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | ERC | Ex | CZ09 | 1.09 | 0.000434 | 0 | 1.21 | 0.000547 | -0.00664 | 1.09 | 0.000434 | 0 | 1.21 | 0.000547 | -0.00664 | CFL | None | 1090 | 0.434 | 1090 | 0.434 | 1.11 | 1.26 | -0.00609
CFLNoneSCGERCExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCG | ERC | Ex | CZ10 | 1.09 | 0.000434 | 0 | 1.19 | 0.000543 | -0.00687 | 1.09 | 0.000434 | 0 | 1.19 | 0.000543 | -0.00687 | CFL | None | 1090 | 0.434 | 1090 | 0.434 | 1.09 | 1.25 | -0.0063
CFLNoneSDGERCExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SDG | ERC | Ex | CZ10 | 1.09 | 0.000434 | 0 | 1.19 | 0.000543 | -0.00687 | 1.09 | 0.000434 | 0 | 1.19 | 0.000543 | -0.00687 | CFL | None | 1090 | 0.434 | 1090 | 0.434 | 1.09 | 1.25 | -0.0063
CFLNoneSCEERCExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | ERC | Ex | CZ10 | 1.09 | 0.000434 | 0 | 1.19 | 0.000543 | -0.00687 | 1.09 | 0.000434 | 0 | 1.19 | 0.000543 | -0.00687 | CFL | None | 1090 | 0.434 | 1090 | 0.434 | 1.09 | 1.25 | -0.0063
CFLNonePGEERCExCZ11 | Com-Iltg-dWatt-CFL_OSnone | PGE | ERC | Ex | CZ11 | 1.09 | 1.25e-05 | 0 | 1.13 | 1.25e-05 | -0.011 | 1.09 | 1.25e-05 | 0 | 1.13 | 1.25e-05 | -0.011 | CFL | None | 1090 | 0.0125 | 1090 | 0.0125 | 1.04 | 1 | -0.0101
CFLNonePGEERCExCZ12 | Com-Iltg-dWatt-CFL_OSnone | PGE | ERC | Ex | CZ12 | 1.09 | 1.25e-05 | 0 | 1.13 | 1.25e-05 | -0.0117 | 1.09 | 1.25e-05 | 0 | 1.13 | 1.25e-05 | -0.0117 | CFL | None | 1090 | 0.0125 | 1090 | 0.0125 | 1.04 | 1 | -0.0107
CFLNonePGEERCExCZ13 | Com-Iltg-dWatt-CFL_OSnone | PGE | ERC | Ex | CZ13 | 1.09 | 1.25e-05 | 0 | 1.18 | 1.25e-05 | -0.00957 | 1.09 | 1.25e-05 | 0 | 1.18 | 1.25e-05 | -0.00957 | CFL | None | 1090 | 0.0125 | 1090 | 0.0125 | 1.08 | 1 | -0.00878
CFLNoneSCGERCExCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCG | ERC | Ex | CZ13 | 1.09 | 1.25e-05 | 0 | 1.18 | 1.25e-05 | -0.00957 | 1.09 | 1.25e-05 | 0 | 1.18 | 1.25e-05 | -0.00957 | CFL | None | 1090 | 0.0125 | 1090 | 0.0125 | 1.08 | 1 | -0.00878
CFLNoneSCEERCExCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | ERC | Ex | CZ13 | 1.09 | 1.25e-05 | 0 | 1.18 | 1.25e-05 | -0.00957 | 1.09 | 1.25e-05 | 0 | 1.18 | 1.25e-05 | -0.00957 | CFL | None | 1090 | 0.0125 | 1090 | 0.0125 | 1.08 | 1 | -0.00878
CFLNoneSDGERCExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SDG | ERC | Ex | CZ14 | 1.09 | 0.000434 | 0 | 1.19 | 0.000551 | -0.00909 | 1.09 | 0.000434 | 0 | 1.19 | 0.000551 | -0.00909 | CFL | None | 1090 | 0.434 | 1090 | 0.434 | 1.09 | 1.27 | -0.00834
CFLNoneSCGERCExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCG | ERC | Ex | CZ14 | 1.09 | 0.000434 | 0 | 1.19 | 0.000551 | -0.00909 | 1.09 | 0.000434 | 0 | 1.19 | 0.000551 | -0.00909 | CFL | None | 1090 | 0.434 | 1090 | 0.434 | 1.09 | 1.27 | -0.00834
CFLNoneSCEERCExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | ERC | Ex | CZ14 | 1.09 | 0.000434 | 0 | 1.19 | 0.000551 | -0.00909 | 1.09 | 0.000434 | 0 | 1.19 | 0.000551 | -0.00909 | CFL | None | 1090 | 0.434 | 1090 | 0.434 | 1.09 | 1.27 | -0.00834
CFLNoneSDGERCExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SDG | ERC | Ex | CZ15 | 1.09 | 0.000434 | 0 | 1.29 | 0.000559 | -0.00334 | 1.09 | 0.000434 | 0 | 1.29 | 0.000559 | -0.00334 | CFL | None | 1090 | 0.434 | 1090 | 0.434 | 1.18 | 1.29 | -0.00306
CFLNoneSCEERCExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | ERC | Ex | CZ15 | 1.09 | 0.000434 | 0 | 1.29 | 0.000559 | -0.00334 | 1.09 | 0.000434 | 0 | 1.29 | 0.000559 | -0.00334 | CFL | None | 1090 | 0.434 | 1090 | 0.434 | 1.18 | 1.29 | -0.00306
CFLNoneSCGERCExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCG | ERC | Ex | CZ15 | 1.09 | 0.000434 | 0 | 1.29 | 0.000559 | -0.00334 | 1.09 | 0.000434 | 0 | 1.29 | 0.000559 | -0.00334 | CFL | None | 1090 | 0.434 | 1090 | 0.434 | 1.18 | 1.29 | -0.00306
CFLNoneSCEERCExCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | ERC | Ex | CZ16 | 1.09 | 1.25e-05 | 0 | 1.08 | 1.25e-05 | -0.0161 | 1.09 | 1.25e-05 | 0 | 1.08 | 1.25e-05 | -0.0161 | CFL | None | 1090 | 0.0125 | 1090 | 0.0125 | 0.991 | 1 | -0.0148
CFLNonePGEERCExCZ16 | Com-Iltg-dWatt-CFL_OSnone | PGE | ERC | Ex | CZ16 | 1.09 | 1.25e-05 | 0 | 1.08 | 1.25e-05 | -0.0161 | 1.09 | 1.25e-05 | 0 | 1.08 | 1.25e-05 | -0.0161 | CFL | None | 1090 | 0.0125 | 1090 | 0.0125 | 0.991 | 1 | -0.0148
CFLNoneSCGERCExCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCG | ERC | Ex | CZ16 | 1.09 | 1.25e-05 | 0 | 1.08 | 1.25e-05 | -0.0161 | 1.09 | 1.25e-05 | 0 | 1.08 | 1.25e-05 | -0.0161 | CFL | None | 1090 | 0.0125 | 1090 | 0.0125 | 0.991 | 1 | -0.0148
CFLNonePGEERCExIOU | Com-Iltg-dWatt-CFL_OSnone | PGE | ERC | Ex | IOU | 1.09 | 8.67e-05 | 0 | 1.13 | 0.000102 | -0.0114 | 1.09 | 8.67e-05 | 0 | 1.13 | 0.000102 | -0.0114 | CFL | None | 1090 | 0.0867 | 1090 | 0.0867 | 1.04 | 1.18 | -0.0105
CFLNoneSCGERCExIOU | Com-Iltg-dWatt-CFL_OSnone | SCG | ERC | Ex | IOU | 1.09 | 0.000412 | 0 | 1.2 | 0.000517 | -0.00682 | 1.09 | 0.000412 | 0 | 1.2 | 0.000517 | -0.00682 | CFL | None | 1090 | 0.412 | 1090 | 0.412 | 1.1 | 1.25 | -0.00626
CFLNoneSDGERCExIOU | Com-Iltg-dWatt-CFL_OSnone | SDG | ERC | Ex | IOU | 1.09 | 0.000434 | 0 | 1.21 | 0.000541 | -0.00598 | 1.09 | 0.000434 | 0 | 1.21 | 0.000541 | -0.00598 | CFL | None | 1090 | 0.434 | 1090 | 0.434 | 1.11 | 1.25 | -0.00549
CFLNoneSCEERCExIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | ERC | Ex | IOU | 1.09 | 0.000406 | 0 | 1.2 | 0.00051 | -0.00689 | 1.09 | 0.000406 | 0 | 1.2 | 0.00051 | -0.00689 | CFL | None | 1090 | 0.406 | 1090 | 0.406 | 1.1 | 1.26 | -0.00632
CFLNonePGEERCNewCZ01 | Com-Iltg-dWatt-CFL_OSnone | PGE | ERC | New | CZ01 | 1.09 | 0.000434 | 0 | 1.12 | 0.000513 | -0.0215 | 1.09 | 0.000434 | 0 | 1.12 | 0.000513 | -0.0215 | CFL | None | 1090 | 0.434 | 1090 | 0.434 | 1.03 | 1.18 | -0.0197
CFLNonePGEERCNewCZ02 | Com-Iltg-dWatt-CFL_OSnone | PGE | ERC | New | CZ02 | 1.09 | 1.25e-05 | 0 | 1.17 | 1.25e-05 | -0.0142 | 1.09 | 1.25e-05 | 0 | 1.17 | 1.25e-05 | -0.0142 | CFL | None | 1090 | 0.0125 | 1090 | 0.0125 | 1.07 | 1 | -0.013
CFLNonePGEERCNewCZ03 | Com-Iltg-dWatt-CFL_OSnone | PGE | ERC | New | CZ03 | 1.09 | 1.25e-05 | 0 | 1.17 | 1.25e-05 | -0.013 | 1.09 | 1.25e-05 | 0 | 1.17 | 1.25e-05 | -0.013 | CFL | None | 1090 | 0.0125 | 1090 | 0.0125 | 1.07 | 1 | -0.0119
CFLNonePGEERCNewCZ04 | Com-Iltg-dWatt-CFL_OSnone | PGE | ERC | New | CZ04 | 1.09 | 0.000434 | 0 | 1.2 | 0.000548 | -0.0112 | 1.09 | 0.000434 | 0 | 1.2 | 0.000548 | -0.0112 | CFL | None | 1090 | 0.434 | 1090 | 0.434 | 1.1 | 1.26 | -0.0103
CFLNoneSCEERCNewCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | ERC | New | CZ05 | 1.09 | 0.000434 | 0 | 1.18 | 0.000584 | -0.0114 | 1.09 | 0.000434 | 0 | 1.18 | 0.000584 | -0.0114 | CFL | None | 1090 | 0.434 | 1090 | 0.434 | 1.08 | 1.35 | -0.0105
CFLNonePGEERCNewCZ05 | Com-Iltg-dWatt-CFL_OSnone | PGE | ERC | New | CZ05 | 1.09 | 0.000434 | 0 | 1.17 | 0.000556 | -0.0124 | 1.09 | 0.000434 | 0 | 1.17 | 0.000556 | -0.0124 | CFL | None | 1090 | 0.434 | 1090 | 0.434 | 1.07 | 1.28 | -0.0114
CFLNoneSCEERCNewCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | ERC | New | CZ06 | 1.09 | 0.000434 | 0 | 1.24 | 0.000559 | -0.00734 | 1.09 | 0.000434 | 0 | 1.24 | 0.000559 | -0.00734 | CFL | None | 1090 | 0.434 | 1090 | 0.434 | 1.14 | 1.29 | -0.00673
CFLNoneSDGERCNewCZ06 | Com-Iltg-dWatt-CFL_OSnone | SDG | ERC | New | CZ06 | 1.09 | 0.000434 | 0 | 1.24 | 0.000556 | -0.00742 | 1.09 | 0.000434 | 0 | 1.24 | 0.000556 | -0.00742 | CFL | None | 1090 | 0.434 | 1090 | 0.434 | 1.14 | 1.28 | -0.00681
CFLNoneSDGERCNewCZ07 | Com-Iltg-dWatt-CFL_OSnone | SDG | ERC | New | CZ07 | 1.09 | 0.000434 | 0 | 1.25 | 0.000547 | -0.00573 | 1.09 | 0.000434 | 0 | 1.25 | 0.000547 | -0.00573 | CFL | None | 1090 | 0.434 | 1090 | 0.434 | 1.15 | 1.26 | -0.00526
CFLNoneSDGERCNewCZ08 | Com-Iltg-dWatt-CFL_OSnone | SDG | ERC | New | CZ08 | 1.09 | 0.000434 | 0 | 1.26 | 0.000569 | -0.00646 | 1.09 | 0.000434 | 0 | 1.26 | 0.000569 | -0.00646 | CFL | None | 1090 | 0.434 | 1090 | 0.434 | 1.16 | 1.31 | -0.00593
CFLNoneSCEERCNewCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | ERC | New | CZ08 | 1.09 | 0.000434 | 0 | 1.26 | 0.000572 | -0.0064 | 1.09 | 0.000434 | 0 | 1.26 | 0.000572 | -0.0064 | CFL | None | 1090 | 0.434 | 1090 | 0.434 | 1.16 | 1.32 | -0.00587
CFLNoneSCEERCNewCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | ERC | New | CZ09 | 1.09 | 0.000434 | 0 | 1.27 | 0.000588 | -0.00688 | 1.09 | 0.000434 | 0 | 1.27 | 0.000588 | -0.00688 | CFL | None | 1090 | 0.434 | 1090 | 0.434 | 1.17 | 1.35 | -0.00631
CFLNoneSDGERCNewCZ10 | Com-Iltg-dWatt-CFL_OSnone | SDG | ERC | New | CZ10 | 1.09 | 0.000434 | 0 | 1.27 | 0.000594 | -0.00735 | 1.09 | 0.000434 | 0 | 1.27 | 0.000594 | -0.00735 | CFL | None | 1090 | 0.434 | 1090 | 0.434 | 1.17 | 1.37 | -0.00674
CFLNoneSCEERCNewCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | ERC | New | CZ10 | 1.09 | 0.000434 | 0 | 1.27 | 0.000598 | -0.00726 | 1.09 | 0.000434 | 0 | 1.27 | 0.000598 | -0.00726 | CFL | None | 1090 | 0.434 | 1090 | 0.434 | 1.17 | 1.38 | -0.00666
CFLNonePGEERCNewCZ11 | Com-Iltg-dWatt-CFL_OSnone | PGE | ERC | New | CZ11 | 1.09 | 1.25e-05 | 0 | 1.23 | 1.25e-05 | -0.013 | 1.09 | 1.25e-05 | 0 | 1.23 | 1.25e-05 | -0.013 | CFL | None | 1090 | 0.0125 | 1090 | 0.0125 | 1.13 | 1 | -0.0119
CFLNonePGEERCNewCZ12 | Com-Iltg-dWatt-CFL_OSnone | PGE | ERC | New | CZ12 | 1.09 | 1.25e-05 | 0 | 1.2 | 1.25e-05 | -0.0132 | 1.09 | 1.25e-05 | 0 | 1.2 | 1.25e-05 | -0.0132 | CFL | None | 1090 | 0.0125 | 1090 | 0.0125 | 1.1 | 1 | -0.0121
CFLNoneSCEERCNewCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | ERC | New | CZ13 | 1.09 | 1.25e-05 | 0 | 1.25 | 1.25e-05 | -0.0106 | 1.09 | 1.25e-05 | 0 | 1.25 | 1.25e-05 | -0.0106 | CFL | None | 1090 | 0.0125 | 1090 | 0.0125 | 1.15 | 1 | -0.00972
CFLNonePGEERCNewCZ13 | Com-Iltg-dWatt-CFL_OSnone | PGE | ERC | New | CZ13 | 1.09 | 1.25e-05 | 0 | 1.22 | 1.25e-05 | -0.0116 | 1.09 | 1.25e-05 | 0 | 1.22 | 1.25e-05 | -0.0116 | CFL | None | 1090 | 0.0125 | 1090 | 0.0125 | 1.12 | 1 | -0.0106
CFLNoneSCEERCNewCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | ERC | New | CZ14 | 1.09 | 0.000434 | 0 | 1.25 | 0.00059 | -0.0105 | 1.09 | 0.000434 | 0 | 1.25 | 0.00059 | -0.0105 | CFL | None | 1090 | 0.434 | 1090 | 0.434 | 1.15 | 1.36 | -0.00963
CFLNoneSDGERCNewCZ14 | Com-Iltg-dWatt-CFL_OSnone | SDG | ERC | New | CZ14 | 1.09 | 0.000434 | 0 | 1.25 | 0.000585 | -0.0107 | 1.09 | 0.000434 | 0 | 1.25 | 0.000585 | -0.0107 | CFL | None | 1090 | 0.434 | 1090 | 0.434 | 1.15 | 1.35 | -0.00982
CFLNoneSCEERCNewCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | ERC | New | CZ15 | 1.09 | 0.000434 | 0 | 1.39 | 0.0006 | -0.00364 | 1.09 | 0.000434 | 0 | 1.39 | 0.0006 | -0.00364 | CFL | None | 1090 | 0.434 | 1090 | 0.434 | 1.28 | 1.38 | -0.00334
CFLNoneSDGERCNewCZ15 | Com-Iltg-dWatt-CFL_OSnone | SDG | ERC | New | CZ15 | 1.09 | 0.000434 | 0 | 1.38 | 0.000595 | -0.00368 | 1.09 | 0.000434 | 0 | 1.38 | 0.000595 | -0.00368 | CFL | None | 1090 | 0.434 | 1090 | 0.434 | 1.27 | 1.37 | -0.00338
CFLNonePGEERCNewCZ16 | Com-Iltg-dWatt-CFL_OSnone | PGE | ERC | New | CZ16 | 1.09 | 1.25e-05 | 0 | 1.12 | 1.25e-05 | -0.0201 | 1.09 | 1.25e-05 | 0 | 1.12 | 1.25e-05 | -0.0201 | CFL | None | 1090 | 0.0125 | 1090 | 0.0125 | 1.03 | 1 | -0.0184
CFLNoneSCEERCNewCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | ERC | New | CZ16 | 1.09 | 1.25e-05 | 0 | 1.12 | 1.25e-05 | -0.0186 | 1.09 | 1.25e-05 | 0 | 1.12 | 1.25e-05 | -0.0186 | CFL | None | 1090 | 0.0125 | 1090 | 0.0125 | 1.03 | 1 | -0.0171
CFLNoneSCGERCNewIOU | Com-Iltg-dWatt-CFL_OSnone | SCG | ERC | New | IOU | 1.09 | 0.000434 | 0 | 1.26 | 0.00058 | -0.00728 | 1.09 | 0.000434 | 0 | 1.26 | 0.00058 | -0.00728 | CFL | None | 1090 | 0.434 | 1090 | 0.434 | 1.16 | 1.34 | -0.00668
CFLNonePGEERCNewIOU | Com-Iltg-dWatt-CFL_OSnone | PGE | ERC | New | IOU | 1.09 | 3.85e-05 | 0 | 1.24 | 4.77e-05 | -0.0111 | 1.09 | 3.85e-05 | 0 | 1.24 | 4.77e-05 | -0.0111 | CFL | None | 1090 | 0.0385 | 1090 | 0.0385 | 1.14 | 1.24 | -0.0102
CFLNoneSCEERCNewIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | ERC | New | IOU | 1.09 | 0.000434 | 0 | 1.26 | 0.00058 | -0.0073 | 1.09 | 0.000434 | 0 | 1.26 | 0.00058 | -0.0073 | CFL | None | 1090 | 0.434 | 1090 | 0.434 | 1.16 | 1.34 | -0.0067
CFLNoneSDGERCNewIOU | Com-Iltg-dWatt-CFL_OSnone | SDG | ERC | New | IOU | 1.09 | 0.000434 | 0 | 1.26 | 0.000564 | -0.00642 | 1.09 | 0.000434 | 0 | 1.26 | 0.000564 | -0.00642 | CFL | None | 1090 | 0.434 | 1090 | 0.434 | 1.16 | 1.3 | -0.00589
CFLNonePGEESeExCZ01 | Com-Iltg-dWatt-CFL_OSnone | PGE | ESe | Ex | CZ01 | 1.52 | 0.000316 | 0 | 1.48 | 0.000374 | -0.031 | 1.52 | 0.000316 | 0 | 1.48 | 0.000374 | -0.031 | CFL | None | 1520 | 0.316 | 1520 | 0.316 | 0.974 | 1.18 | -0.0204
CFLNonePGEESeExCZ02 | Com-Iltg-dWatt-CFL_OSnone | PGE | ESe | Ex | CZ02 | 1.52 | 8.84e-06 | 0 | 1.58 | 8.84e-06 | -0.0195 | 1.52 | 8.84e-06 | 0 | 1.58 | 8.84e-06 | -0.0195 | CFL | None | 1520 | 0.00884 | 1520 | 0.00884 | 1.04 | 1 | -0.0128
CFLNonePGEESeExCZ03 | Com-Iltg-dWatt-CFL_OSnone | PGE | ESe | Ex | CZ03 | 1.52 | 8.84e-06 | 0 | 1.58 | 8.84e-06 | -0.0201 | 1.52 | 8.84e-06 | 0 | 1.58 | 8.84e-06 | -0.0201 | CFL | None | 1520 | 0.00884 | 1520 | 0.00884 | 1.04 | 1 | -0.0132
CFLNonePGEESeExCZ04 | Com-Iltg-dWatt-CFL_OSnone | PGE | ESe | Ex | CZ04 | 1.52 | 0.000316 | 0 | 1.62 | 0.000383 | -0.0155 | 1.52 | 0.000316 | 0 | 1.62 | 0.000383 | -0.0155 | CFL | None | 1520 | 0.316 | 1520 | 0.316 | 1.07 | 1.21 | -0.0102
CFLNoneSCEESeExCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | ESe | Ex | CZ05 | 1.52 | 0.000316 | 0 | 1.61 | 0.000392 | -0.017 | 1.52 | 0.000316 | 0 | 1.61 | 0.000392 | -0.017 | CFL | None | 1520 | 0.316 | 1520 | 0.316 | 1.06 | 1.24 | -0.0112
CFLNoneSCGESeExCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCG | ESe | Ex | CZ05 | 1.52 | 0.000316 | 0 | 1.61 | 0.000392 | -0.017 | 1.52 | 0.000316 | 0 | 1.61 | 0.000392 | -0.017 | CFL | None | 1520 | 0.316 | 1520 | 0.316 | 1.06 | 1.24 | -0.0112
CFLNonePGEESeExCZ05 | Com-Iltg-dWatt-CFL_OSnone | PGE | ESe | Ex | CZ05 | 1.52 | 0.000316 | 0 | 1.61 | 0.000392 | -0.017 | 1.52 | 0.000316 | 0 | 1.61 | 0.000392 | -0.017 | CFL | None | 1520 | 0.316 | 1520 | 0.316 | 1.06 | 1.24 | -0.0112
CFLNoneSCGESeExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCG | ESe | Ex | CZ06 | 1.52 | 0.000316 | 0 | 1.7 | 0.000401 | -0.00874 | 1.52 | 0.000316 | 0 | 1.7 | 0.000401 | -0.00874 | CFL | None | 1520 | 0.316 | 1520 | 0.316 | 1.12 | 1.27 | -0.00575
CFLNoneSCEESeExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | ESe | Ex | CZ06 | 1.52 | 0.000316 | 0 | 1.7 | 0.000401 | -0.00874 | 1.52 | 0.000316 | 0 | 1.7 | 0.000401 | -0.00874 | CFL | None | 1520 | 0.316 | 1520 | 0.316 | 1.12 | 1.27 | -0.00575
CFLNoneSDGESeExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SDG | ESe | Ex | CZ06 | 1.52 | 0.000316 | 0 | 1.7 | 0.000401 | -0.00874 | 1.52 | 0.000316 | 0 | 1.7 | 0.000401 | -0.00874 | CFL | None | 1520 | 0.316 | 1520 | 0.316 | 1.12 | 1.27 | -0.00575
CFLNoneSDGESeExCZ07 | Com-Iltg-dWatt-CFL_OSnone | SDG | ESe | Ex | CZ07 | 1.52 | 0.000316 | 0 | 1.69 | 0.000393 | -0.00771 | 1.52 | 0.000316 | 0 | 1.69 | 0.000393 | -0.00771 | CFL | None | 1520 | 0.316 | 1520 | 0.316 | 1.11 | 1.24 | -0.00507
CFLNoneSCEESeExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | ESe | Ex | CZ08 | 1.52 | 0.000316 | 0 | 1.71 | 0.000399 | -0.00745 | 1.52 | 0.000316 | 0 | 1.71 | 0.000399 | -0.00745 | CFL | None | 1520 | 0.316 | 1520 | 0.316 | 1.13 | 1.26 | -0.0049
CFLNoneSCGESeExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCG | ESe | Ex | CZ08 | 1.52 | 0.000316 | 0 | 1.71 | 0.000399 | -0.00745 | 1.52 | 0.000316 | 0 | 1.71 | 0.000399 | -0.00745 | CFL | None | 1520 | 0.316 | 1520 | 0.316 | 1.13 | 1.26 | -0.0049
CFLNoneSDGESeExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SDG | ESe | Ex | CZ08 | 1.52 | 0.000316 | 0 | 1.71 | 0.000399 | -0.00745 | 1.52 | 0.000316 | 0 | 1.71 | 0.000399 | -0.00745 | CFL | None | 1520 | 0.316 | 1520 | 0.316 | 1.13 | 1.26 | -0.0049
CFLNoneSCEESeExCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | ESe | Ex | CZ09 | 1.52 | 0.000316 | 0 | 1.73 | 0.000406 | -0.00901 | 1.52 | 0.000316 | 0 | 1.73 | 0.000406 | -0.00901 | CFL | None | 1520 | 0.316 | 1520 | 0.316 | 1.14 | 1.28 | -0.00593
CFLNoneSCGESeExCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCG | ESe | Ex | CZ09 | 1.52 | 0.000316 | 0 | 1.73 | 0.000406 | -0.00901 | 1.52 | 0.000316 | 0 | 1.73 | 0.000406 | -0.00901 | CFL | None | 1520 | 0.316 | 1520 | 0.316 | 1.14 | 1.28 | -0.00593
CFLNoneSCGESeExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCG | ESe | Ex | CZ10 | 1.52 | 0.000316 | 0 | 1.7 | 0.000397 | -0.0093 | 1.52 | 0.000316 | 0 | 1.7 | 0.000397 | -0.0093 | CFL | None | 1520 | 0.316 | 1520 | 0.316 | 1.12 | 1.26 | -0.00612
CFLNoneSDGESeExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SDG | ESe | Ex | CZ10 | 1.52 | 0.000316 | 0 | 1.7 | 0.000397 | -0.0093 | 1.52 | 0.000316 | 0 | 1.7 | 0.000397 | -0.0093 | CFL | None | 1520 | 0.316 | 1520 | 0.316 | 1.12 | 1.26 | -0.00612
CFLNoneSCEESeExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | ESe | Ex | CZ10 | 1.52 | 0.000316 | 0 | 1.7 | 0.000397 | -0.0093 | 1.52 | 0.000316 | 0 | 1.7 | 0.000397 | -0.0093 | CFL | None | 1520 | 0.316 | 1520 | 0.316 | 1.12 | 1.26 | -0.00612
CFLNonePGEESeExCZ11 | Com-Iltg-dWatt-CFL_OSnone | PGE | ESe | Ex | CZ11 | 1.52 | 8.84e-06 | 0 | 1.61 | 8.84e-06 | -0.0172 | 1.52 | 8.84e-06 | 0 | 1.61 | 8.84e-06 | -0.0172 | CFL | None | 1520 | 0.00884 | 1520 | 0.00884 | 1.06 | 1 | -0.0113
CFLNonePGEESeExCZ12 | Com-Iltg-dWatt-CFL_OSnone | PGE | ESe | Ex | CZ12 | 1.52 | 8.84e-06 | 0 | 1.6 | 8.84e-06 | -0.0179 | 1.52 | 8.84e-06 | 0 | 1.6 | 8.84e-06 | -0.0179 | CFL | None | 1520 | 0.00884 | 1520 | 0.00884 | 1.05 | 1 | -0.0118
CFLNoneSCEESeExCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | ESe | Ex | CZ13 | 1.52 | 8.84e-06 | 0 | 1.67 | 8.84e-06 | -0.0147 | 1.52 | 8.84e-06 | 0 | 1.67 | 8.84e-06 | -0.0147 | CFL | None | 1520 | 0.00884 | 1520 | 0.00884 | 1.1 | 1 | -0.00967
CFLNonePGEESeExCZ13 | Com-Iltg-dWatt-CFL_OSnone | PGE | ESe | Ex | CZ13 | 1.52 | 8.84e-06 | 0 | 1.67 | 8.84e-06 | -0.0147 | 1.52 | 8.84e-06 | 0 | 1.67 | 8.84e-06 | -0.0147 | CFL | None | 1520 | 0.00884 | 1520 | 0.00884 | 1.1 | 1 | -0.00967
CFLNoneSCGESeExCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCG | ESe | Ex | CZ13 | 1.52 | 8.84e-06 | 0 | 1.67 | 8.84e-06 | -0.0147 | 1.52 | 8.84e-06 | 0 | 1.67 | 8.84e-06 | -0.0147 | CFL | None | 1520 | 0.00884 | 1520 | 0.00884 | 1.1 | 1 | -0.00967
CFLNoneSCGESeExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCG | ESe | Ex | CZ14 | 1.52 | 0.000316 | 0 | 1.65 | 0.000384 | -0.0145 | 1.52 | 0.000316 | 0 | 1.65 | 0.000384 | -0.0145 | CFL | None | 1520 | 0.316 | 1520 | 0.316 | 1.09 | 1.22 | -0.00954
CFLNoneSCEESeExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | ESe | Ex | CZ14 | 1.52 | 0.000316 | 0 | 1.65 | 0.000384 | -0.0145 | 1.52 | 0.000316 | 0 | 1.65 | 0.000384 | -0.0145 | CFL | None | 1520 | 0.316 | 1520 | 0.316 | 1.09 | 1.22 | -0.00954
CFLNoneSDGESeExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SDG | ESe | Ex | CZ14 | 1.52 | 0.000316 | 0 | 1.65 | 0.000384 | -0.0145 | 1.52 | 0.000316 | 0 | 1.65 | 0.000384 | -0.0145 | CFL | None | 1520 | 0.316 | 1520 | 0.316 | 1.09 | 1.22 | -0.00954
CFLNoneSCEESeExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | ESe | Ex | CZ15 | 1.52 | 0.000316 | 0 | 1.85 | 0.000397 | -0.00415 | 1.52 | 0.000316 | 0 | 1.85 | 0.000397 | -0.00415 | CFL | None | 1520 | 0.316 | 1520 | 0.316 | 1.22 | 1.26 | -0.00273
CFLNoneSCGESeExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCG | ESe | Ex | CZ15 | 1.52 | 0.000316 | 0 | 1.85 | 0.000397 | -0.00415 | 1.52 | 0.000316 | 0 | 1.85 | 0.000397 | -0.00415 | CFL | None | 1520 | 0.316 | 1520 | 0.316 | 1.22 | 1.26 | -0.00273
CFLNoneSDGESeExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SDG | ESe | Ex | CZ15 | 1.52 | 0.000316 | 0 | 1.85 | 0.000397 | -0.00415 | 1.52 | 0.000316 | 0 | 1.85 | 0.000397 | -0.00415 | CFL | None | 1520 | 0.316 | 1520 | 0.316 | 1.22 | 1.26 | -0.00273
CFLNonePGEESeExCZ16 | Com-Iltg-dWatt-CFL_OSnone | PGE | ESe | Ex | CZ16 | 1.52 | 8.84e-06 | 0 | 1.48 | 8.84e-06 | -0.0254 | 1.52 | 8.84e-06 | 0 | 1.48 | 8.84e-06 | -0.0254 | CFL | None | 1520 | 0.00884 | 1520 | 0.00884 | 0.974 | 1 | -0.0167
CFLNoneSCGESeExCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCG | ESe | Ex | CZ16 | 1.52 | 8.84e-06 | 0 | 1.48 | 8.84e-06 | -0.0254 | 1.52 | 8.84e-06 | 0 | 1.48 | 8.84e-06 | -0.0254 | CFL | None | 1520 | 0.00884 | 1520 | 0.00884 | 0.974 | 1 | -0.0167
CFLNoneSCEESeExCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | ESe | Ex | CZ16 | 1.52 | 8.84e-06 | 0 | 1.48 | 8.84e-06 | -0.0254 | 1.52 | 8.84e-06 | 0 | 1.48 | 8.84e-06 | -0.0254 | CFL | None | 1520 | 0.00884 | 1520 | 0.00884 | 0.974 | 1 | -0.0167
CFLNonePGEESeExIOU | Com-Iltg-dWatt-CFL_OSnone | PGE | ESe | Ex | IOU | 1.52 | 6.29e-05 | 0 | 1.61 | 7.48e-05 | -0.0179 | 1.52 | 6.29e-05 | 0 | 1.61 | 7.48e-05 | -0.0179 | CFL | None | 1520 | 0.0629 | 1520 | 0.0629 | 1.06 | 1.19 | -0.0118
CFLNoneSDGESeExIOU | Com-Iltg-dWatt-CFL_OSnone | SDG | ESe | Ex | IOU | 1.52 | 0.000316 | 0 | 1.69 | 0.000395 | -0.00832 | 1.52 | 0.000316 | 0 | 1.69 | 0.000395 | -0.00832 | CFL | None | 1520 | 0.316 | 1520 | 0.316 | 1.11 | 1.25 | -0.00547
CFLNoneSCEESeExIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | ESe | Ex | IOU | 1.52 | 0.000296 | 0 | 1.7 | 0.000374 | -0.00938 | 1.52 | 0.000296 | 0 | 1.7 | 0.000374 | -0.00938 | CFL | None | 1520 | 0.296 | 1520 | 0.296 | 1.12 | 1.26 | -0.00617
CFLNoneSCGESeExIOU | Com-Iltg-dWatt-CFL_OSnone | SCG | ESe | Ex | IOU | 1.52 | 0.0003 | 0 | 1.71 | 0.00038 | -0.00925 | 1.52 | 0.0003 | 0 | 1.71 | 0.00038 | -0.00925 | CFL | None | 1520 | 0.3 | 1520 | 0.3 | 1.13 | 1.27 | -0.00609
CFLNonePGEESeNewCZ01 | Com-Iltg-dWatt-CFL_OSnone | PGE | ESe | New | CZ01 | 1.52 | 0.000316 | 0 | 1.5 | 0.000363 | -0.0245 | 1.52 | 0.000316 | 0 | 1.5 | 0.000363 | -0.0245 | CFL | None | 1520 | 0.316 | 1520 | 0.316 | 0.987 | 1.15 | -0.0161
CFLNonePGEESeNewCZ02 | Com-Iltg-dWatt-CFL_OSnone | PGE | ESe | New | CZ02 | 1.52 | 8.84e-06 | 0 | 1.6 | 8.84e-06 | -0.0225 | 1.52 | 8.84e-06 | 0 | 1.6 | 8.84e-06 | -0.0225 | CFL | None | 1520 | 0.00884 | 1520 | 0.00884 | 1.05 | 1 | -0.0148
CFLNonePGEESeNewCZ03 | Com-Iltg-dWatt-CFL_OSnone | PGE | ESe | New | CZ03 | 1.52 | 8.84e-06 | 0 | 1.58 | 8.84e-06 | -0.0198 | 1.52 | 8.84e-06 | 0 | 1.58 | 8.84e-06 | -0.0198 | CFL | None | 1520 | 0.00884 | 1520 | 0.00884 | 1.04 | 1 | -0.013
CFLNonePGEESeNewCZ04 | Com-Iltg-dWatt-CFL_OSnone | PGE | ESe | New | CZ04 | 1.52 | 0.000316 | 0 | 1.62 | 0.000411 | -0.0179 | 1.52 | 0.000316 | 0 | 1.62 | 0.000411 | -0.0179 | CFL | None | 1520 | 0.316 | 1520 | 0.316 | 1.07 | 1.3 | -0.0118
CFLNoneSCEESeNewCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | ESe | New | CZ05 | 1.52 | 0.000316 | 0 | 1.58 | 0.000397 | -0.0158 | 1.52 | 0.000316 | 0 | 1.58 | 0.000397 | -0.0158 | CFL | None | 1520 | 0.316 | 1520 | 0.316 | 1.04 | 1.26 | -0.0104
CFLNonePGEESeNewCZ05 | Com-Iltg-dWatt-CFL_OSnone | PGE | ESe | New | CZ05 | 1.52 | 0.000316 | 0 | 1.57 | 0.000383 | -0.0172 | 1.52 | 0.000316 | 0 | 1.57 | 0.000383 | -0.0172 | CFL | None | 1520 | 0.316 | 1520 | 0.316 | 1.03 | 1.21 | -0.0113
CFLNoneSCEESeNewCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | ESe | New | CZ06 | 1.52 | 0.000316 | 0 | 1.68 | 0.000421 | -0.0113 | 1.52 | 0.000316 | 0 | 1.68 | 0.000421 | -0.0113 | CFL | None | 1520 | 0.316 | 1520 | 0.316 | 1.11 | 1.33 | -0.00743
CFLNoneSDGESeNewCZ06 | Com-Iltg-dWatt-CFL_OSnone | SDG | ESe | New | CZ06 | 1.52 | 0.000316 | 0 | 1.67 | 0.000416 | -0.0113 | 1.52 | 0.000316 | 0 | 1.67 | 0.000416 | -0.0113 | CFL | None | 1520 | 0.316 | 1520 | 0.316 | 1.1 | 1.32 | -0.00743
CFLNoneSDGESeNewCZ07 | Com-Iltg-dWatt-CFL_OSnone | SDG | ESe | New | CZ07 | 1.52 | 0.000316 | 0 | 1.65 | 0.000406 | -0.00979 | 1.52 | 0.000316 | 0 | 1.65 | 0.000406 | -0.00979 | CFL | None | 1520 | 0.316 | 1520 | 0.316 | 1.09 | 1.28 | -0.00644
CFLNoneSDGESeNewCZ08 | Com-Iltg-dWatt-CFL_OSnone | SDG | ESe | New | CZ08 | 1.52 | 0.000316 | 0 | 1.69 | 0.000421 | -0.00924 | 1.52 | 0.000316 | 0 | 1.69 | 0.000421 | -0.00924 | CFL | None | 1520 | 0.316 | 1520 | 0.316 | 1.11 | 1.33 | -0.00608
CFLNoneSCEESeNewCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | ESe | New | CZ08 | 1.52 | 0.000316 | 0 | 1.7 | 0.000425 | -0.00924 | 1.52 | 0.000316 | 0 | 1.7 | 0.000425 | -0.00924 | CFL | None | 1520 | 0.316 | 1520 | 0.316 | 1.12 | 1.34 | -0.00608
CFLNoneSCEESeNewCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | ESe | New | CZ09 | 1.52 | 0.000316 | 0 | 1.7 | 0.00044 | -0.0108 | 1.52 | 0.000316 | 0 | 1.7 | 0.00044 | -0.0108 | CFL | None | 1520 | 0.316 | 1520 | 0.316 | 1.12 | 1.39 | -0.00711
CFLNoneSDGESeNewCZ10 | Com-Iltg-dWatt-CFL_OSnone | SDG | ESe | New | CZ10 | 1.52 | 0.000316 | 0 | 1.7 | 0.00044 | -0.0116 | 1.52 | 0.000316 | 0 | 1.7 | 0.00044 | -0.0116 | CFL | None | 1520 | 0.316 | 1520 | 0.316 | 1.12 | 1.39 | -0.00763
CFLNoneSCEESeNewCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | ESe | New | CZ10 | 1.52 | 0.000316 | 0 | 1.71 | 0.000446 | -0.0116 | 1.52 | 0.000316 | 0 | 1.71 | 0.000446 | -0.0116 | CFL | None | 1520 | 0.316 | 1520 | 0.316 | 1.13 | 1.41 | -0.00763
CFLNonePGEESeNewCZ11 | Com-Iltg-dWatt-CFL_OSnone | PGE | ESe | New | CZ11 | 1.52 | 8.84e-06 | 0 | 1.66 | 8.84e-06 | -0.0195 | 1.52 | 8.84e-06 | 0 | 1.66 | 8.84e-06 | -0.0195 | CFL | None | 1520 | 0.00884 | 1520 | 0.00884 | 1.09 | 1 | -0.0128
CFLNonePGEESeNewCZ12 | Com-Iltg-dWatt-CFL_OSnone | PGE | ESe | New | CZ12 | 1.52 | 8.84e-06 | 0 | 1.64 | 8.84e-06 | -0.0201 | 1.52 | 8.84e-06 | 0 | 1.64 | 8.84e-06 | -0.0201 | CFL | None | 1520 | 0.00884 | 1520 | 0.00884 | 1.08 | 1 | -0.0132
CFLNoneSCEESeNewCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | ESe | New | CZ13 | 1.52 | 8.84e-06 | 0 | 1.7 | 8.84e-06 | -0.017 | 1.52 | 8.84e-06 | 0 | 1.7 | 8.84e-06 | -0.017 | CFL | None | 1520 | 0.00884 | 1520 | 0.00884 | 1.12 | 1 | -0.0112
CFLNonePGEESeNewCZ13 | Com-Iltg-dWatt-CFL_OSnone | PGE | ESe | New | CZ13 | 1.52 | 8.84e-06 | 0 | 1.67 | 8.84e-06 | -0.0181 | 1.52 | 8.84e-06 | 0 | 1.67 | 8.84e-06 | -0.0181 | CFL | None | 1520 | 0.00884 | 1520 | 0.00884 | 1.1 | 1 | -0.0119
CFLNoneSCEESeNewCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | ESe | New | CZ14 | 1.52 | 0.000316 | 0 | 1.68 | 0.000437 | -0.0169 | 1.52 | 0.000316 | 0 | 1.68 | 0.000437 | -0.0169 | CFL | None | 1520 | 0.316 | 1520 | 0.316 | 1.11 | 1.38 | -0.0111
CFLNoneSDGESeNewCZ14 | Com-Iltg-dWatt-CFL_OSnone | SDG | ESe | New | CZ14 | 1.52 | 0.000316 | 0 | 1.67 | 0.000432 | -0.017 | 1.52 | 0.000316 | 0 | 1.67 | 0.000432 | -0.017 | CFL | None | 1520 | 0.316 | 1520 | 0.316 | 1.1 | 1.37 | -0.0112
CFLNoneSCEESeNewCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | ESe | New | CZ15 | 1.52 | 0.000316 | 0 | 1.89 | 0.000442 | -0.00506 | 1.52 | 0.000316 | 0 | 1.89 | 0.000442 | -0.00506 | CFL | None | 1520 | 0.316 | 1520 | 0.316 | 1.24 | 1.4 | -0.00333
CFLNoneSDGESeNewCZ15 | Com-Iltg-dWatt-CFL_OSnone | SDG | ESe | New | CZ15 | 1.52 | 0.000316 | 0 | 1.87 | 0.000437 | -0.00511 | 1.52 | 0.000316 | 0 | 1.87 | 0.000437 | -0.00511 | CFL | None | 1520 | 0.316 | 1520 | 0.316 | 1.23 | 1.38 | -0.00336
CFLNonePGEESeNewCZ16 | Com-Iltg-dWatt-CFL_OSnone | PGE | ESe | New | CZ16 | 1.52 | 8.84e-06 | 0 | 1.52 | 8.84e-06 | -0.0225 | 1.52 | 8.84e-06 | 0 | 1.52 | 8.84e-06 | -0.0225 | CFL | None | 1520 | 0.00884 | 1520 | 0.00884 | 1 | 1 | -0.0148
CFLNoneSCEESeNewCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | ESe | New | CZ16 | 1.52 | 8.84e-06 | 0 | 1.51 | 8.84e-06 | -0.0211 | 1.52 | 8.84e-06 | 0 | 1.51 | 8.84e-06 | -0.0211 | CFL | None | 1520 | 0.00884 | 1520 | 0.00884 | 0.993 | 1 | -0.0139
CFLNoneSCEESeNewIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | ESe | New | IOU | 1.52 | 0.000316 | 0 | 1.7 | 0.00043 | -0.0112 | 1.52 | 0.000316 | 0 | 1.7 | 0.00043 | -0.0112 | CFL | None | 1520 | 0.316 | 1520 | 0.316 | 1.12 | 1.36 | -0.00737
CFLNoneSDGESeNewIOU | Com-Iltg-dWatt-CFL_OSnone | SDG | ESe | New | IOU | 1.52 | 0.000316 | 0 | 1.67 | 0.000419 | -0.0105 | 1.52 | 0.000316 | 0 | 1.67 | 0.000419 | -0.0105 | CFL | None | 1520 | 0.316 | 1520 | 0.316 | 1.1 | 1.33 | -0.00691
CFLNonePGEESeNewIOU | Com-Iltg-dWatt-CFL_OSnone | PGE | ESe | New | IOU | 1.52 | 2.78e-05 | 0 | 1.68 | 3.28e-05 | -0.0171 | 1.52 | 2.78e-05 | 0 | 1.68 | 3.28e-05 | -0.0171 | CFL | None | 1520 | 0.0278 | 1520 | 0.0278 | 1.11 | 1.18 | -0.0113
CFLNoneSCGESeNewIOU | Com-Iltg-dWatt-CFL_OSnone | SCG | ESe | New | IOU | 1.52 | 0.000316 | 0 | 1.7 | 0.00043 | -0.0111 | 1.52 | 0.000316 | 0 | 1.7 | 0.00043 | -0.0111 | CFL | None | 1520 | 0.316 | 1520 | 0.316 | 1.12 | 1.36 | -0.0073
CFLNonePGEEUnExCZ01 | Com-Iltg-dWatt-CFL_OSnone | PGE | EUn | Ex | CZ01 | 2.12 | 0.000623 | 0 | 2.24 | 0.000764 | -0.0225 | 2.12 | 0.000623 | 0 | 2.24 | 0.000764 | -0.0225 | CFL | None | 2120 | 0.623 | 2120 | 0.623 | 1.06 | 1.23 | -0.0106
CFLNonePGEEUnExCZ02 | Com-Iltg-dWatt-CFL_OSnone | PGE | EUn | Ex | CZ02 | 2.12 | 0.000409 | 0 | 2.33 | 0.000507 | -0.0165 | 2.12 | 0.000409 | 0 | 2.33 | 0.000507 | -0.0165 | CFL | None | 2120 | 0.409 | 2120 | 0.409 | 1.1 | 1.24 | -0.00778
CFLNonePGEEUnExCZ03 | Com-Iltg-dWatt-CFL_OSnone | PGE | EUn | Ex | CZ03 | 2.12 | 0.000409 | 0 | 2.33 | 0.000495 | -0.0157 | 2.12 | 0.000409 | 0 | 2.33 | 0.000495 | -0.0157 | CFL | None | 2120 | 0.409 | 2120 | 0.409 | 1.1 | 1.21 | -0.00741
CFLNonePGEEUnExCZ04 | Com-Iltg-dWatt-CFL_OSnone | PGE | EUn | Ex | CZ04 | 2.12 | 0.000623 | 0 | 2.37 | 0.000796 | -0.0128 | 2.12 | 0.000623 | 0 | 2.37 | 0.000796 | -0.0128 | CFL | None | 2120 | 0.623 | 2120 | 0.623 | 1.12 | 1.28 | -0.00604
CFLNoneSCEEUnExCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | EUn | Ex | CZ05 | 2.12 | 0.000623 | 0 | 2.35 | 0.000758 | -0.0151 | 2.12 | 0.000623 | 0 | 2.35 | 0.000758 | -0.0151 | CFL | None | 2120 | 0.623 | 2120 | 0.623 | 1.11 | 1.22 | -0.00712
CFLNoneSCGEUnExCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCG | EUn | Ex | CZ05 | 2.12 | 0.000623 | 0 | 2.35 | 0.000758 | -0.0151 | 2.12 | 0.000623 | 0 | 2.35 | 0.000758 | -0.0151 | CFL | None | 2120 | 0.623 | 2120 | 0.623 | 1.11 | 1.22 | -0.00712
CFLNonePGEEUnExCZ05 | Com-Iltg-dWatt-CFL_OSnone | PGE | EUn | Ex | CZ05 | 2.12 | 0.000623 | 0 | 2.35 | 0.000758 | -0.0151 | 2.12 | 0.000623 | 0 | 2.35 | 0.000758 | -0.0151 | CFL | None | 2120 | 0.623 | 2120 | 0.623 | 1.11 | 1.22 | -0.00712
CFLNoneSCEEUnExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | EUn | Ex | CZ06 | 2.12 | 0.000623 | 0 | 2.42 | 0.000787 | -0.00899 | 2.12 | 0.000623 | 0 | 2.42 | 0.000787 | -0.00899 | CFL | None | 2120 | 0.623 | 2120 | 0.623 | 1.14 | 1.26 | -0.00424
CFLNoneSCGEUnExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCG | EUn | Ex | CZ06 | 2.12 | 0.000623 | 0 | 2.42 | 0.000787 | -0.00899 | 2.12 | 0.000623 | 0 | 2.42 | 0.000787 | -0.00899 | CFL | None | 2120 | 0.623 | 2120 | 0.623 | 1.14 | 1.26 | -0.00424
CFLNoneSDGEUnExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SDG | EUn | Ex | CZ06 | 2.12 | 0.000623 | 0 | 2.42 | 0.000787 | -0.00899 | 2.12 | 0.000623 | 0 | 2.42 | 0.000787 | -0.00899 | CFL | None | 2120 | 0.623 | 2120 | 0.623 | 1.14 | 1.26 | -0.00424
CFLNoneSDGEUnExCZ07 | Com-Iltg-dWatt-CFL_OSnone | SDG | EUn | Ex | CZ07 | 2.12 | 0.000623 | 0 | 2.41 | 0.00078 | -0.00801 | 2.12 | 0.000623 | 0 | 2.41 | 0.00078 | -0.00801 | CFL | None | 2120 | 0.623 | 2120 | 0.623 | 1.14 | 1.25 | -0.00378
CFLNoneSCGEUnExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCG | EUn | Ex | CZ08 | 2.12 | 0.000623 | 0 | 2.43 | 0.000789 | -0.00865 | 2.12 | 0.000623 | 0 | 2.43 | 0.000789 | -0.00865 | CFL | None | 2120 | 0.623 | 2120 | 0.623 | 1.15 | 1.27 | -0.00408
CFLNoneSCEEUnExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | EUn | Ex | CZ08 | 2.12 | 0.000623 | 0 | 2.43 | 0.000789 | -0.00865 | 2.12 | 0.000623 | 0 | 2.43 | 0.000789 | -0.00865 | CFL | None | 2120 | 0.623 | 2120 | 0.623 | 1.15 | 1.27 | -0.00408
CFLNoneSDGEUnExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SDG | EUn | Ex | CZ08 | 2.12 | 0.000623 | 0 | 2.43 | 0.000789 | -0.00865 | 2.12 | 0.000623 | 0 | 2.43 | 0.000789 | -0.00865 | CFL | None | 2120 | 0.623 | 2120 | 0.623 | 1.15 | 1.27 | -0.00408
CFLNoneSCEEUnExCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | EUn | Ex | CZ09 | 2.12 | 0.000623 | 0 | 2.45 | 0.000802 | -0.00941 | 2.12 | 0.000623 | 0 | 2.45 | 0.000802 | -0.00941 | CFL | None | 2120 | 0.623 | 2120 | 0.623 | 1.16 | 1.29 | -0.00444
CFLNoneSCGEUnExCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCG | EUn | Ex | CZ09 | 2.12 | 0.000623 | 0 | 2.45 | 0.000802 | -0.00941 | 2.12 | 0.000623 | 0 | 2.45 | 0.000802 | -0.00941 | CFL | None | 2120 | 0.623 | 2120 | 0.623 | 1.16 | 1.29 | -0.00444
CFLNoneSDGEUnExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SDG | EUn | Ex | CZ10 | 2.12 | 0.000623 | 0 | 2.43 | 0.000802 | -0.0102 | 2.12 | 0.000623 | 0 | 2.43 | 0.000802 | -0.0102 | CFL | None | 2120 | 0.623 | 2120 | 0.623 | 1.15 | 1.29 | -0.00481
CFLNoneSCEEUnExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | EUn | Ex | CZ10 | 2.12 | 0.000623 | 0 | 2.43 | 0.000802 | -0.0102 | 2.12 | 0.000623 | 0 | 2.43 | 0.000802 | -0.0102 | CFL | None | 2120 | 0.623 | 2120 | 0.623 | 1.15 | 1.29 | -0.00481
CFLNoneSCGEUnExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCG | EUn | Ex | CZ10 | 2.12 | 0.000623 | 0 | 2.43 | 0.000802 | -0.0102 | 2.12 | 0.000623 | 0 | 2.43 | 0.000802 | -0.0102 | CFL | None | 2120 | 0.623 | 2120 | 0.623 | 1.15 | 1.29 | -0.00481
CFLNonePGEEUnExCZ11 | Com-Iltg-dWatt-CFL_OSnone | PGE | EUn | Ex | CZ11 | 2.12 | 0.000409 | 0 | 2.38 | 0.000515 | -0.0148 | 2.12 | 0.000409 | 0 | 2.38 | 0.000515 | -0.0148 | CFL | None | 2120 | 0.409 | 2120 | 0.409 | 1.12 | 1.26 | -0.00698
CFLNonePGEEUnExCZ12 | Com-Iltg-dWatt-CFL_OSnone | PGE | EUn | Ex | CZ12 | 2.12 | 0.000409 | 0 | 2.37 | 0.000512 | -0.0147 | 2.12 | 0.000409 | 0 | 2.37 | 0.000512 | -0.0147 | CFL | None | 2120 | 0.409 | 2120 | 0.409 | 1.12 | 1.25 | -0.00693
CFLNoneSCEEUnExCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | EUn | Ex | CZ13 | 2.12 | 0.000409 | 0 | 2.4 | 0.000515 | -0.0116 | 2.12 | 0.000409 | 0 | 2.4 | 0.000515 | -0.0116 | CFL | None | 2120 | 0.409 | 2120 | 0.409 | 1.13 | 1.26 | -0.00547
CFLNonePGEEUnExCZ13 | Com-Iltg-dWatt-CFL_OSnone | PGE | EUn | Ex | CZ13 | 2.12 | 0.000409 | 0 | 2.4 | 0.000515 | -0.0116 | 2.12 | 0.000409 | 0 | 2.4 | 0.000515 | -0.0116 | CFL | None | 2120 | 0.409 | 2120 | 0.409 | 1.13 | 1.26 | -0.00547
CFLNoneSCGEUnExCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCG | EUn | Ex | CZ13 | 2.12 | 0.000409 | 0 | 2.4 | 0.000515 | -0.0116 | 2.12 | 0.000409 | 0 | 2.4 | 0.000515 | -0.0116 | CFL | None | 2120 | 0.409 | 2120 | 0.409 | 1.13 | 1.26 | -0.00547
CFLNoneSCGEUnExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCG | EUn | Ex | CZ14 | 2.12 | 0.000623 | 0 | 2.4 | 0.000792 | -0.0141 | 2.12 | 0.000623 | 0 | 2.4 | 0.000792 | -0.0141 | CFL | None | 2120 | 0.623 | 2120 | 0.623 | 1.13 | 1.27 | -0.00665
CFLNoneSDGEUnExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SDG | EUn | Ex | CZ14 | 2.12 | 0.000623 | 0 | 2.4 | 0.000792 | -0.0141 | 2.12 | 0.000623 | 0 | 2.4 | 0.000792 | -0.0141 | CFL | None | 2120 | 0.623 | 2120 | 0.623 | 1.13 | 1.27 | -0.00665
CFLNoneSCEEUnExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | EUn | Ex | CZ14 | 2.12 | 0.000623 | 0 | 2.4 | 0.000792 | -0.0141 | 2.12 | 0.000623 | 0 | 2.4 | 0.000792 | -0.0141 | CFL | None | 2120 | 0.623 | 2120 | 0.623 | 1.13 | 1.27 | -0.00665
CFLNoneSCEEUnExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | EUn | Ex | CZ15 | 2.12 | 0.000623 | 0 | 2.51 | 0.000791 | -0.00471 | 2.12 | 0.000623 | 0 | 2.51 | 0.000791 | -0.00471 | CFL | None | 2120 | 0.623 | 2120 | 0.623 | 1.18 | 1.27 | -0.00222
CFLNoneSCGEUnExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCG | EUn | Ex | CZ15 | 2.12 | 0.000623 | 0 | 2.51 | 0.000791 | -0.00471 | 2.12 | 0.000623 | 0 | 2.51 | 0.000791 | -0.00471 | CFL | None | 2120 | 0.623 | 2120 | 0.623 | 1.18 | 1.27 | -0.00222
CFLNoneSCEEUnExCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | EUn | Ex | CZ16 | 2.12 | 0.000409 | 0 | 2.23 | 0.000499 | -0.0246 | 2.12 | 0.000409 | 0 | 2.23 | 0.000499 | -0.0246 | CFL | None | 2120 | 0.409 | 2120 | 0.409 | 1.05 | 1.22 | -0.0116
CFLNonePGEEUnExCZ16 | Com-Iltg-dWatt-CFL_OSnone | PGE | EUn | Ex | CZ16 | 2.12 | 0.000409 | 0 | 2.23 | 0.000499 | -0.0246 | 2.12 | 0.000409 | 0 | 2.23 | 0.000499 | -0.0246 | CFL | None | 2120 | 0.409 | 2120 | 0.409 | 1.05 | 1.22 | -0.0116
CFLNoneSCGEUnExCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCG | EUn | Ex | CZ16 | 2.12 | 0.000409 | 0 | 2.23 | 0.000499 | -0.0246 | 2.12 | 0.000409 | 0 | 2.23 | 0.000499 | -0.0246 | CFL | None | 2120 | 0.409 | 2120 | 0.409 | 1.05 | 1.22 | -0.0116
CFLNoneSDGEUnExIOU | Com-Iltg-dWatt-CFL_OSnone | SDG | EUn | Ex | IOU | 2.12 | 0.000623 | 0 | 2.41 | 0.000785 | -0.00857 | 2.12 | 0.000623 | 0 | 2.41 | 0.000785 | -0.00857 | CFL | None | 2120 | 0.623 | 2120 | 0.623 | 1.14 | 1.26 | -0.00404
CFLNoneSCGEUnExIOU | Com-Iltg-dWatt-CFL_OSnone | SCG | EUn | Ex | IOU | 2.12 | 0.000609 | 0 | 2.42 | 0.000774 | -0.00997 | 2.12 | 0.000609 | 0 | 2.42 | 0.000774 | -0.00997 | CFL | None | 2120 | 0.609 | 2120 | 0.609 | 1.14 | 1.27 | -0.0047
CFLNoneSCEEUnExIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | EUn | Ex | IOU | 2.12 | 0.000603 | 0 | 2.42 | 0.000764 | -0.0103 | 2.12 | 0.000603 | 0 | 2.42 | 0.000764 | -0.0103 | CFL | None | 2120 | 0.603 | 2120 | 0.603 | 1.14 | 1.27 | -0.00486
CFLNonePGEEUnExIOU | Com-Iltg-dWatt-CFL_OSnone | PGE | EUn | Ex | IOU | 2.12 | 0.00045 | 0 | 2.35 | 0.000556 | -0.0149 | 2.12 | 0.00045 | 0 | 2.35 | 0.000556 | -0.0149 | CFL | None | 2120 | 0.45 | 2120 | 0.45 | 1.11 | 1.24 | -0.00703
CFLNonePGEEUnNewCZ01 | Com-Iltg-dWatt-CFL_OSnone | PGE | EUn | New | CZ01 | 2.12 | 0.000623 | 0 | 2.22 | 0.000731 | -0.0204 | 2.12 | 0.000623 | 0 | 2.22 | 0.000731 | -0.0204 | CFL | None | 2120 | 0.623 | 2120 | 0.623 | 1.05 | 1.17 | -0.00962
CFLNonePGEEUnNewCZ02 | Com-Iltg-dWatt-CFL_OSnone | PGE | EUn | New | CZ02 | 2.12 | 0.000409 | 0 | 2.34 | 0.000533 | -0.0165 | 2.12 | 0.000409 | 0 | 2.34 | 0.000533 | -0.0165 | CFL | None | 2120 | 0.409 | 2120 | 0.409 | 1.1 | 1.3 | -0.00778
CFLNonePGEEUnNewCZ03 | Com-Iltg-dWatt-CFL_OSnone | PGE | EUn | New | CZ03 | 2.12 | 0.000409 | 0 | 2.3 | 0.000516 | -0.0122 | 2.12 | 0.000409 | 0 | 2.3 | 0.000516 | -0.0122 | CFL | None | 2120 | 0.409 | 2120 | 0.409 | 1.08 | 1.26 | -0.00575
CFLNonePGEEUnNewCZ04 | Com-Iltg-dWatt-CFL_OSnone | PGE | EUn | New | CZ04 | 2.12 | 0.000623 | 0 | 2.36 | 0.000782 | -0.011 | 2.12 | 0.000623 | 0 | 2.36 | 0.000782 | -0.011 | CFL | None | 2120 | 0.623 | 2120 | 0.623 | 1.11 | 1.26 | -0.00519
CFLNoneSCEEUnNewCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | EUn | New | CZ05 | 2.12 | 0.000623 | 0 | 2.3 | 0.000771 | -0.0139 | 2.12 | 0.000623 | 0 | 2.3 | 0.000771 | -0.0139 | CFL | None | 2120 | 0.623 | 2120 | 0.623 | 1.08 | 1.24 | -0.00656
CFLNonePGEEUnNewCZ05 | Com-Iltg-dWatt-CFL_OSnone | PGE | EUn | New | CZ05 | 2.12 | 0.000623 | 0 | 2.3 | 0.00075 | -0.0132 | 2.12 | 0.000623 | 0 | 2.3 | 0.00075 | -0.0132 | CFL | None | 2120 | 0.623 | 2120 | 0.623 | 1.08 | 1.2 | -0.00623
CFLNoneSCEEUnNewCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | EUn | New | CZ06 | 2.12 | 0.000623 | 0 | 2.43 | 0.000791 | -0.00628 | 2.12 | 0.000623 | 0 | 2.43 | 0.000791 | -0.00628 | CFL | None | 2120 | 0.623 | 2120 | 0.623 | 1.15 | 1.27 | -0.00296
CFLNoneSDGEUnNewCZ06 | Com-Iltg-dWatt-CFL_OSnone | SDG | EUn | New | CZ06 | 2.12 | 0.000623 | 0 | 2.44 | 0.000784 | -0.00689 | 2.12 | 0.000623 | 0 | 2.44 | 0.000784 | -0.00689 | CFL | None | 2120 | 0.623 | 2120 | 0.623 | 1.15 | 1.26 | -0.00325
CFLNoneSDGEUnNewCZ07 | Com-Iltg-dWatt-CFL_OSnone | SDG | EUn | New | CZ07 | 2.12 | 0.000623 | 0 | 2.42 | 0.000778 | -0.00615 | 2.12 | 0.000623 | 0 | 2.42 | 0.000778 | -0.00615 | CFL | None | 2120 | 0.623 | 2120 | 0.623 | 1.14 | 1.25 | -0.0029
CFLNoneSDGEUnNewCZ08 | Com-Iltg-dWatt-CFL_OSnone | SDG | EUn | New | CZ08 | 2.12 | 0.000623 | 0 | 2.46 | 0.000792 | -0.00608 | 2.12 | 0.000623 | 0 | 2.46 | 0.000792 | -0.00608 | CFL | None | 2120 | 0.623 | 2120 | 0.623 | 1.16 | 1.27 | -0.00287
CFLNoneSCEEUnNewCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | EUn | New | CZ08 | 2.12 | 0.000623 | 0 | 2.45 | 0.000802 | -0.00555 | 2.12 | 0.000623 | 0 | 2.45 | 0.000802 | -0.00555 | CFL | None | 2120 | 0.623 | 2120 | 0.623 | 1.16 | 1.29 | -0.00262
CFLNoneSCEEUnNewCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | EUn | New | CZ09 | 2.12 | 0.000623 | 0 | 2.46 | 0.000828 | -0.0064 | 2.12 | 0.000623 | 0 | 2.46 | 0.000828 | -0.0064 | CFL | None | 2120 | 0.623 | 2120 | 0.623 | 1.16 | 1.33 | -0.00302
CFLNoneSDGEUnNewCZ10 | Com-Iltg-dWatt-CFL_OSnone | SDG | EUn | New | CZ10 | 2.12 | 0.000623 | 0 | 2.48 | 0.000817 | -0.00704 | 2.12 | 0.000623 | 0 | 2.48 | 0.000817 | -0.00704 | CFL | None | 2120 | 0.623 | 2120 | 0.623 | 1.17 | 1.31 | -0.00332
CFLNoneSCEEUnNewCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | EUn | New | CZ10 | 2.12 | 0.000623 | 0 | 2.47 | 0.00083 | -0.00678 | 2.12 | 0.000623 | 0 | 2.47 | 0.00083 | -0.00678 | CFL | None | 2120 | 0.623 | 2120 | 0.623 | 1.17 | 1.33 | -0.0032
CFLNonePGEEUnNewCZ11 | Com-Iltg-dWatt-CFL_OSnone | PGE | EUn | New | CZ11 | 2.12 | 0.000409 | 0 | 2.41 | 0.00053 | -0.0123 | 2.12 | 0.000409 | 0 | 2.41 | 0.00053 | -0.0123 | CFL | None | 2120 | 0.409 | 2120 | 0.409 | 1.14 | 1.3 | -0.0058
CFLNonePGEEUnNewCZ12 | Com-Iltg-dWatt-CFL_OSnone | PGE | EUn | New | CZ12 | 2.12 | 0.000409 | 0 | 2.39 | 0.000532 | -0.0133 | 2.12 | 0.000409 | 0 | 2.39 | 0.000532 | -0.0133 | CFL | None | 2120 | 0.409 | 2120 | 0.409 | 1.13 | 1.3 | -0.00627
CFLNonePGEEUnNewCZ13 | Com-Iltg-dWatt-CFL_OSnone | PGE | EUn | New | CZ13 | 2.12 | 0.000409 | 0 | 2.45 | 0.000554 | -0.0138 | 2.12 | 0.000409 | 0 | 2.45 | 0.000554 | -0.0138 | CFL | None | 2120 | 0.409 | 2120 | 0.409 | 1.16 | 1.35 | -0.00651
CFLNoneSCEEUnNewCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | EUn | New | CZ13 | 2.12 | 0.000409 | 0 | 2.48 | 0.000588 | -0.0139 | 2.12 | 0.000409 | 0 | 2.48 | 0.000588 | -0.0139 | CFL | None | 2120 | 0.409 | 2120 | 0.409 | 1.17 | 1.44 | -0.00656
CFLNoneSDGEUnNewCZ14 | Com-Iltg-dWatt-CFL_OSnone | SDG | EUn | New | CZ14 | 2.12 | 0.000623 | 0 | 2.38 | 0.000756 | -0.0116 | 2.12 | 0.000623 | 0 | 2.38 | 0.000756 | -0.0116 | CFL | None | 2120 | 0.623 | 2120 | 0.623 | 1.12 | 1.21 | -0.00547
CFLNoneSCEEUnNewCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | EUn | New | CZ14 | 2.12 | 0.000623 | 0 | 2.34 | 0.000759 | -0.0114 | 2.12 | 0.000623 | 0 | 2.34 | 0.000759 | -0.0114 | CFL | None | 2120 | 0.623 | 2120 | 0.623 | 1.1 | 1.22 | -0.00538
CFLNoneSDGEUnNewCZ15 | Com-Iltg-dWatt-CFL_OSnone | SDG | EUn | New | CZ15 | 2.12 | 0.000623 | 0 | 2.59 | 0.000825 | -0.00324 | 2.12 | 0.000623 | 0 | 2.59 | 0.000825 | -0.00324 | CFL | None | 2120 | 0.623 | 2120 | 0.623 | 1.22 | 1.32 | -0.00153
CFLNoneSCEEUnNewCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | EUn | New | CZ15 | 2.12 | 0.000623 | 0 | 2.61 | 0.000844 | -0.0029 | 2.12 | 0.000623 | 0 | 2.61 | 0.000844 | -0.0029 | CFL | None | 2120 | 0.623 | 2120 | 0.623 | 1.23 | 1.35 | -0.00137
CFLNonePGEEUnNewCZ16 | Com-Iltg-dWatt-CFL_OSnone | PGE | EUn | New | CZ16 | 2.12 | 0.000409 | 0 | 2.25 | 0.000511 | -0.022 | 2.12 | 0.000409 | 0 | 2.25 | 0.000511 | -0.022 | CFL | None | 2120 | 0.409 | 2120 | 0.409 | 1.06 | 1.25 | -0.0104
CFLNoneSCEEUnNewCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | EUn | New | CZ16 | 2.12 | 0.000409 | 0 | 2.24 | 0.000528 | -0.0248 | 2.12 | 0.000409 | 0 | 2.24 | 0.000528 | -0.0248 | CFL | None | 2120 | 0.409 | 2120 | 0.409 | 1.06 | 1.29 | -0.0117
CFLNoneSDGEUnNewIOU | Com-Iltg-dWatt-CFL_OSnone | SDG | EUn | New | IOU | 2.12 | 0.000623 | 0 | 2.43 | 0.000787 | -0.00639 | 2.12 | 0.000623 | 0 | 2.43 | 0.000787 | -0.00639 | CFL | None | 2120 | 0.623 | 2120 | 0.623 | 1.15 | 1.26 | -0.00301
CFLNonePGEEUnNewIOU | Com-Iltg-dWatt-CFL_OSnone | PGE | EUn | New | IOU | 2.12 | 0.000473 | 0 | 2.42 | 0.000642 | -0.014 | 2.12 | 0.000473 | 0 | 2.42 | 0.000642 | -0.014 | CFL | None | 2120 | 0.473 | 2120 | 0.473 | 1.14 | 1.36 | -0.0066
CFLNoneSCEEUnNewIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | EUn | New | IOU | 2.12 | 0.000623 | 0 | 2.46 | 0.000795 | -0.00674 | 2.12 | 0.000623 | 0 | 2.46 | 0.000795 | -0.00674 | CFL | None | 2120 | 0.623 | 2120 | 0.623 | 1.16 | 1.28 | -0.00318
CFLNoneSCGEUnNewIOU | Com-Iltg-dWatt-CFL_OSnone | SCG | EUn | New | IOU | 2.12 | 0.000623 | 0 | 2.46 | 0.000795 | -0.00671 | 2.12 | 0.000623 | 0 | 2.46 | 0.000795 | -0.00671 | CFL | None | 2120 | 0.623 | 2120 | 0.623 | 1.16 | 1.28 | -0.00317
CFLNonePGEGroExCZ01 | Com-Iltg-dWatt-CFL_OSnone | PGE | Gro | Ex | CZ01 | 4.9 | 0.000782 | 0 | 3.94 | 0.00073 | -0.0862 | 4.9 | 0.000782 | 0 | 3.94 | 0.00073 | -0.0862 | CFL | None | 4900 | 0.782 | 4900 | 0.782 | 0.804 | 0.934 | -0.0176
CFLNonePGEGroExCZ02 | Com-Iltg-dWatt-CFL_OSnone | PGE | Gro | Ex | CZ02 | 4.9 | 0.000782 | 0 | 4.43 | 0.00105 | -0.0671 | 4.9 | 0.000782 | 0 | 4.43 | 0.00105 | -0.0671 | CFL | None | 4900 | 0.782 | 4900 | 0.782 | 0.904 | 1.34 | -0.0137
CFLNonePGEGroExCZ03 | Com-Iltg-dWatt-CFL_OSnone | PGE | Gro | Ex | CZ03 | 4.9 | 0.000782 | 0 | 4.23 | 0.000987 | -0.0764 | 4.9 | 0.000782 | 0 | 4.23 | 0.000987 | -0.0764 | CFL | None | 4900 | 0.782 | 4900 | 0.782 | 0.863 | 1.26 | -0.0156
CFLNonePGEGroExCZ04 | Com-Iltg-dWatt-CFL_OSnone | PGE | Gro | Ex | CZ04 | 4.9 | 0.000782 | 0 | 4.52 | 0.000993 | -0.0647 | 4.9 | 0.000782 | 0 | 4.52 | 0.000993 | -0.0647 | CFL | None | 4900 | 0.782 | 4900 | 0.782 | 0.922 | 1.27 | -0.0132
CFLNoneSCEGroExCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | Gro | Ex | CZ05 | 4.9 | 0.000782 | 0 | 4.69 | 0.000978 | -0.0853 | 4.9 | 0.000782 | 0 | 4.69 | 0.000978 | -0.0853 | CFL | None | 4900 | 0.782 | 4900 | 0.782 | 0.957 | 1.25 | -0.0174
CFLNoneSCGGroExCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCG | Gro | Ex | CZ05 | 4.9 | 0.000782 | 0 | 4.69 | 0.000978 | -0.0853 | 4.9 | 0.000782 | 0 | 4.69 | 0.000978 | -0.0853 | CFL | None | 4900 | 0.782 | 4900 | 0.782 | 0.957 | 1.25 | -0.0174
CFLNonePGEGroExCZ05 | Com-Iltg-dWatt-CFL_OSnone | PGE | Gro | Ex | CZ05 | 4.9 | 0.000782 | 0 | 4.69 | 0.000978 | -0.0853 | 4.9 | 0.000782 | 0 | 4.69 | 0.000978 | -0.0853 | CFL | None | 4900 | 0.782 | 4900 | 0.782 | 0.957 | 1.25 | -0.0174
CFLNoneSCGGroExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCG | Gro | Ex | CZ06 | 4.9 | 0.000782 | 0 | 4.89 | 0.000965 | -0.0671 | 4.9 | 0.000782 | 0 | 4.89 | 0.000965 | -0.0671 | CFL | None | 4900 | 0.782 | 4900 | 0.782 | 0.998 | 1.23 | -0.0137
CFLNoneSDGGroExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SDG | Gro | Ex | CZ06 | 4.9 | 0.000782 | 0 | 4.89 | 0.000965 | -0.0671 | 4.9 | 0.000782 | 0 | 4.89 | 0.000965 | -0.0671 | CFL | None | 4900 | 0.782 | 4900 | 0.782 | 0.998 | 1.23 | -0.0137
CFLNoneSCEGroExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | Gro | Ex | CZ06 | 4.9 | 0.000782 | 0 | 4.89 | 0.000965 | -0.0671 | 4.9 | 0.000782 | 0 | 4.89 | 0.000965 | -0.0671 | CFL | None | 4900 | 0.782 | 4900 | 0.782 | 0.998 | 1.23 | -0.0137
CFLNoneSDGGroExCZ07 | Com-Iltg-dWatt-CFL_OSnone | SDG | Gro | Ex | CZ07 | 4.9 | 0.000782 | 0 | 4.82 | 0.000951 | -0.072 | 4.9 | 0.000782 | 0 | 4.82 | 0.000951 | -0.072 | CFL | None | 4900 | 0.782 | 4900 | 0.782 | 0.984 | 1.22 | -0.0147
CFLNoneSCEGroExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | Gro | Ex | CZ08 | 4.9 | 0.000782 | 0 | 5 | 0.000991 | -0.0613 | 4.9 | 0.000782 | 0 | 5 | 0.000991 | -0.0613 | CFL | None | 4900 | 0.782 | 4900 | 0.782 | 1.02 | 1.27 | -0.0125
CFLNoneSDGGroExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SDG | Gro | Ex | CZ08 | 4.9 | 0.000782 | 0 | 5 | 0.000991 | -0.0613 | 4.9 | 0.000782 | 0 | 5 | 0.000991 | -0.0613 | CFL | None | 4900 | 0.782 | 4900 | 0.782 | 1.02 | 1.27 | -0.0125
CFLNoneSCGGroExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCG | Gro | Ex | CZ08 | 4.9 | 0.000782 | 0 | 5 | 0.000991 | -0.0613 | 4.9 | 0.000782 | 0 | 5 | 0.000991 | -0.0613 | CFL | None | 4900 | 0.782 | 4900 | 0.782 | 1.02 | 1.27 | -0.0125
CFLNoneSCEGroExCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | Gro | Ex | CZ09 | 4.9 | 0.000782 | 0 | 5.14 | 0.00102 | -0.0608 | 4.9 | 0.000782 | 0 | 5.14 | 0.00102 | -0.0608 | CFL | None | 4900 | 0.782 | 4900 | 0.782 | 1.05 | 1.3 | -0.0124
CFLNoneSCGGroExCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCG | Gro | Ex | CZ09 | 4.9 | 0.000782 | 0 | 5.14 | 0.00102 | -0.0608 | 4.9 | 0.000782 | 0 | 5.14 | 0.00102 | -0.0608 | CFL | None | 4900 | 0.782 | 4900 | 0.782 | 1.05 | 1.3 | -0.0124
CFLNoneSCEGroExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | Gro | Ex | CZ10 | 4.9 | 0.000782 | 0 | 5.09 | 0.00104 | -0.0578 | 4.9 | 0.000782 | 0 | 5.09 | 0.00104 | -0.0578 | CFL | None | 4900 | 0.782 | 4900 | 0.782 | 1.04 | 1.33 | -0.0118
CFLNoneSDGGroExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SDG | Gro | Ex | CZ10 | 4.9 | 0.000782 | 0 | 5.09 | 0.00104 | -0.0578 | 4.9 | 0.000782 | 0 | 5.09 | 0.00104 | -0.0578 | CFL | None | 4900 | 0.782 | 4900 | 0.782 | 1.04 | 1.33 | -0.0118
CFLNoneSCGGroExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCG | Gro | Ex | CZ10 | 4.9 | 0.000782 | 0 | 5.09 | 0.00104 | -0.0578 | 4.9 | 0.000782 | 0 | 5.09 | 0.00104 | -0.0578 | CFL | None | 4900 | 0.782 | 4900 | 0.782 | 1.04 | 1.33 | -0.0118
CFLNonePGEGroExCZ11 | Com-Iltg-dWatt-CFL_OSnone | PGE | Gro | Ex | CZ11 | 4.9 | 0.000782 | 0 | 4.8 | 0.00104 | -0.0549 | 4.9 | 0.000782 | 0 | 4.8 | 0.00104 | -0.0549 | CFL | None | 4900 | 0.782 | 4900 | 0.782 | 0.98 | 1.33 | -0.0112
CFLNonePGEGroExCZ12 | Com-Iltg-dWatt-CFL_OSnone | PGE | Gro | Ex | CZ12 | 4.9 | 0.000782 | 0 | 4.66 | 0.00103 | -0.0598 | 4.9 | 0.000782 | 0 | 4.66 | 0.00103 | -0.0598 | CFL | None | 4900 | 0.782 | 4900 | 0.782 | 0.951 | 1.32 | -0.0122
CFLNoneSCGGroExCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCG | Gro | Ex | CZ13 | 4.9 | 0.000782 | 0 | 5.14 | 0.00103 | -0.0583 | 4.9 | 0.000782 | 0 | 5.14 | 0.00103 | -0.0583 | CFL | None | 4900 | 0.782 | 4900 | 0.782 | 1.05 | 1.32 | -0.0119
CFLNoneSCEGroExCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | Gro | Ex | CZ13 | 4.9 | 0.000782 | 0 | 5.14 | 0.00103 | -0.0583 | 4.9 | 0.000782 | 0 | 5.14 | 0.00103 | -0.0583 | CFL | None | 4900 | 0.782 | 4900 | 0.782 | 1.05 | 1.32 | -0.0119
CFLNonePGEGroExCZ13 | Com-Iltg-dWatt-CFL_OSnone | PGE | Gro | Ex | CZ13 | 4.9 | 0.000782 | 0 | 5.14 | 0.00103 | -0.0583 | 4.9 | 0.000782 | 0 | 5.14 | 0.00103 | -0.0583 | CFL | None | 4900 | 0.782 | 4900 | 0.782 | 1.05 | 1.32 | -0.0119
CFLNoneSCEGroExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | Gro | Ex | CZ14 | 4.9 | 0.000782 | 0 | 5.07 | 0.00106 | -0.0583 | 4.9 | 0.000782 | 0 | 5.07 | 0.00106 | -0.0583 | CFL | None | 4900 | 0.782 | 4900 | 0.782 | 1.03 | 1.36 | -0.0119
CFLNoneSDGGroExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SDG | Gro | Ex | CZ14 | 4.9 | 0.000782 | 0 | 5.07 | 0.00106 | -0.0583 | 4.9 | 0.000782 | 0 | 5.07 | 0.00106 | -0.0583 | CFL | None | 4900 | 0.782 | 4900 | 0.782 | 1.03 | 1.36 | -0.0119
CFLNoneSCGGroExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCG | Gro | Ex | CZ14 | 4.9 | 0.000782 | 0 | 5.07 | 0.00106 | -0.0583 | 4.9 | 0.000782 | 0 | 5.07 | 0.00106 | -0.0583 | CFL | None | 4900 | 0.782 | 4900 | 0.782 | 1.03 | 1.36 | -0.0119
CFLNoneSDGGroExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SDG | Gro | Ex | CZ15 | 4.9 | 0.000782 | 0 | 5.49 | 0.00104 | -0.0336 | 4.9 | 0.000782 | 0 | 5.49 | 0.00104 | -0.0336 | CFL | None | 4900 | 0.782 | 4900 | 0.782 | 1.12 | 1.33 | -0.00686
CFLNoneSCGGroExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCG | Gro | Ex | CZ15 | 4.9 | 0.000782 | 0 | 5.49 | 0.00104 | -0.0336 | 4.9 | 0.000782 | 0 | 5.49 | 0.00104 | -0.0336 | CFL | None | 4900 | 0.782 | 4900 | 0.782 | 1.12 | 1.33 | -0.00686
CFLNoneSCEGroExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | Gro | Ex | CZ15 | 4.9 | 0.000782 | 0 | 5.49 | 0.00104 | -0.0336 | 4.9 | 0.000782 | 0 | 5.49 | 0.00104 | -0.0336 | CFL | None | 4900 | 0.782 | 4900 | 0.782 | 1.12 | 1.33 | -0.00686
CFLNonePGEGroExCZ16 | Com-Iltg-dWatt-CFL_OSnone | PGE | Gro | Ex | CZ16 | 4.9 | 0.000782 | 0 | 4.66 | 0.000985 | -0.0799 | 4.9 | 0.000782 | 0 | 4.66 | 0.000985 | -0.0799 | CFL | None | 4900 | 0.782 | 4900 | 0.782 | 0.951 | 1.26 | -0.0163
CFLNoneSCEGroExCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | Gro | Ex | CZ16 | 4.9 | 0.000782 | 0 | 4.66 | 0.000985 | -0.0799 | 4.9 | 0.000782 | 0 | 4.66 | 0.000985 | -0.0799 | CFL | None | 4900 | 0.782 | 4900 | 0.782 | 0.951 | 1.26 | -0.0163
CFLNoneSCGGroExCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCG | Gro | Ex | CZ16 | 4.9 | 0.000782 | 0 | 4.66 | 0.000985 | -0.0799 | 4.9 | 0.000782 | 0 | 4.66 | 0.000985 | -0.0799 | CFL | None | 4900 | 0.782 | 4900 | 0.782 | 0.951 | 1.26 | -0.0163
CFLNoneSCGGroExIOU | Com-Iltg-dWatt-CFL_OSnone | SCG | Gro | Ex | IOU | 4.9 | 0.000782 | 0 | 5.04 | 0.00101 | -0.0611 | 4.9 | 0.000782 | 0 | 5.04 | 0.00101 | -0.0611 | CFL | None | 4900 | 0.782 | 4900 | 0.782 | 1.03 | 1.29 | -0.0125
CFLNoneSCEGroExIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | Gro | Ex | IOU | 4.9 | 0.000782 | 0 | 5.03 | 0.00101 | -0.0611 | 4.9 | 0.000782 | 0 | 5.03 | 0.00101 | -0.0611 | CFL | None | 4900 | 0.782 | 4900 | 0.782 | 1.03 | 1.29 | -0.0125
CFLNonePGEGroExIOU | Com-Iltg-dWatt-CFL_OSnone | PGE | Gro | Ex | IOU | 4.9 | 0.000782 | 0 | 4.59 | 0.00101 | -0.0662 | 4.9 | 0.000782 | 0 | 4.59 | 0.00101 | -0.0662 | CFL | None | 4900 | 0.782 | 4900 | 0.782 | 0.937 | 1.29 | -0.0135
CFLNoneSDGGroExIOU | Com-Iltg-dWatt-CFL_OSnone | SDG | Gro | Ex | IOU | 4.9 | 0.000782 | 0 | 4.9 | 0.000977 | -0.0675 | 4.9 | 0.000782 | 0 | 4.9 | 0.000977 | -0.0675 | CFL | None | 4900 | 0.782 | 4900 | 0.782 | 1 | 1.25 | -0.0138
CFLNonePGEGroNewCZ01 | Com-Iltg-dWatt-CFL_OSnone | PGE | Gro | New | CZ01 | 4.9 | 0.000782 | 0 | 4.06 | 0.00092 | -0.0916 | 4.9 | 0.000782 | 0 | 4.06 | 0.00092 | -0.0916 | CFL | None | 4900 | 0.782 | 4900 | 0.782 | 0.829 | 1.18 | -0.0187
CFLNonePGEGroNewCZ02 | Com-Iltg-dWatt-CFL_OSnone | PGE | Gro | New | CZ02 | 4.9 | 0.000782 | 0 | 4.61 | 0.00109 | -0.0671 | 4.9 | 0.000782 | 0 | 4.61 | 0.00109 | -0.0671 | CFL | None | 4900 | 0.782 | 4900 | 0.782 | 0.941 | 1.39 | -0.0137
CFLNonePGEGroNewCZ03 | Com-Iltg-dWatt-CFL_OSnone | PGE | Gro | New | CZ03 | 4.9 | 0.000782 | 0 | 4.37 | 0.00102 | -0.0755 | 4.9 | 0.000782 | 0 | 4.37 | 0.00102 | -0.0755 | CFL | None | 4900 | 0.782 | 4900 | 0.782 | 0.892 | 1.3 | -0.0154
CFLNonePGEGroNewCZ04 | Com-Iltg-dWatt-CFL_OSnone | PGE | Gro | New | CZ04 | 4.9 | 0.000782 | 0 | 4.73 | 0.00102 | -0.0617 | 4.9 | 0.000782 | 0 | 4.73 | 0.00102 | -0.0617 | CFL | None | 4900 | 0.782 | 4900 | 0.782 | 0.965 | 1.3 | -0.0126
CFLNonePGEGroNewCZ05 | Com-Iltg-dWatt-CFL_OSnone | PGE | Gro | New | CZ05 | 4.9 | 0.000782 | 0 | 4.37 | 0.000988 | -0.075 | 4.9 | 0.000782 | 0 | 4.37 | 0.000988 | -0.075 | CFL | None | 4900 | 0.782 | 4900 | 0.782 | 0.892 | 1.26 | -0.0153
CFLNoneSCEGroNewCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | Gro | New | CZ05 | 4.9 | 0.000782 | 0 | 4.81 | 0.000988 | -0.0818 | 4.9 | 0.000782 | 0 | 4.81 | 0.000988 | -0.0818 | CFL | None | 4900 | 0.782 | 4900 | 0.782 | 0.982 | 1.26 | -0.0167
CFLNoneSDGGroNewCZ06 | Com-Iltg-dWatt-CFL_OSnone | SDG | Gro | New | CZ06 | 4.9 | 0.000782 | 0 | 5.12 | 0.000986 | -0.0559 | 4.9 | 0.000782 | 0 | 5.12 | 0.000986 | -0.0559 | CFL | None | 4900 | 0.782 | 4900 | 0.782 | 1.04 | 1.26 | -0.0114
CFLNoneSCEGroNewCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | Gro | New | CZ06 | 4.9 | 0.000782 | 0 | 5.16 | 0.000992 | -0.0583 | 4.9 | 0.000782 | 0 | 5.16 | 0.000992 | -0.0583 | CFL | None | 4900 | 0.782 | 4900 | 0.782 | 1.05 | 1.27 | -0.0119
CFLNoneSDGGroNewCZ07 | Com-Iltg-dWatt-CFL_OSnone | SDG | Gro | New | CZ07 | 4.9 | 0.000782 | 0 | 5.07 | 0.000962 | -0.0583 | 4.9 | 0.000782 | 0 | 5.07 | 0.000962 | -0.0583 | CFL | None | 4900 | 0.782 | 4900 | 0.782 | 1.03 | 1.23 | -0.0119
CFLNoneSCEGroNewCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | Gro | New | CZ08 | 4.9 | 0.000782 | 0 | 5.23 | 0.00101 | -0.051 | 4.9 | 0.000782 | 0 | 5.23 | 0.00101 | -0.051 | CFL | None | 4900 | 0.782 | 4900 | 0.782 | 1.07 | 1.29 | -0.0104
CFLNoneSDGGroNewCZ08 | Com-Iltg-dWatt-CFL_OSnone | SDG | Gro | New | CZ08 | 4.9 | 0.000782 | 0 | 5.18 | 0.001 | -0.0488 | 4.9 | 0.000782 | 0 | 5.18 | 0.001 | -0.0488 | CFL | None | 4900 | 0.782 | 4900 | 0.782 | 1.06 | 1.28 | -0.00996
CFLNoneSCEGroNewCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | Gro | New | CZ09 | 4.9 | 0.000782 | 0 | 5.24 | 0.00107 | -0.0539 | 4.9 | 0.000782 | 0 | 5.24 | 0.00107 | -0.0539 | CFL | None | 4900 | 0.782 | 4900 | 0.782 | 1.07 | 1.37 | -0.011
CFLNoneSDGGroNewCZ10 | Com-Iltg-dWatt-CFL_OSnone | SDG | Gro | New | CZ10 | 4.9 | 0.000782 | 0 | 5.24 | 0.0011 | -0.051 | 4.9 | 0.000782 | 0 | 5.24 | 0.0011 | -0.051 | CFL | None | 4900 | 0.782 | 4900 | 0.782 | 1.07 | 1.41 | -0.0104
CFLNoneSCEGroNewCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | Gro | New | CZ10 | 4.9 | 0.000782 | 0 | 5.28 | 0.00111 | -0.0529 | 4.9 | 0.000782 | 0 | 5.28 | 0.00111 | -0.0529 | CFL | None | 4900 | 0.782 | 4900 | 0.782 | 1.08 | 1.42 | -0.0108
CFLNonePGEGroNewCZ11 | Com-Iltg-dWatt-CFL_OSnone | PGE | Gro | New | CZ11 | 4.9 | 0.000782 | 0 | 4.96 | 0.00109 | -0.0534 | 4.9 | 0.000782 | 0 | 4.96 | 0.00109 | -0.0534 | CFL | None | 4900 | 0.782 | 4900 | 0.782 | 1.01 | 1.39 | -0.0109
CFLNonePGEGroNewCZ12 | Com-Iltg-dWatt-CFL_OSnone | PGE | Gro | New | CZ12 | 4.9 | 0.000782 | 0 | 4.86 | 0.0011 | -0.0593 | 4.9 | 0.000782 | 0 | 4.86 | 0.0011 | -0.0593 | CFL | None | 4900 | 0.782 | 4900 | 0.782 | 0.992 | 1.41 | -0.0121
CFLNonePGEGroNewCZ13 | Com-Iltg-dWatt-CFL_OSnone | PGE | Gro | New | CZ13 | 4.9 | 0.000782 | 0 | 5.01 | 0.00106 | -0.0505 | 4.9 | 0.000782 | 0 | 5.01 | 0.00106 | -0.0505 | CFL | None | 4900 | 0.782 | 4900 | 0.782 | 1.02 | 1.36 | -0.0103
CFLNoneSCEGroNewCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | Gro | New | CZ13 | 4.9 | 0.000782 | 0 | 5.29 | 0.00107 | -0.0554 | 4.9 | 0.000782 | 0 | 5.29 | 0.00107 | -0.0554 | CFL | None | 4900 | 0.782 | 4900 | 0.782 | 1.08 | 1.37 | -0.0113
CFLNoneSCEGroNewCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | Gro | New | CZ14 | 4.9 | 0.000782 | 0 | 5.3 | 0.00109 | -0.0583 | 4.9 | 0.000782 | 0 | 5.3 | 0.00109 | -0.0583 | CFL | None | 4900 | 0.782 | 4900 | 0.782 | 1.08 | 1.39 | -0.0119
CFLNoneSDGGroNewCZ14 | Com-Iltg-dWatt-CFL_OSnone | SDG | Gro | New | CZ14 | 4.9 | 0.000782 | 0 | 5.25 | 0.00107 | -0.0559 | 4.9 | 0.000782 | 0 | 5.25 | 0.00107 | -0.0559 | CFL | None | 4900 | 0.782 | 4900 | 0.782 | 1.07 | 1.37 | -0.0114
CFLNoneSDGGroNewCZ15 | Com-Iltg-dWatt-CFL_OSnone | SDG | Gro | New | CZ15 | 4.9 | 0.000782 | 0 | 5.66 | 0.00109 | -0.0289 | 4.9 | 0.000782 | 0 | 5.66 | 0.00109 | -0.0289 | CFL | None | 4900 | 0.782 | 4900 | 0.782 | 1.16 | 1.39 | -0.0059
CFLNoneSCEGroNewCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | Gro | New | CZ15 | 4.9 | 0.000782 | 0 | 5.71 | 0.0011 | -0.0301 | 4.9 | 0.000782 | 0 | 5.71 | 0.0011 | -0.0301 | CFL | None | 4900 | 0.782 | 4900 | 0.782 | 1.17 | 1.41 | -0.00614
CFLNoneSCEGroNewCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | Gro | New | CZ16 | 4.9 | 0.000782 | 0 | 4.81 | 0.00101 | -0.076 | 4.9 | 0.000782 | 0 | 4.81 | 0.00101 | -0.076 | CFL | None | 4900 | 0.782 | 4900 | 0.782 | 0.982 | 1.29 | -0.0155
CFLNonePGEGroNewCZ16 | Com-Iltg-dWatt-CFL_OSnone | PGE | Gro | New | CZ16 | 4.9 | 0.000782 | 0 | 4.42 | 0.000995 | -0.0696 | 4.9 | 0.000782 | 0 | 4.42 | 0.000995 | -0.0696 | CFL | None | 4900 | 0.782 | 4900 | 0.782 | 0.902 | 1.27 | -0.0142
CFLNoneSCGGroNewIOU | Com-Iltg-dWatt-CFL_OSnone | SCG | Gro | New | IOU | 4.9 | 0.000782 | 0 | 5.22 | 0.00104 | -0.0506 | 4.9 | 0.000782 | 0 | 5.22 | 0.00104 | -0.0506 | CFL | None | 4900 | 0.782 | 4900 | 0.782 | 1.07 | 1.33 | -0.0103
CFLNoneSCEGroNewIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | Gro | New | IOU | 4.9 | 0.000782 | 0 | 5.22 | 0.00105 | -0.0505 | 4.9 | 0.000782 | 0 | 5.22 | 0.00105 | -0.0505 | CFL | None | 4900 | 0.782 | 4900 | 0.782 | 1.07 | 1.34 | -0.0103
CFLNoneSDGGroNewIOU | Com-Iltg-dWatt-CFL_OSnone | SDG | Gro | New | IOU | 4.9 | 0.000782 | 0 | 5.12 | 0.001 | -0.0559 | 4.9 | 0.000782 | 0 | 5.12 | 0.001 | -0.0559 | CFL | None | 4900 | 0.782 | 4900 | 0.782 | 1.04 | 1.28 | -0.0114
CFLNonePGEGroNewIOU | Com-Iltg-dWatt-CFL_OSnone | PGE | Gro | New | IOU | 4.9 | 0.000782 | 0 | 5.22 | 0.00106 | -0.0591 | 4.9 | 0.000782 | 0 | 5.22 | 0.00106 | -0.0591 | CFL | None | 4900 | 0.782 | 4900 | 0.782 | 1.07 | 1.36 | -0.0121
CFLNonePGEHspExCZ01 | Com-Iltg-dWatt-CFL_OSnone | PGE | Hsp | Ex | CZ01 | 5.37 | 0.000832 | 0 | 5.75 | 0.000953 | -0.0471 | 5.37 | 0.000832 | 0 | 5.75 | 0.000953 | -0.0471 | CFL | None | 5370 | 0.832 | 5370 | 0.832 | 1.07 | 1.15 | -0.00877
CFLNonePGEHspExCZ02 | Com-Iltg-dWatt-CFL_OSnone | PGE | Hsp | Ex | CZ02 | 5.37 | 0.000832 | 0 | 5.91 | 0.00102 | -0.0368 | 5.37 | 0.000832 | 0 | 5.91 | 0.00102 | -0.0368 | CFL | None | 5370 | 0.832 | 5370 | 0.832 | 1.1 | 1.23 | -0.00685
CFLNonePGEHspExCZ03 | Com-Iltg-dWatt-CFL_OSnone | PGE | Hsp | Ex | CZ03 | 5.37 | 0.000832 | 0 | 5.94 | 0.000998 | -0.035 | 5.37 | 0.000832 | 0 | 5.94 | 0.000998 | -0.035 | CFL | None | 5370 | 0.832 | 5370 | 0.832 | 1.11 | 1.2 | -0.00652
CFLNonePGEHspExCZ04 | Com-Iltg-dWatt-CFL_OSnone | PGE | Hsp | Ex | CZ04 | 5.37 | 0.000832 | 0 | 5.94 | 0.00101 | -0.0332 | 5.37 | 0.000832 | 0 | 5.94 | 0.00101 | -0.0332 | CFL | None | 5370 | 0.832 | 5370 | 0.832 | 1.11 | 1.21 | -0.00618
CFLNoneSCGHspExCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCG | Hsp | Ex | CZ05 | 5.37 | 0.000832 | 0 | 6.02 | 0.00101 | -0.0378 | 5.37 | 0.000832 | 0 | 6.02 | 0.00101 | -0.0378 | CFL | None | 5370 | 0.832 | 5370 | 0.832 | 1.12 | 1.21 | -0.00704
CFLNoneSCEHspExCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | Hsp | Ex | CZ05 | 5.37 | 0.000832 | 0 | 6.02 | 0.00101 | -0.0378 | 5.37 | 0.000832 | 0 | 6.02 | 0.00101 | -0.0378 | CFL | None | 5370 | 0.832 | 5370 | 0.832 | 1.12 | 1.21 | -0.00704
CFLNonePGEHspExCZ05 | Com-Iltg-dWatt-CFL_OSnone | PGE | Hsp | Ex | CZ05 | 5.37 | 0.000832 | 0 | 6.02 | 0.00101 | -0.0378 | 5.37 | 0.000832 | 0 | 6.02 | 0.00101 | -0.0378 | CFL | None | 5370 | 0.832 | 5370 | 0.832 | 1.12 | 1.21 | -0.00704
CFLNoneSCGHspExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCG | Hsp | Ex | CZ06 | 5.37 | 0.000832 | 0 | 6.14 | 0.00103 | -0.0288 | 5.37 | 0.000832 | 0 | 6.14 | 0.00103 | -0.0288 | CFL | None | 5370 | 0.832 | 5370 | 0.832 | 1.14 | 1.24 | -0.00536
CFLNoneSDGHspExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SDG | Hsp | Ex | CZ06 | 5.37 | 0.000832 | 0 | 6.14 | 0.00103 | -0.0288 | 5.37 | 0.000832 | 0 | 6.14 | 0.00103 | -0.0288 | CFL | None | 5370 | 0.832 | 5370 | 0.832 | 1.14 | 1.24 | -0.00536
CFLNoneSCEHspExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | Hsp | Ex | CZ06 | 5.37 | 0.000832 | 0 | 6.14 | 0.00103 | -0.0288 | 5.37 | 0.000832 | 0 | 6.14 | 0.00103 | -0.0288 | CFL | None | 5370 | 0.832 | 5370 | 0.832 | 1.14 | 1.24 | -0.00536
CFLNoneSDGHspExCZ07 | Com-Iltg-dWatt-CFL_OSnone | SDG | Hsp | Ex | CZ07 | 5.37 | 0.000832 | 0 | 6.14 | 0.00102 | -0.0265 | 5.37 | 0.000832 | 0 | 6.14 | 0.00102 | -0.0265 | CFL | None | 5370 | 0.832 | 5370 | 0.832 | 1.14 | 1.23 | -0.00493
CFLNoneSCGHspExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCG | Hsp | Ex | CZ08 | 5.37 | 0.000832 | 0 | 6.18 | 0.00103 | -0.0284 | 5.37 | 0.000832 | 0 | 6.18 | 0.00103 | -0.0284 | CFL | None | 5370 | 0.832 | 5370 | 0.832 | 1.15 | 1.24 | -0.00529
CFLNoneSCEHspExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | Hsp | Ex | CZ08 | 5.37 | 0.000832 | 0 | 6.18 | 0.00103 | -0.0284 | 5.37 | 0.000832 | 0 | 6.18 | 0.00103 | -0.0284 | CFL | None | 5370 | 0.832 | 5370 | 0.832 | 1.15 | 1.24 | -0.00529
CFLNoneSDGHspExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SDG | Hsp | Ex | CZ08 | 5.37 | 0.000832 | 0 | 6.18 | 0.00103 | -0.0284 | 5.37 | 0.000832 | 0 | 6.18 | 0.00103 | -0.0284 | CFL | None | 5370 | 0.832 | 5370 | 0.832 | 1.15 | 1.24 | -0.00529
CFLNoneSCGHspExCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCG | Hsp | Ex | CZ09 | 5.37 | 0.000832 | 0 | 6.27 | 0.00107 | -0.0281 | 5.37 | 0.000832 | 0 | 6.27 | 0.00107 | -0.0281 | CFL | None | 5370 | 0.832 | 5370 | 0.832 | 1.17 | 1.29 | -0.00523
CFLNoneSCEHspExCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | Hsp | Ex | CZ09 | 5.37 | 0.000832 | 0 | 6.27 | 0.00107 | -0.0281 | 5.37 | 0.000832 | 0 | 6.27 | 0.00107 | -0.0281 | CFL | None | 5370 | 0.832 | 5370 | 0.832 | 1.17 | 1.29 | -0.00523
CFLNoneSCEHspExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | Hsp | Ex | CZ10 | 5.37 | 0.000832 | 0 | 6.16 | 0.00105 | -0.0303 | 5.37 | 0.000832 | 0 | 6.16 | 0.00105 | -0.0303 | CFL | None | 5370 | 0.832 | 5370 | 0.832 | 1.15 | 1.26 | -0.00564
CFLNoneSCGHspExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCG | Hsp | Ex | CZ10 | 5.37 | 0.000832 | 0 | 6.16 | 0.00105 | -0.0303 | 5.37 | 0.000832 | 0 | 6.16 | 0.00105 | -0.0303 | CFL | None | 5370 | 0.832 | 5370 | 0.832 | 1.15 | 1.26 | -0.00564
CFLNoneSDGHspExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SDG | Hsp | Ex | CZ10 | 5.37 | 0.000832 | 0 | 6.16 | 0.00105 | -0.0303 | 5.37 | 0.000832 | 0 | 6.16 | 0.00105 | -0.0303 | CFL | None | 5370 | 0.832 | 5370 | 0.832 | 1.15 | 1.26 | -0.00564
CFLNonePGEHspExCZ11 | Com-Iltg-dWatt-CFL_OSnone | PGE | Hsp | Ex | CZ11 | 5.37 | 0.000832 | 0 | 5.97 | 0.00103 | -0.0347 | 5.37 | 0.000832 | 0 | 5.97 | 0.00103 | -0.0347 | CFL | None | 5370 | 0.832 | 5370 | 0.832 | 1.11 | 1.24 | -0.00646
CFLNonePGEHspExCZ12 | Com-Iltg-dWatt-CFL_OSnone | PGE | Hsp | Ex | CZ12 | 5.37 | 0.000832 | 0 | 5.96 | 0.00103 | -0.0337 | 5.37 | 0.000832 | 0 | 5.96 | 0.00103 | -0.0337 | CFL | None | 5370 | 0.832 | 5370 | 0.832 | 1.11 | 1.24 | -0.00628
CFLNoneSCEHspExCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | Hsp | Ex | CZ13 | 5.37 | 0.000832 | 0 | 6.08 | 0.00105 | -0.0345 | 5.37 | 0.000832 | 0 | 6.08 | 0.00105 | -0.0345 | CFL | None | 5370 | 0.832 | 5370 | 0.832 | 1.13 | 1.26 | -0.00642
CFLNoneSCGHspExCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCG | Hsp | Ex | CZ13 | 5.37 | 0.000832 | 0 | 6.08 | 0.00105 | -0.0345 | 5.37 | 0.000832 | 0 | 6.08 | 0.00105 | -0.0345 | CFL | None | 5370 | 0.832 | 5370 | 0.832 | 1.13 | 1.26 | -0.00642
CFLNonePGEHspExCZ13 | Com-Iltg-dWatt-CFL_OSnone | PGE | Hsp | Ex | CZ13 | 5.37 | 0.000832 | 0 | 6.08 | 0.00105 | -0.0345 | 5.37 | 0.000832 | 0 | 6.08 | 0.00105 | -0.0345 | CFL | None | 5370 | 0.832 | 5370 | 0.832 | 1.13 | 1.26 | -0.00642
CFLNoneSDGHspExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SDG | Hsp | Ex | CZ14 | 5.37 | 0.000832 | 0 | 6.08 | 0.00105 | -0.0372 | 5.37 | 0.000832 | 0 | 6.08 | 0.00105 | -0.0372 | CFL | None | 5370 | 0.832 | 5370 | 0.832 | 1.13 | 1.26 | -0.00693
CFLNoneSCEHspExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | Hsp | Ex | CZ14 | 5.37 | 0.000832 | 0 | 6.08 | 0.00105 | -0.0372 | 5.37 | 0.000832 | 0 | 6.08 | 0.00105 | -0.0372 | CFL | None | 5370 | 0.832 | 5370 | 0.832 | 1.13 | 1.26 | -0.00693
CFLNoneSCGHspExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCG | Hsp | Ex | CZ14 | 5.37 | 0.000832 | 0 | 6.08 | 0.00105 | -0.0372 | 5.37 | 0.000832 | 0 | 6.08 | 0.00105 | -0.0372 | CFL | None | 5370 | 0.832 | 5370 | 0.832 | 1.13 | 1.26 | -0.00693
CFLNoneSCEHspExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | Hsp | Ex | CZ15 | 5.37 | 0.000832 | 0 | 6.26 | 0.00104 | -0.0245 | 5.37 | 0.000832 | 0 | 6.26 | 0.00104 | -0.0245 | CFL | None | 5370 | 0.832 | 5370 | 0.832 | 1.17 | 1.25 | -0.00456
CFLNoneSCGHspExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCG | Hsp | Ex | CZ15 | 5.37 | 0.000832 | 0 | 6.26 | 0.00104 | -0.0245 | 5.37 | 0.000832 | 0 | 6.26 | 0.00104 | -0.0245 | CFL | None | 5370 | 0.832 | 5370 | 0.832 | 1.17 | 1.25 | -0.00456
CFLNoneSCGHspExCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCG | Hsp | Ex | CZ16 | 5.37 | 0.000832 | 0 | 5.68 | 0.00102 | -0.0507 | 5.37 | 0.000832 | 0 | 5.68 | 0.00102 | -0.0507 | CFL | None | 5370 | 0.832 | 5370 | 0.832 | 1.06 | 1.23 | -0.00944
CFLNoneSCEHspExCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | Hsp | Ex | CZ16 | 5.37 | 0.000832 | 0 | 5.68 | 0.00102 | -0.0507 | 5.37 | 0.000832 | 0 | 5.68 | 0.00102 | -0.0507 | CFL | None | 5370 | 0.832 | 5370 | 0.832 | 1.06 | 1.23 | -0.00944
CFLNonePGEHspExCZ16 | Com-Iltg-dWatt-CFL_OSnone | PGE | Hsp | Ex | CZ16 | 5.37 | 0.000832 | 0 | 5.68 | 0.00102 | -0.0507 | 5.37 | 0.000832 | 0 | 5.68 | 0.00102 | -0.0507 | CFL | None | 5370 | 0.832 | 5370 | 0.832 | 1.06 | 1.23 | -0.00944
CFLNoneSCEHspExIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | Hsp | Ex | IOU | 5.37 | 0.000832 | 0 | 6.16 | 0.00104 | -0.0297 | 5.37 | 0.000832 | 0 | 6.16 | 0.00104 | -0.0297 | CFL | None | 5370 | 0.832 | 5370 | 0.832 | 1.15 | 1.25 | -0.00553
CFLNoneSDGHspExIOU | Com-Iltg-dWatt-CFL_OSnone | SDG | Hsp | Ex | IOU | 5.37 | 0.000832 | 0 | 6.14 | 0.00102 | -0.0272 | 5.37 | 0.000832 | 0 | 6.14 | 0.00102 | -0.0272 | CFL | None | 5370 | 0.832 | 5370 | 0.832 | 1.14 | 1.23 | -0.00507
CFLNonePGEHspExIOU | Com-Iltg-dWatt-CFL_OSnone | PGE | Hsp | Ex | IOU | 5.37 | 0.000832 | 0 | 5.97 | 0.00102 | -0.0348 | 5.37 | 0.000832 | 0 | 5.97 | 0.00102 | -0.0348 | CFL | None | 5370 | 0.832 | 5370 | 0.832 | 1.11 | 1.23 | -0.00648
CFLNoneSCGHspExIOU | Com-Iltg-dWatt-CFL_OSnone | SCG | Hsp | Ex | IOU | 5.37 | 0.000832 | 0 | 6.18 | 0.00105 | -0.0293 | 5.37 | 0.000832 | 0 | 6.18 | 0.00105 | -0.0293 | CFL | None | 5370 | 0.832 | 5370 | 0.832 | 1.15 | 1.26 | -0.00546
CFLNonePGEHspNewCZ01 | Com-Iltg-dWatt-CFL_OSnone | PGE | Hsp | New | CZ01 | 5.37 | 0.000832 | 0 | 5.49 | 0.000909 | -0.05 | 5.37 | 0.000832 | 0 | 5.49 | 0.000909 | -0.05 | CFL | None | 5370 | 0.832 | 5370 | 0.832 | 1.02 | 1.09 | -0.00931
CFLNonePGEHspNewCZ02 | Com-Iltg-dWatt-CFL_OSnone | PGE | Hsp | New | CZ02 | 5.37 | 0.000832 | 0 | 5.69 | 0.000995 | -0.04 | 5.37 | 0.000832 | 0 | 5.69 | 0.000995 | -0.04 | CFL | None | 5370 | 0.832 | 5370 | 0.832 | 1.06 | 1.2 | -0.00745
CFLNonePGEHspNewCZ03 | Com-Iltg-dWatt-CFL_OSnone | PGE | Hsp | New | CZ03 | 5.37 | 0.000832 | 0 | 5.67 | 0.00097 | -0.0359 | 5.37 | 0.000832 | 0 | 5.67 | 0.00097 | -0.0359 | CFL | None | 5370 | 0.832 | 5370 | 0.832 | 1.06 | 1.17 | -0.00669
CFLNonePGEHspNewCZ04 | Com-Iltg-dWatt-CFL_OSnone | PGE | Hsp | New | CZ04 | 5.37 | 0.000832 | 0 | 5.74 | 0.000987 | -0.035 | 5.37 | 0.000832 | 0 | 5.74 | 0.000987 | -0.035 | CFL | None | 5370 | 0.832 | 5370 | 0.832 | 1.07 | 1.19 | -0.00652
CFLNoneSCEHspNewCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | Hsp | New | CZ05 | 5.37 | 0.000832 | 0 | 5.67 | 0.000983 | -0.0401 | 5.37 | 0.000832 | 0 | 5.67 | 0.000983 | -0.0401 | CFL | None | 5370 | 0.832 | 5370 | 0.832 | 1.06 | 1.18 | -0.00747
CFLNonePGEHspNewCZ05 | Com-Iltg-dWatt-CFL_OSnone | PGE | Hsp | New | CZ05 | 5.37 | 0.000832 | 0 | 5.63 | 0.000957 | -0.0403 | 5.37 | 0.000832 | 0 | 5.63 | 0.000957 | -0.0403 | CFL | None | 5370 | 0.832 | 5370 | 0.832 | 1.05 | 1.15 | -0.0075
CFLNoneSDGHspNewCZ06 | Com-Iltg-dWatt-CFL_OSnone | SDG | Hsp | New | CZ06 | 5.37 | 0.000832 | 0 | 5.87 | 0.000994 | -0.0307 | 5.37 | 0.000832 | 0 | 5.87 | 0.000994 | -0.0307 | CFL | None | 5370 | 0.832 | 5370 | 0.832 | 1.09 | 1.19 | -0.00572
CFLNoneSCEHspNewCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | Hsp | New | CZ06 | 5.37 | 0.000832 | 0 | 5.88 | 0.001 | -0.0308 | 5.37 | 0.000832 | 0 | 5.88 | 0.001 | -0.0308 | CFL | None | 5370 | 0.832 | 5370 | 0.832 | 1.09 | 1.2 | -0.00574
CFLNoneSDGHspNewCZ07 | Com-Iltg-dWatt-CFL_OSnone | SDG | Hsp | New | CZ07 | 5.37 | 0.000832 | 0 | 5.9 | 0.000988 | -0.0263 | 5.37 | 0.000832 | 0 | 5.9 | 0.000988 | -0.0263 | CFL | None | 5370 | 0.832 | 5370 | 0.832 | 1.1 | 1.19 | -0.0049
CFLNoneSDGHspNewCZ08 | Com-Iltg-dWatt-CFL_OSnone | SDG | Hsp | New | CZ08 | 5.37 | 0.000832 | 0 | 5.93 | 0.000999 | -0.0284 | 5.37 | 0.000832 | 0 | 5.93 | 0.000999 | -0.0284 | CFL | None | 5370 | 0.832 | 5370 | 0.832 | 1.1 | 1.2 | -0.00529
CFLNoneSCEHspNewCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | Hsp | New | CZ08 | 5.37 | 0.000832 | 0 | 5.94 | 0.00101 | -0.0284 | 5.37 | 0.000832 | 0 | 5.94 | 0.00101 | -0.0284 | CFL | None | 5370 | 0.832 | 5370 | 0.832 | 1.11 | 1.21 | -0.00529
CFLNoneSCEHspNewCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | Hsp | New | CZ09 | 5.37 | 0.000832 | 0 | 5.97 | 0.00103 | -0.0289 | 5.37 | 0.000832 | 0 | 5.97 | 0.00103 | -0.0289 | CFL | None | 5370 | 0.832 | 5370 | 0.832 | 1.11 | 1.24 | -0.00538
CFLNoneSCEHspNewCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | Hsp | New | CZ10 | 5.37 | 0.000832 | 0 | 5.94 | 0.00104 | -0.0317 | 5.37 | 0.000832 | 0 | 5.94 | 0.00104 | -0.0317 | CFL | None | 5370 | 0.832 | 5370 | 0.832 | 1.11 | 1.25 | -0.0059
CFLNoneSDGHspNewCZ10 | Com-Iltg-dWatt-CFL_OSnone | SDG | Hsp | New | CZ10 | 5.37 | 0.000832 | 0 | 5.93 | 0.00103 | -0.032 | 5.37 | 0.000832 | 0 | 5.93 | 0.00103 | -0.032 | CFL | None | 5370 | 0.832 | 5370 | 0.832 | 1.1 | 1.24 | -0.00596
CFLNonePGEHspNewCZ11 | Com-Iltg-dWatt-CFL_OSnone | PGE | Hsp | New | CZ11 | 5.37 | 0.000832 | 0 | 5.82 | 0.001 | -0.0373 | 5.37 | 0.000832 | 0 | 5.82 | 0.001 | -0.0373 | CFL | None | 5370 | 0.832 | 5370 | 0.832 | 1.08 | 1.2 | -0.00695
CFLNonePGEHspNewCZ12 | Com-Iltg-dWatt-CFL_OSnone | PGE | Hsp | New | CZ12 | 5.37 | 0.000832 | 0 | 5.78 | 0.001 | -0.0362 | 5.37 | 0.000832 | 0 | 5.78 | 0.001 | -0.0362 | CFL | None | 5370 | 0.832 | 5370 | 0.832 | 1.08 | 1.2 | -0.00674
CFLNoneSCEHspNewCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | Hsp | New | CZ13 | 5.37 | 0.000832 | 0 | 5.92 | 0.00103 | -0.0358 | 5.37 | 0.000832 | 0 | 5.92 | 0.00103 | -0.0358 | CFL | None | 5370 | 0.832 | 5370 | 0.832 | 1.1 | 1.24 | -0.00667
CFLNonePGEHspNewCZ13 | Com-Iltg-dWatt-CFL_OSnone | PGE | Hsp | New | CZ13 | 5.37 | 0.000832 | 0 | 5.83 | 0.000998 | -0.0353 | 5.37 | 0.000832 | 0 | 5.83 | 0.000998 | -0.0353 | CFL | None | 5370 | 0.832 | 5370 | 0.832 | 1.09 | 1.2 | -0.00657
CFLNoneSCEHspNewCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | Hsp | New | CZ14 | 5.37 | 0.000832 | 0 | 5.85 | 0.00103 | -0.0395 | 5.37 | 0.000832 | 0 | 5.85 | 0.00103 | -0.0395 | CFL | None | 5370 | 0.832 | 5370 | 0.832 | 1.09 | 1.24 | -0.00736
CFLNoneSDGHspNewCZ14 | Com-Iltg-dWatt-CFL_OSnone | SDG | Hsp | New | CZ14 | 5.37 | 0.000832 | 0 | 5.85 | 0.00102 | -0.0397 | 5.37 | 0.000832 | 0 | 5.85 | 0.00102 | -0.0397 | CFL | None | 5370 | 0.832 | 5370 | 0.832 | 1.09 | 1.23 | -0.00739
CFLNoneSDGHspNewCZ15 | Com-Iltg-dWatt-CFL_OSnone | SDG | Hsp | New | CZ15 | 5.37 | 0.000832 | 0 | 6.21 | 0.00104 | -0.0258 | 5.37 | 0.000832 | 0 | 6.21 | 0.00104 | -0.0258 | CFL | None | 5370 | 0.832 | 5370 | 0.832 | 1.16 | 1.25 | -0.0048
CFLNoneSCEHspNewCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | Hsp | New | CZ15 | 5.37 | 0.000832 | 0 | 6.23 | 0.00105 | -0.0256 | 5.37 | 0.000832 | 0 | 6.23 | 0.00105 | -0.0256 | CFL | None | 5370 | 0.832 | 5370 | 0.832 | 1.16 | 1.26 | -0.00477
CFLNoneSCEHspNewCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | Hsp | New | CZ16 | 5.37 | 0.000832 | 0 | 5.42 | 0.000995 | -0.0569 | 5.37 | 0.000832 | 0 | 5.42 | 0.000995 | -0.0569 | CFL | None | 5370 | 0.832 | 5370 | 0.832 | 1.01 | 1.2 | -0.0106
CFLNonePGEHspNewCZ16 | Com-Iltg-dWatt-CFL_OSnone | PGE | Hsp | New | CZ16 | 5.37 | 0.000832 | 0 | 5.43 | 0.000968 | -0.0596 | 5.37 | 0.000832 | 0 | 5.43 | 0.000968 | -0.0596 | CFL | None | 5370 | 0.832 | 5370 | 0.832 | 1.01 | 1.16 | -0.0111
CFLNoneSCEHspNewIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | Hsp | New | IOU | 5.37 | 0.000832 | 0 | 5.93 | 0.00101 | -0.0306 | 5.37 | 0.000832 | 0 | 5.93 | 0.00101 | -0.0306 | CFL | None | 5370 | 0.832 | 5370 | 0.832 | 1.1 | 1.21 | -0.0057
CFLNoneSDGHspNewIOU | Com-Iltg-dWatt-CFL_OSnone | SDG | Hsp | New | IOU | 5.37 | 0.000832 | 0 | 5.9 | 0.000995 | -0.0273 | 5.37 | 0.000832 | 0 | 5.9 | 0.000995 | -0.0273 | CFL | None | 5370 | 0.832 | 5370 | 0.832 | 1.1 | 1.2 | -0.00508
CFLNonePGEHspNewIOU | Com-Iltg-dWatt-CFL_OSnone | PGE | Hsp | New | IOU | 5.37 | 0.000832 | 0 | 5.89 | 0.00103 | -0.0365 | 5.37 | 0.000832 | 0 | 5.89 | 0.00103 | -0.0365 | CFL | None | 5370 | 0.832 | 5370 | 0.832 | 1.1 | 1.24 | -0.0068
CFLNoneSCGHspNewIOU | Com-Iltg-dWatt-CFL_OSnone | SCG | Hsp | New | IOU | 5.37 | 0.000832 | 0 | 5.93 | 0.00101 | -0.0304 | 5.37 | 0.000832 | 0 | 5.93 | 0.00101 | -0.0304 | CFL | None | 5370 | 0.832 | 5370 | 0.832 | 1.1 | 1.21 | -0.00566
CFLNonePGEHtlExCZ01 | Com-Iltg-dWatt-CFL_OSnone | PGE | Htl | Ex | CZ01 | 1.6 | 0.000198 | 0 | 1.45 | 0.000237 | -0.0084 | 1.6 | 0.000198 | 0 | 1.45 | 0.000237 | -0.0084 | CFL | None | 1600 | 0.198 | 1600 | 0.198 | 0.906 | 1.2 | -0.00525
CFLNonePGEHtlExCZ02 | Com-Iltg-dWatt-CFL_OSnone | PGE | Htl | Ex | CZ02 | 1.6 | 0.000198 | 0 | 1.58 | 0.000246 | -0.00611 | 1.6 | 0.000198 | 0 | 1.58 | 0.000246 | -0.00611 | CFL | None | 1600 | 0.198 | 1600 | 0.198 | 0.988 | 1.24 | -0.00382
CFLNonePGEHtlExCZ03 | Com-Iltg-dWatt-CFL_OSnone | PGE | Htl | Ex | CZ03 | 1.6 | 0.000198 | 0 | 1.6 | 0.000243 | -0.00589 | 1.6 | 0.000198 | 0 | 1.6 | 0.000243 | -0.00589 | CFL | None | 1600 | 0.198 | 1600 | 0.198 | 1 | 1.23 | -0.00368
CFLNonePGEHtlExCZ04 | Com-Iltg-dWatt-CFL_OSnone | PGE | Htl | Ex | CZ04 | 1.6 | 0.000198 | 0 | 1.64 | 0.000245 | -0.00494 | 1.6 | 0.000198 | 0 | 1.64 | 0.000245 | -0.00494 | CFL | None | 1600 | 0.198 | 1600 | 0.198 | 1.03 | 1.24 | -0.00309
CFLNoneSCGHtlExCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCG | Htl | Ex | CZ05 | 1.6 | 0.000198 | 0 | 1.61 | 0.000248 | -0.0048 | 1.6 | 0.000198 | 0 | 1.61 | 0.000248 | -0.0048 | CFL | None | 1600 | 0.198 | 1600 | 0.198 | 1.01 | 1.25 | -0.003
CFLNoneSCEHtlExCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | Htl | Ex | CZ05 | 1.6 | 0.000198 | 0 | 1.61 | 0.000248 | -0.0048 | 1.6 | 0.000198 | 0 | 1.61 | 0.000248 | -0.0048 | CFL | None | 1600 | 0.198 | 1600 | 0.198 | 1.01 | 1.25 | -0.003
CFLNonePGEHtlExCZ05 | Com-Iltg-dWatt-CFL_OSnone | PGE | Htl | Ex | CZ05 | 1.6 | 0.000198 | 0 | 1.61 | 0.000248 | -0.0048 | 1.6 | 0.000198 | 0 | 1.61 | 0.000248 | -0.0048 | CFL | None | 1600 | 0.198 | 1600 | 0.198 | 1.01 | 1.25 | -0.003
CFLNoneSDGHtlExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SDG | Htl | Ex | CZ06 | 1.6 | 0.000198 | 0 | 1.74 | 0.000248 | -0.00325 | 1.6 | 0.000198 | 0 | 1.74 | 0.000248 | -0.00325 | CFL | None | 1600 | 0.198 | 1600 | 0.198 | 1.09 | 1.25 | -0.00203
CFLNoneSCGHtlExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCG | Htl | Ex | CZ06 | 1.6 | 0.000198 | 0 | 1.74 | 0.000248 | -0.00325 | 1.6 | 0.000198 | 0 | 1.74 | 0.000248 | -0.00325 | CFL | None | 1600 | 0.198 | 1600 | 0.198 | 1.09 | 1.25 | -0.00203
CFLNoneSCEHtlExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | Htl | Ex | CZ06 | 1.6 | 0.000198 | 0 | 1.74 | 0.000248 | -0.00325 | 1.6 | 0.000198 | 0 | 1.74 | 0.000248 | -0.00325 | CFL | None | 1600 | 0.198 | 1600 | 0.198 | 1.09 | 1.25 | -0.00203
CFLNoneSDGHtlExCZ07 | Com-Iltg-dWatt-CFL_OSnone | SDG | Htl | Ex | CZ07 | 1.6 | 0.000198 | 0 | 1.77 | 0.000246 | -0.00253 | 1.6 | 0.000198 | 0 | 1.77 | 0.000246 | -0.00253 | CFL | None | 1600 | 0.198 | 1600 | 0.198 | 1.11 | 1.24 | -0.00158
CFLNoneSCGHtlExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCG | Htl | Ex | CZ08 | 1.6 | 0.000198 | 0 | 1.76 | 0.000249 | -0.00293 | 1.6 | 0.000198 | 0 | 1.76 | 0.000249 | -0.00293 | CFL | None | 1600 | 0.198 | 1600 | 0.198 | 1.1 | 1.26 | -0.00183
CFLNoneSCEHtlExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | Htl | Ex | CZ08 | 1.6 | 0.000198 | 0 | 1.76 | 0.000249 | -0.00293 | 1.6 | 0.000198 | 0 | 1.76 | 0.000249 | -0.00293 | CFL | None | 1600 | 0.198 | 1600 | 0.198 | 1.1 | 1.26 | -0.00183
CFLNoneSDGHtlExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SDG | Htl | Ex | CZ08 | 1.6 | 0.000198 | 0 | 1.76 | 0.000249 | -0.00293 | 1.6 | 0.000198 | 0 | 1.76 | 0.000249 | -0.00293 | CFL | None | 1600 | 0.198 | 1600 | 0.198 | 1.1 | 1.26 | -0.00183
CFLNoneSCEHtlExCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | Htl | Ex | CZ09 | 1.6 | 0.000198 | 0 | 1.78 | 0.000256 | -0.00294 | 1.6 | 0.000198 | 0 | 1.78 | 0.000256 | -0.00294 | CFL | None | 1600 | 0.198 | 1600 | 0.198 | 1.11 | 1.29 | -0.00184
CFLNoneSCGHtlExCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCG | Htl | Ex | CZ09 | 1.6 | 0.000198 | 0 | 1.78 | 0.000256 | -0.00294 | 1.6 | 0.000198 | 0 | 1.78 | 0.000256 | -0.00294 | CFL | None | 1600 | 0.198 | 1600 | 0.198 | 1.11 | 1.29 | -0.00184
CFLNoneSCEHtlExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | Htl | Ex | CZ10 | 1.6 | 0.000198 | 0 | 1.74 | 0.000254 | -0.00339 | 1.6 | 0.000198 | 0 | 1.74 | 0.000254 | -0.00339 | CFL | None | 1600 | 0.198 | 1600 | 0.198 | 1.09 | 1.28 | -0.00212
CFLNoneSDGHtlExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SDG | Htl | Ex | CZ10 | 1.6 | 0.000198 | 0 | 1.74 | 0.000254 | -0.00339 | 1.6 | 0.000198 | 0 | 1.74 | 0.000254 | -0.00339 | CFL | None | 1600 | 0.198 | 1600 | 0.198 | 1.09 | 1.28 | -0.00212
CFLNoneSCGHtlExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCG | Htl | Ex | CZ10 | 1.6 | 0.000198 | 0 | 1.74 | 0.000254 | -0.00339 | 1.6 | 0.000198 | 0 | 1.74 | 0.000254 | -0.00339 | CFL | None | 1600 | 0.198 | 1600 | 0.198 | 1.09 | 1.28 | -0.00212
CFLNonePGEHtlExCZ11 | Com-Iltg-dWatt-CFL_OSnone | PGE | Htl | Ex | CZ11 | 1.6 | 0.000198 | 0 | 1.65 | 0.00025 | -0.00534 | 1.6 | 0.000198 | 0 | 1.65 | 0.00025 | -0.00534 | CFL | None | 1600 | 0.198 | 1600 | 0.198 | 1.03 | 1.26 | -0.00334
CFLNonePGEHtlExCZ12 | Com-Iltg-dWatt-CFL_OSnone | PGE | Htl | Ex | CZ12 | 1.6 | 0.000198 | 0 | 1.63 | 0.000249 | -0.00544 | 1.6 | 0.000198 | 0 | 1.63 | 0.000249 | -0.00544 | CFL | None | 1600 | 0.198 | 1600 | 0.198 | 1.02 | 1.26 | -0.0034
CFLNonePGEHtlExCZ13 | Com-Iltg-dWatt-CFL_OSnone | PGE | Htl | Ex | CZ13 | 1.6 | 0.000198 | 0 | 1.69 | 0.000254 | -0.00418 | 1.6 | 0.000198 | 0 | 1.69 | 0.000254 | -0.00418 | CFL | None | 1600 | 0.198 | 1600 | 0.198 | 1.06 | 1.28 | -0.00261
CFLNoneSCGHtlExCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCG | Htl | Ex | CZ13 | 1.6 | 0.000198 | 0 | 1.69 | 0.000254 | -0.00418 | 1.6 | 0.000198 | 0 | 1.69 | 0.000254 | -0.00418 | CFL | None | 1600 | 0.198 | 1600 | 0.198 | 1.06 | 1.28 | -0.00261
CFLNoneSCEHtlExCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | Htl | Ex | CZ13 | 1.6 | 0.000198 | 0 | 1.69 | 0.000254 | -0.00418 | 1.6 | 0.000198 | 0 | 1.69 | 0.000254 | -0.00418 | CFL | None | 1600 | 0.198 | 1600 | 0.198 | 1.06 | 1.28 | -0.00261
CFLNoneSDGHtlExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SDG | Htl | Ex | CZ14 | 1.6 | 0.000198 | 0 | 1.66 | 0.000253 | -0.00462 | 1.6 | 0.000198 | 0 | 1.66 | 0.000253 | -0.00462 | CFL | None | 1600 | 0.198 | 1600 | 0.198 | 1.04 | 1.28 | -0.00289
CFLNoneSCEHtlExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | Htl | Ex | CZ14 | 1.6 | 0.000198 | 0 | 1.66 | 0.000253 | -0.00462 | 1.6 | 0.000198 | 0 | 1.66 | 0.000253 | -0.00462 | CFL | None | 1600 | 0.198 | 1600 | 0.198 | 1.04 | 1.28 | -0.00289
CFLNoneSCGHtlExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCG | Htl | Ex | CZ14 | 1.6 | 0.000198 | 0 | 1.66 | 0.000253 | -0.00462 | 1.6 | 0.000198 | 0 | 1.66 | 0.000253 | -0.00462 | CFL | None | 1600 | 0.198 | 1600 | 0.198 | 1.04 | 1.28 | -0.00289
CFLNoneSCGHtlExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCG | Htl | Ex | CZ15 | 1.6 | 0.000198 | 0 | 1.86 | 0.000255 | -0.00195 | 1.6 | 0.000198 | 0 | 1.86 | 0.000255 | -0.00195 | CFL | None | 1600 | 0.198 | 1600 | 0.198 | 1.16 | 1.29 | -0.00122
CFLNoneSCEHtlExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | Htl | Ex | CZ15 | 1.6 | 0.000198 | 0 | 1.86 | 0.000255 | -0.00195 | 1.6 | 0.000198 | 0 | 1.86 | 0.000255 | -0.00195 | CFL | None | 1600 | 0.198 | 1600 | 0.198 | 1.16 | 1.29 | -0.00122
CFLNoneSDGHtlExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SDG | Htl | Ex | CZ15 | 1.6 | 0.000198 | 0 | 1.86 | 0.000255 | -0.00195 | 1.6 | 0.000198 | 0 | 1.86 | 0.000255 | -0.00195 | CFL | None | 1600 | 0.198 | 1600 | 0.198 | 1.16 | 1.29 | -0.00122
CFLNoneSCGHtlExCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCG | Htl | Ex | CZ16 | 1.6 | 0.000198 | 0 | 1.47 | 0.000249 | -0.00686 | 1.6 | 0.000198 | 0 | 1.47 | 0.000249 | -0.00686 | CFL | None | 1600 | 0.198 | 1600 | 0.198 | 0.919 | 1.26 | -0.00429
CFLNonePGEHtlExCZ16 | Com-Iltg-dWatt-CFL_OSnone | PGE | Htl | Ex | CZ16 | 1.6 | 0.000198 | 0 | 1.47 | 0.000249 | -0.00686 | 1.6 | 0.000198 | 0 | 1.47 | 0.000249 | -0.00686 | CFL | None | 1600 | 0.198 | 1600 | 0.198 | 0.919 | 1.26 | -0.00429
CFLNoneSCEHtlExCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | Htl | Ex | CZ16 | 1.6 | 0.000198 | 0 | 1.47 | 0.000249 | -0.00686 | 1.6 | 0.000198 | 0 | 1.47 | 0.000249 | -0.00686 | CFL | None | 1600 | 0.198 | 1600 | 0.198 | 0.919 | 1.26 | -0.00429
CFLNoneSCGHtlExIOU | Com-Iltg-dWatt-CFL_OSnone | SCG | Htl | Ex | IOU | 1.6 | 0.000198 | 0 | 1.76 | 0.000252 | -0.00309 | 1.6 | 0.000198 | 0 | 1.76 | 0.000252 | -0.00309 | CFL | None | 1600 | 0.198 | 1600 | 0.198 | 1.1 | 1.27 | -0.00193
CFLNoneSCEHtlExIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | Htl | Ex | IOU | 1.6 | 0.000198 | 0 | 1.75 | 0.000251 | -0.00314 | 1.6 | 0.000198 | 0 | 1.75 | 0.000251 | -0.00314 | CFL | None | 1600 | 0.198 | 1600 | 0.198 | 1.09 | 1.27 | -0.00196
CFLNonePGEHtlExIOU | Com-Iltg-dWatt-CFL_OSnone | PGE | Htl | Ex | IOU | 1.6 | 0.000198 | 0 | 1.61 | 0.000246 | -0.00553 | 1.6 | 0.000198 | 0 | 1.61 | 0.000246 | -0.00553 | CFL | None | 1600 | 0.198 | 1600 | 0.198 | 1.01 | 1.24 | -0.00346
CFLNoneSDGHtlExIOU | Com-Iltg-dWatt-CFL_OSnone | SDG | Htl | Ex | IOU | 1.6 | 0.000198 | 0 | 1.77 | 0.000247 | -0.00266 | 1.6 | 0.000198 | 0 | 1.77 | 0.000247 | -0.00266 | CFL | None | 1600 | 0.198 | 1600 | 0.198 | 1.11 | 1.25 | -0.00166
CFLNonePGEHtlNewCZ01 | Com-Iltg-dWatt-CFL_OSnone | PGE | Htl | New | CZ01 | 1.6 | 0.000198 | 0 | 1.41 | 0.000236 | -0.0093 | 1.6 | 0.000198 | 0 | 1.41 | 0.000236 | -0.0093 | CFL | None | 1600 | 0.198 | 1600 | 0.198 | 0.881 | 1.19 | -0.00581
CFLNonePGEHtlNewCZ02 | Com-Iltg-dWatt-CFL_OSnone | PGE | Htl | New | CZ02 | 1.6 | 0.000198 | 0 | 1.56 | 0.000251 | -0.00726 | 1.6 | 0.000198 | 0 | 1.56 | 0.000251 | -0.00726 | CFL | None | 1600 | 0.198 | 1600 | 0.198 | 0.975 | 1.27 | -0.00454
CFLNonePGEHtlNewCZ03 | Com-Iltg-dWatt-CFL_OSnone | PGE | Htl | New | CZ03 | 1.6 | 0.000198 | 0 | 1.56 | 0.000244 | -0.00664 | 1.6 | 0.000198 | 0 | 1.56 | 0.000244 | -0.00664 | CFL | None | 1600 | 0.198 | 1600 | 0.198 | 0.975 | 1.23 | -0.00415
CFLNonePGEHtlNewCZ04 | Com-Iltg-dWatt-CFL_OSnone | PGE | Htl | New | CZ04 | 1.6 | 0.000198 | 0 | 1.62 | 0.000251 | -0.00573 | 1.6 | 0.000198 | 0 | 1.62 | 0.000251 | -0.00573 | CFL | None | 1600 | 0.198 | 1600 | 0.198 | 1.01 | 1.27 | -0.00358
CFLNonePGEHtlNewCZ05 | Com-Iltg-dWatt-CFL_OSnone | PGE | Htl | New | CZ05 | 1.6 | 0.000198 | 0 | 1.55 | 0.000241 | -0.00706 | 1.6 | 0.000198 | 0 | 1.55 | 0.000241 | -0.00706 | CFL | None | 1600 | 0.198 | 1600 | 0.198 | 0.969 | 1.22 | -0.00441
CFLNoneSCEHtlNewCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | Htl | New | CZ05 | 1.6 | 0.000198 | 0 | 1.54 | 0.000251 | -0.00504 | 1.6 | 0.000198 | 0 | 1.54 | 0.000251 | -0.00504 | CFL | None | 1600 | 0.198 | 1600 | 0.198 | 0.963 | 1.27 | -0.00315
CFLNoneSCEHtlNewCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | Htl | New | CZ06 | 1.6 | 0.000198 | 0 | 1.73 | 0.000254 | -0.00277 | 1.6 | 0.000198 | 0 | 1.73 | 0.000254 | -0.00277 | CFL | None | 1600 | 0.198 | 1600 | 0.198 | 1.08 | 1.28 | -0.00173
CFLNoneSDGHtlNewCZ06 | Com-Iltg-dWatt-CFL_OSnone | SDG | Htl | New | CZ06 | 1.6 | 0.000198 | 0 | 1.73 | 0.000253 | -0.00302 | 1.6 | 0.000198 | 0 | 1.73 | 0.000253 | -0.00302 | CFL | None | 1600 | 0.198 | 1600 | 0.198 | 1.08 | 1.28 | -0.00189
CFLNoneSDGHtlNewCZ07 | Com-Iltg-dWatt-CFL_OSnone | SDG | Htl | New | CZ07 | 1.6 | 0.000198 | 0 | 1.76 | 0.000248 | -0.00218 | 1.6 | 0.000198 | 0 | 1.76 | 0.000248 | -0.00218 | CFL | None | 1600 | 0.198 | 1600 | 0.198 | 1.1 | 1.25 | -0.00136
CFLNoneSCEHtlNewCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | Htl | New | CZ08 | 1.6 | 0.000198 | 0 | 1.76 | 0.000256 | -0.00243 | 1.6 | 0.000198 | 0 | 1.76 | 0.000256 | -0.00243 | CFL | None | 1600 | 0.198 | 1600 | 0.198 | 1.1 | 1.29 | -0.00152
CFLNoneSDGHtlNewCZ08 | Com-Iltg-dWatt-CFL_OSnone | SDG | Htl | New | CZ08 | 1.6 | 0.000198 | 0 | 1.76 | 0.000254 | -0.00266 | 1.6 | 0.000198 | 0 | 1.76 | 0.000254 | -0.00266 | CFL | None | 1600 | 0.198 | 1600 | 0.198 | 1.1 | 1.28 | -0.00166
CFLNoneSCEHtlNewCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | Htl | New | CZ09 | 1.6 | 0.000198 | 0 | 1.75 | 0.000262 | -0.00277 | 1.6 | 0.000198 | 0 | 1.75 | 0.000262 | -0.00277 | CFL | None | 1600 | 0.198 | 1600 | 0.198 | 1.09 | 1.32 | -0.00173
CFLNoneSCEHtlNewCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | Htl | New | CZ10 | 1.6 | 0.000198 | 0 | 1.73 | 0.00027 | -0.00307 | 1.6 | 0.000198 | 0 | 1.73 | 0.00027 | -0.00307 | CFL | None | 1600 | 0.198 | 1600 | 0.198 | 1.08 | 1.36 | -0.00192
CFLNoneSDGHtlNewCZ10 | Com-Iltg-dWatt-CFL_OSnone | SDG | Htl | New | CZ10 | 1.6 | 0.000198 | 0 | 1.73 | 0.000267 | -0.00333 | 1.6 | 0.000198 | 0 | 1.73 | 0.000267 | -0.00333 | CFL | None | 1600 | 0.198 | 1600 | 0.198 | 1.08 | 1.35 | -0.00208
CFLNonePGEHtlNewCZ11 | Com-Iltg-dWatt-CFL_OSnone | PGE | Htl | New | CZ11 | 1.6 | 0.000198 | 0 | 1.63 | 0.000253 | -0.0063 | 1.6 | 0.000198 | 0 | 1.63 | 0.000253 | -0.0063 | CFL | None | 1600 | 0.198 | 1600 | 0.198 | 1.02 | 1.28 | -0.00394
CFLNonePGEHtlNewCZ12 | Com-Iltg-dWatt-CFL_OSnone | PGE | Htl | New | CZ12 | 1.6 | 0.000198 | 0 | 1.61 | 0.000252 | -0.00637 | 1.6 | 0.000198 | 0 | 1.61 | 0.000252 | -0.00637 | CFL | None | 1600 | 0.198 | 1600 | 0.198 | 1.01 | 1.27 | -0.00398
CFLNoneSCEHtlNewCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | Htl | New | CZ13 | 1.6 | 0.000198 | 0 | 1.66 | 0.000262 | -0.00421 | 1.6 | 0.000198 | 0 | 1.66 | 0.000262 | -0.00421 | CFL | None | 1600 | 0.198 | 1600 | 0.198 | 1.04 | 1.32 | -0.00263
CFLNonePGEHtlNewCZ13 | Com-Iltg-dWatt-CFL_OSnone | PGE | Htl | New | CZ13 | 1.6 | 0.000198 | 0 | 1.65 | 0.00025 | -0.00578 | 1.6 | 0.000198 | 0 | 1.65 | 0.00025 | -0.00578 | CFL | None | 1600 | 0.198 | 1600 | 0.198 | 1.03 | 1.26 | -0.00361
CFLNoneSDGHtlNewCZ14 | Com-Iltg-dWatt-CFL_OSnone | SDG | Htl | New | CZ14 | 1.6 | 0.000198 | 0 | 1.64 | 0.000262 | -0.00499 | 1.6 | 0.000198 | 0 | 1.64 | 0.000262 | -0.00499 | CFL | None | 1600 | 0.198 | 1600 | 0.198 | 1.03 | 1.32 | -0.00312
CFLNoneSCEHtlNewCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | Htl | New | CZ14 | 1.6 | 0.000198 | 0 | 1.63 | 0.000264 | -0.00462 | 1.6 | 0.000198 | 0 | 1.63 | 0.000264 | -0.00462 | CFL | None | 1600 | 0.198 | 1600 | 0.198 | 1.02 | 1.33 | -0.00289
CFLNoneSDGHtlNewCZ15 | Com-Iltg-dWatt-CFL_OSnone | SDG | Htl | New | CZ15 | 1.6 | 0.000198 | 0 | 1.87 | 0.000266 | -0.00168 | 1.6 | 0.000198 | 0 | 1.87 | 0.000266 | -0.00168 | CFL | None | 1600 | 0.198 | 1600 | 0.198 | 1.17 | 1.34 | -0.00105
CFLNoneSCEHtlNewCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | Htl | New | CZ15 | 1.6 | 0.000198 | 0 | 1.88 | 0.000268 | -0.00153 | 1.6 | 0.000198 | 0 | 1.88 | 0.000268 | -0.00153 | CFL | None | 1600 | 0.198 | 1600 | 0.198 | 1.18 | 1.35 | -0.000956
CFLNoneSCEHtlNewCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | Htl | New | CZ16 | 1.6 | 0.000198 | 0 | 1.41 | 0.000253 | -0.00784 | 1.6 | 0.000198 | 0 | 1.41 | 0.000253 | -0.00784 | CFL | None | 1600 | 0.198 | 1600 | 0.198 | 0.881 | 1.28 | -0.0049
CFLNonePGEHtlNewCZ16 | Com-Iltg-dWatt-CFL_OSnone | PGE | Htl | New | CZ16 | 1.6 | 0.000198 | 0 | 1.44 | 0.000244 | -0.0105 | 1.6 | 0.000198 | 0 | 1.44 | 0.000244 | -0.0105 | CFL | None | 1600 | 0.198 | 1600 | 0.198 | 0.9 | 1.23 | -0.00656
CFLNoneSCGHtlNewIOU | Com-Iltg-dWatt-CFL_OSnone | SCG | Htl | New | IOU | 1.6 | 0.000198 | 0 | 1.77 | 0.000259 | -0.00268 | 1.6 | 0.000198 | 0 | 1.77 | 0.000259 | -0.00268 | CFL | None | 1600 | 0.198 | 1600 | 0.198 | 1.11 | 1.31 | -0.00168
CFLNoneSDGHtlNewIOU | Com-Iltg-dWatt-CFL_OSnone | SDG | Htl | New | IOU | 1.6 | 0.000198 | 0 | 1.76 | 0.00025 | -0.00235 | 1.6 | 0.000198 | 0 | 1.76 | 0.00025 | -0.00235 | CFL | None | 1600 | 0.198 | 1600 | 0.198 | 1.1 | 1.26 | -0.00147
CFLNoneSCEHtlNewIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | Htl | New | IOU | 1.6 | 0.000198 | 0 | 1.78 | 0.00026 | -0.00266 | 1.6 | 0.000198 | 0 | 1.78 | 0.00026 | -0.00266 | CFL | None | 1600 | 0.198 | 1600 | 0.198 | 1.11 | 1.31 | -0.00166
CFLNonePGEHtlNewIOU | Com-Iltg-dWatt-CFL_OSnone | PGE | Htl | New | IOU | 1.6 | 0.000198 | 0 | 1.59 | 0.000257 | -0.00488 | 1.6 | 0.000198 | 0 | 1.59 | 0.000257 | -0.00488 | CFL | None | 1600 | 0.198 | 1600 | 0.198 | 0.994 | 1.3 | -0.00305
CFLNonePGEMBTExCZ01 | Com-Iltg-dWatt-CFL_OSnone | PGE | MBT | Ex | CZ01 | 2.03 | 0.000536 | 0 | 2.19 | 0.000632 | -0.00233 | 2.03 | 0.000536 | 0 | 2.19 | 0.000632 | -0.00233 | CFL | None | 2030 | 0.536 | 2030 | 0.536 | 1.08 | 1.18 | -0.00115
CFLNonePGEMBTExCZ02 | Com-Iltg-dWatt-CFL_OSnone | PGE | MBT | Ex | CZ02 | 2.03 | 0.000536 | 0 | 2.25 | 0.000632 | -0.00117 | 2.03 | 0.000536 | 0 | 2.25 | 0.000632 | -0.00117 | CFL | None | 2030 | 0.536 | 2030 | 0.536 | 1.11 | 1.18 | -0.000576
CFLNonePGEMBTExCZ03 | Com-Iltg-dWatt-CFL_OSnone | PGE | MBT | Ex | CZ03 | 2.03 | 0.000536 | 0 | 2.27 | 0.000634 | -0.00103 | 2.03 | 0.000536 | 0 | 2.27 | 0.000634 | -0.00103 | CFL | None | 2030 | 0.536 | 2030 | 0.536 | 1.12 | 1.18 | -0.000507
CFLNonePGEMBTExCZ04 | Com-Iltg-dWatt-CFL_OSnone | PGE | MBT | Ex | CZ04 | 2.03 | 0.000536 | 0 | 2.27 | 0.000642 | -0.000792 | 2.03 | 0.000536 | 0 | 2.27 | 0.000642 | -0.000792 | CFL | None | 2030 | 0.536 | 2030 | 0.536 | 1.12 | 1.2 | -0.00039
CFLNoneSCEMBTExCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | MBT | Ex | CZ05 | 2.03 | 0.000536 | 0 | 2.33 | 0.000667 | -0.000859 | 2.03 | 0.000536 | 0 | 2.33 | 0.000667 | -0.000859 | CFL | None | 2030 | 0.536 | 2030 | 0.536 | 1.15 | 1.24 | -0.000423
CFLNonePGEMBTExCZ05 | Com-Iltg-dWatt-CFL_OSnone | PGE | MBT | Ex | CZ05 | 2.03 | 0.000536 | 0 | 2.33 | 0.000667 | -0.000859 | 2.03 | 0.000536 | 0 | 2.33 | 0.000667 | -0.000859 | CFL | None | 2030 | 0.536 | 2030 | 0.536 | 1.15 | 1.24 | -0.000423
CFLNoneSCGMBTExCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCG | MBT | Ex | CZ05 | 2.03 | 0.000536 | 0 | 2.33 | 0.000667 | -0.000859 | 2.03 | 0.000536 | 0 | 2.33 | 0.000667 | -0.000859 | CFL | None | 2030 | 0.536 | 2030 | 0.536 | 1.15 | 1.24 | -0.000423
CFLNoneSCEMBTExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | MBT | Ex | CZ06 | 2.03 | 0.000536 | 0 | 2.35 | 0.000644 | -0.000376 | 2.03 | 0.000536 | 0 | 2.35 | 0.000644 | -0.000376 | CFL | None | 2030 | 0.536 | 2030 | 0.536 | 1.16 | 1.2 | -0.000185
CFLNoneSCGMBTExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCG | MBT | Ex | CZ06 | 2.03 | 0.000536 | 0 | 2.35 | 0.000644 | -0.000376 | 2.03 | 0.000536 | 0 | 2.35 | 0.000644 | -0.000376 | CFL | None | 2030 | 0.536 | 2030 | 0.536 | 1.16 | 1.2 | -0.000185
CFLNoneSDGMBTExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SDG | MBT | Ex | CZ06 | 2.03 | 0.000536 | 0 | 2.35 | 0.000644 | -0.000376 | 2.03 | 0.000536 | 0 | 2.35 | 0.000644 | -0.000376 | CFL | None | 2030 | 0.536 | 2030 | 0.536 | 1.16 | 1.2 | -0.000185
CFLNoneSDGMBTExCZ07 | Com-Iltg-dWatt-CFL_OSnone | SDG | MBT | Ex | CZ07 | 2.03 | 0.000536 | 0 | 2.36 | 0.000637 | -0.000102 | 2.03 | 0.000536 | 0 | 2.36 | 0.000637 | -0.000102 | CFL | None | 2030 | 0.536 | 2030 | 0.536 | 1.16 | 1.19 | -5.02e-05
CFLNoneSCGMBTExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCG | MBT | Ex | CZ08 | 2.03 | 0.000536 | 0 | 2.36 | 0.000673 | -0.000244 | 2.03 | 0.000536 | 0 | 2.36 | 0.000673 | -0.000244 | CFL | None | 2030 | 0.536 | 2030 | 0.536 | 1.16 | 1.26 | -0.00012
CFLNoneSDGMBTExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SDG | MBT | Ex | CZ08 | 2.03 | 0.000536 | 0 | 2.36 | 0.000673 | -0.000244 | 2.03 | 0.000536 | 0 | 2.36 | 0.000673 | -0.000244 | CFL | None | 2030 | 0.536 | 2030 | 0.536 | 1.16 | 1.26 | -0.00012
CFLNoneSCEMBTExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | MBT | Ex | CZ08 | 2.03 | 0.000536 | 0 | 2.36 | 0.000673 | -0.000244 | 2.03 | 0.000536 | 0 | 2.36 | 0.000673 | -0.000244 | CFL | None | 2030 | 0.536 | 2030 | 0.536 | 1.16 | 1.26 | -0.00012
CFLNoneSCGMBTExCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCG | MBT | Ex | CZ09 | 2.03 | 0.000536 | 0 | 2.39 | 0.000676 | -0.00057 | 2.03 | 0.000536 | 0 | 2.39 | 0.000676 | -0.00057 | CFL | None | 2030 | 0.536 | 2030 | 0.536 | 1.18 | 1.26 | -0.000281
CFLNoneSCEMBTExCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | MBT | Ex | CZ09 | 2.03 | 0.000536 | 0 | 2.39 | 0.000676 | -0.00057 | 2.03 | 0.000536 | 0 | 2.39 | 0.000676 | -0.00057 | CFL | None | 2030 | 0.536 | 2030 | 0.536 | 1.18 | 1.26 | -0.000281
CFLNoneSCGMBTExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCG | MBT | Ex | CZ10 | 2.03 | 0.000536 | 0 | 2.35 | 0.000687 | -0.000658 | 2.03 | 0.000536 | 0 | 2.35 | 0.000687 | -0.000658 | CFL | None | 2030 | 0.536 | 2030 | 0.536 | 1.16 | 1.28 | -0.000324
CFLNoneSDGMBTExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SDG | MBT | Ex | CZ10 | 2.03 | 0.000536 | 0 | 2.35 | 0.000687 | -0.000658 | 2.03 | 0.000536 | 0 | 2.35 | 0.000687 | -0.000658 | CFL | None | 2030 | 0.536 | 2030 | 0.536 | 1.16 | 1.28 | -0.000324
CFLNoneSCEMBTExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | MBT | Ex | CZ10 | 2.03 | 0.000536 | 0 | 2.35 | 0.000687 | -0.000658 | 2.03 | 0.000536 | 0 | 2.35 | 0.000687 | -0.000658 | CFL | None | 2030 | 0.536 | 2030 | 0.536 | 1.16 | 1.28 | -0.000324
CFLNonePGEMBTExCZ11 | Com-Iltg-dWatt-CFL_OSnone | PGE | MBT | Ex | CZ11 | 2.03 | 0.000536 | 0 | 2.27 | 0.000645 | -0.00126 | 2.03 | 0.000536 | 0 | 2.27 | 0.000645 | -0.00126 | CFL | None | 2030 | 0.536 | 2030 | 0.536 | 1.12 | 1.2 | -0.000621
CFLNonePGEMBTExCZ12 | Com-Iltg-dWatt-CFL_OSnone | PGE | MBT | Ex | CZ12 | 2.03 | 0.000536 | 0 | 2.26 | 0.000628 | -0.00124 | 2.03 | 0.000536 | 0 | 2.26 | 0.000628 | -0.00124 | CFL | None | 2030 | 0.536 | 2030 | 0.536 | 1.11 | 1.17 | -0.000611
CFLNoneSCGMBTExCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCG | MBT | Ex | CZ13 | 2.03 | 0.000536 | 0 | 2.31 | 0.000654 | -0.00133 | 2.03 | 0.000536 | 0 | 2.31 | 0.000654 | -0.00133 | CFL | None | 2030 | 0.536 | 2030 | 0.536 | 1.14 | 1.22 | -0.000655
CFLNoneSCEMBTExCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | MBT | Ex | CZ13 | 2.03 | 0.000536 | 0 | 2.31 | 0.000654 | -0.00133 | 2.03 | 0.000536 | 0 | 2.31 | 0.000654 | -0.00133 | CFL | None | 2030 | 0.536 | 2030 | 0.536 | 1.14 | 1.22 | -0.000655
CFLNonePGEMBTExCZ13 | Com-Iltg-dWatt-CFL_OSnone | PGE | MBT | Ex | CZ13 | 2.03 | 0.000536 | 0 | 2.31 | 0.000654 | -0.00133 | 2.03 | 0.000536 | 0 | 2.31 | 0.000654 | -0.00133 | CFL | None | 2030 | 0.536 | 2030 | 0.536 | 1.14 | 1.22 | -0.000655
CFLNoneSCEMBTExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | MBT | Ex | CZ14 | 2.03 | 0.000536 | 0 | 2.31 | 0.000681 | -0.00157 | 2.03 | 0.000536 | 0 | 2.31 | 0.000681 | -0.00157 | CFL | None | 2030 | 0.536 | 2030 | 0.536 | 1.14 | 1.27 | -0.000773
CFLNoneSDGMBTExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SDG | MBT | Ex | CZ14 | 2.03 | 0.000536 | 0 | 2.31 | 0.000681 | -0.00157 | 2.03 | 0.000536 | 0 | 2.31 | 0.000681 | -0.00157 | CFL | None | 2030 | 0.536 | 2030 | 0.536 | 1.14 | 1.27 | -0.000773
CFLNoneSCGMBTExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCG | MBT | Ex | CZ14 | 2.03 | 0.000536 | 0 | 2.31 | 0.000681 | -0.00157 | 2.03 | 0.000536 | 0 | 2.31 | 0.000681 | -0.00157 | CFL | None | 2030 | 0.536 | 2030 | 0.536 | 1.14 | 1.27 | -0.000773
CFLNoneSDGMBTExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SDG | MBT | Ex | CZ15 | 2.03 | 0.000536 | 0 | 2.44 | 0.000688 | 0 | 2.03 | 0.000536 | 0 | 2.44 | 0.000688 | 0 | CFL | None | 2030 | 0.536 | 2030 | 0.536 | 1.2 | 1.28 | 0
CFLNoneSCEMBTExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | MBT | Ex | CZ15 | 2.03 | 0.000536 | 0 | 2.44 | 0.000688 | 0 | 2.03 | 0.000536 | 0 | 2.44 | 0.000688 | 0 | CFL | None | 2030 | 0.536 | 2030 | 0.536 | 1.2 | 1.28 | 0
CFLNoneSCGMBTExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCG | MBT | Ex | CZ15 | 2.03 | 0.000536 | 0 | 2.44 | 0.000688 | 0 | 2.03 | 0.000536 | 0 | 2.44 | 0.000688 | 0 | CFL | None | 2030 | 0.536 | 2030 | 0.536 | 1.2 | 1.28 | 0
CFLNoneSCEMBTExCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | MBT | Ex | CZ16 | 2.03 | 0.000536 | 0 | 2.17 | 0.000638 | -0.00538 | 2.03 | 0.000536 | 0 | 2.17 | 0.000638 | -0.00538 | CFL | None | 2030 | 0.536 | 2030 | 0.536 | 1.07 | 1.19 | -0.00265
CFLNonePGEMBTExCZ16 | Com-Iltg-dWatt-CFL_OSnone | PGE | MBT | Ex | CZ16 | 2.03 | 0.000536 | 0 | 2.17 | 0.000638 | -0.00538 | 2.03 | 0.000536 | 0 | 2.17 | 0.000638 | -0.00538 | CFL | None | 2030 | 0.536 | 2030 | 0.536 | 1.07 | 1.19 | -0.00265
CFLNoneSCGMBTExCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCG | MBT | Ex | CZ16 | 2.03 | 0.000536 | 0 | 2.17 | 0.000638 | -0.00538 | 2.03 | 0.000536 | 0 | 2.17 | 0.000638 | -0.00538 | CFL | None | 2030 | 0.536 | 2030 | 0.536 | 1.07 | 1.19 | -0.00265
CFLNoneSCEMBTExIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | MBT | Ex | IOU | 2.03 | 0.000536 | 0 | 2.36 | 0.000669 | -0.000566 | 2.03 | 0.000536 | 0 | 2.36 | 0.000669 | -0.000566 | CFL | None | 2030 | 0.536 | 2030 | 0.536 | 1.16 | 1.25 | -0.000279
CFLNoneSDGMBTExIOU | Com-Iltg-dWatt-CFL_OSnone | SDG | MBT | Ex | IOU | 2.03 | 0.000536 | 0 | 2.36 | 0.000654 | -0.000296 | 2.03 | 0.000536 | 0 | 2.36 | 0.000654 | -0.000296 | CFL | None | 2030 | 0.536 | 2030 | 0.536 | 1.16 | 1.22 | -0.000146
CFLNoneSCGMBTExIOU | Com-Iltg-dWatt-CFL_OSnone | SCG | MBT | Ex | IOU | 2.03 | 0.000536 | 0 | 2.36 | 0.00067 | -0.000552 | 2.03 | 0.000536 | 0 | 2.36 | 0.00067 | -0.000552 | CFL | None | 2030 | 0.536 | 2030 | 0.536 | 1.16 | 1.25 | -0.000272
CFLNonePGEMBTExIOU | Com-Iltg-dWatt-CFL_OSnone | PGE | MBT | Ex | IOU | 2.03 | 0.000536 | 0 | 2.27 | 0.000638 | -0.00114 | 2.03 | 0.000536 | 0 | 2.27 | 0.000638 | -0.00114 | CFL | None | 2030 | 0.536 | 2030 | 0.536 | 1.12 | 1.19 | -0.000562
CFLNonePGEMBTNewCZ01 | Com-Iltg-dWatt-CFL_OSnone | PGE | MBT | New | CZ01 | 2.03 | 0.000536 | 0 | 2.08 | 0.000607 | -0.00225 | 2.03 | 0.000536 | 0 | 2.08 | 0.000607 | -0.00225 | CFL | None | 2030 | 0.536 | 2030 | 0.536 | 1.02 | 1.13 | -0.00111
CFLNonePGEMBTNewCZ02 | Com-Iltg-dWatt-CFL_OSnone | PGE | MBT | New | CZ02 | 2.03 | 0.000536 | 0 | 2.17 | 0.000658 | -0.00107 | 2.03 | 0.000536 | 0 | 2.17 | 0.000658 | -0.00107 | CFL | None | 2030 | 0.536 | 2030 | 0.536 | 1.07 | 1.23 | -0.000527
CFLNonePGEMBTNewCZ03 | Com-Iltg-dWatt-CFL_OSnone | PGE | MBT | New | CZ03 | 2.03 | 0.000536 | 0 | 2.15 | 0.000638 | -0.00101 | 2.03 | 0.000536 | 0 | 2.15 | 0.000638 | -0.00101 | CFL | None | 2030 | 0.536 | 2030 | 0.536 | 1.06 | 1.19 | -0.000498
CFLNonePGEMBTNewCZ04 | Com-Iltg-dWatt-CFL_OSnone | PGE | MBT | New | CZ04 | 2.03 | 0.000536 | 0 | 2.19 | 0.000652 | -0.000806 | 2.03 | 0.000536 | 0 | 2.19 | 0.000652 | -0.000806 | CFL | None | 2030 | 0.536 | 2030 | 0.536 | 1.08 | 1.22 | -0.000397
CFLNoneSCEMBTNewCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | MBT | New | CZ05 | 2.03 | 0.000536 | 0 | 2.19 | 0.000662 | -0.000696 | 2.03 | 0.000536 | 0 | 2.19 | 0.000662 | -0.000696 | CFL | None | 2030 | 0.536 | 2030 | 0.536 | 1.08 | 1.24 | -0.000343
CFLNonePGEMBTNewCZ05 | Com-Iltg-dWatt-CFL_OSnone | PGE | MBT | New | CZ05 | 2.03 | 0.000536 | 0 | 2.16 | 0.000635 | -0.000538 | 2.03 | 0.000536 | 0 | 2.16 | 0.000635 | -0.000538 | CFL | None | 2030 | 0.536 | 2030 | 0.536 | 1.06 | 1.18 | -0.000265
CFLNoneSCEMBTNewCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | MBT | New | CZ06 | 2.03 | 0.000536 | 0 | 2.27 | 0.000666 | -0.000666 | 2.03 | 0.000536 | 0 | 2.27 | 0.000666 | -0.000666 | CFL | None | 2030 | 0.536 | 2030 | 0.536 | 1.12 | 1.24 | -0.000328
CFLNoneSDGMBTNewCZ06 | Com-Iltg-dWatt-CFL_OSnone | SDG | MBT | New | CZ06 | 2.03 | 0.000536 | 0 | 2.28 | 0.000671 | -0.000688 | 2.03 | 0.000536 | 0 | 2.28 | 0.000671 | -0.000688 | CFL | None | 2030 | 0.536 | 2030 | 0.536 | 1.12 | 1.25 | -0.000339
CFLNoneSDGMBTNewCZ07 | Com-Iltg-dWatt-CFL_OSnone | SDG | MBT | New | CZ07 | 2.03 | 0.000536 | 0 | 2.27 | 0.000665 | 0 | 2.03 | 0.000536 | 0 | 2.27 | 0.000665 | 0 | CFL | None | 2030 | 0.536 | 2030 | 0.536 | 1.12 | 1.24 | 0
CFLNoneSDGMBTNewCZ08 | Com-Iltg-dWatt-CFL_OSnone | SDG | MBT | New | CZ08 | 2.03 | 0.000536 | 0 | 2.29 | 0.000688 | -0.00055 | 2.03 | 0.000536 | 0 | 2.29 | 0.000688 | -0.00055 | CFL | None | 2030 | 0.536 | 2030 | 0.536 | 1.13 | 1.28 | -0.000271
CFLNoneSCEMBTNewCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | MBT | New | CZ08 | 2.03 | 0.000536 | 0 | 2.28 | 0.000683 | -0.000534 | 2.03 | 0.000536 | 0 | 2.28 | 0.000683 | -0.000534 | CFL | None | 2030 | 0.536 | 2030 | 0.536 | 1.12 | 1.27 | -0.000263
CFLNoneSCEMBTNewCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | MBT | New | CZ09 | 2.03 | 0.000536 | 0 | 2.28 | 0.000698 | -0.000627 | 2.03 | 0.000536 | 0 | 2.28 | 0.000698 | -0.000627 | CFL | None | 2030 | 0.536 | 2030 | 0.536 | 1.12 | 1.3 | -0.000309
CFLNoneSCEMBTNewCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | MBT | New | CZ10 | 2.03 | 0.000536 | 0 | 2.29 | 0.000709 | -0.000662 | 2.03 | 0.000536 | 0 | 2.29 | 0.000709 | -0.000662 | CFL | None | 2030 | 0.536 | 2030 | 0.536 | 1.13 | 1.32 | -0.000326
CFLNoneSDGMBTNewCZ10 | Com-Iltg-dWatt-CFL_OSnone | SDG | MBT | New | CZ10 | 2.03 | 0.000536 | 0 | 2.3 | 0.000716 | -0.000682 | 2.03 | 0.000536 | 0 | 2.3 | 0.000716 | -0.000682 | CFL | None | 2030 | 0.536 | 2030 | 0.536 | 1.13 | 1.34 | -0.000336
CFLNonePGEMBTNewCZ11 | Com-Iltg-dWatt-CFL_OSnone | PGE | MBT | New | CZ11 | 2.03 | 0.000536 | 0 | 2.21 | 0.000665 | -0.00111 | 2.03 | 0.000536 | 0 | 2.21 | 0.000665 | -0.00111 | CFL | None | 2030 | 0.536 | 2030 | 0.536 | 1.09 | 1.24 | -0.000547
CFLNonePGEMBTNewCZ12 | Com-Iltg-dWatt-CFL_OSnone | PGE | MBT | New | CZ12 | 2.03 | 0.000536 | 0 | 2.19 | 0.000659 | -0.000966 | 2.03 | 0.000536 | 0 | 2.19 | 0.000659 | -0.000966 | CFL | None | 2030 | 0.536 | 2030 | 0.536 | 1.08 | 1.23 | -0.000476
CFLNoneSCEMBTNewCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | MBT | New | CZ13 | 2.03 | 0.000536 | 0 | 2.26 | 0.00069 | -0.00117 | 2.03 | 0.000536 | 0 | 2.26 | 0.00069 | -0.00117 | CFL | None | 2030 | 0.536 | 2030 | 0.536 | 1.11 | 1.29 | -0.000576
CFLNonePGEMBTNewCZ13 | Com-Iltg-dWatt-CFL_OSnone | PGE | MBT | New | CZ13 | 2.03 | 0.000536 | 0 | 2.21 | 0.000657 | -0.000899 | 2.03 | 0.000536 | 0 | 2.21 | 0.000657 | -0.000899 | CFL | None | 2030 | 0.536 | 2030 | 0.536 | 1.09 | 1.23 | -0.000443
CFLNoneSDGMBTNewCZ14 | Com-Iltg-dWatt-CFL_OSnone | SDG | MBT | New | CZ14 | 2.03 | 0.000536 | 0 | 2.27 | 0.000706 | -0.00133 | 2.03 | 0.000536 | 0 | 2.27 | 0.000706 | -0.00133 | CFL | None | 2030 | 0.536 | 2030 | 0.536 | 1.12 | 1.32 | -0.000655
CFLNoneSCEMBTNewCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | MBT | New | CZ14 | 2.03 | 0.000536 | 0 | 2.26 | 0.0007 | -0.00128 | 2.03 | 0.000536 | 0 | 2.26 | 0.0007 | -0.00128 | CFL | None | 2030 | 0.536 | 2030 | 0.536 | 1.11 | 1.31 | -0.000631
CFLNoneSDGMBTNewCZ15 | Com-Iltg-dWatt-CFL_OSnone | SDG | MBT | New | CZ15 | 2.03 | 0.000536 | 0 | 2.42 | 0.000716 | 0 | 2.03 | 0.000536 | 0 | 2.42 | 0.000716 | 0 | CFL | None | 2030 | 0.536 | 2030 | 0.536 | 1.19 | 1.34 | 0
CFLNoneSCEMBTNewCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | MBT | New | CZ15 | 2.03 | 0.000536 | 0 | 2.4 | 0.00071 | 0 | 2.03 | 0.000536 | 0 | 2.4 | 0.00071 | 0 | CFL | None | 2030 | 0.536 | 2030 | 0.536 | 1.18 | 1.32 | 0
CFLNoneSCEMBTNewCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | MBT | New | CZ16 | 2.03 | 0.000536 | 0 | 2.15 | 0.000662 | -0.00436 | 2.03 | 0.000536 | 0 | 2.15 | 0.000662 | -0.00436 | CFL | None | 2030 | 0.536 | 2030 | 0.536 | 1.06 | 1.24 | -0.00215
CFLNonePGEMBTNewCZ16 | Com-Iltg-dWatt-CFL_OSnone | PGE | MBT | New | CZ16 | 2.03 | 0.000536 | 0 | 2.12 | 0.000636 | -0.00418 | 2.03 | 0.000536 | 0 | 2.12 | 0.000636 | -0.00418 | CFL | None | 2030 | 0.536 | 2030 | 0.536 | 1.04 | 1.19 | -0.00206
CFLNonePGEMBTNewIOU | Com-Iltg-dWatt-CFL_OSnone | PGE | MBT | New | IOU | 2.03 | 0.000536 | 0 | 2.25 | 0.000685 | -0.00133 | 2.03 | 0.000536 | 0 | 2.25 | 0.000685 | -0.00133 | CFL | None | 2030 | 0.536 | 2030 | 0.536 | 1.11 | 1.28 | -0.000655
CFLNoneSDGMBTNewIOU | Com-Iltg-dWatt-CFL_OSnone | SDG | MBT | New | IOU | 2.03 | 0.000536 | 0 | 2.28 | 0.000682 | -0.000253 | 2.03 | 0.000536 | 0 | 2.28 | 0.000682 | -0.000253 | CFL | None | 2030 | 0.536 | 2030 | 0.536 | 1.12 | 1.27 | -0.000125
CFLNoneSCEMBTNewIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | MBT | New | IOU | 2.03 | 0.000536 | 0 | 2.31 | 0.0007 | -0.000598 | 2.03 | 0.000536 | 0 | 2.31 | 0.0007 | -0.000598 | CFL | None | 2030 | 0.536 | 2030 | 0.536 | 1.14 | 1.31 | -0.000295
CFLNoneSCGMBTNewIOU | Com-Iltg-dWatt-CFL_OSnone | SCG | MBT | New | IOU | 2.03 | 0.000536 | 0 | 2.31 | 0.000699 | -0.000597 | 2.03 | 0.000536 | 0 | 2.31 | 0.000699 | -0.000597 | CFL | None | 2030 | 0.536 | 2030 | 0.536 | 1.14 | 1.3 | -0.000294
CFLNonePGEMLIExCZ01 | Com-Iltg-dWatt-CFL_OSnone | PGE | MLI | Ex | CZ01 | 2.26 | 0.000514 | 0 | 2.2 | 0.000585 | -0.026 | 2.26 | 0.000514 | 0 | 2.2 | 0.000585 | -0.026 | CFL | None | 2260 | 0.514 | 2260 | 0.514 | 0.973 | 1.14 | -0.0115
CFLNonePGEMLIExCZ02 | Com-Iltg-dWatt-CFL_OSnone | PGE | MLI | Ex | CZ02 | 2.26 | 0.000514 | 0 | 2.36 | 0.000596 | -0.0129 | 2.26 | 0.000514 | 0 | 2.36 | 0.000596 | -0.0129 | CFL | None | 2260 | 0.514 | 2260 | 0.514 | 1.04 | 1.16 | -0.00571
CFLNonePGEMLIExCZ03 | Com-Iltg-dWatt-CFL_OSnone | PGE | MLI | Ex | CZ03 | 2.26 | 0.000514 | 0 | 2.35 | 0.000596 | -0.0119 | 2.26 | 0.000514 | 0 | 2.35 | 0.000596 | -0.0119 | CFL | None | 2260 | 0.514 | 2260 | 0.514 | 1.04 | 1.16 | -0.00527
CFLNonePGEMLIExCZ04 | Com-Iltg-dWatt-CFL_OSnone | PGE | MLI | Ex | CZ04 | 2.26 | 0.000514 | 0 | 2.38 | 0.000594 | -0.00963 | 2.26 | 0.000514 | 0 | 2.38 | 0.000594 | -0.00963 | CFL | None | 2260 | 0.514 | 2260 | 0.514 | 1.05 | 1.16 | -0.00426
CFLNoneSCEMLIExCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | MLI | Ex | CZ05 | 2.26 | 0.000514 | 0 | 2.38 | 0.000622 | -0.011 | 2.26 | 0.000514 | 0 | 2.38 | 0.000622 | -0.011 | CFL | None | 2260 | 0.514 | 2260 | 0.514 | 1.05 | 1.21 | -0.00487
CFLNoneSCGMLIExCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCG | MLI | Ex | CZ05 | 2.26 | 0.000514 | 0 | 2.38 | 0.000622 | -0.011 | 2.26 | 0.000514 | 0 | 2.38 | 0.000622 | -0.011 | CFL | None | 2260 | 0.514 | 2260 | 0.514 | 1.05 | 1.21 | -0.00487
CFLNonePGEMLIExCZ05 | Com-Iltg-dWatt-CFL_OSnone | PGE | MLI | Ex | CZ05 | 2.26 | 0.000514 | 0 | 2.38 | 0.000622 | -0.011 | 2.26 | 0.000514 | 0 | 2.38 | 0.000622 | -0.011 | CFL | None | 2260 | 0.514 | 2260 | 0.514 | 1.05 | 1.21 | -0.00487
CFLNoneSDGMLIExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SDG | MLI | Ex | CZ06 | 2.26 | 0.000514 | 0 | 2.45 | 0.00061 | -0.00486 | 2.26 | 0.000514 | 0 | 2.45 | 0.00061 | -0.00486 | CFL | None | 2260 | 0.514 | 2260 | 0.514 | 1.08 | 1.19 | -0.00215
CFLNoneSCEMLIExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | MLI | Ex | CZ06 | 2.26 | 0.000514 | 0 | 2.45 | 0.00061 | -0.00486 | 2.26 | 0.000514 | 0 | 2.45 | 0.00061 | -0.00486 | CFL | None | 2260 | 0.514 | 2260 | 0.514 | 1.08 | 1.19 | -0.00215
CFLNoneSCGMLIExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCG | MLI | Ex | CZ06 | 2.26 | 0.000514 | 0 | 2.45 | 0.00061 | -0.00486 | 2.26 | 0.000514 | 0 | 2.45 | 0.00061 | -0.00486 | CFL | None | 2260 | 0.514 | 2260 | 0.514 | 1.08 | 1.19 | -0.00215
CFLNoneSDGMLIExCZ07 | Com-Iltg-dWatt-CFL_OSnone | SDG | MLI | Ex | CZ07 | 2.26 | 0.000514 | 0 | 2.44 | 0.000609 | -0.00251 | 2.26 | 0.000514 | 0 | 2.44 | 0.000609 | -0.00251 | CFL | None | 2260 | 0.514 | 2260 | 0.514 | 1.08 | 1.18 | -0.00111
CFLNoneSDGMLIExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SDG | MLI | Ex | CZ08 | 2.26 | 0.000514 | 0 | 2.47 | 0.000609 | -0.004 | 2.26 | 0.000514 | 0 | 2.47 | 0.000609 | -0.004 | CFL | None | 2260 | 0.514 | 2260 | 0.514 | 1.09 | 1.18 | -0.00177
CFLNoneSCGMLIExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCG | MLI | Ex | CZ08 | 2.26 | 0.000514 | 0 | 2.47 | 0.000609 | -0.004 | 2.26 | 0.000514 | 0 | 2.47 | 0.000609 | -0.004 | CFL | None | 2260 | 0.514 | 2260 | 0.514 | 1.09 | 1.18 | -0.00177
CFLNoneSCEMLIExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | MLI | Ex | CZ08 | 2.26 | 0.000514 | 0 | 2.47 | 0.000609 | -0.004 | 2.26 | 0.000514 | 0 | 2.47 | 0.000609 | -0.004 | CFL | None | 2260 | 0.514 | 2260 | 0.514 | 1.09 | 1.18 | -0.00177
CFLNoneSCEMLIExCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | MLI | Ex | CZ09 | 2.26 | 0.000514 | 0 | 2.51 | 0.000623 | -0.00427 | 2.26 | 0.000514 | 0 | 2.51 | 0.000623 | -0.00427 | CFL | None | 2260 | 0.514 | 2260 | 0.514 | 1.11 | 1.21 | -0.00189
CFLNoneSCGMLIExCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCG | MLI | Ex | CZ09 | 2.26 | 0.000514 | 0 | 2.51 | 0.000623 | -0.00427 | 2.26 | 0.000514 | 0 | 2.51 | 0.000623 | -0.00427 | CFL | None | 2260 | 0.514 | 2260 | 0.514 | 1.11 | 1.21 | -0.00189
CFLNoneSDGMLIExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SDG | MLI | Ex | CZ10 | 2.26 | 0.000514 | 0 | 2.47 | 0.000625 | -0.00545 | 2.26 | 0.000514 | 0 | 2.47 | 0.000625 | -0.00545 | CFL | None | 2260 | 0.514 | 2260 | 0.514 | 1.09 | 1.22 | -0.00241
CFLNoneSCGMLIExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCG | MLI | Ex | CZ10 | 2.26 | 0.000514 | 0 | 2.47 | 0.000625 | -0.00545 | 2.26 | 0.000514 | 0 | 2.47 | 0.000625 | -0.00545 | CFL | None | 2260 | 0.514 | 2260 | 0.514 | 1.09 | 1.22 | -0.00241
CFLNoneSCEMLIExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | MLI | Ex | CZ10 | 2.26 | 0.000514 | 0 | 2.47 | 0.000625 | -0.00545 | 2.26 | 0.000514 | 0 | 2.47 | 0.000625 | -0.00545 | CFL | None | 2260 | 0.514 | 2260 | 0.514 | 1.09 | 1.22 | -0.00241
CFLNonePGEMLIExCZ11 | Com-Iltg-dWatt-CFL_OSnone | PGE | MLI | Ex | CZ11 | 2.26 | 0.000514 | 0 | 2.36 | 0.000595 | -0.0135 | 2.26 | 0.000514 | 0 | 2.36 | 0.000595 | -0.0135 | CFL | None | 2260 | 0.514 | 2260 | 0.514 | 1.04 | 1.16 | -0.00597
CFLNonePGEMLIExCZ12 | Com-Iltg-dWatt-CFL_OSnone | PGE | MLI | Ex | CZ12 | 2.26 | 0.000514 | 0 | 2.36 | 0.000599 | -0.013 | 2.26 | 0.000514 | 0 | 2.36 | 0.000599 | -0.013 | CFL | None | 2260 | 0.514 | 2260 | 0.514 | 1.04 | 1.17 | -0.00575
CFLNoneSCGMLIExCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCG | MLI | Ex | CZ13 | 2.26 | 0.000514 | 0 | 2.42 | 0.000611 | -0.0122 | 2.26 | 0.000514 | 0 | 2.42 | 0.000611 | -0.0122 | CFL | None | 2260 | 0.514 | 2260 | 0.514 | 1.07 | 1.19 | -0.0054
CFLNoneSCEMLIExCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | MLI | Ex | CZ13 | 2.26 | 0.000514 | 0 | 2.42 | 0.000611 | -0.0122 | 2.26 | 0.000514 | 0 | 2.42 | 0.000611 | -0.0122 | CFL | None | 2260 | 0.514 | 2260 | 0.514 | 1.07 | 1.19 | -0.0054
CFLNonePGEMLIExCZ13 | Com-Iltg-dWatt-CFL_OSnone | PGE | MLI | Ex | CZ13 | 2.26 | 0.000514 | 0 | 2.42 | 0.000611 | -0.0122 | 2.26 | 0.000514 | 0 | 2.42 | 0.000611 | -0.0122 | CFL | None | 2260 | 0.514 | 2260 | 0.514 | 1.07 | 1.19 | -0.0054
CFLNoneSCGMLIExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCG | MLI | Ex | CZ14 | 2.26 | 0.000514 | 0 | 2.39 | 0.000617 | -0.0151 | 2.26 | 0.000514 | 0 | 2.39 | 0.000617 | -0.0151 | CFL | None | 2260 | 0.514 | 2260 | 0.514 | 1.06 | 1.2 | -0.00668
CFLNoneSCEMLIExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | MLI | Ex | CZ14 | 2.26 | 0.000514 | 0 | 2.39 | 0.000617 | -0.0151 | 2.26 | 0.000514 | 0 | 2.39 | 0.000617 | -0.0151 | CFL | None | 2260 | 0.514 | 2260 | 0.514 | 1.06 | 1.2 | -0.00668
CFLNoneSDGMLIExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SDG | MLI | Ex | CZ14 | 2.26 | 0.000514 | 0 | 2.39 | 0.000617 | -0.0151 | 2.26 | 0.000514 | 0 | 2.39 | 0.000617 | -0.0151 | CFL | None | 2260 | 0.514 | 2260 | 0.514 | 1.06 | 1.2 | -0.00668
CFLNoneSDGMLIExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SDG | MLI | Ex | CZ15 | 2.26 | 0.000514 | 0 | 2.65 | 0.000616 | -0.00142 | 2.26 | 0.000514 | 0 | 2.65 | 0.000616 | -0.00142 | CFL | None | 2260 | 0.514 | 2260 | 0.514 | 1.17 | 1.2 | -0.000628
CFLNoneSCEMLIExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | MLI | Ex | CZ15 | 2.26 | 0.000514 | 0 | 2.65 | 0.000616 | -0.00142 | 2.26 | 0.000514 | 0 | 2.65 | 0.000616 | -0.00142 | CFL | None | 2260 | 0.514 | 2260 | 0.514 | 1.17 | 1.2 | -0.000628
CFLNoneSCGMLIExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCG | MLI | Ex | CZ15 | 2.26 | 0.000514 | 0 | 2.65 | 0.000616 | -0.00142 | 2.26 | 0.000514 | 0 | 2.65 | 0.000616 | -0.00142 | CFL | None | 2260 | 0.514 | 2260 | 0.514 | 1.17 | 1.2 | -0.000628
CFLNonePGEMLIExCZ16 | Com-Iltg-dWatt-CFL_OSnone | PGE | MLI | Ex | CZ16 | 2.26 | 0.000514 | 0 | 2.23 | 0.000605 | -0.0273 | 2.26 | 0.000514 | 0 | 2.23 | 0.000605 | -0.0273 | CFL | None | 2260 | 0.514 | 2260 | 0.514 | 0.987 | 1.18 | -0.0121
CFLNoneSCGMLIExCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCG | MLI | Ex | CZ16 | 2.26 | 0.000514 | 0 | 2.23 | 0.000605 | -0.0273 | 2.26 | 0.000514 | 0 | 2.23 | 0.000605 | -0.0273 | CFL | None | 2260 | 0.514 | 2260 | 0.514 | 0.987 | 1.18 | -0.0121
CFLNoneSCEMLIExCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | MLI | Ex | CZ16 | 2.26 | 0.000514 | 0 | 2.23 | 0.000605 | -0.0273 | 2.26 | 0.000514 | 0 | 2.23 | 0.000605 | -0.0273 | CFL | None | 2260 | 0.514 | 2260 | 0.514 | 0.987 | 1.18 | -0.0121
CFLNonePGEMLIExIOU | Com-Iltg-dWatt-CFL_OSnone | PGE | MLI | Ex | IOU | 2.26 | 0.000514 | 0 | 2.37 | 0.000599 | -0.0121 | 2.26 | 0.000514 | 0 | 2.37 | 0.000599 | -0.0121 | CFL | None | 2260 | 0.514 | 2260 | 0.514 | 1.05 | 1.17 | -0.00535
CFLNoneSCEMLIExIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | MLI | Ex | IOU | 2.26 | 0.000514 | 0 | 2.47 | 0.000615 | -0.00545 | 2.26 | 0.000514 | 0 | 2.47 | 0.000615 | -0.00545 | CFL | None | 2260 | 0.514 | 2260 | 0.514 | 1.09 | 1.2 | -0.00241
CFLNoneSDGMLIExIOU | Com-Iltg-dWatt-CFL_OSnone | SDG | MLI | Ex | IOU | 2.26 | 0.000514 | 0 | 2.45 | 0.000614 | -0.00362 | 2.26 | 0.000514 | 0 | 2.45 | 0.000614 | -0.00362 | CFL | None | 2260 | 0.514 | 2260 | 0.514 | 1.08 | 1.19 | -0.0016
CFLNoneSCGMLIExIOU | Com-Iltg-dWatt-CFL_OSnone | SCG | MLI | Ex | IOU | 2.26 | 0.000514 | 0 | 2.48 | 0.000615 | -0.00524 | 2.26 | 0.000514 | 0 | 2.48 | 0.000615 | -0.00524 | CFL | None | 2260 | 0.514 | 2260 | 0.514 | 1.1 | 1.2 | -0.00232
CFLNonePGEMLINewCZ01 | Com-Iltg-dWatt-CFL_OSnone | PGE | MLI | New | CZ01 | 2.26 | 0.000514 | 0 | 2.14 | 0.000559 | -0.0346 | 2.26 | 0.000514 | 0 | 2.14 | 0.000559 | -0.0346 | CFL | None | 2260 | 0.514 | 2260 | 0.514 | 0.947 | 1.09 | -0.0153
CFLNonePGEMLINewCZ02 | Com-Iltg-dWatt-CFL_OSnone | PGE | MLI | New | CZ02 | 2.26 | 0.000514 | 0 | 2.28 | 0.000593 | -0.0191 | 2.26 | 0.000514 | 0 | 2.28 | 0.000593 | -0.0191 | CFL | None | 2260 | 0.514 | 2260 | 0.514 | 1.01 | 1.15 | -0.00845
CFLNonePGEMLINewCZ03 | Com-Iltg-dWatt-CFL_OSnone | PGE | MLI | New | CZ03 | 2.26 | 0.000514 | 0 | 2.24 | 0.000599 | -0.0187 | 2.26 | 0.000514 | 0 | 2.24 | 0.000599 | -0.0187 | CFL | None | 2260 | 0.514 | 2260 | 0.514 | 0.991 | 1.17 | -0.00827
CFLNonePGEMLINewCZ04 | Com-Iltg-dWatt-CFL_OSnone | PGE | MLI | New | CZ04 | 2.26 | 0.000514 | 0 | 2.31 | 0.000591 | -0.0151 | 2.26 | 0.000514 | 0 | 2.31 | 0.000591 | -0.0151 | CFL | None | 2260 | 0.514 | 2260 | 0.514 | 1.02 | 1.15 | -0.00668
CFLNonePGEMLINewCZ05 | Com-Iltg-dWatt-CFL_OSnone | PGE | MLI | New | CZ05 | 2.26 | 0.000514 | 0 | 2.24 | 0.000589 | -0.0183 | 2.26 | 0.000514 | 0 | 2.24 | 0.000589 | -0.0183 | CFL | None | 2260 | 0.514 | 2260 | 0.514 | 0.991 | 1.15 | -0.0081
CFLNoneSCEMLINewCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | MLI | New | CZ05 | 2.26 | 0.000514 | 0 | 2.25 | 0.000612 | -0.0181 | 2.26 | 0.000514 | 0 | 2.25 | 0.000612 | -0.0181 | CFL | None | 2260 | 0.514 | 2260 | 0.514 | 0.996 | 1.19 | -0.00801
CFLNoneSDGMLINewCZ06 | Com-Iltg-dWatt-CFL_OSnone | SDG | MLI | New | CZ06 | 2.26 | 0.000514 | 0 | 2.38 | 0.000603 | -0.00877 | 2.26 | 0.000514 | 0 | 2.38 | 0.000603 | -0.00877 | CFL | None | 2260 | 0.514 | 2260 | 0.514 | 1.05 | 1.17 | -0.00388
CFLNoneSCEMLINewCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | MLI | New | CZ06 | 2.26 | 0.000514 | 0 | 2.37 | 0.0006 | -0.00816 | 2.26 | 0.000514 | 0 | 2.37 | 0.0006 | -0.00816 | CFL | None | 2260 | 0.514 | 2260 | 0.514 | 1.05 | 1.17 | -0.00361
CFLNoneSDGMLINewCZ07 | Com-Iltg-dWatt-CFL_OSnone | SDG | MLI | New | CZ07 | 2.26 | 0.000514 | 0 | 2.36 | 0.000602 | -0.00511 | 2.26 | 0.000514 | 0 | 2.36 | 0.000602 | -0.00511 | CFL | None | 2260 | 0.514 | 2260 | 0.514 | 1.04 | 1.17 | -0.00226
CFLNoneSDGMLINewCZ08 | Com-Iltg-dWatt-CFL_OSnone | SDG | MLI | New | CZ08 | 2.26 | 0.000514 | 0 | 2.42 | 0.000607 | -0.00705 | 2.26 | 0.000514 | 0 | 2.42 | 0.000607 | -0.00705 | CFL | None | 2260 | 0.514 | 2260 | 0.514 | 1.07 | 1.18 | -0.00312
CFLNoneSCEMLINewCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | MLI | New | CZ08 | 2.26 | 0.000514 | 0 | 2.41 | 0.000604 | -0.00658 | 2.26 | 0.000514 | 0 | 2.41 | 0.000604 | -0.00658 | CFL | None | 2260 | 0.514 | 2260 | 0.514 | 1.07 | 1.18 | -0.00291
CFLNoneSCEMLINewCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | MLI | New | CZ09 | 2.26 | 0.000514 | 0 | 2.47 | 0.00066 | -0.00757 | 2.26 | 0.000514 | 0 | 2.47 | 0.00066 | -0.00757 | CFL | None | 2260 | 0.514 | 2260 | 0.514 | 1.09 | 1.28 | -0.00335
CFLNoneSDGMLINewCZ10 | Com-Iltg-dWatt-CFL_OSnone | SDG | MLI | New | CZ10 | 2.26 | 0.000514 | 0 | 2.5 | 0.000677 | -0.00886 | 2.26 | 0.000514 | 0 | 2.5 | 0.000677 | -0.00886 | CFL | None | 2260 | 0.514 | 2260 | 0.514 | 1.11 | 1.32 | -0.00392
CFLNoneSCEMLINewCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | MLI | New | CZ10 | 2.26 | 0.000514 | 0 | 2.49 | 0.000672 | -0.00827 | 2.26 | 0.000514 | 0 | 2.49 | 0.000672 | -0.00827 | CFL | None | 2260 | 0.514 | 2260 | 0.514 | 1.1 | 1.31 | -0.00366
CFLNonePGEMLINewCZ11 | Com-Iltg-dWatt-CFL_OSnone | PGE | MLI | New | CZ11 | 2.26 | 0.000514 | 0 | 2.37 | 0.000614 | -0.016 | 2.26 | 0.000514 | 0 | 2.37 | 0.000614 | -0.016 | CFL | None | 2260 | 0.514 | 2260 | 0.514 | 1.05 | 1.19 | -0.00708
CFLNonePGEMLINewCZ12 | Com-Iltg-dWatt-CFL_OSnone | PGE | MLI | New | CZ12 | 2.26 | 0.000514 | 0 | 2.33 | 0.000606 | -0.0175 | 2.26 | 0.000514 | 0 | 2.33 | 0.000606 | -0.0175 | CFL | None | 2260 | 0.514 | 2260 | 0.514 | 1.03 | 1.18 | -0.00774
CFLNonePGEMLINewCZ13 | Com-Iltg-dWatt-CFL_OSnone | PGE | MLI | New | CZ13 | 2.26 | 0.000514 | 0 | 2.39 | 0.000618 | -0.0151 | 2.26 | 0.000514 | 0 | 2.39 | 0.000618 | -0.0151 | CFL | None | 2260 | 0.514 | 2260 | 0.514 | 1.06 | 1.2 | -0.00668
CFLNoneSCEMLINewCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | MLI | New | CZ13 | 2.26 | 0.000514 | 0 | 2.43 | 0.000646 | -0.015 | 2.26 | 0.000514 | 0 | 2.43 | 0.000646 | -0.015 | CFL | None | 2260 | 0.514 | 2260 | 0.514 | 1.08 | 1.26 | -0.00664
CFLNoneSDGMLINewCZ14 | Com-Iltg-dWatt-CFL_OSnone | SDG | MLI | New | CZ14 | 2.26 | 0.000514 | 0 | 2.4 | 0.000632 | -0.0174 | 2.26 | 0.000514 | 0 | 2.4 | 0.000632 | -0.0174 | CFL | None | 2260 | 0.514 | 2260 | 0.514 | 1.06 | 1.23 | -0.0077
CFLNoneSCEMLINewCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | MLI | New | CZ14 | 2.26 | 0.000514 | 0 | 2.39 | 0.000628 | -0.0163 | 2.26 | 0.000514 | 0 | 2.39 | 0.000628 | -0.0163 | CFL | None | 2260 | 0.514 | 2260 | 0.514 | 1.06 | 1.22 | -0.00721
CFLNoneSCEMLINewCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | MLI | New | CZ15 | 2.26 | 0.000514 | 0 | 2.65 | 0.000683 | -0.00139 | 2.26 | 0.000514 | 0 | 2.65 | 0.000683 | -0.00139 | CFL | None | 2260 | 0.514 | 2260 | 0.514 | 1.17 | 1.33 | -0.000615
CFLNoneSDGMLINewCZ15 | Com-Iltg-dWatt-CFL_OSnone | SDG | MLI | New | CZ15 | 2.26 | 0.000514 | 0 | 2.67 | 0.000689 | -0.00148 | 2.26 | 0.000514 | 0 | 2.67 | 0.000689 | -0.00148 | CFL | None | 2260 | 0.514 | 2260 | 0.514 | 1.18 | 1.34 | -0.000655
CFLNoneSCEMLINewCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | MLI | New | CZ16 | 2.26 | 0.000514 | 0 | 2.23 | 0.000604 | -0.0289 | 2.26 | 0.000514 | 0 | 2.23 | 0.000604 | -0.0289 | CFL | None | 2260 | 0.514 | 2260 | 0.514 | 0.987 | 1.18 | -0.0128
CFLNonePGEMLINewCZ16 | Com-Iltg-dWatt-CFL_OSnone | PGE | MLI | New | CZ16 | 2.26 | 0.000514 | 0 | 2.21 | 0.000584 | -0.0294 | 2.26 | 0.000514 | 0 | 2.21 | 0.000584 | -0.0294 | CFL | None | 2260 | 0.514 | 2260 | 0.514 | 0.978 | 1.14 | -0.013
CFLNoneSCGMLINewIOU | Com-Iltg-dWatt-CFL_OSnone | SCG | MLI | New | IOU | 2.26 | 0.000514 | 0 | 2.47 | 0.000642 | -0.0079 | 2.26 | 0.000514 | 0 | 2.47 | 0.000642 | -0.0079 | CFL | None | 2260 | 0.514 | 2260 | 0.514 | 1.09 | 1.25 | -0.0035
CFLNonePGEMLINewIOU | Com-Iltg-dWatt-CFL_OSnone | PGE | MLI | New | IOU | 2.26 | 0.000514 | 0 | 2.4 | 0.00064 | -0.0162 | 2.26 | 0.000514 | 0 | 2.4 | 0.00064 | -0.0162 | CFL | None | 2260 | 0.514 | 2260 | 0.514 | 1.06 | 1.25 | -0.00717
CFLNoneSCEMLINewIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | MLI | New | IOU | 2.26 | 0.000514 | 0 | 2.47 | 0.000644 | -0.00791 | 2.26 | 0.000514 | 0 | 2.47 | 0.000644 | -0.00791 | CFL | None | 2260 | 0.514 | 2260 | 0.514 | 1.09 | 1.25 | -0.0035
CFLNoneSDGMLINewIOU | Com-Iltg-dWatt-CFL_OSnone | SDG | MLI | New | IOU | 2.26 | 0.000514 | 0 | 2.41 | 0.000625 | -0.00651 | 2.26 | 0.000514 | 0 | 2.41 | 0.000625 | -0.00651 | CFL | None | 2260 | 0.514 | 2260 | 0.514 | 1.07 | 1.22 | -0.00288
CFLNonePGEMtlExCZ01 | Com-Iltg-dWatt-CFL_OSnone | PGE | Mtl | Ex | CZ01 | 0.968 | 8.27e-05 | 0 | 0.954 | 9.84e-05 | -0.00834 | 0.968 | 8.27e-05 | 0 | 0.954 | 9.84e-05 | -0.00834 | CFL | None | 968 | 0.0827 | 968 | 0.0827 | 0.986 | 1.19 | -0.00862
CFLNonePGEMtlExCZ02 | Com-Iltg-dWatt-CFL_OSnone | PGE | Mtl | Ex | CZ02 | 0.968 | 8.27e-05 | 0 | 1.01 | 0.000102 | -0.00553 | 0.968 | 8.27e-05 | 0 | 1.01 | 0.000102 | -0.00553 | CFL | None | 968 | 0.0827 | 968 | 0.0827 | 1.04 | 1.23 | -0.00571
CFLNonePGEMtlExCZ03 | Com-Iltg-dWatt-CFL_OSnone | PGE | Mtl | Ex | CZ03 | 0.968 | 8.27e-05 | 0 | 1.02 | 9.98e-05 | -0.00536 | 0.968 | 8.27e-05 | 0 | 1.02 | 9.98e-05 | -0.00536 | CFL | None | 968 | 0.0827 | 968 | 0.0827 | 1.05 | 1.21 | -0.00554
CFLNonePGEMtlExCZ04 | Com-Iltg-dWatt-CFL_OSnone | PGE | Mtl | Ex | CZ04 | 0.968 | 8.27e-05 | 0 | 1.03 | 0.000101 | -0.00443 | 0.968 | 8.27e-05 | 0 | 1.03 | 0.000101 | -0.00443 | CFL | None | 968 | 0.0827 | 968 | 0.0827 | 1.06 | 1.22 | -0.00458
CFLNonePGEMtlExCZ05 | Com-Iltg-dWatt-CFL_OSnone | PGE | Mtl | Ex | CZ05 | 0.968 | 8.27e-05 | 0 | 1.03 | 0.000104 | -0.00463 | 0.968 | 8.27e-05 | 0 | 1.03 | 0.000104 | -0.00463 | CFL | None | 968 | 0.0827 | 968 | 0.0827 | 1.06 | 1.26 | -0.00478
CFLNoneSCEMtlExCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | Mtl | Ex | CZ05 | 0.968 | 8.27e-05 | 0 | 1.03 | 0.000104 | -0.00463 | 0.968 | 8.27e-05 | 0 | 1.03 | 0.000104 | -0.00463 | CFL | None | 968 | 0.0827 | 968 | 0.0827 | 1.06 | 1.26 | -0.00478
CFLNoneSCGMtlExCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCG | Mtl | Ex | CZ05 | 0.968 | 8.27e-05 | 0 | 1.03 | 0.000104 | -0.00463 | 0.968 | 8.27e-05 | 0 | 1.03 | 0.000104 | -0.00463 | CFL | None | 968 | 0.0827 | 968 | 0.0827 | 1.06 | 1.26 | -0.00478
CFLNoneSCGMtlExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCG | Mtl | Ex | CZ06 | 0.968 | 8.27e-05 | 0 | 1.1 | 0.000104 | -0.00257 | 0.968 | 8.27e-05 | 0 | 1.1 | 0.000104 | -0.00257 | CFL | None | 968 | 0.0827 | 968 | 0.0827 | 1.14 | 1.26 | -0.00265
CFLNoneSDGMtlExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SDG | Mtl | Ex | CZ06 | 0.968 | 8.27e-05 | 0 | 1.1 | 0.000104 | -0.00257 | 0.968 | 8.27e-05 | 0 | 1.1 | 0.000104 | -0.00257 | CFL | None | 968 | 0.0827 | 968 | 0.0827 | 1.14 | 1.26 | -0.00265
CFLNoneSCEMtlExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | Mtl | Ex | CZ06 | 0.968 | 8.27e-05 | 0 | 1.1 | 0.000104 | -0.00257 | 0.968 | 8.27e-05 | 0 | 1.1 | 0.000104 | -0.00257 | CFL | None | 968 | 0.0827 | 968 | 0.0827 | 1.14 | 1.26 | -0.00265
CFLNoneSDGMtlExCZ07 | Com-Iltg-dWatt-CFL_OSnone | SDG | Mtl | Ex | CZ07 | 0.968 | 8.27e-05 | 0 | 1.12 | 0.000103 | -0.00183 | 0.968 | 8.27e-05 | 0 | 1.12 | 0.000103 | -0.00183 | CFL | None | 968 | 0.0827 | 968 | 0.0827 | 1.16 | 1.25 | -0.00189
CFLNoneSDGMtlExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SDG | Mtl | Ex | CZ08 | 0.968 | 8.27e-05 | 0 | 1.11 | 0.000105 | -0.00215 | 0.968 | 8.27e-05 | 0 | 1.11 | 0.000105 | -0.00215 | CFL | None | 968 | 0.0827 | 968 | 0.0827 | 1.15 | 1.27 | -0.00222
CFLNoneSCEMtlExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | Mtl | Ex | CZ08 | 0.968 | 8.27e-05 | 0 | 1.11 | 0.000105 | -0.00215 | 0.968 | 8.27e-05 | 0 | 1.11 | 0.000105 | -0.00215 | CFL | None | 968 | 0.0827 | 968 | 0.0827 | 1.15 | 1.27 | -0.00222
CFLNoneSCGMtlExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCG | Mtl | Ex | CZ08 | 0.968 | 8.27e-05 | 0 | 1.11 | 0.000105 | -0.00215 | 0.968 | 8.27e-05 | 0 | 1.11 | 0.000105 | -0.00215 | CFL | None | 968 | 0.0827 | 968 | 0.0827 | 1.15 | 1.27 | -0.00222
CFLNoneSCGMtlExCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCG | Mtl | Ex | CZ09 | 0.968 | 8.27e-05 | 0 | 1.12 | 0.000109 | -0.00226 | 0.968 | 8.27e-05 | 0 | 1.12 | 0.000109 | -0.00226 | CFL | None | 968 | 0.0827 | 968 | 0.0827 | 1.16 | 1.32 | -0.00233
CFLNoneSCEMtlExCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | Mtl | Ex | CZ09 | 0.968 | 8.27e-05 | 0 | 1.12 | 0.000109 | -0.00226 | 0.968 | 8.27e-05 | 0 | 1.12 | 0.000109 | -0.00226 | CFL | None | 968 | 0.0827 | 968 | 0.0827 | 1.16 | 1.32 | -0.00233
CFLNoneSCEMtlExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | Mtl | Ex | CZ10 | 0.968 | 8.27e-05 | 0 | 1.1 | 0.000108 | -0.00257 | 0.968 | 8.27e-05 | 0 | 1.1 | 0.000108 | -0.00257 | CFL | None | 968 | 0.0827 | 968 | 0.0827 | 1.14 | 1.31 | -0.00265
CFLNoneSCGMtlExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCG | Mtl | Ex | CZ10 | 0.968 | 8.27e-05 | 0 | 1.1 | 0.000108 | -0.00257 | 0.968 | 8.27e-05 | 0 | 1.1 | 0.000108 | -0.00257 | CFL | None | 968 | 0.0827 | 968 | 0.0827 | 1.14 | 1.31 | -0.00265
CFLNoneSDGMtlExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SDG | Mtl | Ex | CZ10 | 0.968 | 8.27e-05 | 0 | 1.1 | 0.000108 | -0.00257 | 0.968 | 8.27e-05 | 0 | 1.1 | 0.000108 | -0.00257 | CFL | None | 968 | 0.0827 | 968 | 0.0827 | 1.14 | 1.31 | -0.00265
CFLNonePGEMtlExCZ11 | Com-Iltg-dWatt-CFL_OSnone | PGE | Mtl | Ex | CZ11 | 0.968 | 8.27e-05 | 0 | 1.04 | 0.000103 | -0.00466 | 0.968 | 8.27e-05 | 0 | 1.04 | 0.000103 | -0.00466 | CFL | None | 968 | 0.0827 | 968 | 0.0827 | 1.07 | 1.25 | -0.00481
CFLNonePGEMtlExCZ12 | Com-Iltg-dWatt-CFL_OSnone | PGE | Mtl | Ex | CZ12 | 0.968 | 8.27e-05 | 0 | 1.03 | 0.000103 | -0.00492 | 0.968 | 8.27e-05 | 0 | 1.03 | 0.000103 | -0.00492 | CFL | None | 968 | 0.0827 | 968 | 0.0827 | 1.06 | 1.25 | -0.00508
CFLNonePGEMtlExCZ13 | Com-Iltg-dWatt-CFL_OSnone | PGE | Mtl | Ex | CZ13 | 0.968 | 8.27e-05 | 0 | 1.08 | 0.000108 | -0.00357 | 0.968 | 8.27e-05 | 0 | 1.08 | 0.000108 | -0.00357 | CFL | None | 968 | 0.0827 | 968 | 0.0827 | 1.12 | 1.31 | -0.00369
CFLNoneSCEMtlExCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | Mtl | Ex | CZ13 | 0.968 | 8.27e-05 | 0 | 1.08 | 0.000108 | -0.00357 | 0.968 | 8.27e-05 | 0 | 1.08 | 0.000108 | -0.00357 | CFL | None | 968 | 0.0827 | 968 | 0.0827 | 1.12 | 1.31 | -0.00369
CFLNoneSCGMtlExCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCG | Mtl | Ex | CZ13 | 0.968 | 8.27e-05 | 0 | 1.08 | 0.000108 | -0.00357 | 0.968 | 8.27e-05 | 0 | 1.08 | 0.000108 | -0.00357 | CFL | None | 968 | 0.0827 | 968 | 0.0827 | 1.12 | 1.31 | -0.00369
CFLNoneSCEMtlExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | Mtl | Ex | CZ14 | 0.968 | 8.27e-05 | 0 | 1.06 | 0.000108 | -0.00361 | 0.968 | 8.27e-05 | 0 | 1.06 | 0.000108 | -0.00361 | CFL | None | 968 | 0.0827 | 968 | 0.0827 | 1.1 | 1.31 | -0.00373
CFLNoneSDGMtlExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SDG | Mtl | Ex | CZ14 | 0.968 | 8.27e-05 | 0 | 1.06 | 0.000108 | -0.00361 | 0.968 | 8.27e-05 | 0 | 1.06 | 0.000108 | -0.00361 | CFL | None | 968 | 0.0827 | 968 | 0.0827 | 1.1 | 1.31 | -0.00373
CFLNoneSCGMtlExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCG | Mtl | Ex | CZ14 | 0.968 | 8.27e-05 | 0 | 1.06 | 0.000108 | -0.00361 | 0.968 | 8.27e-05 | 0 | 1.06 | 0.000108 | -0.00361 | CFL | None | 968 | 0.0827 | 968 | 0.0827 | 1.1 | 1.31 | -0.00373
CFLNoneSCGMtlExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCG | Mtl | Ex | CZ15 | 0.968 | 8.27e-05 | 0 | 1.17 | 0.00011 | -0.00105 | 0.968 | 8.27e-05 | 0 | 1.17 | 0.00011 | -0.00105 | CFL | None | 968 | 0.0827 | 968 | 0.0827 | 1.21 | 1.33 | -0.00108
CFLNoneSDGMtlExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SDG | Mtl | Ex | CZ15 | 0.968 | 8.27e-05 | 0 | 1.17 | 0.00011 | -0.00105 | 0.968 | 8.27e-05 | 0 | 1.17 | 0.00011 | -0.00105 | CFL | None | 968 | 0.0827 | 968 | 0.0827 | 1.21 | 1.33 | -0.00108
CFLNoneSCEMtlExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | Mtl | Ex | CZ15 | 0.968 | 8.27e-05 | 0 | 1.17 | 0.00011 | -0.00105 | 0.968 | 8.27e-05 | 0 | 1.17 | 0.00011 | -0.00105 | CFL | None | 968 | 0.0827 | 968 | 0.0827 | 1.21 | 1.33 | -0.00108
CFLNoneSCEMtlExCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | Mtl | Ex | CZ16 | 0.968 | 8.27e-05 | 0 | 0.963 | 0.000104 | -0.00615 | 0.968 | 8.27e-05 | 0 | 0.963 | 0.000104 | -0.00615 | CFL | None | 968 | 0.0827 | 968 | 0.0827 | 0.995 | 1.26 | -0.00635
CFLNoneSCGMtlExCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCG | Mtl | Ex | CZ16 | 0.968 | 8.27e-05 | 0 | 0.963 | 0.000104 | -0.00615 | 0.968 | 8.27e-05 | 0 | 0.963 | 0.000104 | -0.00615 | CFL | None | 968 | 0.0827 | 968 | 0.0827 | 0.995 | 1.26 | -0.00635
CFLNonePGEMtlExCZ16 | Com-Iltg-dWatt-CFL_OSnone | PGE | Mtl | Ex | CZ16 | 0.968 | 8.27e-05 | 0 | 0.963 | 0.000104 | -0.00615 | 0.968 | 8.27e-05 | 0 | 0.963 | 0.000104 | -0.00615 | CFL | None | 968 | 0.0827 | 968 | 0.0827 | 0.995 | 1.26 | -0.00635
CFLNoneSCGMtlExIOU | Com-Iltg-dWatt-CFL_OSnone | SCG | Mtl | Ex | IOU | 0.968 | 8.27e-05 | 0 | 1.11 | 0.000107 | -0.00236 | 0.968 | 8.27e-05 | 0 | 1.11 | 0.000107 | -0.00236 | CFL | None | 968 | 0.0827 | 968 | 0.0827 | 1.15 | 1.29 | -0.00244
CFLNoneSDGMtlExIOU | Com-Iltg-dWatt-CFL_OSnone | SDG | Mtl | Ex | IOU | 0.968 | 8.27e-05 | 0 | 1.12 | 0.000104 | -0.00194 | 0.968 | 8.27e-05 | 0 | 1.12 | 0.000104 | -0.00194 | CFL | None | 968 | 0.0827 | 968 | 0.0827 | 1.16 | 1.26 | -0.002
CFLNonePGEMtlExIOU | Com-Iltg-dWatt-CFL_OSnone | PGE | Mtl | Ex | IOU | 0.968 | 8.27e-05 | 0 | 1.03 | 0.000102 | -0.00501 | 0.968 | 8.27e-05 | 0 | 1.03 | 0.000102 | -0.00501 | CFL | None | 968 | 0.0827 | 968 | 0.0827 | 1.06 | 1.23 | -0.00518
CFLNoneSCEMtlExIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | Mtl | Ex | IOU | 0.968 | 8.27e-05 | 0 | 1.11 | 0.000106 | -0.00239 | 0.968 | 8.27e-05 | 0 | 1.11 | 0.000106 | -0.00239 | CFL | None | 968 | 0.0827 | 968 | 0.0827 | 1.15 | 1.28 | -0.00247
CFLNonePGEMtlNewCZ01 | Com-Iltg-dWatt-CFL_OSnone | PGE | Mtl | New | CZ01 | 0.968 | 8.27e-05 | 0 | 0.915 | 9.83e-05 | -0.0107 | 0.968 | 8.27e-05 | 0 | 0.915 | 9.83e-05 | -0.0107 | CFL | None | 968 | 0.0827 | 968 | 0.0827 | 0.945 | 1.19 | -0.0111
CFLNonePGEMtlNewCZ02 | Com-Iltg-dWatt-CFL_OSnone | PGE | Mtl | New | CZ02 | 0.968 | 8.27e-05 | 0 | 0.99 | 0.000105 | -0.00725 | 0.968 | 8.27e-05 | 0 | 0.99 | 0.000105 | -0.00725 | CFL | None | 968 | 0.0827 | 968 | 0.0827 | 1.02 | 1.27 | -0.00749
CFLNonePGEMtlNewCZ03 | Com-Iltg-dWatt-CFL_OSnone | PGE | Mtl | New | CZ03 | 0.968 | 8.27e-05 | 0 | 0.998 | 0.000101 | -0.00681 | 0.968 | 8.27e-05 | 0 | 0.998 | 0.000101 | -0.00681 | CFL | None | 968 | 0.0827 | 968 | 0.0827 | 1.03 | 1.22 | -0.00704
CFLNonePGEMtlNewCZ04 | Com-Iltg-dWatt-CFL_OSnone | PGE | Mtl | New | CZ04 | 0.968 | 8.27e-05 | 0 | 1.02 | 0.000104 | -0.00574 | 0.968 | 8.27e-05 | 0 | 1.02 | 0.000104 | -0.00574 | CFL | None | 968 | 0.0827 | 968 | 0.0827 | 1.05 | 1.26 | -0.00593
CFLNoneSCEMtlNewCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | Mtl | New | CZ05 | 0.968 | 8.27e-05 | 0 | 0.997 | 0.000105 | -0.00621 | 0.968 | 8.27e-05 | 0 | 0.997 | 0.000105 | -0.00621 | CFL | None | 968 | 0.0827 | 968 | 0.0827 | 1.03 | 1.27 | -0.00642
CFLNonePGEMtlNewCZ05 | Com-Iltg-dWatt-CFL_OSnone | PGE | Mtl | New | CZ05 | 0.968 | 8.27e-05 | 0 | 0.982 | 0.0001 | -0.00765 | 0.968 | 8.27e-05 | 0 | 0.982 | 0.0001 | -0.00765 | CFL | None | 968 | 0.0827 | 968 | 0.0827 | 1.01 | 1.21 | -0.0079
CFLNoneSCEMtlNewCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | Mtl | New | CZ06 | 0.968 | 8.27e-05 | 0 | 1.09 | 0.000107 | -0.00329 | 0.968 | 8.27e-05 | 0 | 1.09 | 0.000107 | -0.00329 | CFL | None | 968 | 0.0827 | 968 | 0.0827 | 1.13 | 1.29 | -0.0034
CFLNoneSDGMtlNewCZ06 | Com-Iltg-dWatt-CFL_OSnone | SDG | Mtl | New | CZ06 | 0.968 | 8.27e-05 | 0 | 1.09 | 0.000106 | -0.00339 | 0.968 | 8.27e-05 | 0 | 1.09 | 0.000106 | -0.00339 | CFL | None | 968 | 0.0827 | 968 | 0.0827 | 1.13 | 1.28 | -0.0035
CFLNoneSDGMtlNewCZ07 | Com-Iltg-dWatt-CFL_OSnone | SDG | Mtl | New | CZ07 | 0.968 | 8.27e-05 | 0 | 1.11 | 0.000105 | -0.00233 | 0.968 | 8.27e-05 | 0 | 1.11 | 0.000105 | -0.00233 | CFL | None | 968 | 0.0827 | 968 | 0.0827 | 1.15 | 1.27 | -0.00241
CFLNoneSCEMtlNewCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | Mtl | New | CZ08 | 0.968 | 8.27e-05 | 0 | 1.11 | 0.000109 | -0.00274 | 0.968 | 8.27e-05 | 0 | 1.11 | 0.000109 | -0.00274 | CFL | None | 968 | 0.0827 | 968 | 0.0827 | 1.15 | 1.32 | -0.00283
CFLNoneSDGMtlNewCZ08 | Com-Iltg-dWatt-CFL_OSnone | SDG | Mtl | New | CZ08 | 0.968 | 8.27e-05 | 0 | 1.11 | 0.000108 | -0.00283 | 0.968 | 8.27e-05 | 0 | 1.11 | 0.000108 | -0.00283 | CFL | None | 968 | 0.0827 | 968 | 0.0827 | 1.15 | 1.31 | -0.00292
CFLNoneSCEMtlNewCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | Mtl | New | CZ09 | 0.968 | 8.27e-05 | 0 | 1.11 | 0.000111 | -0.00276 | 0.968 | 8.27e-05 | 0 | 1.11 | 0.000111 | -0.00276 | CFL | None | 968 | 0.0827 | 968 | 0.0827 | 1.15 | 1.34 | -0.00285
CFLNoneSDGMtlNewCZ10 | Com-Iltg-dWatt-CFL_OSnone | SDG | Mtl | New | CZ10 | 0.968 | 8.27e-05 | 0 | 1.09 | 0.000111 | -0.00354 | 0.968 | 8.27e-05 | 0 | 1.09 | 0.000111 | -0.00354 | CFL | None | 968 | 0.0827 | 968 | 0.0827 | 1.13 | 1.34 | -0.00366
CFLNoneSCEMtlNewCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | Mtl | New | CZ10 | 0.968 | 8.27e-05 | 0 | 1.09 | 0.000112 | -0.00342 | 0.968 | 8.27e-05 | 0 | 1.09 | 0.000112 | -0.00342 | CFL | None | 968 | 0.0827 | 968 | 0.0827 | 1.13 | 1.35 | -0.00353
CFLNonePGEMtlNewCZ11 | Com-Iltg-dWatt-CFL_OSnone | PGE | Mtl | New | CZ11 | 0.968 | 8.27e-05 | 0 | 1.03 | 0.000106 | -0.00581 | 0.968 | 8.27e-05 | 0 | 1.03 | 0.000106 | -0.00581 | CFL | None | 968 | 0.0827 | 968 | 0.0827 | 1.06 | 1.28 | -0.006
CFLNonePGEMtlNewCZ12 | Com-Iltg-dWatt-CFL_OSnone | PGE | Mtl | New | CZ12 | 0.968 | 8.27e-05 | 0 | 1.02 | 0.000105 | -0.00607 | 0.968 | 8.27e-05 | 0 | 1.02 | 0.000105 | -0.00607 | CFL | None | 968 | 0.0827 | 968 | 0.0827 | 1.05 | 1.27 | -0.00627
CFLNonePGEMtlNewCZ13 | Com-Iltg-dWatt-CFL_OSnone | PGE | Mtl | New | CZ13 | 0.968 | 8.27e-05 | 0 | 1.04 | 0.000105 | -0.00546 | 0.968 | 8.27e-05 | 0 | 1.04 | 0.000105 | -0.00546 | CFL | None | 968 | 0.0827 | 968 | 0.0827 | 1.07 | 1.27 | -0.00564
CFLNoneSCEMtlNewCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | Mtl | New | CZ13 | 0.968 | 8.27e-05 | 0 | 1.06 | 0.00011 | -0.00441 | 0.968 | 8.27e-05 | 0 | 1.06 | 0.00011 | -0.00441 | CFL | None | 968 | 0.0827 | 968 | 0.0827 | 1.1 | 1.33 | -0.00456
CFLNoneSDGMtlNewCZ14 | Com-Iltg-dWatt-CFL_OSnone | SDG | Mtl | New | CZ14 | 0.968 | 8.27e-05 | 0 | 1.05 | 0.000111 | -0.00474 | 0.968 | 8.27e-05 | 0 | 1.05 | 0.000111 | -0.00474 | CFL | None | 968 | 0.0827 | 968 | 0.0827 | 1.08 | 1.34 | -0.0049
CFLNoneSCEMtlNewCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | Mtl | New | CZ14 | 0.968 | 8.27e-05 | 0 | 1.05 | 0.000112 | -0.00459 | 0.968 | 8.27e-05 | 0 | 1.05 | 0.000112 | -0.00459 | CFL | None | 968 | 0.0827 | 968 | 0.0827 | 1.08 | 1.35 | -0.00474
CFLNoneSCEMtlNewCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | Mtl | New | CZ15 | 0.968 | 8.27e-05 | 0 | 1.17 | 0.000114 | -0.00159 | 0.968 | 8.27e-05 | 0 | 1.17 | 0.000114 | -0.00159 | CFL | None | 968 | 0.0827 | 968 | 0.0827 | 1.21 | 1.38 | -0.00164
CFLNoneSDGMtlNewCZ15 | Com-Iltg-dWatt-CFL_OSnone | SDG | Mtl | New | CZ15 | 0.968 | 8.27e-05 | 0 | 1.17 | 0.000113 | -0.00163 | 0.968 | 8.27e-05 | 0 | 1.17 | 0.000113 | -0.00163 | CFL | None | 968 | 0.0827 | 968 | 0.0827 | 1.21 | 1.37 | -0.00168
CFLNonePGEMtlNewCZ16 | Com-Iltg-dWatt-CFL_OSnone | PGE | Mtl | New | CZ16 | 0.968 | 8.27e-05 | 0 | 0.932 | 0.000101 | -0.00856 | 0.968 | 8.27e-05 | 0 | 0.932 | 0.000101 | -0.00856 | CFL | None | 968 | 0.0827 | 968 | 0.0827 | 0.963 | 1.22 | -0.00884
CFLNoneSCEMtlNewCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | Mtl | New | CZ16 | 0.968 | 8.27e-05 | 0 | 0.937 | 0.000105 | -0.00714 | 0.968 | 8.27e-05 | 0 | 0.937 | 0.000105 | -0.00714 | CFL | None | 968 | 0.0827 | 968 | 0.0827 | 0.968 | 1.27 | -0.00738
CFLNoneSCGMtlNewIOU | Com-Iltg-dWatt-CFL_OSnone | SCG | Mtl | New | IOU | 0.968 | 8.27e-05 | 0 | 1.12 | 0.000109 | -0.00283 | 0.968 | 8.27e-05 | 0 | 1.12 | 0.000109 | -0.00283 | CFL | None | 968 | 0.0827 | 968 | 0.0827 | 1.16 | 1.32 | -0.00292
CFLNonePGEMtlNewIOU | Com-Iltg-dWatt-CFL_OSnone | PGE | Mtl | New | IOU | 0.968 | 8.27e-05 | 0 | 1.02 | 0.000108 | -0.00534 | 0.968 | 8.27e-05 | 0 | 1.02 | 0.000108 | -0.00534 | CFL | None | 968 | 0.0827 | 968 | 0.0827 | 1.05 | 1.31 | -0.00552
CFLNoneSCEMtlNewIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | Mtl | New | IOU | 0.968 | 8.27e-05 | 0 | 1.12 | 0.00011 | -0.0028 | 0.968 | 8.27e-05 | 0 | 1.12 | 0.00011 | -0.0028 | CFL | None | 968 | 0.0827 | 968 | 0.0827 | 1.16 | 1.33 | -0.00289
CFLNoneSDGMtlNewIOU | Com-Iltg-dWatt-CFL_OSnone | SDG | Mtl | New | IOU | 0.968 | 8.27e-05 | 0 | 1.11 | 0.000106 | -0.00251 | 0.968 | 8.27e-05 | 0 | 1.11 | 0.000106 | -0.00251 | CFL | None | 968 | 0.0827 | 968 | 0.0827 | 1.15 | 1.28 | -0.00259
CFLNonePGENrsExCZ01 | Com-Iltg-dWatt-CFL_OSnone | PGE | Nrs | Ex | CZ01 | 3.43 | 0.000485 | 0 | 3.37 | 0.000554 | -0.0693 | 3.43 | 0.000485 | 0 | 3.37 | 0.000554 | -0.0693 | CFL | None | 3430 | 0.485 | 3430 | 0.485 | 0.983 | 1.14 | -0.0202
CFLNonePGENrsExCZ02 | Com-Iltg-dWatt-CFL_OSnone | PGE | Nrs | Ex | CZ02 | 3.43 | 0.000485 | 0 | 3.55 | 0.000609 | -0.0501 | 3.43 | 0.000485 | 0 | 3.55 | 0.000609 | -0.0501 | CFL | None | 3430 | 0.485 | 3430 | 0.485 | 1.03 | 1.26 | -0.0146
CFLNonePGENrsExCZ03 | Com-Iltg-dWatt-CFL_OSnone | PGE | Nrs | Ex | CZ03 | 3.43 | 0.000485 | 0 | 3.52 | 0.000591 | -0.0508 | 3.43 | 0.000485 | 0 | 3.52 | 0.000591 | -0.0508 | CFL | None | 3430 | 0.485 | 3430 | 0.485 | 1.03 | 1.22 | -0.0148
CFLNonePGENrsExCZ04 | Com-Iltg-dWatt-CFL_OSnone | PGE | Nrs | Ex | CZ04 | 3.43 | 0.000485 | 0 | 3.6 | 0.000604 | -0.0429 | 3.43 | 0.000485 | 0 | 3.6 | 0.000604 | -0.0429 | CFL | None | 3430 | 0.485 | 3430 | 0.485 | 1.05 | 1.25 | -0.0125
CFLNonePGENrsExCZ05 | Com-Iltg-dWatt-CFL_OSnone | PGE | Nrs | Ex | CZ05 | 3.43 | 0.000485 | 0 | 3.51 | 0.000598 | -0.0501 | 3.43 | 0.000485 | 0 | 3.51 | 0.000598 | -0.0501 | CFL | None | 3430 | 0.485 | 3430 | 0.485 | 1.02 | 1.23 | -0.0146
CFLNoneSCENrsExCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | Nrs | Ex | CZ05 | 3.43 | 0.000485 | 0 | 3.51 | 0.000598 | -0.0501 | 3.43 | 0.000485 | 0 | 3.51 | 0.000598 | -0.0501 | CFL | None | 3430 | 0.485 | 3430 | 0.485 | 1.02 | 1.23 | -0.0146
CFLNoneSCGNrsExCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCG | Nrs | Ex | CZ05 | 3.43 | 0.000485 | 0 | 3.51 | 0.000598 | -0.0501 | 3.43 | 0.000485 | 0 | 3.51 | 0.000598 | -0.0501 | CFL | None | 3430 | 0.485 | 3430 | 0.485 | 1.02 | 1.23 | -0.0146
CFLNoneSDGNrsExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SDG | Nrs | Ex | CZ06 | 3.43 | 0.000485 | 0 | 3.7 | 0.000626 | -0.0325 | 3.43 | 0.000485 | 0 | 3.7 | 0.000626 | -0.0325 | CFL | None | 3430 | 0.485 | 3430 | 0.485 | 1.08 | 1.29 | -0.00948
CFLNoneSCENrsExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | Nrs | Ex | CZ06 | 3.43 | 0.000485 | 0 | 3.7 | 0.000626 | -0.0325 | 3.43 | 0.000485 | 0 | 3.7 | 0.000626 | -0.0325 | CFL | None | 3430 | 0.485 | 3430 | 0.485 | 1.08 | 1.29 | -0.00948
CFLNoneSCGNrsExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCG | Nrs | Ex | CZ06 | 3.43 | 0.000485 | 0 | 3.7 | 0.000626 | -0.0325 | 3.43 | 0.000485 | 0 | 3.7 | 0.000626 | -0.0325 | CFL | None | 3430 | 0.485 | 3430 | 0.485 | 1.08 | 1.29 | -0.00948
CFLNoneSDGNrsExCZ07 | Com-Iltg-dWatt-CFL_OSnone | SDG | Nrs | Ex | CZ07 | 3.43 | 0.000485 | 0 | 3.69 | 0.000615 | -0.0288 | 3.43 | 0.000485 | 0 | 3.69 | 0.000615 | -0.0288 | CFL | None | 3430 | 0.485 | 3430 | 0.485 | 1.08 | 1.27 | -0.0084
CFLNoneSCGNrsExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCG | Nrs | Ex | CZ08 | 3.43 | 0.000485 | 0 | 3.74 | 0.000628 | -0.0314 | 3.43 | 0.000485 | 0 | 3.74 | 0.000628 | -0.0314 | CFL | None | 3430 | 0.485 | 3430 | 0.485 | 1.09 | 1.29 | -0.00915
CFLNoneSCENrsExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | Nrs | Ex | CZ08 | 3.43 | 0.000485 | 0 | 3.74 | 0.000628 | -0.0314 | 3.43 | 0.000485 | 0 | 3.74 | 0.000628 | -0.0314 | CFL | None | 3430 | 0.485 | 3430 | 0.485 | 1.09 | 1.29 | -0.00915
CFLNoneSDGNrsExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SDG | Nrs | Ex | CZ08 | 3.43 | 0.000485 | 0 | 3.74 | 0.000628 | -0.0314 | 3.43 | 0.000485 | 0 | 3.74 | 0.000628 | -0.0314 | CFL | None | 3430 | 0.485 | 3430 | 0.485 | 1.09 | 1.29 | -0.00915
CFLNoneSCGNrsExCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCG | Nrs | Ex | CZ09 | 3.43 | 0.000485 | 0 | 3.78 | 0.000648 | -0.0327 | 3.43 | 0.000485 | 0 | 3.78 | 0.000648 | -0.0327 | CFL | None | 3430 | 0.485 | 3430 | 0.485 | 1.1 | 1.34 | -0.00953
CFLNoneSCENrsExCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | Nrs | Ex | CZ09 | 3.43 | 0.000485 | 0 | 3.78 | 0.000648 | -0.0327 | 3.43 | 0.000485 | 0 | 3.78 | 0.000648 | -0.0327 | CFL | None | 3430 | 0.485 | 3430 | 0.485 | 1.1 | 1.34 | -0.00953
CFLNoneSCENrsExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | Nrs | Ex | CZ10 | 3.43 | 0.000485 | 0 | 3.75 | 0.000648 | -0.0334 | 3.43 | 0.000485 | 0 | 3.75 | 0.000648 | -0.0334 | CFL | None | 3430 | 0.485 | 3430 | 0.485 | 1.09 | 1.34 | -0.00974
CFLNoneSCGNrsExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCG | Nrs | Ex | CZ10 | 3.43 | 0.000485 | 0 | 3.75 | 0.000648 | -0.0334 | 3.43 | 0.000485 | 0 | 3.75 | 0.000648 | -0.0334 | CFL | None | 3430 | 0.485 | 3430 | 0.485 | 1.09 | 1.34 | -0.00974
CFLNoneSDGNrsExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SDG | Nrs | Ex | CZ10 | 3.43 | 0.000485 | 0 | 3.75 | 0.000648 | -0.0334 | 3.43 | 0.000485 | 0 | 3.75 | 0.000648 | -0.0334 | CFL | None | 3430 | 0.485 | 3430 | 0.485 | 1.09 | 1.34 | -0.00974
CFLNonePGENrsExCZ11 | Com-Iltg-dWatt-CFL_OSnone | PGE | Nrs | Ex | CZ11 | 3.43 | 0.000485 | 0 | 3.65 | 0.000614 | -0.0415 | 3.43 | 0.000485 | 0 | 3.65 | 0.000614 | -0.0415 | CFL | None | 3430 | 0.485 | 3430 | 0.485 | 1.06 | 1.27 | -0.0121
CFLNonePGENrsExCZ12 | Com-Iltg-dWatt-CFL_OSnone | PGE | Nrs | Ex | CZ12 | 3.43 | 0.000485 | 0 | 3.62 | 0.000611 | -0.0436 | 3.43 | 0.000485 | 0 | 3.62 | 0.000611 | -0.0436 | CFL | None | 3430 | 0.485 | 3430 | 0.485 | 1.06 | 1.26 | -0.0127
CFLNoneSCGNrsExCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCG | Nrs | Ex | CZ13 | 3.43 | 0.000485 | 0 | 3.7 | 0.00064 | -0.0377 | 3.43 | 0.000485 | 0 | 3.7 | 0.00064 | -0.0377 | CFL | None | 3430 | 0.485 | 3430 | 0.485 | 1.08 | 1.32 | -0.011
CFLNoneSCENrsExCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | Nrs | Ex | CZ13 | 3.43 | 0.000485 | 0 | 3.7 | 0.00064 | -0.0377 | 3.43 | 0.000485 | 0 | 3.7 | 0.00064 | -0.0377 | CFL | None | 3430 | 0.485 | 3430 | 0.485 | 1.08 | 1.32 | -0.011
CFLNonePGENrsExCZ13 | Com-Iltg-dWatt-CFL_OSnone | PGE | Nrs | Ex | CZ13 | 3.43 | 0.000485 | 0 | 3.7 | 0.00064 | -0.0377 | 3.43 | 0.000485 | 0 | 3.7 | 0.00064 | -0.0377 | CFL | None | 3430 | 0.485 | 3430 | 0.485 | 1.08 | 1.32 | -0.011
CFLNoneSCGNrsExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCG | Nrs | Ex | CZ14 | 3.43 | 0.000485 | 0 | 3.71 | 0.000641 | -0.0391 | 3.43 | 0.000485 | 0 | 3.71 | 0.000641 | -0.0391 | CFL | None | 3430 | 0.485 | 3430 | 0.485 | 1.08 | 1.32 | -0.0114
CFLNoneSCENrsExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | Nrs | Ex | CZ14 | 3.43 | 0.000485 | 0 | 3.71 | 0.000641 | -0.0391 | 3.43 | 0.000485 | 0 | 3.71 | 0.000641 | -0.0391 | CFL | None | 3430 | 0.485 | 3430 | 0.485 | 1.08 | 1.32 | -0.0114
CFLNoneSDGNrsExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SDG | Nrs | Ex | CZ14 | 3.43 | 0.000485 | 0 | 3.71 | 0.000641 | -0.0391 | 3.43 | 0.000485 | 0 | 3.71 | 0.000641 | -0.0391 | CFL | None | 3430 | 0.485 | 3430 | 0.485 | 1.08 | 1.32 | -0.0114
CFLNoneSCGNrsExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCG | Nrs | Ex | CZ15 | 3.43 | 0.000485 | 0 | 3.95 | 0.000645 | -0.0192 | 3.43 | 0.000485 | 0 | 3.95 | 0.000645 | -0.0192 | CFL | None | 3430 | 0.485 | 3430 | 0.485 | 1.15 | 1.33 | -0.0056
CFLNoneSCENrsExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | Nrs | Ex | CZ15 | 3.43 | 0.000485 | 0 | 3.95 | 0.000645 | -0.0192 | 3.43 | 0.000485 | 0 | 3.95 | 0.000645 | -0.0192 | CFL | None | 3430 | 0.485 | 3430 | 0.485 | 1.15 | 1.33 | -0.0056
CFLNoneSCENrsExCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | Nrs | Ex | CZ16 | 3.43 | 0.000485 | 0 | 3.42 | 0.000612 | -0.0569 | 3.43 | 0.000485 | 0 | 3.42 | 0.000612 | -0.0569 | CFL | None | 3430 | 0.485 | 3430 | 0.485 | 0.997 | 1.26 | -0.0166
CFLNonePGENrsExCZ16 | Com-Iltg-dWatt-CFL_OSnone | PGE | Nrs | Ex | CZ16 | 3.43 | 0.000485 | 0 | 3.42 | 0.000612 | -0.0569 | 3.43 | 0.000485 | 0 | 3.42 | 0.000612 | -0.0569 | CFL | None | 3430 | 0.485 | 3430 | 0.485 | 0.997 | 1.26 | -0.0166
CFLNoneSCGNrsExCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCG | Nrs | Ex | CZ16 | 3.43 | 0.000485 | 0 | 3.42 | 0.000612 | -0.0569 | 3.43 | 0.000485 | 0 | 3.42 | 0.000612 | -0.0569 | CFL | None | 3430 | 0.485 | 3430 | 0.485 | 0.997 | 1.26 | -0.0166
CFLNoneSCENrsExIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | Nrs | Ex | IOU | 3.43 | 0.000485 | 0 | 3.73 | 0.000634 | -0.0331 | 3.43 | 0.000485 | 0 | 3.73 | 0.000634 | -0.0331 | CFL | None | 3430 | 0.485 | 3430 | 0.485 | 1.09 | 1.31 | -0.00965
CFLNoneSDGNrsExIOU | Com-Iltg-dWatt-CFL_OSnone | SDG | Nrs | Ex | IOU | 3.43 | 0.000485 | 0 | 3.7 | 0.00062 | -0.0297 | 3.43 | 0.000485 | 0 | 3.7 | 0.00062 | -0.0297 | CFL | None | 3430 | 0.485 | 3430 | 0.485 | 1.08 | 1.28 | -0.00866
CFLNoneSCGNrsExIOU | Com-Iltg-dWatt-CFL_OSnone | SCG | Nrs | Ex | IOU | 3.43 | 0.000485 | 0 | 3.74 | 0.000636 | -0.0329 | 3.43 | 0.000485 | 0 | 3.74 | 0.000636 | -0.0329 | CFL | None | 3430 | 0.485 | 3430 | 0.485 | 1.09 | 1.31 | -0.00959
CFLNonePGENrsExIOU | Com-Iltg-dWatt-CFL_OSnone | PGE | Nrs | Ex | IOU | 3.43 | 0.000485 | 0 | 3.59 | 0.000608 | -0.0456 | 3.43 | 0.000485 | 0 | 3.59 | 0.000608 | -0.0456 | CFL | None | 3430 | 0.485 | 3430 | 0.485 | 1.05 | 1.25 | -0.0133
CFLNonePGENrsNewCZ01 | Com-Iltg-dWatt-CFL_OSnone | PGE | Nrs | New | CZ01 | 3.43 | 0.000485 | 0 | 3.26 | 0.00053 | -0.0755 | 3.43 | 0.000485 | 0 | 3.26 | 0.00053 | -0.0755 | CFL | None | 3430 | 0.485 | 3430 | 0.485 | 0.95 | 1.09 | -0.022
CFLNonePGENrsNewCZ02 | Com-Iltg-dWatt-CFL_OSnone | PGE | Nrs | New | CZ02 | 3.43 | 0.000485 | 0 | 3.43 | 0.000606 | -0.0532 | 3.43 | 0.000485 | 0 | 3.43 | 0.000606 | -0.0532 | CFL | None | 3430 | 0.485 | 3430 | 0.485 | 1 | 1.25 | -0.0155
CFLNonePGENrsNewCZ03 | Com-Iltg-dWatt-CFL_OSnone | PGE | Nrs | New | CZ03 | 3.43 | 0.000485 | 0 | 3.38 | 0.000596 | -0.0556 | 3.43 | 0.000485 | 0 | 3.38 | 0.000596 | -0.0556 | CFL | None | 3430 | 0.485 | 3430 | 0.485 | 0.985 | 1.23 | -0.0162
CFLNonePGENrsNewCZ04 | Com-Iltg-dWatt-CFL_OSnone | PGE | Nrs | New | CZ04 | 3.43 | 0.000485 | 0 | 3.52 | 0.000606 | -0.0449 | 3.43 | 0.000485 | 0 | 3.52 | 0.000606 | -0.0449 | CFL | None | 3430 | 0.485 | 3430 | 0.485 | 1.03 | 1.25 | -0.0131
CFLNoneSCENrsNewCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | Nrs | New | CZ05 | 3.43 | 0.000485 | 0 | 3.36 | 0.000591 | -0.0559 | 3.43 | 0.000485 | 0 | 3.36 | 0.000591 | -0.0559 | CFL | None | 3430 | 0.485 | 3430 | 0.485 | 0.98 | 1.22 | -0.0163
CFLNonePGENrsNewCZ05 | Com-Iltg-dWatt-CFL_OSnone | PGE | Nrs | New | CZ05 | 3.43 | 0.000485 | 0 | 3.38 | 0.000575 | -0.0576 | 3.43 | 0.000485 | 0 | 3.38 | 0.000575 | -0.0576 | CFL | None | 3430 | 0.485 | 3430 | 0.485 | 0.985 | 1.19 | -0.0168
CFLNoneSDGNrsNewCZ06 | Com-Iltg-dWatt-CFL_OSnone | SDG | Nrs | New | CZ06 | 3.43 | 0.000485 | 0 | 3.57 | 0.000616 | -0.0346 | 3.43 | 0.000485 | 0 | 3.57 | 0.000616 | -0.0346 | CFL | None | 3430 | 0.485 | 3430 | 0.485 | 1.04 | 1.27 | -0.0101
CFLNoneSCENrsNewCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | Nrs | New | CZ06 | 3.43 | 0.000485 | 0 | 3.57 | 0.000617 | -0.0343 | 3.43 | 0.000485 | 0 | 3.57 | 0.000617 | -0.0343 | CFL | None | 3430 | 0.485 | 3430 | 0.485 | 1.04 | 1.27 | -0.01
CFLNoneSDGNrsNewCZ07 | Com-Iltg-dWatt-CFL_OSnone | SDG | Nrs | New | CZ07 | 3.43 | 0.000485 | 0 | 3.55 | 0.000616 | -0.0323 | 3.43 | 0.000485 | 0 | 3.55 | 0.000616 | -0.0323 | CFL | None | 3430 | 0.485 | 3430 | 0.485 | 1.03 | 1.27 | -0.00942
CFLNoneSCENrsNewCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | Nrs | New | CZ08 | 3.43 | 0.000485 | 0 | 3.63 | 0.00062 | -0.0327 | 3.43 | 0.000485 | 0 | 3.63 | 0.00062 | -0.0327 | CFL | None | 3430 | 0.485 | 3430 | 0.485 | 1.06 | 1.28 | -0.00953
CFLNoneSDGNrsNewCZ08 | Com-Iltg-dWatt-CFL_OSnone | SDG | Nrs | New | CZ08 | 3.43 | 0.000485 | 0 | 3.63 | 0.000618 | -0.0331 | 3.43 | 0.000485 | 0 | 3.63 | 0.000618 | -0.0331 | CFL | None | 3430 | 0.485 | 3430 | 0.485 | 1.06 | 1.27 | -0.00965
CFLNoneSCENrsNewCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | Nrs | New | CZ09 | 3.43 | 0.000485 | 0 | 3.65 | 0.000642 | -0.033 | 3.43 | 0.000485 | 0 | 3.65 | 0.000642 | -0.033 | CFL | None | 3430 | 0.485 | 3430 | 0.485 | 1.06 | 1.32 | -0.00962
CFLNoneSCENrsNewCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | Nrs | New | CZ10 | 3.43 | 0.000485 | 0 | 3.67 | 0.000644 | -0.0336 | 3.43 | 0.000485 | 0 | 3.67 | 0.000644 | -0.0336 | CFL | None | 3430 | 0.485 | 3430 | 0.485 | 1.07 | 1.33 | -0.0098
CFLNoneSDGNrsNewCZ10 | Com-Iltg-dWatt-CFL_OSnone | SDG | Nrs | New | CZ10 | 3.43 | 0.000485 | 0 | 3.67 | 0.000644 | -0.034 | 3.43 | 0.000485 | 0 | 3.67 | 0.000644 | -0.034 | CFL | None | 3430 | 0.485 | 3430 | 0.485 | 1.07 | 1.33 | -0.00991
CFLNonePGENrsNewCZ11 | Com-Iltg-dWatt-CFL_OSnone | PGE | Nrs | New | CZ11 | 3.43 | 0.000485 | 0 | 3.6 | 0.000614 | -0.0429 | 3.43 | 0.000485 | 0 | 3.6 | 0.000614 | -0.0429 | CFL | None | 3430 | 0.485 | 3430 | 0.485 | 1.05 | 1.27 | -0.0125
CFLNonePGENrsNewCZ12 | Com-Iltg-dWatt-CFL_OSnone | PGE | Nrs | New | CZ12 | 3.43 | 0.000485 | 0 | 3.55 | 0.000616 | -0.0449 | 3.43 | 0.000485 | 0 | 3.55 | 0.000616 | -0.0449 | CFL | None | 3430 | 0.485 | 3430 | 0.485 | 1.03 | 1.27 | -0.0131
CFLNonePGENrsNewCZ13 | Com-Iltg-dWatt-CFL_OSnone | PGE | Nrs | New | CZ13 | 3.43 | 0.000485 | 0 | 3.61 | 0.000615 | -0.0408 | 3.43 | 0.000485 | 0 | 3.61 | 0.000615 | -0.0408 | CFL | None | 3430 | 0.485 | 3430 | 0.485 | 1.05 | 1.27 | -0.0119
CFLNoneSCENrsNewCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | Nrs | New | CZ13 | 3.43 | 0.000485 | 0 | 3.64 | 0.000638 | -0.0398 | 3.43 | 0.000485 | 0 | 3.64 | 0.000638 | -0.0398 | CFL | None | 3430 | 0.485 | 3430 | 0.485 | 1.06 | 1.32 | -0.0116
CFLNoneSCENrsNewCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | Nrs | New | CZ14 | 3.43 | 0.000485 | 0 | 3.64 | 0.000628 | -0.0415 | 3.43 | 0.000485 | 0 | 3.64 | 0.000628 | -0.0415 | CFL | None | 3430 | 0.485 | 3430 | 0.485 | 1.06 | 1.29 | -0.0121
CFLNoneSDGNrsNewCZ14 | Com-Iltg-dWatt-CFL_OSnone | SDG | Nrs | New | CZ14 | 3.43 | 0.000485 | 0 | 3.64 | 0.000625 | -0.0418 | 3.43 | 0.000485 | 0 | 3.64 | 0.000625 | -0.0418 | CFL | None | 3430 | 0.485 | 3430 | 0.485 | 1.06 | 1.29 | -0.0122
CFLNoneSDGNrsNewCZ15 | Com-Iltg-dWatt-CFL_OSnone | SDG | Nrs | New | CZ15 | 3.43 | 0.000485 | 0 | 3.94 | 0.000643 | -0.0163 | 3.43 | 0.000485 | 0 | 3.94 | 0.000643 | -0.0163 | CFL | None | 3430 | 0.485 | 3430 | 0.485 | 1.15 | 1.33 | -0.00475
CFLNoneSCENrsNewCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | Nrs | New | CZ15 | 3.43 | 0.000485 | 0 | 3.94 | 0.000645 | -0.0161 | 3.43 | 0.000485 | 0 | 3.94 | 0.000645 | -0.0161 | CFL | None | 3430 | 0.485 | 3430 | 0.485 | 1.15 | 1.33 | -0.00469
CFLNonePGENrsNewCZ16 | Com-Iltg-dWatt-CFL_OSnone | PGE | Nrs | New | CZ16 | 3.43 | 0.000485 | 0 | 3.38 | 0.000588 | -0.0635 | 3.43 | 0.000485 | 0 | 3.38 | 0.000588 | -0.0635 | CFL | None | 3430 | 0.485 | 3430 | 0.485 | 0.985 | 1.21 | -0.0185
CFLNoneSCENrsNewCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | Nrs | New | CZ16 | 3.43 | 0.000485 | 0 | 3.37 | 0.000606 | -0.0617 | 3.43 | 0.000485 | 0 | 3.37 | 0.000606 | -0.0617 | CFL | None | 3430 | 0.485 | 3430 | 0.485 | 0.983 | 1.25 | -0.018
CFLNoneSCGNrsNewIOU | Com-Iltg-dWatt-CFL_OSnone | SCG | Nrs | New | IOU | 3.43 | 0.000485 | 0 | 3.64 | 0.000627 | -0.0332 | 3.43 | 0.000485 | 0 | 3.64 | 0.000627 | -0.0332 | CFL | None | 3430 | 0.485 | 3430 | 0.485 | 1.06 | 1.29 | -0.00968
CFLNoneSDGNrsNewIOU | Com-Iltg-dWatt-CFL_OSnone | SDG | Nrs | New | IOU | 3.43 | 0.000485 | 0 | 3.57 | 0.00062 | -0.0326 | 3.43 | 0.000485 | 0 | 3.57 | 0.00062 | -0.0326 | CFL | None | 3430 | 0.485 | 3430 | 0.485 | 1.04 | 1.28 | -0.0095
CFLNoneSCENrsNewIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | Nrs | New | IOU | 3.43 | 0.000485 | 0 | 3.65 | 0.000628 | -0.0331 | 3.43 | 0.000485 | 0 | 3.65 | 0.000628 | -0.0331 | CFL | None | 3430 | 0.485 | 3430 | 0.485 | 1.06 | 1.29 | -0.00965
CFLNonePGENrsNewIOU | Com-Iltg-dWatt-CFL_OSnone | PGE | Nrs | New | IOU | 3.43 | 0.000485 | 0 | 3.61 | 0.000633 | -0.0416 | 3.43 | 0.000485 | 0 | 3.61 | 0.000633 | -0.0416 | CFL | None | 3430 | 0.485 | 3430 | 0.485 | 1.05 | 1.31 | -0.0121
CFLNonePGEOfLExCZ01 | Com-Iltg-dWatt-CFL_OSnone | PGE | OfL | Ex | CZ01 | 2.04 | 0.000483 | 0 | 2.18 | 0.000613 | -0.0189 | 2.04 | 0.000483 | 0 | 2.18 | 0.000613 | -0.0189 | CFL | None | 2040 | 0.483 | 2040 | 0.483 | 1.07 | 1.27 | -0.00926
CFLNonePGEOfLExCZ02 | Com-Iltg-dWatt-CFL_OSnone | PGE | OfL | Ex | CZ02 | 2.04 | 0.000483 | 0 | 2.24 | 0.000645 | -0.0141 | 2.04 | 0.000483 | 0 | 2.24 | 0.000645 | -0.0141 | CFL | None | 2040 | 0.483 | 2040 | 0.483 | 1.1 | 1.34 | -0.00691
CFLNonePGEOfLExCZ03 | Com-Iltg-dWatt-CFL_OSnone | PGE | OfL | Ex | CZ03 | 2.04 | 0.000483 | 0 | 2.24 | 0.000628 | -0.013 | 2.04 | 0.000483 | 0 | 2.24 | 0.000628 | -0.013 | CFL | None | 2040 | 0.483 | 2040 | 0.483 | 1.1 | 1.3 | -0.00637
CFLNonePGEOfLExCZ04 | Com-Iltg-dWatt-CFL_OSnone | PGE | OfL | Ex | CZ04 | 2.04 | 0.000483 | 0 | 2.26 | 0.000632 | -0.0118 | 2.04 | 0.000483 | 0 | 2.26 | 0.000632 | -0.0118 | CFL | None | 2040 | 0.483 | 2040 | 0.483 | 1.11 | 1.31 | -0.00578
CFLNonePGEOfLExCZ05 | Com-Iltg-dWatt-CFL_OSnone | PGE | OfL | Ex | CZ05 | 2.04 | 0.000483 | 0 | 2.26 | 0.000625 | -0.0141 | 2.04 | 0.000483 | 0 | 2.26 | 0.000625 | -0.0141 | CFL | None | 2040 | 0.483 | 2040 | 0.483 | 1.11 | 1.29 | -0.00691
CFLNoneSCGOfLExCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCG | OfL | Ex | CZ05 | 2.04 | 0.000483 | 0 | 2.26 | 0.000625 | -0.0141 | 2.04 | 0.000483 | 0 | 2.26 | 0.000625 | -0.0141 | CFL | None | 2040 | 0.483 | 2040 | 0.483 | 1.11 | 1.29 | -0.00691
CFLNoneSCEOfLExCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | OfL | Ex | CZ05 | 2.04 | 0.000483 | 0 | 2.26 | 0.000625 | -0.0141 | 2.04 | 0.000483 | 0 | 2.26 | 0.000625 | -0.0141 | CFL | None | 2040 | 0.483 | 2040 | 0.483 | 1.11 | 1.29 | -0.00691
CFLNoneSDGOfLExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SDG | OfL | Ex | CZ06 | 2.04 | 0.000483 | 0 | 2.34 | 0.000616 | -0.0049 | 2.04 | 0.000483 | 0 | 2.34 | 0.000616 | -0.0049 | CFL | None | 2040 | 0.483 | 2040 | 0.483 | 1.15 | 1.28 | -0.0024
CFLNoneSCGOfLExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCG | OfL | Ex | CZ06 | 2.04 | 0.000483 | 0 | 2.34 | 0.000616 | -0.0049 | 2.04 | 0.000483 | 0 | 2.34 | 0.000616 | -0.0049 | CFL | None | 2040 | 0.483 | 2040 | 0.483 | 1.15 | 1.28 | -0.0024
CFLNoneSCEOfLExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | OfL | Ex | CZ06 | 2.04 | 0.000483 | 0 | 2.34 | 0.000616 | -0.0049 | 2.04 | 0.000483 | 0 | 2.34 | 0.000616 | -0.0049 | CFL | None | 2040 | 0.483 | 2040 | 0.483 | 1.15 | 1.28 | -0.0024
CFLNoneSDGOfLExCZ07 | Com-Iltg-dWatt-CFL_OSnone | SDG | OfL | Ex | CZ07 | 2.04 | 0.000483 | 0 | 2.34 | 0.000608 | -0.0042 | 2.04 | 0.000483 | 0 | 2.34 | 0.000608 | -0.0042 | CFL | None | 2040 | 0.483 | 2040 | 0.483 | 1.15 | 1.26 | -0.00206
CFLNoneSDGOfLExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SDG | OfL | Ex | CZ08 | 2.04 | 0.000483 | 0 | 2.35 | 0.000628 | -0.00475 | 2.04 | 0.000483 | 0 | 2.35 | 0.000628 | -0.00475 | CFL | None | 2040 | 0.483 | 2040 | 0.483 | 1.15 | 1.3 | -0.00233
CFLNoneSCEOfLExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | OfL | Ex | CZ08 | 2.04 | 0.000483 | 0 | 2.35 | 0.000628 | -0.00475 | 2.04 | 0.000483 | 0 | 2.35 | 0.000628 | -0.00475 | CFL | None | 2040 | 0.483 | 2040 | 0.483 | 1.15 | 1.3 | -0.00233
CFLNoneSCGOfLExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCG | OfL | Ex | CZ08 | 2.04 | 0.000483 | 0 | 2.35 | 0.000628 | -0.00475 | 2.04 | 0.000483 | 0 | 2.35 | 0.000628 | -0.00475 | CFL | None | 2040 | 0.483 | 2040 | 0.483 | 1.15 | 1.3 | -0.00233
CFLNoneSCGOfLExCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCG | OfL | Ex | CZ09 | 2.04 | 0.000483 | 0 | 2.36 | 0.000656 | -0.0104 | 2.04 | 0.000483 | 0 | 2.36 | 0.000656 | -0.0104 | CFL | None | 2040 | 0.483 | 2040 | 0.483 | 1.16 | 1.36 | -0.0051
CFLNoneSCEOfLExCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | OfL | Ex | CZ09 | 2.04 | 0.000483 | 0 | 2.36 | 0.000656 | -0.0104 | 2.04 | 0.000483 | 0 | 2.36 | 0.000656 | -0.0104 | CFL | None | 2040 | 0.483 | 2040 | 0.483 | 1.16 | 1.36 | -0.0051
CFLNoneSCGOfLExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCG | OfL | Ex | CZ10 | 2.04 | 0.000483 | 0 | 2.35 | 0.000634 | -0.00543 | 2.04 | 0.000483 | 0 | 2.35 | 0.000634 | -0.00543 | CFL | None | 2040 | 0.483 | 2040 | 0.483 | 1.15 | 1.31 | -0.00266
CFLNoneSDGOfLExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SDG | OfL | Ex | CZ10 | 2.04 | 0.000483 | 0 | 2.35 | 0.000634 | -0.00543 | 2.04 | 0.000483 | 0 | 2.35 | 0.000634 | -0.00543 | CFL | None | 2040 | 0.483 | 2040 | 0.483 | 1.15 | 1.31 | -0.00266
CFLNoneSCEOfLExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | OfL | Ex | CZ10 | 2.04 | 0.000483 | 0 | 2.35 | 0.000634 | -0.00543 | 2.04 | 0.000483 | 0 | 2.35 | 0.000634 | -0.00543 | CFL | None | 2040 | 0.483 | 2040 | 0.483 | 1.15 | 1.31 | -0.00266
CFLNonePGEOfLExCZ11 | Com-Iltg-dWatt-CFL_OSnone | PGE | OfL | Ex | CZ11 | 2.04 | 0.000483 | 0 | 2.29 | 0.000644 | -0.0136 | 2.04 | 0.000483 | 0 | 2.29 | 0.000644 | -0.0136 | CFL | None | 2040 | 0.483 | 2040 | 0.483 | 1.12 | 1.33 | -0.00667
CFLNonePGEOfLExCZ12 | Com-Iltg-dWatt-CFL_OSnone | PGE | OfL | Ex | CZ12 | 2.04 | 0.000483 | 0 | 2.26 | 0.000639 | -0.013 | 2.04 | 0.000483 | 0 | 2.26 | 0.000639 | -0.013 | CFL | None | 2040 | 0.483 | 2040 | 0.483 | 1.11 | 1.32 | -0.00637
CFLNonePGEOfLExCZ13 | Com-Iltg-dWatt-CFL_OSnone | PGE | OfL | Ex | CZ13 | 2.04 | 0.000483 | 0 | 2.35 | 0.000639 | -0.0123 | 2.04 | 0.000483 | 0 | 2.35 | 0.000639 | -0.0123 | CFL | None | 2040 | 0.483 | 2040 | 0.483 | 1.15 | 1.32 | -0.00603
CFLNoneSCGOfLExCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCG | OfL | Ex | CZ13 | 2.04 | 0.000483 | 0 | 2.35 | 0.000639 | -0.0123 | 2.04 | 0.000483 | 0 | 2.35 | 0.000639 | -0.0123 | CFL | None | 2040 | 0.483 | 2040 | 0.483 | 1.15 | 1.32 | -0.00603
CFLNoneSCEOfLExCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | OfL | Ex | CZ13 | 2.04 | 0.000483 | 0 | 2.35 | 0.000639 | -0.0123 | 2.04 | 0.000483 | 0 | 2.35 | 0.000639 | -0.0123 | CFL | None | 2040 | 0.483 | 2040 | 0.483 | 1.15 | 1.32 | -0.00603
CFLNoneSDGOfLExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SDG | OfL | Ex | CZ14 | 2.04 | 0.000483 | 0 | 2.31 | 0.000624 | -0.00749 | 2.04 | 0.000483 | 0 | 2.31 | 0.000624 | -0.00749 | CFL | None | 2040 | 0.483 | 2040 | 0.483 | 1.13 | 1.29 | -0.00367
CFLNoneSCGOfLExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCG | OfL | Ex | CZ14 | 2.04 | 0.000483 | 0 | 2.31 | 0.000624 | -0.00749 | 2.04 | 0.000483 | 0 | 2.31 | 0.000624 | -0.00749 | CFL | None | 2040 | 0.483 | 2040 | 0.483 | 1.13 | 1.29 | -0.00367
CFLNoneSCEOfLExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | OfL | Ex | CZ14 | 2.04 | 0.000483 | 0 | 2.31 | 0.000624 | -0.00749 | 2.04 | 0.000483 | 0 | 2.31 | 0.000624 | -0.00749 | CFL | None | 2040 | 0.483 | 2040 | 0.483 | 1.13 | 1.29 | -0.00367
CFLNoneSCGOfLExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCG | OfL | Ex | CZ15 | 2.04 | 0.000483 | 0 | 2.49 | 0.000636 | -0.00314 | 2.04 | 0.000483 | 0 | 2.49 | 0.000636 | -0.00314 | CFL | None | 2040 | 0.483 | 2040 | 0.483 | 1.22 | 1.32 | -0.00154
CFLNoneSCEOfLExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | OfL | Ex | CZ15 | 2.04 | 0.000483 | 0 | 2.49 | 0.000636 | -0.00314 | 2.04 | 0.000483 | 0 | 2.49 | 0.000636 | -0.00314 | CFL | None | 2040 | 0.483 | 2040 | 0.483 | 1.22 | 1.32 | -0.00154
CFLNoneSDGOfLExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SDG | OfL | Ex | CZ15 | 2.04 | 0.000483 | 0 | 2.49 | 0.000636 | -0.00314 | 2.04 | 0.000483 | 0 | 2.49 | 0.000636 | -0.00314 | CFL | None | 2040 | 0.483 | 2040 | 0.483 | 1.22 | 1.32 | -0.00154
CFLNonePGEOfLExCZ16 | Com-Iltg-dWatt-CFL_OSnone | PGE | OfL | Ex | CZ16 | 2.04 | 0.000483 | 0 | 2.16 | 0.000613 | -0.0216 | 2.04 | 0.000483 | 0 | 2.16 | 0.000613 | -0.0216 | CFL | None | 2040 | 0.483 | 2040 | 0.483 | 1.06 | 1.27 | -0.0106
CFLNoneSCGOfLExCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCG | OfL | Ex | CZ16 | 2.04 | 0.000483 | 0 | 2.16 | 0.000613 | -0.0216 | 2.04 | 0.000483 | 0 | 2.16 | 0.000613 | -0.0216 | CFL | None | 2040 | 0.483 | 2040 | 0.483 | 1.06 | 1.27 | -0.0106
CFLNoneSCEOfLExCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | OfL | Ex | CZ16 | 2.04 | 0.000483 | 0 | 2.16 | 0.000613 | -0.0216 | 2.04 | 0.000483 | 0 | 2.16 | 0.000613 | -0.0216 | CFL | None | 2040 | 0.483 | 2040 | 0.483 | 1.06 | 1.27 | -0.0106
CFLNonePGEOfLExIOU | Com-Iltg-dWatt-CFL_OSnone | PGE | OfL | Ex | IOU | 2.04 | 0.000483 | 0 | 2.25 | 0.000632 | -0.0128 | 2.04 | 0.000483 | 0 | 2.25 | 0.000632 | -0.0128 | CFL | None | 2040 | 0.483 | 2040 | 0.483 | 1.1 | 1.31 | -0.00627
CFLNoneSDGOfLExIOU | Com-Iltg-dWatt-CFL_OSnone | SDG | OfL | Ex | IOU | 2.04 | 0.000483 | 0 | 2.34 | 0.000613 | -0.00445 | 2.04 | 0.000483 | 0 | 2.34 | 0.000613 | -0.00445 | CFL | None | 2040 | 0.483 | 2040 | 0.483 | 1.15 | 1.27 | -0.00218
CFLNoneSCGOfLExIOU | Com-Iltg-dWatt-CFL_OSnone | SCG | OfL | Ex | IOU | 2.04 | 0.000483 | 0 | 2.35 | 0.000637 | -0.00717 | 2.04 | 0.000483 | 0 | 2.35 | 0.000637 | -0.00717 | CFL | None | 2040 | 0.483 | 2040 | 0.483 | 1.15 | 1.32 | -0.00351
CFLNoneSCEOfLExIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | OfL | Ex | IOU | 2.04 | 0.000483 | 0 | 2.35 | 0.000631 | -0.00631 | 2.04 | 0.000483 | 0 | 2.35 | 0.000631 | -0.00631 | CFL | None | 2040 | 0.483 | 2040 | 0.483 | 1.15 | 1.31 | -0.00309
CFLNonePGEOfLNewCZ01 | Com-Iltg-dWatt-CFL_OSnone | PGE | OfL | New | CZ01 | 2.04 | 0.000483 | 0 | 2.16 | 0.000588 | -0.0123 | 2.04 | 0.000483 | 0 | 2.16 | 0.000588 | -0.0123 | CFL | None | 2040 | 0.483 | 2040 | 0.483 | 1.06 | 1.22 | -0.00603
CFLNonePGEOfLNewCZ02 | Com-Iltg-dWatt-CFL_OSnone | PGE | OfL | New | CZ02 | 2.04 | 0.000483 | 0 | 2.25 | 0.000598 | -0.0082 | 2.04 | 0.000483 | 0 | 2.25 | 0.000598 | -0.0082 | CFL | None | 2040 | 0.483 | 2040 | 0.483 | 1.1 | 1.24 | -0.00402
CFLNonePGEOfLNewCZ03 | Com-Iltg-dWatt-CFL_OSnone | PGE | OfL | New | CZ03 | 2.04 | 0.000483 | 0 | 2.24 | 0.000597 | -0.0081 | 2.04 | 0.000483 | 0 | 2.24 | 0.000597 | -0.0081 | CFL | None | 2040 | 0.483 | 2040 | 0.483 | 1.1 | 1.24 | -0.00397
CFLNonePGEOfLNewCZ04 | Com-Iltg-dWatt-CFL_OSnone | PGE | OfL | New | CZ04 | 2.04 | 0.000483 | 0 | 2.27 | 0.000599 | -0.00747 | 2.04 | 0.000483 | 0 | 2.27 | 0.000599 | -0.00747 | CFL | None | 2040 | 0.483 | 2040 | 0.483 | 1.11 | 1.24 | -0.00366
CFLNoneSCEOfLNewCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | OfL | New | CZ05 | 2.04 | 0.000483 | 0 | 2.25 | 0.000599 | -0.00663 | 2.04 | 0.000483 | 0 | 2.25 | 0.000599 | -0.00663 | CFL | None | 2040 | 0.483 | 2040 | 0.483 | 1.1 | 1.24 | -0.00325
CFLNonePGEOfLNewCZ05 | Com-Iltg-dWatt-CFL_OSnone | PGE | OfL | New | CZ05 | 2.04 | 0.000483 | 0 | 2.23 | 0.000584 | -0.00645 | 2.04 | 0.000483 | 0 | 2.23 | 0.000584 | -0.00645 | CFL | None | 2040 | 0.483 | 2040 | 0.483 | 1.09 | 1.21 | -0.00316
CFLNoneSDGOfLNewCZ06 | Com-Iltg-dWatt-CFL_OSnone | SDG | OfL | New | CZ06 | 2.04 | 0.000483 | 0 | 2.34 | 0.000601 | -0.00333 | 2.04 | 0.000483 | 0 | 2.34 | 0.000601 | -0.00333 | CFL | None | 2040 | 0.483 | 2040 | 0.483 | 1.15 | 1.24 | -0.00163
CFLNoneSCEOfLNewCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | OfL | New | CZ06 | 2.04 | 0.000483 | 0 | 2.35 | 0.000609 | -0.00443 | 2.04 | 0.000483 | 0 | 2.35 | 0.000609 | -0.00443 | CFL | None | 2040 | 0.483 | 2040 | 0.483 | 1.15 | 1.26 | -0.00217
CFLNoneSDGOfLNewCZ07 | Com-Iltg-dWatt-CFL_OSnone | SDG | OfL | New | CZ07 | 2.04 | 0.000483 | 0 | 2.34 | 0.000594 | -0.00269 | 2.04 | 0.000483 | 0 | 2.34 | 0.000594 | -0.00269 | CFL | None | 2040 | 0.483 | 2040 | 0.483 | 1.15 | 1.23 | -0.00132
CFLNoneSCEOfLNewCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | OfL | New | CZ08 | 2.04 | 0.000483 | 0 | 2.35 | 0.000617 | -0.00386 | 2.04 | 0.000483 | 0 | 2.35 | 0.000617 | -0.00386 | CFL | None | 2040 | 0.483 | 2040 | 0.483 | 1.15 | 1.28 | -0.00189
CFLNoneSDGOfLNewCZ08 | Com-Iltg-dWatt-CFL_OSnone | SDG | OfL | New | CZ08 | 2.04 | 0.000483 | 0 | 2.35 | 0.00061 | -0.00275 | 2.04 | 0.000483 | 0 | 2.35 | 0.00061 | -0.00275 | CFL | None | 2040 | 0.483 | 2040 | 0.483 | 1.15 | 1.26 | -0.00135
CFLNoneSCEOfLNewCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | OfL | New | CZ09 | 2.04 | 0.000483 | 0 | 2.35 | 0.000635 | -0.00539 | 2.04 | 0.000483 | 0 | 2.35 | 0.000635 | -0.00539 | CFL | None | 2040 | 0.483 | 2040 | 0.483 | 1.15 | 1.31 | -0.00264
CFLNoneSDGOfLNewCZ10 | Com-Iltg-dWatt-CFL_OSnone | SDG | OfL | New | CZ10 | 2.04 | 0.000483 | 0 | 2.36 | 0.000628 | -0.00339 | 2.04 | 0.000483 | 0 | 2.36 | 0.000628 | -0.00339 | CFL | None | 2040 | 0.483 | 2040 | 0.483 | 1.16 | 1.3 | -0.00166
CFLNoneSCEOfLNewCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | OfL | New | CZ10 | 2.04 | 0.000483 | 0 | 2.36 | 0.000638 | -0.00467 | 2.04 | 0.000483 | 0 | 2.36 | 0.000638 | -0.00467 | CFL | None | 2040 | 0.483 | 2040 | 0.483 | 1.16 | 1.32 | -0.00229
CFLNonePGEOfLNewCZ11 | Com-Iltg-dWatt-CFL_OSnone | PGE | OfL | New | CZ11 | 2.04 | 0.000483 | 0 | 2.28 | 0.000604 | -0.00706 | 2.04 | 0.000483 | 0 | 2.28 | 0.000604 | -0.00706 | CFL | None | 2040 | 0.483 | 2040 | 0.483 | 1.12 | 1.25 | -0.00346
CFLNonePGEOfLNewCZ12 | Com-Iltg-dWatt-CFL_OSnone | PGE | OfL | New | CZ12 | 2.04 | 0.000483 | 0 | 2.27 | 0.000602 | -0.00794 | 2.04 | 0.000483 | 0 | 2.27 | 0.000602 | -0.00794 | CFL | None | 2040 | 0.483 | 2040 | 0.483 | 1.11 | 1.25 | -0.00389
CFLNoneSCEOfLNewCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | OfL | New | CZ13 | 2.04 | 0.000483 | 0 | 2.32 | 0.000621 | -0.00696 | 2.04 | 0.000483 | 0 | 2.32 | 0.000621 | -0.00696 | CFL | None | 2040 | 0.483 | 2040 | 0.483 | 1.14 | 1.29 | -0.00341
CFLNonePGEOfLNewCZ13 | Com-Iltg-dWatt-CFL_OSnone | PGE | OfL | New | CZ13 | 2.04 | 0.000483 | 0 | 2.29 | 0.000603 | -0.00692 | 2.04 | 0.000483 | 0 | 2.29 | 0.000603 | -0.00692 | CFL | None | 2040 | 0.483 | 2040 | 0.483 | 1.12 | 1.25 | -0.00339
CFLNoneSDGOfLNewCZ14 | Com-Iltg-dWatt-CFL_OSnone | SDG | OfL | New | CZ14 | 2.04 | 0.000483 | 0 | 2.32 | 0.000639 | -0.00532 | 2.04 | 0.000483 | 0 | 2.32 | 0.000639 | -0.00532 | CFL | None | 2040 | 0.483 | 2040 | 0.483 | 1.14 | 1.32 | -0.00261
CFLNoneSCEOfLNewCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | OfL | New | CZ14 | 2.04 | 0.000483 | 0 | 2.33 | 0.000644 | -0.00614 | 2.04 | 0.000483 | 0 | 2.33 | 0.000644 | -0.00614 | CFL | None | 2040 | 0.483 | 2040 | 0.483 | 1.14 | 1.33 | -0.00301
CFLNoneSCEOfLNewCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | OfL | New | CZ15 | 2.04 | 0.000483 | 0 | 2.45 | 0.000632 | -0.00226 | 2.04 | 0.000483 | 0 | 2.45 | 0.000632 | -0.00226 | CFL | None | 2040 | 0.483 | 2040 | 0.483 | 1.2 | 1.31 | -0.00111
CFLNoneSDGOfLNewCZ15 | Com-Iltg-dWatt-CFL_OSnone | SDG | OfL | New | CZ15 | 2.04 | 0.000483 | 0 | 2.45 | 0.000625 | -0.0016 | 2.04 | 0.000483 | 0 | 2.45 | 0.000625 | -0.0016 | CFL | None | 2040 | 0.483 | 2040 | 0.483 | 1.2 | 1.29 | -0.000784
CFLNoneSCEOfLNewCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | OfL | New | CZ16 | 2.04 | 0.000483 | 0 | 2.19 | 0.000606 | -0.017 | 2.04 | 0.000483 | 0 | 2.19 | 0.000606 | -0.017 | CFL | None | 2040 | 0.483 | 2040 | 0.483 | 1.07 | 1.25 | -0.00833
CFLNonePGEOfLNewCZ16 | Com-Iltg-dWatt-CFL_OSnone | PGE | OfL | New | CZ16 | 2.04 | 0.000483 | 0 | 2.18 | 0.000592 | -0.0173 | 2.04 | 0.000483 | 0 | 2.18 | 0.000592 | -0.0173 | CFL | None | 2040 | 0.483 | 2040 | 0.483 | 1.07 | 1.23 | -0.00848
CFLNoneSDGOfLNewIOU | Com-Iltg-dWatt-CFL_OSnone | SDG | OfL | New | IOU | 2.04 | 0.000483 | 0 | 2.34 | 0.000601 | -0.00284 | 2.04 | 0.000483 | 0 | 2.34 | 0.000601 | -0.00284 | CFL | None | 2040 | 0.483 | 2040 | 0.483 | 1.15 | 1.24 | -0.00139
CFLNoneSCEOfLNewIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | OfL | New | IOU | 2.04 | 0.000483 | 0 | 2.36 | 0.000615 | -0.00312 | 2.04 | 0.000483 | 0 | 2.36 | 0.000615 | -0.00312 | CFL | None | 2040 | 0.483 | 2040 | 0.483 | 1.16 | 1.27 | -0.00153
CFLNonePGEOfLNewIOU | Com-Iltg-dWatt-CFL_OSnone | PGE | OfL | New | IOU | 2.04 | 0.000483 | 0 | 2.31 | 0.000617 | -0.00712 | 2.04 | 0.000483 | 0 | 2.31 | 0.000617 | -0.00712 | CFL | None | 2040 | 0.483 | 2040 | 0.483 | 1.13 | 1.28 | -0.00349
CFLNoneSCGOfLNewIOU | Com-Iltg-dWatt-CFL_OSnone | SCG | OfL | New | IOU | 2.04 | 0.000483 | 0 | 2.35 | 0.000613 | -0.00308 | 2.04 | 0.000483 | 0 | 2.35 | 0.000613 | -0.00308 | CFL | None | 2040 | 0.483 | 2040 | 0.483 | 1.15 | 1.27 | -0.00151
CFLNonePGEOfSExCZ01 | Com-Iltg-dWatt-CFL_OSnone | PGE | OfS | Ex | CZ01 | 1.52 | 0.000456 | 0 | 1.53 | 0.000541 | -0.00948 | 1.52 | 0.000456 | 0 | 1.53 | 0.000541 | -0.00948 | CFL | None | 1520 | 0.456 | 1520 | 0.456 | 1.01 | 1.19 | -0.00624
CFLNonePGEOfSExCZ02 | Com-Iltg-dWatt-CFL_OSnone | PGE | OfS | Ex | CZ02 | 1.52 | 0.000456 | 0 | 1.59 | 0.000557 | -0.00616 | 1.52 | 0.000456 | 0 | 1.59 | 0.000557 | -0.00616 | CFL | None | 1520 | 0.456 | 1520 | 0.456 | 1.05 | 1.22 | -0.00405
CFLNonePGEOfSExCZ03 | Com-Iltg-dWatt-CFL_OSnone | PGE | OfS | Ex | CZ03 | 1.52 | 0.000456 | 0 | 1.59 | 0.000556 | -0.00524 | 1.52 | 0.000456 | 0 | 1.59 | 0.000556 | -0.00524 | CFL | None | 1520 | 0.456 | 1520 | 0.456 | 1.05 | 1.22 | -0.00345
CFLNonePGEOfSExCZ04 | Com-Iltg-dWatt-CFL_OSnone | PGE | OfS | Ex | CZ04 | 1.52 | 0.000456 | 0 | 1.62 | 0.000559 | -0.00421 | 1.52 | 0.000456 | 0 | 1.62 | 0.000559 | -0.00421 | CFL | None | 1520 | 0.456 | 1520 | 0.456 | 1.07 | 1.23 | -0.00277
CFLNoneSCGOfSExCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCG | OfS | Ex | CZ05 | 1.52 | 0.000456 | 0 | 1.65 | 0.000573 | -0.00476 | 1.52 | 0.000456 | 0 | 1.65 | 0.000573 | -0.00476 | CFL | None | 1520 | 0.456 | 1520 | 0.456 | 1.09 | 1.26 | -0.00313
CFLNonePGEOfSExCZ05 | Com-Iltg-dWatt-CFL_OSnone | PGE | OfS | Ex | CZ05 | 1.52 | 0.000456 | 0 | 1.65 | 0.000573 | -0.00476 | 1.52 | 0.000456 | 0 | 1.65 | 0.000573 | -0.00476 | CFL | None | 1520 | 0.456 | 1520 | 0.456 | 1.09 | 1.26 | -0.00313
CFLNoneSCEOfSExCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | OfS | Ex | CZ05 | 1.52 | 0.000456 | 0 | 1.65 | 0.000573 | -0.00476 | 1.52 | 0.000456 | 0 | 1.65 | 0.000573 | -0.00476 | CFL | None | 1520 | 0.456 | 1520 | 0.456 | 1.09 | 1.26 | -0.00313
CFLNoneSDGOfSExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SDG | OfS | Ex | CZ06 | 1.52 | 0.000456 | 0 | 1.74 | 0.000575 | -0.00123 | 1.52 | 0.000456 | 0 | 1.74 | 0.000575 | -0.00123 | CFL | None | 1520 | 0.456 | 1520 | 0.456 | 1.14 | 1.26 | -0.000809
CFLNoneSCGOfSExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCG | OfS | Ex | CZ06 | 1.52 | 0.000456 | 0 | 1.74 | 0.000575 | -0.00123 | 1.52 | 0.000456 | 0 | 1.74 | 0.000575 | -0.00123 | CFL | None | 1520 | 0.456 | 1520 | 0.456 | 1.14 | 1.26 | -0.000809
CFLNoneSCEOfSExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | OfS | Ex | CZ06 | 1.52 | 0.000456 | 0 | 1.74 | 0.000575 | -0.00123 | 1.52 | 0.000456 | 0 | 1.74 | 0.000575 | -0.00123 | CFL | None | 1520 | 0.456 | 1520 | 0.456 | 1.14 | 1.26 | -0.000809
CFLNoneSDGOfSExCZ07 | Com-Iltg-dWatt-CFL_OSnone | SDG | OfS | Ex | CZ07 | 1.52 | 0.000456 | 0 | 1.74 | 0.000568 | -0.000333 | 1.52 | 0.000456 | 0 | 1.74 | 0.000568 | -0.000333 | CFL | None | 1520 | 0.456 | 1520 | 0.456 | 1.14 | 1.25 | -0.000219
CFLNoneSCEOfSExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | OfS | Ex | CZ08 | 1.52 | 0.000456 | 0 | 1.75 | 0.000578 | -0.00104 | 1.52 | 0.000456 | 0 | 1.75 | 0.000578 | -0.00104 | CFL | None | 1520 | 0.456 | 1520 | 0.456 | 1.15 | 1.27 | -0.000684
CFLNoneSCGOfSExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCG | OfS | Ex | CZ08 | 1.52 | 0.000456 | 0 | 1.75 | 0.000578 | -0.00104 | 1.52 | 0.000456 | 0 | 1.75 | 0.000578 | -0.00104 | CFL | None | 1520 | 0.456 | 1520 | 0.456 | 1.15 | 1.27 | -0.000684
CFLNoneSDGOfSExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SDG | OfS | Ex | CZ08 | 1.52 | 0.000456 | 0 | 1.75 | 0.000578 | -0.00104 | 1.52 | 0.000456 | 0 | 1.75 | 0.000578 | -0.00104 | CFL | None | 1520 | 0.456 | 1520 | 0.456 | 1.15 | 1.27 | -0.000684
CFLNoneSCGOfSExCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCG | OfS | Ex | CZ09 | 1.52 | 0.000456 | 0 | 1.73 | 0.00059 | -0.00258 | 1.52 | 0.000456 | 0 | 1.73 | 0.00059 | -0.00258 | CFL | None | 1520 | 0.456 | 1520 | 0.456 | 1.14 | 1.29 | -0.0017
CFLNoneSCEOfSExCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | OfS | Ex | CZ09 | 1.52 | 0.000456 | 0 | 1.73 | 0.00059 | -0.00258 | 1.52 | 0.000456 | 0 | 1.73 | 0.00059 | -0.00258 | CFL | None | 1520 | 0.456 | 1520 | 0.456 | 1.14 | 1.29 | -0.0017
CFLNoneSCEOfSExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | OfS | Ex | CZ10 | 1.52 | 0.000456 | 0 | 1.74 | 0.00058 | -0.00158 | 1.52 | 0.000456 | 0 | 1.74 | 0.00058 | -0.00158 | CFL | None | 1520 | 0.456 | 1520 | 0.456 | 1.14 | 1.27 | -0.00104
CFLNoneSCGOfSExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCG | OfS | Ex | CZ10 | 1.52 | 0.000456 | 0 | 1.74 | 0.00058 | -0.00158 | 1.52 | 0.000456 | 0 | 1.74 | 0.00058 | -0.00158 | CFL | None | 1520 | 0.456 | 1520 | 0.456 | 1.14 | 1.27 | -0.00104
CFLNoneSDGOfSExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SDG | OfS | Ex | CZ10 | 1.52 | 0.000456 | 0 | 1.74 | 0.00058 | -0.00158 | 1.52 | 0.000456 | 0 | 1.74 | 0.00058 | -0.00158 | CFL | None | 1520 | 0.456 | 1520 | 0.456 | 1.14 | 1.27 | -0.00104
CFLNonePGEOfSExCZ11 | Com-Iltg-dWatt-CFL_OSnone | PGE | OfS | Ex | CZ11 | 1.52 | 0.000456 | 0 | 1.62 | 0.000558 | -0.00646 | 1.52 | 0.000456 | 0 | 1.62 | 0.000558 | -0.00646 | CFL | None | 1520 | 0.456 | 1520 | 0.456 | 1.07 | 1.22 | -0.00425
CFLNonePGEOfSExCZ12 | Com-Iltg-dWatt-CFL_OSnone | PGE | OfS | Ex | CZ12 | 1.52 | 0.000456 | 0 | 1.61 | 0.000559 | -0.00628 | 1.52 | 0.000456 | 0 | 1.61 | 0.000559 | -0.00628 | CFL | None | 1520 | 0.456 | 1520 | 0.456 | 1.06 | 1.23 | -0.00413
CFLNonePGEOfSExCZ13 | Com-Iltg-dWatt-CFL_OSnone | PGE | OfS | Ex | CZ13 | 1.52 | 0.000456 | 0 | 1.68 | 0.000581 | -0.0057 | 1.52 | 0.000456 | 0 | 1.68 | 0.000581 | -0.0057 | CFL | None | 1520 | 0.456 | 1520 | 0.456 | 1.11 | 1.27 | -0.00375
CFLNoneSCGOfSExCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCG | OfS | Ex | CZ13 | 1.52 | 0.000456 | 0 | 1.68 | 0.000581 | -0.0057 | 1.52 | 0.000456 | 0 | 1.68 | 0.000581 | -0.0057 | CFL | None | 1520 | 0.456 | 1520 | 0.456 | 1.11 | 1.27 | -0.00375
CFLNoneSCEOfSExCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | OfS | Ex | CZ13 | 1.52 | 0.000456 | 0 | 1.68 | 0.000581 | -0.0057 | 1.52 | 0.000456 | 0 | 1.68 | 0.000581 | -0.0057 | CFL | None | 1520 | 0.456 | 1520 | 0.456 | 1.11 | 1.27 | -0.00375
CFLNoneSCEOfSExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | OfS | Ex | CZ14 | 1.52 | 0.000456 | 0 | 1.7 | 0.000587 | -0.00385 | 1.52 | 0.000456 | 0 | 1.7 | 0.000587 | -0.00385 | CFL | None | 1520 | 0.456 | 1520 | 0.456 | 1.12 | 1.29 | -0.00253
CFLNoneSCGOfSExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCG | OfS | Ex | CZ14 | 1.52 | 0.000456 | 0 | 1.7 | 0.000587 | -0.00385 | 1.52 | 0.000456 | 0 | 1.7 | 0.000587 | -0.00385 | CFL | None | 1520 | 0.456 | 1520 | 0.456 | 1.12 | 1.29 | -0.00253
CFLNoneSDGOfSExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SDG | OfS | Ex | CZ14 | 1.52 | 0.000456 | 0 | 1.7 | 0.000587 | -0.00385 | 1.52 | 0.000456 | 0 | 1.7 | 0.000587 | -0.00385 | CFL | None | 1520 | 0.456 | 1520 | 0.456 | 1.12 | 1.29 | -0.00253
CFLNoneSCEOfSExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | OfS | Ex | CZ15 | 1.52 | 0.000456 | 0 | 1.86 | 0.000575 | -0.000333 | 1.52 | 0.000456 | 0 | 1.86 | 0.000575 | -0.000333 | CFL | None | 1520 | 0.456 | 1520 | 0.456 | 1.22 | 1.26 | -0.000219
CFLNoneSDGOfSExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SDG | OfS | Ex | CZ15 | 1.52 | 0.000456 | 0 | 1.86 | 0.000575 | -0.000333 | 1.52 | 0.000456 | 0 | 1.86 | 0.000575 | -0.000333 | CFL | None | 1520 | 0.456 | 1520 | 0.456 | 1.22 | 1.26 | -0.000219
CFLNoneSCGOfSExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCG | OfS | Ex | CZ15 | 1.52 | 0.000456 | 0 | 1.86 | 0.000575 | -0.000333 | 1.52 | 0.000456 | 0 | 1.86 | 0.000575 | -0.000333 | CFL | None | 1520 | 0.456 | 1520 | 0.456 | 1.22 | 1.26 | -0.000219
CFLNoneSCEOfSExCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | OfS | Ex | CZ16 | 1.52 | 0.000456 | 0 | 1.53 | 0.00057 | -0.0108 | 1.52 | 0.000456 | 0 | 1.53 | 0.00057 | -0.0108 | CFL | None | 1520 | 0.456 | 1520 | 0.456 | 1.01 | 1.25 | -0.00711
CFLNonePGEOfSExCZ16 | Com-Iltg-dWatt-CFL_OSnone | PGE | OfS | Ex | CZ16 | 1.52 | 0.000456 | 0 | 1.53 | 0.00057 | -0.0108 | 1.52 | 0.000456 | 0 | 1.53 | 0.00057 | -0.0108 | CFL | None | 1520 | 0.456 | 1520 | 0.456 | 1.01 | 1.25 | -0.00711
CFLNoneSCGOfSExCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCG | OfS | Ex | CZ16 | 1.52 | 0.000456 | 0 | 1.53 | 0.00057 | -0.0108 | 1.52 | 0.000456 | 0 | 1.53 | 0.00057 | -0.0108 | CFL | None | 1520 | 0.456 | 1520 | 0.456 | 1.01 | 1.25 | -0.00711
CFLNonePGEOfSExIOU | Com-Iltg-dWatt-CFL_OSnone | PGE | OfS | Ex | IOU | 1.52 | 0.000456 | 0 | 1.62 | 0.000563 | -0.0056 | 1.52 | 0.000456 | 0 | 1.62 | 0.000563 | -0.0056 | CFL | None | 1520 | 0.456 | 1520 | 0.456 | 1.07 | 1.23 | -0.00368
CFLNoneSCGOfSExIOU | Com-Iltg-dWatt-CFL_OSnone | SCG | OfS | Ex | IOU | 1.52 | 0.000456 | 0 | 1.74 | 0.000581 | -0.00193 | 1.52 | 0.000456 | 0 | 1.74 | 0.000581 | -0.00193 | CFL | None | 1520 | 0.456 | 1520 | 0.456 | 1.14 | 1.27 | -0.00127
CFLNoneSDGOfSExIOU | Com-Iltg-dWatt-CFL_OSnone | SDG | OfS | Ex | IOU | 1.52 | 0.000456 | 0 | 1.74 | 0.000571 | -0.000598 | 1.52 | 0.000456 | 0 | 1.74 | 0.000571 | -0.000598 | CFL | None | 1520 | 0.456 | 1520 | 0.456 | 1.14 | 1.25 | -0.000393
CFLNoneSCEOfSExIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | OfS | Ex | IOU | 1.52 | 0.000456 | 0 | 1.74 | 0.00058 | -0.00185 | 1.52 | 0.000456 | 0 | 1.74 | 0.00058 | -0.00185 | CFL | None | 1520 | 0.456 | 1520 | 0.456 | 1.14 | 1.27 | -0.00122
CFLNonePGEOfSNewCZ01 | Com-Iltg-dWatt-CFL_OSnone | PGE | OfS | New | CZ01 | 1.52 | 0.000456 | 0 | 1.49 | 0.000536 | -0.00879 | 1.52 | 0.000456 | 0 | 1.49 | 0.000536 | -0.00879 | CFL | None | 1520 | 0.456 | 1520 | 0.456 | 0.98 | 1.18 | -0.00578
CFLNonePGEOfSNewCZ02 | Com-Iltg-dWatt-CFL_OSnone | PGE | OfS | New | CZ02 | 1.52 | 0.000456 | 0 | 1.59 | 0.000567 | -0.00473 | 1.52 | 0.000456 | 0 | 1.59 | 0.000567 | -0.00473 | CFL | None | 1520 | 0.456 | 1520 | 0.456 | 1.05 | 1.24 | -0.00311
CFLNonePGEOfSNewCZ03 | Com-Iltg-dWatt-CFL_OSnone | PGE | OfS | New | CZ03 | 1.52 | 0.000456 | 0 | 1.56 | 0.000554 | -0.00515 | 1.52 | 0.000456 | 0 | 1.56 | 0.000554 | -0.00515 | CFL | None | 1520 | 0.456 | 1520 | 0.456 | 1.03 | 1.21 | -0.00339
CFLNonePGEOfSNewCZ04 | Com-Iltg-dWatt-CFL_OSnone | PGE | OfS | New | CZ04 | 1.52 | 0.000456 | 0 | 1.6 | 0.000565 | -0.00377 | 1.52 | 0.000456 | 0 | 1.6 | 0.000565 | -0.00377 | CFL | None | 1520 | 0.456 | 1520 | 0.456 | 1.05 | 1.24 | -0.00248
CFLNonePGEOfSNewCZ05 | Com-Iltg-dWatt-CFL_OSnone | PGE | OfS | New | CZ05 | 1.52 | 0.000456 | 0 | 1.57 | 0.000544 | -0.00409 | 1.52 | 0.000456 | 0 | 1.57 | 0.000544 | -0.00409 | CFL | None | 1520 | 0.456 | 1520 | 0.456 | 1.03 | 1.19 | -0.00269
CFLNoneSCEOfSNewCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | OfS | New | CZ05 | 1.52 | 0.000456 | 0 | 1.59 | 0.000564 | -0.0043 | 1.52 | 0.000456 | 0 | 1.59 | 0.000564 | -0.0043 | CFL | None | 1520 | 0.456 | 1520 | 0.456 | 1.05 | 1.24 | -0.00283
CFLNoneSCEOfSNewCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | OfS | New | CZ06 | 1.52 | 0.000456 | 0 | 1.68 | 0.000572 | -0.00173 | 1.52 | 0.000456 | 0 | 1.68 | 0.000572 | -0.00173 | CFL | None | 1520 | 0.456 | 1520 | 0.456 | 1.11 | 1.25 | -0.00114
CFLNoneSDGOfSNewCZ06 | Com-Iltg-dWatt-CFL_OSnone | SDG | OfS | New | CZ06 | 1.52 | 0.000456 | 0 | 1.67 | 0.000565 | -0.00135 | 1.52 | 0.000456 | 0 | 1.67 | 0.000565 | -0.00135 | CFL | None | 1520 | 0.456 | 1520 | 0.456 | 1.1 | 1.24 | -0.000888
CFLNoneSDGOfSNewCZ07 | Com-Iltg-dWatt-CFL_OSnone | SDG | OfS | New | CZ07 | 1.52 | 0.000456 | 0 | 1.66 | 0.000558 | -0.000315 | 1.52 | 0.000456 | 0 | 1.66 | 0.000558 | -0.000315 | CFL | None | 1520 | 0.456 | 1520 | 0.456 | 1.09 | 1.22 | -0.000207
CFLNoneSCEOfSNewCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | OfS | New | CZ08 | 1.52 | 0.000456 | 0 | 1.69 | 0.000579 | -0.00154 | 1.52 | 0.000456 | 0 | 1.69 | 0.000579 | -0.00154 | CFL | None | 1520 | 0.456 | 1520 | 0.456 | 1.11 | 1.27 | -0.00101
CFLNoneSDGOfSNewCZ08 | Com-Iltg-dWatt-CFL_OSnone | SDG | OfS | New | CZ08 | 1.52 | 0.000456 | 0 | 1.68 | 0.000571 | -0.00114 | 1.52 | 0.000456 | 0 | 1.68 | 0.000571 | -0.00114 | CFL | None | 1520 | 0.456 | 1520 | 0.456 | 1.11 | 1.25 | -0.00075
CFLNoneSCEOfSNewCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | OfS | New | CZ09 | 1.52 | 0.000456 | 0 | 1.68 | 0.000594 | -0.00173 | 1.52 | 0.000456 | 0 | 1.68 | 0.000594 | -0.00173 | CFL | None | 1520 | 0.456 | 1520 | 0.456 | 1.11 | 1.3 | -0.00114
CFLNoneSCEOfSNewCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | OfS | New | CZ10 | 1.52 | 0.000456 | 0 | 1.7 | 0.000601 | -0.00122 | 1.52 | 0.000456 | 0 | 1.7 | 0.000601 | -0.00122 | CFL | None | 1520 | 0.456 | 1520 | 0.456 | 1.12 | 1.32 | -0.000803
CFLNoneSDGOfSNewCZ10 | Com-Iltg-dWatt-CFL_OSnone | SDG | OfS | New | CZ10 | 1.52 | 0.000456 | 0 | 1.69 | 0.000591 | -0.000898 | 1.52 | 0.000456 | 0 | 1.69 | 0.000591 | -0.000898 | CFL | None | 1520 | 0.456 | 1520 | 0.456 | 1.11 | 1.3 | -0.000591
CFLNonePGEOfSNewCZ11 | Com-Iltg-dWatt-CFL_OSnone | PGE | OfS | New | CZ11 | 1.52 | 0.000456 | 0 | 1.62 | 0.000572 | -0.00523 | 1.52 | 0.000456 | 0 | 1.62 | 0.000572 | -0.00523 | CFL | None | 1520 | 0.456 | 1520 | 0.456 | 1.07 | 1.25 | -0.00344
CFLNonePGEOfSNewCZ12 | Com-Iltg-dWatt-CFL_OSnone | PGE | OfS | New | CZ12 | 1.52 | 0.000456 | 0 | 1.61 | 0.00057 | -0.00506 | 1.52 | 0.000456 | 0 | 1.61 | 0.00057 | -0.00506 | CFL | None | 1520 | 0.456 | 1520 | 0.456 | 1.06 | 1.25 | -0.00333
CFLNoneSCEOfSNewCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | OfS | New | CZ13 | 1.52 | 0.000456 | 0 | 1.65 | 0.000591 | -0.00456 | 1.52 | 0.000456 | 0 | 1.65 | 0.000591 | -0.00456 | CFL | None | 1520 | 0.456 | 1520 | 0.456 | 1.09 | 1.3 | -0.003
CFLNonePGEOfSNewCZ13 | Com-Iltg-dWatt-CFL_OSnone | PGE | OfS | New | CZ13 | 1.52 | 0.000456 | 0 | 1.62 | 0.000566 | -0.00482 | 1.52 | 0.000456 | 0 | 1.62 | 0.000566 | -0.00482 | CFL | None | 1520 | 0.456 | 1520 | 0.456 | 1.07 | 1.24 | -0.00317
CFLNoneSCEOfSNewCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | OfS | New | CZ14 | 1.52 | 0.000456 | 0 | 1.66 | 0.000601 | -0.0038 | 1.52 | 0.000456 | 0 | 1.66 | 0.000601 | -0.0038 | CFL | None | 1520 | 0.456 | 1520 | 0.456 | 1.09 | 1.32 | -0.0025
CFLNoneSDGOfSNewCZ14 | Com-Iltg-dWatt-CFL_OSnone | SDG | OfS | New | CZ14 | 1.52 | 0.000456 | 0 | 1.65 | 0.000592 | -0.00344 | 1.52 | 0.000456 | 0 | 1.65 | 0.000592 | -0.00344 | CFL | None | 1520 | 0.456 | 1520 | 0.456 | 1.09 | 1.3 | -0.00226
CFLNoneSCEOfSNewCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | OfS | New | CZ15 | 1.52 | 0.000456 | 0 | 1.78 | 0.000607 | -0.000114 | 1.52 | 0.000456 | 0 | 1.78 | 0.000607 | -0.000114 | CFL | None | 1520 | 0.456 | 1520 | 0.456 | 1.17 | 1.33 | -7.5e-05
CFLNoneSDGOfSNewCZ15 | Com-Iltg-dWatt-CFL_OSnone | SDG | OfS | New | CZ15 | 1.52 | 0.000456 | 0 | 1.77 | 0.000598 | 0 | 1.52 | 0.000456 | 0 | 1.77 | 0.000598 | 0 | CFL | None | 1520 | 0.456 | 1520 | 0.456 | 1.16 | 1.31 | 0
CFLNoneSCEOfSNewCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | OfS | New | CZ16 | 1.52 | 0.000456 | 0 | 1.52 | 0.000572 | -0.0102 | 1.52 | 0.000456 | 0 | 1.52 | 0.000572 | -0.0102 | CFL | None | 1520 | 0.456 | 1520 | 0.456 | 1 | 1.25 | -0.00671
CFLNonePGEOfSNewCZ16 | Com-Iltg-dWatt-CFL_OSnone | PGE | OfS | New | CZ16 | 1.52 | 0.000456 | 0 | 1.51 | 0.000551 | -0.0109 | 1.52 | 0.000456 | 0 | 1.51 | 0.000551 | -0.0109 | CFL | None | 1520 | 0.456 | 1520 | 0.456 | 0.993 | 1.21 | -0.00717
CFLNoneSDGOfSNewIOU | Com-Iltg-dWatt-CFL_OSnone | SDG | OfS | New | IOU | 1.52 | 0.000456 | 0 | 1.67 | 0.000564 | -0.000468 | 1.52 | 0.000456 | 0 | 1.67 | 0.000564 | -0.000468 | CFL | None | 1520 | 0.456 | 1520 | 0.456 | 1.1 | 1.24 | -0.000308
CFLNoneSCGOfSNewIOU | Com-Iltg-dWatt-CFL_OSnone | SCG | OfS | New | IOU | 1.52 | 0.000456 | 0 | 1.69 | 0.000579 | -0.0011 | 1.52 | 0.000456 | 0 | 1.69 | 0.000579 | -0.0011 | CFL | None | 1520 | 0.456 | 1520 | 0.456 | 1.11 | 1.27 | -0.000724
CFLNoneSCEOfSNewIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | OfS | New | IOU | 1.52 | 0.000456 | 0 | 1.69 | 0.00058 | -0.0011 | 1.52 | 0.000456 | 0 | 1.69 | 0.00058 | -0.0011 | CFL | None | 1520 | 0.456 | 1520 | 0.456 | 1.11 | 1.27 | -0.000724
CFLNonePGEOfSNewIOU | Com-Iltg-dWatt-CFL_OSnone | PGE | OfS | New | IOU | 1.52 | 0.000456 | 0 | 1.64 | 0.000589 | -0.00472 | 1.52 | 0.000456 | 0 | 1.64 | 0.000589 | -0.00472 | CFL | None | 1520 | 0.456 | 1520 | 0.456 | 1.08 | 1.29 | -0.00311
CFLNonePGERFFExCZ01 | Com-Iltg-dWatt-CFL_OSnone | PGE | RFF | Ex | CZ01 | 3.72 | 0.00067 | 0 | 3.63 | 0.000761 | -0.0439 | 3.72 | 0.00067 | 0 | 3.63 | 0.000761 | -0.0439 | CFL | None | 3720 | 0.67 | 3720 | 0.67 | 0.976 | 1.14 | -0.0118
CFLNonePGERFFExCZ02 | Com-Iltg-dWatt-CFL_OSnone | PGE | RFF | Ex | CZ02 | 3.72 | 0.00067 | 0 | 3.84 | 0.000778 | -0.0285 | 3.72 | 0.00067 | 0 | 3.84 | 0.000778 | -0.0285 | CFL | None | 3720 | 0.67 | 3720 | 0.67 | 1.03 | 1.16 | -0.00766
CFLNonePGERFFExCZ03 | Com-Iltg-dWatt-CFL_OSnone | PGE | RFF | Ex | CZ03 | 3.72 | 0.00067 | 0 | 3.8 | 0.000773 | -0.0302 | 3.72 | 0.00067 | 0 | 3.8 | 0.000773 | -0.0302 | CFL | None | 3720 | 0.67 | 3720 | 0.67 | 1.02 | 1.15 | -0.00812
CFLNonePGERFFExCZ04 | Com-Iltg-dWatt-CFL_OSnone | PGE | RFF | Ex | CZ04 | 3.72 | 0.00067 | 0 | 3.9 | 0.000777 | -0.024 | 3.72 | 0.00067 | 0 | 3.9 | 0.000777 | -0.024 | CFL | None | 3720 | 0.67 | 3720 | 0.67 | 1.05 | 1.16 | -0.00645
CFLNoneSCGRFFExCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCG | RFF | Ex | CZ05 | 3.72 | 0.00067 | 0 | 3.87 | 0.000793 | -0.0347 | 3.72 | 0.00067 | 0 | 3.87 | 0.000793 | -0.0347 | CFL | None | 3720 | 0.67 | 3720 | 0.67 | 1.04 | 1.18 | -0.00933
CFLNoneSCERFFExCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | RFF | Ex | CZ05 | 3.72 | 0.00067 | 0 | 3.87 | 0.000793 | -0.0347 | 3.72 | 0.00067 | 0 | 3.87 | 0.000793 | -0.0347 | CFL | None | 3720 | 0.67 | 3720 | 0.67 | 1.04 | 1.18 | -0.00933
CFLNonePGERFFExCZ05 | Com-Iltg-dWatt-CFL_OSnone | PGE | RFF | Ex | CZ05 | 3.72 | 0.00067 | 0 | 3.87 | 0.000793 | -0.0347 | 3.72 | 0.00067 | 0 | 3.87 | 0.000793 | -0.0347 | CFL | None | 3720 | 0.67 | 3720 | 0.67 | 1.04 | 1.18 | -0.00933
CFLNoneSCERFFExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | RFF | Ex | CZ06 | 3.72 | 0.00067 | 0 | 4.13 | 0.000818 | -0.0199 | 3.72 | 0.00067 | 0 | 4.13 | 0.000818 | -0.0199 | CFL | None | 3720 | 0.67 | 3720 | 0.67 | 1.11 | 1.22 | -0.00535
CFLNoneSDGRFFExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SDG | RFF | Ex | CZ06 | 3.72 | 0.00067 | 0 | 4.13 | 0.000818 | -0.0199 | 3.72 | 0.00067 | 0 | 4.13 | 0.000818 | -0.0199 | CFL | None | 3720 | 0.67 | 3720 | 0.67 | 1.11 | 1.22 | -0.00535
CFLNoneSCGRFFExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCG | RFF | Ex | CZ06 | 3.72 | 0.00067 | 0 | 4.13 | 0.000818 | -0.0199 | 3.72 | 0.00067 | 0 | 4.13 | 0.000818 | -0.0199 | CFL | None | 3720 | 0.67 | 3720 | 0.67 | 1.11 | 1.22 | -0.00535
CFLNoneSDGRFFExCZ07 | Com-Iltg-dWatt-CFL_OSnone | SDG | RFF | Ex | CZ07 | 3.72 | 0.00067 | 0 | 4.14 | 0.000812 | -0.0179 | 3.72 | 0.00067 | 0 | 4.14 | 0.000812 | -0.0179 | CFL | None | 3720 | 0.67 | 3720 | 0.67 | 1.11 | 1.21 | -0.00481
CFLNoneSDGRFFExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SDG | RFF | Ex | CZ08 | 3.72 | 0.00067 | 0 | 4.16 | 0.000811 | -0.0175 | 3.72 | 0.00067 | 0 | 4.16 | 0.000811 | -0.0175 | CFL | None | 3720 | 0.67 | 3720 | 0.67 | 1.12 | 1.21 | -0.0047
CFLNoneSCERFFExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | RFF | Ex | CZ08 | 3.72 | 0.00067 | 0 | 4.16 | 0.000811 | -0.0175 | 3.72 | 0.00067 | 0 | 4.16 | 0.000811 | -0.0175 | CFL | None | 3720 | 0.67 | 3720 | 0.67 | 1.12 | 1.21 | -0.0047
CFLNoneSCGRFFExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCG | RFF | Ex | CZ08 | 3.72 | 0.00067 | 0 | 4.16 | 0.000811 | -0.0175 | 3.72 | 0.00067 | 0 | 4.16 | 0.000811 | -0.0175 | CFL | None | 3720 | 0.67 | 3720 | 0.67 | 1.12 | 1.21 | -0.0047
CFLNoneSCERFFExCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | RFF | Ex | CZ09 | 3.72 | 0.00067 | 0 | 4.1 | 0.000821 | -0.0179 | 3.72 | 0.00067 | 0 | 4.1 | 0.000821 | -0.0179 | CFL | None | 3720 | 0.67 | 3720 | 0.67 | 1.1 | 1.23 | -0.00481
CFLNoneSCGRFFExCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCG | RFF | Ex | CZ09 | 3.72 | 0.00067 | 0 | 4.1 | 0.000821 | -0.0179 | 3.72 | 0.00067 | 0 | 4.1 | 0.000821 | -0.0179 | CFL | None | 3720 | 0.67 | 3720 | 0.67 | 1.1 | 1.23 | -0.00481
CFLNoneSDGRFFExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SDG | RFF | Ex | CZ10 | 3.72 | 0.00067 | 0 | 4.17 | 0.000825 | -0.0195 | 3.72 | 0.00067 | 0 | 4.17 | 0.000825 | -0.0195 | CFL | None | 3720 | 0.67 | 3720 | 0.67 | 1.12 | 1.23 | -0.00524
CFLNoneSCGRFFExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCG | RFF | Ex | CZ10 | 3.72 | 0.00067 | 0 | 4.17 | 0.000825 | -0.0195 | 3.72 | 0.00067 | 0 | 4.17 | 0.000825 | -0.0195 | CFL | None | 3720 | 0.67 | 3720 | 0.67 | 1.12 | 1.23 | -0.00524
CFLNoneSCERFFExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | RFF | Ex | CZ10 | 3.72 | 0.00067 | 0 | 4.17 | 0.000825 | -0.0195 | 3.72 | 0.00067 | 0 | 4.17 | 0.000825 | -0.0195 | CFL | None | 3720 | 0.67 | 3720 | 0.67 | 1.12 | 1.23 | -0.00524
CFLNonePGERFFExCZ11 | Com-Iltg-dWatt-CFL_OSnone | PGE | RFF | Ex | CZ11 | 3.72 | 0.00067 | 0 | 3.92 | 0.000793 | -0.0235 | 3.72 | 0.00067 | 0 | 3.92 | 0.000793 | -0.0235 | CFL | None | 3720 | 0.67 | 3720 | 0.67 | 1.05 | 1.18 | -0.00632
CFLNonePGERFFExCZ12 | Com-Iltg-dWatt-CFL_OSnone | PGE | RFF | Ex | CZ12 | 3.72 | 0.00067 | 0 | 3.9 | 0.000785 | -0.0246 | 3.72 | 0.00067 | 0 | 3.9 | 0.000785 | -0.0246 | CFL | None | 3720 | 0.67 | 3720 | 0.67 | 1.05 | 1.17 | -0.00661
CFLNoneSCGRFFExCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCG | RFF | Ex | CZ13 | 3.72 | 0.00067 | 0 | 4.02 | 0.000813 | -0.0262 | 3.72 | 0.00067 | 0 | 4.02 | 0.000813 | -0.0262 | CFL | None | 3720 | 0.67 | 3720 | 0.67 | 1.08 | 1.21 | -0.00704
CFLNonePGERFFExCZ13 | Com-Iltg-dWatt-CFL_OSnone | PGE | RFF | Ex | CZ13 | 3.72 | 0.00067 | 0 | 4.02 | 0.000813 | -0.0262 | 3.72 | 0.00067 | 0 | 4.02 | 0.000813 | -0.0262 | CFL | None | 3720 | 0.67 | 3720 | 0.67 | 1.08 | 1.21 | -0.00704
CFLNoneSCERFFExCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | RFF | Ex | CZ13 | 3.72 | 0.00067 | 0 | 4.02 | 0.000813 | -0.0262 | 3.72 | 0.00067 | 0 | 4.02 | 0.000813 | -0.0262 | CFL | None | 3720 | 0.67 | 3720 | 0.67 | 1.08 | 1.21 | -0.00704
CFLNoneSDGRFFExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SDG | RFF | Ex | CZ14 | 3.72 | 0.00067 | 0 | 4.1 | 0.00084 | -0.0275 | 3.72 | 0.00067 | 0 | 4.1 | 0.00084 | -0.0275 | CFL | None | 3720 | 0.67 | 3720 | 0.67 | 1.1 | 1.25 | -0.00739
CFLNoneSCGRFFExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCG | RFF | Ex | CZ14 | 3.72 | 0.00067 | 0 | 4.1 | 0.00084 | -0.0275 | 3.72 | 0.00067 | 0 | 4.1 | 0.00084 | -0.0275 | CFL | None | 3720 | 0.67 | 3720 | 0.67 | 1.1 | 1.25 | -0.00739
CFLNoneSCERFFExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | RFF | Ex | CZ14 | 3.72 | 0.00067 | 0 | 4.1 | 0.00084 | -0.0275 | 3.72 | 0.00067 | 0 | 4.1 | 0.00084 | -0.0275 | CFL | None | 3720 | 0.67 | 3720 | 0.67 | 1.1 | 1.25 | -0.00739
CFLNoneSCGRFFExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCG | RFF | Ex | CZ15 | 3.72 | 0.00067 | 0 | 4.42 | 0.000833 | -0.00904 | 3.72 | 0.00067 | 0 | 4.42 | 0.000833 | -0.00904 | CFL | None | 3720 | 0.67 | 3720 | 0.67 | 1.19 | 1.24 | -0.00243
CFLNoneSCERFFExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | RFF | Ex | CZ15 | 3.72 | 0.00067 | 0 | 4.42 | 0.000833 | -0.00904 | 3.72 | 0.00067 | 0 | 4.42 | 0.000833 | -0.00904 | CFL | None | 3720 | 0.67 | 3720 | 0.67 | 1.19 | 1.24 | -0.00243
CFLNoneSDGRFFExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SDG | RFF | Ex | CZ15 | 3.72 | 0.00067 | 0 | 4.42 | 0.000833 | -0.00904 | 3.72 | 0.00067 | 0 | 4.42 | 0.000833 | -0.00904 | CFL | None | 3720 | 0.67 | 3720 | 0.67 | 1.19 | 1.24 | -0.00243
CFLNonePGERFFExCZ16 | Com-Iltg-dWatt-CFL_OSnone | PGE | RFF | Ex | CZ16 | 3.72 | 0.00067 | 0 | 3.72 | 0.000795 | -0.0502 | 3.72 | 0.00067 | 0 | 3.72 | 0.000795 | -0.0502 | CFL | None | 3720 | 0.67 | 3720 | 0.67 | 1 | 1.19 | -0.0135
CFLNoneSCGRFFExCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCG | RFF | Ex | CZ16 | 3.72 | 0.00067 | 0 | 3.72 | 0.000795 | -0.0502 | 3.72 | 0.00067 | 0 | 3.72 | 0.000795 | -0.0502 | CFL | None | 3720 | 0.67 | 3720 | 0.67 | 1 | 1.19 | -0.0135
CFLNoneSCERFFExCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | RFF | Ex | CZ16 | 3.72 | 0.00067 | 0 | 3.72 | 0.000795 | -0.0502 | 3.72 | 0.00067 | 0 | 3.72 | 0.000795 | -0.0502 | CFL | None | 3720 | 0.67 | 3720 | 0.67 | 1 | 1.19 | -0.0135
CFLNoneSCGRFFExIOU | Com-Iltg-dWatt-CFL_OSnone | SCG | RFF | Ex | IOU | 3.72 | 0.00067 | 0 | 4.14 | 0.000819 | -0.0192 | 3.72 | 0.00067 | 0 | 4.14 | 0.000819 | -0.0192 | CFL | None | 3720 | 0.67 | 3720 | 0.67 | 1.11 | 1.22 | -0.00516
CFLNoneSDGRFFExIOU | Com-Iltg-dWatt-CFL_OSnone | SDG | RFF | Ex | IOU | 3.72 | 0.00067 | 0 | 4.15 | 0.000815 | -0.0183 | 3.72 | 0.00067 | 0 | 4.15 | 0.000815 | -0.0183 | CFL | None | 3720 | 0.67 | 3720 | 0.67 | 1.12 | 1.22 | -0.00492
CFLNoneSCERFFExIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | RFF | Ex | IOU | 3.72 | 0.00067 | 0 | 4.14 | 0.000819 | -0.0195 | 3.72 | 0.00067 | 0 | 4.14 | 0.000819 | -0.0195 | CFL | None | 3720 | 0.67 | 3720 | 0.67 | 1.11 | 1.22 | -0.00524
CFLNonePGERFFExIOU | Com-Iltg-dWatt-CFL_OSnone | PGE | RFF | Ex | IOU | 3.72 | 0.00067 | 0 | 3.88 | 0.000784 | -0.0276 | 3.72 | 0.00067 | 0 | 3.88 | 0.000784 | -0.0276 | CFL | None | 3720 | 0.67 | 3720 | 0.67 | 1.04 | 1.17 | -0.00742
CFLNonePGERFFNewCZ01 | Com-Iltg-dWatt-CFL_OSnone | PGE | RFF | New | CZ01 | 3.72 | 0.00067 | 0 | 3.5 | 0.000729 | -0.0461 | 3.72 | 0.00067 | 0 | 3.5 | 0.000729 | -0.0461 | CFL | None | 3720 | 0.67 | 3720 | 0.67 | 0.941 | 1.09 | -0.0124
CFLNonePGERFFNewCZ02 | Com-Iltg-dWatt-CFL_OSnone | PGE | RFF | New | CZ02 | 3.72 | 0.00067 | 0 | 3.76 | 0.000808 | -0.0338 | 3.72 | 0.00067 | 0 | 3.76 | 0.000808 | -0.0338 | CFL | None | 3720 | 0.67 | 3720 | 0.67 | 1.01 | 1.21 | -0.00909
CFLNonePGERFFNewCZ03 | Com-Iltg-dWatt-CFL_OSnone | PGE | RFF | New | CZ03 | 3.72 | 0.00067 | 0 | 3.68 | 0.000784 | -0.0344 | 3.72 | 0.00067 | 0 | 3.68 | 0.000784 | -0.0344 | CFL | None | 3720 | 0.67 | 3720 | 0.67 | 0.989 | 1.17 | -0.00925
CFLNonePGERFFNewCZ04 | Com-Iltg-dWatt-CFL_OSnone | PGE | RFF | New | CZ04 | 3.72 | 0.00067 | 0 | 3.82 | 0.000799 | -0.0285 | 3.72 | 0.00067 | 0 | 3.82 | 0.000799 | -0.0285 | CFL | None | 3720 | 0.67 | 3720 | 0.67 | 1.03 | 1.19 | -0.00766
CFLNoneSCERFFNewCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | RFF | New | CZ05 | 3.72 | 0.00067 | 0 | 3.81 | 0.000805 | -0.0337 | 3.72 | 0.00067 | 0 | 3.81 | 0.000805 | -0.0337 | CFL | None | 3720 | 0.67 | 3720 | 0.67 | 1.02 | 1.2 | -0.00906
CFLNonePGERFFNewCZ05 | Com-Iltg-dWatt-CFL_OSnone | PGE | RFF | New | CZ05 | 3.72 | 0.00067 | 0 | 3.68 | 0.000773 | -0.0305 | 3.72 | 0.00067 | 0 | 3.68 | 0.000773 | -0.0305 | CFL | None | 3720 | 0.67 | 3720 | 0.67 | 0.989 | 1.15 | -0.0082
CFLNoneSCERFFNewCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | RFF | New | CZ06 | 3.72 | 0.00067 | 0 | 4 | 0.000829 | -0.0201 | 3.72 | 0.00067 | 0 | 4 | 0.000829 | -0.0201 | CFL | None | 3720 | 0.67 | 3720 | 0.67 | 1.08 | 1.24 | -0.0054
CFLNoneSDGRFFNewCZ06 | Com-Iltg-dWatt-CFL_OSnone | SDG | RFF | New | CZ06 | 3.72 | 0.00067 | 0 | 3.99 | 0.000831 | -0.0209 | 3.72 | 0.00067 | 0 | 3.99 | 0.000831 | -0.0209 | CFL | None | 3720 | 0.67 | 3720 | 0.67 | 1.07 | 1.24 | -0.00562
CFLNoneSDGRFFNewCZ07 | Com-Iltg-dWatt-CFL_OSnone | SDG | RFF | New | CZ07 | 3.72 | 0.00067 | 0 | 3.97 | 0.000823 | -0.0221 | 3.72 | 0.00067 | 0 | 3.97 | 0.000823 | -0.0221 | CFL | None | 3720 | 0.67 | 3720 | 0.67 | 1.07 | 1.23 | -0.00594
CFLNoneSCERFFNewCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | RFF | New | CZ08 | 3.72 | 0.00067 | 0 | 4 | 0.000804 | -0.0197 | 3.72 | 0.00067 | 0 | 4 | 0.000804 | -0.0197 | CFL | None | 3720 | 0.67 | 3720 | 0.67 | 1.08 | 1.2 | -0.0053
CFLNoneSDGRFFNewCZ08 | Com-Iltg-dWatt-CFL_OSnone | SDG | RFF | New | CZ08 | 3.72 | 0.00067 | 0 | 4 | 0.000806 | -0.0205 | 3.72 | 0.00067 | 0 | 4 | 0.000806 | -0.0205 | CFL | None | 3720 | 0.67 | 3720 | 0.67 | 1.08 | 1.2 | -0.00551
CFLNoneSCERFFNewCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | RFF | New | CZ09 | 3.72 | 0.00067 | 0 | 4.08 | 0.00086 | -0.022 | 3.72 | 0.00067 | 0 | 4.08 | 0.00086 | -0.022 | CFL | None | 3720 | 0.67 | 3720 | 0.67 | 1.1 | 1.28 | -0.00591
CFLNoneSDGRFFNewCZ10 | Com-Iltg-dWatt-CFL_OSnone | SDG | RFF | New | CZ10 | 3.72 | 0.00067 | 0 | 4.09 | 0.000869 | -0.0238 | 3.72 | 0.00067 | 0 | 4.09 | 0.000869 | -0.0238 | CFL | None | 3720 | 0.67 | 3720 | 0.67 | 1.1 | 1.3 | -0.0064
CFLNoneSCERFFNewCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | RFF | New | CZ10 | 3.72 | 0.00067 | 0 | 4.1 | 0.000866 | -0.0229 | 3.72 | 0.00067 | 0 | 4.1 | 0.000866 | -0.0229 | CFL | None | 3720 | 0.67 | 3720 | 0.67 | 1.1 | 1.29 | -0.00616
CFLNonePGERFFNewCZ11 | Com-Iltg-dWatt-CFL_OSnone | PGE | RFF | New | CZ11 | 3.72 | 0.00067 | 0 | 3.91 | 0.000826 | -0.0257 | 3.72 | 0.00067 | 0 | 3.91 | 0.000826 | -0.0257 | CFL | None | 3720 | 0.67 | 3720 | 0.67 | 1.05 | 1.23 | -0.00691
CFLNonePGERFFNewCZ12 | Com-Iltg-dWatt-CFL_OSnone | PGE | RFF | New | CZ12 | 3.72 | 0.00067 | 0 | 3.87 | 0.000817 | -0.0302 | 3.72 | 0.00067 | 0 | 3.87 | 0.000817 | -0.0302 | CFL | None | 3720 | 0.67 | 3720 | 0.67 | 1.04 | 1.22 | -0.00812
CFLNonePGERFFNewCZ13 | Com-Iltg-dWatt-CFL_OSnone | PGE | RFF | New | CZ13 | 3.72 | 0.00067 | 0 | 3.92 | 0.000816 | -0.0268 | 3.72 | 0.00067 | 0 | 3.92 | 0.000816 | -0.0268 | CFL | None | 3720 | 0.67 | 3720 | 0.67 | 1.05 | 1.22 | -0.0072
CFLNoneSCERFFNewCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | RFF | New | CZ13 | 3.72 | 0.00067 | 0 | 4.08 | 0.000863 | -0.03 | 3.72 | 0.00067 | 0 | 4.08 | 0.000863 | -0.03 | CFL | None | 3720 | 0.67 | 3720 | 0.67 | 1.1 | 1.29 | -0.00806
CFLNoneSDGRFFNewCZ14 | Com-Iltg-dWatt-CFL_OSnone | SDG | RFF | New | CZ14 | 3.72 | 0.00067 | 0 | 4.07 | 0.000874 | -0.0332 | 3.72 | 0.00067 | 0 | 4.07 | 0.000874 | -0.0332 | CFL | None | 3720 | 0.67 | 3720 | 0.67 | 1.09 | 1.3 | -0.00892
CFLNoneSCERFFNewCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | RFF | New | CZ14 | 3.72 | 0.00067 | 0 | 4.08 | 0.000871 | -0.0319 | 3.72 | 0.00067 | 0 | 4.08 | 0.000871 | -0.0319 | CFL | None | 3720 | 0.67 | 3720 | 0.67 | 1.1 | 1.3 | -0.00858
CFLNoneSCERFFNewCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | RFF | New | CZ15 | 3.72 | 0.00067 | 0 | 4.37 | 0.000882 | -0.0114 | 3.72 | 0.00067 | 0 | 4.37 | 0.000882 | -0.0114 | CFL | None | 3720 | 0.67 | 3720 | 0.67 | 1.17 | 1.32 | -0.00306
CFLNoneSDGRFFNewCZ15 | Com-Iltg-dWatt-CFL_OSnone | SDG | RFF | New | CZ15 | 3.72 | 0.00067 | 0 | 4.38 | 0.000885 | -0.0118 | 3.72 | 0.00067 | 0 | 4.38 | 0.000885 | -0.0118 | CFL | None | 3720 | 0.67 | 3720 | 0.67 | 1.18 | 1.32 | -0.00317
CFLNoneSCERFFNewCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | RFF | New | CZ16 | 3.72 | 0.00067 | 0 | 3.77 | 0.000827 | -0.0539 | 3.72 | 0.00067 | 0 | 3.77 | 0.000827 | -0.0539 | CFL | None | 3720 | 0.67 | 3720 | 0.67 | 1.01 | 1.23 | -0.0145
CFLNonePGERFFNewCZ16 | Com-Iltg-dWatt-CFL_OSnone | PGE | RFF | New | CZ16 | 3.72 | 0.00067 | 0 | 3.62 | 0.000789 | -0.0476 | 3.72 | 0.00067 | 0 | 3.62 | 0.000789 | -0.0476 | CFL | None | 3720 | 0.67 | 3720 | 0.67 | 0.973 | 1.18 | -0.0128
CFLNoneSDGRFFNewIOU | Com-Iltg-dWatt-CFL_OSnone | SDG | RFF | New | IOU | 3.72 | 0.00067 | 0 | 4 | 0.000833 | -0.0224 | 3.72 | 0.00067 | 0 | 4 | 0.000833 | -0.0224 | CFL | None | 3720 | 0.67 | 3720 | 0.67 | 1.08 | 1.24 | -0.00602
CFLNoneSCGRFFNewIOU | Com-Iltg-dWatt-CFL_OSnone | SCG | RFF | New | IOU | 3.72 | 0.00067 | 0 | 4.05 | 0.000841 | -0.0219 | 3.72 | 0.00067 | 0 | 4.05 | 0.000841 | -0.0219 | CFL | None | 3720 | 0.67 | 3720 | 0.67 | 1.09 | 1.26 | -0.00589
CFLNonePGERFFNewIOU | Com-Iltg-dWatt-CFL_OSnone | PGE | RFF | New | IOU | 3.72 | 0.00067 | 0 | 4.03 | 0.000853 | -0.0319 | 3.72 | 0.00067 | 0 | 4.03 | 0.000853 | -0.0319 | CFL | None | 3720 | 0.67 | 3720 | 0.67 | 1.08 | 1.27 | -0.00858
CFLNoneSCERFFNewIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | RFF | New | IOU | 3.72 | 0.00067 | 0 | 4.06 | 0.000843 | -0.0219 | 3.72 | 0.00067 | 0 | 4.06 | 0.000843 | -0.0219 | CFL | None | 3720 | 0.67 | 3720 | 0.67 | 1.09 | 1.26 | -0.00589
CFLNonePGERSDExCZ01 | Com-Iltg-dWatt-CFL_OSnone | PGE | RSD | Ex | CZ01 | 3.68 | 0.000616 | 0 | 3.53 | 0.000722 | -0.046 | 3.68 | 0.000616 | 0 | 3.53 | 0.000722 | -0.046 | CFL | None | 3680 | 0.616 | 3680 | 0.616 | 0.959 | 1.17 | -0.0125
CFLNonePGERSDExCZ02 | Com-Iltg-dWatt-CFL_OSnone | PGE | RSD | Ex | CZ02 | 3.68 | 0.000616 | 0 | 3.82 | 0.000722 | -0.027 | 3.68 | 0.000616 | 0 | 3.82 | 0.000722 | -0.027 | CFL | None | 3680 | 0.616 | 3680 | 0.616 | 1.04 | 1.17 | -0.00734
CFLNonePGERSDExCZ03 | Com-Iltg-dWatt-CFL_OSnone | PGE | RSD | Ex | CZ03 | 3.68 | 0.000616 | 0 | 3.76 | 0.000723 | -0.0302 | 3.68 | 0.000616 | 0 | 3.76 | 0.000723 | -0.0302 | CFL | None | 3680 | 0.616 | 3680 | 0.616 | 1.02 | 1.17 | -0.00821
CFLNonePGERSDExCZ04 | Com-Iltg-dWatt-CFL_OSnone | PGE | RSD | Ex | CZ04 | 3.68 | 0.000616 | 0 | 3.88 | 0.000725 | -0.0224 | 3.68 | 0.000616 | 0 | 3.88 | 0.000725 | -0.0224 | CFL | None | 3680 | 0.616 | 3680 | 0.616 | 1.05 | 1.18 | -0.00609
CFLNonePGERSDExCZ05 | Com-Iltg-dWatt-CFL_OSnone | PGE | RSD | Ex | CZ05 | 3.68 | 0.000616 | 0 | 3.87 | 0.000749 | -0.0331 | 3.68 | 0.000616 | 0 | 3.87 | 0.000749 | -0.0331 | CFL | None | 3680 | 0.616 | 3680 | 0.616 | 1.05 | 1.22 | -0.00899
CFLNoneSCERSDExCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | RSD | Ex | CZ05 | 3.68 | 0.000616 | 0 | 3.87 | 0.000749 | -0.0331 | 3.68 | 0.000616 | 0 | 3.87 | 0.000749 | -0.0331 | CFL | None | 3680 | 0.616 | 3680 | 0.616 | 1.05 | 1.22 | -0.00899
CFLNoneSCGRSDExCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCG | RSD | Ex | CZ05 | 3.68 | 0.000616 | 0 | 3.87 | 0.000749 | -0.0331 | 3.68 | 0.000616 | 0 | 3.87 | 0.000749 | -0.0331 | CFL | None | 3680 | 0.616 | 3680 | 0.616 | 1.05 | 1.22 | -0.00899
CFLNoneSCGRSDExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCG | RSD | Ex | CZ06 | 3.68 | 0.000616 | 0 | 4.16 | 0.000765 | -0.0176 | 3.68 | 0.000616 | 0 | 4.16 | 0.000765 | -0.0176 | CFL | None | 3680 | 0.616 | 3680 | 0.616 | 1.13 | 1.24 | -0.00478
CFLNoneSCERSDExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | RSD | Ex | CZ06 | 3.68 | 0.000616 | 0 | 4.16 | 0.000765 | -0.0176 | 3.68 | 0.000616 | 0 | 4.16 | 0.000765 | -0.0176 | CFL | None | 3680 | 0.616 | 3680 | 0.616 | 1.13 | 1.24 | -0.00478
CFLNoneSDGRSDExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SDG | RSD | Ex | CZ06 | 3.68 | 0.000616 | 0 | 4.16 | 0.000765 | -0.0176 | 3.68 | 0.000616 | 0 | 4.16 | 0.000765 | -0.0176 | CFL | None | 3680 | 0.616 | 3680 | 0.616 | 1.13 | 1.24 | -0.00478
CFLNoneSDGRSDExCZ07 | Com-Iltg-dWatt-CFL_OSnone | SDG | RSD | Ex | CZ07 | 3.68 | 0.000616 | 0 | 4.16 | 0.000769 | -0.0153 | 3.68 | 0.000616 | 0 | 4.16 | 0.000769 | -0.0153 | CFL | None | 3680 | 0.616 | 3680 | 0.616 | 1.13 | 1.25 | -0.00416
CFLNoneSCERSDExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | RSD | Ex | CZ08 | 3.68 | 0.000616 | 0 | 4.19 | 0.000747 | -0.0149 | 3.68 | 0.000616 | 0 | 4.19 | 0.000747 | -0.0149 | CFL | None | 3680 | 0.616 | 3680 | 0.616 | 1.14 | 1.21 | -0.00405
CFLNoneSCGRSDExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCG | RSD | Ex | CZ08 | 3.68 | 0.000616 | 0 | 4.19 | 0.000747 | -0.0149 | 3.68 | 0.000616 | 0 | 4.19 | 0.000747 | -0.0149 | CFL | None | 3680 | 0.616 | 3680 | 0.616 | 1.14 | 1.21 | -0.00405
CFLNoneSDGRSDExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SDG | RSD | Ex | CZ08 | 3.68 | 0.000616 | 0 | 4.19 | 0.000747 | -0.0149 | 3.68 | 0.000616 | 0 | 4.19 | 0.000747 | -0.0149 | CFL | None | 3680 | 0.616 | 3680 | 0.616 | 1.14 | 1.21 | -0.00405
CFLNoneSCGRSDExCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCG | RSD | Ex | CZ09 | 3.68 | 0.000616 | 0 | 4.12 | 0.000752 | -0.0164 | 3.68 | 0.000616 | 0 | 4.12 | 0.000752 | -0.0164 | CFL | None | 3680 | 0.616 | 3680 | 0.616 | 1.12 | 1.22 | -0.00446
CFLNoneSCERSDExCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | RSD | Ex | CZ09 | 3.68 | 0.000616 | 0 | 4.12 | 0.000752 | -0.0164 | 3.68 | 0.000616 | 0 | 4.12 | 0.000752 | -0.0164 | CFL | None | 3680 | 0.616 | 3680 | 0.616 | 1.12 | 1.22 | -0.00446
CFLNoneSCERSDExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | RSD | Ex | CZ10 | 3.68 | 0.000616 | 0 | 4.17 | 0.000738 | -0.0176 | 3.68 | 0.000616 | 0 | 4.17 | 0.000738 | -0.0176 | CFL | None | 3680 | 0.616 | 3680 | 0.616 | 1.13 | 1.2 | -0.00478
CFLNoneSDGRSDExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SDG | RSD | Ex | CZ10 | 3.68 | 0.000616 | 0 | 4.17 | 0.000738 | -0.0176 | 3.68 | 0.000616 | 0 | 4.17 | 0.000738 | -0.0176 | CFL | None | 3680 | 0.616 | 3680 | 0.616 | 1.13 | 1.2 | -0.00478
CFLNoneSCGRSDExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCG | RSD | Ex | CZ10 | 3.68 | 0.000616 | 0 | 4.17 | 0.000738 | -0.0176 | 3.68 | 0.000616 | 0 | 4.17 | 0.000738 | -0.0176 | CFL | None | 3680 | 0.616 | 3680 | 0.616 | 1.13 | 1.2 | -0.00478
CFLNonePGERSDExCZ11 | Com-Iltg-dWatt-CFL_OSnone | PGE | RSD | Ex | CZ11 | 3.68 | 0.000616 | 0 | 3.9 | 0.000729 | -0.0233 | 3.68 | 0.000616 | 0 | 3.9 | 0.000729 | -0.0233 | CFL | None | 3680 | 0.616 | 3680 | 0.616 | 1.06 | 1.18 | -0.00633
CFLNonePGERSDExCZ12 | Com-Iltg-dWatt-CFL_OSnone | PGE | RSD | Ex | CZ12 | 3.68 | 0.000616 | 0 | 3.86 | 0.000706 | -0.0241 | 3.68 | 0.000616 | 0 | 3.86 | 0.000706 | -0.0241 | CFL | None | 3680 | 0.616 | 3680 | 0.616 | 1.05 | 1.15 | -0.00655
CFLNoneSCGRSDExCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCG | RSD | Ex | CZ13 | 3.68 | 0.000616 | 0 | 4.03 | 0.000758 | -0.0255 | 3.68 | 0.000616 | 0 | 4.03 | 0.000758 | -0.0255 | CFL | None | 3680 | 0.616 | 3680 | 0.616 | 1.1 | 1.23 | -0.00693
CFLNonePGERSDExCZ13 | Com-Iltg-dWatt-CFL_OSnone | PGE | RSD | Ex | CZ13 | 3.68 | 0.000616 | 0 | 4.03 | 0.000758 | -0.0255 | 3.68 | 0.000616 | 0 | 4.03 | 0.000758 | -0.0255 | CFL | None | 3680 | 0.616 | 3680 | 0.616 | 1.1 | 1.23 | -0.00693
CFLNoneSCERSDExCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | RSD | Ex | CZ13 | 3.68 | 0.000616 | 0 | 4.03 | 0.000758 | -0.0255 | 3.68 | 0.000616 | 0 | 4.03 | 0.000758 | -0.0255 | CFL | None | 3680 | 0.616 | 3680 | 0.616 | 1.1 | 1.23 | -0.00693
CFLNoneSCERSDExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | RSD | Ex | CZ14 | 3.68 | 0.000616 | 0 | 4.07 | 0.000739 | -0.0273 | 3.68 | 0.000616 | 0 | 4.07 | 0.000739 | -0.0273 | CFL | None | 3680 | 0.616 | 3680 | 0.616 | 1.11 | 1.2 | -0.00742
CFLNoneSDGRSDExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SDG | RSD | Ex | CZ14 | 3.68 | 0.000616 | 0 | 4.07 | 0.000739 | -0.0273 | 3.68 | 0.000616 | 0 | 4.07 | 0.000739 | -0.0273 | CFL | None | 3680 | 0.616 | 3680 | 0.616 | 1.11 | 1.2 | -0.00742
CFLNoneSCGRSDExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCG | RSD | Ex | CZ14 | 3.68 | 0.000616 | 0 | 4.07 | 0.000739 | -0.0273 | 3.68 | 0.000616 | 0 | 4.07 | 0.000739 | -0.0273 | CFL | None | 3680 | 0.616 | 3680 | 0.616 | 1.11 | 1.2 | -0.00742
CFLNoneSCERSDExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | RSD | Ex | CZ15 | 3.68 | 0.000616 | 0 | 4.48 | 0.000786 | -0.00651 | 3.68 | 0.000616 | 0 | 4.48 | 0.000786 | -0.00651 | CFL | None | 3680 | 0.616 | 3680 | 0.616 | 1.22 | 1.28 | -0.00177
CFLNoneSDGRSDExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SDG | RSD | Ex | CZ15 | 3.68 | 0.000616 | 0 | 4.48 | 0.000786 | -0.00651 | 3.68 | 0.000616 | 0 | 4.48 | 0.000786 | -0.00651 | CFL | None | 3680 | 0.616 | 3680 | 0.616 | 1.22 | 1.28 | -0.00177
CFLNoneSCGRSDExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCG | RSD | Ex | CZ15 | 3.68 | 0.000616 | 0 | 4.48 | 0.000786 | -0.00651 | 3.68 | 0.000616 | 0 | 4.48 | 0.000786 | -0.00651 | CFL | None | 3680 | 0.616 | 3680 | 0.616 | 1.22 | 1.28 | -0.00177
CFLNoneSCGRSDExCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCG | RSD | Ex | CZ16 | 3.68 | 0.000616 | 0 | 3.7 | 0.00073 | -0.0471 | 3.68 | 0.000616 | 0 | 3.7 | 0.00073 | -0.0471 | CFL | None | 3680 | 0.616 | 3680 | 0.616 | 1.01 | 1.19 | -0.0128
CFLNonePGERSDExCZ16 | Com-Iltg-dWatt-CFL_OSnone | PGE | RSD | Ex | CZ16 | 3.68 | 0.000616 | 0 | 3.7 | 0.00073 | -0.0471 | 3.68 | 0.000616 | 0 | 3.7 | 0.00073 | -0.0471 | CFL | None | 3680 | 0.616 | 3680 | 0.616 | 1.01 | 1.19 | -0.0128
CFLNoneSCERSDExCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | RSD | Ex | CZ16 | 3.68 | 0.000616 | 0 | 3.7 | 0.00073 | -0.0471 | 3.68 | 0.000616 | 0 | 3.7 | 0.00073 | -0.0471 | CFL | None | 3680 | 0.616 | 3680 | 0.616 | 1.01 | 1.19 | -0.0128
CFLNonePGERSDExIOU | Com-Iltg-dWatt-CFL_OSnone | PGE | RSD | Ex | IOU | 3.68 | 0.000616 | 0 | 3.85 | 0.000726 | -0.027 | 3.68 | 0.000616 | 0 | 3.85 | 0.000726 | -0.027 | CFL | None | 3680 | 0.616 | 3680 | 0.616 | 1.05 | 1.18 | -0.00734
CFLNoneSDGRSDExIOU | Com-Iltg-dWatt-CFL_OSnone | SDG | RSD | Ex | IOU | 3.68 | 0.000616 | 0 | 4.16 | 0.000761 | -0.0159 | 3.68 | 0.000616 | 0 | 4.16 | 0.000761 | -0.0159 | CFL | None | 3680 | 0.616 | 3680 | 0.616 | 1.13 | 1.24 | -0.00432
CFLNoneSCGRSDExIOU | Com-Iltg-dWatt-CFL_OSnone | SCG | RSD | Ex | IOU | 3.68 | 0.000616 | 0 | 4.16 | 0.000751 | -0.0172 | 3.68 | 0.000616 | 0 | 4.16 | 0.000751 | -0.0172 | CFL | None | 3680 | 0.616 | 3680 | 0.616 | 1.13 | 1.22 | -0.00467
CFLNoneSCERSDExIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | RSD | Ex | IOU | 3.68 | 0.000616 | 0 | 4.16 | 0.000751 | -0.0174 | 3.68 | 0.000616 | 0 | 4.16 | 0.000751 | -0.0174 | CFL | None | 3680 | 0.616 | 3680 | 0.616 | 1.13 | 1.22 | -0.00473
CFLNonePGERSDNewCZ01 | Com-Iltg-dWatt-CFL_OSnone | PGE | RSD | New | CZ01 | 3.68 | 0.000616 | 0 | 3.51 | 0.0007 | -0.0111 | 3.68 | 0.000616 | 0 | 3.51 | 0.0007 | -0.0111 | CFL | None | 3680 | 0.616 | 3680 | 0.616 | 0.954 | 1.14 | -0.00302
CFLNonePGERSDNewCZ02 | Com-Iltg-dWatt-CFL_OSnone | PGE | RSD | New | CZ02 | 3.68 | 0.000616 | 0 | 3.77 | 0.00075 | -0.03 | 3.68 | 0.000616 | 0 | 3.77 | 0.00075 | -0.03 | CFL | None | 3680 | 0.616 | 3680 | 0.616 | 1.02 | 1.22 | -0.00815
CFLNonePGERSDNewCZ03 | Com-Iltg-dWatt-CFL_OSnone | PGE | RSD | New | CZ03 | 3.68 | 0.000616 | 0 | 3.66 | 0.000715 | -0.0375 | 3.68 | 0.000616 | 0 | 3.66 | 0.000715 | -0.0375 | CFL | None | 3680 | 0.616 | 3680 | 0.616 | 0.995 | 1.16 | -0.0102
CFLNonePGERSDNewCZ04 | Com-Iltg-dWatt-CFL_OSnone | PGE | RSD | New | CZ04 | 3.68 | 0.000616 | 0 | 3.84 | 0.00075 | -0.0251 | 3.68 | 0.000616 | 0 | 3.84 | 0.00075 | -0.0251 | CFL | None | 3680 | 0.616 | 3680 | 0.616 | 1.04 | 1.22 | -0.00682
CFLNonePGERSDNewCZ05 | Com-Iltg-dWatt-CFL_OSnone | PGE | RSD | New | CZ05 | 3.68 | 0.000616 | 0 | 3.69 | 0.000722 | -0.0322 | 3.68 | 0.000616 | 0 | 3.69 | 0.000722 | -0.0322 | CFL | None | 3680 | 0.616 | 3680 | 0.616 | 1 | 1.17 | -0.00875
CFLNoneSCERSDNewCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | RSD | New | CZ05 | 3.68 | 0.000616 | 0 | 3.81 | 0.000756 | -0.036 | 3.68 | 0.000616 | 0 | 3.81 | 0.000756 | -0.036 | CFL | None | 3680 | 0.616 | 3680 | 0.616 | 1.04 | 1.23 | -0.00978
CFLNoneSCERSDNewCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | RSD | New | CZ06 | 3.68 | 0.000616 | 0 | 4.03 | 0.000769 | -0.0203 | 3.68 | 0.000616 | 0 | 4.03 | 0.000769 | -0.0203 | CFL | None | 3680 | 0.616 | 3680 | 0.616 | 1.1 | 1.25 | -0.00552
CFLNoneSDGRSDNewCZ06 | Com-Iltg-dWatt-CFL_OSnone | SDG | RSD | New | CZ06 | 3.68 | 0.000616 | 0 | 4.03 | 0.000771 | -0.0211 | 3.68 | 0.000616 | 0 | 4.03 | 0.000771 | -0.0211 | CFL | None | 3680 | 0.616 | 3680 | 0.616 | 1.1 | 1.25 | -0.00573
CFLNoneSDGRSDNewCZ07 | Com-Iltg-dWatt-CFL_OSnone | SDG | RSD | New | CZ07 | 3.68 | 0.000616 | 0 | 4 | 0.000774 | -0.0194 | 3.68 | 0.000616 | 0 | 4 | 0.000774 | -0.0194 | CFL | None | 3680 | 0.616 | 3680 | 0.616 | 1.09 | 1.26 | -0.00527
CFLNoneSCERSDNewCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | RSD | New | CZ08 | 3.68 | 0.000616 | 0 | 3.96 | 0.00067 | -0.0169 | 3.68 | 0.000616 | 0 | 3.96 | 0.00067 | -0.0169 | CFL | None | 3680 | 0.616 | 3680 | 0.616 | 1.08 | 1.09 | -0.00459
CFLNoneSDGRSDNewCZ08 | Com-Iltg-dWatt-CFL_OSnone | SDG | RSD | New | CZ08 | 3.68 | 0.000616 | 0 | 3.95 | 0.000671 | -0.0175 | 3.68 | 0.000616 | 0 | 3.95 | 0.000671 | -0.0175 | CFL | None | 3680 | 0.616 | 3680 | 0.616 | 1.07 | 1.09 | -0.00476
CFLNoneSCERSDNewCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | RSD | New | CZ09 | 3.68 | 0.000616 | 0 | 4.1 | 0.000807 | -0.0188 | 3.68 | 0.000616 | 0 | 4.1 | 0.000807 | -0.0188 | CFL | None | 3680 | 0.616 | 3680 | 0.616 | 1.11 | 1.31 | -0.00511
CFLNoneSCERSDNewCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | RSD | New | CZ10 | 3.68 | 0.000616 | 0 | 4.11 | 0.000807 | -0.0192 | 3.68 | 0.000616 | 0 | 4.11 | 0.000807 | -0.0192 | CFL | None | 3680 | 0.616 | 3680 | 0.616 | 1.12 | 1.31 | -0.00522
CFLNoneSDGRSDNewCZ10 | Com-Iltg-dWatt-CFL_OSnone | SDG | RSD | New | CZ10 | 3.68 | 0.000616 | 0 | 4.11 | 0.00081 | -0.0199 | 3.68 | 0.000616 | 0 | 4.11 | 0.00081 | -0.0199 | CFL | None | 3680 | 0.616 | 3680 | 0.616 | 1.12 | 1.31 | -0.00541
CFLNonePGERSDNewCZ11 | Com-Iltg-dWatt-CFL_OSnone | PGE | RSD | New | CZ11 | 3.68 | 0.000616 | 0 | 3.89 | 0.000766 | -0.0258 | 3.68 | 0.000616 | 0 | 3.89 | 0.000766 | -0.0258 | CFL | None | 3680 | 0.616 | 3680 | 0.616 | 1.06 | 1.24 | -0.00701
CFLNonePGERSDNewCZ12 | Com-Iltg-dWatt-CFL_OSnone | PGE | RSD | New | CZ12 | 3.68 | 0.000616 | 0 | 3.83 | 0.000738 | -0.026 | 3.68 | 0.000616 | 0 | 3.83 | 0.000738 | -0.026 | CFL | None | 3680 | 0.616 | 3680 | 0.616 | 1.04 | 1.2 | -0.00707
CFLNonePGERSDNewCZ13 | Com-Iltg-dWatt-CFL_OSnone | PGE | RSD | New | CZ13 | 3.68 | 0.000616 | 0 | 3.9 | 0.000764 | -0.0247 | 3.68 | 0.000616 | 0 | 3.9 | 0.000764 | -0.0247 | CFL | None | 3680 | 0.616 | 3680 | 0.616 | 1.06 | 1.24 | -0.00671
CFLNoneSCERSDNewCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | RSD | New | CZ13 | 3.68 | 0.000616 | 0 | 4.07 | 0.000811 | -0.0278 | 3.68 | 0.000616 | 0 | 4.07 | 0.000811 | -0.0278 | CFL | None | 3680 | 0.616 | 3680 | 0.616 | 1.11 | 1.32 | -0.00755
CFLNoneSCERSDNewCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | RSD | New | CZ14 | 3.68 | 0.000616 | 0 | 4.06 | 0.000805 | -0.0286 | 3.68 | 0.000616 | 0 | 4.06 | 0.000805 | -0.0286 | CFL | None | 3680 | 0.616 | 3680 | 0.616 | 1.1 | 1.31 | -0.00777
CFLNoneSDGRSDNewCZ14 | Com-Iltg-dWatt-CFL_OSnone | SDG | RSD | New | CZ14 | 3.68 | 0.000616 | 0 | 4.05 | 0.000808 | -0.0296 | 3.68 | 0.000616 | 0 | 4.05 | 0.000808 | -0.0296 | CFL | None | 3680 | 0.616 | 3680 | 0.616 | 1.1 | 1.31 | -0.00804
CFLNoneSDGRSDNewCZ15 | Com-Iltg-dWatt-CFL_OSnone | SDG | RSD | New | CZ15 | 3.68 | 0.000616 | 0 | 4.42 | 0.000835 | -0.00861 | 3.68 | 0.000616 | 0 | 4.42 | 0.000835 | -0.00861 | CFL | None | 3680 | 0.616 | 3680 | 0.616 | 1.2 | 1.36 | -0.00234
CFLNoneSCERSDNewCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | RSD | New | CZ15 | 3.68 | 0.000616 | 0 | 4.41 | 0.000832 | -0.00832 | 3.68 | 0.000616 | 0 | 4.41 | 0.000832 | -0.00832 | CFL | None | 3680 | 0.616 | 3680 | 0.616 | 1.2 | 1.35 | -0.00226
CFLNonePGERSDNewCZ16 | Com-Iltg-dWatt-CFL_OSnone | PGE | RSD | New | CZ16 | 3.68 | 0.000616 | 0 | 3.57 | 0.000726 | -0.0345 | 3.68 | 0.000616 | 0 | 3.57 | 0.000726 | -0.0345 | CFL | None | 3680 | 0.616 | 3680 | 0.616 | 0.97 | 1.18 | -0.00938
CFLNoneSCERSDNewCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | RSD | New | CZ16 | 3.68 | 0.000616 | 0 | 3.73 | 0.000762 | -0.039 | 3.68 | 0.000616 | 0 | 3.73 | 0.000762 | -0.039 | CFL | None | 3680 | 0.616 | 3680 | 0.616 | 1.01 | 1.24 | -0.0106
CFLNoneSDGRSDNewIOU | Com-Iltg-dWatt-CFL_OSnone | SDG | RSD | New | IOU | 3.68 | 0.000616 | 0 | 4.02 | 0.000779 | -0.0195 | 3.68 | 0.000616 | 0 | 4.02 | 0.000779 | -0.0195 | CFL | None | 3680 | 0.616 | 3680 | 0.616 | 1.09 | 1.26 | -0.0053
CFLNoneSCERSDNewIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | RSD | New | IOU | 3.68 | 0.000616 | 0 | 4.06 | 0.000762 | -0.0194 | 3.68 | 0.000616 | 0 | 4.06 | 0.000762 | -0.0194 | CFL | None | 3680 | 0.616 | 3680 | 0.616 | 1.1 | 1.24 | -0.00527
CFLNoneSCGRSDNewIOU | Com-Iltg-dWatt-CFL_OSnone | SCG | RSD | New | IOU | 3.68 | 0.000616 | 0 | 4.06 | 0.000758 | -0.0194 | 3.68 | 0.000616 | 0 | 4.06 | 0.000758 | -0.0194 | CFL | None | 3680 | 0.616 | 3680 | 0.616 | 1.1 | 1.23 | -0.00527
CFLNonePGERSDNewIOU | Com-Iltg-dWatt-CFL_OSnone | PGE | RSD | New | IOU | 3.68 | 0.000616 | 0 | 4.02 | 0.000801 | -0.0295 | 3.68 | 0.000616 | 0 | 4.02 | 0.000801 | -0.0295 | CFL | None | 3680 | 0.616 | 3680 | 0.616 | 1.09 | 1.3 | -0.00802
CFLNonePGERt3ExCZ01 | Com-Iltg-dWatt-CFL_OSnone | PGE | Rt3 | Ex | CZ01 | 1.89 | 0.000609 | 0 | 1.81 | 0.000755 | -0.0278 | 1.89 | 0.000609 | 0 | 1.81 | 0.000755 | -0.0278 | CFL | None | 1890 | 0.609 | 1890 | 0.609 | 0.958 | 1.24 | -0.0147
CFLNonePGERt3ExCZ02 | Com-Iltg-dWatt-CFL_OSnone | PGE | Rt3 | Ex | CZ02 | 1.89 | 0.000609 | 0 | 1.99 | 0.000741 | -0.0141 | 1.89 | 0.000609 | 0 | 1.99 | 0.000741 | -0.0141 | CFL | None | 1890 | 0.609 | 1890 | 0.609 | 1.05 | 1.22 | -0.00746
CFLNonePGERt3ExCZ03 | Com-Iltg-dWatt-CFL_OSnone | PGE | Rt3 | Ex | CZ03 | 1.89 | 0.000609 | 0 | 2 | 0.000745 | -0.0135 | 1.89 | 0.000609 | 0 | 2 | 0.000745 | -0.0135 | CFL | None | 1890 | 0.609 | 1890 | 0.609 | 1.06 | 1.22 | -0.00714
CFLNonePGERt3ExCZ04 | Com-Iltg-dWatt-CFL_OSnone | PGE | Rt3 | Ex | CZ04 | 1.89 | 0.000609 | 0 | 2.03 | 0.000744 | -0.00932 | 1.89 | 0.000609 | 0 | 2.03 | 0.000744 | -0.00932 | CFL | None | 1890 | 0.609 | 1890 | 0.609 | 1.07 | 1.22 | -0.00493
CFLNoneSCGRt3ExCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCG | Rt3 | Ex | CZ05 | 1.89 | 0.000609 | 0 | 2.03 | 0.000769 | -0.0106 | 1.89 | 0.000609 | 0 | 2.03 | 0.000769 | -0.0106 | CFL | None | 1890 | 0.609 | 1890 | 0.609 | 1.07 | 1.26 | -0.00561
CFLNonePGERt3ExCZ05 | Com-Iltg-dWatt-CFL_OSnone | PGE | Rt3 | Ex | CZ05 | 1.89 | 0.000609 | 0 | 2.03 | 0.000769 | -0.0106 | 1.89 | 0.000609 | 0 | 2.03 | 0.000769 | -0.0106 | CFL | None | 1890 | 0.609 | 1890 | 0.609 | 1.07 | 1.26 | -0.00561
CFLNoneSCERt3ExCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | Rt3 | Ex | CZ05 | 1.89 | 0.000609 | 0 | 2.03 | 0.000769 | -0.0106 | 1.89 | 0.000609 | 0 | 2.03 | 0.000769 | -0.0106 | CFL | None | 1890 | 0.609 | 1890 | 0.609 | 1.07 | 1.26 | -0.00561
CFLNoneSCGRt3ExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCG | Rt3 | Ex | CZ06 | 1.89 | 0.000609 | 0 | 2.15 | 0.000765 | -0.00272 | 1.89 | 0.000609 | 0 | 2.15 | 0.000765 | -0.00272 | CFL | None | 1890 | 0.609 | 1890 | 0.609 | 1.14 | 1.26 | -0.00144
CFLNoneSDGRt3ExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SDG | Rt3 | Ex | CZ06 | 1.89 | 0.000609 | 0 | 2.15 | 0.000765 | -0.00272 | 1.89 | 0.000609 | 0 | 2.15 | 0.000765 | -0.00272 | CFL | None | 1890 | 0.609 | 1890 | 0.609 | 1.14 | 1.26 | -0.00144
CFLNoneSCERt3ExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | Rt3 | Ex | CZ06 | 1.89 | 0.000609 | 0 | 2.15 | 0.000765 | -0.00272 | 1.89 | 0.000609 | 0 | 2.15 | 0.000765 | -0.00272 | CFL | None | 1890 | 0.609 | 1890 | 0.609 | 1.14 | 1.26 | -0.00144
CFLNoneSDGRt3ExCZ07 | Com-Iltg-dWatt-CFL_OSnone | SDG | Rt3 | Ex | CZ07 | 1.89 | 0.000609 | 0 | 2.16 | 0.000751 | -0.00125 | 1.89 | 0.000609 | 0 | 2.16 | 0.000751 | -0.00125 | CFL | None | 1890 | 0.609 | 1890 | 0.609 | 1.14 | 1.23 | -0.000661
CFLNoneSDGRt3ExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SDG | Rt3 | Ex | CZ08 | 1.89 | 0.000609 | 0 | 2.16 | 0.000753 | -0.00236 | 1.89 | 0.000609 | 0 | 2.16 | 0.000753 | -0.00236 | CFL | None | 1890 | 0.609 | 1890 | 0.609 | 1.14 | 1.24 | -0.00125
CFLNoneSCERt3ExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | Rt3 | Ex | CZ08 | 1.89 | 0.000609 | 0 | 2.16 | 0.000753 | -0.00236 | 1.89 | 0.000609 | 0 | 2.16 | 0.000753 | -0.00236 | CFL | None | 1890 | 0.609 | 1890 | 0.609 | 1.14 | 1.24 | -0.00125
CFLNoneSCGRt3ExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCG | Rt3 | Ex | CZ08 | 1.89 | 0.000609 | 0 | 2.16 | 0.000753 | -0.00236 | 1.89 | 0.000609 | 0 | 2.16 | 0.000753 | -0.00236 | CFL | None | 1890 | 0.609 | 1890 | 0.609 | 1.14 | 1.24 | -0.00125
CFLNoneSCGRt3ExCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCG | Rt3 | Ex | CZ09 | 1.89 | 0.000609 | 0 | 2.15 | 0.000769 | -0.00369 | 1.89 | 0.000609 | 0 | 2.15 | 0.000769 | -0.00369 | CFL | None | 1890 | 0.609 | 1890 | 0.609 | 1.14 | 1.26 | -0.00195
CFLNoneSCERt3ExCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | Rt3 | Ex | CZ09 | 1.89 | 0.000609 | 0 | 2.15 | 0.000769 | -0.00369 | 1.89 | 0.000609 | 0 | 2.15 | 0.000769 | -0.00369 | CFL | None | 1890 | 0.609 | 1890 | 0.609 | 1.14 | 1.26 | -0.00195
CFLNoneSCERt3ExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | Rt3 | Ex | CZ10 | 1.89 | 0.000609 | 0 | 2.13 | 0.000763 | -0.00416 | 1.89 | 0.000609 | 0 | 2.13 | 0.000763 | -0.00416 | CFL | None | 1890 | 0.609 | 1890 | 0.609 | 1.13 | 1.25 | -0.0022
CFLNoneSDGRt3ExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SDG | Rt3 | Ex | CZ10 | 1.89 | 0.000609 | 0 | 2.13 | 0.000763 | -0.00416 | 1.89 | 0.000609 | 0 | 2.13 | 0.000763 | -0.00416 | CFL | None | 1890 | 0.609 | 1890 | 0.609 | 1.13 | 1.25 | -0.0022
CFLNoneSCGRt3ExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCG | Rt3 | Ex | CZ10 | 1.89 | 0.000609 | 0 | 2.13 | 0.000763 | -0.00416 | 1.89 | 0.000609 | 0 | 2.13 | 0.000763 | -0.00416 | CFL | None | 1890 | 0.609 | 1890 | 0.609 | 1.13 | 1.25 | -0.0022
CFLNonePGERt3ExCZ11 | Com-Iltg-dWatt-CFL_OSnone | PGE | Rt3 | Ex | CZ11 | 1.89 | 0.000609 | 0 | 2 | 0.000747 | -0.0134 | 1.89 | 0.000609 | 0 | 2 | 0.000747 | -0.0134 | CFL | None | 1890 | 0.609 | 1890 | 0.609 | 1.06 | 1.23 | -0.00709
CFLNonePGERt3ExCZ12 | Com-Iltg-dWatt-CFL_OSnone | PGE | Rt3 | Ex | CZ12 | 1.89 | 0.000609 | 0 | 2 | 0.000751 | -0.013 | 1.89 | 0.000609 | 0 | 2 | 0.000751 | -0.013 | CFL | None | 1890 | 0.609 | 1890 | 0.609 | 1.06 | 1.23 | -0.00688
CFLNonePGERt3ExCZ13 | Com-Iltg-dWatt-CFL_OSnone | PGE | Rt3 | Ex | CZ13 | 1.89 | 0.000609 | 0 | 2.05 | 0.000775 | -0.0118 | 1.89 | 0.000609 | 0 | 2.05 | 0.000775 | -0.0118 | CFL | None | 1890 | 0.609 | 1890 | 0.609 | 1.08 | 1.27 | -0.00624
CFLNoneSCGRt3ExCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCG | Rt3 | Ex | CZ13 | 1.89 | 0.000609 | 0 | 2.05 | 0.000775 | -0.0118 | 1.89 | 0.000609 | 0 | 2.05 | 0.000775 | -0.0118 | CFL | None | 1890 | 0.609 | 1890 | 0.609 | 1.08 | 1.27 | -0.00624
CFLNoneSCERt3ExCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | Rt3 | Ex | CZ13 | 1.89 | 0.000609 | 0 | 2.05 | 0.000775 | -0.0118 | 1.89 | 0.000609 | 0 | 2.05 | 0.000775 | -0.0118 | CFL | None | 1890 | 0.609 | 1890 | 0.609 | 1.08 | 1.27 | -0.00624
CFLNoneSCERt3ExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | Rt3 | Ex | CZ14 | 1.89 | 0.000609 | 0 | 2.03 | 0.000769 | -0.0128 | 1.89 | 0.000609 | 0 | 2.03 | 0.000769 | -0.0128 | CFL | None | 1890 | 0.609 | 1890 | 0.609 | 1.07 | 1.26 | -0.00677
CFLNoneSDGRt3ExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SDG | Rt3 | Ex | CZ14 | 1.89 | 0.000609 | 0 | 2.03 | 0.000769 | -0.0128 | 1.89 | 0.000609 | 0 | 2.03 | 0.000769 | -0.0128 | CFL | None | 1890 | 0.609 | 1890 | 0.609 | 1.07 | 1.26 | -0.00677
CFLNoneSCGRt3ExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCG | Rt3 | Ex | CZ14 | 1.89 | 0.000609 | 0 | 2.03 | 0.000769 | -0.0128 | 1.89 | 0.000609 | 0 | 2.03 | 0.000769 | -0.0128 | CFL | None | 1890 | 0.609 | 1890 | 0.609 | 1.07 | 1.26 | -0.00677
CFLNoneSCGRt3ExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCG | Rt3 | Ex | CZ15 | 1.89 | 0.000609 | 0 | 2.2 | 0.000784 | -0.00106 | 1.89 | 0.000609 | 0 | 2.2 | 0.000784 | -0.00106 | CFL | None | 1890 | 0.609 | 1890 | 0.609 | 1.16 | 1.29 | -0.000561
CFLNoneSCERt3ExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | Rt3 | Ex | CZ15 | 1.89 | 0.000609 | 0 | 2.2 | 0.000784 | -0.00106 | 1.89 | 0.000609 | 0 | 2.2 | 0.000784 | -0.00106 | CFL | None | 1890 | 0.609 | 1890 | 0.609 | 1.16 | 1.29 | -0.000561
CFLNoneSDGRt3ExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SDG | Rt3 | Ex | CZ15 | 1.89 | 0.000609 | 0 | 2.2 | 0.000784 | -0.00106 | 1.89 | 0.000609 | 0 | 2.2 | 0.000784 | -0.00106 | CFL | None | 1890 | 0.609 | 1890 | 0.609 | 1.16 | 1.29 | -0.000561
CFLNonePGERt3ExCZ16 | Com-Iltg-dWatt-CFL_OSnone | PGE | Rt3 | Ex | CZ16 | 1.89 | 0.000609 | 0 | 1.85 | 0.000753 | -0.0244 | 1.89 | 0.000609 | 0 | 1.85 | 0.000753 | -0.0244 | CFL | None | 1890 | 0.609 | 1890 | 0.609 | 0.979 | 1.24 | -0.0129
CFLNoneSCGRt3ExCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCG | Rt3 | Ex | CZ16 | 1.89 | 0.000609 | 0 | 1.85 | 0.000753 | -0.0244 | 1.89 | 0.000609 | 0 | 1.85 | 0.000753 | -0.0244 | CFL | None | 1890 | 0.609 | 1890 | 0.609 | 0.979 | 1.24 | -0.0129
CFLNoneSCERt3ExCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | Rt3 | Ex | CZ16 | 1.89 | 0.000609 | 0 | 1.85 | 0.000753 | -0.0244 | 1.89 | 0.000609 | 0 | 1.85 | 0.000753 | -0.0244 | CFL | None | 1890 | 0.609 | 1890 | 0.609 | 0.979 | 1.24 | -0.0129
CFLNoneSCERt3ExIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | Rt3 | Ex | IOU | 1.89 | 0.000609 | 0 | 2.14 | 0.000763 | -0.0039 | 1.89 | 0.000609 | 0 | 2.14 | 0.000763 | -0.0039 | CFL | None | 1890 | 0.609 | 1890 | 0.609 | 1.13 | 1.25 | -0.00206
CFLNonePGERt3ExIOU | Com-Iltg-dWatt-CFL_OSnone | PGE | Rt3 | Ex | IOU | 1.89 | 0.000609 | 0 | 2.01 | 0.000751 | -0.0127 | 1.89 | 0.000609 | 0 | 2.01 | 0.000751 | -0.0127 | CFL | None | 1890 | 0.609 | 1890 | 0.609 | 1.06 | 1.23 | -0.00672
CFLNoneSDGRt3ExIOU | Com-Iltg-dWatt-CFL_OSnone | SDG | Rt3 | Ex | IOU | 1.89 | 0.000609 | 0 | 2.15 | 0.000755 | -0.00209 | 1.89 | 0.000609 | 0 | 2.15 | 0.000755 | -0.00209 | CFL | None | 1890 | 0.609 | 1890 | 0.609 | 1.14 | 1.24 | -0.00111
CFLNoneSCGRt3ExIOU | Com-Iltg-dWatt-CFL_OSnone | SCG | Rt3 | Ex | IOU | 1.89 | 0.000609 | 0 | 2.14 | 0.000763 | -0.00379 | 1.89 | 0.000609 | 0 | 2.14 | 0.000763 | -0.00379 | CFL | None | 1890 | 0.609 | 1890 | 0.609 | 1.13 | 1.25 | -0.00201
CFLNonePGERt3NewCZ01 | Com-Iltg-dWatt-CFL_OSnone | PGE | Rt3 | New | CZ01 | 1.89 | 0.000609 | 0 | 1.78 | 0.000742 | -0.0306 | 1.89 | 0.000609 | 0 | 1.78 | 0.000742 | -0.0306 | CFL | None | 1890 | 0.609 | 1890 | 0.609 | 0.942 | 1.22 | -0.0162
CFLNonePGERt3NewCZ02 | Com-Iltg-dWatt-CFL_OSnone | PGE | Rt3 | New | CZ02 | 1.89 | 0.000609 | 0 | 1.93 | 0.000723 | -0.0165 | 1.89 | 0.000609 | 0 | 1.93 | 0.000723 | -0.0165 | CFL | None | 1890 | 0.609 | 1890 | 0.609 | 1.02 | 1.19 | -0.00873
CFLNonePGERt3NewCZ03 | Com-Iltg-dWatt-CFL_OSnone | PGE | Rt3 | New | CZ03 | 1.89 | 0.000609 | 0 | 1.92 | 0.000729 | -0.0168 | 1.89 | 0.000609 | 0 | 1.92 | 0.000729 | -0.0168 | CFL | None | 1890 | 0.609 | 1890 | 0.609 | 1.02 | 1.2 | -0.00889
CFLNonePGERt3NewCZ04 | Com-Iltg-dWatt-CFL_OSnone | PGE | Rt3 | New | CZ04 | 1.89 | 0.000609 | 0 | 1.97 | 0.000733 | -0.012 | 1.89 | 0.000609 | 0 | 1.97 | 0.000733 | -0.012 | CFL | None | 1890 | 0.609 | 1890 | 0.609 | 1.04 | 1.2 | -0.00635
CFLNonePGERt3NewCZ05 | Com-Iltg-dWatt-CFL_OSnone | PGE | Rt3 | New | CZ05 | 1.89 | 0.000609 | 0 | 1.93 | 0.000725 | -0.0139 | 1.89 | 0.000609 | 0 | 1.93 | 0.000725 | -0.0139 | CFL | None | 1890 | 0.609 | 1890 | 0.609 | 1.02 | 1.19 | -0.00735
CFLNoneSCERt3NewCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | Rt3 | New | CZ05 | 1.89 | 0.000609 | 0 | 1.96 | 0.000753 | -0.0131 | 1.89 | 0.000609 | 0 | 1.96 | 0.000753 | -0.0131 | CFL | None | 1890 | 0.609 | 1890 | 0.609 | 1.04 | 1.24 | -0.00693
CFLNoneSCERt3NewCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | Rt3 | New | CZ06 | 1.89 | 0.000609 | 0 | 2.1 | 0.000745 | -0.00395 | 1.89 | 0.000609 | 0 | 2.1 | 0.000745 | -0.00395 | CFL | None | 1890 | 0.609 | 1890 | 0.609 | 1.11 | 1.22 | -0.00209
CFLNoneSDGRt3NewCZ06 | Com-Iltg-dWatt-CFL_OSnone | SDG | Rt3 | New | CZ06 | 1.89 | 0.000609 | 0 | 2.09 | 0.000744 | -0.00404 | 1.89 | 0.000609 | 0 | 2.09 | 0.000744 | -0.00404 | CFL | None | 1890 | 0.609 | 1890 | 0.609 | 1.11 | 1.22 | -0.00214
CFLNoneSDGRt3NewCZ07 | Com-Iltg-dWatt-CFL_OSnone | SDG | Rt3 | New | CZ07 | 1.89 | 0.000609 | 0 | 2.11 | 0.00072 | -0.00193 | 1.89 | 0.000609 | 0 | 2.11 | 0.00072 | -0.00193 | CFL | None | 1890 | 0.609 | 1890 | 0.609 | 1.12 | 1.18 | -0.00102
CFLNoneSDGRt3NewCZ08 | Com-Iltg-dWatt-CFL_OSnone | SDG | Rt3 | New | CZ08 | 1.89 | 0.000609 | 0 | 2.11 | 0.000734 | -0.00329 | 1.89 | 0.000609 | 0 | 2.11 | 0.000734 | -0.00329 | CFL | None | 1890 | 0.609 | 1890 | 0.609 | 1.12 | 1.21 | -0.00174
CFLNoneSCERt3NewCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | Rt3 | New | CZ08 | 1.89 | 0.000609 | 0 | 2.11 | 0.000736 | -0.00323 | 1.89 | 0.000609 | 0 | 2.11 | 0.000736 | -0.00323 | CFL | None | 1890 | 0.609 | 1890 | 0.609 | 1.12 | 1.21 | -0.00171
CFLNoneSCERt3NewCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | Rt3 | New | CZ09 | 1.89 | 0.000609 | 0 | 2.09 | 0.000753 | -0.00486 | 1.89 | 0.000609 | 0 | 2.09 | 0.000753 | -0.00486 | CFL | None | 1890 | 0.609 | 1890 | 0.609 | 1.11 | 1.24 | -0.00257
CFLNoneSDGRt3NewCZ10 | Com-Iltg-dWatt-CFL_OSnone | SDG | Rt3 | New | CZ10 | 1.89 | 0.000609 | 0 | 2.09 | 0.000758 | -0.00571 | 1.89 | 0.000609 | 0 | 2.09 | 0.000758 | -0.00571 | CFL | None | 1890 | 0.609 | 1890 | 0.609 | 1.11 | 1.24 | -0.00302
CFLNoneSCERt3NewCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | Rt3 | New | CZ10 | 1.89 | 0.000609 | 0 | 2.09 | 0.00076 | -0.00559 | 1.89 | 0.000609 | 0 | 2.09 | 0.00076 | -0.00559 | CFL | None | 1890 | 0.609 | 1890 | 0.609 | 1.11 | 1.25 | -0.00296
CFLNonePGERt3NewCZ11 | Com-Iltg-dWatt-CFL_OSnone | PGE | Rt3 | New | CZ11 | 1.89 | 0.000609 | 0 | 1.98 | 0.00075 | -0.0142 | 1.89 | 0.000609 | 0 | 1.98 | 0.00075 | -0.0142 | CFL | None | 1890 | 0.609 | 1890 | 0.609 | 1.05 | 1.23 | -0.00751
CFLNonePGERt3NewCZ12 | Com-Iltg-dWatt-CFL_OSnone | PGE | Rt3 | New | CZ12 | 1.89 | 0.000609 | 0 | 1.97 | 0.000747 | -0.0152 | 1.89 | 0.000609 | 0 | 1.97 | 0.000747 | -0.0152 | CFL | None | 1890 | 0.609 | 1890 | 0.609 | 1.04 | 1.23 | -0.00804
CFLNonePGERt3NewCZ13 | Com-Iltg-dWatt-CFL_OSnone | PGE | Rt3 | New | CZ13 | 1.89 | 0.000609 | 0 | 1.99 | 0.000742 | -0.0137 | 1.89 | 0.000609 | 0 | 1.99 | 0.000742 | -0.0137 | CFL | None | 1890 | 0.609 | 1890 | 0.609 | 1.05 | 1.22 | -0.00725
CFLNoneSCERt3NewCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | Rt3 | New | CZ13 | 1.89 | 0.000609 | 0 | 2.03 | 0.000773 | -0.0129 | 1.89 | 0.000609 | 0 | 2.03 | 0.000773 | -0.0129 | CFL | None | 1890 | 0.609 | 1890 | 0.609 | 1.07 | 1.27 | -0.00683
CFLNoneSCERt3NewCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | Rt3 | New | CZ14 | 1.89 | 0.000609 | 0 | 2.02 | 0.000765 | -0.0134 | 1.89 | 0.000609 | 0 | 2.02 | 0.000765 | -0.0134 | CFL | None | 1890 | 0.609 | 1890 | 0.609 | 1.07 | 1.26 | -0.00709
CFLNoneSDGRt3NewCZ14 | Com-Iltg-dWatt-CFL_OSnone | SDG | Rt3 | New | CZ14 | 1.89 | 0.000609 | 0 | 2.02 | 0.000762 | -0.0138 | 1.89 | 0.000609 | 0 | 2.02 | 0.000762 | -0.0138 | CFL | None | 1890 | 0.609 | 1890 | 0.609 | 1.07 | 1.25 | -0.0073
CFLNoneSCERt3NewCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | Rt3 | New | CZ15 | 1.89 | 0.000609 | 0 | 2.21 | 0.000814 | -0.000856 | 1.89 | 0.000609 | 0 | 2.21 | 0.000814 | -0.000856 | CFL | None | 1890 | 0.609 | 1890 | 0.609 | 1.17 | 1.34 | -0.000453
CFLNoneSDGRt3NewCZ15 | Com-Iltg-dWatt-CFL_OSnone | SDG | Rt3 | New | CZ15 | 1.89 | 0.000609 | 0 | 2.2 | 0.000812 | -0.000858 | 1.89 | 0.000609 | 0 | 2.2 | 0.000812 | -0.000858 | CFL | None | 1890 | 0.609 | 1890 | 0.609 | 1.16 | 1.33 | -0.000454
CFLNoneSCERt3NewCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | Rt3 | New | CZ16 | 1.89 | 0.000609 | 0 | 1.83 | 0.000687 | -0.0232 | 1.89 | 0.000609 | 0 | 1.83 | 0.000687 | -0.0232 | CFL | None | 1890 | 0.609 | 1890 | 0.609 | 0.968 | 1.13 | -0.0123
CFLNonePGERt3NewCZ16 | Com-Iltg-dWatt-CFL_OSnone | PGE | Rt3 | New | CZ16 | 1.89 | 0.000609 | 0 | 1.8 | 0.00067 | -0.0248 | 1.89 | 0.000609 | 0 | 1.8 | 0.00067 | -0.0248 | CFL | None | 1890 | 0.609 | 1890 | 0.609 | 0.952 | 1.1 | -0.0131
CFLNoneSCGRt3NewIOU | Com-Iltg-dWatt-CFL_OSnone | SCG | Rt3 | New | IOU | 1.89 | 0.000609 | 0 | 2.1 | 0.000751 | -0.00483 | 1.89 | 0.000609 | 0 | 2.1 | 0.000751 | -0.00483 | CFL | None | 1890 | 0.609 | 1890 | 0.609 | 1.11 | 1.23 | -0.00256
CFLNoneSCERt3NewIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | Rt3 | New | IOU | 1.89 | 0.000609 | 0 | 2.1 | 0.000752 | -0.00492 | 1.89 | 0.000609 | 0 | 2.1 | 0.000752 | -0.00492 | CFL | None | 1890 | 0.609 | 1890 | 0.609 | 1.11 | 1.23 | -0.0026
CFLNonePGERt3NewIOU | Com-Iltg-dWatt-CFL_OSnone | PGE | Rt3 | New | IOU | 1.89 | 0.000609 | 0 | 2.02 | 0.00077 | -0.0131 | 1.89 | 0.000609 | 0 | 2.02 | 0.00077 | -0.0131 | CFL | None | 1890 | 0.609 | 1890 | 0.609 | 1.07 | 1.26 | -0.00693
CFLNoneSDGRt3NewIOU | Com-Iltg-dWatt-CFL_OSnone | SDG | Rt3 | New | IOU | 1.89 | 0.000609 | 0 | 2.1 | 0.000731 | -0.00302 | 1.89 | 0.000609 | 0 | 2.1 | 0.000731 | -0.00302 | CFL | None | 1890 | 0.609 | 1890 | 0.609 | 1.11 | 1.2 | -0.0016
CFLNonePGERtLExCZ01 | Com-Iltg-dWatt-CFL_OSnone | PGE | RtL | Ex | CZ01 | 2.94 | 0.000802 | 0 | 2.85 | 0.000977 | -0.0397 | 2.94 | 0.000802 | 0 | 2.85 | 0.000977 | -0.0397 | CFL | None | 2940 | 0.802 | 2940 | 0.802 | 0.969 | 1.22 | -0.0135
CFLNonePGERtLExCZ02 | Com-Iltg-dWatt-CFL_OSnone | PGE | RtL | Ex | CZ02 | 2.94 | 0.000802 | 0 | 3.09 | 0.000974 | -0.0206 | 2.94 | 0.000802 | 0 | 3.09 | 0.000974 | -0.0206 | CFL | None | 2940 | 0.802 | 2940 | 0.802 | 1.05 | 1.21 | -0.00701
CFLNonePGERtLExCZ03 | Com-Iltg-dWatt-CFL_OSnone | PGE | RtL | Ex | CZ03 | 2.94 | 0.000802 | 0 | 3.11 | 0.00097 | -0.0194 | 2.94 | 0.000802 | 0 | 3.11 | 0.00097 | -0.0194 | CFL | None | 2940 | 0.802 | 2940 | 0.802 | 1.06 | 1.21 | -0.0066
CFLNonePGERtLExCZ04 | Com-Iltg-dWatt-CFL_OSnone | PGE | RtL | Ex | CZ04 | 2.94 | 0.000802 | 0 | 3.15 | 0.000975 | -0.0145 | 2.94 | 0.000802 | 0 | 3.15 | 0.000975 | -0.0145 | CFL | None | 2940 | 0.802 | 2940 | 0.802 | 1.07 | 1.22 | -0.00493
CFLNoneSCERtLExCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | RtL | Ex | CZ05 | 2.94 | 0.000802 | 0 | 3.15 | 0.000999 | -0.0176 | 2.94 | 0.000802 | 0 | 3.15 | 0.000999 | -0.0176 | CFL | None | 2940 | 0.802 | 2940 | 0.802 | 1.07 | 1.25 | -0.00599
CFLNonePGERtLExCZ05 | Com-Iltg-dWatt-CFL_OSnone | PGE | RtL | Ex | CZ05 | 2.94 | 0.000802 | 0 | 3.15 | 0.000999 | -0.0176 | 2.94 | 0.000802 | 0 | 3.15 | 0.000999 | -0.0176 | CFL | None | 2940 | 0.802 | 2940 | 0.802 | 1.07 | 1.25 | -0.00599
CFLNoneSCGRtLExCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCG | RtL | Ex | CZ05 | 2.94 | 0.000802 | 0 | 3.15 | 0.000999 | -0.0176 | 2.94 | 0.000802 | 0 | 3.15 | 0.000999 | -0.0176 | CFL | None | 2940 | 0.802 | 2940 | 0.802 | 1.07 | 1.25 | -0.00599
CFLNoneSCGRtLExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCG | RtL | Ex | CZ06 | 2.94 | 0.000802 | 0 | 3.31 | 0.00101 | -0.00726 | 2.94 | 0.000802 | 0 | 3.31 | 0.00101 | -0.00726 | CFL | None | 2940 | 0.802 | 2940 | 0.802 | 1.13 | 1.26 | -0.00247
CFLNoneSDGRtLExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SDG | RtL | Ex | CZ06 | 2.94 | 0.000802 | 0 | 3.31 | 0.00101 | -0.00726 | 2.94 | 0.000802 | 0 | 3.31 | 0.00101 | -0.00726 | CFL | None | 2940 | 0.802 | 2940 | 0.802 | 1.13 | 1.26 | -0.00247
CFLNoneSCERtLExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | RtL | Ex | CZ06 | 2.94 | 0.000802 | 0 | 3.31 | 0.00101 | -0.00726 | 2.94 | 0.000802 | 0 | 3.31 | 0.00101 | -0.00726 | CFL | None | 2940 | 0.802 | 2940 | 0.802 | 1.13 | 1.26 | -0.00247
CFLNoneSDGRtLExCZ07 | Com-Iltg-dWatt-CFL_OSnone | SDG | RtL | Ex | CZ07 | 2.94 | 0.000802 | 0 | 3.33 | 0.00101 | -0.0052 | 2.94 | 0.000802 | 0 | 3.33 | 0.00101 | -0.0052 | CFL | None | 2940 | 0.802 | 2940 | 0.802 | 1.13 | 1.26 | -0.00177
CFLNoneSDGRtLExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SDG | RtL | Ex | CZ08 | 2.94 | 0.000802 | 0 | 3.32 | 0.00101 | -0.00623 | 2.94 | 0.000802 | 0 | 3.32 | 0.00101 | -0.00623 | CFL | None | 2940 | 0.802 | 2940 | 0.802 | 1.13 | 1.26 | -0.00212
CFLNoneSCERtLExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | RtL | Ex | CZ08 | 2.94 | 0.000802 | 0 | 3.32 | 0.00101 | -0.00623 | 2.94 | 0.000802 | 0 | 3.32 | 0.00101 | -0.00623 | CFL | None | 2940 | 0.802 | 2940 | 0.802 | 1.13 | 1.26 | -0.00212
CFLNoneSCGRtLExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCG | RtL | Ex | CZ08 | 2.94 | 0.000802 | 0 | 3.32 | 0.00101 | -0.00623 | 2.94 | 0.000802 | 0 | 3.32 | 0.00101 | -0.00623 | CFL | None | 2940 | 0.802 | 2940 | 0.802 | 1.13 | 1.26 | -0.00212
CFLNoneSCGRtLExCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCG | RtL | Ex | CZ09 | 2.94 | 0.000802 | 0 | 3.32 | 0.00104 | -0.00735 | 2.94 | 0.000802 | 0 | 3.32 | 0.00104 | -0.00735 | CFL | None | 2940 | 0.802 | 2940 | 0.802 | 1.13 | 1.3 | -0.0025
CFLNoneSCERtLExCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | RtL | Ex | CZ09 | 2.94 | 0.000802 | 0 | 3.32 | 0.00104 | -0.00735 | 2.94 | 0.000802 | 0 | 3.32 | 0.00104 | -0.00735 | CFL | None | 2940 | 0.802 | 2940 | 0.802 | 1.13 | 1.3 | -0.0025
CFLNoneSDGRtLExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SDG | RtL | Ex | CZ10 | 2.94 | 0.000802 | 0 | 3.3 | 0.00103 | -0.00832 | 2.94 | 0.000802 | 0 | 3.3 | 0.00103 | -0.00832 | CFL | None | 2940 | 0.802 | 2940 | 0.802 | 1.12 | 1.28 | -0.00283
CFLNoneSCERtLExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | RtL | Ex | CZ10 | 2.94 | 0.000802 | 0 | 3.3 | 0.00103 | -0.00832 | 2.94 | 0.000802 | 0 | 3.3 | 0.00103 | -0.00832 | CFL | None | 2940 | 0.802 | 2940 | 0.802 | 1.12 | 1.28 | -0.00283
CFLNoneSCGRtLExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCG | RtL | Ex | CZ10 | 2.94 | 0.000802 | 0 | 3.3 | 0.00103 | -0.00832 | 2.94 | 0.000802 | 0 | 3.3 | 0.00103 | -0.00832 | CFL | None | 2940 | 0.802 | 2940 | 0.802 | 1.12 | 1.28 | -0.00283
CFLNonePGERtLExCZ11 | Com-Iltg-dWatt-CFL_OSnone | PGE | RtL | Ex | CZ11 | 2.94 | 0.000802 | 0 | 3.11 | 0.000984 | -0.0196 | 2.94 | 0.000802 | 0 | 3.11 | 0.000984 | -0.0196 | CFL | None | 2940 | 0.802 | 2940 | 0.802 | 1.06 | 1.23 | -0.00667
CFLNonePGERtLExCZ12 | Com-Iltg-dWatt-CFL_OSnone | PGE | RtL | Ex | CZ12 | 2.94 | 0.000802 | 0 | 3.11 | 0.000993 | -0.018 | 2.94 | 0.000802 | 0 | 3.11 | 0.000993 | -0.018 | CFL | None | 2940 | 0.802 | 2940 | 0.802 | 1.06 | 1.24 | -0.00612
CFLNonePGERtLExCZ13 | Com-Iltg-dWatt-CFL_OSnone | PGE | RtL | Ex | CZ13 | 2.94 | 0.000802 | 0 | 3.21 | 0.00103 | -0.0161 | 2.94 | 0.000802 | 0 | 3.21 | 0.00103 | -0.0161 | CFL | None | 2940 | 0.802 | 2940 | 0.802 | 1.09 | 1.28 | -0.00548
CFLNoneSCGRtLExCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCG | RtL | Ex | CZ13 | 2.94 | 0.000802 | 0 | 3.21 | 0.00103 | -0.0161 | 2.94 | 0.000802 | 0 | 3.21 | 0.00103 | -0.0161 | CFL | None | 2940 | 0.802 | 2940 | 0.802 | 1.09 | 1.28 | -0.00548
CFLNoneSCERtLExCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | RtL | Ex | CZ13 | 2.94 | 0.000802 | 0 | 3.21 | 0.00103 | -0.0161 | 2.94 | 0.000802 | 0 | 3.21 | 0.00103 | -0.0161 | CFL | None | 2940 | 0.802 | 2940 | 0.802 | 1.09 | 1.28 | -0.00548
CFLNoneSDGRtLExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SDG | RtL | Ex | CZ14 | 2.94 | 0.000802 | 0 | 3.19 | 0.00105 | -0.017 | 2.94 | 0.000802 | 0 | 3.19 | 0.00105 | -0.017 | CFL | None | 2940 | 0.802 | 2940 | 0.802 | 1.09 | 1.31 | -0.00578
CFLNoneSCERtLExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | RtL | Ex | CZ14 | 2.94 | 0.000802 | 0 | 3.19 | 0.00105 | -0.017 | 2.94 | 0.000802 | 0 | 3.19 | 0.00105 | -0.017 | CFL | None | 2940 | 0.802 | 2940 | 0.802 | 1.09 | 1.31 | -0.00578
CFLNoneSCGRtLExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCG | RtL | Ex | CZ14 | 2.94 | 0.000802 | 0 | 3.19 | 0.00105 | -0.017 | 2.94 | 0.000802 | 0 | 3.19 | 0.00105 | -0.017 | CFL | None | 2940 | 0.802 | 2940 | 0.802 | 1.09 | 1.31 | -0.00578
CFLNoneSCGRtLExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCG | RtL | Ex | CZ15 | 2.94 | 0.000802 | 0 | 3.44 | 0.00105 | -0.00297 | 2.94 | 0.000802 | 0 | 3.44 | 0.00105 | -0.00297 | CFL | None | 2940 | 0.802 | 2940 | 0.802 | 1.17 | 1.31 | -0.00101
CFLNoneSDGRtLExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SDG | RtL | Ex | CZ15 | 2.94 | 0.000802 | 0 | 3.44 | 0.00105 | -0.00297 | 2.94 | 0.000802 | 0 | 3.44 | 0.00105 | -0.00297 | CFL | None | 2940 | 0.802 | 2940 | 0.802 | 1.17 | 1.31 | -0.00101
CFLNoneSCERtLExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | RtL | Ex | CZ15 | 2.94 | 0.000802 | 0 | 3.44 | 0.00105 | -0.00297 | 2.94 | 0.000802 | 0 | 3.44 | 0.00105 | -0.00297 | CFL | None | 2940 | 0.802 | 2940 | 0.802 | 1.17 | 1.31 | -0.00101
CFLNonePGERtLExCZ16 | Com-Iltg-dWatt-CFL_OSnone | PGE | RtL | Ex | CZ16 | 2.94 | 0.000802 | 0 | 2.88 | 0.000986 | -0.0368 | 2.94 | 0.000802 | 0 | 2.88 | 0.000986 | -0.0368 | CFL | None | 2940 | 0.802 | 2940 | 0.802 | 0.98 | 1.23 | -0.0125
CFLNoneSCGRtLExCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCG | RtL | Ex | CZ16 | 2.94 | 0.000802 | 0 | 2.88 | 0.000986 | -0.0368 | 2.94 | 0.000802 | 0 | 2.88 | 0.000986 | -0.0368 | CFL | None | 2940 | 0.802 | 2940 | 0.802 | 0.98 | 1.23 | -0.0125
CFLNoneSCERtLExCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | RtL | Ex | CZ16 | 2.94 | 0.000802 | 0 | 2.88 | 0.000986 | -0.0368 | 2.94 | 0.000802 | 0 | 2.88 | 0.000986 | -0.0368 | CFL | None | 2940 | 0.802 | 2940 | 0.802 | 0.98 | 1.23 | -0.0125
CFLNoneSCGRtLExIOU | Com-Iltg-dWatt-CFL_OSnone | SCG | RtL | Ex | IOU | 2.94 | 0.000802 | 0 | 3.31 | 0.00102 | -0.00784 | 2.94 | 0.000802 | 0 | 3.31 | 0.00102 | -0.00784 | CFL | None | 2940 | 0.802 | 2940 | 0.802 | 1.13 | 1.27 | -0.00267
CFLNonePGERtLExIOU | Com-Iltg-dWatt-CFL_OSnone | PGE | RtL | Ex | IOU | 2.94 | 0.000802 | 0 | 3.13 | 0.000986 | -0.0182 | 2.94 | 0.000802 | 0 | 3.13 | 0.000986 | -0.0182 | CFL | None | 2940 | 0.802 | 2940 | 0.802 | 1.06 | 1.23 | -0.00619
CFLNoneSDGRtLExIOU | Com-Iltg-dWatt-CFL_OSnone | SDG | RtL | Ex | IOU | 2.94 | 0.000802 | 0 | 3.32 | 0.00101 | -0.00611 | 2.94 | 0.000802 | 0 | 3.32 | 0.00101 | -0.00611 | CFL | None | 2940 | 0.802 | 2940 | 0.802 | 1.13 | 1.26 | -0.00208
CFLNoneSCERtLExIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | RtL | Ex | IOU | 2.94 | 0.000802 | 0 | 3.3 | 0.00102 | -0.00802 | 2.94 | 0.000802 | 0 | 3.3 | 0.00102 | -0.00802 | CFL | None | 2940 | 0.802 | 2940 | 0.802 | 1.12 | 1.27 | -0.00273
CFLNonePGERtLNewCZ01 | Com-Iltg-dWatt-CFL_OSnone | PGE | RtL | New | CZ01 | 2.94 | 0.000802 | 0 | 2.83 | 0.000957 | -0.0441 | 2.94 | 0.000802 | 0 | 2.83 | 0.000957 | -0.0441 | CFL | None | 2940 | 0.802 | 2940 | 0.802 | 0.963 | 1.19 | -0.015
CFLNonePGERtLNewCZ02 | Com-Iltg-dWatt-CFL_OSnone | PGE | RtL | New | CZ02 | 2.94 | 0.000802 | 0 | 3.05 | 0.00102 | -0.0234 | 2.94 | 0.000802 | 0 | 3.05 | 0.00102 | -0.0234 | CFL | None | 2940 | 0.802 | 2940 | 0.802 | 1.04 | 1.27 | -0.00796
CFLNonePGERtLNewCZ03 | Com-Iltg-dWatt-CFL_OSnone | PGE | RtL | New | CZ03 | 2.94 | 0.000802 | 0 | 3.02 | 0.000991 | -0.0219 | 2.94 | 0.000802 | 0 | 3.02 | 0.000991 | -0.0219 | CFL | None | 2940 | 0.802 | 2940 | 0.802 | 1.03 | 1.24 | -0.00745
CFLNonePGERtLNewCZ04 | Com-Iltg-dWatt-CFL_OSnone | PGE | RtL | New | CZ04 | 2.94 | 0.000802 | 0 | 3.12 | 0.00101 | -0.0166 | 2.94 | 0.000802 | 0 | 3.12 | 0.00101 | -0.0166 | CFL | None | 2940 | 0.802 | 2940 | 0.802 | 1.06 | 1.26 | -0.00565
CFLNoneSCERtLNewCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | RtL | New | CZ05 | 2.94 | 0.000802 | 0 | 3.06 | 0.001 | -0.021 | 2.94 | 0.000802 | 0 | 3.06 | 0.001 | -0.021 | CFL | None | 2940 | 0.802 | 2940 | 0.802 | 1.04 | 1.25 | -0.00714
CFLNonePGERtLNewCZ05 | Com-Iltg-dWatt-CFL_OSnone | PGE | RtL | New | CZ05 | 2.94 | 0.000802 | 0 | 3.02 | 0.000968 | -0.0228 | 2.94 | 0.000802 | 0 | 3.02 | 0.000968 | -0.0228 | CFL | None | 2940 | 0.802 | 2940 | 0.802 | 1.03 | 1.21 | -0.00776
CFLNoneSDGRtLNewCZ06 | Com-Iltg-dWatt-CFL_OSnone | SDG | RtL | New | CZ06 | 2.94 | 0.000802 | 0 | 3.22 | 0.00102 | -0.0101 | 2.94 | 0.000802 | 0 | 3.22 | 0.00102 | -0.0101 | CFL | None | 2940 | 0.802 | 2940 | 0.802 | 1.1 | 1.27 | -0.00344
CFLNoneSCERtLNewCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | RtL | New | CZ06 | 2.94 | 0.000802 | 0 | 3.22 | 0.00102 | -0.00976 | 2.94 | 0.000802 | 0 | 3.22 | 0.00102 | -0.00976 | CFL | None | 2940 | 0.802 | 2940 | 0.802 | 1.1 | 1.27 | -0.00332
CFLNoneSDGRtLNewCZ07 | Com-Iltg-dWatt-CFL_OSnone | SDG | RtL | New | CZ07 | 2.94 | 0.000802 | 0 | 3.21 | 0.000982 | -0.0072 | 2.94 | 0.000802 | 0 | 3.21 | 0.000982 | -0.0072 | CFL | None | 2940 | 0.802 | 2940 | 0.802 | 1.09 | 1.22 | -0.00245
CFLNoneSDGRtLNewCZ08 | Com-Iltg-dWatt-CFL_OSnone | SDG | RtL | New | CZ08 | 2.94 | 0.000802 | 0 | 3.26 | 0.00103 | -0.0085 | 2.94 | 0.000802 | 0 | 3.26 | 0.00103 | -0.0085 | CFL | None | 2940 | 0.802 | 2940 | 0.802 | 1.11 | 1.28 | -0.00289
CFLNoneSCERtLNewCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | RtL | New | CZ08 | 2.94 | 0.000802 | 0 | 3.26 | 0.00104 | -0.00826 | 2.94 | 0.000802 | 0 | 3.26 | 0.00104 | -0.00826 | CFL | None | 2940 | 0.802 | 2940 | 0.802 | 1.11 | 1.3 | -0.00281
CFLNoneSCERtLNewCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | RtL | New | CZ09 | 2.94 | 0.000802 | 0 | 3.28 | 0.00109 | -0.00817 | 2.94 | 0.000802 | 0 | 3.28 | 0.00109 | -0.00817 | CFL | None | 2940 | 0.802 | 2940 | 0.802 | 1.12 | 1.36 | -0.00278
CFLNoneSDGRtLNewCZ10 | Com-Iltg-dWatt-CFL_OSnone | SDG | RtL | New | CZ10 | 2.94 | 0.000802 | 0 | 3.28 | 0.00109 | -0.00979 | 2.94 | 0.000802 | 0 | 3.28 | 0.00109 | -0.00979 | CFL | None | 2940 | 0.802 | 2940 | 0.802 | 1.12 | 1.36 | -0.00333
CFLNoneSCERtLNewCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | RtL | New | CZ10 | 2.94 | 0.000802 | 0 | 3.29 | 0.00109 | -0.00953 | 2.94 | 0.000802 | 0 | 3.29 | 0.00109 | -0.00953 | CFL | None | 2940 | 0.802 | 2940 | 0.802 | 1.12 | 1.36 | -0.00324
CFLNonePGERtLNewCZ11 | Com-Iltg-dWatt-CFL_OSnone | PGE | RtL | New | CZ11 | 2.94 | 0.000802 | 0 | 3.14 | 0.00102 | -0.021 | 2.94 | 0.000802 | 0 | 3.14 | 0.00102 | -0.021 | CFL | None | 2940 | 0.802 | 2940 | 0.802 | 1.07 | 1.27 | -0.00714
CFLNonePGERtLNewCZ12 | Com-Iltg-dWatt-CFL_OSnone | PGE | RtL | New | CZ12 | 2.94 | 0.000802 | 0 | 3.12 | 0.00104 | -0.0206 | 2.94 | 0.000802 | 0 | 3.12 | 0.00104 | -0.0206 | CFL | None | 2940 | 0.802 | 2940 | 0.802 | 1.06 | 1.3 | -0.00701
CFLNonePGERtLNewCZ13 | Com-Iltg-dWatt-CFL_OSnone | PGE | RtL | New | CZ13 | 2.94 | 0.000802 | 0 | 3.16 | 0.00103 | -0.0196 | 2.94 | 0.000802 | 0 | 3.16 | 0.00103 | -0.0196 | CFL | None | 2940 | 0.802 | 2940 | 0.802 | 1.07 | 1.28 | -0.00667
CFLNoneSCERtLNewCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | RtL | New | CZ13 | 2.94 | 0.000802 | 0 | 3.22 | 0.00108 | -0.018 | 2.94 | 0.000802 | 0 | 3.22 | 0.00108 | -0.018 | CFL | None | 2940 | 0.802 | 2940 | 0.802 | 1.1 | 1.35 | -0.00612
CFLNoneSCERtLNewCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | RtL | New | CZ14 | 2.94 | 0.000802 | 0 | 3.21 | 0.00108 | -0.0184 | 2.94 | 0.000802 | 0 | 3.21 | 0.00108 | -0.0184 | CFL | None | 2940 | 0.802 | 2940 | 0.802 | 1.09 | 1.35 | -0.00626
CFLNoneSDGRtLNewCZ14 | Com-Iltg-dWatt-CFL_OSnone | SDG | RtL | New | CZ14 | 2.94 | 0.000802 | 0 | 3.21 | 0.00108 | -0.0191 | 2.94 | 0.000802 | 0 | 3.21 | 0.00108 | -0.0191 | CFL | None | 2940 | 0.802 | 2940 | 0.802 | 1.09 | 1.35 | -0.0065
CFLNoneSCERtLNewCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | RtL | New | CZ15 | 2.94 | 0.000802 | 0 | 3.48 | 0.0011 | -0.0028 | 2.94 | 0.000802 | 0 | 3.48 | 0.0011 | -0.0028 | CFL | None | 2940 | 0.802 | 2940 | 0.802 | 1.18 | 1.37 | -0.000952
CFLNoneSDGRtLNewCZ15 | Com-Iltg-dWatt-CFL_OSnone | SDG | RtL | New | CZ15 | 2.94 | 0.000802 | 0 | 3.47 | 0.0011 | -0.00287 | 2.94 | 0.000802 | 0 | 3.47 | 0.0011 | -0.00287 | CFL | None | 2940 | 0.802 | 2940 | 0.802 | 1.18 | 1.37 | -0.000976
CFLNoneSCERtLNewCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | RtL | New | CZ16 | 2.94 | 0.000802 | 0 | 2.91 | 0.00102 | -0.0382 | 2.94 | 0.000802 | 0 | 2.91 | 0.00102 | -0.0382 | CFL | None | 2940 | 0.802 | 2940 | 0.802 | 0.99 | 1.27 | -0.013
CFLNonePGERtLNewCZ16 | Com-Iltg-dWatt-CFL_OSnone | PGE | RtL | New | CZ16 | 2.94 | 0.000802 | 0 | 2.88 | 0.00098 | -0.0412 | 2.94 | 0.000802 | 0 | 2.88 | 0.00098 | -0.0412 | CFL | None | 2940 | 0.802 | 2940 | 0.802 | 0.98 | 1.22 | -0.014
CFLNoneSCGRtLNewIOU | Com-Iltg-dWatt-CFL_OSnone | SCG | RtL | New | IOU | 2.94 | 0.000802 | 0 | 3.27 | 0.00106 | -0.00967 | 2.94 | 0.000802 | 0 | 3.27 | 0.00106 | -0.00967 | CFL | None | 2940 | 0.802 | 2940 | 0.802 | 1.11 | 1.32 | -0.00329
CFLNoneSCERtLNewIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | RtL | New | IOU | 2.94 | 0.000802 | 0 | 3.27 | 0.00106 | -0.00971 | 2.94 | 0.000802 | 0 | 3.27 | 0.00106 | -0.00971 | CFL | None | 2940 | 0.802 | 2940 | 0.802 | 1.11 | 1.32 | -0.0033
CFLNonePGERtLNewIOU | Com-Iltg-dWatt-CFL_OSnone | PGE | RtL | New | IOU | 2.94 | 0.000802 | 0 | 3.2 | 0.00107 | -0.0186 | 2.94 | 0.000802 | 0 | 3.2 | 0.00107 | -0.0186 | CFL | None | 2940 | 0.802 | 2940 | 0.802 | 1.09 | 1.33 | -0.00633
CFLNoneSDGRtLNewIOU | Com-Iltg-dWatt-CFL_OSnone | SDG | RtL | New | IOU | 2.94 | 0.000802 | 0 | 3.23 | 0.00101 | -0.00802 | 2.94 | 0.000802 | 0 | 3.23 | 0.00101 | -0.00802 | CFL | None | 2940 | 0.802 | 2940 | 0.802 | 1.1 | 1.26 | -0.00273
CFLNonePGERtSExCZ01 | Com-Iltg-dWatt-CFL_OSnone | PGE | RtS | Ex | CZ01 | 2.26 | 0.000529 | 0 | 2.19 | 0.000625 | -0.0271 | 2.26 | 0.000529 | 0 | 2.19 | 0.000625 | -0.0271 | CFL | None | 2260 | 0.529 | 2260 | 0.529 | 0.969 | 1.18 | -0.012
CFLNonePGERtSExCZ02 | Com-Iltg-dWatt-CFL_OSnone | PGE | RtS | Ex | CZ02 | 2.26 | 0.000529 | 0 | 2.35 | 0.000631 | -0.0148 | 2.26 | 0.000529 | 0 | 2.35 | 0.000631 | -0.0148 | CFL | None | 2260 | 0.529 | 2260 | 0.529 | 1.04 | 1.19 | -0.00655
CFLNonePGERtSExCZ03 | Com-Iltg-dWatt-CFL_OSnone | PGE | RtS | Ex | CZ03 | 2.26 | 0.000529 | 0 | 2.36 | 0.000641 | -0.014 | 2.26 | 0.000529 | 0 | 2.36 | 0.000641 | -0.014 | CFL | None | 2260 | 0.529 | 2260 | 0.529 | 1.04 | 1.21 | -0.00619
CFLNonePGERtSExCZ04 | Com-Iltg-dWatt-CFL_OSnone | PGE | RtS | Ex | CZ04 | 2.26 | 0.000529 | 0 | 2.4 | 0.000641 | -0.0105 | 2.26 | 0.000529 | 0 | 2.4 | 0.000641 | -0.0105 | CFL | None | 2260 | 0.529 | 2260 | 0.529 | 1.06 | 1.21 | -0.00465
CFLNonePGERtSExCZ05 | Com-Iltg-dWatt-CFL_OSnone | PGE | RtS | Ex | CZ05 | 2.26 | 0.000529 | 0 | 2.39 | 0.000658 | -0.0118 | 2.26 | 0.000529 | 0 | 2.39 | 0.000658 | -0.0118 | CFL | None | 2260 | 0.529 | 2260 | 0.529 | 1.06 | 1.24 | -0.00522
CFLNoneSCGRtSExCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCG | RtS | Ex | CZ05 | 2.26 | 0.000529 | 0 | 2.39 | 0.000658 | -0.0118 | 2.26 | 0.000529 | 0 | 2.39 | 0.000658 | -0.0118 | CFL | None | 2260 | 0.529 | 2260 | 0.529 | 1.06 | 1.24 | -0.00522
CFLNoneSCERtSExCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | RtS | Ex | CZ05 | 2.26 | 0.000529 | 0 | 2.39 | 0.000658 | -0.0118 | 2.26 | 0.000529 | 0 | 2.39 | 0.000658 | -0.0118 | CFL | None | 2260 | 0.529 | 2260 | 0.529 | 1.06 | 1.24 | -0.00522
CFLNoneSDGRtSExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SDG | RtS | Ex | CZ06 | 2.26 | 0.000529 | 0 | 2.5 | 0.000662 | -0.00447 | 2.26 | 0.000529 | 0 | 2.5 | 0.000662 | -0.00447 | CFL | None | 2260 | 0.529 | 2260 | 0.529 | 1.11 | 1.25 | -0.00198
CFLNoneSCERtSExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | RtS | Ex | CZ06 | 2.26 | 0.000529 | 0 | 2.5 | 0.000662 | -0.00447 | 2.26 | 0.000529 | 0 | 2.5 | 0.000662 | -0.00447 | CFL | None | 2260 | 0.529 | 2260 | 0.529 | 1.11 | 1.25 | -0.00198
CFLNoneSCGRtSExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCG | RtS | Ex | CZ06 | 2.26 | 0.000529 | 0 | 2.5 | 0.000662 | -0.00447 | 2.26 | 0.000529 | 0 | 2.5 | 0.000662 | -0.00447 | CFL | None | 2260 | 0.529 | 2260 | 0.529 | 1.11 | 1.25 | -0.00198
CFLNoneSDGRtSExCZ07 | Com-Iltg-dWatt-CFL_OSnone | SDG | RtS | Ex | CZ07 | 2.26 | 0.000529 | 0 | 2.51 | 0.000647 | -0.00276 | 2.26 | 0.000529 | 0 | 2.51 | 0.000647 | -0.00276 | CFL | None | 2260 | 0.529 | 2260 | 0.529 | 1.11 | 1.22 | -0.00122
CFLNoneSDGRtSExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SDG | RtS | Ex | CZ08 | 2.26 | 0.000529 | 0 | 2.52 | 0.000663 | -0.0038 | 2.26 | 0.000529 | 0 | 2.52 | 0.000663 | -0.0038 | CFL | None | 2260 | 0.529 | 2260 | 0.529 | 1.12 | 1.25 | -0.00168
CFLNoneSCGRtSExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCG | RtS | Ex | CZ08 | 2.26 | 0.000529 | 0 | 2.52 | 0.000663 | -0.0038 | 2.26 | 0.000529 | 0 | 2.52 | 0.000663 | -0.0038 | CFL | None | 2260 | 0.529 | 2260 | 0.529 | 1.12 | 1.25 | -0.00168
CFLNoneSCERtSExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | RtS | Ex | CZ08 | 2.26 | 0.000529 | 0 | 2.52 | 0.000663 | -0.0038 | 2.26 | 0.000529 | 0 | 2.52 | 0.000663 | -0.0038 | CFL | None | 2260 | 0.529 | 2260 | 0.529 | 1.12 | 1.25 | -0.00168
CFLNoneSCGRtSExCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCG | RtS | Ex | CZ09 | 2.26 | 0.000529 | 0 | 2.52 | 0.000676 | -0.0047 | 2.26 | 0.000529 | 0 | 2.52 | 0.000676 | -0.0047 | CFL | None | 2260 | 0.529 | 2260 | 0.529 | 1.12 | 1.28 | -0.00208
CFLNoneSCERtSExCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | RtS | Ex | CZ09 | 2.26 | 0.000529 | 0 | 2.52 | 0.000676 | -0.0047 | 2.26 | 0.000529 | 0 | 2.52 | 0.000676 | -0.0047 | CFL | None | 2260 | 0.529 | 2260 | 0.529 | 1.12 | 1.28 | -0.00208
CFLNoneSDGRtSExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SDG | RtS | Ex | CZ10 | 2.26 | 0.000529 | 0 | 2.51 | 0.000669 | -0.00529 | 2.26 | 0.000529 | 0 | 2.51 | 0.000669 | -0.00529 | CFL | None | 2260 | 0.529 | 2260 | 0.529 | 1.11 | 1.26 | -0.00234
CFLNoneSCERtSExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | RtS | Ex | CZ10 | 2.26 | 0.000529 | 0 | 2.51 | 0.000669 | -0.00529 | 2.26 | 0.000529 | 0 | 2.51 | 0.000669 | -0.00529 | CFL | None | 2260 | 0.529 | 2260 | 0.529 | 1.11 | 1.26 | -0.00234
CFLNoneSCGRtSExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCG | RtS | Ex | CZ10 | 2.26 | 0.000529 | 0 | 2.51 | 0.000669 | -0.00529 | 2.26 | 0.000529 | 0 | 2.51 | 0.000669 | -0.00529 | CFL | None | 2260 | 0.529 | 2260 | 0.529 | 1.11 | 1.26 | -0.00234
CFLNonePGERtSExCZ11 | Com-Iltg-dWatt-CFL_OSnone | PGE | RtS | Ex | CZ11 | 2.26 | 0.000529 | 0 | 2.37 | 0.000647 | -0.014 | 2.26 | 0.000529 | 0 | 2.37 | 0.000647 | -0.014 | CFL | None | 2260 | 0.529 | 2260 | 0.529 | 1.05 | 1.22 | -0.00619
CFLNonePGERtSExCZ12 | Com-Iltg-dWatt-CFL_OSnone | PGE | RtS | Ex | CZ12 | 2.26 | 0.000529 | 0 | 2.37 | 0.000638 | -0.0144 | 2.26 | 0.000529 | 0 | 2.37 | 0.000638 | -0.0144 | CFL | None | 2260 | 0.529 | 2260 | 0.529 | 1.05 | 1.21 | -0.00637
CFLNoneSCERtSExCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | RtS | Ex | CZ13 | 2.26 | 0.000529 | 0 | 2.43 | 0.000671 | -0.0125 | 2.26 | 0.000529 | 0 | 2.43 | 0.000671 | -0.0125 | CFL | None | 2260 | 0.529 | 2260 | 0.529 | 1.08 | 1.27 | -0.00553
CFLNoneSCGRtSExCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCG | RtS | Ex | CZ13 | 2.26 | 0.000529 | 0 | 2.43 | 0.000671 | -0.0125 | 2.26 | 0.000529 | 0 | 2.43 | 0.000671 | -0.0125 | CFL | None | 2260 | 0.529 | 2260 | 0.529 | 1.08 | 1.27 | -0.00553
CFLNonePGERtSExCZ13 | Com-Iltg-dWatt-CFL_OSnone | PGE | RtS | Ex | CZ13 | 2.26 | 0.000529 | 0 | 2.43 | 0.000671 | -0.0125 | 2.26 | 0.000529 | 0 | 2.43 | 0.000671 | -0.0125 | CFL | None | 2260 | 0.529 | 2260 | 0.529 | 1.08 | 1.27 | -0.00553
CFLNoneSCERtSExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | RtS | Ex | CZ14 | 2.26 | 0.000529 | 0 | 2.44 | 0.000668 | -0.0116 | 2.26 | 0.000529 | 0 | 2.44 | 0.000668 | -0.0116 | CFL | None | 2260 | 0.529 | 2260 | 0.529 | 1.08 | 1.26 | -0.00513
CFLNoneSCGRtSExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCG | RtS | Ex | CZ14 | 2.26 | 0.000529 | 0 | 2.44 | 0.000668 | -0.0116 | 2.26 | 0.000529 | 0 | 2.44 | 0.000668 | -0.0116 | CFL | None | 2260 | 0.529 | 2260 | 0.529 | 1.08 | 1.26 | -0.00513
CFLNoneSDGRtSExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SDG | RtS | Ex | CZ14 | 2.26 | 0.000529 | 0 | 2.44 | 0.000668 | -0.0116 | 2.26 | 0.000529 | 0 | 2.44 | 0.000668 | -0.0116 | CFL | None | 2260 | 0.529 | 2260 | 0.529 | 1.08 | 1.26 | -0.00513
CFLNoneSDGRtSExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SDG | RtS | Ex | CZ15 | 2.26 | 0.000529 | 0 | 2.68 | 0.000658 | -0.00137 | 2.26 | 0.000529 | 0 | 2.68 | 0.000658 | -0.00137 | CFL | None | 2260 | 0.529 | 2260 | 0.529 | 1.19 | 1.24 | -0.000606
CFLNoneSCGRtSExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCG | RtS | Ex | CZ15 | 2.26 | 0.000529 | 0 | 2.68 | 0.000658 | -0.00137 | 2.26 | 0.000529 | 0 | 2.68 | 0.000658 | -0.00137 | CFL | None | 2260 | 0.529 | 2260 | 0.529 | 1.19 | 1.24 | -0.000606
CFLNoneSCERtSExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | RtS | Ex | CZ15 | 2.26 | 0.000529 | 0 | 2.68 | 0.000658 | -0.00137 | 2.26 | 0.000529 | 0 | 2.68 | 0.000658 | -0.00137 | CFL | None | 2260 | 0.529 | 2260 | 0.529 | 1.19 | 1.24 | -0.000606
CFLNonePGERtSExCZ16 | Com-Iltg-dWatt-CFL_OSnone | PGE | RtS | Ex | CZ16 | 2.26 | 0.000529 | 0 | 2.23 | 0.000653 | -0.024 | 2.26 | 0.000529 | 0 | 2.23 | 0.000653 | -0.024 | CFL | None | 2260 | 0.529 | 2260 | 0.529 | 0.987 | 1.23 | -0.0106
CFLNoneSCERtSExCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | RtS | Ex | CZ16 | 2.26 | 0.000529 | 0 | 2.23 | 0.000653 | -0.024 | 2.26 | 0.000529 | 0 | 2.23 | 0.000653 | -0.024 | CFL | None | 2260 | 0.529 | 2260 | 0.529 | 0.987 | 1.23 | -0.0106
CFLNoneSCGRtSExCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCG | RtS | Ex | CZ16 | 2.26 | 0.000529 | 0 | 2.23 | 0.000653 | -0.024 | 2.26 | 0.000529 | 0 | 2.23 | 0.000653 | -0.024 | CFL | None | 2260 | 0.529 | 2260 | 0.529 | 0.987 | 1.23 | -0.0106
CFLNonePGERtSExIOU | Com-Iltg-dWatt-CFL_OSnone | PGE | RtS | Ex | IOU | 2.26 | 0.000529 | 0 | 2.38 | 0.000644 | -0.0136 | 2.26 | 0.000529 | 0 | 2.38 | 0.000644 | -0.0136 | CFL | None | 2260 | 0.529 | 2260 | 0.529 | 1.05 | 1.22 | -0.00602
CFLNoneSDGRtSExIOU | Com-Iltg-dWatt-CFL_OSnone | SDG | RtS | Ex | IOU | 2.26 | 0.000529 | 0 | 2.51 | 0.000654 | -0.00351 | 2.26 | 0.000529 | 0 | 2.51 | 0.000654 | -0.00351 | CFL | None | 2260 | 0.529 | 2260 | 0.529 | 1.11 | 1.24 | -0.00155
CFLNoneSCGRtSExIOU | Com-Iltg-dWatt-CFL_OSnone | SCG | RtS | Ex | IOU | 2.26 | 0.000529 | 0 | 2.51 | 0.000667 | -0.00499 | 2.26 | 0.000529 | 0 | 2.51 | 0.000667 | -0.00499 | CFL | None | 2260 | 0.529 | 2260 | 0.529 | 1.11 | 1.26 | -0.00221
CFLNoneSCERtSExIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | RtS | Ex | IOU | 2.26 | 0.000529 | 0 | 2.51 | 0.000666 | -0.00511 | 2.26 | 0.000529 | 0 | 2.51 | 0.000666 | -0.00511 | CFL | None | 2260 | 0.529 | 2260 | 0.529 | 1.11 | 1.26 | -0.00226
CFLNonePGERtSNewCZ01 | Com-Iltg-dWatt-CFL_OSnone | PGE | RtS | New | CZ01 | 2.26 | 0.000529 | 0 | 2.17 | 0.000616 | -0.0303 | 2.26 | 0.000529 | 0 | 2.17 | 0.000616 | -0.0303 | CFL | None | 2260 | 0.529 | 2260 | 0.529 | 0.96 | 1.16 | -0.0134
CFLNonePGERtSNewCZ02 | Com-Iltg-dWatt-CFL_OSnone | PGE | RtS | New | CZ02 | 2.26 | 0.000529 | 0 | 2.33 | 0.000646 | -0.0163 | 2.26 | 0.000529 | 0 | 2.33 | 0.000646 | -0.0163 | CFL | None | 2260 | 0.529 | 2260 | 0.529 | 1.03 | 1.22 | -0.00721
CFLNonePGERtSNewCZ03 | Com-Iltg-dWatt-CFL_OSnone | PGE | RtS | New | CZ03 | 2.26 | 0.000529 | 0 | 2.29 | 0.000634 | -0.0156 | 2.26 | 0.000529 | 0 | 2.29 | 0.000634 | -0.0156 | CFL | None | 2260 | 0.529 | 2260 | 0.529 | 1.01 | 1.2 | -0.0069
CFLNonePGERtSNewCZ04 | Com-Iltg-dWatt-CFL_OSnone | PGE | RtS | New | CZ04 | 2.26 | 0.000529 | 0 | 2.36 | 0.00064 | -0.0117 | 2.26 | 0.000529 | 0 | 2.36 | 0.00064 | -0.0117 | CFL | None | 2260 | 0.529 | 2260 | 0.529 | 1.04 | 1.21 | -0.00518
CFLNonePGERtSNewCZ05 | Com-Iltg-dWatt-CFL_OSnone | PGE | RtS | New | CZ05 | 2.26 | 0.000529 | 0 | 2.31 | 0.000623 | -0.0139 | 2.26 | 0.000529 | 0 | 2.31 | 0.000623 | -0.0139 | CFL | None | 2260 | 0.529 | 2260 | 0.529 | 1.02 | 1.18 | -0.00615
CFLNoneSCERtSNewCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | RtS | New | CZ05 | 2.26 | 0.000529 | 0 | 2.32 | 0.000643 | -0.0132 | 2.26 | 0.000529 | 0 | 2.32 | 0.000643 | -0.0132 | CFL | None | 2260 | 0.529 | 2260 | 0.529 | 1.03 | 1.22 | -0.00584
CFLNoneSDGRtSNewCZ06 | Com-Iltg-dWatt-CFL_OSnone | SDG | RtS | New | CZ06 | 2.26 | 0.000529 | 0 | 2.44 | 0.000651 | -0.00563 | 2.26 | 0.000529 | 0 | 2.44 | 0.000651 | -0.00563 | CFL | None | 2260 | 0.529 | 2260 | 0.529 | 1.08 | 1.23 | -0.00249
CFLNoneSCERtSNewCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | RtS | New | CZ06 | 2.26 | 0.000529 | 0 | 2.44 | 0.000652 | -0.00551 | 2.26 | 0.000529 | 0 | 2.44 | 0.000652 | -0.00551 | CFL | None | 2260 | 0.529 | 2260 | 0.529 | 1.08 | 1.23 | -0.00244
CFLNoneSDGRtSNewCZ07 | Com-Iltg-dWatt-CFL_OSnone | SDG | RtS | New | CZ07 | 2.26 | 0.000529 | 0 | 2.43 | 0.000643 | -0.00344 | 2.26 | 0.000529 | 0 | 2.43 | 0.000643 | -0.00344 | CFL | None | 2260 | 0.529 | 2260 | 0.529 | 1.08 | 1.22 | -0.00152
CFLNoneSDGRtSNewCZ08 | Com-Iltg-dWatt-CFL_OSnone | SDG | RtS | New | CZ08 | 2.26 | 0.000529 | 0 | 2.46 | 0.000658 | -0.0047 | 2.26 | 0.000529 | 0 | 2.46 | 0.000658 | -0.0047 | CFL | None | 2260 | 0.529 | 2260 | 0.529 | 1.09 | 1.24 | -0.00208
CFLNoneSCERtSNewCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | RtS | New | CZ08 | 2.26 | 0.000529 | 0 | 2.47 | 0.000659 | -0.00461 | 2.26 | 0.000529 | 0 | 2.47 | 0.000659 | -0.00461 | CFL | None | 2260 | 0.529 | 2260 | 0.529 | 1.09 | 1.25 | -0.00204
CFLNoneSCERtSNewCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | RtS | New | CZ09 | 2.26 | 0.000529 | 0 | 2.46 | 0.000676 | -0.00531 | 2.26 | 0.000529 | 0 | 2.46 | 0.000676 | -0.00531 | CFL | None | 2260 | 0.529 | 2260 | 0.529 | 1.09 | 1.28 | -0.00235
CFLNoneSDGRtSNewCZ10 | Com-Iltg-dWatt-CFL_OSnone | SDG | RtS | New | CZ10 | 2.26 | 0.000529 | 0 | 2.48 | 0.000686 | -0.00563 | 2.26 | 0.000529 | 0 | 2.48 | 0.000686 | -0.00563 | CFL | None | 2260 | 0.529 | 2260 | 0.529 | 1.1 | 1.3 | -0.00249
CFLNoneSCERtSNewCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | RtS | New | CZ10 | 2.26 | 0.000529 | 0 | 2.48 | 0.000687 | -0.00551 | 2.26 | 0.000529 | 0 | 2.48 | 0.000687 | -0.00551 | CFL | None | 2260 | 0.529 | 2260 | 0.529 | 1.1 | 1.3 | -0.00244
CFLNonePGERtSNewCZ11 | Com-Iltg-dWatt-CFL_OSnone | PGE | RtS | New | CZ11 | 2.26 | 0.000529 | 0 | 2.38 | 0.000658 | -0.0141 | 2.26 | 0.000529 | 0 | 2.38 | 0.000658 | -0.0141 | CFL | None | 2260 | 0.529 | 2260 | 0.529 | 1.05 | 1.24 | -0.00624
CFLNonePGERtSNewCZ12 | Com-Iltg-dWatt-CFL_OSnone | PGE | RtS | New | CZ12 | 2.26 | 0.000529 | 0 | 2.37 | 0.000652 | -0.0151 | 2.26 | 0.000529 | 0 | 2.37 | 0.000652 | -0.0151 | CFL | None | 2260 | 0.529 | 2260 | 0.529 | 1.05 | 1.23 | -0.00668
CFLNoneSCERtSNewCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | RtS | New | CZ13 | 2.26 | 0.000529 | 0 | 2.42 | 0.000677 | -0.0129 | 2.26 | 0.000529 | 0 | 2.42 | 0.000677 | -0.0129 | CFL | None | 2260 | 0.529 | 2260 | 0.529 | 1.07 | 1.28 | -0.00571
CFLNonePGERtSNewCZ13 | Com-Iltg-dWatt-CFL_OSnone | PGE | RtS | New | CZ13 | 2.26 | 0.000529 | 0 | 2.39 | 0.000651 | -0.0137 | 2.26 | 0.000529 | 0 | 2.39 | 0.000651 | -0.0137 | CFL | None | 2260 | 0.529 | 2260 | 0.529 | 1.06 | 1.23 | -0.00606
CFLNoneSDGRtSNewCZ14 | Com-Iltg-dWatt-CFL_OSnone | SDG | RtS | New | CZ14 | 2.26 | 0.000529 | 0 | 2.43 | 0.000677 | -0.0124 | 2.26 | 0.000529 | 0 | 2.43 | 0.000677 | -0.0124 | CFL | None | 2260 | 0.529 | 2260 | 0.529 | 1.08 | 1.28 | -0.00549
CFLNoneSCERtSNewCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | RtS | New | CZ14 | 2.26 | 0.000529 | 0 | 2.43 | 0.000678 | -0.012 | 2.26 | 0.000529 | 0 | 2.43 | 0.000678 | -0.012 | CFL | None | 2260 | 0.529 | 2260 | 0.529 | 1.08 | 1.28 | -0.00531
CFLNoneSCERtSNewCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | RtS | New | CZ15 | 2.26 | 0.000529 | 0 | 2.6 | 0.000697 | -0.0011 | 2.26 | 0.000529 | 0 | 2.6 | 0.000697 | -0.0011 | CFL | None | 2260 | 0.529 | 2260 | 0.529 | 1.15 | 1.32 | -0.000487
CFLNoneSDGRtSNewCZ15 | Com-Iltg-dWatt-CFL_OSnone | SDG | RtS | New | CZ15 | 2.26 | 0.000529 | 0 | 2.6 | 0.000696 | -0.00109 | 2.26 | 0.000529 | 0 | 2.6 | 0.000696 | -0.00109 | CFL | None | 2260 | 0.529 | 2260 | 0.529 | 1.15 | 1.32 | -0.000482
CFLNonePGERtSNewCZ16 | Com-Iltg-dWatt-CFL_OSnone | PGE | RtS | New | CZ16 | 2.26 | 0.000529 | 0 | 2.21 | 0.000628 | -0.0271 | 2.26 | 0.000529 | 0 | 2.21 | 0.000628 | -0.0271 | CFL | None | 2260 | 0.529 | 2260 | 0.529 | 0.978 | 1.19 | -0.012
CFLNoneSCERtSNewCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | RtS | New | CZ16 | 2.26 | 0.000529 | 0 | 2.22 | 0.00065 | -0.0255 | 2.26 | 0.000529 | 0 | 2.22 | 0.00065 | -0.0255 | CFL | None | 2260 | 0.529 | 2260 | 0.529 | 0.982 | 1.23 | -0.0113
CFLNonePGERtSNewIOU | Com-Iltg-dWatt-CFL_OSnone | PGE | RtS | New | IOU | 2.26 | 0.000529 | 0 | 2.41 | 0.000673 | -0.0131 | 2.26 | 0.000529 | 0 | 2.41 | 0.000673 | -0.0131 | CFL | None | 2260 | 0.529 | 2260 | 0.529 | 1.07 | 1.27 | -0.0058
CFLNoneSCGRtSNewIOU | Com-Iltg-dWatt-CFL_OSnone | SCG | RtS | New | IOU | 2.26 | 0.000529 | 0 | 2.47 | 0.00067 | -0.00552 | 2.26 | 0.000529 | 0 | 2.47 | 0.00067 | -0.00552 | CFL | None | 2260 | 0.529 | 2260 | 0.529 | 1.09 | 1.27 | -0.00244
CFLNoneSDGRtSNewIOU | Com-Iltg-dWatt-CFL_OSnone | SDG | RtS | New | IOU | 2.26 | 0.000529 | 0 | 2.44 | 0.000655 | -0.00414 | 2.26 | 0.000529 | 0 | 2.44 | 0.000655 | -0.00414 | CFL | None | 2260 | 0.529 | 2260 | 0.529 | 1.08 | 1.24 | -0.00183
CFLNoneSCERtSNewIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | RtS | New | IOU | 2.26 | 0.000529 | 0 | 2.47 | 0.000671 | -0.00555 | 2.26 | 0.000529 | 0 | 2.47 | 0.000671 | -0.00555 | CFL | None | 2260 | 0.529 | 2260 | 0.529 | 1.09 | 1.27 | -0.00246
CFLNoneSCEs_AgrExCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_Agr | Ex | CZ05 | 2.11 | 0.000502 | 0 | 2.23 | 0.000612 | -0.00975 | 2.11 | 0.000502 | 0 | 2.23 | 0.000612 | -0.00975 | CFL | None | 2110 | 0.502 | 2110 | 0.502 | 1.06 | 1.22 | -0.00462
CFLNoneSCEs_AgrExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_Agr | Ex | CZ06 | 2.11 | 0.000502 | 0 | 2.31 | 0.000603 | -0.00413 | 2.11 | 0.000502 | 0 | 2.31 | 0.000603 | -0.00413 | CFL | None | 2110 | 0.502 | 2110 | 0.502 | 1.09 | 1.2 | -0.00196
CFLNoneSCEs_AgrExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_Agr | Ex | CZ08 | 2.11 | 0.000502 | 0 | 2.33 | 0.000603 | -0.00341 | 2.11 | 0.000502 | 0 | 2.33 | 0.000603 | -0.00341 | CFL | None | 2110 | 0.502 | 2110 | 0.502 | 1.1 | 1.2 | -0.00162
CFLNoneSCEs_AgrExCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_Agr | Ex | CZ09 | 2.11 | 0.000502 | 0 | 2.35 | 0.000616 | -0.00393 | 2.11 | 0.000502 | 0 | 2.35 | 0.000616 | -0.00393 | CFL | None | 2110 | 0.502 | 2110 | 0.502 | 1.11 | 1.23 | -0.00186
CFLNoneSCEs_AgrExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_Agr | Ex | CZ10 | 2.11 | 0.000502 | 0 | 2.32 | 0.000616 | -0.00468 | 2.11 | 0.000502 | 0 | 2.32 | 0.000616 | -0.00468 | CFL | None | 2110 | 0.502 | 2110 | 0.502 | 1.1 | 1.23 | -0.00222
CFLNoneSCEs_AgrExCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_Agr | Ex | CZ13 | 2.11 | 0.000502 | 0 | 2.27 | 0.000605 | -0.0109 | 2.11 | 0.000502 | 0 | 2.27 | 0.000605 | -0.0109 | CFL | None | 2110 | 0.502 | 2110 | 0.502 | 1.08 | 1.21 | -0.00517
CFLNoneSCEs_AgrExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_Agr | Ex | CZ14 | 2.11 | 0.000502 | 0 | 2.25 | 0.000611 | -0.0129 | 2.11 | 0.000502 | 0 | 2.25 | 0.000611 | -0.0129 | CFL | None | 2110 | 0.502 | 2110 | 0.502 | 1.07 | 1.22 | -0.00611
CFLNoneSCEs_AgrExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_Agr | Ex | CZ15 | 2.11 | 0.000502 | 0 | 2.49 | 0.000608 | -0.0012 | 2.11 | 0.000502 | 0 | 2.49 | 0.000608 | -0.0012 | CFL | None | 2110 | 0.502 | 2110 | 0.502 | 1.18 | 1.21 | -0.000569
CFLNoneSCEs_AgrExCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_Agr | Ex | CZ16 | 2.11 | 0.000502 | 0 | 2.09 | 0.000598 | -0.024 | 2.11 | 0.000502 | 0 | 2.09 | 0.000598 | -0.024 | CFL | None | 2110 | 0.502 | 2110 | 0.502 | 0.991 | 1.19 | -0.0114
CFLNoneSCEs_AgrExIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | s_Agr | Ex | IOU | 2.11 | 0.000502 | 0 | 2.33 | 0.000608 | -0.00473 | 2.11 | 0.000502 | 0 | 2.33 | 0.000608 | -0.00473 | CFL | None | 2110 | 0.502 | 2110 | 0.502 | 1.1 | 1.21 | -0.00224
CFLNoneSCEs_CliExCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_Cli | Ex | CZ05 | 2.48 | 0.000471 | 0 | 2.58 | 0.000586 | -0.0274 | 2.48 | 0.000471 | 0 | 2.58 | 0.000586 | -0.0274 | CFL | None | 2480 | 0.471 | 2480 | 0.471 | 1.04 | 1.24 | -0.011
CFLNoneSCEs_CliExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_Cli | Ex | CZ06 | 2.48 | 0.000471 | 0 | 2.72 | 0.000601 | -0.0169 | 2.48 | 0.000471 | 0 | 2.72 | 0.000601 | -0.0169 | CFL | None | 2480 | 0.471 | 2480 | 0.471 | 1.1 | 1.28 | -0.00681
CFLNoneSCEs_CliExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_Cli | Ex | CZ08 | 2.48 | 0.000471 | 0 | 2.75 | 0.000603 | -0.0162 | 2.48 | 0.000471 | 0 | 2.75 | 0.000603 | -0.0162 | CFL | None | 2480 | 0.471 | 2480 | 0.471 | 1.11 | 1.28 | -0.00653
CFLNoneSCEs_CliExCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_Cli | Ex | CZ09 | 2.48 | 0.000471 | 0 | 2.76 | 0.000619 | -0.0176 | 2.48 | 0.000471 | 0 | 2.76 | 0.000619 | -0.0176 | CFL | None | 2480 | 0.471 | 2480 | 0.471 | 1.11 | 1.31 | -0.0071
CFLNoneSCEs_CliExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_Cli | Ex | CZ10 | 2.48 | 0.000471 | 0 | 2.75 | 0.000614 | -0.0175 | 2.48 | 0.000471 | 0 | 2.75 | 0.000614 | -0.0175 | CFL | None | 2480 | 0.471 | 2480 | 0.471 | 1.11 | 1.3 | -0.00706
CFLNoneSCEs_CliExCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_Cli | Ex | CZ13 | 2.48 | 0.000471 | 0 | 2.69 | 0.000611 | -0.0217 | 2.48 | 0.000471 | 0 | 2.69 | 0.000611 | -0.0217 | CFL | None | 2480 | 0.471 | 2480 | 0.471 | 1.08 | 1.3 | -0.00875
CFLNoneSCEs_CliExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_Cli | Ex | CZ14 | 2.48 | 0.000471 | 0 | 2.71 | 0.000614 | -0.0215 | 2.48 | 0.000471 | 0 | 2.71 | 0.000614 | -0.0215 | CFL | None | 2480 | 0.471 | 2480 | 0.471 | 1.09 | 1.3 | -0.00867
CFLNoneSCEs_CliExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_Cli | Ex | CZ15 | 2.48 | 0.000471 | 0 | 2.91 | 0.00061 | -0.00977 | 2.48 | 0.000471 | 0 | 2.91 | 0.00061 | -0.00977 | CFL | None | 2480 | 0.471 | 2480 | 0.471 | 1.17 | 1.3 | -0.00394
CFLNoneSCEs_CliExCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_Cli | Ex | CZ16 | 2.48 | 0.000471 | 0 | 2.48 | 0.000591 | -0.0339 | 2.48 | 0.000471 | 0 | 2.48 | 0.000591 | -0.0339 | CFL | None | 2480 | 0.471 | 2480 | 0.471 | 1 | 1.25 | -0.0137
CFLNoneSCEs_CliExIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | s_Cli | Ex | IOU | 2.48 | 0.000471 | 0 | 2.74 | 0.000607 | -0.0175 | 2.48 | 0.000471 | 0 | 2.74 | 0.000607 | -0.0175 | CFL | None | 2480 | 0.471 | 2480 | 0.471 | 1.1 | 1.29 | -0.00706
CFLNoneSCEs_FStExCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_FSt | Ex | CZ05 | 3.58 | 0.000656 | 0 | 3.54 | 0.000818 | -0.0486 | 3.58 | 0.000656 | 0 | 3.54 | 0.000818 | -0.0486 | CFL | None | 3580 | 0.656 | 3580 | 0.656 | 0.989 | 1.25 | -0.0136
CFLNoneSCEs_FStExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_FSt | Ex | CZ06 | 3.58 | 0.000656 | 0 | 3.7 | 0.000814 | -0.0358 | 3.58 | 0.000656 | 0 | 3.7 | 0.000814 | -0.0358 | CFL | None | 3580 | 0.656 | 3580 | 0.656 | 1.03 | 1.24 | -0.01
CFLNoneSCEs_FStExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_FSt | Ex | CZ08 | 3.58 | 0.000656 | 0 | 3.76 | 0.000827 | -0.0326 | 3.58 | 0.000656 | 0 | 3.76 | 0.000827 | -0.0326 | CFL | None | 3580 | 0.656 | 3580 | 0.656 | 1.05 | 1.26 | -0.00911
CFLNoneSCEs_FStExCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_FSt | Ex | CZ09 | 3.58 | 0.000656 | 0 | 3.83 | 0.000848 | -0.0328 | 3.58 | 0.000656 | 0 | 3.83 | 0.000848 | -0.0328 | CFL | None | 3580 | 0.656 | 3580 | 0.656 | 1.07 | 1.29 | -0.00916
CFLNoneSCEs_FStExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_FSt | Ex | CZ10 | 3.58 | 0.000656 | 0 | 3.8 | 0.000855 | -0.0315 | 3.58 | 0.000656 | 0 | 3.8 | 0.000855 | -0.0315 | CFL | None | 3580 | 0.656 | 3580 | 0.656 | 1.06 | 1.3 | -0.0088
CFLNoneSCEs_FStExCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_FSt | Ex | CZ13 | 3.58 | 0.000656 | 0 | 3.79 | 0.000851 | -0.0354 | 3.58 | 0.000656 | 0 | 3.79 | 0.000851 | -0.0354 | CFL | None | 3580 | 0.656 | 3580 | 0.656 | 1.06 | 1.3 | -0.00989
CFLNoneSCEs_FStExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_FSt | Ex | CZ14 | 3.58 | 0.000656 | 0 | 3.76 | 0.000864 | -0.035 | 3.58 | 0.000656 | 0 | 3.76 | 0.000864 | -0.035 | CFL | None | 3580 | 0.656 | 3580 | 0.656 | 1.05 | 1.32 | -0.00978
CFLNoneSCEs_FStExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_FSt | Ex | CZ15 | 3.58 | 0.000656 | 0 | 4.09 | 0.000849 | -0.0175 | 3.58 | 0.000656 | 0 | 4.09 | 0.000849 | -0.0175 | CFL | None | 3580 | 0.656 | 3580 | 0.656 | 1.14 | 1.29 | -0.00489
CFLNoneSCEs_FStExCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_FSt | Ex | CZ16 | 3.58 | 0.000656 | 0 | 3.45 | 0.000819 | -0.052 | 3.58 | 0.000656 | 0 | 3.45 | 0.000819 | -0.052 | CFL | None | 3580 | 0.656 | 3580 | 0.656 | 0.964 | 1.25 | -0.0145
CFLNoneSCEs_FStExIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | s_FSt | Ex | IOU | 3.58 | 0.000656 | 0 | 3.77 | 0.000836 | -0.0331 | 3.58 | 0.000656 | 0 | 3.77 | 0.000836 | -0.0331 | CFL | None | 3580 | 0.656 | 3580 | 0.656 | 1.05 | 1.27 | -0.00925
CFLNoneSCEs_IndExCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_Ind | Ex | CZ05 | 2.15 | 0.000525 | 0 | 2.36 | 0.000645 | -0.00593 | 2.15 | 0.000525 | 0 | 2.36 | 0.000645 | -0.00593 | CFL | None | 2150 | 0.525 | 2150 | 0.525 | 1.1 | 1.23 | -0.00276
CFLNoneSCEs_IndExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_Ind | Ex | CZ06 | 2.15 | 0.000525 | 0 | 2.4 | 0.000627 | -0.00262 | 2.15 | 0.000525 | 0 | 2.4 | 0.000627 | -0.00262 | CFL | None | 2150 | 0.525 | 2150 | 0.525 | 1.12 | 1.19 | -0.00122
CFLNoneSCEs_IndExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_Ind | Ex | CZ08 | 2.15 | 0.000525 | 0 | 2.42 | 0.000641 | -0.00212 | 2.15 | 0.000525 | 0 | 2.42 | 0.000641 | -0.00212 | CFL | None | 2150 | 0.525 | 2150 | 0.525 | 1.13 | 1.22 | -0.000986
CFLNoneSCEs_IndExCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_Ind | Ex | CZ09 | 2.15 | 0.000525 | 0 | 2.45 | 0.00065 | -0.00242 | 2.15 | 0.000525 | 0 | 2.45 | 0.00065 | -0.00242 | CFL | None | 2150 | 0.525 | 2150 | 0.525 | 1.14 | 1.24 | -0.00113
CFLNoneSCEs_IndExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_Ind | Ex | CZ10 | 2.15 | 0.000525 | 0 | 2.41 | 0.000656 | -0.00305 | 2.15 | 0.000525 | 0 | 2.41 | 0.000656 | -0.00305 | CFL | None | 2150 | 0.525 | 2150 | 0.525 | 1.12 | 1.25 | -0.00142
CFLNoneSCEs_IndExCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_Ind | Ex | CZ13 | 2.15 | 0.000525 | 0 | 2.37 | 0.000633 | -0.00677 | 2.15 | 0.000525 | 0 | 2.37 | 0.000633 | -0.00677 | CFL | None | 2150 | 0.525 | 2150 | 0.525 | 1.1 | 1.21 | -0.00315
CFLNoneSCEs_IndExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_Ind | Ex | CZ14 | 2.15 | 0.000525 | 0 | 2.35 | 0.000649 | -0.00834 | 2.15 | 0.000525 | 0 | 2.35 | 0.000649 | -0.00834 | CFL | None | 2150 | 0.525 | 2150 | 0.525 | 1.09 | 1.24 | -0.00388
CFLNoneSCEs_IndExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_Ind | Ex | CZ15 | 2.15 | 0.000525 | 0 | 2.55 | 0.000652 | -0.00071 | 2.15 | 0.000525 | 0 | 2.55 | 0.000652 | -0.00071 | CFL | None | 2150 | 0.525 | 2150 | 0.525 | 1.19 | 1.24 | -0.00033
CFLNoneSCEs_IndExCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_Ind | Ex | CZ16 | 2.15 | 0.000525 | 0 | 2.2 | 0.000622 | -0.0163 | 2.15 | 0.000525 | 0 | 2.2 | 0.000622 | -0.0163 | CFL | None | 2150 | 0.525 | 2150 | 0.525 | 1.02 | 1.18 | -0.00758
CFLNoneSCEs_IndExIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | s_Ind | Ex | IOU | 2.15 | 0.000525 | 0 | 2.42 | 0.000642 | -0.00301 | 2.15 | 0.000525 | 0 | 2.42 | 0.000642 | -0.00301 | CFL | None | 2150 | 0.525 | 2150 | 0.525 | 1.13 | 1.22 | -0.0014
CFLNoneSCEs_MiCExCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_MiC | Ex | CZ05 | 2.49 | 0.000534 | 0 | 2.64 | 0.00066 | -0.0166 | 2.49 | 0.000534 | 0 | 2.64 | 0.00066 | -0.0166 | CFL | None | 2490 | 0.534 | 2490 | 0.534 | 1.06 | 1.24 | -0.00667
CFLNoneSCEs_MiCExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_MiC | Ex | CZ06 | 2.49 | 0.000534 | 0 | 2.8 | 0.000667 | -0.00777 | 2.49 | 0.000534 | 0 | 2.8 | 0.000667 | -0.00777 | CFL | None | 2490 | 0.534 | 2490 | 0.534 | 1.12 | 1.25 | -0.00312
CFLNoneSCEs_MiCExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_MiC | Ex | CZ08 | 2.49 | 0.000534 | 0 | 2.82 | 0.000663 | -0.00658 | 2.49 | 0.000534 | 0 | 2.82 | 0.000663 | -0.00658 | CFL | None | 2490 | 0.534 | 2490 | 0.534 | 1.13 | 1.24 | -0.00264
CFLNoneSCEs_MiCExCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_MiC | Ex | CZ09 | 2.49 | 0.000534 | 0 | 2.79 | 0.000673 | -0.00789 | 2.49 | 0.000534 | 0 | 2.79 | 0.000673 | -0.00789 | CFL | None | 2490 | 0.534 | 2490 | 0.534 | 1.12 | 1.26 | -0.00317
CFLNoneSCEs_MiCExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_MiC | Ex | CZ10 | 2.49 | 0.000534 | 0 | 2.81 | 0.000662 | -0.00816 | 2.49 | 0.000534 | 0 | 2.81 | 0.000662 | -0.00816 | CFL | None | 2490 | 0.534 | 2490 | 0.534 | 1.13 | 1.24 | -0.00328
CFLNoneSCEs_MiCExCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_MiC | Ex | CZ13 | 2.49 | 0.000534 | 0 | 2.71 | 0.00067 | -0.0146 | 2.49 | 0.000534 | 0 | 2.71 | 0.00067 | -0.0146 | CFL | None | 2490 | 0.534 | 2490 | 0.534 | 1.09 | 1.25 | -0.00586
CFLNoneSCEs_MiCExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_MiC | Ex | CZ14 | 2.49 | 0.000534 | 0 | 2.74 | 0.000665 | -0.0143 | 2.49 | 0.000534 | 0 | 2.74 | 0.000665 | -0.0143 | CFL | None | 2490 | 0.534 | 2490 | 0.534 | 1.1 | 1.25 | -0.00574
CFLNoneSCEs_MiCExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_MiC | Ex | CZ15 | 2.49 | 0.000534 | 0 | 3.01 | 0.000673 | -0.00274 | 2.49 | 0.000534 | 0 | 3.01 | 0.000673 | -0.00274 | CFL | None | 2490 | 0.534 | 2490 | 0.534 | 1.21 | 1.26 | -0.0011
CFLNoneSCEs_MiCExCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_MiC | Ex | CZ16 | 2.49 | 0.000534 | 0 | 2.49 | 0.000651 | -0.0273 | 2.49 | 0.000534 | 0 | 2.49 | 0.000651 | -0.0273 | CFL | None | 2490 | 0.534 | 2490 | 0.534 | 1 | 1.22 | -0.011
CFLNoneSCEs_MiCExIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | s_MiC | Ex | IOU | 2.49 | 0.000534 | 0 | 2.8 | 0.000666 | -0.00813 | 2.49 | 0.000534 | 0 | 2.8 | 0.000666 | -0.00813 | CFL | None | 2490 | 0.534 | 2490 | 0.534 | 1.12 | 1.25 | -0.00327
CFLNoneSCEs_TCUExCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_TCU | Ex | CZ05 | 1.84 | 0.000436 | 0 | 1.91 | 0.000534 | -0.01 | 1.84 | 0.000436 | 0 | 1.91 | 0.000534 | -0.01 | CFL | None | 1840 | 0.436 | 1840 | 0.436 | 1.04 | 1.22 | -0.00543
CFLNoneSCEs_TCUExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_TCU | Ex | CZ06 | 1.84 | 0.000436 | 0 | 1.99 | 0.000534 | -0.00432 | 1.84 | 0.000436 | 0 | 1.99 | 0.000534 | -0.00432 | CFL | None | 1840 | 0.436 | 1840 | 0.436 | 1.08 | 1.22 | -0.00235
CFLNoneSCEs_TCUExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_TCU | Ex | CZ08 | 1.84 | 0.000436 | 0 | 2.01 | 0.000537 | -0.00377 | 1.84 | 0.000436 | 0 | 2.01 | 0.000537 | -0.00377 | CFL | None | 1840 | 0.436 | 1840 | 0.436 | 1.09 | 1.23 | -0.00205
CFLNoneSCEs_TCUExCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_TCU | Ex | CZ09 | 1.84 | 0.000436 | 0 | 2.01 | 0.000551 | -0.00563 | 1.84 | 0.000436 | 0 | 2.01 | 0.000551 | -0.00563 | CFL | None | 1840 | 0.436 | 1840 | 0.436 | 1.09 | 1.26 | -0.00306
CFLNoneSCEs_TCUExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_TCU | Ex | CZ10 | 1.84 | 0.000436 | 0 | 2.01 | 0.000543 | -0.00479 | 1.84 | 0.000436 | 0 | 2.01 | 0.000543 | -0.00479 | CFL | None | 1840 | 0.436 | 1840 | 0.436 | 1.09 | 1.25 | -0.0026
CFLNoneSCEs_TCUExCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_TCU | Ex | CZ13 | 1.84 | 0.000436 | 0 | 1.97 | 0.00054 | -0.00916 | 1.84 | 0.000436 | 0 | 1.97 | 0.00054 | -0.00916 | CFL | None | 1840 | 0.436 | 1840 | 0.436 | 1.07 | 1.24 | -0.00498
CFLNoneSCEs_TCUExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_TCU | Ex | CZ14 | 1.84 | 0.000436 | 0 | 1.96 | 0.000538 | -0.00871 | 1.84 | 0.000436 | 0 | 1.96 | 0.000538 | -0.00871 | CFL | None | 1840 | 0.436 | 1840 | 0.436 | 1.07 | 1.23 | -0.00473
CFLNoneSCEs_TCUExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_TCU | Ex | CZ15 | 1.84 | 0.000436 | 0 | 2.12 | 0.000538 | -0.00194 | 1.84 | 0.000436 | 0 | 2.12 | 0.000538 | -0.00194 | CFL | None | 1840 | 0.436 | 1840 | 0.436 | 1.15 | 1.23 | -0.00105
CFLNoneSCEs_TCUExCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | s_TCU | Ex | CZ16 | 1.84 | 0.000436 | 0 | 1.83 | 0.000528 | -0.0169 | 1.84 | 0.000436 | 0 | 1.83 | 0.000528 | -0.0169 | CFL | None | 1840 | 0.436 | 1840 | 0.436 | 0.995 | 1.21 | -0.00918
CFLNoneSCEs_TCUExIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | s_TCU | Ex | IOU | 1.84 | 0.000436 | 0 | 2.01 | 0.000539 | -0.00482 | 1.84 | 0.000436 | 0 | 2.01 | 0.000539 | -0.00482 | CFL | None | 1840 | 0.436 | 1840 | 0.436 | 1.09 | 1.24 | -0.00262
CFLNonePGESCnExCZ01 | Com-Iltg-dWatt-CFL_OSnone | PGE | SCn | Ex | CZ01 | 2.03 | 0.000492 | 0 | 1.72 | 0.000492 | -0.0341 | 2.03 | 0.000492 | 0 | 1.72 | 0.000492 | -0.0341 | CFL | None | 2030 | 0.492 | 2030 | 0.492 | 0.847 | 1 | -0.0168
CFLNonePGESCnExCZ02 | Com-Iltg-dWatt-CFL_OSnone | PGE | SCn | Ex | CZ02 | 2.03 | 0.000492 | 0 | 1.94 | 0.000614 | -0.0181 | 2.03 | 0.000492 | 0 | 1.94 | 0.000614 | -0.0181 | CFL | None | 2030 | 0.492 | 2030 | 0.492 | 0.956 | 1.25 | -0.00892
CFLNonePGESCnExCZ03 | Com-Iltg-dWatt-CFL_OSnone | PGE | SCn | Ex | CZ03 | 2.03 | 0.000492 | 0 | 1.88 | 0.000649 | -0.0198 | 2.03 | 0.000492 | 0 | 1.88 | 0.000649 | -0.0198 | CFL | None | 2030 | 0.492 | 2030 | 0.492 | 0.926 | 1.32 | -0.00975
CFLNonePGESCnExCZ04 | Com-Iltg-dWatt-CFL_OSnone | PGE | SCn | Ex | CZ04 | 2.03 | 0.000492 | 0 | 1.99 | 0.000614 | -0.0158 | 2.03 | 0.000492 | 0 | 1.99 | 0.000614 | -0.0158 | CFL | None | 2030 | 0.492 | 2030 | 0.492 | 0.98 | 1.25 | -0.00778
CFLNonePGESCnExCZ05 | Com-Iltg-dWatt-CFL_OSnone | PGE | SCn | Ex | CZ05 | 2.03 | 0.000492 | 0 | 1.89 | 0.000615 | -0.0203 | 2.03 | 0.000492 | 0 | 1.89 | 0.000615 | -0.0203 | CFL | None | 2030 | 0.492 | 2030 | 0.492 | 0.931 | 1.25 | -0.01
CFLNoneSCESCnExCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | SCn | Ex | CZ05 | 2.03 | 0.000492 | 0 | 1.89 | 0.000615 | -0.0203 | 2.03 | 0.000492 | 0 | 1.89 | 0.000615 | -0.0203 | CFL | None | 2030 | 0.492 | 2030 | 0.492 | 0.931 | 1.25 | -0.01
CFLNoneSCGSCnExCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCG | SCn | Ex | CZ05 | 2.03 | 0.000492 | 0 | 1.89 | 0.000615 | -0.0203 | 2.03 | 0.000492 | 0 | 1.89 | 0.000615 | -0.0203 | CFL | None | 2030 | 0.492 | 2030 | 0.492 | 0.931 | 1.25 | -0.01
CFLNoneSDGSCnExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SDG | SCn | Ex | CZ06 | 2.03 | 0.000492 | 0 | 2.08 | 0.000633 | -0.0106 | 2.03 | 0.000492 | 0 | 2.08 | 0.000633 | -0.0106 | CFL | None | 2030 | 0.492 | 2030 | 0.492 | 1.02 | 1.29 | -0.00522
CFLNoneSCESCnExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | SCn | Ex | CZ06 | 2.03 | 0.000492 | 0 | 2.08 | 0.000633 | -0.0106 | 2.03 | 0.000492 | 0 | 2.08 | 0.000633 | -0.0106 | CFL | None | 2030 | 0.492 | 2030 | 0.492 | 1.02 | 1.29 | -0.00522
CFLNoneSCGSCnExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCG | SCn | Ex | CZ06 | 2.03 | 0.000492 | 0 | 2.08 | 0.000633 | -0.0106 | 2.03 | 0.000492 | 0 | 2.08 | 0.000633 | -0.0106 | CFL | None | 2030 | 0.492 | 2030 | 0.492 | 1.02 | 1.29 | -0.00522
CFLNoneSDGSCnExCZ07 | Com-Iltg-dWatt-CFL_OSnone | SDG | SCn | Ex | CZ07 | 2.03 | 0.000492 | 0 | 2.05 | 0.000636 | -0.00851 | 2.03 | 0.000492 | 0 | 2.05 | 0.000636 | -0.00851 | CFL | None | 2030 | 0.492 | 2030 | 0.492 | 1.01 | 1.29 | -0.00419
CFLNoneSDGSCnExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SDG | SCn | Ex | CZ08 | 2.03 | 0.000492 | 0 | 2.12 | 0.000632 | -0.00905 | 2.03 | 0.000492 | 0 | 2.12 | 0.000632 | -0.00905 | CFL | None | 2030 | 0.492 | 2030 | 0.492 | 1.04 | 1.28 | -0.00446
CFLNoneSCESCnExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | SCn | Ex | CZ08 | 2.03 | 0.000492 | 0 | 2.12 | 0.000632 | -0.00905 | 2.03 | 0.000492 | 0 | 2.12 | 0.000632 | -0.00905 | CFL | None | 2030 | 0.492 | 2030 | 0.492 | 1.04 | 1.28 | -0.00446
CFLNoneSCGSCnExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCG | SCn | Ex | CZ08 | 2.03 | 0.000492 | 0 | 2.12 | 0.000632 | -0.00905 | 2.03 | 0.000492 | 0 | 2.12 | 0.000632 | -0.00905 | CFL | None | 2030 | 0.492 | 2030 | 0.492 | 1.04 | 1.28 | -0.00446
CFLNoneSCGSCnExCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCG | SCn | Ex | CZ09 | 2.03 | 0.000492 | 0 | 2.12 | 0.000648 | -0.0109 | 2.03 | 0.000492 | 0 | 2.12 | 0.000648 | -0.0109 | CFL | None | 2030 | 0.492 | 2030 | 0.492 | 1.04 | 1.32 | -0.00537
CFLNoneSCESCnExCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | SCn | Ex | CZ09 | 2.03 | 0.000492 | 0 | 2.12 | 0.000648 | -0.0109 | 2.03 | 0.000492 | 0 | 2.12 | 0.000648 | -0.0109 | CFL | None | 2030 | 0.492 | 2030 | 0.492 | 1.04 | 1.32 | -0.00537
CFLNoneSCESCnExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | SCn | Ex | CZ10 | 2.03 | 0.000492 | 0 | 2.12 | 0.00064 | -0.0115 | 2.03 | 0.000492 | 0 | 2.12 | 0.00064 | -0.0115 | CFL | None | 2030 | 0.492 | 2030 | 0.492 | 1.04 | 1.3 | -0.00567
CFLNoneSCGSCnExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCG | SCn | Ex | CZ10 | 2.03 | 0.000492 | 0 | 2.12 | 0.00064 | -0.0115 | 2.03 | 0.000492 | 0 | 2.12 | 0.00064 | -0.0115 | CFL | None | 2030 | 0.492 | 2030 | 0.492 | 1.04 | 1.3 | -0.00567
CFLNoneSDGSCnExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SDG | SCn | Ex | CZ10 | 2.03 | 0.000492 | 0 | 2.12 | 0.00064 | -0.0115 | 2.03 | 0.000492 | 0 | 2.12 | 0.00064 | -0.0115 | CFL | None | 2030 | 0.492 | 2030 | 0.492 | 1.04 | 1.3 | -0.00567
CFLNonePGESCnExCZ11 | Com-Iltg-dWatt-CFL_OSnone | PGE | SCn | Ex | CZ11 | 2.03 | 0.000492 | 0 | 1.99 | 0.000598 | -0.0168 | 2.03 | 0.000492 | 0 | 1.99 | 0.000598 | -0.0168 | CFL | None | 2030 | 0.492 | 2030 | 0.492 | 0.98 | 1.22 | -0.00828
CFLNonePGESCnExCZ12 | Com-Iltg-dWatt-CFL_OSnone | PGE | SCn | Ex | CZ12 | 2.03 | 0.000492 | 0 | 2 | 0.000606 | -0.0169 | 2.03 | 0.000492 | 0 | 2 | 0.000606 | -0.0169 | CFL | None | 2030 | 0.492 | 2030 | 0.492 | 0.985 | 1.23 | -0.00833
CFLNoneSCESCnExCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | SCn | Ex | CZ13 | 2.03 | 0.000492 | 0 | 2.07 | 0.000632 | -0.0156 | 2.03 | 0.000492 | 0 | 2.07 | 0.000632 | -0.0156 | CFL | None | 2030 | 0.492 | 2030 | 0.492 | 1.02 | 1.28 | -0.00768
CFLNonePGESCnExCZ13 | Com-Iltg-dWatt-CFL_OSnone | PGE | SCn | Ex | CZ13 | 2.03 | 0.000492 | 0 | 2.07 | 0.000632 | -0.0156 | 2.03 | 0.000492 | 0 | 2.07 | 0.000632 | -0.0156 | CFL | None | 2030 | 0.492 | 2030 | 0.492 | 1.02 | 1.28 | -0.00768
CFLNoneSCGSCnExCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCG | SCn | Ex | CZ13 | 2.03 | 0.000492 | 0 | 2.07 | 0.000632 | -0.0156 | 2.03 | 0.000492 | 0 | 2.07 | 0.000632 | -0.0156 | CFL | None | 2030 | 0.492 | 2030 | 0.492 | 1.02 | 1.28 | -0.00768
CFLNoneSDGSCnExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SDG | SCn | Ex | CZ14 | 2.03 | 0.000492 | 0 | 2.06 | 0.000628 | -0.0171 | 2.03 | 0.000492 | 0 | 2.06 | 0.000628 | -0.0171 | CFL | None | 2030 | 0.492 | 2030 | 0.492 | 1.01 | 1.28 | -0.00842
CFLNoneSCGSCnExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCG | SCn | Ex | CZ14 | 2.03 | 0.000492 | 0 | 2.06 | 0.000628 | -0.0171 | 2.03 | 0.000492 | 0 | 2.06 | 0.000628 | -0.0171 | CFL | None | 2030 | 0.492 | 2030 | 0.492 | 1.01 | 1.28 | -0.00842
CFLNoneSCESCnExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | SCn | Ex | CZ14 | 2.03 | 0.000492 | 0 | 2.06 | 0.000628 | -0.0171 | 2.03 | 0.000492 | 0 | 2.06 | 0.000628 | -0.0171 | CFL | None | 2030 | 0.492 | 2030 | 0.492 | 1.01 | 1.28 | -0.00842
CFLNoneSDGSCnExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SDG | SCn | Ex | CZ15 | 2.03 | 0.000492 | 0 | 2.27 | 0.000629 | -0.00479 | 2.03 | 0.000492 | 0 | 2.27 | 0.000629 | -0.00479 | CFL | None | 2030 | 0.492 | 2030 | 0.492 | 1.12 | 1.28 | -0.00236
CFLNoneSCESCnExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | SCn | Ex | CZ15 | 2.03 | 0.000492 | 0 | 2.27 | 0.000629 | -0.00479 | 2.03 | 0.000492 | 0 | 2.27 | 0.000629 | -0.00479 | CFL | None | 2030 | 0.492 | 2030 | 0.492 | 1.12 | 1.28 | -0.00236
CFLNoneSCGSCnExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCG | SCn | Ex | CZ15 | 2.03 | 0.000492 | 0 | 2.27 | 0.000629 | -0.00479 | 2.03 | 0.000492 | 0 | 2.27 | 0.000629 | -0.00479 | CFL | None | 2030 | 0.492 | 2030 | 0.492 | 1.12 | 1.28 | -0.00236
CFLNoneSCESCnExCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | SCn | Ex | CZ16 | 2.03 | 0.000492 | 0 | 1.86 | 0.000614 | -0.0248 | 2.03 | 0.000492 | 0 | 1.86 | 0.000614 | -0.0248 | CFL | None | 2030 | 0.492 | 2030 | 0.492 | 0.916 | 1.25 | -0.0122
CFLNoneSCGSCnExCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCG | SCn | Ex | CZ16 | 2.03 | 0.000492 | 0 | 1.86 | 0.000614 | -0.0248 | 2.03 | 0.000492 | 0 | 1.86 | 0.000614 | -0.0248 | CFL | None | 2030 | 0.492 | 2030 | 0.492 | 0.916 | 1.25 | -0.0122
CFLNonePGESCnExCZ16 | Com-Iltg-dWatt-CFL_OSnone | PGE | SCn | Ex | CZ16 | 2.03 | 0.000492 | 0 | 1.86 | 0.000614 | -0.0248 | 2.03 | 0.000492 | 0 | 1.86 | 0.000614 | -0.0248 | CFL | None | 2030 | 0.492 | 2030 | 0.492 | 0.916 | 1.25 | -0.0122
CFLNoneSCGSCnExIOU | Com-Iltg-dWatt-CFL_OSnone | SCG | SCn | Ex | IOU | 2.03 | 0.000492 | 0 | 2.11 | 0.000638 | -0.0105 | 2.03 | 0.000492 | 0 | 2.11 | 0.000638 | -0.0105 | CFL | None | 2030 | 0.492 | 2030 | 0.492 | 1.04 | 1.3 | -0.00517
CFLNoneSCESCnExIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | SCn | Ex | IOU | 2.03 | 0.000492 | 0 | 2.11 | 0.000636 | -0.0105 | 2.03 | 0.000492 | 0 | 2.11 | 0.000636 | -0.0105 | CFL | None | 2030 | 0.492 | 2030 | 0.492 | 1.04 | 1.29 | -0.00517
CFLNonePGESCnExIOU | Com-Iltg-dWatt-CFL_OSnone | PGE | SCn | Ex | IOU | 2.03 | 0.000492 | 0 | 1.96 | 0.000625 | -0.0179 | 2.03 | 0.000492 | 0 | 1.96 | 0.000625 | -0.0179 | CFL | None | 2030 | 0.492 | 2030 | 0.492 | 0.966 | 1.27 | -0.00882
CFLNoneSDGSCnExIOU | Com-Iltg-dWatt-CFL_OSnone | SDG | SCn | Ex | IOU | 2.03 | 0.000492 | 0 | 2.07 | 0.000637 | -0.00949 | 2.03 | 0.000492 | 0 | 2.07 | 0.000637 | -0.00949 | CFL | None | 2030 | 0.492 | 2030 | 0.492 | 1.02 | 1.29 | -0.00467
CFLNonePGESCnNewCZ01 | Com-Iltg-dWatt-CFL_OSnone | PGE | SCn | New | CZ01 | 2.03 | 0.000492 | 0 | 1.74 | 0.000492 | -0.0367 | 2.03 | 0.000492 | 0 | 1.74 | 0.000492 | -0.0367 | CFL | None | 2030 | 0.492 | 2030 | 0.492 | 0.857 | 1 | -0.0181
CFLNonePGESCnNewCZ02 | Com-Iltg-dWatt-CFL_OSnone | PGE | SCn | New | CZ02 | 2.03 | 0.000492 | 0 | 1.94 | 0.000596 | -0.0192 | 2.03 | 0.000492 | 0 | 1.94 | 0.000596 | -0.0192 | CFL | None | 2030 | 0.492 | 2030 | 0.492 | 0.956 | 1.21 | -0.00946
CFLNonePGESCnNewCZ03 | Com-Iltg-dWatt-CFL_OSnone | PGE | SCn | New | CZ03 | 2.03 | 0.000492 | 0 | 1.88 | 0.000615 | -0.0215 | 2.03 | 0.000492 | 0 | 1.88 | 0.000615 | -0.0215 | CFL | None | 2030 | 0.492 | 2030 | 0.492 | 0.926 | 1.25 | -0.0106
CFLNonePGESCnNewCZ04 | Com-Iltg-dWatt-CFL_OSnone | PGE | SCn | New | CZ04 | 2.03 | 0.000492 | 0 | 1.98 | 0.000591 | -0.0171 | 2.03 | 0.000492 | 0 | 1.98 | 0.000591 | -0.0171 | CFL | None | 2030 | 0.492 | 2030 | 0.492 | 0.975 | 1.2 | -0.00842
CFLNoneSCESCnNewCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | SCn | New | CZ05 | 2.03 | 0.000492 | 0 | 1.89 | 0.000617 | -0.0223 | 2.03 | 0.000492 | 0 | 1.89 | 0.000617 | -0.0223 | CFL | None | 2030 | 0.492 | 2030 | 0.492 | 0.931 | 1.25 | -0.011
CFLNonePGESCnNewCZ05 | Com-Iltg-dWatt-CFL_OSnone | PGE | SCn | New | CZ05 | 2.03 | 0.000492 | 0 | 1.86 | 0.000588 | -0.0217 | 2.03 | 0.000492 | 0 | 1.86 | 0.000588 | -0.0217 | CFL | None | 2030 | 0.492 | 2030 | 0.492 | 0.916 | 1.2 | -0.0107
CFLNoneSCESCnNewCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | SCn | New | CZ06 | 2.03 | 0.000492 | 0 | 2.03 | 0.000592 | -0.0119 | 2.03 | 0.000492 | 0 | 2.03 | 0.000592 | -0.0119 | CFL | None | 2030 | 0.492 | 2030 | 0.492 | 1 | 1.2 | -0.00586
CFLNoneSDGSCnNewCZ06 | Com-Iltg-dWatt-CFL_OSnone | SDG | SCn | New | CZ06 | 2.03 | 0.000492 | 0 | 2.03 | 0.000589 | -0.012 | 2.03 | 0.000492 | 0 | 2.03 | 0.000589 | -0.012 | CFL | None | 2030 | 0.492 | 2030 | 0.492 | 1 | 1.2 | -0.00591
CFLNoneSDGSCnNewCZ07 | Com-Iltg-dWatt-CFL_OSnone | SDG | SCn | New | CZ07 | 2.03 | 0.000492 | 0 | 2.02 | 0.000602 | -0.00993 | 2.03 | 0.000492 | 0 | 2.02 | 0.000602 | -0.00993 | CFL | None | 2030 | 0.492 | 2030 | 0.492 | 0.995 | 1.22 | -0.00489
CFLNoneSDGSCnNewCZ08 | Com-Iltg-dWatt-CFL_OSnone | SDG | SCn | New | CZ08 | 2.03 | 0.000492 | 0 | 2.07 | 0.000598 | -0.0104 | 2.03 | 0.000492 | 0 | 2.07 | 0.000598 | -0.0104 | CFL | None | 2030 | 0.492 | 2030 | 0.492 | 1.02 | 1.22 | -0.00512
CFLNoneSCESCnNewCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | SCn | New | CZ08 | 2.03 | 0.000492 | 0 | 2.08 | 0.0006 | -0.0103 | 2.03 | 0.000492 | 0 | 2.08 | 0.0006 | -0.0103 | CFL | None | 2030 | 0.492 | 2030 | 0.492 | 1.02 | 1.22 | -0.00507
CFLNoneSCESCnNewCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | SCn | New | CZ09 | 2.03 | 0.000492 | 0 | 2.08 | 0.00062 | -0.0111 | 2.03 | 0.000492 | 0 | 2.08 | 0.00062 | -0.0111 | CFL | None | 2030 | 0.492 | 2030 | 0.492 | 1.02 | 1.26 | -0.00547
CFLNoneSCESCnNewCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | SCn | New | CZ10 | 2.03 | 0.000492 | 0 | 2.09 | 0.000615 | -0.0121 | 2.03 | 0.000492 | 0 | 2.09 | 0.000615 | -0.0121 | CFL | None | 2030 | 0.492 | 2030 | 0.492 | 1.03 | 1.25 | -0.00596
CFLNoneSDGSCnNewCZ10 | Com-Iltg-dWatt-CFL_OSnone | SDG | SCn | New | CZ10 | 2.03 | 0.000492 | 0 | 2.08 | 0.000612 | -0.0122 | 2.03 | 0.000492 | 0 | 2.08 | 0.000612 | -0.0122 | CFL | None | 2030 | 0.492 | 2030 | 0.492 | 1.02 | 1.24 | -0.00601
CFLNonePGESCnNewCZ11 | Com-Iltg-dWatt-CFL_OSnone | PGE | SCn | New | CZ11 | 2.03 | 0.000492 | 0 | 1.98 | 0.000584 | -0.0175 | 2.03 | 0.000492 | 0 | 1.98 | 0.000584 | -0.0175 | CFL | None | 2030 | 0.492 | 2030 | 0.492 | 0.975 | 1.19 | -0.00862
CFLNonePGESCnNewCZ12 | Com-Iltg-dWatt-CFL_OSnone | PGE | SCn | New | CZ12 | 2.03 | 0.000492 | 0 | 1.98 | 0.000587 | -0.0178 | 2.03 | 0.000492 | 0 | 1.98 | 0.000587 | -0.0178 | CFL | None | 2030 | 0.492 | 2030 | 0.492 | 0.975 | 1.19 | -0.00877
CFLNonePGESCnNewCZ13 | Com-Iltg-dWatt-CFL_OSnone | PGE | SCn | New | CZ13 | 2.03 | 0.000492 | 0 | 1.97 | 0.000572 | -0.0154 | 2.03 | 0.000492 | 0 | 1.97 | 0.000572 | -0.0154 | CFL | None | 2030 | 0.492 | 2030 | 0.492 | 0.97 | 1.16 | -0.00759
CFLNoneSCESCnNewCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | SCn | New | CZ13 | 2.03 | 0.000492 | 0 | 2.03 | 0.000599 | -0.0159 | 2.03 | 0.000492 | 0 | 2.03 | 0.000599 | -0.0159 | CFL | None | 2030 | 0.492 | 2030 | 0.492 | 1 | 1.22 | -0.00783
CFLNoneSDGSCnNewCZ14 | Com-Iltg-dWatt-CFL_OSnone | SDG | SCn | New | CZ14 | 2.03 | 0.000492 | 0 | 2.04 | 0.00061 | -0.0179 | 2.03 | 0.000492 | 0 | 2.04 | 0.00061 | -0.0179 | CFL | None | 2030 | 0.492 | 2030 | 0.492 | 1 | 1.24 | -0.00882
CFLNoneSCESCnNewCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | SCn | New | CZ14 | 2.03 | 0.000492 | 0 | 2.05 | 0.000613 | -0.0178 | 2.03 | 0.000492 | 0 | 2.05 | 0.000613 | -0.0178 | CFL | None | 2030 | 0.492 | 2030 | 0.492 | 1.01 | 1.25 | -0.00877
CFLNoneSDGSCnNewCZ15 | Com-Iltg-dWatt-CFL_OSnone | SDG | SCn | New | CZ15 | 2.03 | 0.000492 | 0 | 2.21 | 0.000615 | -0.0038 | 2.03 | 0.000492 | 0 | 2.21 | 0.000615 | -0.0038 | CFL | None | 2030 | 0.492 | 2030 | 0.492 | 1.09 | 1.25 | -0.00187
CFLNoneSCESCnNewCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | SCn | New | CZ15 | 2.03 | 0.000492 | 0 | 2.22 | 0.000618 | -0.00378 | 2.03 | 0.000492 | 0 | 2.22 | 0.000618 | -0.00378 | CFL | None | 2030 | 0.492 | 2030 | 0.492 | 1.09 | 1.26 | -0.00186
CFLNoneSCESCnNewCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | SCn | New | CZ16 | 2.03 | 0.000492 | 0 | 1.84 | 0.000592 | -0.0258 | 2.03 | 0.000492 | 0 | 1.84 | 0.000592 | -0.0258 | CFL | None | 2030 | 0.492 | 2030 | 0.492 | 0.906 | 1.2 | -0.0127
CFLNonePGESCnNewCZ16 | Com-Iltg-dWatt-CFL_OSnone | PGE | SCn | New | CZ16 | 2.03 | 0.000492 | 0 | 1.8 | 0.000568 | -0.025 | 2.03 | 0.000492 | 0 | 1.8 | 0.000568 | -0.025 | CFL | None | 2030 | 0.492 | 2030 | 0.492 | 0.887 | 1.15 | -0.0123
CFLNoneSCGSCnNewIOU | Com-Iltg-dWatt-CFL_OSnone | SCG | SCn | New | IOU | 2.03 | 0.000492 | 0 | 2.07 | 0.000607 | -0.0117 | 2.03 | 0.000492 | 0 | 2.07 | 0.000607 | -0.0117 | CFL | None | 2030 | 0.492 | 2030 | 0.492 | 1.02 | 1.23 | -0.00576
CFLNonePGESCnNewIOU | Com-Iltg-dWatt-CFL_OSnone | PGE | SCn | New | IOU | 2.03 | 0.000492 | 0 | 2.02 | 0.000599 | -0.0165 | 2.03 | 0.000492 | 0 | 2.02 | 0.000599 | -0.0165 | CFL | None | 2030 | 0.492 | 2030 | 0.492 | 0.995 | 1.22 | -0.00813
CFLNoneSCESCnNewIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | SCn | New | IOU | 2.03 | 0.000492 | 0 | 2.08 | 0.000607 | -0.0118 | 2.03 | 0.000492 | 0 | 2.08 | 0.000607 | -0.0118 | CFL | None | 2030 | 0.492 | 2030 | 0.492 | 1.02 | 1.23 | -0.00581
CFLNoneSDGSCnNewIOU | Com-Iltg-dWatt-CFL_OSnone | SDG | SCn | New | IOU | 2.03 | 0.000492 | 0 | 2.04 | 0.000605 | -0.0107 | 2.03 | 0.000492 | 0 | 2.04 | 0.000605 | -0.0107 | CFL | None | 2030 | 0.492 | 2030 | 0.492 | 1 | 1.23 | -0.00527
CFLNonePGESUnExCZ01 | Com-Iltg-dWatt-CFL_OSnone | PGE | SUn | Ex | CZ01 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | CFL | None | 1350 | 0.236 | 1350 | 0.236 | 1 | 1 | 0
CFLNonePGESUnExCZ02 | Com-Iltg-dWatt-CFL_OSnone | PGE | SUn | Ex | CZ02 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | CFL | None | 1350 | 0.236 | 1350 | 0.236 | 1 | 1 | 0
CFLNonePGESUnExCZ03 | Com-Iltg-dWatt-CFL_OSnone | PGE | SUn | Ex | CZ03 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | CFL | None | 1350 | 0.236 | 1350 | 0.236 | 1 | 1 | 0
CFLNonePGESUnExCZ04 | Com-Iltg-dWatt-CFL_OSnone | PGE | SUn | Ex | CZ04 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | CFL | None | 1350 | 0.236 | 1350 | 0.236 | 1 | 1 | 0
CFLNoneSCESUnExCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | SUn | Ex | CZ05 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | CFL | None | 1350 | 0.236 | 1350 | 0.236 | 1 | 1 | 0
CFLNonePGESUnExCZ05 | Com-Iltg-dWatt-CFL_OSnone | PGE | SUn | Ex | CZ05 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | CFL | None | 1350 | 0.236 | 1350 | 0.236 | 1 | 1 | 0
CFLNoneSCGSUnExCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCG | SUn | Ex | CZ05 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | CFL | None | 1350 | 0.236 | 1350 | 0.236 | 1 | 1 | 0
CFLNoneSCESUnExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | SUn | Ex | CZ06 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | CFL | None | 1350 | 0.236 | 1350 | 0.236 | 1 | 1 | 0
CFLNoneSCGSUnExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCG | SUn | Ex | CZ06 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | CFL | None | 1350 | 0.236 | 1350 | 0.236 | 1 | 1 | 0
CFLNoneSDGSUnExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SDG | SUn | Ex | CZ06 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | CFL | None | 1350 | 0.236 | 1350 | 0.236 | 1 | 1 | 0
CFLNoneSDGSUnExCZ07 | Com-Iltg-dWatt-CFL_OSnone | SDG | SUn | Ex | CZ07 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | CFL | None | 1350 | 0.236 | 1350 | 0.236 | 1 | 1 | 0
CFLNoneSCESUnExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | SUn | Ex | CZ08 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | CFL | None | 1350 | 0.236 | 1350 | 0.236 | 1 | 1 | 0
CFLNoneSDGSUnExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SDG | SUn | Ex | CZ08 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | CFL | None | 1350 | 0.236 | 1350 | 0.236 | 1 | 1 | 0
CFLNoneSCGSUnExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCG | SUn | Ex | CZ08 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | CFL | None | 1350 | 0.236 | 1350 | 0.236 | 1 | 1 | 0
CFLNoneSCGSUnExCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCG | SUn | Ex | CZ09 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | CFL | None | 1350 | 0.236 | 1350 | 0.236 | 1 | 1 | 0
CFLNoneSCESUnExCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | SUn | Ex | CZ09 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | CFL | None | 1350 | 0.236 | 1350 | 0.236 | 1 | 1 | 0
CFLNoneSDGSUnExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SDG | SUn | Ex | CZ10 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | CFL | None | 1350 | 0.236 | 1350 | 0.236 | 1 | 1 | 0
CFLNoneSCGSUnExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCG | SUn | Ex | CZ10 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | CFL | None | 1350 | 0.236 | 1350 | 0.236 | 1 | 1 | 0
CFLNoneSCESUnExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | SUn | Ex | CZ10 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | CFL | None | 1350 | 0.236 | 1350 | 0.236 | 1 | 1 | 0
CFLNonePGESUnExCZ11 | Com-Iltg-dWatt-CFL_OSnone | PGE | SUn | Ex | CZ11 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | CFL | None | 1350 | 0.236 | 1350 | 0.236 | 1 | 1 | 0
CFLNonePGESUnExCZ12 | Com-Iltg-dWatt-CFL_OSnone | PGE | SUn | Ex | CZ12 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | CFL | None | 1350 | 0.236 | 1350 | 0.236 | 1 | 1 | 0
CFLNonePGESUnExCZ13 | Com-Iltg-dWatt-CFL_OSnone | PGE | SUn | Ex | CZ13 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | CFL | None | 1350 | 0.236 | 1350 | 0.236 | 1 | 1 | 0
CFLNoneSCGSUnExCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCG | SUn | Ex | CZ13 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | CFL | None | 1350 | 0.236 | 1350 | 0.236 | 1 | 1 | 0
CFLNoneSCESUnExCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | SUn | Ex | CZ13 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | CFL | None | 1350 | 0.236 | 1350 | 0.236 | 1 | 1 | 0
CFLNoneSCGSUnExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCG | SUn | Ex | CZ14 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | CFL | None | 1350 | 0.236 | 1350 | 0.236 | 1 | 1 | 0
CFLNoneSDGSUnExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SDG | SUn | Ex | CZ14 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | CFL | None | 1350 | 0.236 | 1350 | 0.236 | 1 | 1 | 0
CFLNoneSCESUnExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | SUn | Ex | CZ14 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | CFL | None | 1350 | 0.236 | 1350 | 0.236 | 1 | 1 | 0
CFLNoneSCESUnExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | SUn | Ex | CZ15 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | CFL | None | 1350 | 0.236 | 1350 | 0.236 | 1 | 1 | 0
CFLNoneSDGSUnExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SDG | SUn | Ex | CZ15 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | CFL | None | 1350 | 0.236 | 1350 | 0.236 | 1 | 1 | 0
CFLNoneSCGSUnExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCG | SUn | Ex | CZ15 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | CFL | None | 1350 | 0.236 | 1350 | 0.236 | 1 | 1 | 0
CFLNoneSCESUnExCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | SUn | Ex | CZ16 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | CFL | None | 1350 | 0.236 | 1350 | 0.236 | 1 | 1 | 0
CFLNoneSCGSUnExCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCG | SUn | Ex | CZ16 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | CFL | None | 1350 | 0.236 | 1350 | 0.236 | 1 | 1 | 0
CFLNonePGESUnExCZ16 | Com-Iltg-dWatt-CFL_OSnone | PGE | SUn | Ex | CZ16 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | CFL | None | 1350 | 0.236 | 1350 | 0.236 | 1 | 1 | 0
CFLNonePGESUnExIOU | Com-Iltg-dWatt-CFL_OSnone | PGE | SUn | Ex | IOU | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | CFL | None | 1350 | 0.236 | 1350 | 0.236 | 1 | 1 | 0
CFLNoneSCESUnExIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | SUn | Ex | IOU | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | CFL | None | 1350 | 0.236 | 1350 | 0.236 | 1 | 1 | 0
CFLNoneSCGSUnExIOU | Com-Iltg-dWatt-CFL_OSnone | SCG | SUn | Ex | IOU | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | CFL | None | 1350 | 0.236 | 1350 | 0.236 | 1 | 1 | 0
CFLNoneSDGSUnExIOU | Com-Iltg-dWatt-CFL_OSnone | SDG | SUn | Ex | IOU | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | CFL | None | 1350 | 0.236 | 1350 | 0.236 | 1 | 1 | 0
CFLNonePGESUnNewCZ01 | Com-Iltg-dWatt-CFL_OSnone | PGE | SUn | New | CZ01 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | CFL | None | 1350 | 0.236 | 1350 | 0.236 | 1 | 1 | 0
CFLNonePGESUnNewCZ02 | Com-Iltg-dWatt-CFL_OSnone | PGE | SUn | New | CZ02 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | CFL | None | 1350 | 0.236 | 1350 | 0.236 | 1 | 1 | 0
CFLNonePGESUnNewCZ03 | Com-Iltg-dWatt-CFL_OSnone | PGE | SUn | New | CZ03 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | CFL | None | 1350 | 0.236 | 1350 | 0.236 | 1 | 1 | 0
CFLNonePGESUnNewCZ04 | Com-Iltg-dWatt-CFL_OSnone | PGE | SUn | New | CZ04 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | CFL | None | 1350 | 0.236 | 1350 | 0.236 | 1 | 1 | 0
CFLNoneSCESUnNewCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | SUn | New | CZ05 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | CFL | None | 1350 | 0.236 | 1350 | 0.236 | 1 | 1 | 0
CFLNonePGESUnNewCZ05 | Com-Iltg-dWatt-CFL_OSnone | PGE | SUn | New | CZ05 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | CFL | None | 1350 | 0.236 | 1350 | 0.236 | 1 | 1 | 0
CFLNoneSCESUnNewCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | SUn | New | CZ06 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | CFL | None | 1350 | 0.236 | 1350 | 0.236 | 1 | 1 | 0
CFLNoneSDGSUnNewCZ06 | Com-Iltg-dWatt-CFL_OSnone | SDG | SUn | New | CZ06 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | CFL | None | 1350 | 0.236 | 1350 | 0.236 | 1 | 1 | 0
CFLNoneSDGSUnNewCZ07 | Com-Iltg-dWatt-CFL_OSnone | SDG | SUn | New | CZ07 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | CFL | None | 1350 | 0.236 | 1350 | 0.236 | 1 | 1 | 0
CFLNoneSCESUnNewCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | SUn | New | CZ08 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | CFL | None | 1350 | 0.236 | 1350 | 0.236 | 1 | 1 | 0
CFLNoneSDGSUnNewCZ08 | Com-Iltg-dWatt-CFL_OSnone | SDG | SUn | New | CZ08 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | CFL | None | 1350 | 0.236 | 1350 | 0.236 | 1 | 1 | 0
CFLNoneSCESUnNewCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | SUn | New | CZ09 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | CFL | None | 1350 | 0.236 | 1350 | 0.236 | 1 | 1 | 0
CFLNoneSDGSUnNewCZ10 | Com-Iltg-dWatt-CFL_OSnone | SDG | SUn | New | CZ10 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | CFL | None | 1350 | 0.236 | 1350 | 0.236 | 1 | 1 | 0
CFLNoneSCESUnNewCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | SUn | New | CZ10 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | CFL | None | 1350 | 0.236 | 1350 | 0.236 | 1 | 1 | 0
CFLNonePGESUnNewCZ11 | Com-Iltg-dWatt-CFL_OSnone | PGE | SUn | New | CZ11 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | CFL | None | 1350 | 0.236 | 1350 | 0.236 | 1 | 1 | 0
CFLNonePGESUnNewCZ12 | Com-Iltg-dWatt-CFL_OSnone | PGE | SUn | New | CZ12 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | CFL | None | 1350 | 0.236 | 1350 | 0.236 | 1 | 1 | 0
CFLNonePGESUnNewCZ13 | Com-Iltg-dWatt-CFL_OSnone | PGE | SUn | New | CZ13 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | CFL | None | 1350 | 0.236 | 1350 | 0.236 | 1 | 1 | 0
CFLNoneSCESUnNewCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | SUn | New | CZ13 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | CFL | None | 1350 | 0.236 | 1350 | 0.236 | 1 | 1 | 0
CFLNoneSDGSUnNewCZ14 | Com-Iltg-dWatt-CFL_OSnone | SDG | SUn | New | CZ14 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | CFL | None | 1350 | 0.236 | 1350 | 0.236 | 1 | 1 | 0
CFLNoneSCESUnNewCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | SUn | New | CZ14 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | CFL | None | 1350 | 0.236 | 1350 | 0.236 | 1 | 1 | 0
CFLNoneSDGSUnNewCZ15 | Com-Iltg-dWatt-CFL_OSnone | SDG | SUn | New | CZ15 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | CFL | None | 1350 | 0.236 | 1350 | 0.236 | 1 | 1 | 0
CFLNoneSCESUnNewCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | SUn | New | CZ15 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | CFL | None | 1350 | 0.236 | 1350 | 0.236 | 1 | 1 | 0
CFLNoneSCESUnNewCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | SUn | New | CZ16 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | CFL | None | 1350 | 0.236 | 1350 | 0.236 | 1 | 1 | 0
CFLNonePGESUnNewCZ16 | Com-Iltg-dWatt-CFL_OSnone | PGE | SUn | New | CZ16 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | CFL | None | 1350 | 0.236 | 1350 | 0.236 | 1 | 1 | 0
CFLNoneSCESUnNewIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | SUn | New | IOU | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | CFL | None | 1350 | 0.236 | 1350 | 0.236 | 1 | 1 | 0
CFLNoneSCGSUnNewIOU | Com-Iltg-dWatt-CFL_OSnone | SCG | SUn | New | IOU | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | CFL | None | 1350 | 0.236 | 1350 | 0.236 | 1 | 1 | 0
CFLNoneSDGSUnNewIOU | Com-Iltg-dWatt-CFL_OSnone | SDG | SUn | New | IOU | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | CFL | None | 1350 | 0.236 | 1350 | 0.236 | 1 | 1 | 0
CFLNonePGESUnNewIOU | Com-Iltg-dWatt-CFL_OSnone | PGE | SUn | New | IOU | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | 1.35 | 0.000236 | 0 | CFL | None | 1350 | 0.236 | 1350 | 0.236 | 1 | 1 | 0
CFLNonePGEWRfExCZ01 | Com-Iltg-dWatt-CFL_OSnone | PGE | WRf | Ex | CZ01 | 4.71 | 0.000563 | 0 | 7.52 | 0.000794 | 0 | 4.71 | 0.000563 | 0 | 7.52 | 0.000794 | 0 | CFL | None | 4710 | 0.563 | 4710 | 0.563 | 1.6 | 1.41 | 0
CFLNonePGEWRfExCZ02 | Com-Iltg-dWatt-CFL_OSnone | PGE | WRf | Ex | CZ02 | 4.71 | 0.000563 | 0 | 7.63 | 0.000715 | 0 | 4.71 | 0.000563 | 0 | 7.63 | 0.000715 | 0 | CFL | None | 4710 | 0.563 | 4710 | 0.563 | 1.62 | 1.27 | 0
CFLNonePGEWRfExCZ03 | Com-Iltg-dWatt-CFL_OSnone | PGE | WRf | Ex | CZ03 | 4.71 | 0.000563 | 0 | 7.62 | 0.000745 | 0 | 4.71 | 0.000563 | 0 | 7.62 | 0.000745 | 0 | CFL | None | 4710 | 0.563 | 4710 | 0.563 | 1.62 | 1.32 | 0
CFLNonePGEWRfExCZ04 | Com-Iltg-dWatt-CFL_OSnone | PGE | WRf | Ex | CZ04 | 4.71 | 0.000563 | 0 | 7.63 | 0.000719 | 0 | 4.71 | 0.000563 | 0 | 7.63 | 0.000719 | 0 | CFL | None | 4710 | 0.563 | 4710 | 0.563 | 1.62 | 1.28 | 0
CFLNonePGEWRfExCZ05 | Com-Iltg-dWatt-CFL_OSnone | PGE | WRf | Ex | CZ05 | 4.71 | 0.000563 | 0 | 7.2 | 0.000864 | 0 | 4.71 | 0.000563 | 0 | 7.2 | 0.000864 | 0 | CFL | None | 4710 | 0.563 | 4710 | 0.563 | 1.53 | 1.53 | 0
CFLNoneSCEWRfExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | WRf | Ex | CZ06 | 4.71 | 0.000563 | 0 | 7.41 | 0.000706 | 0 | 4.71 | 0.000563 | 0 | 7.41 | 0.000706 | 0 | CFL | None | 4710 | 0.563 | 4710 | 0.563 | 1.57 | 1.25 | 0
CFLNoneSCGWRfExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCG | WRf | Ex | CZ06 | 4.71 | 0.000563 | 0 | 7.41 | 0.000706 | 0 | 4.71 | 0.000563 | 0 | 7.41 | 0.000706 | 0 | CFL | None | 4710 | 0.563 | 4710 | 0.563 | 1.57 | 1.25 | 0
CFLNoneSDGWRfExCZ06 | Com-Iltg-dWatt-CFL_OSnone | SDG | WRf | Ex | CZ06 | 4.71 | 0.000563 | 0 | 7.41 | 0.000706 | 0 | 4.71 | 0.000563 | 0 | 7.41 | 0.000706 | 0 | CFL | None | 4710 | 0.563 | 4710 | 0.563 | 1.57 | 1.25 | 0
CFLNoneSDGWRfExCZ07 | Com-Iltg-dWatt-CFL_OSnone | SDG | WRf | Ex | CZ07 | 4.71 | 0.000563 | 0 | 7.37 | 0.000707 | 0 | 4.71 | 0.000563 | 0 | 7.37 | 0.000707 | 0 | CFL | None | 4710 | 0.563 | 4710 | 0.563 | 1.56 | 1.26 | 0
CFLNoneSCGWRfExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCG | WRf | Ex | CZ08 | 4.71 | 0.000563 | 0 | 7.35 | 0.000702 | 0 | 4.71 | 0.000563 | 0 | 7.35 | 0.000702 | 0 | CFL | None | 4710 | 0.563 | 4710 | 0.563 | 1.56 | 1.25 | 0
CFLNoneSCEWRfExCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | WRf | Ex | CZ08 | 4.71 | 0.000563 | 0 | 7.35 | 0.000702 | 0 | 4.71 | 0.000563 | 0 | 7.35 | 0.000702 | 0 | CFL | None | 4710 | 0.563 | 4710 | 0.563 | 1.56 | 1.25 | 0
CFLNoneSCEWRfExCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | WRf | Ex | CZ09 | 4.71 | 0.000563 | 0 | 7.54 | 0.000725 | 0 | 4.71 | 0.000563 | 0 | 7.54 | 0.000725 | 0 | CFL | None | 4710 | 0.563 | 4710 | 0.563 | 1.6 | 1.29 | 0
CFLNoneSCGWRfExCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCG | WRf | Ex | CZ09 | 4.71 | 0.000563 | 0 | 7.54 | 0.000725 | 0 | 4.71 | 0.000563 | 0 | 7.54 | 0.000725 | 0 | CFL | None | 4710 | 0.563 | 4710 | 0.563 | 1.6 | 1.29 | 0
CFLNoneSDGWRfExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SDG | WRf | Ex | CZ10 | 4.71 | 0.000563 | 0 | 7.59 | 0.000712 | 0 | 4.71 | 0.000563 | 0 | 7.59 | 0.000712 | 0 | CFL | None | 4710 | 0.563 | 4710 | 0.563 | 1.61 | 1.26 | 0
CFLNoneSCEWRfExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | WRf | Ex | CZ10 | 4.71 | 0.000563 | 0 | 7.59 | 0.000712 | 0 | 4.71 | 0.000563 | 0 | 7.59 | 0.000712 | 0 | CFL | None | 4710 | 0.563 | 4710 | 0.563 | 1.61 | 1.26 | 0
CFLNoneSCGWRfExCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCG | WRf | Ex | CZ10 | 4.71 | 0.000563 | 0 | 7.59 | 0.000712 | 0 | 4.71 | 0.000563 | 0 | 7.59 | 0.000712 | 0 | CFL | None | 4710 | 0.563 | 4710 | 0.563 | 1.61 | 1.26 | 0
CFLNonePGEWRfExCZ11 | Com-Iltg-dWatt-CFL_OSnone | PGE | WRf | Ex | CZ11 | 4.71 | 0.000563 | 0 | 7.6 | 0.000736 | 0 | 4.71 | 0.000563 | 0 | 7.6 | 0.000736 | 0 | CFL | None | 4710 | 0.563 | 4710 | 0.563 | 1.61 | 1.31 | 0
CFLNonePGEWRfExCZ12 | Com-Iltg-dWatt-CFL_OSnone | PGE | WRf | Ex | CZ12 | 4.71 | 0.000563 | 0 | 7.55 | 0.000722 | 0 | 4.71 | 0.000563 | 0 | 7.55 | 0.000722 | 0 | CFL | None | 4710 | 0.563 | 4710 | 0.563 | 1.6 | 1.28 | 0
CFLNoneSCEWRfExCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | WRf | Ex | CZ13 | 4.71 | 0.000563 | 0 | 7.6 | 0.00071 | 0 | 4.71 | 0.000563 | 0 | 7.6 | 0.00071 | 0 | CFL | None | 4710 | 0.563 | 4710 | 0.563 | 1.61 | 1.26 | 0
CFLNonePGEWRfExCZ13 | Com-Iltg-dWatt-CFL_OSnone | PGE | WRf | Ex | CZ13 | 4.71 | 0.000563 | 0 | 7.6 | 0.00071 | 0 | 4.71 | 0.000563 | 0 | 7.6 | 0.00071 | 0 | CFL | None | 4710 | 0.563 | 4710 | 0.563 | 1.61 | 1.26 | 0
CFLNoneSCGWRfExCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCG | WRf | Ex | CZ13 | 4.71 | 0.000563 | 0 | 7.6 | 0.00071 | 0 | 4.71 | 0.000563 | 0 | 7.6 | 0.00071 | 0 | CFL | None | 4710 | 0.563 | 4710 | 0.563 | 1.61 | 1.26 | 0
CFLNoneSCEWRfExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | WRf | Ex | CZ14 | 4.71 | 0.000563 | 0 | 7.19 | 0.000703 | 0 | 4.71 | 0.000563 | 0 | 7.19 | 0.000703 | 0 | CFL | None | 4710 | 0.563 | 4710 | 0.563 | 1.53 | 1.25 | 0
CFLNoneSCGWRfExCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCG | WRf | Ex | CZ14 | 4.71 | 0.000563 | 0 | 7.19 | 0.000703 | 0 | 4.71 | 0.000563 | 0 | 7.19 | 0.000703 | 0 | CFL | None | 4710 | 0.563 | 4710 | 0.563 | 1.53 | 1.25 | 0
CFLNoneSCEWRfExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | WRf | Ex | CZ15 | 4.71 | 0.000563 | 0 | 7.58 | 0.000708 | 0 | 4.71 | 0.000563 | 0 | 7.58 | 0.000708 | 0 | CFL | None | 4710 | 0.563 | 4710 | 0.563 | 1.61 | 1.26 | 0
CFLNoneSCGWRfExCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCG | WRf | Ex | CZ15 | 4.71 | 0.000563 | 0 | 7.58 | 0.000708 | 0 | 4.71 | 0.000563 | 0 | 7.58 | 0.000708 | 0 | CFL | None | 4710 | 0.563 | 4710 | 0.563 | 1.61 | 1.26 | 0
CFLNonePGEWRfExCZ16 | Com-Iltg-dWatt-CFL_OSnone | PGE | WRf | Ex | CZ16 | 4.71 | 0.000563 | 0 | 6.86 | 0.000798 | 0 | 4.71 | 0.000563 | 0 | 6.86 | 0.000798 | 0 | CFL | None | 4710 | 0.563 | 4710 | 0.563 | 1.46 | 1.42 | 0
CFLNoneSCGWRfExCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCG | WRf | Ex | CZ16 | 4.71 | 0.000563 | 0 | 6.86 | 0.000798 | 0 | 4.71 | 0.000563 | 0 | 6.86 | 0.000798 | 0 | CFL | None | 4710 | 0.563 | 4710 | 0.563 | 1.46 | 1.42 | 0
CFLNoneSCEWRfExCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | WRf | Ex | CZ16 | 4.71 | 0.000563 | 0 | 6.86 | 0.000798 | 0 | 4.71 | 0.000563 | 0 | 6.86 | 0.000798 | 0 | CFL | None | 4710 | 0.563 | 4710 | 0.563 | 1.46 | 1.42 | 0
CFLNonePGEWRfExIOU | Com-Iltg-dWatt-CFL_OSnone | PGE | WRf | Ex | IOU | 4.71 | 0.000563 | 0 | 7.58 | 0.000732 | 0 | 4.71 | 0.000563 | 0 | 7.58 | 0.000732 | 0 | CFL | None | 4710 | 0.563 | 4710 | 0.563 | 1.61 | 1.3 | 0
CFLNoneSDGWRfExIOU | Com-Iltg-dWatt-CFL_OSnone | SDG | WRf | Ex | IOU | 4.71 | 0.000563 | 0 | 7.42 | 0.000708 | 0 | 4.71 | 0.000563 | 0 | 7.42 | 0.000708 | 0 | CFL | None | 4710 | 0.563 | 4710 | 0.563 | 1.58 | 1.26 | 0
CFLNoneSCGWRfExIOU | Com-Iltg-dWatt-CFL_OSnone | SCG | WRf | Ex | IOU | 4.71 | 0.000563 | 0 | 7.47 | 0.00071 | 0 | 4.71 | 0.000563 | 0 | 7.47 | 0.00071 | 0 | CFL | None | 4710 | 0.563 | 4710 | 0.563 | 1.59 | 1.26 | 0
CFLNoneSCEWRfExIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | WRf | Ex | IOU | 4.71 | 0.000563 | 0 | 7.46 | 0.000709 | 0 | 4.71 | 0.000563 | 0 | 7.46 | 0.000709 | 0 | CFL | None | 4710 | 0.563 | 4710 | 0.563 | 1.58 | 1.26 | 0
CFLNonePGEWRfNewCZ01 | Com-Iltg-dWatt-CFL_OSnone | PGE | WRf | New | CZ01 | 4.71 | 0.000563 | 0 | 6.25 | 0.00113 | 0 | 4.71 | 0.000563 | 0 | 6.25 | 0.00113 | 0 | CFL | None | 4710 | 0.563 | 4710 | 0.563 | 1.33 | 2.01 | 0
CFLNonePGEWRfNewCZ02 | Com-Iltg-dWatt-CFL_OSnone | PGE | WRf | New | CZ02 | 4.71 | 0.000563 | 0 | 6.62 | 0.000761 | 0 | 4.71 | 0.000563 | 0 | 6.62 | 0.000761 | 0 | CFL | None | 4710 | 0.563 | 4710 | 0.563 | 1.41 | 1.35 | 0
CFLNonePGEWRfNewCZ03 | Com-Iltg-dWatt-CFL_OSnone | PGE | WRf | New | CZ03 | 4.71 | 0.000563 | 0 | 6.68 | 0.00113 | 0 | 4.71 | 0.000563 | 0 | 6.68 | 0.00113 | 0 | CFL | None | 4710 | 0.563 | 4710 | 0.563 | 1.42 | 2.01 | 0
CFLNonePGEWRfNewCZ04 | Com-Iltg-dWatt-CFL_OSnone | PGE | WRf | New | CZ04 | 4.71 | 0.000563 | 0 | 6.8 | 0.000825 | 0 | 4.71 | 0.000563 | 0 | 6.8 | 0.000825 | 0 | CFL | None | 4710 | 0.563 | 4710 | 0.563 | 1.44 | 1.47 | 0
CFLNoneSCEWRfNewCZ05 | Com-Iltg-dWatt-CFL_OSnone | SCE | WRf | New | CZ05 | 4.71 | 0.000563 | 0 | 6.62 | 0.00113 | 0 | 4.71 | 0.000563 | 0 | 6.62 | 0.00113 | 0 | CFL | None | 4710 | 0.563 | 4710 | 0.563 | 1.41 | 2.01 | 0
CFLNonePGEWRfNewCZ05 | Com-Iltg-dWatt-CFL_OSnone | PGE | WRf | New | CZ05 | 4.71 | 0.000563 | 0 | 6.62 | 0.00113 | 0 | 4.71 | 0.000563 | 0 | 6.62 | 0.00113 | 0 | CFL | None | 4710 | 0.563 | 4710 | 0.563 | 1.41 | 2.01 | 0
CFLNoneSCEWRfNewCZ06 | Com-Iltg-dWatt-CFL_OSnone | SCE | WRf | New | CZ06 | 4.71 | 0.000563 | 0 | 7.14 | 0.000694 | 0 | 4.71 | 0.000563 | 0 | 7.14 | 0.000694 | 0 | CFL | None | 4710 | 0.563 | 4710 | 0.563 | 1.52 | 1.23 | 0
CFLNoneSDGWRfNewCZ06 | Com-Iltg-dWatt-CFL_OSnone | SDG | WRf | New | CZ06 | 4.71 | 0.000563 | 0 | 7.14 | 0.000694 | 0 | 4.71 | 0.000563 | 0 | 7.14 | 0.000694 | 0 | CFL | None | 4710 | 0.563 | 4710 | 0.563 | 1.52 | 1.23 | 0
CFLNoneSDGWRfNewCZ07 | Com-Iltg-dWatt-CFL_OSnone | SDG | WRf | New | CZ07 | 4.71 | 0.000563 | 0 | 7.2 | 0.000695 | 0 | 4.71 | 0.000563 | 0 | 7.2 | 0.000695 | 0 | CFL | None | 4710 | 0.563 | 4710 | 0.563 | 1.53 | 1.23 | 0
CFLNoneSDGWRfNewCZ08 | Com-Iltg-dWatt-CFL_OSnone | SDG | WRf | New | CZ08 | 4.71 | 0.000563 | 0 | 7.1 | 0.000695 | 0 | 4.71 | 0.000563 | 0 | 7.1 | 0.000695 | 0 | CFL | None | 4710 | 0.563 | 4710 | 0.563 | 1.51 | 1.23 | 0
CFLNoneSCEWRfNewCZ08 | Com-Iltg-dWatt-CFL_OSnone | SCE | WRf | New | CZ08 | 4.71 | 0.000563 | 0 | 7.1 | 0.000695 | 0 | 4.71 | 0.000563 | 0 | 7.1 | 0.000695 | 0 | CFL | None | 4710 | 0.563 | 4710 | 0.563 | 1.51 | 1.23 | 0
CFLNoneSCEWRfNewCZ09 | Com-Iltg-dWatt-CFL_OSnone | SCE | WRf | New | CZ09 | 4.71 | 0.000563 | 0 | 6.95 | 0.000722 | 0 | 4.71 | 0.000563 | 0 | 6.95 | 0.000722 | 0 | CFL | None | 4710 | 0.563 | 4710 | 0.563 | 1.48 | 1.28 | 0
CFLNoneSCEWRfNewCZ10 | Com-Iltg-dWatt-CFL_OSnone | SCE | WRf | New | CZ10 | 4.71 | 0.000563 | 0 | 6.93 | 0.000704 | 0 | 4.71 | 0.000563 | 0 | 6.93 | 0.000704 | 0 | CFL | None | 4710 | 0.563 | 4710 | 0.563 | 1.47 | 1.25 | 0
CFLNoneSDGWRfNewCZ10 | Com-Iltg-dWatt-CFL_OSnone | SDG | WRf | New | CZ10 | 4.71 | 0.000563 | 0 | 6.93 | 0.000704 | 0 | 4.71 | 0.000563 | 0 | 6.93 | 0.000704 | 0 | CFL | None | 4710 | 0.563 | 4710 | 0.563 | 1.47 | 1.25 | 0
CFLNonePGEWRfNewCZ11 | Com-Iltg-dWatt-CFL_OSnone | PGE | WRf | New | CZ11 | 4.71 | 0.000563 | 0 | 6.78 | 0.000889 | 0 | 4.71 | 0.000563 | 0 | 6.78 | 0.000889 | 0 | CFL | None | 4710 | 0.563 | 4710 | 0.563 | 1.44 | 1.58 | 0
CFLNonePGEWRfNewCZ12 | Com-Iltg-dWatt-CFL_OSnone | PGE | WRf | New | CZ12 | 4.71 | 0.000563 | 0 | 6.75 | 0.00077 | 0 | 4.71 | 0.000563 | 0 | 6.75 | 0.00077 | 0 | CFL | None | 4710 | 0.563 | 4710 | 0.563 | 1.43 | 1.37 | 0
CFLNoneSCEWRfNewCZ13 | Com-Iltg-dWatt-CFL_OSnone | SCE | WRf | New | CZ13 | 4.71 | 0.000563 | 0 | 6.91 | 0.000704 | 0 | 4.71 | 0.000563 | 0 | 6.91 | 0.000704 | 0 | CFL | None | 4710 | 0.563 | 4710 | 0.563 | 1.47 | 1.25 | 0
CFLNonePGEWRfNewCZ13 | Com-Iltg-dWatt-CFL_OSnone | PGE | WRf | New | CZ13 | 4.71 | 0.000563 | 0 | 6.91 | 0.000704 | 0 | 4.71 | 0.000563 | 0 | 6.91 | 0.000704 | 0 | CFL | None | 4710 | 0.563 | 4710 | 0.563 | 1.47 | 1.25 | 0
CFLNoneSCEWRfNewCZ14 | Com-Iltg-dWatt-CFL_OSnone | SCE | WRf | New | CZ14 | 4.71 | 0.000563 | 0 | 6.67 | 0.000698 | 0 | 4.71 | 0.000563 | 0 | 6.67 | 0.000698 | 0 | CFL | None | 4710 | 0.563 | 4710 | 0.563 | 1.42 | 1.24 | 0
CFLNoneSDGWRfNewCZ14 | Com-Iltg-dWatt-CFL_OSnone | SDG | WRf | New | CZ14 | 4.71 | 0.000563 | 0 | 6.67 | 0.000698 | 0 | 4.71 | 0.000563 | 0 | 6.67 | 0.000698 | 0 | CFL | None | 4710 | 0.563 | 4710 | 0.563 | 1.42 | 1.24 | 0
CFLNoneSDGWRfNewCZ15 | Com-Iltg-dWatt-CFL_OSnone | SDG | WRf | New | CZ15 | 4.71 | 0.000563 | 0 | 7.16 | 0.000702 | 0 | 4.71 | 0.000563 | 0 | 7.16 | 0.000702 | 0 | CFL | None | 4710 | 0.563 | 4710 | 0.563 | 1.52 | 1.25 | 0
CFLNoneSCEWRfNewCZ15 | Com-Iltg-dWatt-CFL_OSnone | SCE | WRf | New | CZ15 | 4.71 | 0.000563 | 0 | 7.16 | 0.000702 | 0 | 4.71 | 0.000563 | 0 | 7.16 | 0.000702 | 0 | CFL | None | 4710 | 0.563 | 4710 | 0.563 | 1.52 | 1.25 | 0
CFLNonePGEWRfNewCZ16 | Com-Iltg-dWatt-CFL_OSnone | PGE | WRf | New | CZ16 | 4.71 | 0.000563 | 0 | 6.2 | 0.00113 | 0 | 4.71 | 0.000563 | 0 | 6.2 | 0.00113 | 0 | CFL | None | 4710 | 0.563 | 4710 | 0.563 | 1.32 | 2.01 | 0
CFLNoneSCEWRfNewCZ16 | Com-Iltg-dWatt-CFL_OSnone | SCE | WRf | New | CZ16 | 4.71 | 0.000563 | 0 | 6.2 | 0.00113 | 0 | 4.71 | 0.000563 | 0 | 6.2 | 0.00113 | 0 | CFL | None | 4710 | 0.563 | 4710 | 0.563 | 1.32 | 2.01 | 0
CFLNonePGEWRfNewIOU | Com-Iltg-dWatt-CFL_OSnone | PGE | WRf | New | IOU | 4.71 | 0.000563 | 0 | 6.89 | 0.000733 | 0 | 4.71 | 0.000563 | 0 | 6.89 | 0.000733 | 0 | CFL | None | 4710 | 0.563 | 4710 | 0.563 | 1.46 | 1.3 | 0
CFLNoneSCGWRfNewIOU | Com-Iltg-dWatt-CFL_OSnone | SCG | WRf | New | IOU | 4.71 | 0.000563 | 0 | 7.06 | 0.000697 | 0 | 4.71 | 0.000563 | 0 | 7.06 | 0.000697 | 0 | CFL | None | 4710 | 0.563 | 4710 | 0.563 | 1.5 | 1.24 | 0
CFLNoneSDGWRfNewIOU | Com-Iltg-dWatt-CFL_OSnone | SDG | WRf | New | IOU | 4.71 | 0.000563 | 0 | 7.14 | 0.000697 | 0 | 4.71 | 0.000563 | 0 | 7.14 | 0.000697 | 0 | CFL | None | 4710 | 0.563 | 4710 | 0.563 | 1.52 | 1.24 | 0
CFLNoneSCEWRfNewIOU | Com-Iltg-dWatt-CFL_OSnone | SCE | WRf | New | IOU | 4.71 | 0.000563 | 0 | 7.06 | 0.000698 | 0 | 4.71 | 0.000563 | 0 | 7.06 | 0.000698 | 0 | CFL | None | 4710 | 0.563 | 4710 | 0.563 | 1.5 | 1.24 | 0
CFLAllSpcPGEAsmExCZ01 | Com-Iltg-dWatt-CFL_OSspc | PGE | Asm | Ex | CZ01 | 1.04 | 0.000183 | 0 | 0.99 | 0.000212 | -0.0185 | 1.04 | 0.000183 | 0 | 0.99 | 0.000212 | -0.0185 | CFL | AllSpc | 1040 | 0.183 | 1040 | 0.183 | 0.952 | 1.16 | -0.0178
CFLAllSpcPGEAsmExCZ02 | Com-Iltg-dWatt-CFL_OSspc | PGE | Asm | Ex | CZ02 | 1.04 | 0.000183 | 0 | 1.07 | 0.000214 | -0.0107 | 1.04 | 0.000183 | 0 | 1.07 | 0.000214 | -0.0107 | CFL | AllSpc | 1040 | 0.183 | 1040 | 0.183 | 1.03 | 1.17 | -0.0103
CFLAllSpcPGEAsmExCZ03 | Com-Iltg-dWatt-CFL_OSspc | PGE | Asm | Ex | CZ03 | 1.04 | 0.000183 | 0 | 1.06 | 0.000214 | -0.0118 | 1.04 | 0.000183 | 0 | 1.06 | 0.000214 | -0.0118 | CFL | AllSpc | 1040 | 0.183 | 1040 | 0.183 | 1.02 | 1.17 | -0.0113
CFLAllSpcPGEAsmExCZ04 | Com-Iltg-dWatt-CFL_OSspc | PGE | Asm | Ex | CZ04 | 1.04 | 0.000183 | 0 | 1.09 | 0.000214 | -0.00868 | 1.04 | 0.000183 | 0 | 1.09 | 0.000214 | -0.00868 | CFL | AllSpc | 1040 | 0.183 | 1040 | 0.183 | 1.05 | 1.17 | -0.00835
CFLAllSpcSCGAsmExCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCG | Asm | Ex | CZ05 | 1.04 | 0.000183 | 0 | 1.09 | 0.000219 | -0.0101 | 1.04 | 0.000183 | 0 | 1.09 | 0.000219 | -0.0101 | CFL | AllSpc | 1040 | 0.183 | 1040 | 0.183 | 1.05 | 1.2 | -0.00971
CFLAllSpcSCEAsmExCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCE | Asm | Ex | CZ05 | 1.04 | 0.000183 | 0 | 1.09 | 0.000219 | -0.0101 | 1.04 | 0.000183 | 0 | 1.09 | 0.000219 | -0.0101 | CFL | AllSpc | 1040 | 0.183 | 1040 | 0.183 | 1.05 | 1.2 | -0.00971
CFLAllSpcPGEAsmExCZ05 | Com-Iltg-dWatt-CFL_OSspc | PGE | Asm | Ex | CZ05 | 1.04 | 0.000183 | 0 | 1.09 | 0.000219 | -0.0101 | 1.04 | 0.000183 | 0 | 1.09 | 0.000219 | -0.0101 | CFL | AllSpc | 1040 | 0.183 | 1040 | 0.183 | 1.05 | 1.2 | -0.00971
CFLAllSpcSDGAsmExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SDG | Asm | Ex | CZ06 | 1.04 | 0.000183 | 0 | 1.14 | 0.000227 | -0.00543 | 1.04 | 0.000183 | 0 | 1.14 | 0.000227 | -0.00543 | CFL | AllSpc | 1040 | 0.183 | 1040 | 0.183 | 1.1 | 1.24 | -0.00522
CFLAllSpcSCGAsmExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCG | Asm | Ex | CZ06 | 1.04 | 0.000183 | 0 | 1.14 | 0.000227 | -0.00543 | 1.04 | 0.000183 | 0 | 1.14 | 0.000227 | -0.00543 | CFL | AllSpc | 1040 | 0.183 | 1040 | 0.183 | 1.1 | 1.24 | -0.00522
CFLAllSpcSCEAsmExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCE | Asm | Ex | CZ06 | 1.04 | 0.000183 | 0 | 1.14 | 0.000227 | -0.00543 | 1.04 | 0.000183 | 0 | 1.14 | 0.000227 | -0.00543 | CFL | AllSpc | 1040 | 0.183 | 1040 | 0.183 | 1.1 | 1.24 | -0.00522
CFLAllSpcSDGAsmExCZ07 | Com-Iltg-dWatt-CFL_OSspc | SDG | Asm | Ex | CZ07 | 1.04 | 0.000183 | 0 | 1.14 | 0.000227 | -0.00498 | 1.04 | 0.000183 | 0 | 1.14 | 0.000227 | -0.00498 | CFL | AllSpc | 1040 | 0.183 | 1040 | 0.183 | 1.1 | 1.24 | -0.00479
CFLAllSpcSCGAsmExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCG | Asm | Ex | CZ08 | 1.04 | 0.000183 | 0 | 1.15 | 0.000221 | -0.00474 | 1.04 | 0.000183 | 0 | 1.15 | 0.000221 | -0.00474 | CFL | AllSpc | 1040 | 0.183 | 1040 | 0.183 | 1.11 | 1.21 | -0.00456
CFLAllSpcSCEAsmExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCE | Asm | Ex | CZ08 | 1.04 | 0.000183 | 0 | 1.15 | 0.000221 | -0.00474 | 1.04 | 0.000183 | 0 | 1.15 | 0.000221 | -0.00474 | CFL | AllSpc | 1040 | 0.183 | 1040 | 0.183 | 1.11 | 1.21 | -0.00456
CFLAllSpcSDGAsmExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SDG | Asm | Ex | CZ08 | 1.04 | 0.000183 | 0 | 1.15 | 0.000221 | -0.00474 | 1.04 | 0.000183 | 0 | 1.15 | 0.000221 | -0.00474 | CFL | AllSpc | 1040 | 0.183 | 1040 | 0.183 | 1.11 | 1.21 | -0.00456
CFLAllSpcSCEAsmExCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCE | Asm | Ex | CZ09 | 1.04 | 0.000183 | 0 | 1.16 | 0.000227 | -0.00519 | 1.04 | 0.000183 | 0 | 1.16 | 0.000227 | -0.00519 | CFL | AllSpc | 1040 | 0.183 | 1040 | 0.183 | 1.12 | 1.24 | -0.00499
CFLAllSpcSCGAsmExCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCG | Asm | Ex | CZ09 | 1.04 | 0.000183 | 0 | 1.16 | 0.000227 | -0.00519 | 1.04 | 0.000183 | 0 | 1.16 | 0.000227 | -0.00519 | CFL | AllSpc | 1040 | 0.183 | 1040 | 0.183 | 1.12 | 1.24 | -0.00499
CFLAllSpcSCGAsmExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCG | Asm | Ex | CZ10 | 1.04 | 0.000183 | 0 | 1.14 | 0.000222 | -0.00603 | 1.04 | 0.000183 | 0 | 1.14 | 0.000222 | -0.00603 | CFL | AllSpc | 1040 | 0.183 | 1040 | 0.183 | 1.1 | 1.21 | -0.0058
CFLAllSpcSCEAsmExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCE | Asm | Ex | CZ10 | 1.04 | 0.000183 | 0 | 1.14 | 0.000222 | -0.00603 | 1.04 | 0.000183 | 0 | 1.14 | 0.000222 | -0.00603 | CFL | AllSpc | 1040 | 0.183 | 1040 | 0.183 | 1.1 | 1.21 | -0.0058
CFLAllSpcSDGAsmExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SDG | Asm | Ex | CZ10 | 1.04 | 0.000183 | 0 | 1.14 | 0.000222 | -0.00603 | 1.04 | 0.000183 | 0 | 1.14 | 0.000222 | -0.00603 | CFL | AllSpc | 1040 | 0.183 | 1040 | 0.183 | 1.1 | 1.21 | -0.0058
CFLAllSpcPGEAsmExCZ11 | Com-Iltg-dWatt-CFL_OSspc | PGE | Asm | Ex | CZ11 | 1.04 | 0.000183 | 0 | 1.1 | 0.000214 | -0.00921 | 1.04 | 0.000183 | 0 | 1.1 | 0.000214 | -0.00921 | CFL | AllSpc | 1040 | 0.183 | 1040 | 0.183 | 1.06 | 1.17 | -0.00886
CFLAllSpcPGEAsmExCZ12 | Com-Iltg-dWatt-CFL_OSspc | PGE | Asm | Ex | CZ12 | 1.04 | 0.000183 | 0 | 1.08 | 0.000216 | -0.00971 | 1.04 | 0.000183 | 0 | 1.08 | 0.000216 | -0.00971 | CFL | AllSpc | 1040 | 0.183 | 1040 | 0.183 | 1.04 | 1.18 | -0.00934
CFLAllSpcSCGAsmExCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCG | Asm | Ex | CZ13 | 1.04 | 0.000183 | 0 | 1.12 | 0.000222 | -0.00894 | 1.04 | 0.000183 | 0 | 1.12 | 0.000222 | -0.00894 | CFL | AllSpc | 1040 | 0.183 | 1040 | 0.183 | 1.08 | 1.21 | -0.0086
CFLAllSpcSCEAsmExCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCE | Asm | Ex | CZ13 | 1.04 | 0.000183 | 0 | 1.12 | 0.000222 | -0.00894 | 1.04 | 0.000183 | 0 | 1.12 | 0.000222 | -0.00894 | CFL | AllSpc | 1040 | 0.183 | 1040 | 0.183 | 1.08 | 1.21 | -0.0086
CFLAllSpcPGEAsmExCZ13 | Com-Iltg-dWatt-CFL_OSspc | PGE | Asm | Ex | CZ13 | 1.04 | 0.000183 | 0 | 1.12 | 0.000222 | -0.00894 | 1.04 | 0.000183 | 0 | 1.12 | 0.000222 | -0.00894 | CFL | AllSpc | 1040 | 0.183 | 1040 | 0.183 | 1.08 | 1.21 | -0.0086
CFLAllSpcSCGAsmExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCG | Asm | Ex | CZ14 | 1.04 | 0.000183 | 0 | 1.11 | 0.000208 | -0.00947 | 1.04 | 0.000183 | 0 | 1.11 | 0.000208 | -0.00947 | CFL | AllSpc | 1040 | 0.183 | 1040 | 0.183 | 1.07 | 1.14 | -0.00911
CFLAllSpcSDGAsmExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SDG | Asm | Ex | CZ14 | 1.04 | 0.000183 | 0 | 1.11 | 0.000208 | -0.00947 | 1.04 | 0.000183 | 0 | 1.11 | 0.000208 | -0.00947 | CFL | AllSpc | 1040 | 0.183 | 1040 | 0.183 | 1.07 | 1.14 | -0.00911
CFLAllSpcSCEAsmExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCE | Asm | Ex | CZ14 | 1.04 | 0.000183 | 0 | 1.11 | 0.000208 | -0.00947 | 1.04 | 0.000183 | 0 | 1.11 | 0.000208 | -0.00947 | CFL | AllSpc | 1040 | 0.183 | 1040 | 0.183 | 1.07 | 1.14 | -0.00911
CFLAllSpcSCGAsmExCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCG | Asm | Ex | CZ15 | 1.04 | 0.000183 | 0 | 1.3 | 0.000216 | -0.00265 | 1.04 | 0.000183 | 0 | 1.3 | 0.000216 | -0.00265 | CFL | AllSpc | 1040 | 0.183 | 1040 | 0.183 | 1.25 | 1.18 | -0.00255
CFLAllSpcSDGAsmExCZ15 | Com-Iltg-dWatt-CFL_OSspc | SDG | Asm | Ex | CZ15 | 1.04 | 0.000183 | 0 | 1.3 | 0.000216 | -0.00265 | 1.04 | 0.000183 | 0 | 1.3 | 0.000216 | -0.00265 | CFL | AllSpc | 1040 | 0.183 | 1040 | 0.183 | 1.25 | 1.18 | -0.00255
CFLAllSpcSCEAsmExCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCE | Asm | Ex | CZ15 | 1.04 | 0.000183 | 0 | 1.3 | 0.000216 | -0.00265 | 1.04 | 0.000183 | 0 | 1.3 | 0.000216 | -0.00265 | CFL | AllSpc | 1040 | 0.183 | 1040 | 0.183 | 1.25 | 1.18 | -0.00255
CFLAllSpcSCEAsmExCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCE | Asm | Ex | CZ16 | 1.04 | 0.000183 | 0 | 1.03 | 0.000218 | -0.0139 | 1.04 | 0.000183 | 0 | 1.03 | 0.000218 | -0.0139 | CFL | AllSpc | 1040 | 0.183 | 1040 | 0.183 | 0.99 | 1.19 | -0.0134
CFLAllSpcPGEAsmExCZ16 | Com-Iltg-dWatt-CFL_OSspc | PGE | Asm | Ex | CZ16 | 1.04 | 0.000183 | 0 | 1.03 | 0.000218 | -0.0139 | 1.04 | 0.000183 | 0 | 1.03 | 0.000218 | -0.0139 | CFL | AllSpc | 1040 | 0.183 | 1040 | 0.183 | 0.99 | 1.19 | -0.0134
CFLAllSpcSCGAsmExCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCG | Asm | Ex | CZ16 | 1.04 | 0.000183 | 0 | 1.03 | 0.000218 | -0.0139 | 1.04 | 0.000183 | 0 | 1.03 | 0.000218 | -0.0139 | CFL | AllSpc | 1040 | 0.183 | 1040 | 0.183 | 0.99 | 1.19 | -0.0134
CFLAllSpcSCGAsmExIOU | Com-Iltg-dWatt-CFL_OSspc | SCG | Asm | Ex | IOU | 1.04 | 0.000183 | 0 | 1.15 | 0.000223 | -0.00546 | 1.04 | 0.000183 | 0 | 1.15 | 0.000223 | -0.00546 | CFL | AllSpc | 1040 | 0.183 | 1040 | 0.183 | 1.11 | 1.22 | -0.00525
CFLAllSpcSDGAsmExIOU | Com-Iltg-dWatt-CFL_OSspc | SDG | Asm | Ex | IOU | 1.04 | 0.000183 | 0 | 1.14 | 0.000225 | -0.00534 | 1.04 | 0.000183 | 0 | 1.14 | 0.000225 | -0.00534 | CFL | AllSpc | 1040 | 0.183 | 1040 | 0.183 | 1.1 | 1.23 | -0.00513
CFLAllSpcSCEAsmExIOU | Com-Iltg-dWatt-CFL_OSspc | SCE | Asm | Ex | IOU | 1.04 | 0.000183 | 0 | 1.15 | 0.000223 | -0.00554 | 1.04 | 0.000183 | 0 | 1.15 | 0.000223 | -0.00554 | CFL | AllSpc | 1040 | 0.183 | 1040 | 0.183 | 1.11 | 1.22 | -0.00533
CFLAllSpcPGEAsmExIOU | Com-Iltg-dWatt-CFL_OSspc | PGE | Asm | Ex | IOU | 1.04 | 0.000183 | 0 | 1.08 | 0.000216 | -0.0103 | 1.04 | 0.000183 | 0 | 1.08 | 0.000216 | -0.0103 | CFL | AllSpc | 1040 | 0.183 | 1040 | 0.183 | 1.04 | 1.18 | -0.0099
CFLAllSpcPGEAsmNewCZ01 | Com-Iltg-dWatt-CFL_OSspc | PGE | Asm | New | CZ01 | 1.04 | 0.000183 | 0 | 0.995 | 0.000212 | -0.0184 | 1.04 | 0.000183 | 0 | 0.995 | 0.000212 | -0.0184 | CFL | AllSpc | 1040 | 0.183 | 1040 | 0.183 | 0.957 | 1.16 | -0.0177
CFLAllSpcPGEAsmNewCZ02 | Com-Iltg-dWatt-CFL_OSspc | PGE | Asm | New | CZ02 | 1.04 | 0.000183 | 0 | 1.06 | 0.000214 | -0.0116 | 1.04 | 0.000183 | 0 | 1.06 | 0.000214 | -0.0116 | CFL | AllSpc | 1040 | 0.183 | 1040 | 0.183 | 1.02 | 1.17 | -0.0112
CFLAllSpcPGEAsmNewCZ03 | Com-Iltg-dWatt-CFL_OSspc | PGE | Asm | New | CZ03 | 1.04 | 0.000183 | 0 | 1.05 | 0.000211 | -0.0121 | 1.04 | 0.000183 | 0 | 1.05 | 0.000211 | -0.0121 | CFL | AllSpc | 1040 | 0.183 | 1040 | 0.183 | 1.01 | 1.15 | -0.0116
CFLAllSpcPGEAsmNewCZ04 | Com-Iltg-dWatt-CFL_OSspc | PGE | Asm | New | CZ04 | 1.04 | 0.000183 | 0 | 1.08 | 0.000214 | -0.00952 | 1.04 | 0.000183 | 0 | 1.08 | 0.000214 | -0.00952 | CFL | AllSpc | 1040 | 0.183 | 1040 | 0.183 | 1.04 | 1.17 | -0.00915
CFLAllSpcSCEAsmNewCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCE | Asm | New | CZ05 | 1.04 | 0.000183 | 0 | 1.08 | 0.000216 | -0.0103 | 1.04 | 0.000183 | 0 | 1.08 | 0.000216 | -0.0103 | CFL | AllSpc | 1040 | 0.183 | 1040 | 0.183 | 1.04 | 1.18 | -0.0099
CFLAllSpcPGEAsmNewCZ05 | Com-Iltg-dWatt-CFL_OSspc | PGE | Asm | New | CZ05 | 1.04 | 0.000183 | 0 | 1.06 | 0.000209 | -0.0105 | 1.04 | 0.000183 | 0 | 1.06 | 0.000209 | -0.0105 | CFL | AllSpc | 1040 | 0.183 | 1040 | 0.183 | 1.02 | 1.14 | -0.0101
CFLAllSpcSDGAsmNewCZ06 | Com-Iltg-dWatt-CFL_OSspc | SDG | Asm | New | CZ06 | 1.04 | 0.000183 | 0 | 1.12 | 0.000226 | -0.00702 | 1.04 | 0.000183 | 0 | 1.12 | 0.000226 | -0.00702 | CFL | AllSpc | 1040 | 0.183 | 1040 | 0.183 | 1.08 | 1.23 | -0.00675
CFLAllSpcSCEAsmNewCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCE | Asm | New | CZ06 | 1.04 | 0.000183 | 0 | 1.12 | 0.000224 | -0.00654 | 1.04 | 0.000183 | 0 | 1.12 | 0.000224 | -0.00654 | CFL | AllSpc | 1040 | 0.183 | 1040 | 0.183 | 1.08 | 1.22 | -0.00629
CFLAllSpcSDGAsmNewCZ07 | Com-Iltg-dWatt-CFL_OSspc | SDG | Asm | New | CZ07 | 1.04 | 0.000183 | 0 | 1.13 | 0.000225 | -0.00616 | 1.04 | 0.000183 | 0 | 1.13 | 0.000225 | -0.00616 | CFL | AllSpc | 1040 | 0.183 | 1040 | 0.183 | 1.09 | 1.23 | -0.00592
CFLAllSpcSCEAsmNewCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCE | Asm | New | CZ08 | 1.04 | 0.000183 | 0 | 1.13 | 0.000221 | -0.00506 | 1.04 | 0.000183 | 0 | 1.13 | 0.000221 | -0.00506 | CFL | AllSpc | 1040 | 0.183 | 1040 | 0.183 | 1.09 | 1.21 | -0.00487
CFLAllSpcSDGAsmNewCZ08 | Com-Iltg-dWatt-CFL_OSspc | SDG | Asm | New | CZ08 | 1.04 | 0.000183 | 0 | 1.14 | 0.000223 | -0.00544 | 1.04 | 0.000183 | 0 | 1.14 | 0.000223 | -0.00544 | CFL | AllSpc | 1040 | 0.183 | 1040 | 0.183 | 1.1 | 1.22 | -0.00523
CFLAllSpcSCEAsmNewCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCE | Asm | New | CZ09 | 1.04 | 0.000183 | 0 | 1.13 | 0.000234 | -0.00608 | 1.04 | 0.000183 | 0 | 1.13 | 0.000234 | -0.00608 | CFL | AllSpc | 1040 | 0.183 | 1040 | 0.183 | 1.09 | 1.28 | -0.00585
CFLAllSpcSCEAsmNewCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCE | Asm | New | CZ10 | 1.04 | 0.000183 | 0 | 1.13 | 0.000226 | -0.00601 | 1.04 | 0.000183 | 0 | 1.13 | 0.000226 | -0.00601 | CFL | AllSpc | 1040 | 0.183 | 1040 | 0.183 | 1.09 | 1.23 | -0.00578
CFLAllSpcSDGAsmNewCZ10 | Com-Iltg-dWatt-CFL_OSspc | SDG | Asm | New | CZ10 | 1.04 | 0.000183 | 0 | 1.13 | 0.000228 | -0.00647 | 1.04 | 0.000183 | 0 | 1.13 | 0.000228 | -0.00647 | CFL | AllSpc | 1040 | 0.183 | 1040 | 0.183 | 1.09 | 1.25 | -0.00622
CFLAllSpcPGEAsmNewCZ11 | Com-Iltg-dWatt-CFL_OSspc | PGE | Asm | New | CZ11 | 1.04 | 0.000183 | 0 | 1.08 | 0.000218 | -0.01 | 1.04 | 0.000183 | 0 | 1.08 | 0.000218 | -0.01 | CFL | AllSpc | 1040 | 0.183 | 1040 | 0.183 | 1.04 | 1.19 | -0.00962
CFLAllSpcPGEAsmNewCZ12 | Com-Iltg-dWatt-CFL_OSspc | PGE | Asm | New | CZ12 | 1.04 | 0.000183 | 0 | 1.07 | 0.000217 | -0.0106 | 1.04 | 0.000183 | 0 | 1.07 | 0.000217 | -0.0106 | CFL | AllSpc | 1040 | 0.183 | 1040 | 0.183 | 1.03 | 1.19 | -0.0102
CFLAllSpcPGEAsmNewCZ13 | Com-Iltg-dWatt-CFL_OSspc | PGE | Asm | New | CZ13 | 1.04 | 0.000183 | 0 | 1.09 | 0.000218 | -0.00964 | 1.04 | 0.000183 | 0 | 1.09 | 0.000218 | -0.00964 | CFL | AllSpc | 1040 | 0.183 | 1040 | 0.183 | 1.05 | 1.19 | -0.00927
CFLAllSpcSCEAsmNewCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCE | Asm | New | CZ13 | 1.04 | 0.000183 | 0 | 1.11 | 0.000228 | -0.00951 | 1.04 | 0.000183 | 0 | 1.11 | 0.000228 | -0.00951 | CFL | AllSpc | 1040 | 0.183 | 1040 | 0.183 | 1.07 | 1.25 | -0.00914
CFLAllSpcSCEAsmNewCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCE | Asm | New | CZ14 | 1.04 | 0.000183 | 0 | 1.1 | 0.000218 | -0.00934 | 1.04 | 0.000183 | 0 | 1.1 | 0.000218 | -0.00934 | CFL | AllSpc | 1040 | 0.183 | 1040 | 0.183 | 1.06 | 1.19 | -0.00898
CFLAllSpcSDGAsmNewCZ14 | Com-Iltg-dWatt-CFL_OSspc | SDG | Asm | New | CZ14 | 1.04 | 0.000183 | 0 | 1.1 | 0.000219 | -0.01 | 1.04 | 0.000183 | 0 | 1.1 | 0.000219 | -0.01 | CFL | AllSpc | 1040 | 0.183 | 1040 | 0.183 | 1.06 | 1.2 | -0.00962
CFLAllSpcSDGAsmNewCZ15 | Com-Iltg-dWatt-CFL_OSspc | SDG | Asm | New | CZ15 | 1.04 | 0.000183 | 0 | 1.25 | 0.000229 | -0.00311 | 1.04 | 0.000183 | 0 | 1.25 | 0.000229 | -0.00311 | CFL | AllSpc | 1040 | 0.183 | 1040 | 0.183 | 1.2 | 1.25 | -0.00299
CFLAllSpcSCEAsmNewCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCE | Asm | New | CZ15 | 1.04 | 0.000183 | 0 | 1.24 | 0.000228 | -0.00289 | 1.04 | 0.000183 | 0 | 1.24 | 0.000228 | -0.00289 | CFL | AllSpc | 1040 | 0.183 | 1040 | 0.183 | 1.19 | 1.25 | -0.00278
CFLAllSpcSCEAsmNewCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCE | Asm | New | CZ16 | 1.04 | 0.000183 | 0 | 1.03 | 0.000218 | -0.0138 | 1.04 | 0.000183 | 0 | 1.03 | 0.000218 | -0.0138 | CFL | AllSpc | 1040 | 0.183 | 1040 | 0.183 | 0.99 | 1.19 | -0.0133
CFLAllSpcPGEAsmNewCZ16 | Com-Iltg-dWatt-CFL_OSspc | PGE | Asm | New | CZ16 | 1.04 | 0.000183 | 0 | 1.02 | 0.00021 | -0.0139 | 1.04 | 0.000183 | 0 | 1.02 | 0.00021 | -0.0139 | CFL | AllSpc | 1040 | 0.183 | 1040 | 0.183 | 0.981 | 1.15 | -0.0134
CFLAllSpcPGEAsmNewIOU | Com-Iltg-dWatt-CFL_OSspc | PGE | Asm | New | IOU | 1.04 | 0.000183 | 0 | 1.1 | 0.000226 | -0.00988 | 1.04 | 0.000183 | 0 | 1.1 | 0.000226 | -0.00988 | CFL | AllSpc | 1040 | 0.183 | 1040 | 0.183 | 1.06 | 1.23 | -0.0095
CFLAllSpcSCGAsmNewIOU | Com-Iltg-dWatt-CFL_OSspc | SCG | Asm | New | IOU | 1.04 | 0.000183 | 0 | 1.14 | 0.000226 | -0.00606 | 1.04 | 0.000183 | 0 | 1.14 | 0.000226 | -0.00606 | CFL | AllSpc | 1040 | 0.183 | 1040 | 0.183 | 1.1 | 1.23 | -0.00583
CFLAllSpcSDGAsmNewIOU | Com-Iltg-dWatt-CFL_OSspc | SDG | Asm | New | IOU | 1.04 | 0.000183 | 0 | 1.13 | 0.000226 | -0.00629 | 1.04 | 0.000183 | 0 | 1.13 | 0.000226 | -0.00629 | CFL | AllSpc | 1040 | 0.183 | 1040 | 0.183 | 1.09 | 1.23 | -0.00605
CFLAllSpcSCEAsmNewIOU | Com-Iltg-dWatt-CFL_OSspc | SCE | Asm | New | IOU | 1.04 | 0.000183 | 0 | 1.14 | 0.000226 | -0.00607 | 1.04 | 0.000183 | 0 | 1.14 | 0.000226 | -0.00607 | CFL | AllSpc | 1040 | 0.183 | 1040 | 0.183 | 1.1 | 1.23 | -0.00584
CFLAllSpcPGEComExCZ01 | Com-Iltg-dWatt-CFL_OSspc | PGE | Com | Ex | CZ01 | 2 | 0.000434 | 0 | 1.97 | 0.000505 | -0.0247 | 2 | 0.000434 | 0 | 1.97 | 0.000505 | -0.0247 | CFL | AllSpc | 2000 | 0.434 | 2000 | 0.434 | 0.985 | 1.16 | -0.0124
CFLAllSpcPGEComExCZ02 | Com-Iltg-dWatt-CFL_OSspc | PGE | Com | Ex | CZ02 | 2.08 | 0.000395 | 0 | 2.16 | 0.000486 | -0.0164 | 2.08 | 0.000395 | 0 | 2.16 | 0.000486 | -0.0164 | CFL | AllSpc | 2080 | 0.395 | 2080 | 0.395 | 1.04 | 1.23 | -0.00788
CFLAllSpcPGEComExCZ03 | Com-Iltg-dWatt-CFL_OSspc | PGE | Com | Ex | CZ03 | 1.95 | 0.000385 | 0 | 2.05 | 0.000474 | -0.0142 | 1.95 | 0.000385 | 0 | 2.05 | 0.000474 | -0.0142 | CFL | AllSpc | 1950 | 0.385 | 1950 | 0.385 | 1.05 | 1.23 | -0.00728
CFLAllSpcPGEComExCZ04 | Com-Iltg-dWatt-CFL_OSspc | PGE | Com | Ex | CZ04 | 1.92 | 0.000416 | 0 | 2.05 | 0.000512 | -0.0116 | 1.92 | 0.000416 | 0 | 2.05 | 0.000512 | -0.0116 | CFL | AllSpc | 1920 | 0.416 | 1920 | 0.416 | 1.07 | 1.23 | -0.00604
CFLAllSpcSCGComExCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCG | Com | Ex | CZ05 | 2.58 | 0.000503 | 0 | 2.75 | 0.000626 | -0.0222 | 2.58 | 0.000503 | 0 | 2.75 | 0.000626 | -0.0222 | CFL | AllSpc | 2580 | 0.503 | 2580 | 0.503 | 1.07 | 1.24 | -0.0086
CFLAllSpcSCEComExCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCE | Com | Ex | CZ05 | 2.58 | 0.000503 | 0 | 2.75 | 0.000626 | -0.0222 | 2.58 | 0.000503 | 0 | 2.75 | 0.000626 | -0.0222 | CFL | AllSpc | 2580 | 0.503 | 2580 | 0.503 | 1.07 | 1.24 | -0.0086
CFLAllSpcPGEComExCZ05 | Com-Iltg-dWatt-CFL_OSspc | PGE | Com | Ex | CZ05 | 2.01 | 0.000425 | 0 | 2.16 | 0.00053 | -0.0155 | 2.01 | 0.000425 | 0 | 2.16 | 0.00053 | -0.0155 | CFL | AllSpc | 2010 | 0.425 | 2010 | 0.425 | 1.07 | 1.25 | -0.00771
CFLAllSpcSCGComExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCG | Com | Ex | CZ06 | 2.01 | 0.000431 | 0 | 2.24 | 0.000538 | -0.00817 | 2.01 | 0.000431 | 0 | 2.24 | 0.000538 | -0.00817 | CFL | AllSpc | 2010 | 0.431 | 2010 | 0.431 | 1.11 | 1.25 | -0.00406
CFLAllSpcSCEComExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCE | Com | Ex | CZ06 | 2.02 | 0.000433 | 0 | 2.25 | 0.000539 | -0.0082 | 2.02 | 0.000433 | 0 | 2.25 | 0.000539 | -0.0082 | CFL | AllSpc | 2020 | 0.433 | 2020 | 0.433 | 1.11 | 1.24 | -0.00406
CFLAllSpcSDGComExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SDG | Com | Ex | CZ06 | 2.11 | 0.000435 | 0 | 2.29 | 0.000541 | -0.0115 | 2.11 | 0.000435 | 0 | 2.29 | 0.000541 | -0.0115 | CFL | AllSpc | 2110 | 0.435 | 2110 | 0.435 | 1.09 | 1.24 | -0.00545
CFLAllSpcSDGComExCZ07 | Com-Iltg-dWatt-CFL_OSspc | SDG | Com | Ex | CZ07 | 1.99 | 0.000423 | 0 | 2.2 | 0.000523 | -0.00785 | 1.99 | 0.000423 | 0 | 2.2 | 0.000523 | -0.00785 | CFL | AllSpc | 1990 | 0.423 | 1990 | 0.423 | 1.11 | 1.24 | -0.00394
CFLAllSpcSDGComExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SDG | Com | Ex | CZ08 | 2.18 | 0.000494 | 0 | 2.43 | 0.00062 | -0.00853 | 2.18 | 0.000494 | 0 | 2.43 | 0.00062 | -0.00853 | CFL | AllSpc | 2180 | 0.494 | 2180 | 0.494 | 1.11 | 1.26 | -0.00391
CFLAllSpcSCGComExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCG | Com | Ex | CZ08 | 1.96 | 0.00042 | 0 | 2.18 | 0.000525 | -0.00728 | 1.96 | 0.00042 | 0 | 2.18 | 0.000525 | -0.00728 | CFL | AllSpc | 1960 | 0.42 | 1960 | 0.42 | 1.11 | 1.25 | -0.00371
CFLAllSpcSCEComExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCE | Com | Ex | CZ08 | 1.96 | 0.00042 | 0 | 2.18 | 0.000524 | -0.00729 | 1.96 | 0.00042 | 0 | 2.18 | 0.000524 | -0.00729 | CFL | AllSpc | 1960 | 0.42 | 1960 | 0.42 | 1.11 | 1.25 | -0.00372
CFLAllSpcSCEComExCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCE | Com | Ex | CZ09 | 1.98 | 0.000427 | 0 | 2.22 | 0.00055 | -0.00887 | 1.98 | 0.000427 | 0 | 2.22 | 0.00055 | -0.00887 | CFL | AllSpc | 1980 | 0.427 | 1980 | 0.427 | 1.12 | 1.29 | -0.00448
CFLAllSpcSCGComExCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCG | Com | Ex | CZ09 | 1.98 | 0.000426 | 0 | 2.23 | 0.000549 | -0.00904 | 1.98 | 0.000426 | 0 | 2.23 | 0.000549 | -0.00904 | CFL | AllSpc | 1980 | 0.426 | 1980 | 0.426 | 1.13 | 1.29 | -0.00457
CFLAllSpcSDGComExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SDG | Com | Ex | CZ10 | 1.99 | 0.000436 | 0 | 2.19 | 0.000554 | -0.0091 | 1.99 | 0.000436 | 0 | 2.19 | 0.000554 | -0.0091 | CFL | AllSpc | 1990 | 0.436 | 1990 | 0.436 | 1.1 | 1.27 | -0.00457
CFLAllSpcSCGComExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCG | Com | Ex | CZ10 | 2.01 | 0.000432 | 0 | 2.21 | 0.000544 | -0.00879 | 2.01 | 0.000432 | 0 | 2.21 | 0.000544 | -0.00879 | CFL | AllSpc | 2010 | 0.432 | 2010 | 0.432 | 1.1 | 1.26 | -0.00437
CFLAllSpcSCEComExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCE | Com | Ex | CZ10 | 2.01 | 0.000432 | 0 | 2.21 | 0.000544 | -0.00879 | 2.01 | 0.000432 | 0 | 2.21 | 0.000544 | -0.00879 | CFL | AllSpc | 2010 | 0.432 | 2010 | 0.432 | 1.1 | 1.26 | -0.00437
CFLAllSpcPGEComExCZ11 | Com-Iltg-dWatt-CFL_OSspc | PGE | Com | Ex | CZ11 | 2.08 | 0.000393 | 0 | 2.21 | 0.000484 | -0.0148 | 2.08 | 0.000393 | 0 | 2.21 | 0.000484 | -0.0148 | CFL | AllSpc | 2080 | 0.393 | 2080 | 0.393 | 1.06 | 1.23 | -0.00712
CFLAllSpcPGEComExCZ12 | Com-Iltg-dWatt-CFL_OSspc | PGE | Com | Ex | CZ12 | 2.05 | 0.0004 | 0 | 2.17 | 0.000493 | -0.0142 | 2.05 | 0.0004 | 0 | 2.17 | 0.000493 | -0.0142 | CFL | AllSpc | 2050 | 0.4 | 2050 | 0.4 | 1.06 | 1.23 | -0.00693
CFLAllSpcSCEComExCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCE | Com | Ex | CZ13 | 2.13 | 0.0004 | 0 | 2.41 | 0.000506 | -0.0131 | 2.13 | 0.0004 | 0 | 2.41 | 0.000506 | -0.0131 | CFL | AllSpc | 2130 | 0.4 | 2130 | 0.4 | 1.13 | 1.27 | -0.00615
CFLAllSpcPGEComExCZ13 | Com-Iltg-dWatt-CFL_OSspc | PGE | Com | Ex | CZ13 | 2.09 | 0.000394 | 0 | 2.32 | 0.000497 | -0.0132 | 2.09 | 0.000394 | 0 | 2.32 | 0.000497 | -0.0132 | CFL | AllSpc | 2090 | 0.394 | 2090 | 0.394 | 1.11 | 1.26 | -0.00632
CFLAllSpcSCGComExCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCG | Com | Ex | CZ13 | 2.13 | 0.0004 | 0 | 2.41 | 0.000506 | -0.0131 | 2.13 | 0.0004 | 0 | 2.41 | 0.000506 | -0.0131 | CFL | AllSpc | 2130 | 0.4 | 2130 | 0.4 | 1.13 | 1.27 | -0.00615
CFLAllSpcSDGComExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SDG | Com | Ex | CZ14 | 1.67 | 0.000358 | 0 | 1.82 | 0.000451 | -0.00992 | 1.67 | 0.000358 | 0 | 1.82 | 0.000451 | -0.00992 | CFL | AllSpc | 1670 | 0.358 | 1670 | 0.358 | 1.09 | 1.26 | -0.00594
CFLAllSpcSCEComExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCE | Com | Ex | CZ14 | 2.09 | 0.00046 | 0 | 2.27 | 0.000584 | -0.0145 | 2.09 | 0.00046 | 0 | 2.27 | 0.000584 | -0.0145 | CFL | AllSpc | 2090 | 0.46 | 2090 | 0.46 | 1.09 | 1.27 | -0.00694
CFLAllSpcSCGComExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCG | Com | Ex | CZ14 | 2.09 | 0.00046 | 0 | 2.27 | 0.000584 | -0.0145 | 2.09 | 0.00046 | 0 | 2.27 | 0.000584 | -0.0145 | CFL | AllSpc | 2090 | 0.46 | 2090 | 0.46 | 1.09 | 1.27 | -0.00694
CFLAllSpcSCGComExCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCG | Com | Ex | CZ15 | 1.89 | 0.000395 | 0 | 2.24 | 0.000502 | -0.00365 | 1.89 | 0.000395 | 0 | 2.24 | 0.000502 | -0.00365 | CFL | AllSpc | 1890 | 0.395 | 1890 | 0.395 | 1.19 | 1.27 | -0.00193
CFLAllSpcSCEComExCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCE | Com | Ex | CZ15 | 1.89 | 0.000395 | 0 | 2.24 | 0.000502 | -0.00365 | 1.89 | 0.000395 | 0 | 2.24 | 0.000502 | -0.00365 | CFL | AllSpc | 1890 | 0.395 | 1890 | 0.395 | 1.19 | 1.27 | -0.00193
CFLAllSpcSDGComExCZ15 | Com-Iltg-dWatt-CFL_OSspc | SDG | Com | Ex | CZ15 | 1.51 | 0.000283 | 0 | 1.78 | 0.000359 | -0.00258 | 1.51 | 0.000283 | 0 | 1.78 | 0.000359 | -0.00258 | CFL | AllSpc | 1510 | 0.283 | 1510 | 0.283 | 1.18 | 1.27 | -0.00171
CFLAllSpcSCEComExCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCE | Com | Ex | CZ16 | 1.92 | 0.000351 | 0 | 1.93 | 0.000429 | -0.0224 | 1.92 | 0.000351 | 0 | 1.93 | 0.000429 | -0.0224 | CFL | AllSpc | 1920 | 0.351 | 1920 | 0.351 | 1.01 | 1.22 | -0.0117
CFLAllSpcPGEComExCZ16 | Com-Iltg-dWatt-CFL_OSspc | PGE | Com | Ex | CZ16 | 1.91 | 0.000345 | 0 | 1.89 | 0.00042 | -0.0213 | 1.91 | 0.000345 | 0 | 1.89 | 0.00042 | -0.0213 | CFL | AllSpc | 1910 | 0.345 | 1910 | 0.345 | 0.99 | 1.22 | -0.0112
CFLAllSpcSCGComExCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCG | Com | Ex | CZ16 | 1.92 | 0.000351 | 0 | 1.93 | 0.000429 | -0.0224 | 1.92 | 0.000351 | 0 | 1.93 | 0.000429 | -0.0224 | CFL | AllSpc | 1920 | 0.351 | 1920 | 0.351 | 1.01 | 1.22 | -0.0117
CFLAllSpcSCEComExIOU | Com-Iltg-dWatt-CFL_OSspc | SCE | Com | Ex | IOU | 1.99 | 0.000425 | 0 | 2.22 | 0.000534 | -0.00855 | 1.99 | 0.000425 | 0 | 2.22 | 0.000534 | -0.00855 | CFL | AllSpc | 1990 | 0.425 | 1990 | 0.425 | 1.12 | 1.26 | -0.0043
CFLAllSpcPGEComExIOU | Com-Iltg-dWatt-CFL_OSspc | PGE | Com | Ex | IOU | 2 | 0.000396 | 0 | 2.13 | 0.000489 | -0.014 | 2 | 0.000396 | 0 | 2.13 | 0.000489 | -0.014 | CFL | AllSpc | 2000 | 0.396 | 2000 | 0.396 | 1.07 | 1.23 | -0.007
CFLAllSpcSCGComExIOU | Com-Iltg-dWatt-CFL_OSspc | SCG | Com | Ex | IOU | 1.99 | 0.000425 | 0 | 2.22 | 0.000536 | -0.00858 | 1.99 | 0.000425 | 0 | 2.22 | 0.000536 | -0.00858 | CFL | AllSpc | 1990 | 0.425 | 1990 | 0.425 | 1.12 | 1.26 | -0.00431
CFLAllSpcSDGComExIOU | Com-Iltg-dWatt-CFL_OSspc | SDG | Com | Ex | IOU | 2 | 0.000428 | 0 | 2.2 | 0.000533 | -0.00827 | 2 | 0.000428 | 0 | 2.2 | 0.000533 | -0.00827 | CFL | AllSpc | 2000 | 0.428 | 2000 | 0.428 | 1.1 | 1.25 | -0.00414
CFLAllSpcPGEComNewCZ05 | Com-Iltg-dWatt-CFL_OSspc | PGE | Com | New | CZ05 | 2 | 0.000418 | 0 | 2.06 | 0.000509 | -0.0154 | 2 | 0.000418 | 0 | 2.06 | 0.000509 | -0.0154 | CFL | AllSpc | 2000 | 0.418 | 2000 | 0.418 | 1.03 | 1.22 | -0.0077
CFLAllSpcSCEComNewCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCE | Com | New | CZ05 | 2.6 | 0.000525 | 0 | 2.67 | 0.000643 | -0.0234 | 2.6 | 0.000525 | 0 | 2.67 | 0.000643 | -0.0234 | CFL | AllSpc | 2600 | 0.525 | 2600 | 0.525 | 1.03 | 1.22 | -0.009
CFLAllSpcSDGComNewCZ06 | Com-Iltg-dWatt-CFL_OSspc | SDG | Com | New | CZ06 | 2.13 | 0.000427 | 0 | 2.29 | 0.00053 | -0.0116 | 2.13 | 0.000427 | 0 | 2.29 | 0.00053 | -0.0116 | CFL | AllSpc | 2130 | 0.427 | 2130 | 0.427 | 1.08 | 1.24 | -0.00545
CFLAllSpcSCEComNewCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCE | Com | New | CZ06 | 2.11 | 0.000454 | 0 | 2.31 | 0.000562 | -0.00927 | 2.11 | 0.000454 | 0 | 2.31 | 0.000562 | -0.00927 | CFL | AllSpc | 2110 | 0.454 | 2110 | 0.454 | 1.09 | 1.24 | -0.00439
CFLAllSpcSDGComNewCZ07 | Com-Iltg-dWatt-CFL_OSspc | SDG | Com | New | CZ07 | 1.97 | 0.000414 | 0 | 2.14 | 0.000504 | -0.00765 | 1.97 | 0.000414 | 0 | 2.14 | 0.000504 | -0.00765 | CFL | AllSpc | 1970 | 0.414 | 1970 | 0.414 | 1.09 | 1.22 | -0.00388
CFLAllSpcSCEComNewCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCE | Com | New | CZ08 | 2.04 | 0.000435 | 0 | 2.23 | 0.000537 | -0.00779 | 2.04 | 0.000435 | 0 | 2.23 | 0.000537 | -0.00779 | CFL | AllSpc | 2040 | 0.435 | 2040 | 0.435 | 1.09 | 1.23 | -0.00382
CFLAllSpcSDGComNewCZ08 | Com-Iltg-dWatt-CFL_OSspc | SDG | Com | New | CZ08 | 2.22 | 0.000508 | 0 | 2.43 | 0.000635 | -0.00864 | 2.22 | 0.000508 | 0 | 2.43 | 0.000635 | -0.00864 | CFL | AllSpc | 2220 | 0.508 | 2220 | 0.508 | 1.09 | 1.25 | -0.00389
CFLAllSpcSCEComNewCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCE | Com | New | CZ09 | 2.06 | 0.000442 | 0 | 2.27 | 0.000572 | -0.00861 | 2.06 | 0.000442 | 0 | 2.27 | 0.000572 | -0.00861 | CFL | AllSpc | 2060 | 0.442 | 2060 | 0.442 | 1.1 | 1.29 | -0.00418
CFLAllSpcSDGComNewCZ10 | Com-Iltg-dWatt-CFL_OSspc | SDG | Com | New | CZ10 | 2.03 | 0.000439 | 0 | 2.23 | 0.000574 | -0.00938 | 2.03 | 0.000439 | 0 | 2.23 | 0.000574 | -0.00938 | CFL | AllSpc | 2030 | 0.439 | 2030 | 0.439 | 1.1 | 1.31 | -0.00462
CFLAllSpcSCEComNewCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCE | Com | New | CZ10 | 1.93 | 0.000407 | 0 | 2.08 | 0.000517 | -0.00814 | 1.93 | 0.000407 | 0 | 2.08 | 0.000517 | -0.00814 | CFL | AllSpc | 1930 | 0.407 | 1930 | 0.407 | 1.08 | 1.27 | -0.00422
CFLAllSpcPGEComNewCZ11 | Com-Iltg-dWatt-CFL_OSspc | PGE | Com | New | CZ11 | 2.07 | 0.000393 | 0 | 2.19 | 0.000491 | -0.0144 | 2.07 | 0.000393 | 0 | 2.19 | 0.000491 | -0.0144 | CFL | AllSpc | 2070 | 0.393 | 2070 | 0.393 | 1.06 | 1.25 | -0.00696
CFLAllSpcPGEComNewCZ12 | Com-Iltg-dWatt-CFL_OSspc | PGE | Com | New | CZ12 | 2.04 | 0.000397 | 0 | 2.17 | 0.000492 | -0.0137 | 2.04 | 0.000397 | 0 | 2.17 | 0.000492 | -0.0137 | CFL | AllSpc | 2040 | 0.397 | 2040 | 0.397 | 1.06 | 1.24 | -0.00672
CFLAllSpcPGEComNewCZ13 | Com-Iltg-dWatt-CFL_OSspc | PGE | Com | New | CZ13 | 2.11 | 0.000401 | 0 | 2.29 | 0.000494 | -0.013 | 2.11 | 0.000401 | 0 | 2.29 | 0.000494 | -0.013 | CFL | AllSpc | 2110 | 0.401 | 2110 | 0.401 | 1.09 | 1.23 | -0.00616
CFLAllSpcSCEComNewCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCE | Com | New | CZ13 | 2.2 | 0.000417 | 0 | 2.49 | 0.000535 | -0.013 | 2.2 | 0.000417 | 0 | 2.49 | 0.000535 | -0.013 | CFL | AllSpc | 2200 | 0.417 | 2200 | 0.417 | 1.13 | 1.28 | -0.00591
CFLAllSpcSCEComNewCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCE | Com | New | CZ14 | 2.14 | 0.000465 | 0 | 2.32 | 0.000604 | -0.0152 | 2.14 | 0.000465 | 0 | 2.32 | 0.000604 | -0.0152 | CFL | AllSpc | 2140 | 0.465 | 2140 | 0.465 | 1.08 | 1.3 | -0.0071
CFLAllSpcSDGComNewCZ14 | Com-Iltg-dWatt-CFL_OSspc | SDG | Com | New | CZ14 | 1.69 | 0.000344 | 0 | 1.83 | 0.000444 | -0.0102 | 1.69 | 0.000344 | 0 | 1.83 | 0.000444 | -0.0102 | CFL | AllSpc | 1690 | 0.344 | 1690 | 0.344 | 1.08 | 1.29 | -0.00604
CFLAllSpcSDGComNewCZ15 | Com-Iltg-dWatt-CFL_OSspc | SDG | Com | New | CZ15 | 1.48 | 0.000256 | 0 | 1.74 | 0.000339 | -0.00235 | 1.48 | 0.000256 | 0 | 1.74 | 0.000339 | -0.00235 | CFL | AllSpc | 1480 | 0.256 | 1480 | 0.256 | 1.18 | 1.32 | -0.00159
CFLAllSpcSCEComNewCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCE | Com | New | CZ15 | 1.87 | 0.000394 | 0 | 2.2 | 0.000523 | -0.00312 | 1.87 | 0.000394 | 0 | 2.2 | 0.000523 | -0.00312 | CFL | AllSpc | 1870 | 0.394 | 1870 | 0.394 | 1.18 | 1.33 | -0.00167
CFLAllSpcPGEComNewCZ16 | Com-Iltg-dWatt-CFL_OSspc | PGE | Com | New | CZ16 | 1.89 | 0.000342 | 0 | 1.83 | 0.000405 | -0.0202 | 1.89 | 0.000342 | 0 | 1.83 | 0.000405 | -0.0202 | CFL | AllSpc | 1890 | 0.342 | 1890 | 0.342 | 0.968 | 1.18 | -0.0107
CFLAllSpcSCEComNewCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCE | Com | New | CZ16 | 1.93 | 0.000365 | 0 | 1.94 | 0.000451 | -0.0217 | 1.93 | 0.000365 | 0 | 1.94 | 0.000451 | -0.0217 | CFL | AllSpc | 1930 | 0.365 | 1930 | 0.365 | 1.01 | 1.24 | -0.0112
CFLAllSpcSCGComNewIOU | Com-Iltg-dWatt-CFL_OSspc | SCG | Com | New | IOU | 2.02 | 0.000428 | 0 | 2.21 | 0.000539 | -0.00825 | 2.02 | 0.000428 | 0 | 2.21 | 0.000539 | -0.00825 | CFL | AllSpc | 2020 | 0.428 | 2020 | 0.428 | 1.09 | 1.26 | -0.00408
CFLAllSpcPGEComNewIOU | Com-Iltg-dWatt-CFL_OSspc | PGE | Com | New | IOU | 2.03 | 0.000402 | 0 | 2.21 | 0.000511 | -0.0127 | 2.03 | 0.000402 | 0 | 2.21 | 0.000511 | -0.0127 | CFL | AllSpc | 2030 | 0.402 | 2030 | 0.402 | 1.09 | 1.27 | -0.00626
CFLAllSpcSCEComNewIOU | Com-Iltg-dWatt-CFL_OSspc | SCE | Com | New | IOU | 2.01 | 0.000427 | 0 | 2.2 | 0.000538 | -0.00827 | 2.01 | 0.000427 | 0 | 2.2 | 0.000538 | -0.00827 | CFL | AllSpc | 2010 | 0.427 | 2010 | 0.427 | 1.09 | 1.26 | -0.00411
CFLAllSpcSDGComNewIOU | Com-Iltg-dWatt-CFL_OSspc | SDG | Com | New | IOU | 1.99 | 0.000422 | 0 | 2.17 | 0.000524 | -0.00821 | 1.99 | 0.000422 | 0 | 2.17 | 0.000524 | -0.00821 | CFL | AllSpc | 1990 | 0.422 | 1990 | 0.422 | 1.09 | 1.24 | -0.00413
CFLAllSpcPGEECCExCZ01 | Com-Iltg-dWatt-CFL_OSspc | PGE | ECC | Ex | CZ01 | 1.41 | 0.000437 | 0 | 1.45 | 0.000534 | -0.0279 | 1.41 | 0.000437 | 0 | 1.45 | 0.000534 | -0.0279 | CFL | AllSpc | 1410 | 0.437 | 1410 | 0.437 | 1.03 | 1.22 | -0.0198
CFLAllSpcPGEECCExCZ02 | Com-Iltg-dWatt-CFL_OSspc | PGE | ECC | Ex | CZ02 | 1.41 | 0.000284 | 0 | 1.53 | 0.000374 | -0.0171 | 1.41 | 0.000284 | 0 | 1.53 | 0.000374 | -0.0171 | CFL | AllSpc | 1410 | 0.284 | 1410 | 0.284 | 1.09 | 1.32 | -0.0121
CFLAllSpcPGEECCExCZ03 | Com-Iltg-dWatt-CFL_OSspc | PGE | ECC | Ex | CZ03 | 1.41 | 0.000284 | 0 | 1.52 | 0.000354 | -0.0178 | 1.41 | 0.000284 | 0 | 1.52 | 0.000354 | -0.0178 | CFL | AllSpc | 1410 | 0.284 | 1410 | 0.284 | 1.08 | 1.25 | -0.0126
CFLAllSpcPGEECCExCZ04 | Com-Iltg-dWatt-CFL_OSspc | PGE | ECC | Ex | CZ04 | 1.41 | 0.000437 | 0 | 1.56 | 0.000568 | -0.0136 | 1.41 | 0.000437 | 0 | 1.56 | 0.000568 | -0.0136 | CFL | AllSpc | 1410 | 0.437 | 1410 | 0.437 | 1.11 | 1.3 | -0.00965
CFLAllSpcSCEECCExCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCE | ECC | Ex | CZ05 | 1.41 | 0.000437 | 0 | 1.52 | 0.000541 | -0.0166 | 1.41 | 0.000437 | 0 | 1.52 | 0.000541 | -0.0166 | CFL | AllSpc | 1410 | 0.437 | 1410 | 0.437 | 1.08 | 1.24 | -0.0118
CFLAllSpcPGEECCExCZ05 | Com-Iltg-dWatt-CFL_OSspc | PGE | ECC | Ex | CZ05 | 1.41 | 0.000437 | 0 | 1.52 | 0.000541 | -0.0166 | 1.41 | 0.000437 | 0 | 1.52 | 0.000541 | -0.0166 | CFL | AllSpc | 1410 | 0.437 | 1410 | 0.437 | 1.08 | 1.24 | -0.0118
CFLAllSpcSCGECCExCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCG | ECC | Ex | CZ05 | 1.41 | 0.000437 | 0 | 1.52 | 0.000541 | -0.0166 | 1.41 | 0.000437 | 0 | 1.52 | 0.000541 | -0.0166 | CFL | AllSpc | 1410 | 0.437 | 1410 | 0.437 | 1.08 | 1.24 | -0.0118
CFLAllSpcSDGECCExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SDG | ECC | Ex | CZ06 | 1.41 | 0.000437 | 0 | 1.58 | 0.000558 | -0.00819 | 1.41 | 0.000437 | 0 | 1.58 | 0.000558 | -0.00819 | CFL | AllSpc | 1410 | 0.437 | 1410 | 0.437 | 1.12 | 1.28 | -0.00581
CFLAllSpcSCEECCExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCE | ECC | Ex | CZ06 | 1.41 | 0.000437 | 0 | 1.58 | 0.000558 | -0.00819 | 1.41 | 0.000437 | 0 | 1.58 | 0.000558 | -0.00819 | CFL | AllSpc | 1410 | 0.437 | 1410 | 0.437 | 1.12 | 1.28 | -0.00581
CFLAllSpcSCGECCExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCG | ECC | Ex | CZ06 | 1.41 | 0.000437 | 0 | 1.58 | 0.000558 | -0.00819 | 1.41 | 0.000437 | 0 | 1.58 | 0.000558 | -0.00819 | CFL | AllSpc | 1410 | 0.437 | 1410 | 0.437 | 1.12 | 1.28 | -0.00581
CFLAllSpcSDGECCExCZ07 | Com-Iltg-dWatt-CFL_OSspc | SDG | ECC | Ex | CZ07 | 1.41 | 0.000437 | 0 | 1.59 | 0.000557 | -0.00677 | 1.41 | 0.000437 | 0 | 1.59 | 0.000557 | -0.00677 | CFL | AllSpc | 1410 | 0.437 | 1410 | 0.437 | 1.13 | 1.27 | -0.0048
CFLAllSpcSDGECCExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SDG | ECC | Ex | CZ08 | 1.41 | 0.000437 | 0 | 1.6 | 0.000555 | -0.00736 | 1.41 | 0.000437 | 0 | 1.6 | 0.000555 | -0.00736 | CFL | AllSpc | 1410 | 0.437 | 1410 | 0.437 | 1.13 | 1.27 | -0.00522
CFLAllSpcSCEECCExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCE | ECC | Ex | CZ08 | 1.41 | 0.000437 | 0 | 1.6 | 0.000555 | -0.00736 | 1.41 | 0.000437 | 0 | 1.6 | 0.000555 | -0.00736 | CFL | AllSpc | 1410 | 0.437 | 1410 | 0.437 | 1.13 | 1.27 | -0.00522
CFLAllSpcSCGECCExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCG | ECC | Ex | CZ08 | 1.41 | 0.000437 | 0 | 1.6 | 0.000555 | -0.00736 | 1.41 | 0.000437 | 0 | 1.6 | 0.000555 | -0.00736 | CFL | AllSpc | 1410 | 0.437 | 1410 | 0.437 | 1.13 | 1.27 | -0.00522
CFLAllSpcSCGECCExCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCG | ECC | Ex | CZ09 | 1.41 | 0.000437 | 0 | 1.62 | 0.00057 | -0.00819 | 1.41 | 0.000437 | 0 | 1.62 | 0.00057 | -0.00819 | CFL | AllSpc | 1410 | 0.437 | 1410 | 0.437 | 1.15 | 1.3 | -0.00581
CFLAllSpcSCEECCExCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCE | ECC | Ex | CZ09 | 1.41 | 0.000437 | 0 | 1.62 | 0.00057 | -0.00819 | 1.41 | 0.000437 | 0 | 1.62 | 0.00057 | -0.00819 | CFL | AllSpc | 1410 | 0.437 | 1410 | 0.437 | 1.15 | 1.3 | -0.00581
CFLAllSpcSCGECCExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCG | ECC | Ex | CZ10 | 1.41 | 0.000437 | 0 | 1.59 | 0.000566 | -0.00873 | 1.41 | 0.000437 | 0 | 1.59 | 0.000566 | -0.00873 | CFL | AllSpc | 1410 | 0.437 | 1410 | 0.437 | 1.13 | 1.3 | -0.00619
CFLAllSpcSCEECCExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCE | ECC | Ex | CZ10 | 1.41 | 0.000437 | 0 | 1.59 | 0.000566 | -0.00873 | 1.41 | 0.000437 | 0 | 1.59 | 0.000566 | -0.00873 | CFL | AllSpc | 1410 | 0.437 | 1410 | 0.437 | 1.13 | 1.3 | -0.00619
CFLAllSpcSDGECCExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SDG | ECC | Ex | CZ10 | 1.41 | 0.000437 | 0 | 1.59 | 0.000566 | -0.00873 | 1.41 | 0.000437 | 0 | 1.59 | 0.000566 | -0.00873 | CFL | AllSpc | 1410 | 0.437 | 1410 | 0.437 | 1.13 | 1.3 | -0.00619
CFLAllSpcPGEECCExCZ11 | Com-Iltg-dWatt-CFL_OSspc | PGE | ECC | Ex | CZ11 | 1.41 | 0.000284 | 0 | 1.57 | 0.000354 | -0.0157 | 1.41 | 0.000284 | 0 | 1.57 | 0.000354 | -0.0157 | CFL | AllSpc | 1410 | 0.284 | 1410 | 0.284 | 1.11 | 1.25 | -0.0111
CFLAllSpcPGEECCExCZ12 | Com-Iltg-dWatt-CFL_OSspc | PGE | ECC | Ex | CZ12 | 1.41 | 0.000284 | 0 | 1.56 | 0.000357 | -0.0154 | 1.41 | 0.000284 | 0 | 1.56 | 0.000357 | -0.0154 | CFL | AllSpc | 1410 | 0.284 | 1410 | 0.284 | 1.11 | 1.26 | -0.0109
CFLAllSpcPGEECCExCZ13 | Com-Iltg-dWatt-CFL_OSspc | PGE | ECC | Ex | CZ13 | 1.41 | 0.000284 | 0 | 1.58 | 0.000368 | -0.0123 | 1.41 | 0.000284 | 0 | 1.58 | 0.000368 | -0.0123 | CFL | AllSpc | 1410 | 0.284 | 1410 | 0.284 | 1.12 | 1.3 | -0.00872
CFLAllSpcSCEECCExCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCE | ECC | Ex | CZ13 | 1.41 | 0.000284 | 0 | 1.58 | 0.000368 | -0.0123 | 1.41 | 0.000284 | 0 | 1.58 | 0.000368 | -0.0123 | CFL | AllSpc | 1410 | 0.284 | 1410 | 0.284 | 1.12 | 1.3 | -0.00872
CFLAllSpcSCGECCExCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCG | ECC | Ex | CZ13 | 1.41 | 0.000284 | 0 | 1.58 | 0.000368 | -0.0123 | 1.41 | 0.000284 | 0 | 1.58 | 0.000368 | -0.0123 | CFL | AllSpc | 1410 | 0.284 | 1410 | 0.284 | 1.12 | 1.3 | -0.00872
CFLAllSpcSCEECCExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCE | ECC | Ex | CZ14 | 1.41 | 0.000437 | 0 | 1.56 | 0.000558 | -0.0132 | 1.41 | 0.000437 | 0 | 1.56 | 0.000558 | -0.0132 | CFL | AllSpc | 1410 | 0.437 | 1410 | 0.437 | 1.11 | 1.28 | -0.00936
CFLAllSpcSDGECCExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SDG | ECC | Ex | CZ14 | 1.41 | 0.000437 | 0 | 1.56 | 0.000558 | -0.0132 | 1.41 | 0.000437 | 0 | 1.56 | 0.000558 | -0.0132 | CFL | AllSpc | 1410 | 0.437 | 1410 | 0.437 | 1.11 | 1.28 | -0.00936
CFLAllSpcSCGECCExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCG | ECC | Ex | CZ14 | 1.41 | 0.000437 | 0 | 1.56 | 0.000558 | -0.0132 | 1.41 | 0.000437 | 0 | 1.56 | 0.000558 | -0.0132 | CFL | AllSpc | 1410 | 0.437 | 1410 | 0.437 | 1.11 | 1.28 | -0.00936
CFLAllSpcSCGECCExCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCG | ECC | Ex | CZ15 | 1.41 | 0.000437 | 0 | 1.69 | 0.000552 | -0.00362 | 1.41 | 0.000437 | 0 | 1.69 | 0.000552 | -0.00362 | CFL | AllSpc | 1410 | 0.437 | 1410 | 0.437 | 1.2 | 1.26 | -0.00257
CFLAllSpcSCEECCExCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCE | ECC | Ex | CZ15 | 1.41 | 0.000437 | 0 | 1.69 | 0.000552 | -0.00362 | 1.41 | 0.000437 | 0 | 1.69 | 0.000552 | -0.00362 | CFL | AllSpc | 1410 | 0.437 | 1410 | 0.437 | 1.2 | 1.26 | -0.00257
CFLAllSpcSCEECCExCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCE | ECC | Ex | CZ16 | 1.41 | 0.000284 | 0 | 1.47 | 0.00035 | -0.0233 | 1.41 | 0.000284 | 0 | 1.47 | 0.00035 | -0.0233 | CFL | AllSpc | 1410 | 0.284 | 1410 | 0.284 | 1.04 | 1.23 | -0.0165
CFLAllSpcPGEECCExCZ16 | Com-Iltg-dWatt-CFL_OSspc | PGE | ECC | Ex | CZ16 | 1.41 | 0.000284 | 0 | 1.47 | 0.00035 | -0.0233 | 1.41 | 0.000284 | 0 | 1.47 | 0.00035 | -0.0233 | CFL | AllSpc | 1410 | 0.284 | 1410 | 0.284 | 1.04 | 1.23 | -0.0165
CFLAllSpcSCGECCExCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCG | ECC | Ex | CZ16 | 1.41 | 0.000284 | 0 | 1.47 | 0.00035 | -0.0233 | 1.41 | 0.000284 | 0 | 1.47 | 0.00035 | -0.0233 | CFL | AllSpc | 1410 | 0.284 | 1410 | 0.284 | 1.04 | 1.23 | -0.0165
CFLAllSpcSCGECCExIOU | Com-Iltg-dWatt-CFL_OSspc | SCG | ECC | Ex | IOU | 1.41 | 0.000427 | 0 | 1.59 | 0.000547 | -0.00883 | 1.41 | 0.000427 | 0 | 1.59 | 0.000547 | -0.00883 | CFL | AllSpc | 1410 | 0.427 | 1410 | 0.427 | 1.13 | 1.28 | -0.00626
CFLAllSpcPGEECCExIOU | Com-Iltg-dWatt-CFL_OSspc | PGE | ECC | Ex | IOU | 1.41 | 0.000313 | 0 | 1.54 | 0.000396 | -0.0163 | 1.41 | 0.000313 | 0 | 1.54 | 0.000396 | -0.0163 | CFL | AllSpc | 1410 | 0.313 | 1410 | 0.313 | 1.09 | 1.27 | -0.0116
CFLAllSpcSCEECCExIOU | Com-Iltg-dWatt-CFL_OSspc | SCE | ECC | Ex | IOU | 1.41 | 0.000422 | 0 | 1.59 | 0.000539 | -0.00917 | 1.41 | 0.000422 | 0 | 1.59 | 0.000539 | -0.00917 | CFL | AllSpc | 1410 | 0.422 | 1410 | 0.422 | 1.13 | 1.28 | -0.0065
CFLAllSpcSDGECCExIOU | Com-Iltg-dWatt-CFL_OSspc | SDG | ECC | Ex | IOU | 1.41 | 0.000437 | 0 | 1.59 | 0.000559 | -0.00728 | 1.41 | 0.000437 | 0 | 1.59 | 0.000559 | -0.00728 | CFL | AllSpc | 1410 | 0.437 | 1410 | 0.437 | 1.13 | 1.28 | -0.00516
CFLAllSpcPGEECCNewCZ01 | Com-Iltg-dWatt-CFL_OSspc | PGE | ECC | New | CZ01 | 1.41 | 0.000437 | 0 | 1.44 | 0.00051 | -0.0288 | 1.41 | 0.000437 | 0 | 1.44 | 0.00051 | -0.0288 | CFL | AllSpc | 1410 | 0.437 | 1410 | 0.437 | 1.02 | 1.17 | -0.0204
CFLAllSpcPGEECCNewCZ02 | Com-Iltg-dWatt-CFL_OSspc | PGE | ECC | New | CZ02 | 1.41 | 0.000284 | 0 | 1.52 | 0.000387 | -0.0175 | 1.41 | 0.000284 | 0 | 1.52 | 0.000387 | -0.0175 | CFL | AllSpc | 1410 | 0.284 | 1410 | 0.284 | 1.08 | 1.36 | -0.0124
CFLAllSpcPGEECCNewCZ03 | Com-Iltg-dWatt-CFL_OSspc | PGE | ECC | New | CZ03 | 1.41 | 0.000284 | 0 | 1.5 | 0.000372 | -0.0192 | 1.41 | 0.000284 | 0 | 1.5 | 0.000372 | -0.0192 | CFL | AllSpc | 1410 | 0.284 | 1410 | 0.284 | 1.06 | 1.31 | -0.0136
CFLAllSpcPGEECCNewCZ04 | Com-Iltg-dWatt-CFL_OSspc | PGE | ECC | New | CZ04 | 1.41 | 0.000437 | 0 | 1.54 | 0.000555 | -0.0141 | 1.41 | 0.000437 | 0 | 1.54 | 0.000555 | -0.0141 | CFL | AllSpc | 1410 | 0.437 | 1410 | 0.437 | 1.09 | 1.27 | -0.01
CFLAllSpcSCEECCNewCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCE | ECC | New | CZ05 | 1.41 | 0.000437 | 0 | 1.5 | 0.000553 | -0.0193 | 1.41 | 0.000437 | 0 | 1.5 | 0.000553 | -0.0193 | CFL | AllSpc | 1410 | 0.437 | 1410 | 0.437 | 1.06 | 1.27 | -0.0137
CFLAllSpcPGEECCNewCZ05 | Com-Iltg-dWatt-CFL_OSspc | PGE | ECC | New | CZ05 | 1.41 | 0.000437 | 0 | 1.5 | 0.000536 | -0.0186 | 1.41 | 0.000437 | 0 | 1.5 | 0.000536 | -0.0186 | CFL | AllSpc | 1410 | 0.437 | 1410 | 0.437 | 1.06 | 1.23 | -0.0132
CFLAllSpcSCEECCNewCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCE | ECC | New | CZ06 | 1.41 | 0.000437 | 0 | 1.58 | 0.000565 | -0.01 | 1.41 | 0.000437 | 0 | 1.58 | 0.000565 | -0.01 | CFL | AllSpc | 1410 | 0.437 | 1410 | 0.437 | 1.12 | 1.29 | -0.00709
CFLAllSpcSDGECCNewCZ06 | Com-Iltg-dWatt-CFL_OSspc | SDG | ECC | New | CZ06 | 1.41 | 0.000437 | 0 | 1.58 | 0.000561 | -0.00998 | 1.41 | 0.000437 | 0 | 1.58 | 0.000561 | -0.00998 | CFL | AllSpc | 1410 | 0.437 | 1410 | 0.437 | 1.12 | 1.28 | -0.00708
CFLAllSpcSDGECCNewCZ07 | Com-Iltg-dWatt-CFL_OSspc | SDG | ECC | New | CZ07 | 1.41 | 0.000437 | 0 | 1.58 | 0.000565 | -0.00749 | 1.41 | 0.000437 | 0 | 1.58 | 0.000565 | -0.00749 | CFL | AllSpc | 1410 | 0.437 | 1410 | 0.437 | 1.12 | 1.29 | -0.00531
CFLAllSpcSDGECCNewCZ08 | Com-Iltg-dWatt-CFL_OSspc | SDG | ECC | New | CZ08 | 1.41 | 0.000437 | 0 | 1.6 | 0.00056 | -0.0073 | 1.41 | 0.000437 | 0 | 1.6 | 0.00056 | -0.0073 | CFL | AllSpc | 1410 | 0.437 | 1410 | 0.437 | 1.13 | 1.28 | -0.00518
CFLAllSpcSCEECCNewCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCE | ECC | New | CZ08 | 1.41 | 0.000437 | 0 | 1.6 | 0.000565 | -0.00711 | 1.41 | 0.000437 | 0 | 1.6 | 0.000565 | -0.00711 | CFL | AllSpc | 1410 | 0.437 | 1410 | 0.437 | 1.13 | 1.29 | -0.00504
CFLAllSpcSCEECCNewCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCE | ECC | New | CZ09 | 1.41 | 0.000437 | 0 | 1.6 | 0.000581 | -0.00826 | 1.41 | 0.000437 | 0 | 1.6 | 0.000581 | -0.00826 | CFL | AllSpc | 1410 | 0.437 | 1410 | 0.437 | 1.13 | 1.33 | -0.00586
CFLAllSpcSCEECCNewCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCE | ECC | New | CZ10 | 1.41 | 0.000437 | 0 | 1.61 | 0.000587 | -0.00821 | 1.41 | 0.000437 | 0 | 1.61 | 0.000587 | -0.00821 | CFL | AllSpc | 1410 | 0.437 | 1410 | 0.437 | 1.14 | 1.34 | -0.00582
CFLAllSpcSDGECCNewCZ10 | Com-Iltg-dWatt-CFL_OSspc | SDG | ECC | New | CZ10 | 1.41 | 0.000437 | 0 | 1.61 | 0.000577 | -0.0083 | 1.41 | 0.000437 | 0 | 1.61 | 0.000577 | -0.0083 | CFL | AllSpc | 1410 | 0.437 | 1410 | 0.437 | 1.14 | 1.32 | -0.00589
CFLAllSpcPGEECCNewCZ11 | Com-Iltg-dWatt-CFL_OSspc | PGE | ECC | New | CZ11 | 1.41 | 0.000284 | 0 | 1.57 | 0.000379 | -0.0147 | 1.41 | 0.000284 | 0 | 1.57 | 0.000379 | -0.0147 | CFL | AllSpc | 1410 | 0.284 | 1410 | 0.284 | 1.11 | 1.33 | -0.0104
CFLAllSpcPGEECCNewCZ12 | Com-Iltg-dWatt-CFL_OSspc | PGE | ECC | New | CZ12 | 1.41 | 0.000284 | 0 | 1.56 | 0.000388 | -0.0149 | 1.41 | 0.000284 | 0 | 1.56 | 0.000388 | -0.0149 | CFL | AllSpc | 1410 | 0.284 | 1410 | 0.284 | 1.11 | 1.37 | -0.0106
CFLAllSpcPGEECCNewCZ13 | Com-Iltg-dWatt-CFL_OSspc | PGE | ECC | New | CZ13 | 1.41 | 0.000284 | 0 | 1.58 | 0.000383 | -0.0128 | 1.41 | 0.000284 | 0 | 1.58 | 0.000383 | -0.0128 | CFL | AllSpc | 1410 | 0.284 | 1410 | 0.284 | 1.12 | 1.35 | -0.00908
CFLAllSpcSCEECCNewCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCE | ECC | New | CZ13 | 1.41 | 0.000284 | 0 | 1.59 | 0.000399 | -0.0128 | 1.41 | 0.000284 | 0 | 1.59 | 0.000399 | -0.0128 | CFL | AllSpc | 1410 | 0.284 | 1410 | 0.284 | 1.13 | 1.4 | -0.00908
CFLAllSpcSDGECCNewCZ14 | Com-Iltg-dWatt-CFL_OSspc | SDG | ECC | New | CZ14 | 1.41 | 0.000437 | 0 | 1.59 | 0.000559 | -0.0131 | 1.41 | 0.000437 | 0 | 1.59 | 0.000559 | -0.0131 | CFL | AllSpc | 1410 | 0.437 | 1410 | 0.437 | 1.13 | 1.28 | -0.00929
CFLAllSpcSCEECCNewCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCE | ECC | New | CZ14 | 1.41 | 0.000437 | 0 | 1.59 | 0.000569 | -0.0133 | 1.41 | 0.000437 | 0 | 1.59 | 0.000569 | -0.0133 | CFL | AllSpc | 1410 | 0.437 | 1410 | 0.437 | 1.13 | 1.3 | -0.00943
CFLAllSpcSDGECCNewCZ15 | Com-Iltg-dWatt-CFL_OSspc | SDG | ECC | New | CZ15 | 1.41 | 0.000437 | 0 | 1.7 | 0.000573 | -0.00326 | 1.41 | 0.000437 | 0 | 1.7 | 0.000573 | -0.00326 | CFL | AllSpc | 1410 | 0.437 | 1410 | 0.437 | 1.21 | 1.31 | -0.00231
CFLAllSpcSCEECCNewCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCE | ECC | New | CZ15 | 1.41 | 0.000437 | 0 | 1.71 | 0.000585 | -0.00314 | 1.41 | 0.000437 | 0 | 1.71 | 0.000585 | -0.00314 | CFL | AllSpc | 1410 | 0.437 | 1410 | 0.437 | 1.21 | 1.34 | -0.00223
CFLAllSpcPGEECCNewCZ16 | Com-Iltg-dWatt-CFL_OSspc | PGE | ECC | New | CZ16 | 1.41 | 0.000284 | 0 | 1.48 | 0.000368 | -0.0234 | 1.41 | 0.000284 | 0 | 1.48 | 0.000368 | -0.0234 | CFL | AllSpc | 1410 | 0.284 | 1410 | 0.284 | 1.05 | 1.3 | -0.0166
CFLAllSpcSCEECCNewCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCE | ECC | New | CZ16 | 1.41 | 0.000284 | 0 | 1.48 | 0.000382 | -0.024 | 1.41 | 0.000284 | 0 | 1.48 | 0.000382 | -0.024 | CFL | AllSpc | 1410 | 0.284 | 1410 | 0.284 | 1.05 | 1.35 | -0.017
CFLAllSpcSDGECCNewIOU | Com-Iltg-dWatt-CFL_OSspc | SDG | ECC | New | IOU | 1.41 | 0.000437 | 0 | 1.59 | 0.000568 | -0.00772 | 1.41 | 0.000437 | 0 | 1.59 | 0.000568 | -0.00772 | CFL | AllSpc | 1410 | 0.437 | 1410 | 0.437 | 1.13 | 1.3 | -0.00548
CFLAllSpcSCGECCNewIOU | Com-Iltg-dWatt-CFL_OSspc | SCG | ECC | New | IOU | 1.41 | 0.000437 | 0 | 1.6 | 0.000565 | -0.00834 | 1.41 | 0.000437 | 0 | 1.6 | 0.000565 | -0.00834 | CFL | AllSpc | 1410 | 0.437 | 1410 | 0.437 | 1.13 | 1.29 | -0.00591
CFLAllSpcPGEECCNewIOU | Com-Iltg-dWatt-CFL_OSspc | PGE | ECC | New | IOU | 1.41 | 0.00033 | 0 | 1.56 | 0.000445 | -0.0149 | 1.41 | 0.00033 | 0 | 1.56 | 0.000445 | -0.0149 | CFL | AllSpc | 1410 | 0.33 | 1410 | 0.33 | 1.11 | 1.35 | -0.0106
CFLAllSpcSCEECCNewIOU | Com-Iltg-dWatt-CFL_OSspc | SCE | ECC | New | IOU | 1.41 | 0.000437 | 0 | 1.6 | 0.000565 | -0.00835 | 1.41 | 0.000437 | 0 | 1.6 | 0.000565 | -0.00835 | CFL | AllSpc | 1410 | 0.437 | 1410 | 0.437 | 1.13 | 1.29 | -0.00592
CFLAllSpcPGEEPrExCZ01 | Com-Iltg-dWatt-CFL_OSspc | PGE | EPr | Ex | CZ01 | 1.12 | 0.000364 | 0 | 1.11 | 0.000433 | -0.0202 | 1.12 | 0.000364 | 0 | 1.11 | 0.000433 | -0.0202 | CFL | AllSpc | 1120 | 0.364 | 1120 | 0.364 | 0.991 | 1.19 | -0.018
CFLAllSpcPGEEPrExCZ02 | Com-Iltg-dWatt-CFL_OSspc | PGE | EPr | Ex | CZ02 | 1.12 | 1.16e-05 | 0 | 1.18 | 1.16e-05 | -0.0121 | 1.12 | 1.16e-05 | 0 | 1.18 | 1.16e-05 | -0.0121 | CFL | AllSpc | 1120 | 0.0116 | 1120 | 0.0116 | 1.05 | 1 | -0.0108
CFLAllSpcPGEEPrExCZ03 | Com-Iltg-dWatt-CFL_OSspc | PGE | EPr | Ex | CZ03 | 1.12 | 1.16e-05 | 0 | 1.19 | 1.16e-05 | -0.0118 | 1.12 | 1.16e-05 | 0 | 1.19 | 1.16e-05 | -0.0118 | CFL | AllSpc | 1120 | 0.0116 | 1120 | 0.0116 | 1.06 | 1 | -0.0105
CFLAllSpcPGEEPrExCZ04 | Com-Iltg-dWatt-CFL_OSspc | PGE | EPr | Ex | CZ04 | 1.12 | 0.000364 | 0 | 1.21 | 0.000446 | -0.00932 | 1.12 | 0.000364 | 0 | 1.21 | 0.000446 | -0.00932 | CFL | AllSpc | 1120 | 0.364 | 1120 | 0.364 | 1.08 | 1.23 | -0.00832
CFLAllSpcSCGEPrExCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCG | EPr | Ex | CZ05 | 1.12 | 0.000364 | 0 | 1.22 | 0.000461 | -0.0102 | 1.12 | 0.000364 | 0 | 1.22 | 0.000461 | -0.0102 | CFL | AllSpc | 1120 | 0.364 | 1120 | 0.364 | 1.09 | 1.27 | -0.00911
CFLAllSpcSCEEPrExCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCE | EPr | Ex | CZ05 | 1.12 | 0.000364 | 0 | 1.22 | 0.000461 | -0.0102 | 1.12 | 0.000364 | 0 | 1.22 | 0.000461 | -0.0102 | CFL | AllSpc | 1120 | 0.364 | 1120 | 0.364 | 1.09 | 1.27 | -0.00911
CFLAllSpcPGEEPrExCZ05 | Com-Iltg-dWatt-CFL_OSspc | PGE | EPr | Ex | CZ05 | 1.12 | 0.000364 | 0 | 1.22 | 0.000461 | -0.0102 | 1.12 | 0.000364 | 0 | 1.22 | 0.000461 | -0.0102 | CFL | AllSpc | 1120 | 0.364 | 1120 | 0.364 | 1.09 | 1.27 | -0.00911
CFLAllSpcSDGEPrExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SDG | EPr | Ex | CZ06 | 1.12 | 0.000364 | 0 | 1.26 | 0.000464 | -0.00522 | 1.12 | 0.000364 | 0 | 1.26 | 0.000464 | -0.00522 | CFL | AllSpc | 1120 | 0.364 | 1120 | 0.364 | 1.13 | 1.27 | -0.00466
CFLAllSpcSCGEPrExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCG | EPr | Ex | CZ06 | 1.12 | 0.000364 | 0 | 1.26 | 0.000464 | -0.00522 | 1.12 | 0.000364 | 0 | 1.26 | 0.000464 | -0.00522 | CFL | AllSpc | 1120 | 0.364 | 1120 | 0.364 | 1.13 | 1.27 | -0.00466
CFLAllSpcSCEEPrExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCE | EPr | Ex | CZ06 | 1.12 | 0.000364 | 0 | 1.26 | 0.000464 | -0.00522 | 1.12 | 0.000364 | 0 | 1.26 | 0.000464 | -0.00522 | CFL | AllSpc | 1120 | 0.364 | 1120 | 0.364 | 1.13 | 1.27 | -0.00466
CFLAllSpcSDGEPrExCZ07 | Com-Iltg-dWatt-CFL_OSspc | SDG | EPr | Ex | CZ07 | 1.12 | 0.000364 | 0 | 1.26 | 0.000468 | -0.0048 | 1.12 | 0.000364 | 0 | 1.26 | 0.000468 | -0.0048 | CFL | AllSpc | 1120 | 0.364 | 1120 | 0.364 | 1.13 | 1.29 | -0.00429
CFLAllSpcSCEEPrExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCE | EPr | Ex | CZ08 | 1.12 | 0.000364 | 0 | 1.28 | 0.000469 | -0.00439 | 1.12 | 0.000364 | 0 | 1.28 | 0.000469 | -0.00439 | CFL | AllSpc | 1120 | 0.364 | 1120 | 0.364 | 1.14 | 1.29 | -0.00392
CFLAllSpcSDGEPrExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SDG | EPr | Ex | CZ08 | 1.12 | 0.000364 | 0 | 1.28 | 0.000469 | -0.00439 | 1.12 | 0.000364 | 0 | 1.28 | 0.000469 | -0.00439 | CFL | AllSpc | 1120 | 0.364 | 1120 | 0.364 | 1.14 | 1.29 | -0.00392
CFLAllSpcSCGEPrExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCG | EPr | Ex | CZ08 | 1.12 | 0.000364 | 0 | 1.28 | 0.000469 | -0.00439 | 1.12 | 0.000364 | 0 | 1.28 | 0.000469 | -0.00439 | CFL | AllSpc | 1120 | 0.364 | 1120 | 0.364 | 1.14 | 1.29 | -0.00392
CFLAllSpcSCGEPrExCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCG | EPr | Ex | CZ09 | 1.12 | 0.000364 | 0 | 1.29 | 0.000474 | -0.00519 | 1.12 | 0.000364 | 0 | 1.29 | 0.000474 | -0.00519 | CFL | AllSpc | 1120 | 0.364 | 1120 | 0.364 | 1.15 | 1.3 | -0.00463
CFLAllSpcSCEEPrExCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCE | EPr | Ex | CZ09 | 1.12 | 0.000364 | 0 | 1.29 | 0.000474 | -0.00519 | 1.12 | 0.000364 | 0 | 1.29 | 0.000474 | -0.00519 | CFL | AllSpc | 1120 | 0.364 | 1120 | 0.364 | 1.15 | 1.3 | -0.00463
CFLAllSpcSDGEPrExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SDG | EPr | Ex | CZ10 | 1.12 | 0.000364 | 0 | 1.27 | 0.000464 | -0.00552 | 1.12 | 0.000364 | 0 | 1.27 | 0.000464 | -0.00552 | CFL | AllSpc | 1120 | 0.364 | 1120 | 0.364 | 1.13 | 1.27 | -0.00493
CFLAllSpcSCGEPrExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCG | EPr | Ex | CZ10 | 1.12 | 0.000364 | 0 | 1.27 | 0.000464 | -0.00552 | 1.12 | 0.000364 | 0 | 1.27 | 0.000464 | -0.00552 | CFL | AllSpc | 1120 | 0.364 | 1120 | 0.364 | 1.13 | 1.27 | -0.00493
CFLAllSpcSCEEPrExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCE | EPr | Ex | CZ10 | 1.12 | 0.000364 | 0 | 1.27 | 0.000464 | -0.00552 | 1.12 | 0.000364 | 0 | 1.27 | 0.000464 | -0.00552 | CFL | AllSpc | 1120 | 0.364 | 1120 | 0.364 | 1.13 | 1.27 | -0.00493
CFLAllSpcPGEEPrExCZ11 | Com-Iltg-dWatt-CFL_OSspc | PGE | EPr | Ex | CZ11 | 1.12 | 1.16e-05 | 0 | 1.19 | 1.16e-05 | -0.0111 | 1.12 | 1.16e-05 | 0 | 1.19 | 1.16e-05 | -0.0111 | CFL | AllSpc | 1120 | 0.0116 | 1120 | 0.0116 | 1.06 | 1 | -0.00991
CFLAllSpcPGEEPrExCZ12 | Com-Iltg-dWatt-CFL_OSspc | PGE | EPr | Ex | CZ12 | 1.12 | 1.16e-05 | 0 | 1.19 | 1.16e-05 | -0.0115 | 1.12 | 1.16e-05 | 0 | 1.19 | 1.16e-05 | -0.0115 | CFL | AllSpc | 1120 | 0.0116 | 1120 | 0.0116 | 1.06 | 1 | -0.0103
CFLAllSpcSCGEPrExCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCG | EPr | Ex | CZ13 | 1.12 | 1.16e-05 | 0 | 1.22 | 1.16e-05 | -0.00932 | 1.12 | 1.16e-05 | 0 | 1.22 | 1.16e-05 | -0.00932 | CFL | AllSpc | 1120 | 0.0116 | 1120 | 0.0116 | 1.09 | 1 | -0.00832
CFLAllSpcSCEEPrExCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCE | EPr | Ex | CZ13 | 1.12 | 1.16e-05 | 0 | 1.22 | 1.16e-05 | -0.00932 | 1.12 | 1.16e-05 | 0 | 1.22 | 1.16e-05 | -0.00932 | CFL | AllSpc | 1120 | 0.0116 | 1120 | 0.0116 | 1.09 | 1 | -0.00832
CFLAllSpcPGEEPrExCZ13 | Com-Iltg-dWatt-CFL_OSspc | PGE | EPr | Ex | CZ13 | 1.12 | 1.16e-05 | 0 | 1.22 | 1.16e-05 | -0.00932 | 1.12 | 1.16e-05 | 0 | 1.22 | 1.16e-05 | -0.00932 | CFL | AllSpc | 1120 | 0.0116 | 1120 | 0.0116 | 1.09 | 1 | -0.00832
CFLAllSpcSCGEPrExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCG | EPr | Ex | CZ14 | 1.12 | 0.000364 | 0 | 1.22 | 0.000465 | -0.0092 | 1.12 | 0.000364 | 0 | 1.22 | 0.000465 | -0.0092 | CFL | AllSpc | 1120 | 0.364 | 1120 | 0.364 | 1.09 | 1.28 | -0.00821
CFLAllSpcSCEEPrExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCE | EPr | Ex | CZ14 | 1.12 | 0.000364 | 0 | 1.22 | 0.000465 | -0.0092 | 1.12 | 0.000364 | 0 | 1.22 | 0.000465 | -0.0092 | CFL | AllSpc | 1120 | 0.364 | 1120 | 0.364 | 1.09 | 1.28 | -0.00821
CFLAllSpcSDGEPrExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SDG | EPr | Ex | CZ14 | 1.12 | 0.000364 | 0 | 1.22 | 0.000465 | -0.0092 | 1.12 | 0.000364 | 0 | 1.22 | 0.000465 | -0.0092 | CFL | AllSpc | 1120 | 0.364 | 1120 | 0.364 | 1.09 | 1.28 | -0.00821
CFLAllSpcSCEEPrExCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCE | EPr | Ex | CZ15 | 1.12 | 0.000364 | 0 | 1.36 | 0.000467 | -0.00234 | 1.12 | 0.000364 | 0 | 1.36 | 0.000467 | -0.00234 | CFL | AllSpc | 1120 | 0.364 | 1120 | 0.364 | 1.21 | 1.28 | -0.00209
CFLAllSpcSCGEPrExCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCG | EPr | Ex | CZ15 | 1.12 | 0.000364 | 0 | 1.36 | 0.000467 | -0.00234 | 1.12 | 0.000364 | 0 | 1.36 | 0.000467 | -0.00234 | CFL | AllSpc | 1120 | 0.364 | 1120 | 0.364 | 1.21 | 1.28 | -0.00209
CFLAllSpcSDGEPrExCZ15 | Com-Iltg-dWatt-CFL_OSspc | SDG | EPr | Ex | CZ15 | 1.12 | 0.000364 | 0 | 1.36 | 0.000467 | -0.00234 | 1.12 | 0.000364 | 0 | 1.36 | 0.000467 | -0.00234 | CFL | AllSpc | 1120 | 0.364 | 1120 | 0.364 | 1.21 | 1.28 | -0.00209
CFLAllSpcSCEEPrExCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCE | EPr | Ex | CZ16 | 1.12 | 1.16e-05 | 0 | 1.08 | 1.16e-05 | -0.0184 | 1.12 | 1.16e-05 | 0 | 1.08 | 1.16e-05 | -0.0184 | CFL | AllSpc | 1120 | 0.0116 | 1120 | 0.0116 | 0.964 | 1 | -0.0164
CFLAllSpcPGEEPrExCZ16 | Com-Iltg-dWatt-CFL_OSspc | PGE | EPr | Ex | CZ16 | 1.12 | 1.16e-05 | 0 | 1.08 | 1.16e-05 | -0.0184 | 1.12 | 1.16e-05 | 0 | 1.08 | 1.16e-05 | -0.0184 | CFL | AllSpc | 1120 | 0.0116 | 1120 | 0.0116 | 0.964 | 1 | -0.0164
CFLAllSpcSCGEPrExCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCG | EPr | Ex | CZ16 | 1.12 | 1.16e-05 | 0 | 1.08 | 1.16e-05 | -0.0184 | 1.12 | 1.16e-05 | 0 | 1.08 | 1.16e-05 | -0.0184 | CFL | AllSpc | 1120 | 0.0116 | 1120 | 0.0116 | 0.964 | 1 | -0.0164
CFLAllSpcSCEEPrExIOU | Com-Iltg-dWatt-CFL_OSspc | SCE | EPr | Ex | IOU | 1.12 | 0.000341 | 0 | 1.27 | 0.000438 | -0.00568 | 1.12 | 0.000341 | 0 | 1.27 | 0.000438 | -0.00568 | CFL | AllSpc | 1120 | 0.341 | 1120 | 0.341 | 1.13 | 1.28 | -0.00507
CFLAllSpcPGEEPrExIOU | Com-Iltg-dWatt-CFL_OSspc | PGE | EPr | Ex | IOU | 1.12 | 7.36e-05 | 0 | 1.2 | 8.82e-05 | -0.011 | 1.12 | 7.36e-05 | 0 | 1.2 | 8.82e-05 | -0.011 | CFL | AllSpc | 1120 | 0.0736 | 1120 | 0.0736 | 1.07 | 1.2 | -0.00982
CFLAllSpcSCGEPrExIOU | Com-Iltg-dWatt-CFL_OSspc | SCG | EPr | Ex | IOU | 1.12 | 0.000345 | 0 | 1.27 | 0.000444 | -0.00555 | 1.12 | 0.000345 | 0 | 1.27 | 0.000444 | -0.00555 | CFL | AllSpc | 1120 | 0.345 | 1120 | 0.345 | 1.13 | 1.29 | -0.00496
CFLAllSpcSDGEPrExIOU | Com-Iltg-dWatt-CFL_OSspc | SDG | EPr | Ex | IOU | 1.12 | 0.000364 | 0 | 1.26 | 0.000467 | -0.00507 | 1.12 | 0.000364 | 0 | 1.26 | 0.000467 | -0.00507 | CFL | AllSpc | 1120 | 0.364 | 1120 | 0.364 | 1.13 | 1.28 | -0.00453
CFLAllSpcPGEEPrNewCZ01 | Com-Iltg-dWatt-CFL_OSspc | PGE | EPr | New | CZ01 | 1.12 | 0.000368 | 0 | 1.1 | 0.000424 | -0.0239 | 1.12 | 0.000368 | 0 | 1.1 | 0.000424 | -0.0239 | CFL | AllSpc | 1120 | 0.368 | 1120 | 0.368 | 0.982 | 1.15 | -0.0213
CFLAllSpcPGEEPrNewCZ02 | Com-Iltg-dWatt-CFL_OSspc | PGE | EPr | New | CZ02 | 1.12 | 1.17e-05 | 0 | 1.17 | 1.17e-05 | -0.0153 | 1.12 | 1.17e-05 | 0 | 1.17 | 1.17e-05 | -0.0153 | CFL | AllSpc | 1120 | 0.0117 | 1120 | 0.0117 | 1.04 | 1 | -0.0137
CFLAllSpcPGEEPrNewCZ03 | Com-Iltg-dWatt-CFL_OSspc | PGE | EPr | New | CZ03 | 1.12 | 1.17e-05 | 0 | 1.15 | 1.17e-05 | -0.0146 | 1.12 | 1.17e-05 | 0 | 1.15 | 1.17e-05 | -0.0146 | CFL | AllSpc | 1120 | 0.0117 | 1120 | 0.0117 | 1.03 | 1 | -0.013
CFLAllSpcPGEEPrNewCZ04 | Com-Iltg-dWatt-CFL_OSspc | PGE | EPr | New | CZ04 | 1.12 | 0.000368 | 0 | 1.19 | 0.000478 | -0.0119 | 1.12 | 0.000368 | 0 | 1.19 | 0.000478 | -0.0119 | CFL | AllSpc | 1120 | 0.368 | 1120 | 0.368 | 1.06 | 1.3 | -0.0106
CFLAllSpcSCEEPrNewCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCE | EPr | New | CZ05 | 1.12 | 0.000368 | 0 | 1.17 | 0.000474 | -0.0111 | 1.12 | 0.000368 | 0 | 1.17 | 0.000474 | -0.0111 | CFL | AllSpc | 1120 | 0.368 | 1120 | 0.368 | 1.04 | 1.29 | -0.00991
CFLAllSpcPGEEPrNewCZ05 | Com-Iltg-dWatt-CFL_OSspc | PGE | EPr | New | CZ05 | 1.12 | 0.000368 | 0 | 1.16 | 0.000454 | -0.0121 | 1.12 | 0.000368 | 0 | 1.16 | 0.000454 | -0.0121 | CFL | AllSpc | 1120 | 0.368 | 1120 | 0.368 | 1.04 | 1.23 | -0.0108
CFLAllSpcSCEEPrNewCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCE | EPr | New | CZ06 | 1.12 | 0.000368 | 0 | 1.23 | 0.000495 | -0.00703 | 1.12 | 0.000368 | 0 | 1.23 | 0.000495 | -0.00703 | CFL | AllSpc | 1120 | 0.368 | 1120 | 0.368 | 1.1 | 1.35 | -0.00628
CFLAllSpcSDGEPrNewCZ06 | Com-Iltg-dWatt-CFL_OSspc | SDG | EPr | New | CZ06 | 1.12 | 0.000368 | 0 | 1.23 | 0.000492 | -0.00711 | 1.12 | 0.000368 | 0 | 1.23 | 0.000492 | -0.00711 | CFL | AllSpc | 1120 | 0.368 | 1120 | 0.368 | 1.1 | 1.34 | -0.00635
CFLAllSpcSDGEPrNewCZ07 | Com-Iltg-dWatt-CFL_OSspc | SDG | EPr | New | CZ07 | 1.12 | 0.000368 | 0 | 1.21 | 0.000487 | -0.00662 | 1.12 | 0.000368 | 0 | 1.21 | 0.000487 | -0.00662 | CFL | AllSpc | 1120 | 0.368 | 1120 | 0.368 | 1.08 | 1.32 | -0.00591
CFLAllSpcSCEEPrNewCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCE | EPr | New | CZ08 | 1.12 | 0.000368 | 0 | 1.25 | 0.000509 | -0.00604 | 1.12 | 0.000368 | 0 | 1.25 | 0.000509 | -0.00604 | CFL | AllSpc | 1120 | 0.368 | 1120 | 0.368 | 1.12 | 1.38 | -0.00539
CFLAllSpcSDGEPrNewCZ08 | Com-Iltg-dWatt-CFL_OSspc | SDG | EPr | New | CZ08 | 1.12 | 0.000368 | 0 | 1.25 | 0.000506 | -0.0061 | 1.12 | 0.000368 | 0 | 1.25 | 0.000506 | -0.0061 | CFL | AllSpc | 1120 | 0.368 | 1120 | 0.368 | 1.12 | 1.38 | -0.00545
CFLAllSpcSCEEPrNewCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCE | EPr | New | CZ09 | 1.12 | 0.000368 | 0 | 1.25 | 0.00052 | -0.00685 | 1.12 | 0.000368 | 0 | 1.25 | 0.00052 | -0.00685 | CFL | AllSpc | 1120 | 0.368 | 1120 | 0.368 | 1.12 | 1.41 | -0.00612
CFLAllSpcSDGEPrNewCZ10 | Com-Iltg-dWatt-CFL_OSspc | SDG | EPr | New | CZ10 | 1.12 | 0.000368 | 0 | 1.25 | 0.000524 | -0.00736 | 1.12 | 0.000368 | 0 | 1.25 | 0.000524 | -0.00736 | CFL | AllSpc | 1120 | 0.368 | 1120 | 0.368 | 1.12 | 1.42 | -0.00657
CFLAllSpcSCEEPrNewCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCE | EPr | New | CZ10 | 1.12 | 0.000368 | 0 | 1.25 | 0.000528 | -0.00727 | 1.12 | 0.000368 | 0 | 1.25 | 0.000528 | -0.00727 | CFL | AllSpc | 1120 | 0.368 | 1120 | 0.368 | 1.12 | 1.43 | -0.00649
CFLAllSpcPGEEPrNewCZ11 | Com-Iltg-dWatt-CFL_OSspc | PGE | EPr | New | CZ11 | 1.12 | 1.17e-05 | 0 | 1.2 | 1.17e-05 | -0.0134 | 1.12 | 1.17e-05 | 0 | 1.2 | 1.17e-05 | -0.0134 | CFL | AllSpc | 1120 | 0.0117 | 1120 | 0.0117 | 1.07 | 1 | -0.012
CFLAllSpcPGEEPrNewCZ12 | Com-Iltg-dWatt-CFL_OSspc | PGE | EPr | New | CZ12 | 1.12 | 1.17e-05 | 0 | 1.19 | 1.17e-05 | -0.0138 | 1.12 | 1.17e-05 | 0 | 1.19 | 1.17e-05 | -0.0138 | CFL | AllSpc | 1120 | 0.0117 | 1120 | 0.0117 | 1.06 | 1 | -0.0123
CFLAllSpcSCEEPrNewCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCE | EPr | New | CZ13 | 1.12 | 1.17e-05 | 0 | 1.23 | 1.17e-05 | -0.0114 | 1.12 | 1.17e-05 | 0 | 1.23 | 1.17e-05 | -0.0114 | CFL | AllSpc | 1120 | 0.0117 | 1120 | 0.0117 | 1.1 | 1 | -0.0102
CFLAllSpcPGEEPrNewCZ13 | Com-Iltg-dWatt-CFL_OSspc | PGE | EPr | New | CZ13 | 1.12 | 1.17e-05 | 0 | 1.21 | 1.17e-05 | -0.0123 | 1.12 | 1.17e-05 | 0 | 1.21 | 1.17e-05 | -0.0123 | CFL | AllSpc | 1120 | 0.0117 | 1120 | 0.0117 | 1.08 | 1 | -0.011
CFLAllSpcSDGEPrNewCZ14 | Com-Iltg-dWatt-CFL_OSspc | SDG | EPr | New | CZ14 | 1.12 | 0.000368 | 0 | 1.23 | 0.000513 | -0.0115 | 1.12 | 0.000368 | 0 | 1.23 | 0.000513 | -0.0115 | CFL | AllSpc | 1120 | 0.368 | 1120 | 0.368 | 1.1 | 1.39 | -0.0103
CFLAllSpcSCEEPrNewCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCE | EPr | New | CZ14 | 1.12 | 0.000368 | 0 | 1.23 | 0.000517 | -0.0114 | 1.12 | 0.000368 | 0 | 1.23 | 0.000517 | -0.0114 | CFL | AllSpc | 1120 | 0.368 | 1120 | 0.368 | 1.1 | 1.4 | -0.0102
CFLAllSpcSDGEPrNewCZ15 | Com-Iltg-dWatt-CFL_OSspc | SDG | EPr | New | CZ15 | 1.12 | 0.000368 | 0 | 1.36 | 0.00053 | -0.00321 | 1.12 | 0.000368 | 0 | 1.36 | 0.00053 | -0.00321 | CFL | AllSpc | 1120 | 0.368 | 1120 | 0.368 | 1.21 | 1.44 | -0.00287
CFLAllSpcSCEEPrNewCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCE | EPr | New | CZ15 | 1.12 | 0.000368 | 0 | 1.36 | 0.000535 | -0.00318 | 1.12 | 0.000368 | 0 | 1.36 | 0.000535 | -0.00318 | CFL | AllSpc | 1120 | 0.368 | 1120 | 0.368 | 1.21 | 1.45 | -0.00284
CFLAllSpcPGEEPrNewCZ16 | Com-Iltg-dWatt-CFL_OSspc | PGE | EPr | New | CZ16 | 1.12 | 1.17e-05 | 0 | 1.12 | 1.17e-05 | -0.0176 | 1.12 | 1.17e-05 | 0 | 1.12 | 1.17e-05 | -0.0176 | CFL | AllSpc | 1120 | 0.0117 | 1120 | 0.0117 | 1 | 1 | -0.0157
CFLAllSpcSCEEPrNewCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCE | EPr | New | CZ16 | 1.12 | 1.17e-05 | 0 | 1.1 | 1.17e-05 | -0.0164 | 1.12 | 1.17e-05 | 0 | 1.1 | 1.17e-05 | -0.0164 | CFL | AllSpc | 1120 | 0.0117 | 1120 | 0.0117 | 0.982 | 1 | -0.0146
CFLAllSpcSCGEPrNewIOU | Com-Iltg-dWatt-CFL_OSspc | SCG | EPr | New | IOU | 1.12 | 0.000368 | 0 | 1.25 | 0.000513 | -0.00718 | 1.12 | 0.000368 | 0 | 1.25 | 0.000513 | -0.00718 | CFL | AllSpc | 1120 | 0.368 | 1120 | 0.368 | 1.12 | 1.39 | -0.00641
CFLAllSpcSCEEPrNewIOU | Com-Iltg-dWatt-CFL_OSspc | SCE | EPr | New | IOU | 1.12 | 0.000368 | 0 | 1.25 | 0.000513 | -0.00722 | 1.12 | 0.000368 | 0 | 1.25 | 0.000513 | -0.00722 | CFL | AllSpc | 1120 | 0.368 | 1120 | 0.368 | 1.12 | 1.39 | -0.00645
CFLAllSpcSDGEPrNewIOU | Com-Iltg-dWatt-CFL_OSspc | SDG | EPr | New | IOU | 1.12 | 0.000368 | 0 | 1.23 | 0.000501 | -0.00689 | 1.12 | 0.000368 | 0 | 1.23 | 0.000501 | -0.00689 | CFL | AllSpc | 1120 | 0.368 | 1120 | 0.368 | 1.1 | 1.36 | -0.00615
CFLAllSpcPGEEPrNewIOU | Com-Iltg-dWatt-CFL_OSspc | PGE | EPr | New | IOU | 1.12 | 3.37e-05 | 0 | 1.22 | 4.02e-05 | -0.0116 | 1.12 | 3.37e-05 | 0 | 1.22 | 4.02e-05 | -0.0116 | CFL | AllSpc | 1120 | 0.0337 | 1120 | 0.0337 | 1.09 | 1.19 | -0.0104
CFLAllSpcPGEERCExCZ01 | Com-Iltg-dWatt-CFL_OSspc | PGE | ERC | Ex | CZ01 | 0.998 | 0.000371 | 0 | 0.969 | 0.00044 | -0.0167 | 0.998 | 0.000371 | 0 | 0.969 | 0.00044 | -0.0167 | CFL | AllSpc | 998 | 0.371 | 998 | 0.371 | 0.971 | 1.19 | -0.0167
CFLAllSpcPGEERCExCZ02 | Com-Iltg-dWatt-CFL_OSspc | PGE | ERC | Ex | CZ02 | 0.998 | 1.07e-05 | 0 | 1.01 | 1.07e-05 | -0.012 | 0.998 | 1.07e-05 | 0 | 1.01 | 1.07e-05 | -0.012 | CFL | AllSpc | 998 | 0.0107 | 998 | 0.0107 | 1.01 | 1 | -0.012
CFLAllSpcPGEERCExCZ03 | Com-Iltg-dWatt-CFL_OSspc | PGE | ERC | Ex | CZ03 | 0.998 | 1.07e-05 | 0 | 1.01 | 1.07e-05 | -0.0112 | 0.998 | 1.07e-05 | 0 | 1.01 | 1.07e-05 | -0.0112 | CFL | AllSpc | 998 | 0.0107 | 998 | 0.0107 | 1.01 | 1 | -0.0112
CFLAllSpcPGEERCExCZ04 | Com-Iltg-dWatt-CFL_OSspc | PGE | ERC | Ex | CZ04 | 0.998 | 0.000371 | 0 | 1.04 | 0.000446 | -0.00935 | 0.998 | 0.000371 | 0 | 1.04 | 0.000446 | -0.00935 | CFL | AllSpc | 998 | 0.371 | 998 | 0.371 | 1.04 | 1.2 | -0.00937
CFLAllSpcSCEERCExCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCE | ERC | Ex | CZ05 | 0.998 | 0.000371 | 0 | 1.04 | 0.000464 | -0.0102 | 0.998 | 0.000371 | 0 | 1.04 | 0.000464 | -0.0102 | CFL | AllSpc | 998 | 0.371 | 998 | 0.371 | 1.04 | 1.25 | -0.0102
CFLAllSpcPGEERCExCZ05 | Com-Iltg-dWatt-CFL_OSspc | PGE | ERC | Ex | CZ05 | 0.998 | 0.000371 | 0 | 1.04 | 0.000464 | -0.0102 | 0.998 | 0.000371 | 0 | 1.04 | 0.000464 | -0.0102 | CFL | AllSpc | 998 | 0.371 | 998 | 0.371 | 1.04 | 1.25 | -0.0102
CFLAllSpcSCGERCExCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCG | ERC | Ex | CZ05 | 0.998 | 0.000371 | 0 | 1.04 | 0.000464 | -0.0102 | 0.998 | 0.000371 | 0 | 1.04 | 0.000464 | -0.0102 | CFL | AllSpc | 998 | 0.371 | 998 | 0.371 | 1.04 | 1.25 | -0.0102
CFLAllSpcSDGERCExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SDG | ERC | Ex | CZ06 | 0.998 | 0.000371 | 0 | 1.09 | 0.000462 | -0.00615 | 0.998 | 0.000371 | 0 | 1.09 | 0.000462 | -0.00615 | CFL | AllSpc | 998 | 0.371 | 998 | 0.371 | 1.09 | 1.25 | -0.00616
CFLAllSpcSCGERCExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCG | ERC | Ex | CZ06 | 0.998 | 0.000371 | 0 | 1.09 | 0.000462 | -0.00615 | 0.998 | 0.000371 | 0 | 1.09 | 0.000462 | -0.00615 | CFL | AllSpc | 998 | 0.371 | 998 | 0.371 | 1.09 | 1.25 | -0.00616
CFLAllSpcSCEERCExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCE | ERC | Ex | CZ06 | 0.998 | 0.000371 | 0 | 1.09 | 0.000462 | -0.00615 | 0.998 | 0.000371 | 0 | 1.09 | 0.000462 | -0.00615 | CFL | AllSpc | 998 | 0.371 | 998 | 0.371 | 1.09 | 1.25 | -0.00616
CFLAllSpcSDGERCExCZ07 | Com-Iltg-dWatt-CFL_OSspc | SDG | ERC | Ex | CZ07 | 0.998 | 0.000371 | 0 | 1.12 | 0.000461 | -0.00492 | 0.998 | 0.000371 | 0 | 1.12 | 0.000461 | -0.00492 | CFL | AllSpc | 998 | 0.371 | 998 | 0.371 | 1.12 | 1.24 | -0.00493
CFLAllSpcSCGERCExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCG | ERC | Ex | CZ08 | 0.998 | 0.000371 | 0 | 1.11 | 0.000467 | -0.00539 | 0.998 | 0.000371 | 0 | 1.11 | 0.000467 | -0.00539 | CFL | AllSpc | 998 | 0.371 | 998 | 0.371 | 1.11 | 1.26 | -0.0054
CFLAllSpcSDGERCExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SDG | ERC | Ex | CZ08 | 0.998 | 0.000371 | 0 | 1.11 | 0.000467 | -0.00539 | 0.998 | 0.000371 | 0 | 1.11 | 0.000467 | -0.00539 | CFL | AllSpc | 998 | 0.371 | 998 | 0.371 | 1.11 | 1.26 | -0.0054
CFLAllSpcSCEERCExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCE | ERC | Ex | CZ08 | 0.998 | 0.000371 | 0 | 1.11 | 0.000467 | -0.00539 | 0.998 | 0.000371 | 0 | 1.11 | 0.000467 | -0.00539 | CFL | AllSpc | 998 | 0.371 | 998 | 0.371 | 1.11 | 1.26 | -0.0054
CFLAllSpcSCEERCExCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCE | ERC | Ex | CZ09 | 0.998 | 0.000371 | 0 | 1.11 | 0.000467 | -0.00608 | 0.998 | 0.000371 | 0 | 1.11 | 0.000467 | -0.00608 | CFL | AllSpc | 998 | 0.371 | 998 | 0.371 | 1.11 | 1.26 | -0.00609
CFLAllSpcSCGERCExCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCG | ERC | Ex | CZ09 | 0.998 | 0.000371 | 0 | 1.11 | 0.000467 | -0.00608 | 0.998 | 0.000371 | 0 | 1.11 | 0.000467 | -0.00608 | CFL | AllSpc | 998 | 0.371 | 998 | 0.371 | 1.11 | 1.26 | -0.00609
CFLAllSpcSCGERCExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCG | ERC | Ex | CZ10 | 0.998 | 0.000371 | 0 | 1.09 | 0.000464 | -0.00629 | 0.998 | 0.000371 | 0 | 1.09 | 0.000464 | -0.00629 | CFL | AllSpc | 998 | 0.371 | 998 | 0.371 | 1.09 | 1.25 | -0.0063
CFLAllSpcSCEERCExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCE | ERC | Ex | CZ10 | 0.998 | 0.000371 | 0 | 1.09 | 0.000464 | -0.00629 | 0.998 | 0.000371 | 0 | 1.09 | 0.000464 | -0.00629 | CFL | AllSpc | 998 | 0.371 | 998 | 0.371 | 1.09 | 1.25 | -0.0063
CFLAllSpcSDGERCExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SDG | ERC | Ex | CZ10 | 0.998 | 0.000371 | 0 | 1.09 | 0.000464 | -0.00629 | 0.998 | 0.000371 | 0 | 1.09 | 0.000464 | -0.00629 | CFL | AllSpc | 998 | 0.371 | 998 | 0.371 | 1.09 | 1.25 | -0.0063
CFLAllSpcPGEERCExCZ11 | Com-Iltg-dWatt-CFL_OSspc | PGE | ERC | Ex | CZ11 | 0.998 | 1.07e-05 | 0 | 1.03 | 1.07e-05 | -0.0101 | 0.998 | 1.07e-05 | 0 | 1.03 | 1.07e-05 | -0.0101 | CFL | AllSpc | 998 | 0.0107 | 998 | 0.0107 | 1.03 | 1 | -0.0101
CFLAllSpcPGEERCExCZ12 | Com-Iltg-dWatt-CFL_OSspc | PGE | ERC | Ex | CZ12 | 0.998 | 1.07e-05 | 0 | 1.03 | 1.07e-05 | -0.0107 | 0.998 | 1.07e-05 | 0 | 1.03 | 1.07e-05 | -0.0107 | CFL | AllSpc | 998 | 0.0107 | 998 | 0.0107 | 1.03 | 1 | -0.0107
CFLAllSpcPGEERCExCZ13 | Com-Iltg-dWatt-CFL_OSspc | PGE | ERC | Ex | CZ13 | 0.998 | 1.07e-05 | 0 | 1.08 | 1.07e-05 | -0.00876 | 0.998 | 1.07e-05 | 0 | 1.08 | 1.07e-05 | -0.00876 | CFL | AllSpc | 998 | 0.0107 | 998 | 0.0107 | 1.08 | 1 | -0.00878
CFLAllSpcSCGERCExCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCG | ERC | Ex | CZ13 | 0.998 | 1.07e-05 | 0 | 1.08 | 1.07e-05 | -0.00876 | 0.998 | 1.07e-05 | 0 | 1.08 | 1.07e-05 | -0.00876 | CFL | AllSpc | 998 | 0.0107 | 998 | 0.0107 | 1.08 | 1 | -0.00878
CFLAllSpcSCEERCExCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCE | ERC | Ex | CZ13 | 0.998 | 1.07e-05 | 0 | 1.08 | 1.07e-05 | -0.00876 | 0.998 | 1.07e-05 | 0 | 1.08 | 1.07e-05 | -0.00876 | CFL | AllSpc | 998 | 0.0107 | 998 | 0.0107 | 1.08 | 1 | -0.00878
CFLAllSpcSCGERCExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCG | ERC | Ex | CZ14 | 0.998 | 0.000371 | 0 | 1.09 | 0.000471 | -0.00832 | 0.998 | 0.000371 | 0 | 1.09 | 0.000471 | -0.00832 | CFL | AllSpc | 998 | 0.371 | 998 | 0.371 | 1.09 | 1.27 | -0.00834
CFLAllSpcSDGERCExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SDG | ERC | Ex | CZ14 | 0.998 | 0.000371 | 0 | 1.09 | 0.000471 | -0.00832 | 0.998 | 0.000371 | 0 | 1.09 | 0.000471 | -0.00832 | CFL | AllSpc | 998 | 0.371 | 998 | 0.371 | 1.09 | 1.27 | -0.00834
CFLAllSpcSCEERCExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCE | ERC | Ex | CZ14 | 0.998 | 0.000371 | 0 | 1.09 | 0.000471 | -0.00832 | 0.998 | 0.000371 | 0 | 1.09 | 0.000471 | -0.00832 | CFL | AllSpc | 998 | 0.371 | 998 | 0.371 | 1.09 | 1.27 | -0.00834
CFLAllSpcSDGERCExCZ15 | Com-Iltg-dWatt-CFL_OSspc | SDG | ERC | Ex | CZ15 | 0.998 | 0.000371 | 0 | 1.18 | 0.000478 | -0.00305 | 0.998 | 0.000371 | 0 | 1.18 | 0.000478 | -0.00305 | CFL | AllSpc | 998 | 0.371 | 998 | 0.371 | 1.18 | 1.29 | -0.00306
CFLAllSpcSCGERCExCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCG | ERC | Ex | CZ15 | 0.998 | 0.000371 | 0 | 1.18 | 0.000478 | -0.00305 | 0.998 | 0.000371 | 0 | 1.18 | 0.000478 | -0.00305 | CFL | AllSpc | 998 | 0.371 | 998 | 0.371 | 1.18 | 1.29 | -0.00306
CFLAllSpcSCEERCExCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCE | ERC | Ex | CZ15 | 0.998 | 0.000371 | 0 | 1.18 | 0.000478 | -0.00305 | 0.998 | 0.000371 | 0 | 1.18 | 0.000478 | -0.00305 | CFL | AllSpc | 998 | 0.371 | 998 | 0.371 | 1.18 | 1.29 | -0.00306
CFLAllSpcSCGERCExCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCG | ERC | Ex | CZ16 | 0.998 | 1.07e-05 | 0 | 0.993 | 1.07e-05 | -0.0148 | 0.998 | 1.07e-05 | 0 | 0.993 | 1.07e-05 | -0.0148 | CFL | AllSpc | 998 | 0.0107 | 998 | 0.0107 | 0.995 | 1 | -0.0148
CFLAllSpcPGEERCExCZ16 | Com-Iltg-dWatt-CFL_OSspc | PGE | ERC | Ex | CZ16 | 0.998 | 1.07e-05 | 0 | 0.993 | 1.07e-05 | -0.0148 | 0.998 | 1.07e-05 | 0 | 0.993 | 1.07e-05 | -0.0148 | CFL | AllSpc | 998 | 0.0107 | 998 | 0.0107 | 0.995 | 1 | -0.0148
CFLAllSpcSCEERCExCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCE | ERC | Ex | CZ16 | 0.998 | 1.07e-05 | 0 | 0.993 | 1.07e-05 | -0.0148 | 0.998 | 1.07e-05 | 0 | 0.993 | 1.07e-05 | -0.0148 | CFL | AllSpc | 998 | 0.0107 | 998 | 0.0107 | 0.995 | 1 | -0.0148
CFLAllSpcPGEERCExIOU | Com-Iltg-dWatt-CFL_OSspc | PGE | ERC | Ex | IOU | 0.998 | 7.41e-05 | 0 | 1.03 | 8.76e-05 | -0.0105 | 0.998 | 7.41e-05 | 0 | 1.03 | 8.76e-05 | -0.0105 | CFL | AllSpc | 998 | 0.0741 | 998 | 0.0741 | 1.03 | 1.18 | -0.0105
CFLAllSpcSDGERCExIOU | Com-Iltg-dWatt-CFL_OSspc | SDG | ERC | Ex | IOU | 0.998 | 0.000371 | 0 | 1.11 | 0.000462 | -0.00548 | 0.998 | 0.000371 | 0 | 1.11 | 0.000462 | -0.00548 | CFL | AllSpc | 998 | 0.371 | 998 | 0.371 | 1.11 | 1.25 | -0.00549
CFLAllSpcSCGERCExIOU | Com-Iltg-dWatt-CFL_OSspc | SCG | ERC | Ex | IOU | 0.998 | 0.000352 | 0 | 1.1 | 0.000442 | -0.00624 | 0.998 | 0.000352 | 0 | 1.1 | 0.000442 | -0.00624 | CFL | AllSpc | 998 | 0.352 | 998 | 0.352 | 1.1 | 1.26 | -0.00625
CFLAllSpcSCEERCExIOU | Com-Iltg-dWatt-CFL_OSspc | SCE | ERC | Ex | IOU | 0.998 | 0.000347 | 0 | 1.1 | 0.000436 | -0.00631 | 0.998 | 0.000347 | 0 | 1.1 | 0.000436 | -0.00631 | CFL | AllSpc | 998 | 0.347 | 998 | 0.347 | 1.1 | 1.26 | -0.00632
CFLAllSpcPGEERCNewCZ01 | Com-Iltg-dWatt-CFL_OSspc | PGE | ERC | New | CZ01 | 0.998 | 0.000376 | 0 | 1.03 | 0.000445 | -0.0197 | 0.998 | 0.000376 | 0 | 1.03 | 0.000445 | -0.0197 | CFL | AllSpc | 998 | 0.376 | 998 | 0.376 | 1.03 | 1.18 | -0.0197
CFLAllSpcPGEERCNewCZ02 | Com-Iltg-dWatt-CFL_OSspc | PGE | ERC | New | CZ02 | 0.998 | 1.09e-05 | 0 | 1.07 | 1.09e-05 | -0.013 | 0.998 | 1.09e-05 | 0 | 1.07 | 1.09e-05 | -0.013 | CFL | AllSpc | 998 | 0.0109 | 998 | 0.0109 | 1.07 | 1 | -0.013
CFLAllSpcPGEERCNewCZ03 | Com-Iltg-dWatt-CFL_OSspc | PGE | ERC | New | CZ03 | 0.998 | 1.09e-05 | 0 | 1.07 | 1.09e-05 | -0.0119 | 0.998 | 1.09e-05 | 0 | 1.07 | 1.09e-05 | -0.0119 | CFL | AllSpc | 998 | 0.0109 | 998 | 0.0109 | 1.07 | 1 | -0.0119
CFLAllSpcPGEERCNewCZ04 | Com-Iltg-dWatt-CFL_OSspc | PGE | ERC | New | CZ04 | 0.998 | 0.000376 | 0 | 1.1 | 0.000475 | -0.0103 | 0.998 | 0.000376 | 0 | 1.1 | 0.000475 | -0.0103 | CFL | AllSpc | 998 | 0.376 | 998 | 0.376 | 1.1 | 1.26 | -0.0103
CFLAllSpcPGEERCNewCZ05 | Com-Iltg-dWatt-CFL_OSspc | PGE | ERC | New | CZ05 | 0.998 | 0.000376 | 0 | 1.07 | 0.000482 | -0.0114 | 0.998 | 0.000376 | 0 | 1.07 | 0.000482 | -0.0114 | CFL | AllSpc | 998 | 0.376 | 998 | 0.376 | 1.07 | 1.28 | -0.0114
CFLAllSpcSCEERCNewCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCE | ERC | New | CZ05 | 0.998 | 0.000376 | 0 | 1.08 | 0.000506 | -0.0105 | 0.998 | 0.000376 | 0 | 1.08 | 0.000506 | -0.0105 | CFL | AllSpc | 998 | 0.376 | 998 | 0.376 | 1.08 | 1.35 | -0.0105
CFLAllSpcSCEERCNewCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCE | ERC | New | CZ06 | 0.998 | 0.000376 | 0 | 1.14 | 0.000484 | -0.00672 | 0.998 | 0.000376 | 0 | 1.14 | 0.000484 | -0.00672 | CFL | AllSpc | 998 | 0.376 | 998 | 0.376 | 1.14 | 1.29 | -0.00673
CFLAllSpcSDGERCNewCZ06 | Com-Iltg-dWatt-CFL_OSspc | SDG | ERC | New | CZ06 | 0.998 | 0.000376 | 0 | 1.14 | 0.000481 | -0.0068 | 0.998 | 0.000376 | 0 | 1.14 | 0.000481 | -0.0068 | CFL | AllSpc | 998 | 0.376 | 998 | 0.376 | 1.14 | 1.28 | -0.00681
CFLAllSpcSDGERCNewCZ07 | Com-Iltg-dWatt-CFL_OSspc | SDG | ERC | New | CZ07 | 0.998 | 0.000376 | 0 | 1.14 | 0.000474 | -0.00525 | 0.998 | 0.000376 | 0 | 1.14 | 0.000474 | -0.00525 | CFL | AllSpc | 998 | 0.376 | 998 | 0.376 | 1.14 | 1.26 | -0.00526
CFLAllSpcSDGERCNewCZ08 | Com-Iltg-dWatt-CFL_OSspc | SDG | ERC | New | CZ08 | 0.998 | 0.000376 | 0 | 1.15 | 0.000493 | -0.00592 | 0.998 | 0.000376 | 0 | 1.15 | 0.000493 | -0.00592 | CFL | AllSpc | 998 | 0.376 | 998 | 0.376 | 1.15 | 1.31 | -0.00593
CFLAllSpcSCEERCNewCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCE | ERC | New | CZ08 | 0.998 | 0.000376 | 0 | 1.16 | 0.000496 | -0.00586 | 0.998 | 0.000376 | 0 | 1.16 | 0.000496 | -0.00586 | CFL | AllSpc | 998 | 0.376 | 998 | 0.376 | 1.16 | 1.32 | -0.00587
CFLAllSpcSCEERCNewCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCE | ERC | New | CZ09 | 0.998 | 0.000376 | 0 | 1.16 | 0.000509 | -0.0063 | 0.998 | 0.000376 | 0 | 1.16 | 0.000509 | -0.0063 | CFL | AllSpc | 998 | 0.376 | 998 | 0.376 | 1.16 | 1.35 | -0.00631
CFLAllSpcSDGERCNewCZ10 | Com-Iltg-dWatt-CFL_OSspc | SDG | ERC | New | CZ10 | 0.998 | 0.000376 | 0 | 1.16 | 0.000515 | -0.00673 | 0.998 | 0.000376 | 0 | 1.16 | 0.000515 | -0.00673 | CFL | AllSpc | 998 | 0.376 | 998 | 0.376 | 1.16 | 1.37 | -0.00674
CFLAllSpcSCEERCNewCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCE | ERC | New | CZ10 | 0.998 | 0.000376 | 0 | 1.16 | 0.000519 | -0.00665 | 0.998 | 0.000376 | 0 | 1.16 | 0.000519 | -0.00665 | CFL | AllSpc | 998 | 0.376 | 998 | 0.376 | 1.16 | 1.38 | -0.00666
CFLAllSpcPGEERCNewCZ11 | Com-Iltg-dWatt-CFL_OSspc | PGE | ERC | New | CZ11 | 0.998 | 1.09e-05 | 0 | 1.12 | 1.09e-05 | -0.0119 | 0.998 | 1.09e-05 | 0 | 1.12 | 1.09e-05 | -0.0119 | CFL | AllSpc | 998 | 0.0109 | 998 | 0.0109 | 1.12 | 1 | -0.0119
CFLAllSpcPGEERCNewCZ12 | Com-Iltg-dWatt-CFL_OSspc | PGE | ERC | New | CZ12 | 0.998 | 1.09e-05 | 0 | 1.1 | 1.09e-05 | -0.0121 | 0.998 | 1.09e-05 | 0 | 1.1 | 1.09e-05 | -0.0121 | CFL | AllSpc | 998 | 0.0109 | 998 | 0.0109 | 1.1 | 1 | -0.0121
CFLAllSpcPGEERCNewCZ13 | Com-Iltg-dWatt-CFL_OSspc | PGE | ERC | New | CZ13 | 0.998 | 1.09e-05 | 0 | 1.12 | 1.09e-05 | -0.0106 | 0.998 | 1.09e-05 | 0 | 1.12 | 1.09e-05 | -0.0106 | CFL | AllSpc | 998 | 0.0109 | 998 | 0.0109 | 1.12 | 1 | -0.0106
CFLAllSpcSCEERCNewCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCE | ERC | New | CZ13 | 0.998 | 1.09e-05 | 0 | 1.15 | 1.09e-05 | -0.00973 | 0.998 | 1.09e-05 | 0 | 1.15 | 1.09e-05 | -0.00973 | CFL | AllSpc | 998 | 0.0109 | 998 | 0.0109 | 1.15 | 1 | -0.00975
CFLAllSpcSDGERCNewCZ14 | Com-Iltg-dWatt-CFL_OSspc | SDG | ERC | New | CZ14 | 0.998 | 0.000376 | 0 | 1.14 | 0.000507 | -0.00977 | 0.998 | 0.000376 | 0 | 1.14 | 0.000507 | -0.00977 | CFL | AllSpc | 998 | 0.376 | 998 | 0.376 | 1.14 | 1.35 | -0.00979
CFLAllSpcSCEERCNewCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCE | ERC | New | CZ14 | 0.998 | 0.000376 | 0 | 1.15 | 0.000511 | -0.00965 | 0.998 | 0.000376 | 0 | 1.15 | 0.000511 | -0.00965 | CFL | AllSpc | 998 | 0.376 | 998 | 0.376 | 1.15 | 1.36 | -0.00967
CFLAllSpcSCEERCNewCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCE | ERC | New | CZ15 | 0.998 | 0.000376 | 0 | 1.27 | 0.00052 | -0.00333 | 0.998 | 0.000376 | 0 | 1.27 | 0.00052 | -0.00333 | CFL | AllSpc | 998 | 0.376 | 998 | 0.376 | 1.27 | 1.38 | -0.00334
CFLAllSpcSDGERCNewCZ15 | Com-Iltg-dWatt-CFL_OSspc | SDG | ERC | New | CZ15 | 0.998 | 0.000376 | 0 | 1.26 | 0.000515 | -0.00337 | 0.998 | 0.000376 | 0 | 1.26 | 0.000515 | -0.00337 | CFL | AllSpc | 998 | 0.376 | 998 | 0.376 | 1.26 | 1.37 | -0.00338
CFLAllSpcPGEERCNewCZ16 | Com-Iltg-dWatt-CFL_OSspc | PGE | ERC | New | CZ16 | 0.998 | 1.09e-05 | 0 | 1.02 | 1.09e-05 | -0.0184 | 0.998 | 1.09e-05 | 0 | 1.02 | 1.09e-05 | -0.0184 | CFL | AllSpc | 998 | 0.0109 | 998 | 0.0109 | 1.02 | 1 | -0.0184
CFLAllSpcSCEERCNewCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCE | ERC | New | CZ16 | 0.998 | 1.09e-05 | 0 | 1.02 | 1.09e-05 | -0.0171 | 0.998 | 1.09e-05 | 0 | 1.02 | 1.09e-05 | -0.0171 | CFL | AllSpc | 998 | 0.0109 | 998 | 0.0109 | 1.02 | 1 | -0.0171
CFLAllSpcPGEERCNewIOU | Com-Iltg-dWatt-CFL_OSspc | PGE | ERC | New | IOU | 0.998 | 3.34e-05 | 0 | 1.14 | 4.14e-05 | -0.0102 | 0.998 | 3.34e-05 | 0 | 1.14 | 4.14e-05 | -0.0102 | CFL | AllSpc | 998 | 0.0334 | 998 | 0.0334 | 1.14 | 1.24 | -0.0102
CFLAllSpcSCEERCNewIOU | Com-Iltg-dWatt-CFL_OSspc | SCE | ERC | New | IOU | 0.998 | 0.000376 | 0 | 1.16 | 0.000503 | -0.00669 | 0.998 | 0.000376 | 0 | 1.16 | 0.000503 | -0.00669 | CFL | AllSpc | 998 | 0.376 | 998 | 0.376 | 1.16 | 1.34 | -0.0067
CFLAllSpcSDGERCNewIOU | Com-Iltg-dWatt-CFL_OSspc | SDG | ERC | New | IOU | 0.998 | 0.000376 | 0 | 1.15 | 0.000489 | -0.00588 | 0.998 | 0.000376 | 0 | 1.15 | 0.000489 | -0.00588 | CFL | AllSpc | 998 | 0.376 | 998 | 0.376 | 1.15 | 1.3 | -0.00589
CFLAllSpcSCGERCNewIOU | Com-Iltg-dWatt-CFL_OSspc | SCG | ERC | New | IOU | 0.998 | 0.000376 | 0 | 1.16 | 0.000502 | -0.00666 | 0.998 | 0.000376 | 0 | 1.16 | 0.000502 | -0.00666 | CFL | AllSpc | 998 | 0.376 | 998 | 0.376 | 1.16 | 1.34 | -0.00667
CFLAllSpcPGEESeExCZ01 | Com-Iltg-dWatt-CFL_OSspc | PGE | ESe | Ex | CZ01 | 1.39 | 0.000274 | 0 | 1.35 | 0.000324 | -0.0284 | 1.39 | 0.000274 | 0 | 1.35 | 0.000324 | -0.0284 | CFL | AllSpc | 1390 | 0.274 | 1390 | 0.274 | 0.971 | 1.18 | -0.0204
CFLAllSpcPGEESeExCZ02 | Com-Iltg-dWatt-CFL_OSspc | PGE | ESe | Ex | CZ02 | 1.39 | 7.65e-06 | 0 | 1.45 | 7.65e-06 | -0.0178 | 1.39 | 7.65e-06 | 0 | 1.45 | 7.65e-06 | -0.0178 | CFL | AllSpc | 1390 | 0.00765 | 1390 | 0.00765 | 1.04 | 1 | -0.0128
CFLAllSpcPGEESeExCZ03 | Com-Iltg-dWatt-CFL_OSspc | PGE | ESe | Ex | CZ03 | 1.39 | 7.65e-06 | 0 | 1.45 | 7.65e-06 | -0.0183 | 1.39 | 7.65e-06 | 0 | 1.45 | 7.65e-06 | -0.0183 | CFL | AllSpc | 1390 | 0.00765 | 1390 | 0.00765 | 1.04 | 1 | -0.0132
CFLAllSpcPGEESeExCZ04 | Com-Iltg-dWatt-CFL_OSspc | PGE | ESe | Ex | CZ04 | 1.39 | 0.000274 | 0 | 1.48 | 0.000332 | -0.0142 | 1.39 | 0.000274 | 0 | 1.48 | 0.000332 | -0.0142 | CFL | AllSpc | 1390 | 0.274 | 1390 | 0.274 | 1.06 | 1.21 | -0.0102
CFLAllSpcPGEESeExCZ05 | Com-Iltg-dWatt-CFL_OSspc | PGE | ESe | Ex | CZ05 | 1.39 | 0.000274 | 0 | 1.47 | 0.000339 | -0.0156 | 1.39 | 0.000274 | 0 | 1.47 | 0.000339 | -0.0156 | CFL | AllSpc | 1390 | 0.274 | 1390 | 0.274 | 1.06 | 1.24 | -0.0112
CFLAllSpcSCGESeExCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCG | ESe | Ex | CZ05 | 1.39 | 0.000274 | 0 | 1.47 | 0.000339 | -0.0156 | 1.39 | 0.000274 | 0 | 1.47 | 0.000339 | -0.0156 | CFL | AllSpc | 1390 | 0.274 | 1390 | 0.274 | 1.06 | 1.24 | -0.0112
CFLAllSpcSCEESeExCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCE | ESe | Ex | CZ05 | 1.39 | 0.000274 | 0 | 1.47 | 0.000339 | -0.0156 | 1.39 | 0.000274 | 0 | 1.47 | 0.000339 | -0.0156 | CFL | AllSpc | 1390 | 0.274 | 1390 | 0.274 | 1.06 | 1.24 | -0.0112
CFLAllSpcSCEESeExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCE | ESe | Ex | CZ06 | 1.39 | 0.000274 | 0 | 1.55 | 0.000348 | -0.00799 | 1.39 | 0.000274 | 0 | 1.55 | 0.000348 | -0.00799 | CFL | AllSpc | 1390 | 0.274 | 1390 | 0.274 | 1.12 | 1.27 | -0.00575
CFLAllSpcSDGESeExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SDG | ESe | Ex | CZ06 | 1.39 | 0.000274 | 0 | 1.55 | 0.000348 | -0.00799 | 1.39 | 0.000274 | 0 | 1.55 | 0.000348 | -0.00799 | CFL | AllSpc | 1390 | 0.274 | 1390 | 0.274 | 1.12 | 1.27 | -0.00575
CFLAllSpcSCGESeExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCG | ESe | Ex | CZ06 | 1.39 | 0.000274 | 0 | 1.55 | 0.000348 | -0.00799 | 1.39 | 0.000274 | 0 | 1.55 | 0.000348 | -0.00799 | CFL | AllSpc | 1390 | 0.274 | 1390 | 0.274 | 1.12 | 1.27 | -0.00575
CFLAllSpcSDGESeExCZ07 | Com-Iltg-dWatt-CFL_OSspc | SDG | ESe | Ex | CZ07 | 1.39 | 0.000274 | 0 | 1.55 | 0.000341 | -0.00705 | 1.39 | 0.000274 | 0 | 1.55 | 0.000341 | -0.00705 | CFL | AllSpc | 1390 | 0.274 | 1390 | 0.274 | 1.12 | 1.24 | -0.00507
CFLAllSpcSDGESeExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SDG | ESe | Ex | CZ08 | 1.39 | 0.000274 | 0 | 1.57 | 0.000346 | -0.00681 | 1.39 | 0.000274 | 0 | 1.57 | 0.000346 | -0.00681 | CFL | AllSpc | 1390 | 0.274 | 1390 | 0.274 | 1.13 | 1.26 | -0.0049
CFLAllSpcSCEESeExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCE | ESe | Ex | CZ08 | 1.39 | 0.000274 | 0 | 1.57 | 0.000346 | -0.00681 | 1.39 | 0.000274 | 0 | 1.57 | 0.000346 | -0.00681 | CFL | AllSpc | 1390 | 0.274 | 1390 | 0.274 | 1.13 | 1.26 | -0.0049
CFLAllSpcSCGESeExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCG | ESe | Ex | CZ08 | 1.39 | 0.000274 | 0 | 1.57 | 0.000346 | -0.00681 | 1.39 | 0.000274 | 0 | 1.57 | 0.000346 | -0.00681 | CFL | AllSpc | 1390 | 0.274 | 1390 | 0.274 | 1.13 | 1.26 | -0.0049
CFLAllSpcSCGESeExCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCG | ESe | Ex | CZ09 | 1.39 | 0.000274 | 0 | 1.59 | 0.000352 | -0.00824 | 1.39 | 0.000274 | 0 | 1.59 | 0.000352 | -0.00824 | CFL | AllSpc | 1390 | 0.274 | 1390 | 0.274 | 1.14 | 1.28 | -0.00593
CFLAllSpcSCEESeExCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCE | ESe | Ex | CZ09 | 1.39 | 0.000274 | 0 | 1.59 | 0.000352 | -0.00824 | 1.39 | 0.000274 | 0 | 1.59 | 0.000352 | -0.00824 | CFL | AllSpc | 1390 | 0.274 | 1390 | 0.274 | 1.14 | 1.28 | -0.00593
CFLAllSpcSCEESeExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCE | ESe | Ex | CZ10 | 1.39 | 0.000274 | 0 | 1.56 | 0.000344 | -0.00851 | 1.39 | 0.000274 | 0 | 1.56 | 0.000344 | -0.00851 | CFL | AllSpc | 1390 | 0.274 | 1390 | 0.274 | 1.12 | 1.26 | -0.00612
CFLAllSpcSDGESeExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SDG | ESe | Ex | CZ10 | 1.39 | 0.000274 | 0 | 1.56 | 0.000344 | -0.00851 | 1.39 | 0.000274 | 0 | 1.56 | 0.000344 | -0.00851 | CFL | AllSpc | 1390 | 0.274 | 1390 | 0.274 | 1.12 | 1.26 | -0.00612
CFLAllSpcSCGESeExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCG | ESe | Ex | CZ10 | 1.39 | 0.000274 | 0 | 1.56 | 0.000344 | -0.00851 | 1.39 | 0.000274 | 0 | 1.56 | 0.000344 | -0.00851 | CFL | AllSpc | 1390 | 0.274 | 1390 | 0.274 | 1.12 | 1.26 | -0.00612
CFLAllSpcPGEESeExCZ11 | Com-Iltg-dWatt-CFL_OSspc | PGE | ESe | Ex | CZ11 | 1.39 | 7.65e-06 | 0 | 1.48 | 7.65e-06 | -0.0157 | 1.39 | 7.65e-06 | 0 | 1.48 | 7.65e-06 | -0.0157 | CFL | AllSpc | 1390 | 0.00765 | 1390 | 0.00765 | 1.06 | 1 | -0.0113
CFLAllSpcPGEESeExCZ12 | Com-Iltg-dWatt-CFL_OSspc | PGE | ESe | Ex | CZ12 | 1.39 | 7.65e-06 | 0 | 1.47 | 7.65e-06 | -0.0164 | 1.39 | 7.65e-06 | 0 | 1.47 | 7.65e-06 | -0.0164 | CFL | AllSpc | 1390 | 0.00765 | 1390 | 0.00765 | 1.06 | 1 | -0.0118
CFLAllSpcSCGESeExCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCG | ESe | Ex | CZ13 | 1.39 | 7.65e-06 | 0 | 1.52 | 7.65e-06 | -0.0135 | 1.39 | 7.65e-06 | 0 | 1.52 | 7.65e-06 | -0.0135 | CFL | AllSpc | 1390 | 0.00765 | 1390 | 0.00765 | 1.09 | 1 | -0.00971
CFLAllSpcSCEESeExCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCE | ESe | Ex | CZ13 | 1.39 | 7.65e-06 | 0 | 1.52 | 7.65e-06 | -0.0135 | 1.39 | 7.65e-06 | 0 | 1.52 | 7.65e-06 | -0.0135 | CFL | AllSpc | 1390 | 0.00765 | 1390 | 0.00765 | 1.09 | 1 | -0.00971
CFLAllSpcPGEESeExCZ13 | Com-Iltg-dWatt-CFL_OSspc | PGE | ESe | Ex | CZ13 | 1.39 | 7.65e-06 | 0 | 1.52 | 7.65e-06 | -0.0135 | 1.39 | 7.65e-06 | 0 | 1.52 | 7.65e-06 | -0.0135 | CFL | AllSpc | 1390 | 0.00765 | 1390 | 0.00765 | 1.09 | 1 | -0.00971
CFLAllSpcSCGESeExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCG | ESe | Ex | CZ14 | 1.39 | 0.000274 | 0 | 1.51 | 0.000333 | -0.0133 | 1.39 | 0.000274 | 0 | 1.51 | 0.000333 | -0.0133 | CFL | AllSpc | 1390 | 0.274 | 1390 | 0.274 | 1.09 | 1.22 | -0.00957
CFLAllSpcSCEESeExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCE | ESe | Ex | CZ14 | 1.39 | 0.000274 | 0 | 1.51 | 0.000333 | -0.0133 | 1.39 | 0.000274 | 0 | 1.51 | 0.000333 | -0.0133 | CFL | AllSpc | 1390 | 0.274 | 1390 | 0.274 | 1.09 | 1.22 | -0.00957
CFLAllSpcSDGESeExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SDG | ESe | Ex | CZ14 | 1.39 | 0.000274 | 0 | 1.51 | 0.000333 | -0.0133 | 1.39 | 0.000274 | 0 | 1.51 | 0.000333 | -0.0133 | CFL | AllSpc | 1390 | 0.274 | 1390 | 0.274 | 1.09 | 1.22 | -0.00957
CFLAllSpcSDGESeExCZ15 | Com-Iltg-dWatt-CFL_OSspc | SDG | ESe | Ex | CZ15 | 1.39 | 0.000274 | 0 | 1.69 | 0.000344 | -0.00379 | 1.39 | 0.000274 | 0 | 1.69 | 0.000344 | -0.00379 | CFL | AllSpc | 1390 | 0.274 | 1390 | 0.274 | 1.22 | 1.26 | -0.00273
CFLAllSpcSCEESeExCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCE | ESe | Ex | CZ15 | 1.39 | 0.000274 | 0 | 1.69 | 0.000344 | -0.00379 | 1.39 | 0.000274 | 0 | 1.69 | 0.000344 | -0.00379 | CFL | AllSpc | 1390 | 0.274 | 1390 | 0.274 | 1.22 | 1.26 | -0.00273
CFLAllSpcSCGESeExCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCG | ESe | Ex | CZ15 | 1.39 | 0.000274 | 0 | 1.69 | 0.000344 | -0.00379 | 1.39 | 0.000274 | 0 | 1.69 | 0.000344 | -0.00379 | CFL | AllSpc | 1390 | 0.274 | 1390 | 0.274 | 1.22 | 1.26 | -0.00273
CFLAllSpcSCEESeExCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCE | ESe | Ex | CZ16 | 1.39 | 7.65e-06 | 0 | 1.36 | 7.65e-06 | -0.0232 | 1.39 | 7.65e-06 | 0 | 1.36 | 7.65e-06 | -0.0232 | CFL | AllSpc | 1390 | 0.00765 | 1390 | 0.00765 | 0.978 | 1 | -0.0167
CFLAllSpcPGEESeExCZ16 | Com-Iltg-dWatt-CFL_OSspc | PGE | ESe | Ex | CZ16 | 1.39 | 7.65e-06 | 0 | 1.36 | 7.65e-06 | -0.0232 | 1.39 | 7.65e-06 | 0 | 1.36 | 7.65e-06 | -0.0232 | CFL | AllSpc | 1390 | 0.00765 | 1390 | 0.00765 | 0.978 | 1 | -0.0167
CFLAllSpcSCGESeExCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCG | ESe | Ex | CZ16 | 1.39 | 7.65e-06 | 0 | 1.36 | 7.65e-06 | -0.0232 | 1.39 | 7.65e-06 | 0 | 1.36 | 7.65e-06 | -0.0232 | CFL | AllSpc | 1390 | 0.00765 | 1390 | 0.00765 | 0.978 | 1 | -0.0167
CFLAllSpcSDGESeExIOU | Com-Iltg-dWatt-CFL_OSspc | SDG | ESe | Ex | IOU | 1.39 | 0.000274 | 0 | 1.55 | 0.000343 | -0.00761 | 1.39 | 0.000274 | 0 | 1.55 | 0.000343 | -0.00761 | CFL | AllSpc | 1390 | 0.274 | 1390 | 0.274 | 1.12 | 1.25 | -0.00547
CFLAllSpcSCGESeExIOU | Com-Iltg-dWatt-CFL_OSspc | SCG | ESe | Ex | IOU | 1.39 | 0.00026 | 0 | 1.56 | 0.000329 | -0.00846 | 1.39 | 0.00026 | 0 | 1.56 | 0.000329 | -0.00846 | CFL | AllSpc | 1390 | 0.26 | 1390 | 0.26 | 1.12 | 1.27 | -0.00609
CFLAllSpcPGEESeExIOU | Com-Iltg-dWatt-CFL_OSspc | PGE | ESe | Ex | IOU | 1.39 | 5.45e-05 | 0 | 1.47 | 6.48e-05 | -0.0164 | 1.39 | 5.45e-05 | 0 | 1.47 | 6.48e-05 | -0.0164 | CFL | AllSpc | 1390 | 0.0545 | 1390 | 0.0545 | 1.06 | 1.19 | -0.0118
CFLAllSpcSCEESeExIOU | Com-Iltg-dWatt-CFL_OSspc | SCE | ESe | Ex | IOU | 1.39 | 0.000256 | 0 | 1.56 | 0.000324 | -0.00858 | 1.39 | 0.000256 | 0 | 1.56 | 0.000324 | -0.00858 | CFL | AllSpc | 1390 | 0.256 | 1390 | 0.256 | 1.12 | 1.27 | -0.00617
CFLAllSpcPGEESeNewCZ01 | Com-Iltg-dWatt-CFL_OSspc | PGE | ESe | New | CZ01 | 1.39 | 0.000278 | 0 | 1.37 | 0.00032 | -0.0224 | 1.39 | 0.000278 | 0 | 1.37 | 0.00032 | -0.0224 | CFL | AllSpc | 1390 | 0.278 | 1390 | 0.278 | 0.986 | 1.15 | -0.0161
CFLAllSpcPGEESeNewCZ02 | Com-Iltg-dWatt-CFL_OSspc | PGE | ESe | New | CZ02 | 1.39 | 7.78e-06 | 0 | 1.46 | 7.78e-06 | -0.0206 | 1.39 | 7.78e-06 | 0 | 1.46 | 7.78e-06 | -0.0206 | CFL | AllSpc | 1390 | 0.00778 | 1390 | 0.00778 | 1.05 | 1 | -0.0148
CFLAllSpcPGEESeNewCZ03 | Com-Iltg-dWatt-CFL_OSspc | PGE | ESe | New | CZ03 | 1.39 | 7.78e-06 | 0 | 1.45 | 7.78e-06 | -0.0181 | 1.39 | 7.78e-06 | 0 | 1.45 | 7.78e-06 | -0.0181 | CFL | AllSpc | 1390 | 0.00778 | 1390 | 0.00778 | 1.04 | 1 | -0.013
CFLAllSpcPGEESeNewCZ04 | Com-Iltg-dWatt-CFL_OSspc | PGE | ESe | New | CZ04 | 1.39 | 0.000278 | 0 | 1.49 | 0.000362 | -0.0164 | 1.39 | 0.000278 | 0 | 1.49 | 0.000362 | -0.0164 | CFL | AllSpc | 1390 | 0.278 | 1390 | 0.278 | 1.07 | 1.3 | -0.0118
CFLAllSpcPGEESeNewCZ05 | Com-Iltg-dWatt-CFL_OSspc | PGE | ESe | New | CZ05 | 1.39 | 0.000278 | 0 | 1.44 | 0.000337 | -0.0157 | 1.39 | 0.000278 | 0 | 1.44 | 0.000337 | -0.0157 | CFL | AllSpc | 1390 | 0.278 | 1390 | 0.278 | 1.04 | 1.21 | -0.0113
CFLAllSpcSCEESeNewCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCE | ESe | New | CZ05 | 1.39 | 0.000278 | 0 | 1.45 | 0.000349 | -0.0145 | 1.39 | 0.000278 | 0 | 1.45 | 0.000349 | -0.0145 | CFL | AllSpc | 1390 | 0.278 | 1390 | 0.278 | 1.04 | 1.26 | -0.0104
CFLAllSpcSDGESeNewCZ06 | Com-Iltg-dWatt-CFL_OSspc | SDG | ESe | New | CZ06 | 1.39 | 0.000278 | 0 | 1.52 | 0.000366 | -0.0103 | 1.39 | 0.000278 | 0 | 1.52 | 0.000366 | -0.0103 | CFL | AllSpc | 1390 | 0.278 | 1390 | 0.278 | 1.09 | 1.32 | -0.00741
CFLAllSpcSCEESeNewCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCE | ESe | New | CZ06 | 1.39 | 0.000278 | 0 | 1.53 | 0.00037 | -0.0103 | 1.39 | 0.000278 | 0 | 1.53 | 0.00037 | -0.0103 | CFL | AllSpc | 1390 | 0.278 | 1390 | 0.278 | 1.1 | 1.33 | -0.00741
CFLAllSpcSDGESeNewCZ07 | Com-Iltg-dWatt-CFL_OSspc | SDG | ESe | New | CZ07 | 1.39 | 0.000278 | 0 | 1.51 | 0.000357 | -0.00895 | 1.39 | 0.000278 | 0 | 1.51 | 0.000357 | -0.00895 | CFL | AllSpc | 1390 | 0.278 | 1390 | 0.278 | 1.09 | 1.28 | -0.00644
CFLAllSpcSCEESeNewCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCE | ESe | New | CZ08 | 1.39 | 0.000278 | 0 | 1.55 | 0.000374 | -0.00845 | 1.39 | 0.000278 | 0 | 1.55 | 0.000374 | -0.00845 | CFL | AllSpc | 1390 | 0.278 | 1390 | 0.278 | 1.12 | 1.35 | -0.00608
CFLAllSpcSDGESeNewCZ08 | Com-Iltg-dWatt-CFL_OSspc | SDG | ESe | New | CZ08 | 1.39 | 0.000278 | 0 | 1.54 | 0.00037 | -0.00845 | 1.39 | 0.000278 | 0 | 1.54 | 0.00037 | -0.00845 | CFL | AllSpc | 1390 | 0.278 | 1390 | 0.278 | 1.11 | 1.33 | -0.00608
CFLAllSpcSCEESeNewCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCE | ESe | New | CZ09 | 1.39 | 0.000278 | 0 | 1.55 | 0.000387 | -0.00991 | 1.39 | 0.000278 | 0 | 1.55 | 0.000387 | -0.00991 | CFL | AllSpc | 1390 | 0.278 | 1390 | 0.278 | 1.12 | 1.39 | -0.00713
CFLAllSpcSDGESeNewCZ10 | Com-Iltg-dWatt-CFL_OSspc | SDG | ESe | New | CZ10 | 1.39 | 0.000278 | 0 | 1.56 | 0.000387 | -0.0106 | 1.39 | 0.000278 | 0 | 1.56 | 0.000387 | -0.0106 | CFL | AllSpc | 1390 | 0.278 | 1390 | 0.278 | 1.12 | 1.39 | -0.00763
CFLAllSpcSCEESeNewCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCE | ESe | New | CZ10 | 1.39 | 0.000278 | 0 | 1.56 | 0.000392 | -0.0106 | 1.39 | 0.000278 | 0 | 1.56 | 0.000392 | -0.0106 | CFL | AllSpc | 1390 | 0.278 | 1390 | 0.278 | 1.12 | 1.41 | -0.00763
CFLAllSpcPGEESeNewCZ11 | Com-Iltg-dWatt-CFL_OSspc | PGE | ESe | New | CZ11 | 1.39 | 7.78e-06 | 0 | 1.51 | 7.78e-06 | -0.0178 | 1.39 | 7.78e-06 | 0 | 1.51 | 7.78e-06 | -0.0178 | CFL | AllSpc | 1390 | 0.00778 | 1390 | 0.00778 | 1.09 | 1 | -0.0128
CFLAllSpcPGEESeNewCZ12 | Com-Iltg-dWatt-CFL_OSspc | PGE | ESe | New | CZ12 | 1.39 | 7.78e-06 | 0 | 1.5 | 7.78e-06 | -0.0183 | 1.39 | 7.78e-06 | 0 | 1.5 | 7.78e-06 | -0.0183 | CFL | AllSpc | 1390 | 0.00778 | 1390 | 0.00778 | 1.08 | 1 | -0.0132
CFLAllSpcSCEESeNewCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCE | ESe | New | CZ13 | 1.39 | 7.78e-06 | 0 | 1.55 | 7.78e-06 | -0.0156 | 1.39 | 7.78e-06 | 0 | 1.55 | 7.78e-06 | -0.0156 | CFL | AllSpc | 1390 | 0.00778 | 1390 | 0.00778 | 1.12 | 1 | -0.0112
CFLAllSpcPGEESeNewCZ13 | Com-Iltg-dWatt-CFL_OSspc | PGE | ESe | New | CZ13 | 1.39 | 7.78e-06 | 0 | 1.53 | 7.78e-06 | -0.0165 | 1.39 | 7.78e-06 | 0 | 1.53 | 7.78e-06 | -0.0165 | CFL | AllSpc | 1390 | 0.00778 | 1390 | 0.00778 | 1.1 | 1 | -0.0119
CFLAllSpcSDGESeNewCZ14 | Com-Iltg-dWatt-CFL_OSspc | SDG | ESe | New | CZ14 | 1.39 | 0.000278 | 0 | 1.53 | 0.00038 | -0.0156 | 1.39 | 0.000278 | 0 | 1.53 | 0.00038 | -0.0156 | CFL | AllSpc | 1390 | 0.278 | 1390 | 0.278 | 1.1 | 1.37 | -0.0112
CFLAllSpcSCEESeNewCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCE | ESe | New | CZ14 | 1.39 | 0.000278 | 0 | 1.54 | 0.000384 | -0.0154 | 1.39 | 0.000278 | 0 | 1.54 | 0.000384 | -0.0154 | CFL | AllSpc | 1390 | 0.278 | 1390 | 0.278 | 1.11 | 1.38 | -0.0111
CFLAllSpcSDGESeNewCZ15 | Com-Iltg-dWatt-CFL_OSspc | SDG | ESe | New | CZ15 | 1.39 | 0.000278 | 0 | 1.71 | 0.000385 | -0.00467 | 1.39 | 0.000278 | 0 | 1.71 | 0.000385 | -0.00467 | CFL | AllSpc | 1390 | 0.278 | 1390 | 0.278 | 1.23 | 1.38 | -0.00336
CFLAllSpcSCEESeNewCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCE | ESe | New | CZ15 | 1.39 | 0.000278 | 0 | 1.73 | 0.000389 | -0.00463 | 1.39 | 0.000278 | 0 | 1.73 | 0.000389 | -0.00463 | CFL | AllSpc | 1390 | 0.278 | 1390 | 0.278 | 1.24 | 1.4 | -0.00333
CFLAllSpcPGEESeNewCZ16 | Com-Iltg-dWatt-CFL_OSspc | PGE | ESe | New | CZ16 | 1.39 | 7.78e-06 | 0 | 1.39 | 7.78e-06 | -0.0206 | 1.39 | 7.78e-06 | 0 | 1.39 | 7.78e-06 | -0.0206 | CFL | AllSpc | 1390 | 0.00778 | 1390 | 0.00778 | 1 | 1 | -0.0148
CFLAllSpcSCEESeNewCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCE | ESe | New | CZ16 | 1.39 | 7.78e-06 | 0 | 1.38 | 7.78e-06 | -0.0193 | 1.39 | 7.78e-06 | 0 | 1.38 | 7.78e-06 | -0.0193 | CFL | AllSpc | 1390 | 0.00778 | 1390 | 0.00778 | 0.993 | 1 | -0.0139
CFLAllSpcSDGESeNewIOU | Com-Iltg-dWatt-CFL_OSspc | SDG | ESe | New | IOU | 1.39 | 0.000278 | 0 | 1.53 | 0.000368 | -0.00958 | 1.39 | 0.000278 | 0 | 1.53 | 0.000368 | -0.00958 | CFL | AllSpc | 1390 | 0.278 | 1390 | 0.278 | 1.1 | 1.32 | -0.00689
CFLAllSpcSCGESeNewIOU | Com-Iltg-dWatt-CFL_OSspc | SCG | ESe | New | IOU | 1.39 | 0.000278 | 0 | 1.55 | 0.000378 | -0.0102 | 1.39 | 0.000278 | 0 | 1.55 | 0.000378 | -0.0102 | CFL | AllSpc | 1390 | 0.278 | 1390 | 0.278 | 1.12 | 1.36 | -0.00734
CFLAllSpcPGEESeNewIOU | Com-Iltg-dWatt-CFL_OSspc | PGE | ESe | New | IOU | 1.39 | 2.44e-05 | 0 | 1.54 | 2.88e-05 | -0.0157 | 1.39 | 2.44e-05 | 0 | 1.54 | 2.88e-05 | -0.0157 | CFL | AllSpc | 1390 | 0.0244 | 1390 | 0.0244 | 1.11 | 1.18 | -0.0113
CFLAllSpcSCEESeNewIOU | Com-Iltg-dWatt-CFL_OSspc | SCE | ESe | New | IOU | 1.39 | 0.000278 | 0 | 1.55 | 0.000378 | -0.0102 | 1.39 | 0.000278 | 0 | 1.55 | 0.000378 | -0.0102 | CFL | AllSpc | 1390 | 0.278 | 1390 | 0.278 | 1.12 | 1.36 | -0.00734
CFLAllSpcPGEEUnExCZ01 | Com-Iltg-dWatt-CFL_OSspc | PGE | EUn | Ex | CZ01 | 1.94 | 0.000512 | 0 | 2.05 | 0.000628 | -0.0206 | 1.94 | 0.000512 | 0 | 2.05 | 0.000628 | -0.0206 | CFL | AllSpc | 1940 | 0.512 | 1940 | 0.512 | 1.06 | 1.23 | -0.0106
CFLAllSpcPGEEUnExCZ02 | Com-Iltg-dWatt-CFL_OSspc | PGE | EUn | Ex | CZ02 | 1.94 | 0.000336 | 0 | 2.13 | 0.000417 | -0.0151 | 1.94 | 0.000336 | 0 | 2.13 | 0.000417 | -0.0151 | CFL | AllSpc | 1940 | 0.336 | 1940 | 0.336 | 1.1 | 1.24 | -0.00778
CFLAllSpcPGEEUnExCZ03 | Com-Iltg-dWatt-CFL_OSspc | PGE | EUn | Ex | CZ03 | 1.94 | 0.000336 | 0 | 2.13 | 0.000407 | -0.0144 | 1.94 | 0.000336 | 0 | 2.13 | 0.000407 | -0.0144 | CFL | AllSpc | 1940 | 0.336 | 1940 | 0.336 | 1.1 | 1.21 | -0.00742
CFLAllSpcPGEEUnExCZ04 | Com-Iltg-dWatt-CFL_OSspc | PGE | EUn | Ex | CZ04 | 1.94 | 0.000512 | 0 | 2.17 | 0.000654 | -0.0117 | 1.94 | 0.000512 | 0 | 2.17 | 0.000654 | -0.0117 | CFL | AllSpc | 1940 | 0.512 | 1940 | 0.512 | 1.12 | 1.28 | -0.00603
CFLAllSpcPGEEUnExCZ05 | Com-Iltg-dWatt-CFL_OSspc | PGE | EUn | Ex | CZ05 | 1.94 | 0.000512 | 0 | 2.15 | 0.000623 | -0.0138 | 1.94 | 0.000512 | 0 | 2.15 | 0.000623 | -0.0138 | CFL | AllSpc | 1940 | 0.512 | 1940 | 0.512 | 1.11 | 1.22 | -0.00711
CFLAllSpcSCEEUnExCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCE | EUn | Ex | CZ05 | 1.94 | 0.000512 | 0 | 2.15 | 0.000623 | -0.0138 | 1.94 | 0.000512 | 0 | 2.15 | 0.000623 | -0.0138 | CFL | AllSpc | 1940 | 0.512 | 1940 | 0.512 | 1.11 | 1.22 | -0.00711
CFLAllSpcSCGEUnExCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCG | EUn | Ex | CZ05 | 1.94 | 0.000512 | 0 | 2.15 | 0.000623 | -0.0138 | 1.94 | 0.000512 | 0 | 2.15 | 0.000623 | -0.0138 | CFL | AllSpc | 1940 | 0.512 | 1940 | 0.512 | 1.11 | 1.22 | -0.00711
CFLAllSpcSDGEUnExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SDG | EUn | Ex | CZ06 | 1.94 | 0.000512 | 0 | 2.21 | 0.000647 | -0.00823 | 1.94 | 0.000512 | 0 | 2.21 | 0.000647 | -0.00823 | CFL | AllSpc | 1940 | 0.512 | 1940 | 0.512 | 1.14 | 1.26 | -0.00424
CFLAllSpcSCGEUnExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCG | EUn | Ex | CZ06 | 1.94 | 0.000512 | 0 | 2.21 | 0.000647 | -0.00823 | 1.94 | 0.000512 | 0 | 2.21 | 0.000647 | -0.00823 | CFL | AllSpc | 1940 | 0.512 | 1940 | 0.512 | 1.14 | 1.26 | -0.00424
CFLAllSpcSCEEUnExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCE | EUn | Ex | CZ06 | 1.94 | 0.000512 | 0 | 2.21 | 0.000647 | -0.00823 | 1.94 | 0.000512 | 0 | 2.21 | 0.000647 | -0.00823 | CFL | AllSpc | 1940 | 0.512 | 1940 | 0.512 | 1.14 | 1.26 | -0.00424
CFLAllSpcSDGEUnExCZ07 | Com-Iltg-dWatt-CFL_OSspc | SDG | EUn | Ex | CZ07 | 1.94 | 0.000512 | 0 | 2.2 | 0.000641 | -0.00733 | 1.94 | 0.000512 | 0 | 2.2 | 0.000641 | -0.00733 | CFL | AllSpc | 1940 | 0.512 | 1940 | 0.512 | 1.13 | 1.25 | -0.00378
CFLAllSpcSDGEUnExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SDG | EUn | Ex | CZ08 | 1.94 | 0.000512 | 0 | 2.23 | 0.000649 | -0.00792 | 1.94 | 0.000512 | 0 | 2.23 | 0.000649 | -0.00792 | CFL | AllSpc | 1940 | 0.512 | 1940 | 0.512 | 1.15 | 1.27 | -0.00408
CFLAllSpcSCEEUnExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCE | EUn | Ex | CZ08 | 1.94 | 0.000512 | 0 | 2.23 | 0.000649 | -0.00792 | 1.94 | 0.000512 | 0 | 2.23 | 0.000649 | -0.00792 | CFL | AllSpc | 1940 | 0.512 | 1940 | 0.512 | 1.15 | 1.27 | -0.00408
CFLAllSpcSCGEUnExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCG | EUn | Ex | CZ08 | 1.94 | 0.000512 | 0 | 2.23 | 0.000649 | -0.00792 | 1.94 | 0.000512 | 0 | 2.23 | 0.000649 | -0.00792 | CFL | AllSpc | 1940 | 0.512 | 1940 | 0.512 | 1.15 | 1.27 | -0.00408
CFLAllSpcSCGEUnExCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCG | EUn | Ex | CZ09 | 1.94 | 0.000512 | 0 | 2.24 | 0.000659 | -0.00861 | 1.94 | 0.000512 | 0 | 2.24 | 0.000659 | -0.00861 | CFL | AllSpc | 1940 | 0.512 | 1940 | 0.512 | 1.15 | 1.29 | -0.00444
CFLAllSpcSCEEUnExCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCE | EUn | Ex | CZ09 | 1.94 | 0.000512 | 0 | 2.24 | 0.000659 | -0.00861 | 1.94 | 0.000512 | 0 | 2.24 | 0.000659 | -0.00861 | CFL | AllSpc | 1940 | 0.512 | 1940 | 0.512 | 1.15 | 1.29 | -0.00444
CFLAllSpcSCEEUnExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCE | EUn | Ex | CZ10 | 1.94 | 0.000512 | 0 | 2.22 | 0.000659 | -0.00933 | 1.94 | 0.000512 | 0 | 2.22 | 0.000659 | -0.00933 | CFL | AllSpc | 1940 | 0.512 | 1940 | 0.512 | 1.14 | 1.29 | -0.00481
CFLAllSpcSDGEUnExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SDG | EUn | Ex | CZ10 | 1.94 | 0.000512 | 0 | 2.22 | 0.000659 | -0.00933 | 1.94 | 0.000512 | 0 | 2.22 | 0.000659 | -0.00933 | CFL | AllSpc | 1940 | 0.512 | 1940 | 0.512 | 1.14 | 1.29 | -0.00481
CFLAllSpcSCGEUnExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCG | EUn | Ex | CZ10 | 1.94 | 0.000512 | 0 | 2.22 | 0.000659 | -0.00933 | 1.94 | 0.000512 | 0 | 2.22 | 0.000659 | -0.00933 | CFL | AllSpc | 1940 | 0.512 | 1940 | 0.512 | 1.14 | 1.29 | -0.00481
CFLAllSpcPGEEUnExCZ11 | Com-Iltg-dWatt-CFL_OSspc | PGE | EUn | Ex | CZ11 | 1.94 | 0.000336 | 0 | 2.17 | 0.000423 | -0.0136 | 1.94 | 0.000336 | 0 | 2.17 | 0.000423 | -0.0136 | CFL | AllSpc | 1940 | 0.336 | 1940 | 0.336 | 1.12 | 1.26 | -0.00701
CFLAllSpcPGEEUnExCZ12 | Com-Iltg-dWatt-CFL_OSspc | PGE | EUn | Ex | CZ12 | 1.94 | 0.000336 | 0 | 2.17 | 0.00042 | -0.0135 | 1.94 | 0.000336 | 0 | 2.17 | 0.00042 | -0.0135 | CFL | AllSpc | 1940 | 0.336 | 1940 | 0.336 | 1.12 | 1.25 | -0.00696
CFLAllSpcSCEEUnExCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCE | EUn | Ex | CZ13 | 1.94 | 0.000336 | 0 | 2.19 | 0.000423 | -0.0107 | 1.94 | 0.000336 | 0 | 2.19 | 0.000423 | -0.0107 | CFL | AllSpc | 1940 | 0.336 | 1940 | 0.336 | 1.13 | 1.26 | -0.00552
CFLAllSpcPGEEUnExCZ13 | Com-Iltg-dWatt-CFL_OSspc | PGE | EUn | Ex | CZ13 | 1.94 | 0.000336 | 0 | 2.19 | 0.000423 | -0.0107 | 1.94 | 0.000336 | 0 | 2.19 | 0.000423 | -0.0107 | CFL | AllSpc | 1940 | 0.336 | 1940 | 0.336 | 1.13 | 1.26 | -0.00552
CFLAllSpcSCGEUnExCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCG | EUn | Ex | CZ13 | 1.94 | 0.000336 | 0 | 2.19 | 0.000423 | -0.0107 | 1.94 | 0.000336 | 0 | 2.19 | 0.000423 | -0.0107 | CFL | AllSpc | 1940 | 0.336 | 1940 | 0.336 | 1.13 | 1.26 | -0.00552
CFLAllSpcSDGEUnExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SDG | EUn | Ex | CZ14 | 1.94 | 0.000512 | 0 | 2.2 | 0.000651 | -0.0129 | 1.94 | 0.000512 | 0 | 2.2 | 0.000651 | -0.0129 | CFL | AllSpc | 1940 | 0.512 | 1940 | 0.512 | 1.13 | 1.27 | -0.00665
CFLAllSpcSCEEUnExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCE | EUn | Ex | CZ14 | 1.94 | 0.000512 | 0 | 2.2 | 0.000651 | -0.0129 | 1.94 | 0.000512 | 0 | 2.2 | 0.000651 | -0.0129 | CFL | AllSpc | 1940 | 0.512 | 1940 | 0.512 | 1.13 | 1.27 | -0.00665
CFLAllSpcSCGEUnExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCG | EUn | Ex | CZ14 | 1.94 | 0.000512 | 0 | 2.2 | 0.000651 | -0.0129 | 1.94 | 0.000512 | 0 | 2.2 | 0.000651 | -0.0129 | CFL | AllSpc | 1940 | 0.512 | 1940 | 0.512 | 1.13 | 1.27 | -0.00665
CFLAllSpcSCGEUnExCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCG | EUn | Ex | CZ15 | 1.94 | 0.000512 | 0 | 2.3 | 0.00065 | -0.00431 | 1.94 | 0.000512 | 0 | 2.3 | 0.00065 | -0.00431 | CFL | AllSpc | 1940 | 0.512 | 1940 | 0.512 | 1.19 | 1.27 | -0.00222
CFLAllSpcSCEEUnExCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCE | EUn | Ex | CZ15 | 1.94 | 0.000512 | 0 | 2.3 | 0.00065 | -0.00431 | 1.94 | 0.000512 | 0 | 2.3 | 0.00065 | -0.00431 | CFL | AllSpc | 1940 | 0.512 | 1940 | 0.512 | 1.19 | 1.27 | -0.00222
CFLAllSpcSCGEUnExCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCG | EUn | Ex | CZ16 | 1.94 | 0.000336 | 0 | 2.04 | 0.00041 | -0.0225 | 1.94 | 0.000336 | 0 | 2.04 | 0.00041 | -0.0225 | CFL | AllSpc | 1940 | 0.336 | 1940 | 0.336 | 1.05 | 1.22 | -0.0116
CFLAllSpcSCEEUnExCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCE | EUn | Ex | CZ16 | 1.94 | 0.000336 | 0 | 2.04 | 0.00041 | -0.0225 | 1.94 | 0.000336 | 0 | 2.04 | 0.00041 | -0.0225 | CFL | AllSpc | 1940 | 0.336 | 1940 | 0.336 | 1.05 | 1.22 | -0.0116
CFLAllSpcPGEEUnExCZ16 | Com-Iltg-dWatt-CFL_OSspc | PGE | EUn | Ex | CZ16 | 1.94 | 0.000336 | 0 | 2.04 | 0.00041 | -0.0225 | 1.94 | 0.000336 | 0 | 2.04 | 0.00041 | -0.0225 | CFL | AllSpc | 1940 | 0.336 | 1940 | 0.336 | 1.05 | 1.22 | -0.0116
CFLAllSpcSDGEUnExIOU | Com-Iltg-dWatt-CFL_OSspc | SDG | EUn | Ex | IOU | 1.94 | 0.000512 | 0 | 2.21 | 0.000645 | -0.00784 | 1.94 | 0.000512 | 0 | 2.21 | 0.000645 | -0.00784 | CFL | AllSpc | 1940 | 0.512 | 1940 | 0.512 | 1.14 | 1.26 | -0.00404
CFLAllSpcPGEEUnExIOU | Com-Iltg-dWatt-CFL_OSspc | PGE | EUn | Ex | IOU | 1.94 | 0.00037 | 0 | 2.15 | 0.000457 | -0.0137 | 1.94 | 0.00037 | 0 | 2.15 | 0.000457 | -0.0137 | CFL | AllSpc | 1940 | 0.37 | 1940 | 0.37 | 1.11 | 1.24 | -0.00706
CFLAllSpcSCEEUnExIOU | Com-Iltg-dWatt-CFL_OSspc | SCE | EUn | Ex | IOU | 1.94 | 0.000495 | 0 | 2.21 | 0.000628 | -0.00942 | 1.94 | 0.000495 | 0 | 2.21 | 0.000628 | -0.00942 | CFL | AllSpc | 1940 | 0.495 | 1940 | 0.495 | 1.14 | 1.27 | -0.00486
CFLAllSpcSCGEUnExIOU | Com-Iltg-dWatt-CFL_OSspc | SCG | EUn | Ex | IOU | 1.94 | 0.0005 | 0 | 2.22 | 0.000637 | -0.00912 | 1.94 | 0.0005 | 0 | 2.22 | 0.000637 | -0.00912 | CFL | AllSpc | 1940 | 0.5 | 1940 | 0.5 | 1.14 | 1.27 | -0.0047
CFLAllSpcPGEEUnNewCZ01 | Com-Iltg-dWatt-CFL_OSspc | PGE | EUn | New | CZ01 | 1.94 | 0.000511 | 0 | 2.03 | 0.0006 | -0.0187 | 1.94 | 0.000511 | 0 | 2.03 | 0.0006 | -0.0187 | CFL | AllSpc | 1940 | 0.511 | 1940 | 0.511 | 1.05 | 1.17 | -0.00964
CFLAllSpcPGEEUnNewCZ02 | Com-Iltg-dWatt-CFL_OSspc | PGE | EUn | New | CZ02 | 1.94 | 0.000335 | 0 | 2.15 | 0.000436 | -0.0151 | 1.94 | 0.000335 | 0 | 2.15 | 0.000436 | -0.0151 | CFL | AllSpc | 1940 | 0.335 | 1940 | 0.335 | 1.11 | 1.3 | -0.00778
CFLAllSpcPGEEUnNewCZ03 | Com-Iltg-dWatt-CFL_OSspc | PGE | EUn | New | CZ03 | 1.94 | 0.000335 | 0 | 2.11 | 0.000422 | -0.0112 | 1.94 | 0.000335 | 0 | 2.11 | 0.000422 | -0.0112 | CFL | AllSpc | 1940 | 0.335 | 1940 | 0.335 | 1.09 | 1.26 | -0.00577
CFLAllSpcPGEEUnNewCZ04 | Com-Iltg-dWatt-CFL_OSspc | PGE | EUn | New | CZ04 | 1.94 | 0.000511 | 0 | 2.16 | 0.000641 | -0.01 | 1.94 | 0.000511 | 0 | 2.16 | 0.000641 | -0.01 | CFL | AllSpc | 1940 | 0.511 | 1940 | 0.511 | 1.11 | 1.25 | -0.00515
CFLAllSpcPGEEUnNewCZ05 | Com-Iltg-dWatt-CFL_OSspc | PGE | EUn | New | CZ05 | 1.94 | 0.000511 | 0 | 2.11 | 0.000615 | -0.0121 | 1.94 | 0.000511 | 0 | 2.11 | 0.000615 | -0.0121 | CFL | AllSpc | 1940 | 0.511 | 1940 | 0.511 | 1.09 | 1.2 | -0.00624
CFLAllSpcSCEEUnNewCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCE | EUn | New | CZ05 | 1.94 | 0.000511 | 0 | 2.1 | 0.000632 | -0.0127 | 1.94 | 0.000511 | 0 | 2.1 | 0.000632 | -0.0127 | CFL | AllSpc | 1940 | 0.511 | 1940 | 0.511 | 1.08 | 1.24 | -0.00655
CFLAllSpcSDGEUnNewCZ06 | Com-Iltg-dWatt-CFL_OSspc | SDG | EUn | New | CZ06 | 1.94 | 0.000511 | 0 | 2.24 | 0.000643 | -0.00631 | 1.94 | 0.000511 | 0 | 2.24 | 0.000643 | -0.00631 | CFL | AllSpc | 1940 | 0.511 | 1940 | 0.511 | 1.15 | 1.26 | -0.00325
CFLAllSpcSCEEUnNewCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCE | EUn | New | CZ06 | 1.94 | 0.000511 | 0 | 2.22 | 0.000648 | -0.00574 | 1.94 | 0.000511 | 0 | 2.22 | 0.000648 | -0.00574 | CFL | AllSpc | 1940 | 0.511 | 1940 | 0.511 | 1.14 | 1.27 | -0.00296
CFLAllSpcSDGEUnNewCZ07 | Com-Iltg-dWatt-CFL_OSspc | SDG | EUn | New | CZ07 | 1.94 | 0.000511 | 0 | 2.21 | 0.000638 | -0.00563 | 1.94 | 0.000511 | 0 | 2.21 | 0.000638 | -0.00563 | CFL | AllSpc | 1940 | 0.511 | 1940 | 0.511 | 1.14 | 1.25 | -0.0029
CFLAllSpcSCEEUnNewCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCE | EUn | New | CZ08 | 1.94 | 0.000511 | 0 | 2.24 | 0.000658 | -0.00508 | 1.94 | 0.000511 | 0 | 2.24 | 0.000658 | -0.00508 | CFL | AllSpc | 1940 | 0.511 | 1940 | 0.511 | 1.15 | 1.29 | -0.00262
CFLAllSpcSDGEUnNewCZ08 | Com-Iltg-dWatt-CFL_OSspc | SDG | EUn | New | CZ08 | 1.94 | 0.000511 | 0 | 2.25 | 0.00065 | -0.00557 | 1.94 | 0.000511 | 0 | 2.25 | 0.00065 | -0.00557 | CFL | AllSpc | 1940 | 0.511 | 1940 | 0.511 | 1.16 | 1.27 | -0.00287
CFLAllSpcSCEEUnNewCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCE | EUn | New | CZ09 | 1.94 | 0.000511 | 0 | 2.25 | 0.000679 | -0.00586 | 1.94 | 0.000511 | 0 | 2.25 | 0.000679 | -0.00586 | CFL | AllSpc | 1940 | 0.511 | 1940 | 0.511 | 1.16 | 1.33 | -0.00302
CFLAllSpcSDGEUnNewCZ10 | Com-Iltg-dWatt-CFL_OSspc | SDG | EUn | New | CZ10 | 1.94 | 0.000511 | 0 | 2.27 | 0.00067 | -0.00644 | 1.94 | 0.000511 | 0 | 2.27 | 0.00067 | -0.00644 | CFL | AllSpc | 1940 | 0.511 | 1940 | 0.511 | 1.17 | 1.31 | -0.00332
CFLAllSpcSCEEUnNewCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCE | EUn | New | CZ10 | 1.94 | 0.000511 | 0 | 2.26 | 0.000681 | -0.00621 | 1.94 | 0.000511 | 0 | 2.26 | 0.000681 | -0.00621 | CFL | AllSpc | 1940 | 0.511 | 1940 | 0.511 | 1.16 | 1.33 | -0.0032
CFLAllSpcPGEEUnNewCZ11 | Com-Iltg-dWatt-CFL_OSspc | PGE | EUn | New | CZ11 | 1.94 | 0.000335 | 0 | 2.2 | 0.000434 | -0.0112 | 1.94 | 0.000335 | 0 | 2.2 | 0.000434 | -0.0112 | CFL | AllSpc | 1940 | 0.335 | 1940 | 0.335 | 1.13 | 1.3 | -0.00577
CFLAllSpcPGEEUnNewCZ12 | Com-Iltg-dWatt-CFL_OSspc | PGE | EUn | New | CZ12 | 1.94 | 0.000335 | 0 | 2.19 | 0.000435 | -0.0122 | 1.94 | 0.000335 | 0 | 2.19 | 0.000435 | -0.0122 | CFL | AllSpc | 1940 | 0.335 | 1940 | 0.335 | 1.13 | 1.3 | -0.00629
CFLAllSpcSCEEUnNewCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCE | EUn | New | CZ13 | 1.94 | 0.000335 | 0 | 2.27 | 0.000482 | -0.0127 | 1.94 | 0.000335 | 0 | 2.27 | 0.000482 | -0.0127 | CFL | AllSpc | 1940 | 0.335 | 1940 | 0.335 | 1.17 | 1.44 | -0.00655
CFLAllSpcPGEEUnNewCZ13 | Com-Iltg-dWatt-CFL_OSspc | PGE | EUn | New | CZ13 | 1.94 | 0.000335 | 0 | 2.25 | 0.000454 | -0.0126 | 1.94 | 0.000335 | 0 | 2.25 | 0.000454 | -0.0126 | CFL | AllSpc | 1940 | 0.335 | 1940 | 0.335 | 1.16 | 1.36 | -0.00649
CFLAllSpcSCEEUnNewCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCE | EUn | New | CZ14 | 1.94 | 0.000511 | 0 | 2.15 | 0.000622 | -0.0104 | 1.94 | 0.000511 | 0 | 2.15 | 0.000622 | -0.0104 | CFL | AllSpc | 1940 | 0.511 | 1940 | 0.511 | 1.11 | 1.22 | -0.00536
CFLAllSpcSDGEUnNewCZ14 | Com-Iltg-dWatt-CFL_OSspc | SDG | EUn | New | CZ14 | 1.94 | 0.000511 | 0 | 2.18 | 0.00062 | -0.0107 | 1.94 | 0.000511 | 0 | 2.18 | 0.00062 | -0.0107 | CFL | AllSpc | 1940 | 0.511 | 1940 | 0.511 | 1.12 | 1.21 | -0.00552
CFLAllSpcSDGEUnNewCZ15 | Com-Iltg-dWatt-CFL_OSspc | SDG | EUn | New | CZ15 | 1.94 | 0.000511 | 0 | 2.37 | 0.000677 | -0.00297 | 1.94 | 0.000511 | 0 | 2.37 | 0.000677 | -0.00297 | CFL | AllSpc | 1940 | 0.511 | 1940 | 0.511 | 1.22 | 1.32 | -0.00153
CFLAllSpcSCEEUnNewCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCE | EUn | New | CZ15 | 1.94 | 0.000511 | 0 | 2.39 | 0.000692 | -0.00266 | 1.94 | 0.000511 | 0 | 2.39 | 0.000692 | -0.00266 | CFL | AllSpc | 1940 | 0.511 | 1940 | 0.511 | 1.23 | 1.35 | -0.00137
CFLAllSpcPGEEUnNewCZ16 | Com-Iltg-dWatt-CFL_OSspc | PGE | EUn | New | CZ16 | 1.94 | 0.000335 | 0 | 2.06 | 0.000418 | -0.0202 | 1.94 | 0.000335 | 0 | 2.06 | 0.000418 | -0.0202 | CFL | AllSpc | 1940 | 0.335 | 1940 | 0.335 | 1.06 | 1.25 | -0.0104
CFLAllSpcSCEEUnNewCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCE | EUn | New | CZ16 | 1.94 | 0.000335 | 0 | 2.05 | 0.000433 | -0.0227 | 1.94 | 0.000335 | 0 | 2.05 | 0.000433 | -0.0227 | CFL | AllSpc | 1940 | 0.335 | 1940 | 0.335 | 1.06 | 1.29 | -0.0117
CFLAllSpcSCEEUnNewIOU | Com-Iltg-dWatt-CFL_OSspc | SCE | EUn | New | IOU | 1.94 | 0.000511 | 0 | 2.25 | 0.000652 | -0.00617 | 1.94 | 0.000511 | 0 | 2.25 | 0.000652 | -0.00617 | CFL | AllSpc | 1940 | 0.511 | 1940 | 0.511 | 1.16 | 1.28 | -0.00318
CFLAllSpcPGEEUnNewIOU | Com-Iltg-dWatt-CFL_OSspc | PGE | EUn | New | IOU | 1.94 | 0.000388 | 0 | 2.22 | 0.000527 | -0.0128 | 1.94 | 0.000388 | 0 | 2.22 | 0.000527 | -0.0128 | CFL | AllSpc | 1940 | 0.388 | 1940 | 0.388 | 1.14 | 1.36 | -0.0066
CFLAllSpcSCGEUnNewIOU | Com-Iltg-dWatt-CFL_OSspc | SCG | EUn | New | IOU | 1.94 | 0.000511 | 0 | 2.25 | 0.000652 | -0.00615 | 1.94 | 0.000511 | 0 | 2.25 | 0.000652 | -0.00615 | CFL | AllSpc | 1940 | 0.511 | 1940 | 0.511 | 1.16 | 1.28 | -0.00317
CFLAllSpcSDGEUnNewIOU | Com-Iltg-dWatt-CFL_OSspc | SDG | EUn | New | IOU | 1.94 | 0.000511 | 0 | 2.22 | 0.000646 | -0.00585 | 1.94 | 0.000511 | 0 | 2.22 | 0.000646 | -0.00585 | CFL | AllSpc | 1940 | 0.511 | 1940 | 0.511 | 1.14 | 1.26 | -0.00302
CFLAllSpcPGEGroExCZ01 | Com-Iltg-dWatt-CFL_OSspc | PGE | Gro | Ex | CZ01 | 4.78 | 0.000756 | 0 | 3.84 | 0.000705 | -0.0841 | 4.78 | 0.000756 | 0 | 3.84 | 0.000705 | -0.0841 | CFL | AllSpc | 4780 | 0.756 | 4780 | 0.756 | 0.803 | 0.933 | -0.0176
CFLAllSpcPGEGroExCZ02 | Com-Iltg-dWatt-CFL_OSspc | PGE | Gro | Ex | CZ02 | 4.78 | 0.000756 | 0 | 4.32 | 0.00101 | -0.0655 | 4.78 | 0.000756 | 0 | 4.32 | 0.00101 | -0.0655 | CFL | AllSpc | 4780 | 0.756 | 4780 | 0.756 | 0.904 | 1.34 | -0.0137
CFLAllSpcPGEGroExCZ03 | Com-Iltg-dWatt-CFL_OSspc | PGE | Gro | Ex | CZ03 | 4.78 | 0.000756 | 0 | 4.13 | 0.000954 | -0.0746 | 4.78 | 0.000756 | 0 | 4.13 | 0.000954 | -0.0746 | CFL | AllSpc | 4780 | 0.756 | 4780 | 0.756 | 0.864 | 1.26 | -0.0156
CFLAllSpcPGEGroExCZ04 | Com-Iltg-dWatt-CFL_OSspc | PGE | Gro | Ex | CZ04 | 4.78 | 0.000756 | 0 | 4.41 | 0.00096 | -0.0631 | 4.78 | 0.000756 | 0 | 4.41 | 0.00096 | -0.0631 | CFL | AllSpc | 4780 | 0.756 | 4780 | 0.756 | 0.923 | 1.27 | -0.0132
CFLAllSpcSCEGroExCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCE | Gro | Ex | CZ05 | 4.78 | 0.000756 | 0 | 4.58 | 0.000946 | -0.0832 | 4.78 | 0.000756 | 0 | 4.58 | 0.000946 | -0.0832 | CFL | AllSpc | 4780 | 0.756 | 4780 | 0.756 | 0.958 | 1.25 | -0.0174
CFLAllSpcPGEGroExCZ05 | Com-Iltg-dWatt-CFL_OSspc | PGE | Gro | Ex | CZ05 | 4.78 | 0.000756 | 0 | 4.58 | 0.000946 | -0.0832 | 4.78 | 0.000756 | 0 | 4.58 | 0.000946 | -0.0832 | CFL | AllSpc | 4780 | 0.756 | 4780 | 0.756 | 0.958 | 1.25 | -0.0174
CFLAllSpcSCGGroExCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCG | Gro | Ex | CZ05 | 4.78 | 0.000756 | 0 | 4.58 | 0.000946 | -0.0832 | 4.78 | 0.000756 | 0 | 4.58 | 0.000946 | -0.0832 | CFL | AllSpc | 4780 | 0.756 | 4780 | 0.756 | 0.958 | 1.25 | -0.0174
CFLAllSpcSCGGroExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCG | Gro | Ex | CZ06 | 4.78 | 0.000756 | 0 | 4.77 | 0.000933 | -0.0655 | 4.78 | 0.000756 | 0 | 4.77 | 0.000933 | -0.0655 | CFL | AllSpc | 4780 | 0.756 | 4780 | 0.756 | 0.998 | 1.23 | -0.0137
CFLAllSpcSCEGroExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCE | Gro | Ex | CZ06 | 4.78 | 0.000756 | 0 | 4.77 | 0.000933 | -0.0655 | 4.78 | 0.000756 | 0 | 4.77 | 0.000933 | -0.0655 | CFL | AllSpc | 4780 | 0.756 | 4780 | 0.756 | 0.998 | 1.23 | -0.0137
CFLAllSpcSDGGroExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SDG | Gro | Ex | CZ06 | 4.78 | 0.000756 | 0 | 4.77 | 0.000933 | -0.0655 | 4.78 | 0.000756 | 0 | 4.77 | 0.000933 | -0.0655 | CFL | AllSpc | 4780 | 0.756 | 4780 | 0.756 | 0.998 | 1.23 | -0.0137
CFLAllSpcSDGGroExCZ07 | Com-Iltg-dWatt-CFL_OSspc | SDG | Gro | Ex | CZ07 | 4.78 | 0.000756 | 0 | 4.7 | 0.000919 | -0.0703 | 4.78 | 0.000756 | 0 | 4.7 | 0.000919 | -0.0703 | CFL | AllSpc | 4780 | 0.756 | 4780 | 0.756 | 0.983 | 1.22 | -0.0147
CFLAllSpcSCGGroExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCG | Gro | Ex | CZ08 | 4.78 | 0.000756 | 0 | 4.88 | 0.000958 | -0.0598 | 4.78 | 0.000756 | 0 | 4.88 | 0.000958 | -0.0598 | CFL | AllSpc | 4780 | 0.756 | 4780 | 0.756 | 1.02 | 1.27 | -0.0125
CFLAllSpcSDGGroExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SDG | Gro | Ex | CZ08 | 4.78 | 0.000756 | 0 | 4.88 | 0.000958 | -0.0598 | 4.78 | 0.000756 | 0 | 4.88 | 0.000958 | -0.0598 | CFL | AllSpc | 4780 | 0.756 | 4780 | 0.756 | 1.02 | 1.27 | -0.0125
CFLAllSpcSCEGroExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCE | Gro | Ex | CZ08 | 4.78 | 0.000756 | 0 | 4.88 | 0.000958 | -0.0598 | 4.78 | 0.000756 | 0 | 4.88 | 0.000958 | -0.0598 | CFL | AllSpc | 4780 | 0.756 | 4780 | 0.756 | 1.02 | 1.27 | -0.0125
CFLAllSpcSCGGroExCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCG | Gro | Ex | CZ09 | 4.78 | 0.000756 | 0 | 5.01 | 0.000989 | -0.0593 | 4.78 | 0.000756 | 0 | 5.01 | 0.000989 | -0.0593 | CFL | AllSpc | 4780 | 0.756 | 4780 | 0.756 | 1.05 | 1.31 | -0.0124
CFLAllSpcSCEGroExCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCE | Gro | Ex | CZ09 | 4.78 | 0.000756 | 0 | 5.01 | 0.000989 | -0.0593 | 4.78 | 0.000756 | 0 | 5.01 | 0.000989 | -0.0593 | CFL | AllSpc | 4780 | 0.756 | 4780 | 0.756 | 1.05 | 1.31 | -0.0124
CFLAllSpcSDGGroExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SDG | Gro | Ex | CZ10 | 4.78 | 0.000756 | 0 | 4.97 | 0.00101 | -0.0564 | 4.78 | 0.000756 | 0 | 4.97 | 0.00101 | -0.0564 | CFL | AllSpc | 4780 | 0.756 | 4780 | 0.756 | 1.04 | 1.34 | -0.0118
CFLAllSpcSCGGroExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCG | Gro | Ex | CZ10 | 4.78 | 0.000756 | 0 | 4.97 | 0.00101 | -0.0564 | 4.78 | 0.000756 | 0 | 4.97 | 0.00101 | -0.0564 | CFL | AllSpc | 4780 | 0.756 | 4780 | 0.756 | 1.04 | 1.34 | -0.0118
CFLAllSpcSCEGroExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCE | Gro | Ex | CZ10 | 4.78 | 0.000756 | 0 | 4.97 | 0.00101 | -0.0564 | 4.78 | 0.000756 | 0 | 4.97 | 0.00101 | -0.0564 | CFL | AllSpc | 4780 | 0.756 | 4780 | 0.756 | 1.04 | 1.34 | -0.0118
CFLAllSpcPGEGroExCZ11 | Com-Iltg-dWatt-CFL_OSspc | PGE | Gro | Ex | CZ11 | 4.78 | 0.000756 | 0 | 4.68 | 0.00101 | -0.0535 | 4.78 | 0.000756 | 0 | 4.68 | 0.00101 | -0.0535 | CFL | AllSpc | 4780 | 0.756 | 4780 | 0.756 | 0.979 | 1.34 | -0.0112
CFLAllSpcPGEGroExCZ12 | Com-Iltg-dWatt-CFL_OSspc | PGE | Gro | Ex | CZ12 | 4.78 | 0.000756 | 0 | 4.55 | 0.001 | -0.0583 | 4.78 | 0.000756 | 0 | 4.55 | 0.001 | -0.0583 | CFL | AllSpc | 4780 | 0.756 | 4780 | 0.756 | 0.952 | 1.32 | -0.0122
CFLAllSpcSCEGroExCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCE | Gro | Ex | CZ13 | 4.78 | 0.000756 | 0 | 5.01 | 0.000999 | -0.0569 | 4.78 | 0.000756 | 0 | 5.01 | 0.000999 | -0.0569 | CFL | AllSpc | 4780 | 0.756 | 4780 | 0.756 | 1.05 | 1.32 | -0.0119
CFLAllSpcPGEGroExCZ13 | Com-Iltg-dWatt-CFL_OSspc | PGE | Gro | Ex | CZ13 | 4.78 | 0.000756 | 0 | 5.01 | 0.000999 | -0.0569 | 4.78 | 0.000756 | 0 | 5.01 | 0.000999 | -0.0569 | CFL | AllSpc | 4780 | 0.756 | 4780 | 0.756 | 1.05 | 1.32 | -0.0119
CFLAllSpcSCGGroExCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCG | Gro | Ex | CZ13 | 4.78 | 0.000756 | 0 | 5.01 | 0.000999 | -0.0569 | 4.78 | 0.000756 | 0 | 5.01 | 0.000999 | -0.0569 | CFL | AllSpc | 4780 | 0.756 | 4780 | 0.756 | 1.05 | 1.32 | -0.0119
CFLAllSpcSCGGroExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCG | Gro | Ex | CZ14 | 4.78 | 0.000756 | 0 | 4.95 | 0.00102 | -0.0569 | 4.78 | 0.000756 | 0 | 4.95 | 0.00102 | -0.0569 | CFL | AllSpc | 4780 | 0.756 | 4780 | 0.756 | 1.04 | 1.35 | -0.0119
CFLAllSpcSDGGroExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SDG | Gro | Ex | CZ14 | 4.78 | 0.000756 | 0 | 4.95 | 0.00102 | -0.0569 | 4.78 | 0.000756 | 0 | 4.95 | 0.00102 | -0.0569 | CFL | AllSpc | 4780 | 0.756 | 4780 | 0.756 | 1.04 | 1.35 | -0.0119
CFLAllSpcSCEGroExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCE | Gro | Ex | CZ14 | 4.78 | 0.000756 | 0 | 4.95 | 0.00102 | -0.0569 | 4.78 | 0.000756 | 0 | 4.95 | 0.00102 | -0.0569 | CFL | AllSpc | 4780 | 0.756 | 4780 | 0.756 | 1.04 | 1.35 | -0.0119
CFLAllSpcSCGGroExCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCG | Gro | Ex | CZ15 | 4.78 | 0.000756 | 0 | 5.35 | 0.001 | -0.0327 | 4.78 | 0.000756 | 0 | 5.35 | 0.001 | -0.0327 | CFL | AllSpc | 4780 | 0.756 | 4780 | 0.756 | 1.12 | 1.32 | -0.00684
CFLAllSpcSCEGroExCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCE | Gro | Ex | CZ15 | 4.78 | 0.000756 | 0 | 5.35 | 0.001 | -0.0327 | 4.78 | 0.000756 | 0 | 5.35 | 0.001 | -0.0327 | CFL | AllSpc | 4780 | 0.756 | 4780 | 0.756 | 1.12 | 1.32 | -0.00684
CFLAllSpcSDGGroExCZ15 | Com-Iltg-dWatt-CFL_OSspc | SDG | Gro | Ex | CZ15 | 4.78 | 0.000756 | 0 | 5.35 | 0.001 | -0.0327 | 4.78 | 0.000756 | 0 | 5.35 | 0.001 | -0.0327 | CFL | AllSpc | 4780 | 0.756 | 4780 | 0.756 | 1.12 | 1.32 | -0.00684
CFLAllSpcSCGGroExCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCG | Gro | Ex | CZ16 | 4.78 | 0.000756 | 0 | 4.54 | 0.000953 | -0.0779 | 4.78 | 0.000756 | 0 | 4.54 | 0.000953 | -0.0779 | CFL | AllSpc | 4780 | 0.756 | 4780 | 0.756 | 0.95 | 1.26 | -0.0163
CFLAllSpcPGEGroExCZ16 | Com-Iltg-dWatt-CFL_OSspc | PGE | Gro | Ex | CZ16 | 4.78 | 0.000756 | 0 | 4.54 | 0.000953 | -0.0779 | 4.78 | 0.000756 | 0 | 4.54 | 0.000953 | -0.0779 | CFL | AllSpc | 4780 | 0.756 | 4780 | 0.756 | 0.95 | 1.26 | -0.0163
CFLAllSpcSCEGroExCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCE | Gro | Ex | CZ16 | 4.78 | 0.000756 | 0 | 4.54 | 0.000953 | -0.0779 | 4.78 | 0.000756 | 0 | 4.54 | 0.000953 | -0.0779 | CFL | AllSpc | 4780 | 0.756 | 4780 | 0.756 | 0.95 | 1.26 | -0.0163
CFLAllSpcSCGGroExIOU | Com-Iltg-dWatt-CFL_OSspc | SCG | Gro | Ex | IOU | 4.78 | 0.000756 | 0 | 4.92 | 0.000975 | -0.0597 | 4.78 | 0.000756 | 0 | 4.92 | 0.000975 | -0.0597 | CFL | AllSpc | 4780 | 0.756 | 4780 | 0.756 | 1.03 | 1.29 | -0.0125
CFLAllSpcPGEGroExIOU | Com-Iltg-dWatt-CFL_OSspc | PGE | Gro | Ex | IOU | 4.78 | 0.000756 | 0 | 4.47 | 0.000978 | -0.0646 | 4.78 | 0.000756 | 0 | 4.47 | 0.000978 | -0.0646 | CFL | AllSpc | 4780 | 0.756 | 4780 | 0.756 | 0.935 | 1.29 | -0.0135
CFLAllSpcSDGGroExIOU | Com-Iltg-dWatt-CFL_OSspc | SDG | Gro | Ex | IOU | 4.78 | 0.000756 | 0 | 4.78 | 0.000946 | -0.0659 | 4.78 | 0.000756 | 0 | 4.78 | 0.000946 | -0.0659 | CFL | AllSpc | 4780 | 0.756 | 4780 | 0.756 | 1 | 1.25 | -0.0138
CFLAllSpcSCEGroExIOU | Com-Iltg-dWatt-CFL_OSspc | SCE | Gro | Ex | IOU | 4.78 | 0.000756 | 0 | 4.91 | 0.000974 | -0.0596 | 4.78 | 0.000756 | 0 | 4.91 | 0.000974 | -0.0596 | CFL | AllSpc | 4780 | 0.756 | 4780 | 0.756 | 1.03 | 1.29 | -0.0125
CFLAllSpcPGEGroNewCZ01 | Com-Iltg-dWatt-CFL_OSspc | PGE | Gro | New | CZ01 | 4.78 | 0.000755 | 0 | 3.96 | 0.000889 | -0.0894 | 4.78 | 0.000755 | 0 | 3.96 | 0.000889 | -0.0894 | CFL | AllSpc | 4780 | 0.755 | 4780 | 0.755 | 0.828 | 1.18 | -0.0187
CFLAllSpcPGEGroNewCZ02 | Com-Iltg-dWatt-CFL_OSspc | PGE | Gro | New | CZ02 | 4.78 | 0.000755 | 0 | 4.5 | 0.00105 | -0.0655 | 4.78 | 0.000755 | 0 | 4.5 | 0.00105 | -0.0655 | CFL | AllSpc | 4780 | 0.755 | 4780 | 0.755 | 0.941 | 1.39 | -0.0137
CFLAllSpcPGEGroNewCZ03 | Com-Iltg-dWatt-CFL_OSspc | PGE | Gro | New | CZ03 | 4.78 | 0.000755 | 0 | 4.26 | 0.000987 | -0.0736 | 4.78 | 0.000755 | 0 | 4.26 | 0.000987 | -0.0736 | CFL | AllSpc | 4780 | 0.755 | 4780 | 0.755 | 0.891 | 1.31 | -0.0154
CFLAllSpcPGEGroNewCZ04 | Com-Iltg-dWatt-CFL_OSspc | PGE | Gro | New | CZ04 | 4.78 | 0.000755 | 0 | 4.62 | 0.000986 | -0.0602 | 4.78 | 0.000755 | 0 | 4.62 | 0.000986 | -0.0602 | CFL | AllSpc | 4780 | 0.755 | 4780 | 0.755 | 0.967 | 1.31 | -0.0126
CFLAllSpcPGEGroNewCZ05 | Com-Iltg-dWatt-CFL_OSspc | PGE | Gro | New | CZ05 | 4.78 | 0.000755 | 0 | 4.26 | 0.000954 | -0.0731 | 4.78 | 0.000755 | 0 | 4.26 | 0.000954 | -0.0731 | CFL | AllSpc | 4780 | 0.755 | 4780 | 0.755 | 0.891 | 1.26 | -0.0153
CFLAllSpcSCEGroNewCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCE | Gro | New | CZ05 | 4.78 | 0.000755 | 0 | 4.69 | 0.000954 | -0.0798 | 4.78 | 0.000755 | 0 | 4.69 | 0.000954 | -0.0798 | CFL | AllSpc | 4780 | 0.755 | 4780 | 0.755 | 0.981 | 1.26 | -0.0167
CFLAllSpcSDGGroNewCZ06 | Com-Iltg-dWatt-CFL_OSspc | SDG | Gro | New | CZ06 | 4.78 | 0.000755 | 0 | 5 | 0.000952 | -0.0545 | 4.78 | 0.000755 | 0 | 5 | 0.000952 | -0.0545 | CFL | AllSpc | 4780 | 0.755 | 4780 | 0.755 | 1.05 | 1.26 | -0.0114
CFLAllSpcSCEGroNewCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCE | Gro | New | CZ06 | 4.78 | 0.000755 | 0 | 5.04 | 0.000958 | -0.0569 | 4.78 | 0.000755 | 0 | 5.04 | 0.000958 | -0.0569 | CFL | AllSpc | 4780 | 0.755 | 4780 | 0.755 | 1.05 | 1.27 | -0.0119
CFLAllSpcSDGGroNewCZ07 | Com-Iltg-dWatt-CFL_OSspc | SDG | Gro | New | CZ07 | 4.78 | 0.000755 | 0 | 4.95 | 0.000929 | -0.0569 | 4.78 | 0.000755 | 0 | 4.95 | 0.000929 | -0.0569 | CFL | AllSpc | 4780 | 0.755 | 4780 | 0.755 | 1.04 | 1.23 | -0.0119
CFLAllSpcSDGGroNewCZ08 | Com-Iltg-dWatt-CFL_OSspc | SDG | Gro | New | CZ08 | 4.78 | 0.000755 | 0 | 5.06 | 0.000969 | -0.0476 | 4.78 | 0.000755 | 0 | 5.06 | 0.000969 | -0.0476 | CFL | AllSpc | 4780 | 0.755 | 4780 | 0.755 | 1.06 | 1.28 | -0.00996
CFLAllSpcSCEGroNewCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCE | Gro | New | CZ08 | 4.78 | 0.000755 | 0 | 5.1 | 0.000975 | -0.0497 | 4.78 | 0.000755 | 0 | 5.1 | 0.000975 | -0.0497 | CFL | AllSpc | 4780 | 0.755 | 4780 | 0.755 | 1.07 | 1.29 | -0.0104
CFLAllSpcSCEGroNewCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCE | Gro | New | CZ09 | 4.78 | 0.000755 | 0 | 5.11 | 0.00103 | -0.0526 | 4.78 | 0.000755 | 0 | 5.11 | 0.00103 | -0.0526 | CFL | AllSpc | 4780 | 0.755 | 4780 | 0.755 | 1.07 | 1.36 | -0.011
CFLAllSpcSDGGroNewCZ10 | Com-Iltg-dWatt-CFL_OSspc | SDG | Gro | New | CZ10 | 4.78 | 0.000755 | 0 | 5.11 | 0.00106 | -0.0497 | 4.78 | 0.000755 | 0 | 5.11 | 0.00106 | -0.0497 | CFL | AllSpc | 4780 | 0.755 | 4780 | 0.755 | 1.07 | 1.4 | -0.0104
CFLAllSpcSCEGroNewCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCE | Gro | New | CZ10 | 4.78 | 0.000755 | 0 | 5.15 | 0.00107 | -0.0516 | 4.78 | 0.000755 | 0 | 5.15 | 0.00107 | -0.0516 | CFL | AllSpc | 4780 | 0.755 | 4780 | 0.755 | 1.08 | 1.42 | -0.0108
CFLAllSpcPGEGroNewCZ11 | Com-Iltg-dWatt-CFL_OSspc | PGE | Gro | New | CZ11 | 4.78 | 0.000755 | 0 | 4.84 | 0.00106 | -0.0521 | 4.78 | 0.000755 | 0 | 4.84 | 0.00106 | -0.0521 | CFL | AllSpc | 4780 | 0.755 | 4780 | 0.755 | 1.01 | 1.4 | -0.0109
CFLAllSpcPGEGroNewCZ12 | Com-Iltg-dWatt-CFL_OSspc | PGE | Gro | New | CZ12 | 4.78 | 0.000755 | 0 | 4.74 | 0.00106 | -0.0578 | 4.78 | 0.000755 | 0 | 4.74 | 0.00106 | -0.0578 | CFL | AllSpc | 4780 | 0.755 | 4780 | 0.755 | 0.992 | 1.4 | -0.0121
CFLAllSpcSCEGroNewCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCE | Gro | New | CZ13 | 4.78 | 0.000755 | 0 | 5.16 | 0.00104 | -0.054 | 4.78 | 0.000755 | 0 | 5.16 | 0.00104 | -0.054 | CFL | AllSpc | 4780 | 0.755 | 4780 | 0.755 | 1.08 | 1.38 | -0.0113
CFLAllSpcPGEGroNewCZ13 | Com-Iltg-dWatt-CFL_OSspc | PGE | Gro | New | CZ13 | 4.78 | 0.000755 | 0 | 4.89 | 0.00102 | -0.0492 | 4.78 | 0.000755 | 0 | 4.89 | 0.00102 | -0.0492 | CFL | AllSpc | 4780 | 0.755 | 4780 | 0.755 | 1.02 | 1.35 | -0.0103
CFLAllSpcSCEGroNewCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCE | Gro | New | CZ14 | 4.78 | 0.000755 | 0 | 5.17 | 0.00105 | -0.0569 | 4.78 | 0.000755 | 0 | 5.17 | 0.00105 | -0.0569 | CFL | AllSpc | 4780 | 0.755 | 4780 | 0.755 | 1.08 | 1.39 | -0.0119
CFLAllSpcSDGGroNewCZ14 | Com-Iltg-dWatt-CFL_OSspc | SDG | Gro | New | CZ14 | 4.78 | 0.000755 | 0 | 5.12 | 0.00104 | -0.0545 | 4.78 | 0.000755 | 0 | 5.12 | 0.00104 | -0.0545 | CFL | AllSpc | 4780 | 0.755 | 4780 | 0.755 | 1.07 | 1.38 | -0.0114
CFLAllSpcSCEGroNewCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCE | Gro | New | CZ15 | 4.78 | 0.000755 | 0 | 5.57 | 0.00107 | -0.0293 | 4.78 | 0.000755 | 0 | 5.57 | 0.00107 | -0.0293 | CFL | AllSpc | 4780 | 0.755 | 4780 | 0.755 | 1.17 | 1.42 | -0.00613
CFLAllSpcSDGGroNewCZ15 | Com-Iltg-dWatt-CFL_OSspc | SDG | Gro | New | CZ15 | 4.78 | 0.000755 | 0 | 5.53 | 0.00105 | -0.0282 | 4.78 | 0.000755 | 0 | 5.53 | 0.00105 | -0.0282 | CFL | AllSpc | 4780 | 0.755 | 4780 | 0.755 | 1.16 | 1.39 | -0.0059
CFLAllSpcSCEGroNewCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCE | Gro | New | CZ16 | 4.78 | 0.000755 | 0 | 4.69 | 0.000972 | -0.0741 | 4.78 | 0.000755 | 0 | 4.69 | 0.000972 | -0.0741 | CFL | AllSpc | 4780 | 0.755 | 4780 | 0.755 | 0.981 | 1.29 | -0.0155
CFLAllSpcPGEGroNewCZ16 | Com-Iltg-dWatt-CFL_OSspc | PGE | Gro | New | CZ16 | 4.78 | 0.000755 | 0 | 4.32 | 0.00096 | -0.0679 | 4.78 | 0.000755 | 0 | 4.32 | 0.00096 | -0.0679 | CFL | AllSpc | 4780 | 0.755 | 4780 | 0.755 | 0.904 | 1.27 | -0.0142
CFLAllSpcSCEGroNewIOU | Com-Iltg-dWatt-CFL_OSspc | SCE | Gro | New | IOU | 4.78 | 0.000755 | 0 | 5.1 | 0.00101 | -0.0493 | 4.78 | 0.000755 | 0 | 5.1 | 0.00101 | -0.0493 | CFL | AllSpc | 4780 | 0.755 | 4780 | 0.755 | 1.07 | 1.34 | -0.0103
CFLAllSpcSCGGroNewIOU | Com-Iltg-dWatt-CFL_OSspc | SCG | Gro | New | IOU | 4.78 | 0.000755 | 0 | 5.09 | 0.00101 | -0.0493 | 4.78 | 0.000755 | 0 | 5.09 | 0.00101 | -0.0493 | CFL | AllSpc | 4780 | 0.755 | 4780 | 0.755 | 1.06 | 1.34 | -0.0103
CFLAllSpcPGEGroNewIOU | Com-Iltg-dWatt-CFL_OSspc | PGE | Gro | New | IOU | 4.78 | 0.000755 | 0 | 5.09 | 0.00103 | -0.0576 | 4.78 | 0.000755 | 0 | 5.09 | 0.00103 | -0.0576 | CFL | AllSpc | 4780 | 0.755 | 4780 | 0.755 | 1.06 | 1.36 | -0.0121
CFLAllSpcSDGGroNewIOU | Com-Iltg-dWatt-CFL_OSspc | SDG | Gro | New | IOU | 4.78 | 0.000755 | 0 | 5 | 0.000967 | -0.0545 | 4.78 | 0.000755 | 0 | 5 | 0.000967 | -0.0545 | CFL | AllSpc | 4780 | 0.755 | 4780 | 0.755 | 1.05 | 1.28 | -0.0114
CFLAllSpcPGEHspExCZ01 | Com-Iltg-dWatt-CFL_OSspc | PGE | Hsp | Ex | CZ01 | 5.01 | 0.000762 | 0 | 5.37 | 0.000873 | -0.044 | 5.01 | 0.000762 | 0 | 5.37 | 0.000873 | -0.044 | CFL | AllSpc | 5010 | 0.762 | 5010 | 0.762 | 1.07 | 1.15 | -0.00878
CFLAllSpcPGEHspExCZ02 | Com-Iltg-dWatt-CFL_OSspc | PGE | Hsp | Ex | CZ02 | 5.01 | 0.000762 | 0 | 5.52 | 0.000936 | -0.0344 | 5.01 | 0.000762 | 0 | 5.52 | 0.000936 | -0.0344 | CFL | AllSpc | 5010 | 0.762 | 5010 | 0.762 | 1.1 | 1.23 | -0.00687
CFLAllSpcPGEHspExCZ03 | Com-Iltg-dWatt-CFL_OSspc | PGE | Hsp | Ex | CZ03 | 5.01 | 0.000762 | 0 | 5.54 | 0.000914 | -0.0326 | 5.01 | 0.000762 | 0 | 5.54 | 0.000914 | -0.0326 | CFL | AllSpc | 5010 | 0.762 | 5010 | 0.762 | 1.11 | 1.2 | -0.00651
CFLAllSpcPGEHspExCZ04 | Com-Iltg-dWatt-CFL_OSspc | PGE | Hsp | Ex | CZ04 | 5.01 | 0.000762 | 0 | 5.55 | 0.000929 | -0.031 | 5.01 | 0.000762 | 0 | 5.55 | 0.000929 | -0.031 | CFL | AllSpc | 5010 | 0.762 | 5010 | 0.762 | 1.11 | 1.22 | -0.00619
CFLAllSpcSCGHspExCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCG | Hsp | Ex | CZ05 | 5.01 | 0.000762 | 0 | 5.62 | 0.000927 | -0.0353 | 5.01 | 0.000762 | 0 | 5.62 | 0.000927 | -0.0353 | CFL | AllSpc | 5010 | 0.762 | 5010 | 0.762 | 1.12 | 1.22 | -0.00705
CFLAllSpcPGEHspExCZ05 | Com-Iltg-dWatt-CFL_OSspc | PGE | Hsp | Ex | CZ05 | 5.01 | 0.000762 | 0 | 5.62 | 0.000927 | -0.0353 | 5.01 | 0.000762 | 0 | 5.62 | 0.000927 | -0.0353 | CFL | AllSpc | 5010 | 0.762 | 5010 | 0.762 | 1.12 | 1.22 | -0.00705
CFLAllSpcSCEHspExCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCE | Hsp | Ex | CZ05 | 5.01 | 0.000762 | 0 | 5.62 | 0.000927 | -0.0353 | 5.01 | 0.000762 | 0 | 5.62 | 0.000927 | -0.0353 | CFL | AllSpc | 5010 | 0.762 | 5010 | 0.762 | 1.12 | 1.22 | -0.00705
CFLAllSpcSDGHspExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SDG | Hsp | Ex | CZ06 | 5.01 | 0.000762 | 0 | 5.73 | 0.000943 | -0.0269 | 5.01 | 0.000762 | 0 | 5.73 | 0.000943 | -0.0269 | CFL | AllSpc | 5010 | 0.762 | 5010 | 0.762 | 1.14 | 1.24 | -0.00537
CFLAllSpcSCGHspExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCG | Hsp | Ex | CZ06 | 5.01 | 0.000762 | 0 | 5.73 | 0.000943 | -0.0269 | 5.01 | 0.000762 | 0 | 5.73 | 0.000943 | -0.0269 | CFL | AllSpc | 5010 | 0.762 | 5010 | 0.762 | 1.14 | 1.24 | -0.00537
CFLAllSpcSCEHspExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCE | Hsp | Ex | CZ06 | 5.01 | 0.000762 | 0 | 5.73 | 0.000943 | -0.0269 | 5.01 | 0.000762 | 0 | 5.73 | 0.000943 | -0.0269 | CFL | AllSpc | 5010 | 0.762 | 5010 | 0.762 | 1.14 | 1.24 | -0.00537
CFLAllSpcSDGHspExCZ07 | Com-Iltg-dWatt-CFL_OSspc | SDG | Hsp | Ex | CZ07 | 5.01 | 0.000762 | 0 | 5.73 | 0.000934 | -0.0247 | 5.01 | 0.000762 | 0 | 5.73 | 0.000934 | -0.0247 | CFL | AllSpc | 5010 | 0.762 | 5010 | 0.762 | 1.14 | 1.23 | -0.00493
CFLAllSpcSCEHspExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCE | Hsp | Ex | CZ08 | 5.01 | 0.000762 | 0 | 5.76 | 0.000941 | -0.0265 | 5.01 | 0.000762 | 0 | 5.76 | 0.000941 | -0.0265 | CFL | AllSpc | 5010 | 0.762 | 5010 | 0.762 | 1.15 | 1.23 | -0.00529
CFLAllSpcSDGHspExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SDG | Hsp | Ex | CZ08 | 5.01 | 0.000762 | 0 | 5.76 | 0.000941 | -0.0265 | 5.01 | 0.000762 | 0 | 5.76 | 0.000941 | -0.0265 | CFL | AllSpc | 5010 | 0.762 | 5010 | 0.762 | 1.15 | 1.23 | -0.00529
CFLAllSpcSCGHspExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCG | Hsp | Ex | CZ08 | 5.01 | 0.000762 | 0 | 5.76 | 0.000941 | -0.0265 | 5.01 | 0.000762 | 0 | 5.76 | 0.000941 | -0.0265 | CFL | AllSpc | 5010 | 0.762 | 5010 | 0.762 | 1.15 | 1.23 | -0.00529
CFLAllSpcSCGHspExCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCG | Hsp | Ex | CZ09 | 5.01 | 0.000762 | 0 | 5.85 | 0.000977 | -0.0263 | 5.01 | 0.000762 | 0 | 5.85 | 0.000977 | -0.0263 | CFL | AllSpc | 5010 | 0.762 | 5010 | 0.762 | 1.17 | 1.28 | -0.00525
CFLAllSpcSCEHspExCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCE | Hsp | Ex | CZ09 | 5.01 | 0.000762 | 0 | 5.85 | 0.000977 | -0.0263 | 5.01 | 0.000762 | 0 | 5.85 | 0.000977 | -0.0263 | CFL | AllSpc | 5010 | 0.762 | 5010 | 0.762 | 1.17 | 1.28 | -0.00525
CFLAllSpcSCEHspExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCE | Hsp | Ex | CZ10 | 5.01 | 0.000762 | 0 | 5.75 | 0.000964 | -0.0283 | 5.01 | 0.000762 | 0 | 5.75 | 0.000964 | -0.0283 | CFL | AllSpc | 5010 | 0.762 | 5010 | 0.762 | 1.15 | 1.27 | -0.00565
CFLAllSpcSDGHspExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SDG | Hsp | Ex | CZ10 | 5.01 | 0.000762 | 0 | 5.75 | 0.000964 | -0.0283 | 5.01 | 0.000762 | 0 | 5.75 | 0.000964 | -0.0283 | CFL | AllSpc | 5010 | 0.762 | 5010 | 0.762 | 1.15 | 1.27 | -0.00565
CFLAllSpcSCGHspExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCG | Hsp | Ex | CZ10 | 5.01 | 0.000762 | 0 | 5.75 | 0.000964 | -0.0283 | 5.01 | 0.000762 | 0 | 5.75 | 0.000964 | -0.0283 | CFL | AllSpc | 5010 | 0.762 | 5010 | 0.762 | 1.15 | 1.27 | -0.00565
CFLAllSpcPGEHspExCZ11 | Com-Iltg-dWatt-CFL_OSspc | PGE | Hsp | Ex | CZ11 | 5.01 | 0.000762 | 0 | 5.57 | 0.000943 | -0.0324 | 5.01 | 0.000762 | 0 | 5.57 | 0.000943 | -0.0324 | CFL | AllSpc | 5010 | 0.762 | 5010 | 0.762 | 1.11 | 1.24 | -0.00647
CFLAllSpcPGEHspExCZ12 | Com-Iltg-dWatt-CFL_OSspc | PGE | Hsp | Ex | CZ12 | 5.01 | 0.000762 | 0 | 5.56 | 0.00094 | -0.0315 | 5.01 | 0.000762 | 0 | 5.56 | 0.00094 | -0.0315 | CFL | AllSpc | 5010 | 0.762 | 5010 | 0.762 | 1.11 | 1.23 | -0.00629
CFLAllSpcSCEHspExCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCE | Hsp | Ex | CZ13 | 5.01 | 0.000762 | 0 | 5.67 | 0.000961 | -0.0322 | 5.01 | 0.000762 | 0 | 5.67 | 0.000961 | -0.0322 | CFL | AllSpc | 5010 | 0.762 | 5010 | 0.762 | 1.13 | 1.26 | -0.00643
CFLAllSpcPGEHspExCZ13 | Com-Iltg-dWatt-CFL_OSspc | PGE | Hsp | Ex | CZ13 | 5.01 | 0.000762 | 0 | 5.67 | 0.000961 | -0.0322 | 5.01 | 0.000762 | 0 | 5.67 | 0.000961 | -0.0322 | CFL | AllSpc | 5010 | 0.762 | 5010 | 0.762 | 1.13 | 1.26 | -0.00643
CFLAllSpcSCGHspExCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCG | Hsp | Ex | CZ13 | 5.01 | 0.000762 | 0 | 5.67 | 0.000961 | -0.0322 | 5.01 | 0.000762 | 0 | 5.67 | 0.000961 | -0.0322 | CFL | AllSpc | 5010 | 0.762 | 5010 | 0.762 | 1.13 | 1.26 | -0.00643
CFLAllSpcSCEHspExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCE | Hsp | Ex | CZ14 | 5.01 | 0.000762 | 0 | 5.68 | 0.000958 | -0.0347 | 5.01 | 0.000762 | 0 | 5.68 | 0.000958 | -0.0347 | CFL | AllSpc | 5010 | 0.762 | 5010 | 0.762 | 1.13 | 1.26 | -0.00693
CFLAllSpcSCGHspExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCG | Hsp | Ex | CZ14 | 5.01 | 0.000762 | 0 | 5.68 | 0.000958 | -0.0347 | 5.01 | 0.000762 | 0 | 5.68 | 0.000958 | -0.0347 | CFL | AllSpc | 5010 | 0.762 | 5010 | 0.762 | 1.13 | 1.26 | -0.00693
CFLAllSpcSDGHspExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SDG | Hsp | Ex | CZ14 | 5.01 | 0.000762 | 0 | 5.68 | 0.000958 | -0.0347 | 5.01 | 0.000762 | 0 | 5.68 | 0.000958 | -0.0347 | CFL | AllSpc | 5010 | 0.762 | 5010 | 0.762 | 1.13 | 1.26 | -0.00693
CFLAllSpcSCGHspExCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCG | Hsp | Ex | CZ15 | 5.01 | 0.000762 | 0 | 5.84 | 0.000956 | -0.0229 | 5.01 | 0.000762 | 0 | 5.84 | 0.000956 | -0.0229 | CFL | AllSpc | 5010 | 0.762 | 5010 | 0.762 | 1.17 | 1.25 | -0.00457
CFLAllSpcSCEHspExCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCE | Hsp | Ex | CZ15 | 5.01 | 0.000762 | 0 | 5.84 | 0.000956 | -0.0229 | 5.01 | 0.000762 | 0 | 5.84 | 0.000956 | -0.0229 | CFL | AllSpc | 5010 | 0.762 | 5010 | 0.762 | 1.17 | 1.25 | -0.00457
CFLAllSpcSCGHspExCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCG | Hsp | Ex | CZ16 | 5.01 | 0.000762 | 0 | 5.3 | 0.000933 | -0.0473 | 5.01 | 0.000762 | 0 | 5.3 | 0.000933 | -0.0473 | CFL | AllSpc | 5010 | 0.762 | 5010 | 0.762 | 1.06 | 1.22 | -0.00944
CFLAllSpcSCEHspExCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCE | Hsp | Ex | CZ16 | 5.01 | 0.000762 | 0 | 5.3 | 0.000933 | -0.0473 | 5.01 | 0.000762 | 0 | 5.3 | 0.000933 | -0.0473 | CFL | AllSpc | 5010 | 0.762 | 5010 | 0.762 | 1.06 | 1.22 | -0.00944
CFLAllSpcPGEHspExCZ16 | Com-Iltg-dWatt-CFL_OSspc | PGE | Hsp | Ex | CZ16 | 5.01 | 0.000762 | 0 | 5.3 | 0.000933 | -0.0473 | 5.01 | 0.000762 | 0 | 5.3 | 0.000933 | -0.0473 | CFL | AllSpc | 5010 | 0.762 | 5010 | 0.762 | 1.06 | 1.22 | -0.00944
CFLAllSpcSCGHspExIOU | Com-Iltg-dWatt-CFL_OSspc | SCG | Hsp | Ex | IOU | 5.01 | 0.000762 | 0 | 5.77 | 0.000956 | -0.0274 | 5.01 | 0.000762 | 0 | 5.77 | 0.000956 | -0.0274 | CFL | AllSpc | 5010 | 0.762 | 5010 | 0.762 | 1.15 | 1.25 | -0.00547
CFLAllSpcSDGHspExIOU | Com-Iltg-dWatt-CFL_OSspc | SDG | Hsp | Ex | IOU | 5.01 | 0.000762 | 0 | 5.73 | 0.000939 | -0.0253 | 5.01 | 0.000762 | 0 | 5.73 | 0.000939 | -0.0253 | CFL | AllSpc | 5010 | 0.762 | 5010 | 0.762 | 1.14 | 1.23 | -0.00505
CFLAllSpcSCEHspExIOU | Com-Iltg-dWatt-CFL_OSspc | SCE | Hsp | Ex | IOU | 5.01 | 0.000762 | 0 | 5.75 | 0.000952 | -0.0277 | 5.01 | 0.000762 | 0 | 5.75 | 0.000952 | -0.0277 | CFL | AllSpc | 5010 | 0.762 | 5010 | 0.762 | 1.15 | 1.25 | -0.00553
CFLAllSpcPGEHspExIOU | Com-Iltg-dWatt-CFL_OSspc | PGE | Hsp | Ex | IOU | 5.01 | 0.000762 | 0 | 5.57 | 0.000933 | -0.0325 | 5.01 | 0.000762 | 0 | 5.57 | 0.000933 | -0.0325 | CFL | AllSpc | 5010 | 0.762 | 5010 | 0.762 | 1.11 | 1.22 | -0.00649
CFLAllSpcPGEHspNewCZ01 | Com-Iltg-dWatt-CFL_OSspc | PGE | Hsp | New | CZ01 | 5.01 | 0.000761 | 0 | 5.13 | 0.000831 | -0.0466 | 5.01 | 0.000761 | 0 | 5.13 | 0.000831 | -0.0466 | CFL | AllSpc | 5010 | 0.761 | 5010 | 0.761 | 1.02 | 1.09 | -0.0093
CFLAllSpcPGEHspNewCZ02 | Com-Iltg-dWatt-CFL_OSspc | PGE | Hsp | New | CZ02 | 5.01 | 0.000761 | 0 | 5.31 | 0.00091 | -0.0373 | 5.01 | 0.000761 | 0 | 5.31 | 0.00091 | -0.0373 | CFL | AllSpc | 5010 | 0.761 | 5010 | 0.761 | 1.06 | 1.2 | -0.00745
CFLAllSpcPGEHspNewCZ03 | Com-Iltg-dWatt-CFL_OSspc | PGE | Hsp | New | CZ03 | 5.01 | 0.000761 | 0 | 5.29 | 0.000887 | -0.0335 | 5.01 | 0.000761 | 0 | 5.29 | 0.000887 | -0.0335 | CFL | AllSpc | 5010 | 0.761 | 5010 | 0.761 | 1.06 | 1.17 | -0.00669
CFLAllSpcPGEHspNewCZ04 | Com-Iltg-dWatt-CFL_OSspc | PGE | Hsp | New | CZ04 | 5.01 | 0.000761 | 0 | 5.36 | 0.000903 | -0.0326 | 5.01 | 0.000761 | 0 | 5.36 | 0.000903 | -0.0326 | CFL | AllSpc | 5010 | 0.761 | 5010 | 0.761 | 1.07 | 1.19 | -0.00651
CFLAllSpcSCEHspNewCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCE | Hsp | New | CZ05 | 5.01 | 0.000761 | 0 | 5.29 | 0.000899 | -0.0374 | 5.01 | 0.000761 | 0 | 5.29 | 0.000899 | -0.0374 | CFL | AllSpc | 5010 | 0.761 | 5010 | 0.761 | 1.06 | 1.18 | -0.00747
CFLAllSpcPGEHspNewCZ05 | Com-Iltg-dWatt-CFL_OSspc | PGE | Hsp | New | CZ05 | 5.01 | 0.000761 | 0 | 5.26 | 0.000875 | -0.0376 | 5.01 | 0.000761 | 0 | 5.26 | 0.000875 | -0.0376 | CFL | AllSpc | 5010 | 0.761 | 5010 | 0.761 | 1.05 | 1.15 | -0.0075
CFLAllSpcSDGHspNewCZ06 | Com-Iltg-dWatt-CFL_OSspc | SDG | Hsp | New | CZ06 | 5.01 | 0.000761 | 0 | 5.48 | 0.000909 | -0.0286 | 5.01 | 0.000761 | 0 | 5.48 | 0.000909 | -0.0286 | CFL | AllSpc | 5010 | 0.761 | 5010 | 0.761 | 1.09 | 1.19 | -0.00571
CFLAllSpcSCEHspNewCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCE | Hsp | New | CZ06 | 5.01 | 0.000761 | 0 | 5.49 | 0.000916 | -0.0287 | 5.01 | 0.000761 | 0 | 5.49 | 0.000916 | -0.0287 | CFL | AllSpc | 5010 | 0.761 | 5010 | 0.761 | 1.1 | 1.2 | -0.00573
CFLAllSpcSDGHspNewCZ07 | Com-Iltg-dWatt-CFL_OSspc | SDG | Hsp | New | CZ07 | 5.01 | 0.000761 | 0 | 5.5 | 0.000904 | -0.0245 | 5.01 | 0.000761 | 0 | 5.5 | 0.000904 | -0.0245 | CFL | AllSpc | 5010 | 0.761 | 5010 | 0.761 | 1.1 | 1.19 | -0.00489
CFLAllSpcSCEHspNewCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCE | Hsp | New | CZ08 | 5.01 | 0.000761 | 0 | 5.54 | 0.000921 | -0.0265 | 5.01 | 0.000761 | 0 | 5.54 | 0.000921 | -0.0265 | CFL | AllSpc | 5010 | 0.761 | 5010 | 0.761 | 1.11 | 1.21 | -0.00529
CFLAllSpcSDGHspNewCZ08 | Com-Iltg-dWatt-CFL_OSspc | SDG | Hsp | New | CZ08 | 5.01 | 0.000761 | 0 | 5.54 | 0.000914 | -0.0265 | 5.01 | 0.000761 | 0 | 5.54 | 0.000914 | -0.0265 | CFL | AllSpc | 5010 | 0.761 | 5010 | 0.761 | 1.11 | 1.2 | -0.00529
CFLAllSpcSCEHspNewCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCE | Hsp | New | CZ09 | 5.01 | 0.000761 | 0 | 5.57 | 0.000946 | -0.027 | 5.01 | 0.000761 | 0 | 5.57 | 0.000946 | -0.027 | CFL | AllSpc | 5010 | 0.761 | 5010 | 0.761 | 1.11 | 1.24 | -0.00539
CFLAllSpcSDGHspNewCZ10 | Com-Iltg-dWatt-CFL_OSspc | SDG | Hsp | New | CZ10 | 5.01 | 0.000761 | 0 | 5.54 | 0.000942 | -0.0298 | 5.01 | 0.000761 | 0 | 5.54 | 0.000942 | -0.0298 | CFL | AllSpc | 5010 | 0.761 | 5010 | 0.761 | 1.11 | 1.24 | -0.00595
CFLAllSpcSCEHspNewCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCE | Hsp | New | CZ10 | 5.01 | 0.000761 | 0 | 5.54 | 0.000951 | -0.0296 | 5.01 | 0.000761 | 0 | 5.54 | 0.000951 | -0.0296 | CFL | AllSpc | 5010 | 0.761 | 5010 | 0.761 | 1.11 | 1.25 | -0.00591
CFLAllSpcPGEHspNewCZ11 | Com-Iltg-dWatt-CFL_OSspc | PGE | Hsp | New | CZ11 | 5.01 | 0.000761 | 0 | 5.43 | 0.000915 | -0.0348 | 5.01 | 0.000761 | 0 | 5.43 | 0.000915 | -0.0348 | CFL | AllSpc | 5010 | 0.761 | 5010 | 0.761 | 1.08 | 1.2 | -0.00695
CFLAllSpcPGEHspNewCZ12 | Com-Iltg-dWatt-CFL_OSspc | PGE | Hsp | New | CZ12 | 5.01 | 0.000761 | 0 | 5.39 | 0.000915 | -0.0338 | 5.01 | 0.000761 | 0 | 5.39 | 0.000915 | -0.0338 | CFL | AllSpc | 5010 | 0.761 | 5010 | 0.761 | 1.08 | 1.2 | -0.00675
CFLAllSpcSCEHspNewCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCE | Hsp | New | CZ13 | 5.01 | 0.000761 | 0 | 5.52 | 0.000946 | -0.0334 | 5.01 | 0.000761 | 0 | 5.52 | 0.000946 | -0.0334 | CFL | AllSpc | 5010 | 0.761 | 5010 | 0.761 | 1.1 | 1.24 | -0.00667
CFLAllSpcPGEHspNewCZ13 | Com-Iltg-dWatt-CFL_OSspc | PGE | Hsp | New | CZ13 | 5.01 | 0.000761 | 0 | 5.44 | 0.000913 | -0.033 | 5.01 | 0.000761 | 0 | 5.44 | 0.000913 | -0.033 | CFL | AllSpc | 5010 | 0.761 | 5010 | 0.761 | 1.09 | 1.2 | -0.00659
CFLAllSpcSCEHspNewCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCE | Hsp | New | CZ14 | 5.01 | 0.000761 | 0 | 5.46 | 0.000944 | -0.0368 | 5.01 | 0.000761 | 0 | 5.46 | 0.000944 | -0.0368 | CFL | AllSpc | 5010 | 0.761 | 5010 | 0.761 | 1.09 | 1.24 | -0.00735
CFLAllSpcSDGHspNewCZ14 | Com-Iltg-dWatt-CFL_OSspc | SDG | Hsp | New | CZ14 | 5.01 | 0.000761 | 0 | 5.46 | 0.000935 | -0.0371 | 5.01 | 0.000761 | 0 | 5.46 | 0.000935 | -0.0371 | CFL | AllSpc | 5010 | 0.761 | 5010 | 0.761 | 1.09 | 1.23 | -0.00741
CFLAllSpcSCEHspNewCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCE | Hsp | New | CZ15 | 5.01 | 0.000761 | 0 | 5.81 | 0.000958 | -0.0238 | 5.01 | 0.000761 | 0 | 5.81 | 0.000958 | -0.0238 | CFL | AllSpc | 5010 | 0.761 | 5010 | 0.761 | 1.16 | 1.26 | -0.00475
CFLAllSpcSDGHspNewCZ15 | Com-Iltg-dWatt-CFL_OSspc | SDG | Hsp | New | CZ15 | 5.01 | 0.000761 | 0 | 5.79 | 0.000949 | -0.024 | 5.01 | 0.000761 | 0 | 5.79 | 0.000949 | -0.024 | CFL | AllSpc | 5010 | 0.761 | 5010 | 0.761 | 1.16 | 1.25 | -0.00479
CFLAllSpcPGEHspNewCZ16 | Com-Iltg-dWatt-CFL_OSspc | PGE | Hsp | New | CZ16 | 5.01 | 0.000761 | 0 | 5.07 | 0.000885 | -0.0556 | 5.01 | 0.000761 | 0 | 5.07 | 0.000885 | -0.0556 | CFL | AllSpc | 5010 | 0.761 | 5010 | 0.761 | 1.01 | 1.16 | -0.0111
CFLAllSpcSCEHspNewCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCE | Hsp | New | CZ16 | 5.01 | 0.000761 | 0 | 5.06 | 0.00091 | -0.0531 | 5.01 | 0.000761 | 0 | 5.06 | 0.00091 | -0.0531 | CFL | AllSpc | 5010 | 0.761 | 5010 | 0.761 | 1.01 | 1.2 | -0.0106
CFLAllSpcPGEHspNewIOU | Com-Iltg-dWatt-CFL_OSspc | PGE | Hsp | New | IOU | 5.01 | 0.000761 | 0 | 5.49 | 0.000941 | -0.0341 | 5.01 | 0.000761 | 0 | 5.49 | 0.000941 | -0.0341 | CFL | AllSpc | 5010 | 0.761 | 5010 | 0.761 | 1.1 | 1.24 | -0.00681
CFLAllSpcSDGHspNewIOU | Com-Iltg-dWatt-CFL_OSspc | SDG | Hsp | New | IOU | 5.01 | 0.000761 | 0 | 5.51 | 0.00091 | -0.0254 | 5.01 | 0.000761 | 0 | 5.51 | 0.00091 | -0.0254 | CFL | AllSpc | 5010 | 0.761 | 5010 | 0.761 | 1.1 | 1.2 | -0.00507
CFLAllSpcSCGHspNewIOU | Com-Iltg-dWatt-CFL_OSspc | SCG | Hsp | New | IOU | 5.01 | 0.000761 | 0 | 5.53 | 0.000924 | -0.0284 | 5.01 | 0.000761 | 0 | 5.53 | 0.000924 | -0.0284 | CFL | AllSpc | 5010 | 0.761 | 5010 | 0.761 | 1.1 | 1.21 | -0.00567
CFLAllSpcSCEHspNewIOU | Com-Iltg-dWatt-CFL_OSspc | SCE | Hsp | New | IOU | 5.01 | 0.000761 | 0 | 5.54 | 0.000925 | -0.0285 | 5.01 | 0.000761 | 0 | 5.54 | 0.000925 | -0.0285 | CFL | AllSpc | 5010 | 0.761 | 5010 | 0.761 | 1.11 | 1.22 | -0.00569
CFLAllSpcPGEHtlExCZ01 | Com-Iltg-dWatt-CFL_OSspc | PGE | Htl | Ex | CZ01 | 1.41 | 0.00017 | 0 | 1.28 | 0.000204 | -0.0074 | 1.41 | 0.00017 | 0 | 1.28 | 0.000204 | -0.0074 | CFL | AllSpc | 1410 | 0.17 | 1410 | 0.17 | 0.908 | 1.2 | -0.00525
CFLAllSpcPGEHtlExCZ02 | Com-Iltg-dWatt-CFL_OSspc | PGE | Htl | Ex | CZ02 | 1.41 | 0.00017 | 0 | 1.39 | 0.000211 | -0.00539 | 1.41 | 0.00017 | 0 | 1.39 | 0.000211 | -0.00539 | CFL | AllSpc | 1410 | 0.17 | 1410 | 0.17 | 0.986 | 1.24 | -0.00382
CFLAllSpcPGEHtlExCZ03 | Com-Iltg-dWatt-CFL_OSspc | PGE | Htl | Ex | CZ03 | 1.41 | 0.00017 | 0 | 1.41 | 0.000208 | -0.00519 | 1.41 | 0.00017 | 0 | 1.41 | 0.000208 | -0.00519 | CFL | AllSpc | 1410 | 0.17 | 1410 | 0.17 | 1 | 1.22 | -0.00368
CFLAllSpcPGEHtlExCZ04 | Com-Iltg-dWatt-CFL_OSspc | PGE | Htl | Ex | CZ04 | 1.41 | 0.00017 | 0 | 1.44 | 0.000211 | -0.00436 | 1.41 | 0.00017 | 0 | 1.44 | 0.000211 | -0.00436 | CFL | AllSpc | 1410 | 0.17 | 1410 | 0.17 | 1.02 | 1.24 | -0.00309
CFLAllSpcPGEHtlExCZ05 | Com-Iltg-dWatt-CFL_OSspc | PGE | Htl | Ex | CZ05 | 1.41 | 0.00017 | 0 | 1.42 | 0.000213 | -0.00423 | 1.41 | 0.00017 | 0 | 1.42 | 0.000213 | -0.00423 | CFL | AllSpc | 1410 | 0.17 | 1410 | 0.17 | 1.01 | 1.25 | -0.003
CFLAllSpcSCEHtlExCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCE | Htl | Ex | CZ05 | 1.41 | 0.00017 | 0 | 1.42 | 0.000213 | -0.00423 | 1.41 | 0.00017 | 0 | 1.42 | 0.000213 | -0.00423 | CFL | AllSpc | 1410 | 0.17 | 1410 | 0.17 | 1.01 | 1.25 | -0.003
CFLAllSpcSCGHtlExCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCG | Htl | Ex | CZ05 | 1.41 | 0.00017 | 0 | 1.42 | 0.000213 | -0.00423 | 1.41 | 0.00017 | 0 | 1.42 | 0.000213 | -0.00423 | CFL | AllSpc | 1410 | 0.17 | 1410 | 0.17 | 1.01 | 1.25 | -0.003
CFLAllSpcSCEHtlExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCE | Htl | Ex | CZ06 | 1.41 | 0.00017 | 0 | 1.53 | 0.000213 | -0.00286 | 1.41 | 0.00017 | 0 | 1.53 | 0.000213 | -0.00286 | CFL | AllSpc | 1410 | 0.17 | 1410 | 0.17 | 1.09 | 1.25 | -0.00203
CFLAllSpcSDGHtlExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SDG | Htl | Ex | CZ06 | 1.41 | 0.00017 | 0 | 1.53 | 0.000213 | -0.00286 | 1.41 | 0.00017 | 0 | 1.53 | 0.000213 | -0.00286 | CFL | AllSpc | 1410 | 0.17 | 1410 | 0.17 | 1.09 | 1.25 | -0.00203
CFLAllSpcSCGHtlExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCG | Htl | Ex | CZ06 | 1.41 | 0.00017 | 0 | 1.53 | 0.000213 | -0.00286 | 1.41 | 0.00017 | 0 | 1.53 | 0.000213 | -0.00286 | CFL | AllSpc | 1410 | 0.17 | 1410 | 0.17 | 1.09 | 1.25 | -0.00203
CFLAllSpcSDGHtlExCZ07 | Com-Iltg-dWatt-CFL_OSspc | SDG | Htl | Ex | CZ07 | 1.41 | 0.00017 | 0 | 1.56 | 0.000211 | -0.00223 | 1.41 | 0.00017 | 0 | 1.56 | 0.000211 | -0.00223 | CFL | AllSpc | 1410 | 0.17 | 1410 | 0.17 | 1.11 | 1.24 | -0.00158
CFLAllSpcSDGHtlExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SDG | Htl | Ex | CZ08 | 1.41 | 0.00017 | 0 | 1.56 | 0.000214 | -0.00258 | 1.41 | 0.00017 | 0 | 1.56 | 0.000214 | -0.00258 | CFL | AllSpc | 1410 | 0.17 | 1410 | 0.17 | 1.11 | 1.26 | -0.00183
CFLAllSpcSCEHtlExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCE | Htl | Ex | CZ08 | 1.41 | 0.00017 | 0 | 1.56 | 0.000214 | -0.00258 | 1.41 | 0.00017 | 0 | 1.56 | 0.000214 | -0.00258 | CFL | AllSpc | 1410 | 0.17 | 1410 | 0.17 | 1.11 | 1.26 | -0.00183
CFLAllSpcSCGHtlExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCG | Htl | Ex | CZ08 | 1.41 | 0.00017 | 0 | 1.56 | 0.000214 | -0.00258 | 1.41 | 0.00017 | 0 | 1.56 | 0.000214 | -0.00258 | CFL | AllSpc | 1410 | 0.17 | 1410 | 0.17 | 1.11 | 1.26 | -0.00183
CFLAllSpcSCGHtlExCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCG | Htl | Ex | CZ09 | 1.41 | 0.00017 | 0 | 1.57 | 0.00022 | -0.00259 | 1.41 | 0.00017 | 0 | 1.57 | 0.00022 | -0.00259 | CFL | AllSpc | 1410 | 0.17 | 1410 | 0.17 | 1.11 | 1.29 | -0.00184
CFLAllSpcSCEHtlExCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCE | Htl | Ex | CZ09 | 1.41 | 0.00017 | 0 | 1.57 | 0.00022 | -0.00259 | 1.41 | 0.00017 | 0 | 1.57 | 0.00022 | -0.00259 | CFL | AllSpc | 1410 | 0.17 | 1410 | 0.17 | 1.11 | 1.29 | -0.00184
CFLAllSpcSDGHtlExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SDG | Htl | Ex | CZ10 | 1.41 | 0.00017 | 0 | 1.53 | 0.000218 | -0.00299 | 1.41 | 0.00017 | 0 | 1.53 | 0.000218 | -0.00299 | CFL | AllSpc | 1410 | 0.17 | 1410 | 0.17 | 1.09 | 1.28 | -0.00212
CFLAllSpcSCEHtlExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCE | Htl | Ex | CZ10 | 1.41 | 0.00017 | 0 | 1.53 | 0.000218 | -0.00299 | 1.41 | 0.00017 | 0 | 1.53 | 0.000218 | -0.00299 | CFL | AllSpc | 1410 | 0.17 | 1410 | 0.17 | 1.09 | 1.28 | -0.00212
CFLAllSpcSCGHtlExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCG | Htl | Ex | CZ10 | 1.41 | 0.00017 | 0 | 1.53 | 0.000218 | -0.00299 | 1.41 | 0.00017 | 0 | 1.53 | 0.000218 | -0.00299 | CFL | AllSpc | 1410 | 0.17 | 1410 | 0.17 | 1.09 | 1.28 | -0.00212
CFLAllSpcPGEHtlExCZ11 | Com-Iltg-dWatt-CFL_OSspc | PGE | Htl | Ex | CZ11 | 1.41 | 0.00017 | 0 | 1.46 | 0.000215 | -0.00471 | 1.41 | 0.00017 | 0 | 1.46 | 0.000215 | -0.00471 | CFL | AllSpc | 1410 | 0.17 | 1410 | 0.17 | 1.04 | 1.26 | -0.00334
CFLAllSpcPGEHtlExCZ12 | Com-Iltg-dWatt-CFL_OSspc | PGE | Htl | Ex | CZ12 | 1.41 | 0.00017 | 0 | 1.43 | 0.000214 | -0.00479 | 1.41 | 0.00017 | 0 | 1.43 | 0.000214 | -0.00479 | CFL | AllSpc | 1410 | 0.17 | 1410 | 0.17 | 1.01 | 1.26 | -0.0034
CFLAllSpcPGEHtlExCZ13 | Com-Iltg-dWatt-CFL_OSspc | PGE | Htl | Ex | CZ13 | 1.41 | 0.00017 | 0 | 1.49 | 0.000218 | -0.00368 | 1.41 | 0.00017 | 0 | 1.49 | 0.000218 | -0.00368 | CFL | AllSpc | 1410 | 0.17 | 1410 | 0.17 | 1.06 | 1.28 | -0.00261
CFLAllSpcSCGHtlExCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCG | Htl | Ex | CZ13 | 1.41 | 0.00017 | 0 | 1.49 | 0.000218 | -0.00368 | 1.41 | 0.00017 | 0 | 1.49 | 0.000218 | -0.00368 | CFL | AllSpc | 1410 | 0.17 | 1410 | 0.17 | 1.06 | 1.28 | -0.00261
CFLAllSpcSCEHtlExCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCE | Htl | Ex | CZ13 | 1.41 | 0.00017 | 0 | 1.49 | 0.000218 | -0.00368 | 1.41 | 0.00017 | 0 | 1.49 | 0.000218 | -0.00368 | CFL | AllSpc | 1410 | 0.17 | 1410 | 0.17 | 1.06 | 1.28 | -0.00261
CFLAllSpcSCEHtlExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCE | Htl | Ex | CZ14 | 1.41 | 0.00017 | 0 | 1.47 | 0.000218 | -0.00407 | 1.41 | 0.00017 | 0 | 1.47 | 0.000218 | -0.00407 | CFL | AllSpc | 1410 | 0.17 | 1410 | 0.17 | 1.04 | 1.28 | -0.00289
CFLAllSpcSCGHtlExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCG | Htl | Ex | CZ14 | 1.41 | 0.00017 | 0 | 1.47 | 0.000218 | -0.00407 | 1.41 | 0.00017 | 0 | 1.47 | 0.000218 | -0.00407 | CFL | AllSpc | 1410 | 0.17 | 1410 | 0.17 | 1.04 | 1.28 | -0.00289
CFLAllSpcSDGHtlExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SDG | Htl | Ex | CZ14 | 1.41 | 0.00017 | 0 | 1.47 | 0.000218 | -0.00407 | 1.41 | 0.00017 | 0 | 1.47 | 0.000218 | -0.00407 | CFL | AllSpc | 1410 | 0.17 | 1410 | 0.17 | 1.04 | 1.28 | -0.00289
CFLAllSpcSCGHtlExCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCG | Htl | Ex | CZ15 | 1.41 | 0.00017 | 0 | 1.64 | 0.000219 | -0.00172 | 1.41 | 0.00017 | 0 | 1.64 | 0.000219 | -0.00172 | CFL | AllSpc | 1410 | 0.17 | 1410 | 0.17 | 1.16 | 1.29 | -0.00122
CFLAllSpcSDGHtlExCZ15 | Com-Iltg-dWatt-CFL_OSspc | SDG | Htl | Ex | CZ15 | 1.41 | 0.00017 | 0 | 1.64 | 0.000219 | -0.00172 | 1.41 | 0.00017 | 0 | 1.64 | 0.000219 | -0.00172 | CFL | AllSpc | 1410 | 0.17 | 1410 | 0.17 | 1.16 | 1.29 | -0.00122
CFLAllSpcSCEHtlExCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCE | Htl | Ex | CZ15 | 1.41 | 0.00017 | 0 | 1.64 | 0.000219 | -0.00172 | 1.41 | 0.00017 | 0 | 1.64 | 0.000219 | -0.00172 | CFL | AllSpc | 1410 | 0.17 | 1410 | 0.17 | 1.16 | 1.29 | -0.00122
CFLAllSpcPGEHtlExCZ16 | Com-Iltg-dWatt-CFL_OSspc | PGE | Htl | Ex | CZ16 | 1.41 | 0.00017 | 0 | 1.29 | 0.000214 | -0.00605 | 1.41 | 0.00017 | 0 | 1.29 | 0.000214 | -0.00605 | CFL | AllSpc | 1410 | 0.17 | 1410 | 0.17 | 0.915 | 1.26 | -0.00429
CFLAllSpcSCEHtlExCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCE | Htl | Ex | CZ16 | 1.41 | 0.00017 | 0 | 1.29 | 0.000214 | -0.00605 | 1.41 | 0.00017 | 0 | 1.29 | 0.000214 | -0.00605 | CFL | AllSpc | 1410 | 0.17 | 1410 | 0.17 | 0.915 | 1.26 | -0.00429
CFLAllSpcSCGHtlExCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCG | Htl | Ex | CZ16 | 1.41 | 0.00017 | 0 | 1.29 | 0.000214 | -0.00605 | 1.41 | 0.00017 | 0 | 1.29 | 0.000214 | -0.00605 | CFL | AllSpc | 1410 | 0.17 | 1410 | 0.17 | 0.915 | 1.26 | -0.00429
CFLAllSpcSCEHtlExIOU | Com-Iltg-dWatt-CFL_OSspc | SCE | Htl | Ex | IOU | 1.41 | 0.00017 | 0 | 1.55 | 0.000216 | -0.00276 | 1.41 | 0.00017 | 0 | 1.55 | 0.000216 | -0.00276 | CFL | AllSpc | 1410 | 0.17 | 1410 | 0.17 | 1.1 | 1.27 | -0.00196
CFLAllSpcSCGHtlExIOU | Com-Iltg-dWatt-CFL_OSspc | SCG | Htl | Ex | IOU | 1.41 | 0.00017 | 0 | 1.55 | 0.000216 | -0.00273 | 1.41 | 0.00017 | 0 | 1.55 | 0.000216 | -0.00273 | CFL | AllSpc | 1410 | 0.17 | 1410 | 0.17 | 1.1 | 1.27 | -0.00194
CFLAllSpcSDGHtlExIOU | Com-Iltg-dWatt-CFL_OSspc | SDG | Htl | Ex | IOU | 1.41 | 0.00017 | 0 | 1.56 | 0.000212 | -0.00234 | 1.41 | 0.00017 | 0 | 1.56 | 0.000212 | -0.00234 | CFL | AllSpc | 1410 | 0.17 | 1410 | 0.17 | 1.11 | 1.25 | -0.00166
CFLAllSpcPGEHtlExIOU | Com-Iltg-dWatt-CFL_OSspc | PGE | Htl | Ex | IOU | 1.41 | 0.00017 | 0 | 1.42 | 0.000211 | -0.00487 | 1.41 | 0.00017 | 0 | 1.42 | 0.000211 | -0.00487 | CFL | AllSpc | 1410 | 0.17 | 1410 | 0.17 | 1.01 | 1.24 | -0.00345
CFLAllSpcPGEHtlNewCZ01 | Com-Iltg-dWatt-CFL_OSspc | PGE | Htl | New | CZ01 | 1.42 | 0.00017 | 0 | 1.25 | 0.000203 | -0.00825 | 1.42 | 0.00017 | 0 | 1.25 | 0.000203 | -0.00825 | CFL | AllSpc | 1420 | 0.17 | 1420 | 0.17 | 0.88 | 1.19 | -0.00581
CFLAllSpcPGEHtlNewCZ02 | Com-Iltg-dWatt-CFL_OSspc | PGE | Htl | New | CZ02 | 1.42 | 0.00017 | 0 | 1.38 | 0.000216 | -0.00645 | 1.42 | 0.00017 | 0 | 1.38 | 0.000216 | -0.00645 | CFL | AllSpc | 1420 | 0.17 | 1420 | 0.17 | 0.972 | 1.27 | -0.00454
CFLAllSpcPGEHtlNewCZ03 | Com-Iltg-dWatt-CFL_OSspc | PGE | Htl | New | CZ03 | 1.42 | 0.00017 | 0 | 1.38 | 0.000209 | -0.00589 | 1.42 | 0.00017 | 0 | 1.38 | 0.000209 | -0.00589 | CFL | AllSpc | 1420 | 0.17 | 1420 | 0.17 | 0.972 | 1.23 | -0.00415
CFLAllSpcPGEHtlNewCZ04 | Com-Iltg-dWatt-CFL_OSspc | PGE | Htl | New | CZ04 | 1.42 | 0.00017 | 0 | 1.44 | 0.000216 | -0.00508 | 1.42 | 0.00017 | 0 | 1.44 | 0.000216 | -0.00508 | CFL | AllSpc | 1420 | 0.17 | 1420 | 0.17 | 1.01 | 1.27 | -0.00358
CFLAllSpcPGEHtlNewCZ05 | Com-Iltg-dWatt-CFL_OSspc | PGE | Htl | New | CZ05 | 1.42 | 0.00017 | 0 | 1.37 | 0.000207 | -0.00626 | 1.42 | 0.00017 | 0 | 1.37 | 0.000207 | -0.00626 | CFL | AllSpc | 1420 | 0.17 | 1420 | 0.17 | 0.965 | 1.22 | -0.00441
CFLAllSpcSCEHtlNewCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCE | Htl | New | CZ05 | 1.42 | 0.00017 | 0 | 1.36 | 0.000215 | -0.00447 | 1.42 | 0.00017 | 0 | 1.36 | 0.000215 | -0.00447 | CFL | AllSpc | 1420 | 0.17 | 1420 | 0.17 | 0.958 | 1.26 | -0.00315
CFLAllSpcSCEHtlNewCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCE | Htl | New | CZ06 | 1.42 | 0.00017 | 0 | 1.54 | 0.000218 | -0.00246 | 1.42 | 0.00017 | 0 | 1.54 | 0.000218 | -0.00246 | CFL | AllSpc | 1420 | 0.17 | 1420 | 0.17 | 1.08 | 1.28 | -0.00173
CFLAllSpcSDGHtlNewCZ06 | Com-Iltg-dWatt-CFL_OSspc | SDG | Htl | New | CZ06 | 1.42 | 0.00017 | 0 | 1.54 | 0.000217 | -0.00268 | 1.42 | 0.00017 | 0 | 1.54 | 0.000217 | -0.00268 | CFL | AllSpc | 1420 | 0.17 | 1420 | 0.17 | 1.08 | 1.28 | -0.00189
CFLAllSpcSDGHtlNewCZ07 | Com-Iltg-dWatt-CFL_OSspc | SDG | Htl | New | CZ07 | 1.42 | 0.00017 | 0 | 1.57 | 0.000213 | -0.00193 | 1.42 | 0.00017 | 0 | 1.57 | 0.000213 | -0.00193 | CFL | AllSpc | 1420 | 0.17 | 1420 | 0.17 | 1.11 | 1.25 | -0.00136
CFLAllSpcSCEHtlNewCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCE | Htl | New | CZ08 | 1.42 | 0.00017 | 0 | 1.56 | 0.00022 | -0.00216 | 1.42 | 0.00017 | 0 | 1.56 | 0.00022 | -0.00216 | CFL | AllSpc | 1420 | 0.17 | 1420 | 0.17 | 1.1 | 1.29 | -0.00152
CFLAllSpcSDGHtlNewCZ08 | Com-Iltg-dWatt-CFL_OSspc | SDG | Htl | New | CZ08 | 1.42 | 0.00017 | 0 | 1.56 | 0.000218 | -0.00236 | 1.42 | 0.00017 | 0 | 1.56 | 0.000218 | -0.00236 | CFL | AllSpc | 1420 | 0.17 | 1420 | 0.17 | 1.1 | 1.28 | -0.00166
CFLAllSpcSCEHtlNewCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCE | Htl | New | CZ09 | 1.42 | 0.00017 | 0 | 1.55 | 0.000225 | -0.00246 | 1.42 | 0.00017 | 0 | 1.55 | 0.000225 | -0.00246 | CFL | AllSpc | 1420 | 0.17 | 1420 | 0.17 | 1.09 | 1.32 | -0.00173
CFLAllSpcSDGHtlNewCZ10 | Com-Iltg-dWatt-CFL_OSspc | SDG | Htl | New | CZ10 | 1.42 | 0.00017 | 0 | 1.54 | 0.000229 | -0.00295 | 1.42 | 0.00017 | 0 | 1.54 | 0.000229 | -0.00295 | CFL | AllSpc | 1420 | 0.17 | 1420 | 0.17 | 1.08 | 1.35 | -0.00208
CFLAllSpcSCEHtlNewCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCE | Htl | New | CZ10 | 1.42 | 0.00017 | 0 | 1.54 | 0.000232 | -0.00273 | 1.42 | 0.00017 | 0 | 1.54 | 0.000232 | -0.00273 | CFL | AllSpc | 1420 | 0.17 | 1420 | 0.17 | 1.08 | 1.36 | -0.00192
CFLAllSpcPGEHtlNewCZ11 | Com-Iltg-dWatt-CFL_OSspc | PGE | Htl | New | CZ11 | 1.42 | 0.00017 | 0 | 1.45 | 0.000217 | -0.00559 | 1.42 | 0.00017 | 0 | 1.45 | 0.000217 | -0.00559 | CFL | AllSpc | 1420 | 0.17 | 1420 | 0.17 | 1.02 | 1.28 | -0.00394
CFLAllSpcPGEHtlNewCZ12 | Com-Iltg-dWatt-CFL_OSspc | PGE | Htl | New | CZ12 | 1.42 | 0.00017 | 0 | 1.43 | 0.000217 | -0.00565 | 1.42 | 0.00017 | 0 | 1.43 | 0.000217 | -0.00565 | CFL | AllSpc | 1420 | 0.17 | 1420 | 0.17 | 1.01 | 1.28 | -0.00398
CFLAllSpcPGEHtlNewCZ13 | Com-Iltg-dWatt-CFL_OSspc | PGE | Htl | New | CZ13 | 1.42 | 0.00017 | 0 | 1.47 | 0.000215 | -0.00513 | 1.42 | 0.00017 | 0 | 1.47 | 0.000215 | -0.00513 | CFL | AllSpc | 1420 | 0.17 | 1420 | 0.17 | 1.04 | 1.26 | -0.00361
CFLAllSpcSCEHtlNewCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCE | Htl | New | CZ13 | 1.42 | 0.00017 | 0 | 1.48 | 0.000225 | -0.00373 | 1.42 | 0.00017 | 0 | 1.48 | 0.000225 | -0.00373 | CFL | AllSpc | 1420 | 0.17 | 1420 | 0.17 | 1.04 | 1.32 | -0.00263
CFLAllSpcSDGHtlNewCZ14 | Com-Iltg-dWatt-CFL_OSspc | SDG | Htl | New | CZ14 | 1.42 | 0.00017 | 0 | 1.45 | 0.000225 | -0.00443 | 1.42 | 0.00017 | 0 | 1.45 | 0.000225 | -0.00443 | CFL | AllSpc | 1420 | 0.17 | 1420 | 0.17 | 1.02 | 1.32 | -0.00312
CFLAllSpcSCEHtlNewCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCE | Htl | New | CZ14 | 1.42 | 0.00017 | 0 | 1.45 | 0.000227 | -0.0041 | 1.42 | 0.00017 | 0 | 1.45 | 0.000227 | -0.0041 | CFL | AllSpc | 1420 | 0.17 | 1420 | 0.17 | 1.02 | 1.34 | -0.00289
CFLAllSpcSCEHtlNewCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCE | Htl | New | CZ15 | 1.42 | 0.00017 | 0 | 1.67 | 0.00023 | -0.00136 | 1.42 | 0.00017 | 0 | 1.67 | 0.00023 | -0.00136 | CFL | AllSpc | 1420 | 0.17 | 1420 | 0.17 | 1.18 | 1.35 | -0.000958
CFLAllSpcSDGHtlNewCZ15 | Com-Iltg-dWatt-CFL_OSspc | SDG | Htl | New | CZ15 | 1.42 | 0.00017 | 0 | 1.66 | 0.000228 | -0.00149 | 1.42 | 0.00017 | 0 | 1.66 | 0.000228 | -0.00149 | CFL | AllSpc | 1420 | 0.17 | 1420 | 0.17 | 1.17 | 1.34 | -0.00105
CFLAllSpcPGEHtlNewCZ16 | Com-Iltg-dWatt-CFL_OSspc | PGE | Htl | New | CZ16 | 1.42 | 0.00017 | 0 | 1.28 | 0.000209 | -0.00929 | 1.42 | 0.00017 | 0 | 1.28 | 0.000209 | -0.00929 | CFL | AllSpc | 1420 | 0.17 | 1420 | 0.17 | 0.901 | 1.23 | -0.00654
CFLAllSpcSCEHtlNewCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCE | Htl | New | CZ16 | 1.42 | 0.00017 | 0 | 1.25 | 0.000218 | -0.00696 | 1.42 | 0.00017 | 0 | 1.25 | 0.000218 | -0.00696 | CFL | AllSpc | 1420 | 0.17 | 1420 | 0.17 | 0.88 | 1.28 | -0.0049
CFLAllSpcPGEHtlNewIOU | Com-Iltg-dWatt-CFL_OSspc | PGE | Htl | New | IOU | 1.42 | 0.00017 | 0 | 1.41 | 0.000221 | -0.00432 | 1.42 | 0.00017 | 0 | 1.41 | 0.000221 | -0.00432 | CFL | AllSpc | 1420 | 0.17 | 1420 | 0.17 | 0.993 | 1.3 | -0.00304
CFLAllSpcSCEHtlNewIOU | Com-Iltg-dWatt-CFL_OSspc | SCE | Htl | New | IOU | 1.42 | 0.00017 | 0 | 1.58 | 0.000223 | -0.00236 | 1.42 | 0.00017 | 0 | 1.58 | 0.000223 | -0.00236 | CFL | AllSpc | 1420 | 0.17 | 1420 | 0.17 | 1.11 | 1.31 | -0.00166
CFLAllSpcSDGHtlNewIOU | Com-Iltg-dWatt-CFL_OSspc | SDG | Htl | New | IOU | 1.42 | 0.00017 | 0 | 1.57 | 0.000215 | -0.00208 | 1.42 | 0.00017 | 0 | 1.57 | 0.000215 | -0.00208 | CFL | AllSpc | 1420 | 0.17 | 1420 | 0.17 | 1.11 | 1.26 | -0.00146
CFLAllSpcSCGHtlNewIOU | Com-Iltg-dWatt-CFL_OSspc | SCG | Htl | New | IOU | 1.42 | 0.00017 | 0 | 1.58 | 0.000222 | -0.00238 | 1.42 | 0.00017 | 0 | 1.58 | 0.000222 | -0.00238 | CFL | AllSpc | 1420 | 0.17 | 1420 | 0.17 | 1.11 | 1.31 | -0.00168
CFLAllSpcPGEMBTExCZ01 | Com-Iltg-dWatt-CFL_OSspc | PGE | MBT | Ex | CZ01 | 1.83 | 0.000459 | 0 | 1.97 | 0.000541 | -0.0021 | 1.83 | 0.000459 | 0 | 1.97 | 0.000541 | -0.0021 | CFL | AllSpc | 1830 | 0.459 | 1830 | 0.459 | 1.08 | 1.18 | -0.00115
CFLAllSpcPGEMBTExCZ02 | Com-Iltg-dWatt-CFL_OSspc | PGE | MBT | Ex | CZ02 | 1.83 | 0.000459 | 0 | 2.03 | 0.000542 | -0.00106 | 1.83 | 0.000459 | 0 | 2.03 | 0.000542 | -0.00106 | CFL | AllSpc | 1830 | 0.459 | 1830 | 0.459 | 1.11 | 1.18 | -0.000579
CFLAllSpcPGEMBTExCZ03 | Com-Iltg-dWatt-CFL_OSspc | PGE | MBT | Ex | CZ03 | 1.83 | 0.000459 | 0 | 2.05 | 0.000543 | -0.000924 | 1.83 | 0.000459 | 0 | 2.05 | 0.000543 | -0.000924 | CFL | AllSpc | 1830 | 0.459 | 1830 | 0.459 | 1.12 | 1.18 | -0.000505
CFLAllSpcPGEMBTExCZ04 | Com-Iltg-dWatt-CFL_OSspc | PGE | MBT | Ex | CZ04 | 1.83 | 0.000459 | 0 | 2.04 | 0.00055 | -0.000714 | 1.83 | 0.000459 | 0 | 2.04 | 0.00055 | -0.000714 | CFL | AllSpc | 1830 | 0.459 | 1830 | 0.459 | 1.11 | 1.2 | -0.00039
CFLAllSpcSCGMBTExCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCG | MBT | Ex | CZ05 | 1.83 | 0.000459 | 0 | 2.1 | 0.000571 | -0.000774 | 1.83 | 0.000459 | 0 | 2.1 | 0.000571 | -0.000774 | CFL | AllSpc | 1830 | 0.459 | 1830 | 0.459 | 1.15 | 1.24 | -0.000423
CFLAllSpcPGEMBTExCZ05 | Com-Iltg-dWatt-CFL_OSspc | PGE | MBT | Ex | CZ05 | 1.83 | 0.000459 | 0 | 2.1 | 0.000571 | -0.000774 | 1.83 | 0.000459 | 0 | 2.1 | 0.000571 | -0.000774 | CFL | AllSpc | 1830 | 0.459 | 1830 | 0.459 | 1.15 | 1.24 | -0.000423
CFLAllSpcSCEMBTExCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCE | MBT | Ex | CZ05 | 1.83 | 0.000459 | 0 | 2.1 | 0.000571 | -0.000774 | 1.83 | 0.000459 | 0 | 2.1 | 0.000571 | -0.000774 | CFL | AllSpc | 1830 | 0.459 | 1830 | 0.459 | 1.15 | 1.24 | -0.000423
CFLAllSpcSDGMBTExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SDG | MBT | Ex | CZ06 | 1.83 | 0.000459 | 0 | 2.12 | 0.000552 | -0.000339 | 1.83 | 0.000459 | 0 | 2.12 | 0.000552 | -0.000339 | CFL | AllSpc | 1830 | 0.459 | 1830 | 0.459 | 1.16 | 1.2 | -0.000185
CFLAllSpcSCEMBTExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCE | MBT | Ex | CZ06 | 1.83 | 0.000459 | 0 | 2.12 | 0.000552 | -0.000339 | 1.83 | 0.000459 | 0 | 2.12 | 0.000552 | -0.000339 | CFL | AllSpc | 1830 | 0.459 | 1830 | 0.459 | 1.16 | 1.2 | -0.000185
CFLAllSpcSCGMBTExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCG | MBT | Ex | CZ06 | 1.83 | 0.000459 | 0 | 2.12 | 0.000552 | -0.000339 | 1.83 | 0.000459 | 0 | 2.12 | 0.000552 | -0.000339 | CFL | AllSpc | 1830 | 0.459 | 1830 | 0.459 | 1.16 | 1.2 | -0.000185
CFLAllSpcSDGMBTExCZ07 | Com-Iltg-dWatt-CFL_OSspc | SDG | MBT | Ex | CZ07 | 1.83 | 0.000459 | 0 | 2.13 | 0.000545 | -9.19e-05 | 1.83 | 0.000459 | 0 | 2.13 | 0.000545 | -9.19e-05 | CFL | AllSpc | 1830 | 0.459 | 1830 | 0.459 | 1.16 | 1.19 | -5.02e-05
CFLAllSpcSCGMBTExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCG | MBT | Ex | CZ08 | 1.83 | 0.000459 | 0 | 2.12 | 0.000576 | -0.00022 | 1.83 | 0.000459 | 0 | 2.12 | 0.000576 | -0.00022 | CFL | AllSpc | 1830 | 0.459 | 1830 | 0.459 | 1.16 | 1.25 | -0.00012
CFLAllSpcSDGMBTExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SDG | MBT | Ex | CZ08 | 1.83 | 0.000459 | 0 | 2.12 | 0.000576 | -0.00022 | 1.83 | 0.000459 | 0 | 2.12 | 0.000576 | -0.00022 | CFL | AllSpc | 1830 | 0.459 | 1830 | 0.459 | 1.16 | 1.25 | -0.00012
CFLAllSpcSCEMBTExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCE | MBT | Ex | CZ08 | 1.83 | 0.000459 | 0 | 2.12 | 0.000576 | -0.00022 | 1.83 | 0.000459 | 0 | 2.12 | 0.000576 | -0.00022 | CFL | AllSpc | 1830 | 0.459 | 1830 | 0.459 | 1.16 | 1.25 | -0.00012
CFLAllSpcSCEMBTExCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCE | MBT | Ex | CZ09 | 1.83 | 0.000459 | 0 | 2.15 | 0.000579 | -0.000514 | 1.83 | 0.000459 | 0 | 2.15 | 0.000579 | -0.000514 | CFL | AllSpc | 1830 | 0.459 | 1830 | 0.459 | 1.17 | 1.26 | -0.000281
CFLAllSpcSCGMBTExCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCG | MBT | Ex | CZ09 | 1.83 | 0.000459 | 0 | 2.15 | 0.000579 | -0.000514 | 1.83 | 0.000459 | 0 | 2.15 | 0.000579 | -0.000514 | CFL | AllSpc | 1830 | 0.459 | 1830 | 0.459 | 1.17 | 1.26 | -0.000281
CFLAllSpcSDGMBTExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SDG | MBT | Ex | CZ10 | 1.83 | 0.000459 | 0 | 2.12 | 0.000588 | -0.000593 | 1.83 | 0.000459 | 0 | 2.12 | 0.000588 | -0.000593 | CFL | AllSpc | 1830 | 0.459 | 1830 | 0.459 | 1.16 | 1.28 | -0.000324
CFLAllSpcSCGMBTExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCG | MBT | Ex | CZ10 | 1.83 | 0.000459 | 0 | 2.12 | 0.000588 | -0.000593 | 1.83 | 0.000459 | 0 | 2.12 | 0.000588 | -0.000593 | CFL | AllSpc | 1830 | 0.459 | 1830 | 0.459 | 1.16 | 1.28 | -0.000324
CFLAllSpcSCEMBTExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCE | MBT | Ex | CZ10 | 1.83 | 0.000459 | 0 | 2.12 | 0.000588 | -0.000593 | 1.83 | 0.000459 | 0 | 2.12 | 0.000588 | -0.000593 | CFL | AllSpc | 1830 | 0.459 | 1830 | 0.459 | 1.16 | 1.28 | -0.000324
CFLAllSpcPGEMBTExCZ11 | Com-Iltg-dWatt-CFL_OSspc | PGE | MBT | Ex | CZ11 | 1.83 | 0.000459 | 0 | 2.04 | 0.000553 | -0.00114 | 1.83 | 0.000459 | 0 | 2.04 | 0.000553 | -0.00114 | CFL | AllSpc | 1830 | 0.459 | 1830 | 0.459 | 1.11 | 1.2 | -0.000623
CFLAllSpcPGEMBTExCZ12 | Com-Iltg-dWatt-CFL_OSspc | PGE | MBT | Ex | CZ12 | 1.83 | 0.000459 | 0 | 2.03 | 0.000538 | -0.00112 | 1.83 | 0.000459 | 0 | 2.03 | 0.000538 | -0.00112 | CFL | AllSpc | 1830 | 0.459 | 1830 | 0.459 | 1.11 | 1.17 | -0.000612
CFLAllSpcPGEMBTExCZ13 | Com-Iltg-dWatt-CFL_OSspc | PGE | MBT | Ex | CZ13 | 1.83 | 0.000459 | 0 | 2.08 | 0.00056 | -0.0012 | 1.83 | 0.000459 | 0 | 2.08 | 0.00056 | -0.0012 | CFL | AllSpc | 1830 | 0.459 | 1830 | 0.459 | 1.14 | 1.22 | -0.000656
CFLAllSpcSCGMBTExCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCG | MBT | Ex | CZ13 | 1.83 | 0.000459 | 0 | 2.08 | 0.00056 | -0.0012 | 1.83 | 0.000459 | 0 | 2.08 | 0.00056 | -0.0012 | CFL | AllSpc | 1830 | 0.459 | 1830 | 0.459 | 1.14 | 1.22 | -0.000656
CFLAllSpcSCEMBTExCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCE | MBT | Ex | CZ13 | 1.83 | 0.000459 | 0 | 2.08 | 0.00056 | -0.0012 | 1.83 | 0.000459 | 0 | 2.08 | 0.00056 | -0.0012 | CFL | AllSpc | 1830 | 0.459 | 1830 | 0.459 | 1.14 | 1.22 | -0.000656
CFLAllSpcSDGMBTExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SDG | MBT | Ex | CZ14 | 1.83 | 0.000459 | 0 | 2.08 | 0.000583 | -0.00142 | 1.83 | 0.000459 | 0 | 2.08 | 0.000583 | -0.00142 | CFL | AllSpc | 1830 | 0.459 | 1830 | 0.459 | 1.14 | 1.27 | -0.000776
CFLAllSpcSCGMBTExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCG | MBT | Ex | CZ14 | 1.83 | 0.000459 | 0 | 2.08 | 0.000583 | -0.00142 | 1.83 | 0.000459 | 0 | 2.08 | 0.000583 | -0.00142 | CFL | AllSpc | 1830 | 0.459 | 1830 | 0.459 | 1.14 | 1.27 | -0.000776
CFLAllSpcSCEMBTExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCE | MBT | Ex | CZ14 | 1.83 | 0.000459 | 0 | 2.08 | 0.000583 | -0.00142 | 1.83 | 0.000459 | 0 | 2.08 | 0.000583 | -0.00142 | CFL | AllSpc | 1830 | 0.459 | 1830 | 0.459 | 1.14 | 1.27 | -0.000776
CFLAllSpcSCEMBTExCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCE | MBT | Ex | CZ15 | 1.83 | 0.000459 | 0 | 2.2 | 0.000589 | 0 | 1.83 | 0.000459 | 0 | 2.2 | 0.000589 | 0 | CFL | AllSpc | 1830 | 0.459 | 1830 | 0.459 | 1.2 | 1.28 | 0
CFLAllSpcSDGMBTExCZ15 | Com-Iltg-dWatt-CFL_OSspc | SDG | MBT | Ex | CZ15 | 1.83 | 0.000459 | 0 | 2.2 | 0.000589 | 0 | 1.83 | 0.000459 | 0 | 2.2 | 0.000589 | 0 | CFL | AllSpc | 1830 | 0.459 | 1830 | 0.459 | 1.2 | 1.28 | 0
CFLAllSpcSCGMBTExCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCG | MBT | Ex | CZ15 | 1.83 | 0.000459 | 0 | 2.2 | 0.000589 | 0 | 1.83 | 0.000459 | 0 | 2.2 | 0.000589 | 0 | CFL | AllSpc | 1830 | 0.459 | 1830 | 0.459 | 1.2 | 1.28 | 0
CFLAllSpcPGEMBTExCZ16 | Com-Iltg-dWatt-CFL_OSspc | PGE | MBT | Ex | CZ16 | 1.83 | 0.000459 | 0 | 1.96 | 0.000547 | -0.00485 | 1.83 | 0.000459 | 0 | 1.96 | 0.000547 | -0.00485 | CFL | AllSpc | 1830 | 0.459 | 1830 | 0.459 | 1.07 | 1.19 | -0.00265
CFLAllSpcSCEMBTExCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCE | MBT | Ex | CZ16 | 1.83 | 0.000459 | 0 | 1.96 | 0.000547 | -0.00485 | 1.83 | 0.000459 | 0 | 1.96 | 0.000547 | -0.00485 | CFL | AllSpc | 1830 | 0.459 | 1830 | 0.459 | 1.07 | 1.19 | -0.00265
CFLAllSpcSCGMBTExCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCG | MBT | Ex | CZ16 | 1.83 | 0.000459 | 0 | 1.96 | 0.000547 | -0.00485 | 1.83 | 0.000459 | 0 | 1.96 | 0.000547 | -0.00485 | CFL | AllSpc | 1830 | 0.459 | 1830 | 0.459 | 1.07 | 1.19 | -0.00265
CFLAllSpcSCEMBTExIOU | Com-Iltg-dWatt-CFL_OSspc | SCE | MBT | Ex | IOU | 1.83 | 0.000459 | 0 | 2.12 | 0.000573 | -0.00051 | 1.83 | 0.000459 | 0 | 2.12 | 0.000573 | -0.00051 | CFL | AllSpc | 1830 | 0.459 | 1830 | 0.459 | 1.16 | 1.25 | -0.000279
CFLAllSpcPGEMBTExIOU | Com-Iltg-dWatt-CFL_OSspc | PGE | MBT | Ex | IOU | 1.83 | 0.000459 | 0 | 2.05 | 0.000546 | -0.00102 | 1.83 | 0.000459 | 0 | 2.05 | 0.000546 | -0.00102 | CFL | AllSpc | 1830 | 0.459 | 1830 | 0.459 | 1.12 | 1.19 | -0.000557
CFLAllSpcSCGMBTExIOU | Com-Iltg-dWatt-CFL_OSspc | SCG | MBT | Ex | IOU | 1.83 | 0.000459 | 0 | 2.13 | 0.000574 | -0.000498 | 1.83 | 0.000459 | 0 | 2.13 | 0.000574 | -0.000498 | CFL | AllSpc | 1830 | 0.459 | 1830 | 0.459 | 1.16 | 1.25 | -0.000272
CFLAllSpcSDGMBTExIOU | Com-Iltg-dWatt-CFL_OSspc | SDG | MBT | Ex | IOU | 1.83 | 0.000459 | 0 | 2.13 | 0.000559 | -0.000267 | 1.83 | 0.000459 | 0 | 2.13 | 0.000559 | -0.000267 | CFL | AllSpc | 1830 | 0.459 | 1830 | 0.459 | 1.16 | 1.22 | -0.000146
CFLAllSpcPGEMBTNewCZ01 | Com-Iltg-dWatt-CFL_OSspc | PGE | MBT | New | CZ01 | 1.83 | 0.000459 | 0 | 1.87 | 0.00052 | -0.00203 | 1.83 | 0.000459 | 0 | 1.87 | 0.00052 | -0.00203 | CFL | AllSpc | 1830 | 0.459 | 1830 | 0.459 | 1.02 | 1.13 | -0.00111
CFLAllSpcPGEMBTNewCZ02 | Com-Iltg-dWatt-CFL_OSspc | PGE | MBT | New | CZ02 | 1.83 | 0.000459 | 0 | 1.95 | 0.000564 | -0.000963 | 1.83 | 0.000459 | 0 | 1.95 | 0.000564 | -0.000963 | CFL | AllSpc | 1830 | 0.459 | 1830 | 0.459 | 1.07 | 1.23 | -0.000526
CFLAllSpcPGEMBTNewCZ03 | Com-Iltg-dWatt-CFL_OSspc | PGE | MBT | New | CZ03 | 1.83 | 0.000459 | 0 | 1.94 | 0.000547 | -0.00091 | 1.83 | 0.000459 | 0 | 1.94 | 0.000547 | -0.00091 | CFL | AllSpc | 1830 | 0.459 | 1830 | 0.459 | 1.06 | 1.19 | -0.000497
CFLAllSpcPGEMBTNewCZ04 | Com-Iltg-dWatt-CFL_OSspc | PGE | MBT | New | CZ04 | 1.83 | 0.000459 | 0 | 1.97 | 0.000559 | -0.000727 | 1.83 | 0.000459 | 0 | 1.97 | 0.000559 | -0.000727 | CFL | AllSpc | 1830 | 0.459 | 1830 | 0.459 | 1.08 | 1.22 | -0.000397
CFLAllSpcPGEMBTNewCZ05 | Com-Iltg-dWatt-CFL_OSspc | PGE | MBT | New | CZ05 | 1.83 | 0.000459 | 0 | 1.94 | 0.000544 | -0.000485 | 1.83 | 0.000459 | 0 | 1.94 | 0.000544 | -0.000485 | CFL | AllSpc | 1830 | 0.459 | 1830 | 0.459 | 1.06 | 1.19 | -0.000265
CFLAllSpcSCEMBTNewCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCE | MBT | New | CZ05 | 1.83 | 0.000459 | 0 | 1.97 | 0.000567 | -0.000628 | 1.83 | 0.000459 | 0 | 1.97 | 0.000567 | -0.000628 | CFL | AllSpc | 1830 | 0.459 | 1830 | 0.459 | 1.08 | 1.24 | -0.000343
CFLAllSpcSCEMBTNewCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCE | MBT | New | CZ06 | 1.83 | 0.000459 | 0 | 2.05 | 0.00057 | -0.0006 | 1.83 | 0.000459 | 0 | 2.05 | 0.00057 | -0.0006 | CFL | AllSpc | 1830 | 0.459 | 1830 | 0.459 | 1.12 | 1.24 | -0.000328
CFLAllSpcSDGMBTNewCZ06 | Com-Iltg-dWatt-CFL_OSspc | SDG | MBT | New | CZ06 | 1.83 | 0.000459 | 0 | 2.05 | 0.000574 | -0.00062 | 1.83 | 0.000459 | 0 | 2.05 | 0.000574 | -0.00062 | CFL | AllSpc | 1830 | 0.459 | 1830 | 0.459 | 1.12 | 1.25 | -0.000339
CFLAllSpcSDGMBTNewCZ07 | Com-Iltg-dWatt-CFL_OSspc | SDG | MBT | New | CZ07 | 1.83 | 0.000459 | 0 | 2.04 | 0.000569 | 0 | 1.83 | 0.000459 | 0 | 2.04 | 0.000569 | 0 | CFL | AllSpc | 1830 | 0.459 | 1830 | 0.459 | 1.11 | 1.24 | 0
CFLAllSpcSDGMBTNewCZ08 | Com-Iltg-dWatt-CFL_OSspc | SDG | MBT | New | CZ08 | 1.83 | 0.000459 | 0 | 2.06 | 0.000589 | -0.000496 | 1.83 | 0.000459 | 0 | 2.06 | 0.000589 | -0.000496 | CFL | AllSpc | 1830 | 0.459 | 1830 | 0.459 | 1.13 | 1.28 | -0.000271
CFLAllSpcSCEMBTNewCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCE | MBT | New | CZ08 | 1.83 | 0.000459 | 0 | 2.06 | 0.000585 | -0.000481 | 1.83 | 0.000459 | 0 | 2.06 | 0.000585 | -0.000481 | CFL | AllSpc | 1830 | 0.459 | 1830 | 0.459 | 1.13 | 1.27 | -0.000263
CFLAllSpcSCEMBTNewCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCE | MBT | New | CZ09 | 1.83 | 0.000459 | 0 | 2.05 | 0.000598 | -0.000565 | 1.83 | 0.000459 | 0 | 2.05 | 0.000598 | -0.000565 | CFL | AllSpc | 1830 | 0.459 | 1830 | 0.459 | 1.12 | 1.3 | -0.000309
CFLAllSpcSCEMBTNewCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCE | MBT | New | CZ10 | 1.83 | 0.000459 | 0 | 2.06 | 0.000607 | -0.000597 | 1.83 | 0.000459 | 0 | 2.06 | 0.000607 | -0.000597 | CFL | AllSpc | 1830 | 0.459 | 1830 | 0.459 | 1.13 | 1.32 | -0.000326
CFLAllSpcSDGMBTNewCZ10 | Com-Iltg-dWatt-CFL_OSspc | SDG | MBT | New | CZ10 | 1.83 | 0.000459 | 0 | 2.07 | 0.000613 | -0.000615 | 1.83 | 0.000459 | 0 | 2.07 | 0.000613 | -0.000615 | CFL | AllSpc | 1830 | 0.459 | 1830 | 0.459 | 1.13 | 1.34 | -0.000336
CFLAllSpcPGEMBTNewCZ11 | Com-Iltg-dWatt-CFL_OSspc | PGE | MBT | New | CZ11 | 1.83 | 0.000459 | 0 | 1.99 | 0.000569 | -0.001 | 1.83 | 0.000459 | 0 | 1.99 | 0.000569 | -0.001 | CFL | AllSpc | 1830 | 0.459 | 1830 | 0.459 | 1.09 | 1.24 | -0.000546
CFLAllSpcPGEMBTNewCZ12 | Com-Iltg-dWatt-CFL_OSspc | PGE | MBT | New | CZ12 | 1.83 | 0.000459 | 0 | 1.98 | 0.000565 | -0.000871 | 1.83 | 0.000459 | 0 | 1.98 | 0.000565 | -0.000871 | CFL | AllSpc | 1830 | 0.459 | 1830 | 0.459 | 1.08 | 1.23 | -0.000476
CFLAllSpcSCEMBTNewCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCE | MBT | New | CZ13 | 1.83 | 0.000459 | 0 | 2.04 | 0.000591 | -0.00105 | 1.83 | 0.000459 | 0 | 2.04 | 0.000591 | -0.00105 | CFL | AllSpc | 1830 | 0.459 | 1830 | 0.459 | 1.11 | 1.29 | -0.000574
CFLAllSpcPGEMBTNewCZ13 | Com-Iltg-dWatt-CFL_OSspc | PGE | MBT | New | CZ13 | 1.83 | 0.000459 | 0 | 2 | 0.000563 | -0.000811 | 1.83 | 0.000459 | 0 | 2 | 0.000563 | -0.000811 | CFL | AllSpc | 1830 | 0.459 | 1830 | 0.459 | 1.09 | 1.23 | -0.000443
CFLAllSpcSDGMBTNewCZ14 | Com-Iltg-dWatt-CFL_OSspc | SDG | MBT | New | CZ14 | 1.83 | 0.000459 | 0 | 2.05 | 0.000605 | -0.00119 | 1.83 | 0.000459 | 0 | 2.05 | 0.000605 | -0.00119 | CFL | AllSpc | 1830 | 0.459 | 1830 | 0.459 | 1.12 | 1.32 | -0.00065
CFLAllSpcSCEMBTNewCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCE | MBT | New | CZ14 | 1.83 | 0.000459 | 0 | 2.04 | 0.000599 | -0.00116 | 1.83 | 0.000459 | 0 | 2.04 | 0.000599 | -0.00116 | CFL | AllSpc | 1830 | 0.459 | 1830 | 0.459 | 1.11 | 1.31 | -0.000634
CFLAllSpcSCEMBTNewCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCE | MBT | New | CZ15 | 1.83 | 0.000459 | 0 | 2.17 | 0.000608 | 0 | 1.83 | 0.000459 | 0 | 2.17 | 0.000608 | 0 | CFL | AllSpc | 1830 | 0.459 | 1830 | 0.459 | 1.19 | 1.32 | 0
CFLAllSpcSDGMBTNewCZ15 | Com-Iltg-dWatt-CFL_OSspc | SDG | MBT | New | CZ15 | 1.83 | 0.000459 | 0 | 2.18 | 0.000613 | 0 | 1.83 | 0.000459 | 0 | 2.18 | 0.000613 | 0 | CFL | AllSpc | 1830 | 0.459 | 1830 | 0.459 | 1.19 | 1.34 | 0
CFLAllSpcSCEMBTNewCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCE | MBT | New | CZ16 | 1.83 | 0.000459 | 0 | 1.93 | 0.000567 | -0.00393 | 1.83 | 0.000459 | 0 | 1.93 | 0.000567 | -0.00393 | CFL | AllSpc | 1830 | 0.459 | 1830 | 0.459 | 1.05 | 1.24 | -0.00215
CFLAllSpcPGEMBTNewCZ16 | Com-Iltg-dWatt-CFL_OSspc | PGE | MBT | New | CZ16 | 1.83 | 0.000459 | 0 | 1.91 | 0.000544 | -0.00377 | 1.83 | 0.000459 | 0 | 1.91 | 0.000544 | -0.00377 | CFL | AllSpc | 1830 | 0.459 | 1830 | 0.459 | 1.04 | 1.19 | -0.00206
CFLAllSpcSCGMBTNewIOU | Com-Iltg-dWatt-CFL_OSspc | SCG | MBT | New | IOU | 1.83 | 0.000459 | 0 | 2.08 | 0.000598 | -0.000538 | 1.83 | 0.000459 | 0 | 2.08 | 0.000598 | -0.000538 | CFL | AllSpc | 1830 | 0.459 | 1830 | 0.459 | 1.14 | 1.3 | -0.000294
CFLAllSpcPGEMBTNewIOU | Com-Iltg-dWatt-CFL_OSspc | PGE | MBT | New | IOU | 1.83 | 0.000459 | 0 | 2.03 | 0.000587 | -0.0012 | 1.83 | 0.000459 | 0 | 2.03 | 0.000587 | -0.0012 | CFL | AllSpc | 1830 | 0.459 | 1830 | 0.459 | 1.11 | 1.28 | -0.000656
CFLAllSpcSCEMBTNewIOU | Com-Iltg-dWatt-CFL_OSspc | SCE | MBT | New | IOU | 1.83 | 0.000459 | 0 | 2.08 | 0.000599 | -0.000538 | 1.83 | 0.000459 | 0 | 2.08 | 0.000599 | -0.000538 | CFL | AllSpc | 1830 | 0.459 | 1830 | 0.459 | 1.14 | 1.31 | -0.000294
CFLAllSpcSDGMBTNewIOU | Com-Iltg-dWatt-CFL_OSspc | SDG | MBT | New | IOU | 1.83 | 0.000459 | 0 | 2.05 | 0.000583 | -0.000228 | 1.83 | 0.000459 | 0 | 2.05 | 0.000583 | -0.000228 | CFL | AllSpc | 1830 | 0.459 | 1830 | 0.459 | 1.12 | 1.27 | -0.000125
CFLAllSpcPGEMLIExCZ01 | Com-Iltg-dWatt-CFL_OSspc | PGE | MLI | Ex | CZ01 | 2.01 | 0.000437 | 0 | 1.96 | 0.000497 | -0.0231 | 2.01 | 0.000437 | 0 | 1.96 | 0.000497 | -0.0231 | CFL | AllSpc | 2010 | 0.437 | 2010 | 0.437 | 0.975 | 1.14 | -0.0115
CFLAllSpcPGEMLIExCZ02 | Com-Iltg-dWatt-CFL_OSspc | PGE | MLI | Ex | CZ02 | 2.01 | 0.000437 | 0 | 2.1 | 0.000506 | -0.0114 | 2.01 | 0.000437 | 0 | 2.1 | 0.000506 | -0.0114 | CFL | AllSpc | 2010 | 0.437 | 2010 | 0.437 | 1.04 | 1.16 | -0.00567
CFLAllSpcPGEMLIExCZ03 | Com-Iltg-dWatt-CFL_OSspc | PGE | MLI | Ex | CZ03 | 2.01 | 0.000437 | 0 | 2.09 | 0.000507 | -0.0106 | 2.01 | 0.000437 | 0 | 2.09 | 0.000507 | -0.0106 | CFL | AllSpc | 2010 | 0.437 | 2010 | 0.437 | 1.04 | 1.16 | -0.00527
CFLAllSpcPGEMLIExCZ04 | Com-Iltg-dWatt-CFL_OSspc | PGE | MLI | Ex | CZ04 | 2.01 | 0.000437 | 0 | 2.12 | 0.000505 | -0.00856 | 2.01 | 0.000437 | 0 | 2.12 | 0.000505 | -0.00856 | CFL | AllSpc | 2010 | 0.437 | 2010 | 0.437 | 1.05 | 1.16 | -0.00426
CFLAllSpcSCGMLIExCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCG | MLI | Ex | CZ05 | 2.01 | 0.000437 | 0 | 2.12 | 0.000529 | -0.00975 | 2.01 | 0.000437 | 0 | 2.12 | 0.000529 | -0.00975 | CFL | AllSpc | 2010 | 0.437 | 2010 | 0.437 | 1.05 | 1.21 | -0.00485
CFLAllSpcSCEMLIExCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCE | MLI | Ex | CZ05 | 2.01 | 0.000437 | 0 | 2.12 | 0.000529 | -0.00975 | 2.01 | 0.000437 | 0 | 2.12 | 0.000529 | -0.00975 | CFL | AllSpc | 2010 | 0.437 | 2010 | 0.437 | 1.05 | 1.21 | -0.00485
CFLAllSpcPGEMLIExCZ05 | Com-Iltg-dWatt-CFL_OSspc | PGE | MLI | Ex | CZ05 | 2.01 | 0.000437 | 0 | 2.12 | 0.000529 | -0.00975 | 2.01 | 0.000437 | 0 | 2.12 | 0.000529 | -0.00975 | CFL | AllSpc | 2010 | 0.437 | 2010 | 0.437 | 1.05 | 1.21 | -0.00485
CFLAllSpcSCEMLIExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCE | MLI | Ex | CZ06 | 2.01 | 0.000437 | 0 | 2.18 | 0.000519 | -0.00432 | 2.01 | 0.000437 | 0 | 2.18 | 0.000519 | -0.00432 | CFL | AllSpc | 2010 | 0.437 | 2010 | 0.437 | 1.08 | 1.19 | -0.00215
CFLAllSpcSDGMLIExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SDG | MLI | Ex | CZ06 | 2.01 | 0.000437 | 0 | 2.18 | 0.000519 | -0.00432 | 2.01 | 0.000437 | 0 | 2.18 | 0.000519 | -0.00432 | CFL | AllSpc | 2010 | 0.437 | 2010 | 0.437 | 1.08 | 1.19 | -0.00215
CFLAllSpcSCGMLIExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCG | MLI | Ex | CZ06 | 2.01 | 0.000437 | 0 | 2.18 | 0.000519 | -0.00432 | 2.01 | 0.000437 | 0 | 2.18 | 0.000519 | -0.00432 | CFL | AllSpc | 2010 | 0.437 | 2010 | 0.437 | 1.08 | 1.19 | -0.00215
CFLAllSpcSDGMLIExCZ07 | Com-Iltg-dWatt-CFL_OSspc | SDG | MLI | Ex | CZ07 | 2.01 | 0.000437 | 0 | 2.17 | 0.000517 | -0.00223 | 2.01 | 0.000437 | 0 | 2.17 | 0.000517 | -0.00223 | CFL | AllSpc | 2010 | 0.437 | 2010 | 0.437 | 1.08 | 1.18 | -0.00111
CFLAllSpcSDGMLIExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SDG | MLI | Ex | CZ08 | 2.01 | 0.000437 | 0 | 2.2 | 0.000518 | -0.00356 | 2.01 | 0.000437 | 0 | 2.2 | 0.000518 | -0.00356 | CFL | AllSpc | 2010 | 0.437 | 2010 | 0.437 | 1.09 | 1.19 | -0.00177
CFLAllSpcSCEMLIExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCE | MLI | Ex | CZ08 | 2.01 | 0.000437 | 0 | 2.2 | 0.000518 | -0.00356 | 2.01 | 0.000437 | 0 | 2.2 | 0.000518 | -0.00356 | CFL | AllSpc | 2010 | 0.437 | 2010 | 0.437 | 1.09 | 1.19 | -0.00177
CFLAllSpcSCGMLIExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCG | MLI | Ex | CZ08 | 2.01 | 0.000437 | 0 | 2.2 | 0.000518 | -0.00356 | 2.01 | 0.000437 | 0 | 2.2 | 0.000518 | -0.00356 | CFL | AllSpc | 2010 | 0.437 | 2010 | 0.437 | 1.09 | 1.19 | -0.00177
CFLAllSpcSCEMLIExCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCE | MLI | Ex | CZ09 | 2.01 | 0.000437 | 0 | 2.23 | 0.00053 | -0.0038 | 2.01 | 0.000437 | 0 | 2.23 | 0.00053 | -0.0038 | CFL | AllSpc | 2010 | 0.437 | 2010 | 0.437 | 1.11 | 1.21 | -0.00189
CFLAllSpcSCGMLIExCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCG | MLI | Ex | CZ09 | 2.01 | 0.000437 | 0 | 2.23 | 0.00053 | -0.0038 | 2.01 | 0.000437 | 0 | 2.23 | 0.00053 | -0.0038 | CFL | AllSpc | 2010 | 0.437 | 2010 | 0.437 | 1.11 | 1.21 | -0.00189
CFLAllSpcSCGMLIExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCG | MLI | Ex | CZ10 | 2.01 | 0.000437 | 0 | 2.19 | 0.000531 | -0.00484 | 2.01 | 0.000437 | 0 | 2.19 | 0.000531 | -0.00484 | CFL | AllSpc | 2010 | 0.437 | 2010 | 0.437 | 1.09 | 1.22 | -0.00241
CFLAllSpcSCEMLIExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCE | MLI | Ex | CZ10 | 2.01 | 0.000437 | 0 | 2.19 | 0.000531 | -0.00484 | 2.01 | 0.000437 | 0 | 2.19 | 0.000531 | -0.00484 | CFL | AllSpc | 2010 | 0.437 | 2010 | 0.437 | 1.09 | 1.22 | -0.00241
CFLAllSpcSDGMLIExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SDG | MLI | Ex | CZ10 | 2.01 | 0.000437 | 0 | 2.19 | 0.000531 | -0.00484 | 2.01 | 0.000437 | 0 | 2.19 | 0.000531 | -0.00484 | CFL | AllSpc | 2010 | 0.437 | 2010 | 0.437 | 1.09 | 1.22 | -0.00241
CFLAllSpcPGEMLIExCZ11 | Com-Iltg-dWatt-CFL_OSspc | PGE | MLI | Ex | CZ11 | 2.01 | 0.000437 | 0 | 2.1 | 0.000506 | -0.012 | 2.01 | 0.000437 | 0 | 2.1 | 0.000506 | -0.012 | CFL | AllSpc | 2010 | 0.437 | 2010 | 0.437 | 1.04 | 1.16 | -0.00597
CFLAllSpcPGEMLIExCZ12 | Com-Iltg-dWatt-CFL_OSspc | PGE | MLI | Ex | CZ12 | 2.01 | 0.000437 | 0 | 2.1 | 0.000509 | -0.0116 | 2.01 | 0.000437 | 0 | 2.1 | 0.000509 | -0.0116 | CFL | AllSpc | 2010 | 0.437 | 2010 | 0.437 | 1.04 | 1.16 | -0.00577
CFLAllSpcSCGMLIExCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCG | MLI | Ex | CZ13 | 2.01 | 0.000437 | 0 | 2.15 | 0.00052 | -0.0108 | 2.01 | 0.000437 | 0 | 2.15 | 0.00052 | -0.0108 | CFL | AllSpc | 2010 | 0.437 | 2010 | 0.437 | 1.07 | 1.19 | -0.00537
CFLAllSpcPGEMLIExCZ13 | Com-Iltg-dWatt-CFL_OSspc | PGE | MLI | Ex | CZ13 | 2.01 | 0.000437 | 0 | 2.15 | 0.00052 | -0.0108 | 2.01 | 0.000437 | 0 | 2.15 | 0.00052 | -0.0108 | CFL | AllSpc | 2010 | 0.437 | 2010 | 0.437 | 1.07 | 1.19 | -0.00537
CFLAllSpcSCEMLIExCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCE | MLI | Ex | CZ13 | 2.01 | 0.000437 | 0 | 2.15 | 0.00052 | -0.0108 | 2.01 | 0.000437 | 0 | 2.15 | 0.00052 | -0.0108 | CFL | AllSpc | 2010 | 0.437 | 2010 | 0.437 | 1.07 | 1.19 | -0.00537
CFLAllSpcSDGMLIExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SDG | MLI | Ex | CZ14 | 2.01 | 0.000437 | 0 | 2.13 | 0.000525 | -0.0134 | 2.01 | 0.000437 | 0 | 2.13 | 0.000525 | -0.0134 | CFL | AllSpc | 2010 | 0.437 | 2010 | 0.437 | 1.06 | 1.2 | -0.00667
CFLAllSpcSCGMLIExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCG | MLI | Ex | CZ14 | 2.01 | 0.000437 | 0 | 2.13 | 0.000525 | -0.0134 | 2.01 | 0.000437 | 0 | 2.13 | 0.000525 | -0.0134 | CFL | AllSpc | 2010 | 0.437 | 2010 | 0.437 | 1.06 | 1.2 | -0.00667
CFLAllSpcSCEMLIExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCE | MLI | Ex | CZ14 | 2.01 | 0.000437 | 0 | 2.13 | 0.000525 | -0.0134 | 2.01 | 0.000437 | 0 | 2.13 | 0.000525 | -0.0134 | CFL | AllSpc | 2010 | 0.437 | 2010 | 0.437 | 1.06 | 1.2 | -0.00667
CFLAllSpcSDGMLIExCZ15 | Com-Iltg-dWatt-CFL_OSspc | SDG | MLI | Ex | CZ15 | 2.01 | 0.000437 | 0 | 2.36 | 0.000524 | -0.00127 | 2.01 | 0.000437 | 0 | 2.36 | 0.000524 | -0.00127 | CFL | AllSpc | 2010 | 0.437 | 2010 | 0.437 | 1.17 | 1.2 | -0.000632
CFLAllSpcSCGMLIExCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCG | MLI | Ex | CZ15 | 2.01 | 0.000437 | 0 | 2.36 | 0.000524 | -0.00127 | 2.01 | 0.000437 | 0 | 2.36 | 0.000524 | -0.00127 | CFL | AllSpc | 2010 | 0.437 | 2010 | 0.437 | 1.17 | 1.2 | -0.000632
CFLAllSpcSCEMLIExCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCE | MLI | Ex | CZ15 | 2.01 | 0.000437 | 0 | 2.36 | 0.000524 | -0.00127 | 2.01 | 0.000437 | 0 | 2.36 | 0.000524 | -0.00127 | CFL | AllSpc | 2010 | 0.437 | 2010 | 0.437 | 1.17 | 1.2 | -0.000632
CFLAllSpcSCGMLIExCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCG | MLI | Ex | CZ16 | 2.01 | 0.000437 | 0 | 1.98 | 0.000514 | -0.0243 | 2.01 | 0.000437 | 0 | 1.98 | 0.000514 | -0.0243 | CFL | AllSpc | 2010 | 0.437 | 2010 | 0.437 | 0.985 | 1.18 | -0.0121
CFLAllSpcSCEMLIExCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCE | MLI | Ex | CZ16 | 2.01 | 0.000437 | 0 | 1.98 | 0.000514 | -0.0243 | 2.01 | 0.000437 | 0 | 1.98 | 0.000514 | -0.0243 | CFL | AllSpc | 2010 | 0.437 | 2010 | 0.437 | 0.985 | 1.18 | -0.0121
CFLAllSpcPGEMLIExCZ16 | Com-Iltg-dWatt-CFL_OSspc | PGE | MLI | Ex | CZ16 | 2.01 | 0.000437 | 0 | 1.98 | 0.000514 | -0.0243 | 2.01 | 0.000437 | 0 | 1.98 | 0.000514 | -0.0243 | CFL | AllSpc | 2010 | 0.437 | 2010 | 0.437 | 0.985 | 1.18 | -0.0121
CFLAllSpcSDGMLIExIOU | Com-Iltg-dWatt-CFL_OSspc | SDG | MLI | Ex | IOU | 2.01 | 0.000437 | 0 | 2.18 | 0.000521 | -0.00322 | 2.01 | 0.000437 | 0 | 2.18 | 0.000521 | -0.00322 | CFL | AllSpc | 2010 | 0.437 | 2010 | 0.437 | 1.08 | 1.19 | -0.0016
CFLAllSpcSCGMLIExIOU | Com-Iltg-dWatt-CFL_OSspc | SCG | MLI | Ex | IOU | 2.01 | 0.000437 | 0 | 2.2 | 0.000523 | -0.00466 | 2.01 | 0.000437 | 0 | 2.2 | 0.000523 | -0.00466 | CFL | AllSpc | 2010 | 0.437 | 2010 | 0.437 | 1.09 | 1.2 | -0.00232
CFLAllSpcSCEMLIExIOU | Com-Iltg-dWatt-CFL_OSspc | SCE | MLI | Ex | IOU | 2.01 | 0.000437 | 0 | 2.2 | 0.000523 | -0.00485 | 2.01 | 0.000437 | 0 | 2.2 | 0.000523 | -0.00485 | CFL | AllSpc | 2010 | 0.437 | 2010 | 0.437 | 1.09 | 1.2 | -0.00241
CFLAllSpcPGEMLIExIOU | Com-Iltg-dWatt-CFL_OSspc | PGE | MLI | Ex | IOU | 2.01 | 0.000437 | 0 | 2.1 | 0.000509 | -0.0108 | 2.01 | 0.000437 | 0 | 2.1 | 0.000509 | -0.0108 | CFL | AllSpc | 2010 | 0.437 | 2010 | 0.437 | 1.04 | 1.16 | -0.00537
CFLAllSpcPGEMLINewCZ01 | Com-Iltg-dWatt-CFL_OSspc | PGE | MLI | New | CZ01 | 2.01 | 0.000437 | 0 | 1.91 | 0.000475 | -0.0308 | 2.01 | 0.000437 | 0 | 1.91 | 0.000475 | -0.0308 | CFL | AllSpc | 2010 | 0.437 | 2010 | 0.437 | 0.95 | 1.09 | -0.0153
CFLAllSpcPGEMLINewCZ02 | Com-Iltg-dWatt-CFL_OSspc | PGE | MLI | New | CZ02 | 2.01 | 0.000437 | 0 | 2.02 | 0.000504 | -0.017 | 2.01 | 0.000437 | 0 | 2.02 | 0.000504 | -0.017 | CFL | AllSpc | 2010 | 0.437 | 2010 | 0.437 | 1 | 1.15 | -0.00846
CFLAllSpcPGEMLINewCZ03 | Com-Iltg-dWatt-CFL_OSspc | PGE | MLI | New | CZ03 | 2.01 | 0.000437 | 0 | 1.99 | 0.000509 | -0.0166 | 2.01 | 0.000437 | 0 | 1.99 | 0.000509 | -0.0166 | CFL | AllSpc | 2010 | 0.437 | 2010 | 0.437 | 0.99 | 1.16 | -0.00826
CFLAllSpcPGEMLINewCZ04 | Com-Iltg-dWatt-CFL_OSspc | PGE | MLI | New | CZ04 | 2.01 | 0.000437 | 0 | 2.05 | 0.000503 | -0.0134 | 2.01 | 0.000437 | 0 | 2.05 | 0.000503 | -0.0134 | CFL | AllSpc | 2010 | 0.437 | 2010 | 0.437 | 1.02 | 1.15 | -0.00667
CFLAllSpcSCEMLINewCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCE | MLI | New | CZ05 | 2.01 | 0.000437 | 0 | 2 | 0.00052 | -0.0161 | 2.01 | 0.000437 | 0 | 2 | 0.00052 | -0.0161 | CFL | AllSpc | 2010 | 0.437 | 2010 | 0.437 | 0.995 | 1.19 | -0.00801
CFLAllSpcPGEMLINewCZ05 | Com-Iltg-dWatt-CFL_OSspc | PGE | MLI | New | CZ05 | 2.01 | 0.000437 | 0 | 1.99 | 0.000501 | -0.0162 | 2.01 | 0.000437 | 0 | 1.99 | 0.000501 | -0.0162 | CFL | AllSpc | 2010 | 0.437 | 2010 | 0.437 | 0.99 | 1.15 | -0.00806
CFLAllSpcSCEMLINewCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCE | MLI | New | CZ06 | 2.01 | 0.000437 | 0 | 2.11 | 0.00051 | -0.00726 | 2.01 | 0.000437 | 0 | 2.11 | 0.00051 | -0.00726 | CFL | AllSpc | 2010 | 0.437 | 2010 | 0.437 | 1.05 | 1.17 | -0.00361
CFLAllSpcSDGMLINewCZ06 | Com-Iltg-dWatt-CFL_OSspc | SDG | MLI | New | CZ06 | 2.01 | 0.000437 | 0 | 2.11 | 0.000513 | -0.0078 | 2.01 | 0.000437 | 0 | 2.11 | 0.000513 | -0.0078 | CFL | AllSpc | 2010 | 0.437 | 2010 | 0.437 | 1.05 | 1.17 | -0.00388
CFLAllSpcSDGMLINewCZ07 | Com-Iltg-dWatt-CFL_OSspc | SDG | MLI | New | CZ07 | 2.01 | 0.000437 | 0 | 2.1 | 0.000512 | -0.00454 | 2.01 | 0.000437 | 0 | 2.1 | 0.000512 | -0.00454 | CFL | AllSpc | 2010 | 0.437 | 2010 | 0.437 | 1.04 | 1.17 | -0.00226
CFLAllSpcSDGMLINewCZ08 | Com-Iltg-dWatt-CFL_OSspc | SDG | MLI | New | CZ08 | 2.01 | 0.000437 | 0 | 2.15 | 0.000516 | -0.00627 | 2.01 | 0.000437 | 0 | 2.15 | 0.000516 | -0.00627 | CFL | AllSpc | 2010 | 0.437 | 2010 | 0.437 | 1.07 | 1.18 | -0.00312
CFLAllSpcSCEMLINewCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCE | MLI | New | CZ08 | 2.01 | 0.000437 | 0 | 2.14 | 0.000513 | -0.00585 | 2.01 | 0.000437 | 0 | 2.14 | 0.000513 | -0.00585 | CFL | AllSpc | 2010 | 0.437 | 2010 | 0.437 | 1.06 | 1.17 | -0.00291
CFLAllSpcSCEMLINewCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCE | MLI | New | CZ09 | 2.01 | 0.000437 | 0 | 2.2 | 0.000562 | -0.00673 | 2.01 | 0.000437 | 0 | 2.2 | 0.000562 | -0.00673 | CFL | AllSpc | 2010 | 0.437 | 2010 | 0.437 | 1.09 | 1.29 | -0.00335
CFLAllSpcSCEMLINewCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCE | MLI | New | CZ10 | 2.01 | 0.000437 | 0 | 2.21 | 0.000571 | -0.00736 | 2.01 | 0.000437 | 0 | 2.21 | 0.000571 | -0.00736 | CFL | AllSpc | 2010 | 0.437 | 2010 | 0.437 | 1.1 | 1.31 | -0.00366
CFLAllSpcSDGMLINewCZ10 | Com-Iltg-dWatt-CFL_OSspc | SDG | MLI | New | CZ10 | 2.01 | 0.000437 | 0 | 2.22 | 0.000576 | -0.00788 | 2.01 | 0.000437 | 0 | 2.22 | 0.000576 | -0.00788 | CFL | AllSpc | 2010 | 0.437 | 2010 | 0.437 | 1.1 | 1.32 | -0.00392
CFLAllSpcPGEMLINewCZ11 | Com-Iltg-dWatt-CFL_OSspc | PGE | MLI | New | CZ11 | 2.01 | 0.000437 | 0 | 2.1 | 0.000522 | -0.0143 | 2.01 | 0.000437 | 0 | 2.1 | 0.000522 | -0.0143 | CFL | AllSpc | 2010 | 0.437 | 2010 | 0.437 | 1.04 | 1.19 | -0.00711
CFLAllSpcPGEMLINewCZ12 | Com-Iltg-dWatt-CFL_OSspc | PGE | MLI | New | CZ12 | 2.01 | 0.000437 | 0 | 2.07 | 0.000515 | -0.0155 | 2.01 | 0.000437 | 0 | 2.07 | 0.000515 | -0.0155 | CFL | AllSpc | 2010 | 0.437 | 2010 | 0.437 | 1.03 | 1.18 | -0.00771
CFLAllSpcPGEMLINewCZ13 | Com-Iltg-dWatt-CFL_OSspc | PGE | MLI | New | CZ13 | 2.01 | 0.000437 | 0 | 2.13 | 0.000525 | -0.0134 | 2.01 | 0.000437 | 0 | 2.13 | 0.000525 | -0.0134 | CFL | AllSpc | 2010 | 0.437 | 2010 | 0.437 | 1.06 | 1.2 | -0.00667
CFLAllSpcSCEMLINewCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCE | MLI | New | CZ13 | 2.01 | 0.000437 | 0 | 2.16 | 0.000549 | -0.0133 | 2.01 | 0.000437 | 0 | 2.16 | 0.000549 | -0.0133 | CFL | AllSpc | 2010 | 0.437 | 2010 | 0.437 | 1.07 | 1.26 | -0.00662
CFLAllSpcSCEMLINewCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCE | MLI | New | CZ14 | 2.01 | 0.000437 | 0 | 2.13 | 0.000534 | -0.0145 | 2.01 | 0.000437 | 0 | 2.13 | 0.000534 | -0.0145 | CFL | AllSpc | 2010 | 0.437 | 2010 | 0.437 | 1.06 | 1.22 | -0.00721
CFLAllSpcSDGMLINewCZ14 | Com-Iltg-dWatt-CFL_OSspc | SDG | MLI | New | CZ14 | 2.01 | 0.000437 | 0 | 2.13 | 0.000537 | -0.0155 | 2.01 | 0.000437 | 0 | 2.13 | 0.000537 | -0.0155 | CFL | AllSpc | 2010 | 0.437 | 2010 | 0.437 | 1.06 | 1.23 | -0.00771
CFLAllSpcSDGMLINewCZ15 | Com-Iltg-dWatt-CFL_OSspc | SDG | MLI | New | CZ15 | 2.01 | 0.000437 | 0 | 2.37 | 0.000586 | -0.00132 | 2.01 | 0.000437 | 0 | 2.37 | 0.000586 | -0.00132 | CFL | AllSpc | 2010 | 0.437 | 2010 | 0.437 | 1.18 | 1.34 | -0.000657
CFLAllSpcSCEMLINewCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCE | MLI | New | CZ15 | 2.01 | 0.000437 | 0 | 2.36 | 0.00058 | -0.00123 | 2.01 | 0.000437 | 0 | 2.36 | 0.00058 | -0.00123 | CFL | AllSpc | 2010 | 0.437 | 2010 | 0.437 | 1.17 | 1.33 | -0.000612
CFLAllSpcPGEMLINewCZ16 | Com-Iltg-dWatt-CFL_OSspc | PGE | MLI | New | CZ16 | 2.01 | 0.000437 | 0 | 1.97 | 0.000496 | -0.0261 | 2.01 | 0.000437 | 0 | 1.97 | 0.000496 | -0.0261 | CFL | AllSpc | 2010 | 0.437 | 2010 | 0.437 | 0.98 | 1.14 | -0.013
CFLAllSpcSCEMLINewCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCE | MLI | New | CZ16 | 2.01 | 0.000437 | 0 | 1.98 | 0.000514 | -0.0257 | 2.01 | 0.000437 | 0 | 1.98 | 0.000514 | -0.0257 | CFL | AllSpc | 2010 | 0.437 | 2010 | 0.437 | 0.985 | 1.18 | -0.0128
CFLAllSpcSDGMLINewIOU | Com-Iltg-dWatt-CFL_OSspc | SDG | MLI | New | IOU | 2.01 | 0.000437 | 0 | 2.14 | 0.000532 | -0.00579 | 2.01 | 0.000437 | 0 | 2.14 | 0.000532 | -0.00579 | CFL | AllSpc | 2010 | 0.437 | 2010 | 0.437 | 1.06 | 1.22 | -0.00288
CFLAllSpcSCGMLINewIOU | Com-Iltg-dWatt-CFL_OSspc | SCG | MLI | New | IOU | 2.01 | 0.000437 | 0 | 2.19 | 0.000546 | -0.00702 | 2.01 | 0.000437 | 0 | 2.19 | 0.000546 | -0.00702 | CFL | AllSpc | 2010 | 0.437 | 2010 | 0.437 | 1.09 | 1.25 | -0.00349
CFLAllSpcSCEMLINewIOU | Com-Iltg-dWatt-CFL_OSspc | SCE | MLI | New | IOU | 2.01 | 0.000437 | 0 | 2.2 | 0.000548 | -0.00704 | 2.01 | 0.000437 | 0 | 2.2 | 0.000548 | -0.00704 | CFL | AllSpc | 2010 | 0.437 | 2010 | 0.437 | 1.09 | 1.25 | -0.0035
CFLAllSpcPGEMLINewIOU | Com-Iltg-dWatt-CFL_OSspc | PGE | MLI | New | IOU | 2.01 | 0.000437 | 0 | 2.13 | 0.000544 | -0.0144 | 2.01 | 0.000437 | 0 | 2.13 | 0.000544 | -0.0144 | CFL | AllSpc | 2010 | 0.437 | 2010 | 0.437 | 1.06 | 1.24 | -0.00716
CFLAllSpcPGEMtlExCZ01 | Com-Iltg-dWatt-CFL_OSspc | PGE | Mtl | Ex | CZ01 | 0.862 | 7.17e-05 | 0 | 0.85 | 8.53e-05 | -0.00743 | 0.862 | 7.17e-05 | 0 | 0.85 | 8.53e-05 | -0.00743 | CFL | AllSpc | 862 | 0.0717 | 862 | 0.0717 | 0.986 | 1.19 | -0.00862
CFLAllSpcPGEMtlExCZ02 | Com-Iltg-dWatt-CFL_OSspc | PGE | Mtl | Ex | CZ02 | 0.862 | 7.17e-05 | 0 | 0.898 | 8.85e-05 | -0.00492 | 0.862 | 7.17e-05 | 0 | 0.898 | 8.85e-05 | -0.00492 | CFL | AllSpc | 862 | 0.0717 | 862 | 0.0717 | 1.04 | 1.23 | -0.00571
CFLAllSpcPGEMtlExCZ03 | Com-Iltg-dWatt-CFL_OSspc | PGE | Mtl | Ex | CZ03 | 0.862 | 7.17e-05 | 0 | 0.908 | 8.65e-05 | -0.00478 | 0.862 | 7.17e-05 | 0 | 0.908 | 8.65e-05 | -0.00478 | CFL | AllSpc | 862 | 0.0717 | 862 | 0.0717 | 1.05 | 1.21 | -0.00555
CFLAllSpcPGEMtlExCZ04 | Com-Iltg-dWatt-CFL_OSspc | PGE | Mtl | Ex | CZ04 | 0.862 | 7.17e-05 | 0 | 0.92 | 8.77e-05 | -0.00395 | 0.862 | 7.17e-05 | 0 | 0.92 | 8.77e-05 | -0.00395 | CFL | AllSpc | 862 | 0.0717 | 862 | 0.0717 | 1.07 | 1.22 | -0.00458
CFLAllSpcPGEMtlExCZ05 | Com-Iltg-dWatt-CFL_OSspc | PGE | Mtl | Ex | CZ05 | 0.862 | 7.17e-05 | 0 | 0.921 | 9.01e-05 | -0.00412 | 0.862 | 7.17e-05 | 0 | 0.921 | 9.01e-05 | -0.00412 | CFL | AllSpc | 862 | 0.0717 | 862 | 0.0717 | 1.07 | 1.26 | -0.00478
CFLAllSpcSCGMtlExCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCG | Mtl | Ex | CZ05 | 0.862 | 7.17e-05 | 0 | 0.921 | 9.01e-05 | -0.00412 | 0.862 | 7.17e-05 | 0 | 0.921 | 9.01e-05 | -0.00412 | CFL | AllSpc | 862 | 0.0717 | 862 | 0.0717 | 1.07 | 1.26 | -0.00478
CFLAllSpcSCEMtlExCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCE | Mtl | Ex | CZ05 | 0.862 | 7.17e-05 | 0 | 0.921 | 9.01e-05 | -0.00412 | 0.862 | 7.17e-05 | 0 | 0.921 | 9.01e-05 | -0.00412 | CFL | AllSpc | 862 | 0.0717 | 862 | 0.0717 | 1.07 | 1.26 | -0.00478
CFLAllSpcSCEMtlExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCE | Mtl | Ex | CZ06 | 0.862 | 7.17e-05 | 0 | 0.976 | 9e-05 | -0.00229 | 0.862 | 7.17e-05 | 0 | 0.976 | 9e-05 | -0.00229 | CFL | AllSpc | 862 | 0.0717 | 862 | 0.0717 | 1.13 | 1.26 | -0.00266
CFLAllSpcSDGMtlExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SDG | Mtl | Ex | CZ06 | 0.862 | 7.17e-05 | 0 | 0.976 | 9e-05 | -0.00229 | 0.862 | 7.17e-05 | 0 | 0.976 | 9e-05 | -0.00229 | CFL | AllSpc | 862 | 0.0717 | 862 | 0.0717 | 1.13 | 1.26 | -0.00266
CFLAllSpcSCGMtlExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCG | Mtl | Ex | CZ06 | 0.862 | 7.17e-05 | 0 | 0.976 | 9e-05 | -0.00229 | 0.862 | 7.17e-05 | 0 | 0.976 | 9e-05 | -0.00229 | CFL | AllSpc | 862 | 0.0717 | 862 | 0.0717 | 1.13 | 1.26 | -0.00266
CFLAllSpcSDGMtlExCZ07 | Com-Iltg-dWatt-CFL_OSspc | SDG | Mtl | Ex | CZ07 | 0.862 | 7.17e-05 | 0 | 0.994 | 8.94e-05 | -0.00163 | 0.862 | 7.17e-05 | 0 | 0.994 | 8.94e-05 | -0.00163 | CFL | AllSpc | 862 | 0.0717 | 862 | 0.0717 | 1.15 | 1.25 | -0.00189
CFLAllSpcSDGMtlExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SDG | Mtl | Ex | CZ08 | 0.862 | 7.17e-05 | 0 | 0.988 | 9.1e-05 | -0.00191 | 0.862 | 7.17e-05 | 0 | 0.988 | 9.1e-05 | -0.00191 | CFL | AllSpc | 862 | 0.0717 | 862 | 0.0717 | 1.15 | 1.27 | -0.00222
CFLAllSpcSCEMtlExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCE | Mtl | Ex | CZ08 | 0.862 | 7.17e-05 | 0 | 0.988 | 9.1e-05 | -0.00191 | 0.862 | 7.17e-05 | 0 | 0.988 | 9.1e-05 | -0.00191 | CFL | AllSpc | 862 | 0.0717 | 862 | 0.0717 | 1.15 | 1.27 | -0.00222
CFLAllSpcSCGMtlExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCG | Mtl | Ex | CZ08 | 0.862 | 7.17e-05 | 0 | 0.988 | 9.1e-05 | -0.00191 | 0.862 | 7.17e-05 | 0 | 0.988 | 9.1e-05 | -0.00191 | CFL | AllSpc | 862 | 0.0717 | 862 | 0.0717 | 1.15 | 1.27 | -0.00222
CFLAllSpcSCGMtlExCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCG | Mtl | Ex | CZ09 | 0.862 | 7.17e-05 | 0 | 0.996 | 9.41e-05 | -0.00201 | 0.862 | 7.17e-05 | 0 | 0.996 | 9.41e-05 | -0.00201 | CFL | AllSpc | 862 | 0.0717 | 862 | 0.0717 | 1.16 | 1.31 | -0.00233
CFLAllSpcSCEMtlExCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCE | Mtl | Ex | CZ09 | 0.862 | 7.17e-05 | 0 | 0.996 | 9.41e-05 | -0.00201 | 0.862 | 7.17e-05 | 0 | 0.996 | 9.41e-05 | -0.00201 | CFL | AllSpc | 862 | 0.0717 | 862 | 0.0717 | 1.16 | 1.31 | -0.00233
CFLAllSpcSCGMtlExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCG | Mtl | Ex | CZ10 | 0.862 | 7.17e-05 | 0 | 0.979 | 9.37e-05 | -0.00228 | 0.862 | 7.17e-05 | 0 | 0.979 | 9.37e-05 | -0.00228 | CFL | AllSpc | 862 | 0.0717 | 862 | 0.0717 | 1.14 | 1.31 | -0.00265
CFLAllSpcSDGMtlExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SDG | Mtl | Ex | CZ10 | 0.862 | 7.17e-05 | 0 | 0.979 | 9.37e-05 | -0.00228 | 0.862 | 7.17e-05 | 0 | 0.979 | 9.37e-05 | -0.00228 | CFL | AllSpc | 862 | 0.0717 | 862 | 0.0717 | 1.14 | 1.31 | -0.00265
CFLAllSpcSCEMtlExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCE | Mtl | Ex | CZ10 | 0.862 | 7.17e-05 | 0 | 0.979 | 9.37e-05 | -0.00228 | 0.862 | 7.17e-05 | 0 | 0.979 | 9.37e-05 | -0.00228 | CFL | AllSpc | 862 | 0.0717 | 862 | 0.0717 | 1.14 | 1.31 | -0.00265
CFLAllSpcPGEMtlExCZ11 | Com-Iltg-dWatt-CFL_OSspc | PGE | Mtl | Ex | CZ11 | 0.862 | 7.17e-05 | 0 | 0.927 | 8.93e-05 | -0.00415 | 0.862 | 7.17e-05 | 0 | 0.927 | 8.93e-05 | -0.00415 | CFL | AllSpc | 862 | 0.0717 | 862 | 0.0717 | 1.08 | 1.25 | -0.00481
CFLAllSpcPGEMtlExCZ12 | Com-Iltg-dWatt-CFL_OSspc | PGE | Mtl | Ex | CZ12 | 0.862 | 7.17e-05 | 0 | 0.919 | 8.93e-05 | -0.00438 | 0.862 | 7.17e-05 | 0 | 0.919 | 8.93e-05 | -0.00438 | CFL | AllSpc | 862 | 0.0717 | 862 | 0.0717 | 1.07 | 1.25 | -0.00508
CFLAllSpcSCEMtlExCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCE | Mtl | Ex | CZ13 | 0.862 | 7.17e-05 | 0 | 0.96 | 9.37e-05 | -0.00318 | 0.862 | 7.17e-05 | 0 | 0.96 | 9.37e-05 | -0.00318 | CFL | AllSpc | 862 | 0.0717 | 862 | 0.0717 | 1.11 | 1.31 | -0.00369
CFLAllSpcPGEMtlExCZ13 | Com-Iltg-dWatt-CFL_OSspc | PGE | Mtl | Ex | CZ13 | 0.862 | 7.17e-05 | 0 | 0.96 | 9.37e-05 | -0.00318 | 0.862 | 7.17e-05 | 0 | 0.96 | 9.37e-05 | -0.00318 | CFL | AllSpc | 862 | 0.0717 | 862 | 0.0717 | 1.11 | 1.31 | -0.00369
CFLAllSpcSCGMtlExCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCG | Mtl | Ex | CZ13 | 0.862 | 7.17e-05 | 0 | 0.96 | 9.37e-05 | -0.00318 | 0.862 | 7.17e-05 | 0 | 0.96 | 9.37e-05 | -0.00318 | CFL | AllSpc | 862 | 0.0717 | 862 | 0.0717 | 1.11 | 1.31 | -0.00369
CFLAllSpcSDGMtlExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SDG | Mtl | Ex | CZ14 | 0.862 | 7.17e-05 | 0 | 0.948 | 9.35e-05 | -0.00322 | 0.862 | 7.17e-05 | 0 | 0.948 | 9.35e-05 | -0.00322 | CFL | AllSpc | 862 | 0.0717 | 862 | 0.0717 | 1.1 | 1.3 | -0.00374
CFLAllSpcSCEMtlExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCE | Mtl | Ex | CZ14 | 0.862 | 7.17e-05 | 0 | 0.948 | 9.35e-05 | -0.00322 | 0.862 | 7.17e-05 | 0 | 0.948 | 9.35e-05 | -0.00322 | CFL | AllSpc | 862 | 0.0717 | 862 | 0.0717 | 1.1 | 1.3 | -0.00374
CFLAllSpcSCGMtlExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCG | Mtl | Ex | CZ14 | 0.862 | 7.17e-05 | 0 | 0.948 | 9.35e-05 | -0.00322 | 0.862 | 7.17e-05 | 0 | 0.948 | 9.35e-05 | -0.00322 | CFL | AllSpc | 862 | 0.0717 | 862 | 0.0717 | 1.1 | 1.3 | -0.00374
CFLAllSpcSDGMtlExCZ15 | Com-Iltg-dWatt-CFL_OSspc | SDG | Mtl | Ex | CZ15 | 0.862 | 7.17e-05 | 0 | 1.04 | 9.51e-05 | -0.000931 | 0.862 | 7.17e-05 | 0 | 1.04 | 9.51e-05 | -0.000931 | CFL | AllSpc | 862 | 0.0717 | 862 | 0.0717 | 1.21 | 1.33 | -0.00108
CFLAllSpcSCEMtlExCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCE | Mtl | Ex | CZ15 | 0.862 | 7.17e-05 | 0 | 1.04 | 9.51e-05 | -0.000931 | 0.862 | 7.17e-05 | 0 | 1.04 | 9.51e-05 | -0.000931 | CFL | AllSpc | 862 | 0.0717 | 862 | 0.0717 | 1.21 | 1.33 | -0.00108
CFLAllSpcSCGMtlExCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCG | Mtl | Ex | CZ15 | 0.862 | 7.17e-05 | 0 | 1.04 | 9.51e-05 | -0.000931 | 0.862 | 7.17e-05 | 0 | 1.04 | 9.51e-05 | -0.000931 | CFL | AllSpc | 862 | 0.0717 | 862 | 0.0717 | 1.21 | 1.33 | -0.00108
CFLAllSpcPGEMtlExCZ16 | Com-Iltg-dWatt-CFL_OSspc | PGE | Mtl | Ex | CZ16 | 0.862 | 7.17e-05 | 0 | 0.858 | 9.01e-05 | -0.00547 | 0.862 | 7.17e-05 | 0 | 0.858 | 9.01e-05 | -0.00547 | CFL | AllSpc | 862 | 0.0717 | 862 | 0.0717 | 0.995 | 1.26 | -0.00635
CFLAllSpcSCGMtlExCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCG | Mtl | Ex | CZ16 | 0.862 | 7.17e-05 | 0 | 0.858 | 9.01e-05 | -0.00547 | 0.862 | 7.17e-05 | 0 | 0.858 | 9.01e-05 | -0.00547 | CFL | AllSpc | 862 | 0.0717 | 862 | 0.0717 | 0.995 | 1.26 | -0.00635
CFLAllSpcSCEMtlExCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCE | Mtl | Ex | CZ16 | 0.862 | 7.17e-05 | 0 | 0.858 | 9.01e-05 | -0.00547 | 0.862 | 7.17e-05 | 0 | 0.858 | 9.01e-05 | -0.00547 | CFL | AllSpc | 862 | 0.0717 | 862 | 0.0717 | 0.995 | 1.26 | -0.00635
CFLAllSpcSCGMtlExIOU | Com-Iltg-dWatt-CFL_OSspc | SCG | Mtl | Ex | IOU | 0.862 | 7.17e-05 | 0 | 0.987 | 9.22e-05 | -0.0021 | 0.862 | 7.17e-05 | 0 | 0.987 | 9.22e-05 | -0.0021 | CFL | AllSpc | 862 | 0.0717 | 862 | 0.0717 | 1.15 | 1.29 | -0.00244
CFLAllSpcPGEMtlExIOU | Com-Iltg-dWatt-CFL_OSspc | PGE | Mtl | Ex | IOU | 0.862 | 7.17e-05 | 0 | 0.915 | 8.82e-05 | -0.00447 | 0.862 | 7.17e-05 | 0 | 0.915 | 8.82e-05 | -0.00447 | CFL | AllSpc | 862 | 0.0717 | 862 | 0.0717 | 1.06 | 1.23 | -0.00519
CFLAllSpcSCEMtlExIOU | Com-Iltg-dWatt-CFL_OSspc | SCE | Mtl | Ex | IOU | 0.862 | 7.17e-05 | 0 | 0.986 | 9.19e-05 | -0.00213 | 0.862 | 7.17e-05 | 0 | 0.986 | 9.19e-05 | -0.00213 | CFL | AllSpc | 862 | 0.0717 | 862 | 0.0717 | 1.14 | 1.28 | -0.00247
CFLAllSpcSDGMtlExIOU | Com-Iltg-dWatt-CFL_OSspc | SDG | Mtl | Ex | IOU | 0.862 | 7.17e-05 | 0 | 0.992 | 8.99e-05 | -0.00173 | 0.862 | 7.17e-05 | 0 | 0.992 | 8.99e-05 | -0.00173 | CFL | AllSpc | 862 | 0.0717 | 862 | 0.0717 | 1.15 | 1.25 | -0.00201
CFLAllSpcPGEMtlNewCZ01 | Com-Iltg-dWatt-CFL_OSspc | PGE | Mtl | New | CZ01 | 0.862 | 7.17e-05 | 0 | 0.815 | 8.53e-05 | -0.00957 | 0.862 | 7.17e-05 | 0 | 0.815 | 8.53e-05 | -0.00957 | CFL | AllSpc | 862 | 0.0717 | 862 | 0.0717 | 0.945 | 1.19 | -0.0111
CFLAllSpcPGEMtlNewCZ02 | Com-Iltg-dWatt-CFL_OSspc | PGE | Mtl | New | CZ02 | 0.862 | 7.17e-05 | 0 | 0.882 | 9.06e-05 | -0.00646 | 0.862 | 7.17e-05 | 0 | 0.882 | 9.06e-05 | -0.00646 | CFL | AllSpc | 862 | 0.0717 | 862 | 0.0717 | 1.02 | 1.26 | -0.00749
CFLAllSpcPGEMtlNewCZ03 | Com-Iltg-dWatt-CFL_OSspc | PGE | Mtl | New | CZ03 | 0.862 | 7.17e-05 | 0 | 0.889 | 8.78e-05 | -0.00607 | 0.862 | 7.17e-05 | 0 | 0.889 | 8.78e-05 | -0.00607 | CFL | AllSpc | 862 | 0.0717 | 862 | 0.0717 | 1.03 | 1.22 | -0.00704
CFLAllSpcPGEMtlNewCZ04 | Com-Iltg-dWatt-CFL_OSspc | PGE | Mtl | New | CZ04 | 0.862 | 7.17e-05 | 0 | 0.91 | 8.98e-05 | -0.00511 | 0.862 | 7.17e-05 | 0 | 0.91 | 8.98e-05 | -0.00511 | CFL | AllSpc | 862 | 0.0717 | 862 | 0.0717 | 1.06 | 1.25 | -0.00593
CFLAllSpcSCEMtlNewCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCE | Mtl | New | CZ05 | 0.862 | 7.17e-05 | 0 | 0.888 | 9.08e-05 | -0.00553 | 0.862 | 7.17e-05 | 0 | 0.888 | 9.08e-05 | -0.00553 | CFL | AllSpc | 862 | 0.0717 | 862 | 0.0717 | 1.03 | 1.27 | -0.00642
CFLAllSpcPGEMtlNewCZ05 | Com-Iltg-dWatt-CFL_OSspc | PGE | Mtl | New | CZ05 | 0.862 | 7.17e-05 | 0 | 0.874 | 8.7e-05 | -0.00681 | 0.862 | 7.17e-05 | 0 | 0.874 | 8.7e-05 | -0.00681 | CFL | AllSpc | 862 | 0.0717 | 862 | 0.0717 | 1.01 | 1.21 | -0.0079
CFLAllSpcSDGMtlNewCZ06 | Com-Iltg-dWatt-CFL_OSspc | SDG | Mtl | New | CZ06 | 0.862 | 7.17e-05 | 0 | 0.969 | 9.2e-05 | -0.00302 | 0.862 | 7.17e-05 | 0 | 0.969 | 9.2e-05 | -0.00302 | CFL | AllSpc | 862 | 0.0717 | 862 | 0.0717 | 1.12 | 1.28 | -0.0035
CFLAllSpcSCEMtlNewCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCE | Mtl | New | CZ06 | 0.862 | 7.17e-05 | 0 | 0.973 | 9.26e-05 | -0.00293 | 0.862 | 7.17e-05 | 0 | 0.973 | 9.26e-05 | -0.00293 | CFL | AllSpc | 862 | 0.0717 | 862 | 0.0717 | 1.13 | 1.29 | -0.0034
CFLAllSpcSDGMtlNewCZ07 | Com-Iltg-dWatt-CFL_OSspc | SDG | Mtl | New | CZ07 | 0.862 | 7.17e-05 | 0 | 0.989 | 9.08e-05 | -0.00208 | 0.862 | 7.17e-05 | 0 | 0.989 | 9.08e-05 | -0.00208 | CFL | AllSpc | 862 | 0.0717 | 862 | 0.0717 | 1.15 | 1.27 | -0.00241
CFLAllSpcSDGMtlNewCZ08 | Com-Iltg-dWatt-CFL_OSspc | SDG | Mtl | New | CZ08 | 0.862 | 7.17e-05 | 0 | 0.985 | 9.34e-05 | -0.00252 | 0.862 | 7.17e-05 | 0 | 0.985 | 9.34e-05 | -0.00252 | CFL | AllSpc | 862 | 0.0717 | 862 | 0.0717 | 1.14 | 1.3 | -0.00292
CFLAllSpcSCEMtlNewCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCE | Mtl | New | CZ08 | 0.862 | 7.17e-05 | 0 | 0.989 | 9.41e-05 | -0.00244 | 0.862 | 7.17e-05 | 0 | 0.989 | 9.41e-05 | -0.00244 | CFL | AllSpc | 862 | 0.0717 | 862 | 0.0717 | 1.15 | 1.31 | -0.00283
CFLAllSpcSCEMtlNewCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCE | Mtl | New | CZ09 | 0.862 | 7.17e-05 | 0 | 0.99 | 9.66e-05 | -0.00246 | 0.862 | 7.17e-05 | 0 | 0.99 | 9.66e-05 | -0.00246 | CFL | AllSpc | 862 | 0.0717 | 862 | 0.0717 | 1.15 | 1.35 | -0.00285
CFLAllSpcSDGMtlNewCZ10 | Com-Iltg-dWatt-CFL_OSspc | SDG | Mtl | New | CZ10 | 0.862 | 7.17e-05 | 0 | 0.97 | 9.62e-05 | -0.00315 | 0.862 | 7.17e-05 | 0 | 0.97 | 9.62e-05 | -0.00315 | CFL | AllSpc | 862 | 0.0717 | 862 | 0.0717 | 1.13 | 1.34 | -0.00365
CFLAllSpcSCEMtlNewCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCE | Mtl | New | CZ10 | 0.862 | 7.17e-05 | 0 | 0.974 | 9.69e-05 | -0.00304 | 0.862 | 7.17e-05 | 0 | 0.974 | 9.69e-05 | -0.00304 | CFL | AllSpc | 862 | 0.0717 | 862 | 0.0717 | 1.13 | 1.35 | -0.00353
CFLAllSpcPGEMtlNewCZ11 | Com-Iltg-dWatt-CFL_OSspc | PGE | Mtl | New | CZ11 | 0.862 | 7.17e-05 | 0 | 0.919 | 9.16e-05 | -0.00517 | 0.862 | 7.17e-05 | 0 | 0.919 | 9.16e-05 | -0.00517 | CFL | AllSpc | 862 | 0.0717 | 862 | 0.0717 | 1.07 | 1.28 | -0.006
CFLAllSpcPGEMtlNewCZ12 | Com-Iltg-dWatt-CFL_OSspc | PGE | Mtl | New | CZ12 | 0.862 | 7.17e-05 | 0 | 0.91 | 9.12e-05 | -0.0054 | 0.862 | 7.17e-05 | 0 | 0.91 | 9.12e-05 | -0.0054 | CFL | AllSpc | 862 | 0.0717 | 862 | 0.0717 | 1.06 | 1.27 | -0.00626
CFLAllSpcSCEMtlNewCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCE | Mtl | New | CZ13 | 0.862 | 7.17e-05 | 0 | 0.948 | 9.57e-05 | -0.00393 | 0.862 | 7.17e-05 | 0 | 0.948 | 9.57e-05 | -0.00393 | CFL | AllSpc | 862 | 0.0717 | 862 | 0.0717 | 1.1 | 1.33 | -0.00456
CFLAllSpcPGEMtlNewCZ13 | Com-Iltg-dWatt-CFL_OSspc | PGE | Mtl | New | CZ13 | 0.862 | 7.17e-05 | 0 | 0.925 | 9.08e-05 | -0.00486 | 0.862 | 7.17e-05 | 0 | 0.925 | 9.08e-05 | -0.00486 | CFL | AllSpc | 862 | 0.0717 | 862 | 0.0717 | 1.07 | 1.27 | -0.00564
CFLAllSpcSDGMtlNewCZ14 | Com-Iltg-dWatt-CFL_OSspc | SDG | Mtl | New | CZ14 | 0.862 | 7.17e-05 | 0 | 0.934 | 9.6e-05 | -0.00422 | 0.862 | 7.17e-05 | 0 | 0.934 | 9.6e-05 | -0.00422 | CFL | AllSpc | 862 | 0.0717 | 862 | 0.0717 | 1.08 | 1.34 | -0.0049
CFLAllSpcSCEMtlNewCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCE | Mtl | New | CZ14 | 0.862 | 7.17e-05 | 0 | 0.937 | 9.67e-05 | -0.00409 | 0.862 | 7.17e-05 | 0 | 0.937 | 9.67e-05 | -0.00409 | CFL | AllSpc | 862 | 0.0717 | 862 | 0.0717 | 1.09 | 1.35 | -0.00474
CFLAllSpcSDGMtlNewCZ15 | Com-Iltg-dWatt-CFL_OSspc | SDG | Mtl | New | CZ15 | 0.862 | 7.17e-05 | 0 | 1.04 | 9.82e-05 | -0.00145 | 0.862 | 7.17e-05 | 0 | 1.04 | 9.82e-05 | -0.00145 | CFL | AllSpc | 862 | 0.0717 | 862 | 0.0717 | 1.21 | 1.37 | -0.00168
CFLAllSpcSCEMtlNewCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCE | Mtl | New | CZ15 | 0.862 | 7.17e-05 | 0 | 1.05 | 9.91e-05 | -0.00141 | 0.862 | 7.17e-05 | 0 | 1.05 | 9.91e-05 | -0.00141 | CFL | AllSpc | 862 | 0.0717 | 862 | 0.0717 | 1.22 | 1.38 | -0.00164
CFLAllSpcPGEMtlNewCZ16 | Com-Iltg-dWatt-CFL_OSspc | PGE | Mtl | New | CZ16 | 0.862 | 7.17e-05 | 0 | 0.83 | 8.75e-05 | -0.00762 | 0.862 | 7.17e-05 | 0 | 0.83 | 8.75e-05 | -0.00762 | CFL | AllSpc | 862 | 0.0717 | 862 | 0.0717 | 0.963 | 1.22 | -0.00884
CFLAllSpcSCEMtlNewCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCE | Mtl | New | CZ16 | 0.862 | 7.17e-05 | 0 | 0.834 | 9.14e-05 | -0.00636 | 0.862 | 7.17e-05 | 0 | 0.834 | 9.14e-05 | -0.00636 | CFL | AllSpc | 862 | 0.0717 | 862 | 0.0717 | 0.968 | 1.27 | -0.00738
CFLAllSpcSDGMtlNewIOU | Com-Iltg-dWatt-CFL_OSspc | SDG | Mtl | New | IOU | 0.862 | 7.17e-05 | 0 | 0.986 | 9.15e-05 | -0.00224 | 0.862 | 7.17e-05 | 0 | 0.986 | 9.15e-05 | -0.00224 | CFL | AllSpc | 862 | 0.0717 | 862 | 0.0717 | 1.14 | 1.28 | -0.0026
CFLAllSpcSCEMtlNewIOU | Com-Iltg-dWatt-CFL_OSspc | SCE | Mtl | New | IOU | 0.862 | 7.17e-05 | 0 | 0.994 | 9.51e-05 | -0.00249 | 0.862 | 7.17e-05 | 0 | 0.994 | 9.51e-05 | -0.00249 | CFL | AllSpc | 862 | 0.0717 | 862 | 0.0717 | 1.15 | 1.33 | -0.00289
CFLAllSpcPGEMtlNewIOU | Com-Iltg-dWatt-CFL_OSspc | PGE | Mtl | New | IOU | 0.862 | 7.17e-05 | 0 | 0.915 | 9.35e-05 | -0.00475 | 0.862 | 7.17e-05 | 0 | 0.915 | 9.35e-05 | -0.00475 | CFL | AllSpc | 862 | 0.0717 | 862 | 0.0717 | 1.06 | 1.3 | -0.00551
CFLAllSpcSCGMtlNewIOU | Com-Iltg-dWatt-CFL_OSspc | SCG | Mtl | New | IOU | 0.862 | 7.17e-05 | 0 | 0.992 | 9.48e-05 | -0.00252 | 0.862 | 7.17e-05 | 0 | 0.992 | 9.48e-05 | -0.00252 | CFL | AllSpc | 862 | 0.0717 | 862 | 0.0717 | 1.15 | 1.32 | -0.00292
CFLAllSpcPGENrsExCZ01 | Com-Iltg-dWatt-CFL_OSspc | PGE | Nrs | Ex | CZ01 | 3.05 | 0.000416 | 0 | 3 | 0.000475 | -0.0616 | 3.05 | 0.000416 | 0 | 3 | 0.000475 | -0.0616 | CFL | AllSpc | 3050 | 0.416 | 3050 | 0.416 | 0.984 | 1.14 | -0.0202
CFLAllSpcPGENrsExCZ02 | Com-Iltg-dWatt-CFL_OSspc | PGE | Nrs | Ex | CZ02 | 3.05 | 0.000416 | 0 | 3.16 | 0.000522 | -0.0445 | 3.05 | 0.000416 | 0 | 3.16 | 0.000522 | -0.0445 | CFL | AllSpc | 3050 | 0.416 | 3050 | 0.416 | 1.04 | 1.25 | -0.0146
CFLAllSpcPGENrsExCZ03 | Com-Iltg-dWatt-CFL_OSspc | PGE | Nrs | Ex | CZ03 | 3.05 | 0.000416 | 0 | 3.13 | 0.000507 | -0.0451 | 3.05 | 0.000416 | 0 | 3.13 | 0.000507 | -0.0451 | CFL | AllSpc | 3050 | 0.416 | 3050 | 0.416 | 1.03 | 1.22 | -0.0148
CFLAllSpcPGENrsExCZ04 | Com-Iltg-dWatt-CFL_OSspc | PGE | Nrs | Ex | CZ04 | 3.05 | 0.000416 | 0 | 3.21 | 0.000518 | -0.0381 | 3.05 | 0.000416 | 0 | 3.21 | 0.000518 | -0.0381 | CFL | AllSpc | 3050 | 0.416 | 3050 | 0.416 | 1.05 | 1.25 | -0.0125
CFLAllSpcSCENrsExCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCE | Nrs | Ex | CZ05 | 3.05 | 0.000416 | 0 | 3.12 | 0.000513 | -0.0445 | 3.05 | 0.000416 | 0 | 3.12 | 0.000513 | -0.0445 | CFL | AllSpc | 3050 | 0.416 | 3050 | 0.416 | 1.02 | 1.23 | -0.0146
CFLAllSpcPGENrsExCZ05 | Com-Iltg-dWatt-CFL_OSspc | PGE | Nrs | Ex | CZ05 | 3.05 | 0.000416 | 0 | 3.12 | 0.000513 | -0.0445 | 3.05 | 0.000416 | 0 | 3.12 | 0.000513 | -0.0445 | CFL | AllSpc | 3050 | 0.416 | 3050 | 0.416 | 1.02 | 1.23 | -0.0146
CFLAllSpcSCGNrsExCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCG | Nrs | Ex | CZ05 | 3.05 | 0.000416 | 0 | 3.12 | 0.000513 | -0.0445 | 3.05 | 0.000416 | 0 | 3.12 | 0.000513 | -0.0445 | CFL | AllSpc | 3050 | 0.416 | 3050 | 0.416 | 1.02 | 1.23 | -0.0146
CFLAllSpcSDGNrsExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SDG | Nrs | Ex | CZ06 | 3.05 | 0.000416 | 0 | 3.29 | 0.000537 | -0.0289 | 3.05 | 0.000416 | 0 | 3.29 | 0.000537 | -0.0289 | CFL | AllSpc | 3050 | 0.416 | 3050 | 0.416 | 1.08 | 1.29 | -0.00948
CFLAllSpcSCENrsExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCE | Nrs | Ex | CZ06 | 3.05 | 0.000416 | 0 | 3.29 | 0.000537 | -0.0289 | 3.05 | 0.000416 | 0 | 3.29 | 0.000537 | -0.0289 | CFL | AllSpc | 3050 | 0.416 | 3050 | 0.416 | 1.08 | 1.29 | -0.00948
CFLAllSpcSCGNrsExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCG | Nrs | Ex | CZ06 | 3.05 | 0.000416 | 0 | 3.29 | 0.000537 | -0.0289 | 3.05 | 0.000416 | 0 | 3.29 | 0.000537 | -0.0289 | CFL | AllSpc | 3050 | 0.416 | 3050 | 0.416 | 1.08 | 1.29 | -0.00948
CFLAllSpcSDGNrsExCZ07 | Com-Iltg-dWatt-CFL_OSspc | SDG | Nrs | Ex | CZ07 | 3.05 | 0.000416 | 0 | 3.28 | 0.000527 | -0.0256 | 3.05 | 0.000416 | 0 | 3.28 | 0.000527 | -0.0256 | CFL | AllSpc | 3050 | 0.416 | 3050 | 0.416 | 1.08 | 1.27 | -0.00839
CFLAllSpcSCGNrsExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCG | Nrs | Ex | CZ08 | 3.05 | 0.000416 | 0 | 3.32 | 0.000539 | -0.0279 | 3.05 | 0.000416 | 0 | 3.32 | 0.000539 | -0.0279 | CFL | AllSpc | 3050 | 0.416 | 3050 | 0.416 | 1.09 | 1.3 | -0.00915
CFLAllSpcSCENrsExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCE | Nrs | Ex | CZ08 | 3.05 | 0.000416 | 0 | 3.32 | 0.000539 | -0.0279 | 3.05 | 0.000416 | 0 | 3.32 | 0.000539 | -0.0279 | CFL | AllSpc | 3050 | 0.416 | 3050 | 0.416 | 1.09 | 1.3 | -0.00915
CFLAllSpcSDGNrsExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SDG | Nrs | Ex | CZ08 | 3.05 | 0.000416 | 0 | 3.32 | 0.000539 | -0.0279 | 3.05 | 0.000416 | 0 | 3.32 | 0.000539 | -0.0279 | CFL | AllSpc | 3050 | 0.416 | 3050 | 0.416 | 1.09 | 1.3 | -0.00915
CFLAllSpcSCGNrsExCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCG | Nrs | Ex | CZ09 | 3.05 | 0.000416 | 0 | 3.36 | 0.000556 | -0.0291 | 3.05 | 0.000416 | 0 | 3.36 | 0.000556 | -0.0291 | CFL | AllSpc | 3050 | 0.416 | 3050 | 0.416 | 1.1 | 1.34 | -0.00954
CFLAllSpcSCENrsExCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCE | Nrs | Ex | CZ09 | 3.05 | 0.000416 | 0 | 3.36 | 0.000556 | -0.0291 | 3.05 | 0.000416 | 0 | 3.36 | 0.000556 | -0.0291 | CFL | AllSpc | 3050 | 0.416 | 3050 | 0.416 | 1.1 | 1.34 | -0.00954
CFLAllSpcSDGNrsExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SDG | Nrs | Ex | CZ10 | 3.05 | 0.000416 | 0 | 3.34 | 0.000556 | -0.0297 | 3.05 | 0.000416 | 0 | 3.34 | 0.000556 | -0.0297 | CFL | AllSpc | 3050 | 0.416 | 3050 | 0.416 | 1.1 | 1.34 | -0.00974
CFLAllSpcSCENrsExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCE | Nrs | Ex | CZ10 | 3.05 | 0.000416 | 0 | 3.34 | 0.000556 | -0.0297 | 3.05 | 0.000416 | 0 | 3.34 | 0.000556 | -0.0297 | CFL | AllSpc | 3050 | 0.416 | 3050 | 0.416 | 1.1 | 1.34 | -0.00974
CFLAllSpcSCGNrsExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCG | Nrs | Ex | CZ10 | 3.05 | 0.000416 | 0 | 3.34 | 0.000556 | -0.0297 | 3.05 | 0.000416 | 0 | 3.34 | 0.000556 | -0.0297 | CFL | AllSpc | 3050 | 0.416 | 3050 | 0.416 | 1.1 | 1.34 | -0.00974
CFLAllSpcPGENrsExCZ11 | Com-Iltg-dWatt-CFL_OSspc | PGE | Nrs | Ex | CZ11 | 3.05 | 0.000416 | 0 | 3.25 | 0.000527 | -0.0369 | 3.05 | 0.000416 | 0 | 3.25 | 0.000527 | -0.0369 | CFL | AllSpc | 3050 | 0.416 | 3050 | 0.416 | 1.07 | 1.27 | -0.0121
CFLAllSpcPGENrsExCZ12 | Com-Iltg-dWatt-CFL_OSspc | PGE | Nrs | Ex | CZ12 | 3.05 | 0.000416 | 0 | 3.22 | 0.000524 | -0.0387 | 3.05 | 0.000416 | 0 | 3.22 | 0.000524 | -0.0387 | CFL | AllSpc | 3050 | 0.416 | 3050 | 0.416 | 1.06 | 1.26 | -0.0127
CFLAllSpcPGENrsExCZ13 | Com-Iltg-dWatt-CFL_OSspc | PGE | Nrs | Ex | CZ13 | 3.05 | 0.000416 | 0 | 3.29 | 0.000549 | -0.0335 | 3.05 | 0.000416 | 0 | 3.29 | 0.000549 | -0.0335 | CFL | AllSpc | 3050 | 0.416 | 3050 | 0.416 | 1.08 | 1.32 | -0.011
CFLAllSpcSCENrsExCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCE | Nrs | Ex | CZ13 | 3.05 | 0.000416 | 0 | 3.29 | 0.000549 | -0.0335 | 3.05 | 0.000416 | 0 | 3.29 | 0.000549 | -0.0335 | CFL | AllSpc | 3050 | 0.416 | 3050 | 0.416 | 1.08 | 1.32 | -0.011
CFLAllSpcSCGNrsExCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCG | Nrs | Ex | CZ13 | 3.05 | 0.000416 | 0 | 3.29 | 0.000549 | -0.0335 | 3.05 | 0.000416 | 0 | 3.29 | 0.000549 | -0.0335 | CFL | AllSpc | 3050 | 0.416 | 3050 | 0.416 | 1.08 | 1.32 | -0.011
CFLAllSpcSDGNrsExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SDG | Nrs | Ex | CZ14 | 3.05 | 0.000416 | 0 | 3.3 | 0.00055 | -0.0348 | 3.05 | 0.000416 | 0 | 3.3 | 0.00055 | -0.0348 | CFL | AllSpc | 3050 | 0.416 | 3050 | 0.416 | 1.08 | 1.32 | -0.0114
CFLAllSpcSCENrsExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCE | Nrs | Ex | CZ14 | 3.05 | 0.000416 | 0 | 3.3 | 0.00055 | -0.0348 | 3.05 | 0.000416 | 0 | 3.3 | 0.00055 | -0.0348 | CFL | AllSpc | 3050 | 0.416 | 3050 | 0.416 | 1.08 | 1.32 | -0.0114
CFLAllSpcSCGNrsExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCG | Nrs | Ex | CZ14 | 3.05 | 0.000416 | 0 | 3.3 | 0.00055 | -0.0348 | 3.05 | 0.000416 | 0 | 3.3 | 0.00055 | -0.0348 | CFL | AllSpc | 3050 | 0.416 | 3050 | 0.416 | 1.08 | 1.32 | -0.0114
CFLAllSpcSCGNrsExCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCG | Nrs | Ex | CZ15 | 3.05 | 0.000416 | 0 | 3.51 | 0.000553 | -0.0171 | 3.05 | 0.000416 | 0 | 3.51 | 0.000553 | -0.0171 | CFL | AllSpc | 3050 | 0.416 | 3050 | 0.416 | 1.15 | 1.33 | -0.00561
CFLAllSpcSCENrsExCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCE | Nrs | Ex | CZ15 | 3.05 | 0.000416 | 0 | 3.51 | 0.000553 | -0.0171 | 3.05 | 0.000416 | 0 | 3.51 | 0.000553 | -0.0171 | CFL | AllSpc | 3050 | 0.416 | 3050 | 0.416 | 1.15 | 1.33 | -0.00561
CFLAllSpcSCENrsExCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCE | Nrs | Ex | CZ16 | 3.05 | 0.000416 | 0 | 3.04 | 0.000525 | -0.0506 | 3.05 | 0.000416 | 0 | 3.04 | 0.000525 | -0.0506 | CFL | AllSpc | 3050 | 0.416 | 3050 | 0.416 | 0.997 | 1.26 | -0.0166
CFLAllSpcSCGNrsExCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCG | Nrs | Ex | CZ16 | 3.05 | 0.000416 | 0 | 3.04 | 0.000525 | -0.0506 | 3.05 | 0.000416 | 0 | 3.04 | 0.000525 | -0.0506 | CFL | AllSpc | 3050 | 0.416 | 3050 | 0.416 | 0.997 | 1.26 | -0.0166
CFLAllSpcPGENrsExCZ16 | Com-Iltg-dWatt-CFL_OSspc | PGE | Nrs | Ex | CZ16 | 3.05 | 0.000416 | 0 | 3.04 | 0.000525 | -0.0506 | 3.05 | 0.000416 | 0 | 3.04 | 0.000525 | -0.0506 | CFL | AllSpc | 3050 | 0.416 | 3050 | 0.416 | 0.997 | 1.26 | -0.0166
CFLAllSpcPGENrsExIOU | Com-Iltg-dWatt-CFL_OSspc | PGE | Nrs | Ex | IOU | 3.05 | 0.000416 | 0 | 3.2 | 0.000522 | -0.0405 | 3.05 | 0.000416 | 0 | 3.2 | 0.000522 | -0.0405 | CFL | AllSpc | 3050 | 0.416 | 3050 | 0.416 | 1.05 | 1.25 | -0.0133
CFLAllSpcSCGNrsExIOU | Com-Iltg-dWatt-CFL_OSspc | SCG | Nrs | Ex | IOU | 3.05 | 0.000416 | 0 | 3.32 | 0.000546 | -0.0293 | 3.05 | 0.000416 | 0 | 3.32 | 0.000546 | -0.0293 | CFL | AllSpc | 3050 | 0.416 | 3050 | 0.416 | 1.09 | 1.31 | -0.00961
CFLAllSpcSCENrsExIOU | Com-Iltg-dWatt-CFL_OSspc | SCE | Nrs | Ex | IOU | 3.05 | 0.000416 | 0 | 3.32 | 0.000544 | -0.0294 | 3.05 | 0.000416 | 0 | 3.32 | 0.000544 | -0.0294 | CFL | AllSpc | 3050 | 0.416 | 3050 | 0.416 | 1.09 | 1.31 | -0.00964
CFLAllSpcSDGNrsExIOU | Com-Iltg-dWatt-CFL_OSspc | SDG | Nrs | Ex | IOU | 3.05 | 0.000416 | 0 | 3.29 | 0.000532 | -0.0264 | 3.05 | 0.000416 | 0 | 3.29 | 0.000532 | -0.0264 | CFL | AllSpc | 3050 | 0.416 | 3050 | 0.416 | 1.08 | 1.28 | -0.00866
CFLAllSpcPGENrsNewCZ01 | Com-Iltg-dWatt-CFL_OSspc | PGE | Nrs | New | CZ01 | 3.05 | 0.000417 | 0 | 2.89 | 0.000455 | -0.0671 | 3.05 | 0.000417 | 0 | 2.89 | 0.000455 | -0.0671 | CFL | AllSpc | 3050 | 0.417 | 3050 | 0.417 | 0.948 | 1.09 | -0.022
CFLAllSpcPGENrsNewCZ02 | Com-Iltg-dWatt-CFL_OSspc | PGE | Nrs | New | CZ02 | 3.05 | 0.000417 | 0 | 3.05 | 0.000521 | -0.0473 | 3.05 | 0.000417 | 0 | 3.05 | 0.000521 | -0.0473 | CFL | AllSpc | 3050 | 0.417 | 3050 | 0.417 | 1 | 1.25 | -0.0155
CFLAllSpcPGENrsNewCZ03 | Com-Iltg-dWatt-CFL_OSspc | PGE | Nrs | New | CZ03 | 3.05 | 0.000417 | 0 | 3 | 0.000512 | -0.0494 | 3.05 | 0.000417 | 0 | 3 | 0.000512 | -0.0494 | CFL | AllSpc | 3050 | 0.417 | 3050 | 0.417 | 0.984 | 1.23 | -0.0162
CFLAllSpcPGENrsNewCZ04 | Com-Iltg-dWatt-CFL_OSspc | PGE | Nrs | New | CZ04 | 3.05 | 0.000417 | 0 | 3.13 | 0.000521 | -0.04 | 3.05 | 0.000417 | 0 | 3.13 | 0.000521 | -0.04 | CFL | AllSpc | 3050 | 0.417 | 3050 | 0.417 | 1.03 | 1.25 | -0.0131
CFLAllSpcPGENrsNewCZ05 | Com-Iltg-dWatt-CFL_OSspc | PGE | Nrs | New | CZ05 | 3.05 | 0.000417 | 0 | 3 | 0.000494 | -0.0512 | 3.05 | 0.000417 | 0 | 3 | 0.000494 | -0.0512 | CFL | AllSpc | 3050 | 0.417 | 3050 | 0.417 | 0.984 | 1.18 | -0.0168
CFLAllSpcSCENrsNewCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCE | Nrs | New | CZ05 | 3.05 | 0.000417 | 0 | 2.99 | 0.000508 | -0.0497 | 3.05 | 0.000417 | 0 | 2.99 | 0.000508 | -0.0497 | CFL | AllSpc | 3050 | 0.417 | 3050 | 0.417 | 0.98 | 1.22 | -0.0163
CFLAllSpcSCENrsNewCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCE | Nrs | New | CZ06 | 3.05 | 0.000417 | 0 | 3.18 | 0.000531 | -0.0305 | 3.05 | 0.000417 | 0 | 3.18 | 0.000531 | -0.0305 | CFL | AllSpc | 3050 | 0.417 | 3050 | 0.417 | 1.04 | 1.27 | -0.01
CFLAllSpcSDGNrsNewCZ06 | Com-Iltg-dWatt-CFL_OSspc | SDG | Nrs | New | CZ06 | 3.05 | 0.000417 | 0 | 3.18 | 0.00053 | -0.0308 | 3.05 | 0.000417 | 0 | 3.18 | 0.00053 | -0.0308 | CFL | AllSpc | 3050 | 0.417 | 3050 | 0.417 | 1.04 | 1.27 | -0.0101
CFLAllSpcSDGNrsNewCZ07 | Com-Iltg-dWatt-CFL_OSspc | SDG | Nrs | New | CZ07 | 3.05 | 0.000417 | 0 | 3.15 | 0.00053 | -0.0288 | 3.05 | 0.000417 | 0 | 3.15 | 0.00053 | -0.0288 | CFL | AllSpc | 3050 | 0.417 | 3050 | 0.417 | 1.03 | 1.27 | -0.00944
CFLAllSpcSDGNrsNewCZ08 | Com-Iltg-dWatt-CFL_OSspc | SDG | Nrs | New | CZ08 | 3.05 | 0.000417 | 0 | 3.23 | 0.000532 | -0.0294 | 3.05 | 0.000417 | 0 | 3.23 | 0.000532 | -0.0294 | CFL | AllSpc | 3050 | 0.417 | 3050 | 0.417 | 1.06 | 1.28 | -0.00964
CFLAllSpcSCENrsNewCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCE | Nrs | New | CZ08 | 3.05 | 0.000417 | 0 | 3.23 | 0.000533 | -0.0291 | 3.05 | 0.000417 | 0 | 3.23 | 0.000533 | -0.0291 | CFL | AllSpc | 3050 | 0.417 | 3050 | 0.417 | 1.06 | 1.28 | -0.00954
CFLAllSpcSCENrsNewCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCE | Nrs | New | CZ09 | 3.05 | 0.000417 | 0 | 3.25 | 0.000552 | -0.0293 | 3.05 | 0.000417 | 0 | 3.25 | 0.000552 | -0.0293 | CFL | AllSpc | 3050 | 0.417 | 3050 | 0.417 | 1.07 | 1.32 | -0.00961
CFLAllSpcSDGNrsNewCZ10 | Com-Iltg-dWatt-CFL_OSspc | SDG | Nrs | New | CZ10 | 3.05 | 0.000417 | 0 | 3.26 | 0.000553 | -0.0302 | 3.05 | 0.000417 | 0 | 3.26 | 0.000553 | -0.0302 | CFL | AllSpc | 3050 | 0.417 | 3050 | 0.417 | 1.07 | 1.33 | -0.0099
CFLAllSpcSCENrsNewCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCE | Nrs | New | CZ10 | 3.05 | 0.000417 | 0 | 3.26 | 0.000554 | -0.0299 | 3.05 | 0.000417 | 0 | 3.26 | 0.000554 | -0.0299 | CFL | AllSpc | 3050 | 0.417 | 3050 | 0.417 | 1.07 | 1.33 | -0.0098
CFLAllSpcPGENrsNewCZ11 | Com-Iltg-dWatt-CFL_OSspc | PGE | Nrs | New | CZ11 | 3.05 | 0.000417 | 0 | 3.2 | 0.000528 | -0.0381 | 3.05 | 0.000417 | 0 | 3.2 | 0.000528 | -0.0381 | CFL | AllSpc | 3050 | 0.417 | 3050 | 0.417 | 1.05 | 1.27 | -0.0125
CFLAllSpcPGENrsNewCZ12 | Com-Iltg-dWatt-CFL_OSspc | PGE | Nrs | New | CZ12 | 3.05 | 0.000417 | 0 | 3.16 | 0.00053 | -0.04 | 3.05 | 0.000417 | 0 | 3.16 | 0.00053 | -0.04 | CFL | AllSpc | 3050 | 0.417 | 3050 | 0.417 | 1.04 | 1.27 | -0.0131
CFLAllSpcSCENrsNewCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCE | Nrs | New | CZ13 | 3.05 | 0.000417 | 0 | 3.24 | 0.000548 | -0.0354 | 3.05 | 0.000417 | 0 | 3.24 | 0.000548 | -0.0354 | CFL | AllSpc | 3050 | 0.417 | 3050 | 0.417 | 1.06 | 1.31 | -0.0116
CFLAllSpcPGENrsNewCZ13 | Com-Iltg-dWatt-CFL_OSspc | PGE | Nrs | New | CZ13 | 3.05 | 0.000417 | 0 | 3.21 | 0.000529 | -0.0363 | 3.05 | 0.000417 | 0 | 3.21 | 0.000529 | -0.0363 | CFL | AllSpc | 3050 | 0.417 | 3050 | 0.417 | 1.05 | 1.27 | -0.0119
CFLAllSpcSCENrsNewCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCE | Nrs | New | CZ14 | 3.05 | 0.000417 | 0 | 3.24 | 0.00054 | -0.0369 | 3.05 | 0.000417 | 0 | 3.24 | 0.00054 | -0.0369 | CFL | AllSpc | 3050 | 0.417 | 3050 | 0.417 | 1.06 | 1.29 | -0.0121
CFLAllSpcSDGNrsNewCZ14 | Com-Iltg-dWatt-CFL_OSspc | SDG | Nrs | New | CZ14 | 3.05 | 0.000417 | 0 | 3.24 | 0.000538 | -0.0372 | 3.05 | 0.000417 | 0 | 3.24 | 0.000538 | -0.0372 | CFL | AllSpc | 3050 | 0.417 | 3050 | 0.417 | 1.06 | 1.29 | -0.0122
CFLAllSpcSCENrsNewCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCE | Nrs | New | CZ15 | 3.05 | 0.000417 | 0 | 3.51 | 0.000554 | -0.0143 | 3.05 | 0.000417 | 0 | 3.51 | 0.000554 | -0.0143 | CFL | AllSpc | 3050 | 0.417 | 3050 | 0.417 | 1.15 | 1.33 | -0.00469
CFLAllSpcSDGNrsNewCZ15 | Com-Iltg-dWatt-CFL_OSspc | SDG | Nrs | New | CZ15 | 3.05 | 0.000417 | 0 | 3.5 | 0.000553 | -0.0145 | 3.05 | 0.000417 | 0 | 3.5 | 0.000553 | -0.0145 | CFL | AllSpc | 3050 | 0.417 | 3050 | 0.417 | 1.15 | 1.33 | -0.00475
CFLAllSpcSCENrsNewCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCE | Nrs | New | CZ16 | 3.05 | 0.000417 | 0 | 3 | 0.000521 | -0.0549 | 3.05 | 0.000417 | 0 | 3 | 0.000521 | -0.0549 | CFL | AllSpc | 3050 | 0.417 | 3050 | 0.417 | 0.984 | 1.25 | -0.018
CFLAllSpcPGENrsNewCZ16 | Com-Iltg-dWatt-CFL_OSspc | PGE | Nrs | New | CZ16 | 3.05 | 0.000417 | 0 | 3.01 | 0.000505 | -0.0564 | 3.05 | 0.000417 | 0 | 3.01 | 0.000505 | -0.0564 | CFL | AllSpc | 3050 | 0.417 | 3050 | 0.417 | 0.987 | 1.21 | -0.0185
CFLAllSpcPGENrsNewIOU | Com-Iltg-dWatt-CFL_OSspc | PGE | Nrs | New | IOU | 3.05 | 0.000417 | 0 | 3.21 | 0.000544 | -0.037 | 3.05 | 0.000417 | 0 | 3.21 | 0.000544 | -0.037 | CFL | AllSpc | 3050 | 0.417 | 3050 | 0.417 | 1.05 | 1.3 | -0.0121
CFLAllSpcSCGNrsNewIOU | Com-Iltg-dWatt-CFL_OSspc | SCG | Nrs | New | IOU | 3.05 | 0.000417 | 0 | 3.24 | 0.000539 | -0.0295 | 3.05 | 0.000417 | 0 | 3.24 | 0.000539 | -0.0295 | CFL | AllSpc | 3050 | 0.417 | 3050 | 0.417 | 1.06 | 1.29 | -0.00967
CFLAllSpcSDGNrsNewIOU | Com-Iltg-dWatt-CFL_OSspc | SDG | Nrs | New | IOU | 3.05 | 0.000417 | 0 | 3.17 | 0.000533 | -0.0291 | 3.05 | 0.000417 | 0 | 3.17 | 0.000533 | -0.0291 | CFL | AllSpc | 3050 | 0.417 | 3050 | 0.417 | 1.04 | 1.28 | -0.00954
CFLAllSpcSCENrsNewIOU | Com-Iltg-dWatt-CFL_OSspc | SCE | Nrs | New | IOU | 3.05 | 0.000417 | 0 | 3.24 | 0.00054 | -0.0294 | 3.05 | 0.000417 | 0 | 3.24 | 0.00054 | -0.0294 | CFL | AllSpc | 3050 | 0.417 | 3050 | 0.417 | 1.06 | 1.29 | -0.00964
CFLAllSpcPGEOfLExCZ01 | Com-Iltg-dWatt-CFL_OSspc | PGE | OfL | Ex | CZ01 | 1.76 | 0.000392 | 0 | 1.88 | 0.000497 | -0.0163 | 1.76 | 0.000392 | 0 | 1.88 | 0.000497 | -0.0163 | CFL | AllSpc | 1760 | 0.392 | 1760 | 0.392 | 1.07 | 1.27 | -0.00926
CFLAllSpcPGEOfLExCZ02 | Com-Iltg-dWatt-CFL_OSspc | PGE | OfL | Ex | CZ02 | 1.76 | 0.000392 | 0 | 1.93 | 0.000524 | -0.0122 | 1.76 | 0.000392 | 0 | 1.93 | 0.000524 | -0.0122 | CFL | AllSpc | 1760 | 0.392 | 1760 | 0.392 | 1.1 | 1.34 | -0.00693
CFLAllSpcPGEOfLExCZ03 | Com-Iltg-dWatt-CFL_OSspc | PGE | OfL | Ex | CZ03 | 1.76 | 0.000392 | 0 | 1.93 | 0.00051 | -0.0112 | 1.76 | 0.000392 | 0 | 1.93 | 0.00051 | -0.0112 | CFL | AllSpc | 1760 | 0.392 | 1760 | 0.392 | 1.1 | 1.3 | -0.00636
CFLAllSpcPGEOfLExCZ04 | Com-Iltg-dWatt-CFL_OSspc | PGE | OfL | Ex | CZ04 | 1.76 | 0.000392 | 0 | 1.95 | 0.000513 | -0.0102 | 1.76 | 0.000392 | 0 | 1.95 | 0.000513 | -0.0102 | CFL | AllSpc | 1760 | 0.392 | 1760 | 0.392 | 1.11 | 1.31 | -0.0058
CFLAllSpcSCEOfLExCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCE | OfL | Ex | CZ05 | 1.76 | 0.000392 | 0 | 1.95 | 0.000507 | -0.0122 | 1.76 | 0.000392 | 0 | 1.95 | 0.000507 | -0.0122 | CFL | AllSpc | 1760 | 0.392 | 1760 | 0.392 | 1.11 | 1.29 | -0.00693
CFLAllSpcSCGOfLExCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCG | OfL | Ex | CZ05 | 1.76 | 0.000392 | 0 | 1.95 | 0.000507 | -0.0122 | 1.76 | 0.000392 | 0 | 1.95 | 0.000507 | -0.0122 | CFL | AllSpc | 1760 | 0.392 | 1760 | 0.392 | 1.11 | 1.29 | -0.00693
CFLAllSpcPGEOfLExCZ05 | Com-Iltg-dWatt-CFL_OSspc | PGE | OfL | Ex | CZ05 | 1.76 | 0.000392 | 0 | 1.95 | 0.000507 | -0.0122 | 1.76 | 0.000392 | 0 | 1.95 | 0.000507 | -0.0122 | CFL | AllSpc | 1760 | 0.392 | 1760 | 0.392 | 1.11 | 1.29 | -0.00693
CFLAllSpcSCEOfLExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCE | OfL | Ex | CZ06 | 1.76 | 0.000392 | 0 | 2.02 | 0.0005 | -0.00422 | 1.76 | 0.000392 | 0 | 2.02 | 0.0005 | -0.00422 | CFL | AllSpc | 1760 | 0.392 | 1760 | 0.392 | 1.15 | 1.28 | -0.0024
CFLAllSpcSDGOfLExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SDG | OfL | Ex | CZ06 | 1.76 | 0.000392 | 0 | 2.02 | 0.0005 | -0.00422 | 1.76 | 0.000392 | 0 | 2.02 | 0.0005 | -0.00422 | CFL | AllSpc | 1760 | 0.392 | 1760 | 0.392 | 1.15 | 1.28 | -0.0024
CFLAllSpcSCGOfLExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCG | OfL | Ex | CZ06 | 1.76 | 0.000392 | 0 | 2.02 | 0.0005 | -0.00422 | 1.76 | 0.000392 | 0 | 2.02 | 0.0005 | -0.00422 | CFL | AllSpc | 1760 | 0.392 | 1760 | 0.392 | 1.15 | 1.28 | -0.0024
CFLAllSpcSDGOfLExCZ07 | Com-Iltg-dWatt-CFL_OSspc | SDG | OfL | Ex | CZ07 | 1.76 | 0.000392 | 0 | 2.02 | 0.000493 | -0.00363 | 1.76 | 0.000392 | 0 | 2.02 | 0.000493 | -0.00363 | CFL | AllSpc | 1760 | 0.392 | 1760 | 0.392 | 1.15 | 1.26 | -0.00206
CFLAllSpcSDGOfLExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SDG | OfL | Ex | CZ08 | 1.76 | 0.000392 | 0 | 2.03 | 0.00051 | -0.0041 | 1.76 | 0.000392 | 0 | 2.03 | 0.00051 | -0.0041 | CFL | AllSpc | 1760 | 0.392 | 1760 | 0.392 | 1.15 | 1.3 | -0.00233
CFLAllSpcSCEOfLExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCE | OfL | Ex | CZ08 | 1.76 | 0.000392 | 0 | 2.03 | 0.00051 | -0.0041 | 1.76 | 0.000392 | 0 | 2.03 | 0.00051 | -0.0041 | CFL | AllSpc | 1760 | 0.392 | 1760 | 0.392 | 1.15 | 1.3 | -0.00233
CFLAllSpcSCGOfLExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCG | OfL | Ex | CZ08 | 1.76 | 0.000392 | 0 | 2.03 | 0.00051 | -0.0041 | 1.76 | 0.000392 | 0 | 2.03 | 0.00051 | -0.0041 | CFL | AllSpc | 1760 | 0.392 | 1760 | 0.392 | 1.15 | 1.3 | -0.00233
CFLAllSpcSCEOfLExCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCE | OfL | Ex | CZ09 | 1.76 | 0.000392 | 0 | 2.04 | 0.000532 | -0.00894 | 1.76 | 0.000392 | 0 | 2.04 | 0.000532 | -0.00894 | CFL | AllSpc | 1760 | 0.392 | 1760 | 0.392 | 1.16 | 1.36 | -0.00508
CFLAllSpcSCGOfLExCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCG | OfL | Ex | CZ09 | 1.76 | 0.000392 | 0 | 2.04 | 0.000532 | -0.00894 | 1.76 | 0.000392 | 0 | 2.04 | 0.000532 | -0.00894 | CFL | AllSpc | 1760 | 0.392 | 1760 | 0.392 | 1.16 | 1.36 | -0.00508
CFLAllSpcSDGOfLExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SDG | OfL | Ex | CZ10 | 1.76 | 0.000392 | 0 | 2.02 | 0.000514 | -0.00468 | 1.76 | 0.000392 | 0 | 2.02 | 0.000514 | -0.00468 | CFL | AllSpc | 1760 | 0.392 | 1760 | 0.392 | 1.15 | 1.31 | -0.00266
CFLAllSpcSCEOfLExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCE | OfL | Ex | CZ10 | 1.76 | 0.000392 | 0 | 2.02 | 0.000514 | -0.00468 | 1.76 | 0.000392 | 0 | 2.02 | 0.000514 | -0.00468 | CFL | AllSpc | 1760 | 0.392 | 1760 | 0.392 | 1.15 | 1.31 | -0.00266
CFLAllSpcSCGOfLExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCG | OfL | Ex | CZ10 | 1.76 | 0.000392 | 0 | 2.02 | 0.000514 | -0.00468 | 1.76 | 0.000392 | 0 | 2.02 | 0.000514 | -0.00468 | CFL | AllSpc | 1760 | 0.392 | 1760 | 0.392 | 1.15 | 1.31 | -0.00266
CFLAllSpcPGEOfLExCZ11 | Com-Iltg-dWatt-CFL_OSspc | PGE | OfL | Ex | CZ11 | 1.76 | 0.000392 | 0 | 1.98 | 0.000523 | -0.0117 | 1.76 | 0.000392 | 0 | 1.98 | 0.000523 | -0.0117 | CFL | AllSpc | 1760 | 0.392 | 1760 | 0.392 | 1.13 | 1.33 | -0.00665
CFLAllSpcPGEOfLExCZ12 | Com-Iltg-dWatt-CFL_OSspc | PGE | OfL | Ex | CZ12 | 1.76 | 0.000392 | 0 | 1.95 | 0.000518 | -0.0112 | 1.76 | 0.000392 | 0 | 1.95 | 0.000518 | -0.0112 | CFL | AllSpc | 1760 | 0.392 | 1760 | 0.392 | 1.11 | 1.32 | -0.00636
CFLAllSpcPGEOfLExCZ13 | Com-Iltg-dWatt-CFL_OSspc | PGE | OfL | Ex | CZ13 | 1.76 | 0.000392 | 0 | 2.02 | 0.000518 | -0.0106 | 1.76 | 0.000392 | 0 | 2.02 | 0.000518 | -0.0106 | CFL | AllSpc | 1760 | 0.392 | 1760 | 0.392 | 1.15 | 1.32 | -0.00602
CFLAllSpcSCEOfLExCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCE | OfL | Ex | CZ13 | 1.76 | 0.000392 | 0 | 2.02 | 0.000518 | -0.0106 | 1.76 | 0.000392 | 0 | 2.02 | 0.000518 | -0.0106 | CFL | AllSpc | 1760 | 0.392 | 1760 | 0.392 | 1.15 | 1.32 | -0.00602
CFLAllSpcSCGOfLExCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCG | OfL | Ex | CZ13 | 1.76 | 0.000392 | 0 | 2.02 | 0.000518 | -0.0106 | 1.76 | 0.000392 | 0 | 2.02 | 0.000518 | -0.0106 | CFL | AllSpc | 1760 | 0.392 | 1760 | 0.392 | 1.15 | 1.32 | -0.00602
CFLAllSpcSCEOfLExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCE | OfL | Ex | CZ14 | 1.76 | 0.000392 | 0 | 1.99 | 0.000506 | -0.00646 | 1.76 | 0.000392 | 0 | 1.99 | 0.000506 | -0.00646 | CFL | AllSpc | 1760 | 0.392 | 1760 | 0.392 | 1.13 | 1.29 | -0.00367
CFLAllSpcSCGOfLExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCG | OfL | Ex | CZ14 | 1.76 | 0.000392 | 0 | 1.99 | 0.000506 | -0.00646 | 1.76 | 0.000392 | 0 | 1.99 | 0.000506 | -0.00646 | CFL | AllSpc | 1760 | 0.392 | 1760 | 0.392 | 1.13 | 1.29 | -0.00367
CFLAllSpcSDGOfLExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SDG | OfL | Ex | CZ14 | 1.76 | 0.000392 | 0 | 1.99 | 0.000506 | -0.00646 | 1.76 | 0.000392 | 0 | 1.99 | 0.000506 | -0.00646 | CFL | AllSpc | 1760 | 0.392 | 1760 | 0.392 | 1.13 | 1.29 | -0.00367
CFLAllSpcSDGOfLExCZ15 | Com-Iltg-dWatt-CFL_OSspc | SDG | OfL | Ex | CZ15 | 1.76 | 0.000392 | 0 | 2.15 | 0.000516 | -0.00271 | 1.76 | 0.000392 | 0 | 2.15 | 0.000516 | -0.00271 | CFL | AllSpc | 1760 | 0.392 | 1760 | 0.392 | 1.22 | 1.32 | -0.00154
CFLAllSpcSCGOfLExCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCG | OfL | Ex | CZ15 | 1.76 | 0.000392 | 0 | 2.15 | 0.000516 | -0.00271 | 1.76 | 0.000392 | 0 | 2.15 | 0.000516 | -0.00271 | CFL | AllSpc | 1760 | 0.392 | 1760 | 0.392 | 1.22 | 1.32 | -0.00154
CFLAllSpcSCEOfLExCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCE | OfL | Ex | CZ15 | 1.76 | 0.000392 | 0 | 2.15 | 0.000516 | -0.00271 | 1.76 | 0.000392 | 0 | 2.15 | 0.000516 | -0.00271 | CFL | AllSpc | 1760 | 0.392 | 1760 | 0.392 | 1.22 | 1.32 | -0.00154
CFLAllSpcSCEOfLExCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCE | OfL | Ex | CZ16 | 1.76 | 0.000392 | 0 | 1.86 | 0.000497 | -0.0187 | 1.76 | 0.000392 | 0 | 1.86 | 0.000497 | -0.0187 | CFL | AllSpc | 1760 | 0.392 | 1760 | 0.392 | 1.06 | 1.27 | -0.0106
CFLAllSpcSCGOfLExCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCG | OfL | Ex | CZ16 | 1.76 | 0.000392 | 0 | 1.86 | 0.000497 | -0.0187 | 1.76 | 0.000392 | 0 | 1.86 | 0.000497 | -0.0187 | CFL | AllSpc | 1760 | 0.392 | 1760 | 0.392 | 1.06 | 1.27 | -0.0106
CFLAllSpcPGEOfLExCZ16 | Com-Iltg-dWatt-CFL_OSspc | PGE | OfL | Ex | CZ16 | 1.76 | 0.000392 | 0 | 1.86 | 0.000497 | -0.0187 | 1.76 | 0.000392 | 0 | 1.86 | 0.000497 | -0.0187 | CFL | AllSpc | 1760 | 0.392 | 1760 | 0.392 | 1.06 | 1.27 | -0.0106
CFLAllSpcSDGOfLExIOU | Com-Iltg-dWatt-CFL_OSspc | SDG | OfL | Ex | IOU | 1.76 | 0.000392 | 0 | 2.02 | 0.000497 | -0.00385 | 1.76 | 0.000392 | 0 | 2.02 | 0.000497 | -0.00385 | CFL | AllSpc | 1760 | 0.392 | 1760 | 0.392 | 1.15 | 1.27 | -0.00219
CFLAllSpcSCEOfLExIOU | Com-Iltg-dWatt-CFL_OSspc | SCE | OfL | Ex | IOU | 1.76 | 0.000392 | 0 | 2.03 | 0.000512 | -0.00544 | 1.76 | 0.000392 | 0 | 2.03 | 0.000512 | -0.00544 | CFL | AllSpc | 1760 | 0.392 | 1760 | 0.392 | 1.15 | 1.31 | -0.00309
CFLAllSpcSCGOfLExIOU | Com-Iltg-dWatt-CFL_OSspc | SCG | OfL | Ex | IOU | 1.76 | 0.000392 | 0 | 2.03 | 0.000516 | -0.00618 | 1.76 | 0.000392 | 0 | 2.03 | 0.000516 | -0.00618 | CFL | AllSpc | 1760 | 0.392 | 1760 | 0.392 | 1.15 | 1.32 | -0.00351
CFLAllSpcPGEOfLExIOU | Com-Iltg-dWatt-CFL_OSspc | PGE | OfL | Ex | IOU | 1.76 | 0.000392 | 0 | 1.94 | 0.000513 | -0.0111 | 1.76 | 0.000392 | 0 | 1.94 | 0.000513 | -0.0111 | CFL | AllSpc | 1760 | 0.392 | 1760 | 0.392 | 1.1 | 1.31 | -0.00631
CFLAllSpcPGEOfLNewCZ01 | Com-Iltg-dWatt-CFL_OSspc | PGE | OfL | New | CZ01 | 1.75 | 0.000391 | 0 | 1.86 | 0.000476 | -0.0106 | 1.75 | 0.000391 | 0 | 1.86 | 0.000476 | -0.0106 | CFL | AllSpc | 1750 | 0.391 | 1750 | 0.391 | 1.06 | 1.22 | -0.00606
CFLAllSpcPGEOfLNewCZ02 | Com-Iltg-dWatt-CFL_OSspc | PGE | OfL | New | CZ02 | 1.75 | 0.000391 | 0 | 1.93 | 0.000484 | -0.00704 | 1.75 | 0.000391 | 0 | 1.93 | 0.000484 | -0.00704 | CFL | AllSpc | 1750 | 0.391 | 1750 | 0.391 | 1.1 | 1.24 | -0.00402
CFLAllSpcPGEOfLNewCZ03 | Com-Iltg-dWatt-CFL_OSspc | PGE | OfL | New | CZ03 | 1.75 | 0.000391 | 0 | 1.92 | 0.000483 | -0.00695 | 1.75 | 0.000391 | 0 | 1.92 | 0.000483 | -0.00695 | CFL | AllSpc | 1750 | 0.391 | 1750 | 0.391 | 1.1 | 1.24 | -0.00397
CFLAllSpcPGEOfLNewCZ04 | Com-Iltg-dWatt-CFL_OSspc | PGE | OfL | New | CZ04 | 1.75 | 0.000391 | 0 | 1.94 | 0.000485 | -0.00641 | 1.75 | 0.000391 | 0 | 1.94 | 0.000485 | -0.00641 | CFL | AllSpc | 1750 | 0.391 | 1750 | 0.391 | 1.11 | 1.24 | -0.00366
CFLAllSpcSCEOfLNewCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCE | OfL | New | CZ05 | 1.75 | 0.000391 | 0 | 1.93 | 0.000485 | -0.00569 | 1.75 | 0.000391 | 0 | 1.93 | 0.000485 | -0.00569 | CFL | AllSpc | 1750 | 0.391 | 1750 | 0.391 | 1.1 | 1.24 | -0.00325
CFLAllSpcPGEOfLNewCZ05 | Com-Iltg-dWatt-CFL_OSspc | PGE | OfL | New | CZ05 | 1.75 | 0.000391 | 0 | 1.91 | 0.000473 | -0.00553 | 1.75 | 0.000391 | 0 | 1.91 | 0.000473 | -0.00553 | CFL | AllSpc | 1750 | 0.391 | 1750 | 0.391 | 1.09 | 1.21 | -0.00316
CFLAllSpcSDGOfLNewCZ06 | Com-Iltg-dWatt-CFL_OSspc | SDG | OfL | New | CZ06 | 1.75 | 0.000391 | 0 | 2.01 | 0.000487 | -0.00285 | 1.75 | 0.000391 | 0 | 2.01 | 0.000487 | -0.00285 | CFL | AllSpc | 1750 | 0.391 | 1750 | 0.391 | 1.15 | 1.25 | -0.00163
CFLAllSpcSCEOfLNewCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCE | OfL | New | CZ06 | 1.75 | 0.000391 | 0 | 2.01 | 0.000493 | -0.0038 | 1.75 | 0.000391 | 0 | 2.01 | 0.000493 | -0.0038 | CFL | AllSpc | 1750 | 0.391 | 1750 | 0.391 | 1.15 | 1.26 | -0.00217
CFLAllSpcSDGOfLNewCZ07 | Com-Iltg-dWatt-CFL_OSspc | SDG | OfL | New | CZ07 | 1.75 | 0.000391 | 0 | 2 | 0.000481 | -0.00231 | 1.75 | 0.000391 | 0 | 2 | 0.000481 | -0.00231 | CFL | AllSpc | 1750 | 0.391 | 1750 | 0.391 | 1.14 | 1.23 | -0.00132
CFLAllSpcSDGOfLNewCZ08 | Com-Iltg-dWatt-CFL_OSspc | SDG | OfL | New | CZ08 | 1.75 | 0.000391 | 0 | 2.01 | 0.000493 | -0.00236 | 1.75 | 0.000391 | 0 | 2.01 | 0.000493 | -0.00236 | CFL | AllSpc | 1750 | 0.391 | 1750 | 0.391 | 1.15 | 1.26 | -0.00135
CFLAllSpcSCEOfLNewCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCE | OfL | New | CZ08 | 1.75 | 0.000391 | 0 | 2.02 | 0.000499 | -0.00331 | 1.75 | 0.000391 | 0 | 2.02 | 0.000499 | -0.00331 | CFL | AllSpc | 1750 | 0.391 | 1750 | 0.391 | 1.15 | 1.28 | -0.00189
CFLAllSpcSCEOfLNewCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCE | OfL | New | CZ09 | 1.75 | 0.000391 | 0 | 2.01 | 0.000514 | -0.00462 | 1.75 | 0.000391 | 0 | 2.01 | 0.000514 | -0.00462 | CFL | AllSpc | 1750 | 0.391 | 1750 | 0.391 | 1.15 | 1.31 | -0.00264
CFLAllSpcSDGOfLNewCZ10 | Com-Iltg-dWatt-CFL_OSspc | SDG | OfL | New | CZ10 | 1.75 | 0.000391 | 0 | 2.02 | 0.000509 | -0.00291 | 1.75 | 0.000391 | 0 | 2.02 | 0.000509 | -0.00291 | CFL | AllSpc | 1750 | 0.391 | 1750 | 0.391 | 1.15 | 1.3 | -0.00166
CFLAllSpcSCEOfLNewCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCE | OfL | New | CZ10 | 1.75 | 0.000391 | 0 | 2.03 | 0.000516 | -0.00401 | 1.75 | 0.000391 | 0 | 2.03 | 0.000516 | -0.00401 | CFL | AllSpc | 1750 | 0.391 | 1750 | 0.391 | 1.16 | 1.32 | -0.00229
CFLAllSpcPGEOfLNewCZ11 | Com-Iltg-dWatt-CFL_OSspc | PGE | OfL | New | CZ11 | 1.75 | 0.000391 | 0 | 1.96 | 0.000489 | -0.00605 | 1.75 | 0.000391 | 0 | 1.96 | 0.000489 | -0.00605 | CFL | AllSpc | 1750 | 0.391 | 1750 | 0.391 | 1.12 | 1.25 | -0.00346
CFLAllSpcPGEOfLNewCZ12 | Com-Iltg-dWatt-CFL_OSspc | PGE | OfL | New | CZ12 | 1.75 | 0.000391 | 0 | 1.95 | 0.000487 | -0.00681 | 1.75 | 0.000391 | 0 | 1.95 | 0.000487 | -0.00681 | CFL | AllSpc | 1750 | 0.391 | 1750 | 0.391 | 1.11 | 1.25 | -0.00389
CFLAllSpcPGEOfLNewCZ13 | Com-Iltg-dWatt-CFL_OSspc | PGE | OfL | New | CZ13 | 1.75 | 0.000391 | 0 | 1.96 | 0.000488 | -0.00593 | 1.75 | 0.000391 | 0 | 1.96 | 0.000488 | -0.00593 | CFL | AllSpc | 1750 | 0.391 | 1750 | 0.391 | 1.12 | 1.25 | -0.00339
CFLAllSpcSCEOfLNewCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCE | OfL | New | CZ13 | 1.75 | 0.000391 | 0 | 1.99 | 0.000502 | -0.00597 | 1.75 | 0.000391 | 0 | 1.99 | 0.000502 | -0.00597 | CFL | AllSpc | 1750 | 0.391 | 1750 | 0.391 | 1.14 | 1.28 | -0.00341
CFLAllSpcSDGOfLNewCZ14 | Com-Iltg-dWatt-CFL_OSspc | SDG | OfL | New | CZ14 | 1.75 | 0.000391 | 0 | 1.99 | 0.000518 | -0.00457 | 1.75 | 0.000391 | 0 | 1.99 | 0.000518 | -0.00457 | CFL | AllSpc | 1750 | 0.391 | 1750 | 0.391 | 1.14 | 1.32 | -0.00261
CFLAllSpcSCEOfLNewCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCE | OfL | New | CZ14 | 1.75 | 0.000391 | 0 | 2 | 0.000522 | -0.00527 | 1.75 | 0.000391 | 0 | 2 | 0.000522 | -0.00527 | CFL | AllSpc | 1750 | 0.391 | 1750 | 0.391 | 1.14 | 1.34 | -0.00301
CFLAllSpcSCEOfLNewCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCE | OfL | New | CZ15 | 1.75 | 0.000391 | 0 | 2.11 | 0.000511 | -0.00194 | 1.75 | 0.000391 | 0 | 2.11 | 0.000511 | -0.00194 | CFL | AllSpc | 1750 | 0.391 | 1750 | 0.391 | 1.21 | 1.31 | -0.00111
CFLAllSpcSDGOfLNewCZ15 | Com-Iltg-dWatt-CFL_OSspc | SDG | OfL | New | CZ15 | 1.75 | 0.000391 | 0 | 2.1 | 0.000506 | -0.00137 | 1.75 | 0.000391 | 0 | 2.1 | 0.000506 | -0.00137 | CFL | AllSpc | 1750 | 0.391 | 1750 | 0.391 | 1.2 | 1.29 | -0.000783
CFLAllSpcSCEOfLNewCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCE | OfL | New | CZ16 | 1.75 | 0.000391 | 0 | 1.88 | 0.00049 | -0.0146 | 1.75 | 0.000391 | 0 | 1.88 | 0.00049 | -0.0146 | CFL | AllSpc | 1750 | 0.391 | 1750 | 0.391 | 1.07 | 1.25 | -0.00834
CFLAllSpcPGEOfLNewCZ16 | Com-Iltg-dWatt-CFL_OSspc | PGE | OfL | New | CZ16 | 1.75 | 0.000391 | 0 | 1.87 | 0.000479 | -0.0148 | 1.75 | 0.000391 | 0 | 1.87 | 0.000479 | -0.0148 | CFL | AllSpc | 1750 | 0.391 | 1750 | 0.391 | 1.07 | 1.23 | -0.00846
CFLAllSpcPGEOfLNewIOU | Com-Iltg-dWatt-CFL_OSspc | PGE | OfL | New | IOU | 1.75 | 0.000391 | 0 | 1.98 | 0.000499 | -0.00611 | 1.75 | 0.000391 | 0 | 1.98 | 0.000499 | -0.00611 | CFL | AllSpc | 1750 | 0.391 | 1750 | 0.391 | 1.13 | 1.28 | -0.00349
CFLAllSpcSDGOfLNewIOU | Com-Iltg-dWatt-CFL_OSspc | SDG | OfL | New | IOU | 1.75 | 0.000391 | 0 | 2 | 0.000486 | -0.00244 | 1.75 | 0.000391 | 0 | 2 | 0.000486 | -0.00244 | CFL | AllSpc | 1750 | 0.391 | 1750 | 0.391 | 1.14 | 1.24 | -0.00139
CFLAllSpcSCGOfLNewIOU | Com-Iltg-dWatt-CFL_OSspc | SCG | OfL | New | IOU | 1.75 | 0.000391 | 0 | 2.02 | 0.000496 | -0.00264 | 1.75 | 0.000391 | 0 | 2.02 | 0.000496 | -0.00264 | CFL | AllSpc | 1750 | 0.391 | 1750 | 0.391 | 1.15 | 1.27 | -0.00151
CFLAllSpcSCEOfLNewIOU | Com-Iltg-dWatt-CFL_OSspc | SCE | OfL | New | IOU | 1.75 | 0.000391 | 0 | 2.02 | 0.000498 | -0.00267 | 1.75 | 0.000391 | 0 | 2.02 | 0.000498 | -0.00267 | CFL | AllSpc | 1750 | 0.391 | 1750 | 0.391 | 1.15 | 1.27 | -0.00153
CFLAllSpcPGEOfSExCZ01 | Com-Iltg-dWatt-CFL_OSspc | PGE | OfS | Ex | CZ01 | 1.24 | 0.000338 | 0 | 1.24 | 0.000401 | -0.00774 | 1.24 | 0.000338 | 0 | 1.24 | 0.000401 | -0.00774 | CFL | AllSpc | 1240 | 0.338 | 1240 | 0.338 | 1 | 1.19 | -0.00624
CFLAllSpcPGEOfSExCZ02 | Com-Iltg-dWatt-CFL_OSspc | PGE | OfS | Ex | CZ02 | 1.24 | 0.000338 | 0 | 1.3 | 0.000413 | -0.00502 | 1.24 | 0.000338 | 0 | 1.3 | 0.000413 | -0.00502 | CFL | AllSpc | 1240 | 0.338 | 1240 | 0.338 | 1.05 | 1.22 | -0.00405
CFLAllSpcPGEOfSExCZ03 | Com-Iltg-dWatt-CFL_OSspc | PGE | OfS | Ex | CZ03 | 1.24 | 0.000338 | 0 | 1.3 | 0.000412 | -0.00428 | 1.24 | 0.000338 | 0 | 1.3 | 0.000412 | -0.00428 | CFL | AllSpc | 1240 | 0.338 | 1240 | 0.338 | 1.05 | 1.22 | -0.00345
CFLAllSpcPGEOfSExCZ04 | Com-Iltg-dWatt-CFL_OSspc | PGE | OfS | Ex | CZ04 | 1.24 | 0.000338 | 0 | 1.32 | 0.000414 | -0.00343 | 1.24 | 0.000338 | 0 | 1.32 | 0.000414 | -0.00343 | CFL | AllSpc | 1240 | 0.338 | 1240 | 0.338 | 1.06 | 1.22 | -0.00277
CFLAllSpcSCGOfSExCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCG | OfS | Ex | CZ05 | 1.24 | 0.000338 | 0 | 1.35 | 0.000425 | -0.00388 | 1.24 | 0.000338 | 0 | 1.35 | 0.000425 | -0.00388 | CFL | AllSpc | 1240 | 0.338 | 1240 | 0.338 | 1.09 | 1.26 | -0.00313
CFLAllSpcPGEOfSExCZ05 | Com-Iltg-dWatt-CFL_OSspc | PGE | OfS | Ex | CZ05 | 1.24 | 0.000338 | 0 | 1.35 | 0.000425 | -0.00388 | 1.24 | 0.000338 | 0 | 1.35 | 0.000425 | -0.00388 | CFL | AllSpc | 1240 | 0.338 | 1240 | 0.338 | 1.09 | 1.26 | -0.00313
CFLAllSpcSCEOfSExCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCE | OfS | Ex | CZ05 | 1.24 | 0.000338 | 0 | 1.35 | 0.000425 | -0.00388 | 1.24 | 0.000338 | 0 | 1.35 | 0.000425 | -0.00388 | CFL | AllSpc | 1240 | 0.338 | 1240 | 0.338 | 1.09 | 1.26 | -0.00313
CFLAllSpcSCGOfSExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCG | OfS | Ex | CZ06 | 1.24 | 0.000338 | 0 | 1.42 | 0.000426 | -0.000999 | 1.24 | 0.000338 | 0 | 1.42 | 0.000426 | -0.000999 | CFL | AllSpc | 1240 | 0.338 | 1240 | 0.338 | 1.15 | 1.26 | -0.000806
CFLAllSpcSDGOfSExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SDG | OfS | Ex | CZ06 | 1.24 | 0.000338 | 0 | 1.42 | 0.000426 | -0.000999 | 1.24 | 0.000338 | 0 | 1.42 | 0.000426 | -0.000999 | CFL | AllSpc | 1240 | 0.338 | 1240 | 0.338 | 1.15 | 1.26 | -0.000806
CFLAllSpcSCEOfSExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCE | OfS | Ex | CZ06 | 1.24 | 0.000338 | 0 | 1.42 | 0.000426 | -0.000999 | 1.24 | 0.000338 | 0 | 1.42 | 0.000426 | -0.000999 | CFL | AllSpc | 1240 | 0.338 | 1240 | 0.338 | 1.15 | 1.26 | -0.000806
CFLAllSpcSDGOfSExCZ07 | Com-Iltg-dWatt-CFL_OSspc | SDG | OfS | Ex | CZ07 | 1.24 | 0.000338 | 0 | 1.42 | 0.000421 | -0.000272 | 1.24 | 0.000338 | 0 | 1.42 | 0.000421 | -0.000272 | CFL | AllSpc | 1240 | 0.338 | 1240 | 0.338 | 1.15 | 1.25 | -0.000219
CFLAllSpcSDGOfSExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SDG | OfS | Ex | CZ08 | 1.24 | 0.000338 | 0 | 1.43 | 0.000428 | -0.000846 | 1.24 | 0.000338 | 0 | 1.43 | 0.000428 | -0.000846 | CFL | AllSpc | 1240 | 0.338 | 1240 | 0.338 | 1.15 | 1.27 | -0.000682
CFLAllSpcSCEOfSExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCE | OfS | Ex | CZ08 | 1.24 | 0.000338 | 0 | 1.43 | 0.000428 | -0.000846 | 1.24 | 0.000338 | 0 | 1.43 | 0.000428 | -0.000846 | CFL | AllSpc | 1240 | 0.338 | 1240 | 0.338 | 1.15 | 1.27 | -0.000682
CFLAllSpcSCGOfSExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCG | OfS | Ex | CZ08 | 1.24 | 0.000338 | 0 | 1.43 | 0.000428 | -0.000846 | 1.24 | 0.000338 | 0 | 1.43 | 0.000428 | -0.000846 | CFL | AllSpc | 1240 | 0.338 | 1240 | 0.338 | 1.15 | 1.27 | -0.000682
CFLAllSpcSCEOfSExCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCE | OfS | Ex | CZ09 | 1.24 | 0.000338 | 0 | 1.41 | 0.000437 | -0.00211 | 1.24 | 0.000338 | 0 | 1.41 | 0.000437 | -0.00211 | CFL | AllSpc | 1240 | 0.338 | 1240 | 0.338 | 1.14 | 1.29 | -0.0017
CFLAllSpcSCGOfSExCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCG | OfS | Ex | CZ09 | 1.24 | 0.000338 | 0 | 1.41 | 0.000437 | -0.00211 | 1.24 | 0.000338 | 0 | 1.41 | 0.000437 | -0.00211 | CFL | AllSpc | 1240 | 0.338 | 1240 | 0.338 | 1.14 | 1.29 | -0.0017
CFLAllSpcSDGOfSExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SDG | OfS | Ex | CZ10 | 1.24 | 0.000338 | 0 | 1.42 | 0.00043 | -0.00129 | 1.24 | 0.000338 | 0 | 1.42 | 0.00043 | -0.00129 | CFL | AllSpc | 1240 | 0.338 | 1240 | 0.338 | 1.15 | 1.27 | -0.00104
CFLAllSpcSCEOfSExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCE | OfS | Ex | CZ10 | 1.24 | 0.000338 | 0 | 1.42 | 0.00043 | -0.00129 | 1.24 | 0.000338 | 0 | 1.42 | 0.00043 | -0.00129 | CFL | AllSpc | 1240 | 0.338 | 1240 | 0.338 | 1.15 | 1.27 | -0.00104
CFLAllSpcSCGOfSExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCG | OfS | Ex | CZ10 | 1.24 | 0.000338 | 0 | 1.42 | 0.00043 | -0.00129 | 1.24 | 0.000338 | 0 | 1.42 | 0.00043 | -0.00129 | CFL | AllSpc | 1240 | 0.338 | 1240 | 0.338 | 1.15 | 1.27 | -0.00104
CFLAllSpcPGEOfSExCZ11 | Com-Iltg-dWatt-CFL_OSspc | PGE | OfS | Ex | CZ11 | 1.24 | 0.000338 | 0 | 1.32 | 0.000413 | -0.00527 | 1.24 | 0.000338 | 0 | 1.32 | 0.000413 | -0.00527 | CFL | AllSpc | 1240 | 0.338 | 1240 | 0.338 | 1.06 | 1.22 | -0.00425
CFLAllSpcPGEOfSExCZ12 | Com-Iltg-dWatt-CFL_OSspc | PGE | OfS | Ex | CZ12 | 1.24 | 0.000338 | 0 | 1.31 | 0.000414 | -0.00512 | 1.24 | 0.000338 | 0 | 1.31 | 0.000414 | -0.00512 | CFL | AllSpc | 1240 | 0.338 | 1240 | 0.338 | 1.06 | 1.22 | -0.00413
CFLAllSpcSCEOfSExCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCE | OfS | Ex | CZ13 | 1.24 | 0.000338 | 0 | 1.37 | 0.000431 | -0.00465 | 1.24 | 0.000338 | 0 | 1.37 | 0.000431 | -0.00465 | CFL | AllSpc | 1240 | 0.338 | 1240 | 0.338 | 1.1 | 1.28 | -0.00375
CFLAllSpcPGEOfSExCZ13 | Com-Iltg-dWatt-CFL_OSspc | PGE | OfS | Ex | CZ13 | 1.24 | 0.000338 | 0 | 1.37 | 0.000431 | -0.00465 | 1.24 | 0.000338 | 0 | 1.37 | 0.000431 | -0.00465 | CFL | AllSpc | 1240 | 0.338 | 1240 | 0.338 | 1.1 | 1.28 | -0.00375
CFLAllSpcSCGOfSExCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCG | OfS | Ex | CZ13 | 1.24 | 0.000338 | 0 | 1.37 | 0.000431 | -0.00465 | 1.24 | 0.000338 | 0 | 1.37 | 0.000431 | -0.00465 | CFL | AllSpc | 1240 | 0.338 | 1240 | 0.338 | 1.1 | 1.28 | -0.00375
CFLAllSpcSCEOfSExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCE | OfS | Ex | CZ14 | 1.24 | 0.000338 | 0 | 1.39 | 0.000435 | -0.00314 | 1.24 | 0.000338 | 0 | 1.39 | 0.000435 | -0.00314 | CFL | AllSpc | 1240 | 0.338 | 1240 | 0.338 | 1.12 | 1.29 | -0.00253
CFLAllSpcSDGOfSExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SDG | OfS | Ex | CZ14 | 1.24 | 0.000338 | 0 | 1.39 | 0.000435 | -0.00314 | 1.24 | 0.000338 | 0 | 1.39 | 0.000435 | -0.00314 | CFL | AllSpc | 1240 | 0.338 | 1240 | 0.338 | 1.12 | 1.29 | -0.00253
CFLAllSpcSCGOfSExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCG | OfS | Ex | CZ14 | 1.24 | 0.000338 | 0 | 1.39 | 0.000435 | -0.00314 | 1.24 | 0.000338 | 0 | 1.39 | 0.000435 | -0.00314 | CFL | AllSpc | 1240 | 0.338 | 1240 | 0.338 | 1.12 | 1.29 | -0.00253
CFLAllSpcSCGOfSExCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCG | OfS | Ex | CZ15 | 1.24 | 0.000338 | 0 | 1.52 | 0.000426 | -0.000272 | 1.24 | 0.000338 | 0 | 1.52 | 0.000426 | -0.000272 | CFL | AllSpc | 1240 | 0.338 | 1240 | 0.338 | 1.23 | 1.26 | -0.000219
CFLAllSpcSCEOfSExCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCE | OfS | Ex | CZ15 | 1.24 | 0.000338 | 0 | 1.52 | 0.000426 | -0.000272 | 1.24 | 0.000338 | 0 | 1.52 | 0.000426 | -0.000272 | CFL | AllSpc | 1240 | 0.338 | 1240 | 0.338 | 1.23 | 1.26 | -0.000219
CFLAllSpcSDGOfSExCZ15 | Com-Iltg-dWatt-CFL_OSspc | SDG | OfS | Ex | CZ15 | 1.24 | 0.000338 | 0 | 1.52 | 0.000426 | -0.000272 | 1.24 | 0.000338 | 0 | 1.52 | 0.000426 | -0.000272 | CFL | AllSpc | 1240 | 0.338 | 1240 | 0.338 | 1.23 | 1.26 | -0.000219
CFLAllSpcSCGOfSExCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCG | OfS | Ex | CZ16 | 1.24 | 0.000338 | 0 | 1.24 | 0.000423 | -0.00879 | 1.24 | 0.000338 | 0 | 1.24 | 0.000423 | -0.00879 | CFL | AllSpc | 1240 | 0.338 | 1240 | 0.338 | 1 | 1.25 | -0.00709
CFLAllSpcSCEOfSExCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCE | OfS | Ex | CZ16 | 1.24 | 0.000338 | 0 | 1.24 | 0.000423 | -0.00879 | 1.24 | 0.000338 | 0 | 1.24 | 0.000423 | -0.00879 | CFL | AllSpc | 1240 | 0.338 | 1240 | 0.338 | 1 | 1.25 | -0.00709
CFLAllSpcPGEOfSExCZ16 | Com-Iltg-dWatt-CFL_OSspc | PGE | OfS | Ex | CZ16 | 1.24 | 0.000338 | 0 | 1.24 | 0.000423 | -0.00879 | 1.24 | 0.000338 | 0 | 1.24 | 0.000423 | -0.00879 | CFL | AllSpc | 1240 | 0.338 | 1240 | 0.338 | 1 | 1.25 | -0.00709
CFLAllSpcSDGOfSExIOU | Com-Iltg-dWatt-CFL_OSspc | SDG | OfS | Ex | IOU | 1.24 | 0.000338 | 0 | 1.42 | 0.000423 | -0.000488 | 1.24 | 0.000338 | 0 | 1.42 | 0.000423 | -0.000488 | CFL | AllSpc | 1240 | 0.338 | 1240 | 0.338 | 1.15 | 1.25 | -0.000394
CFLAllSpcPGEOfSExIOU | Com-Iltg-dWatt-CFL_OSspc | PGE | OfS | Ex | IOU | 1.24 | 0.000338 | 0 | 1.32 | 0.000417 | -0.00457 | 1.24 | 0.000338 | 0 | 1.32 | 0.000417 | -0.00457 | CFL | AllSpc | 1240 | 0.338 | 1240 | 0.338 | 1.06 | 1.23 | -0.00369
CFLAllSpcSCGOfSExIOU | Com-Iltg-dWatt-CFL_OSspc | SCG | OfS | Ex | IOU | 1.24 | 0.000338 | 0 | 1.42 | 0.000431 | -0.00157 | 1.24 | 0.000338 | 0 | 1.42 | 0.000431 | -0.00157 | CFL | AllSpc | 1240 | 0.338 | 1240 | 0.338 | 1.15 | 1.28 | -0.00127
CFLAllSpcSCEOfSExIOU | Com-Iltg-dWatt-CFL_OSspc | SCE | OfS | Ex | IOU | 1.24 | 0.000338 | 0 | 1.42 | 0.000429 | -0.00151 | 1.24 | 0.000338 | 0 | 1.42 | 0.000429 | -0.00151 | CFL | AllSpc | 1240 | 0.338 | 1240 | 0.338 | 1.15 | 1.27 | -0.00122
CFLAllSpcPGEOfSNewCZ01 | Com-Iltg-dWatt-CFL_OSspc | PGE | OfS | New | CZ01 | 1.25 | 0.000339 | 0 | 1.23 | 0.000399 | -0.00723 | 1.25 | 0.000339 | 0 | 1.23 | 0.000399 | -0.00723 | CFL | AllSpc | 1250 | 0.339 | 1250 | 0.339 | 0.984 | 1.18 | -0.00578
CFLAllSpcPGEOfSNewCZ02 | Com-Iltg-dWatt-CFL_OSspc | PGE | OfS | New | CZ02 | 1.25 | 0.000339 | 0 | 1.31 | 0.000422 | -0.00389 | 1.25 | 0.000339 | 0 | 1.31 | 0.000422 | -0.00389 | CFL | AllSpc | 1250 | 0.339 | 1250 | 0.339 | 1.05 | 1.24 | -0.00311
CFLAllSpcPGEOfSNewCZ03 | Com-Iltg-dWatt-CFL_OSspc | PGE | OfS | New | CZ03 | 1.25 | 0.000339 | 0 | 1.29 | 0.000412 | -0.00424 | 1.25 | 0.000339 | 0 | 1.29 | 0.000412 | -0.00424 | CFL | AllSpc | 1250 | 0.339 | 1250 | 0.339 | 1.03 | 1.22 | -0.00339
CFLAllSpcPGEOfSNewCZ04 | Com-Iltg-dWatt-CFL_OSspc | PGE | OfS | New | CZ04 | 1.25 | 0.000339 | 0 | 1.32 | 0.00042 | -0.0031 | 1.25 | 0.000339 | 0 | 1.32 | 0.00042 | -0.0031 | CFL | AllSpc | 1250 | 0.339 | 1250 | 0.339 | 1.06 | 1.24 | -0.00248
CFLAllSpcSCEOfSNewCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCE | OfS | New | CZ05 | 1.25 | 0.000339 | 0 | 1.31 | 0.000419 | -0.00354 | 1.25 | 0.000339 | 0 | 1.31 | 0.000419 | -0.00354 | CFL | AllSpc | 1250 | 0.339 | 1250 | 0.339 | 1.05 | 1.24 | -0.00283
CFLAllSpcPGEOfSNewCZ05 | Com-Iltg-dWatt-CFL_OSspc | PGE | OfS | New | CZ05 | 1.25 | 0.000339 | 0 | 1.29 | 0.000405 | -0.00336 | 1.25 | 0.000339 | 0 | 1.29 | 0.000405 | -0.00336 | CFL | AllSpc | 1250 | 0.339 | 1250 | 0.339 | 1.03 | 1.19 | -0.00269
CFLAllSpcSDGOfSNewCZ06 | Com-Iltg-dWatt-CFL_OSspc | SDG | OfS | New | CZ06 | 1.25 | 0.000339 | 0 | 1.37 | 0.00042 | -0.00111 | 1.25 | 0.000339 | 0 | 1.37 | 0.00042 | -0.00111 | CFL | AllSpc | 1250 | 0.339 | 1250 | 0.339 | 1.1 | 1.24 | -0.000888
CFLAllSpcSCEOfSNewCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCE | OfS | New | CZ06 | 1.25 | 0.000339 | 0 | 1.38 | 0.000425 | -0.00143 | 1.25 | 0.000339 | 0 | 1.38 | 0.000425 | -0.00143 | CFL | AllSpc | 1250 | 0.339 | 1250 | 0.339 | 1.1 | 1.25 | -0.00114
CFLAllSpcSDGOfSNewCZ07 | Com-Iltg-dWatt-CFL_OSspc | SDG | OfS | New | CZ07 | 1.25 | 0.000339 | 0 | 1.37 | 0.000415 | -0.000259 | 1.25 | 0.000339 | 0 | 1.37 | 0.000415 | -0.000259 | CFL | AllSpc | 1250 | 0.339 | 1250 | 0.339 | 1.1 | 1.22 | -0.000207
CFLAllSpcSDGOfSNewCZ08 | Com-Iltg-dWatt-CFL_OSspc | SDG | OfS | New | CZ08 | 1.25 | 0.000339 | 0 | 1.38 | 0.000425 | -0.000935 | 1.25 | 0.000339 | 0 | 1.38 | 0.000425 | -0.000935 | CFL | AllSpc | 1250 | 0.339 | 1250 | 0.339 | 1.1 | 1.25 | -0.000748
CFLAllSpcSCEOfSNewCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCE | OfS | New | CZ08 | 1.25 | 0.000339 | 0 | 1.39 | 0.000431 | -0.00126 | 1.25 | 0.000339 | 0 | 1.39 | 0.000431 | -0.00126 | CFL | AllSpc | 1250 | 0.339 | 1250 | 0.339 | 1.11 | 1.27 | -0.00101
CFLAllSpcSCEOfSNewCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCE | OfS | New | CZ09 | 1.25 | 0.000339 | 0 | 1.39 | 0.000441 | -0.00143 | 1.25 | 0.000339 | 0 | 1.39 | 0.000441 | -0.00143 | CFL | AllSpc | 1250 | 0.339 | 1250 | 0.339 | 1.11 | 1.3 | -0.00114
CFLAllSpcSDGOfSNewCZ10 | Com-Iltg-dWatt-CFL_OSspc | SDG | OfS | New | CZ10 | 1.25 | 0.000339 | 0 | 1.39 | 0.00044 | -0.000739 | 1.25 | 0.000339 | 0 | 1.39 | 0.00044 | -0.000739 | CFL | AllSpc | 1250 | 0.339 | 1250 | 0.339 | 1.11 | 1.3 | -0.000591
CFLAllSpcSCEOfSNewCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCE | OfS | New | CZ10 | 1.25 | 0.000339 | 0 | 1.4 | 0.000447 | -0.001 | 1.25 | 0.000339 | 0 | 1.4 | 0.000447 | -0.001 | CFL | AllSpc | 1250 | 0.339 | 1250 | 0.339 | 1.12 | 1.32 | -0.0008
CFLAllSpcPGEOfSNewCZ11 | Com-Iltg-dWatt-CFL_OSspc | PGE | OfS | New | CZ11 | 1.25 | 0.000339 | 0 | 1.33 | 0.000425 | -0.0043 | 1.25 | 0.000339 | 0 | 1.33 | 0.000425 | -0.0043 | CFL | AllSpc | 1250 | 0.339 | 1250 | 0.339 | 1.06 | 1.25 | -0.00344
CFLAllSpcPGEOfSNewCZ12 | Com-Iltg-dWatt-CFL_OSspc | PGE | OfS | New | CZ12 | 1.25 | 0.000339 | 0 | 1.32 | 0.000423 | -0.00416 | 1.25 | 0.000339 | 0 | 1.32 | 0.000423 | -0.00416 | CFL | AllSpc | 1250 | 0.339 | 1250 | 0.339 | 1.06 | 1.25 | -0.00333
CFLAllSpcSCEOfSNewCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCE | OfS | New | CZ13 | 1.25 | 0.000339 | 0 | 1.36 | 0.000439 | -0.00375 | 1.25 | 0.000339 | 0 | 1.36 | 0.000439 | -0.00375 | CFL | AllSpc | 1250 | 0.339 | 1250 | 0.339 | 1.09 | 1.29 | -0.003
CFLAllSpcPGEOfSNewCZ13 | Com-Iltg-dWatt-CFL_OSspc | PGE | OfS | New | CZ13 | 1.25 | 0.000339 | 0 | 1.33 | 0.000421 | -0.00396 | 1.25 | 0.000339 | 0 | 1.33 | 0.000421 | -0.00396 | CFL | AllSpc | 1250 | 0.339 | 1250 | 0.339 | 1.06 | 1.24 | -0.00317
CFLAllSpcSDGOfSNewCZ14 | Com-Iltg-dWatt-CFL_OSspc | SDG | OfS | New | CZ14 | 1.25 | 0.000339 | 0 | 1.36 | 0.00044 | -0.00282 | 1.25 | 0.000339 | 0 | 1.36 | 0.00044 | -0.00282 | CFL | AllSpc | 1250 | 0.339 | 1250 | 0.339 | 1.09 | 1.3 | -0.00226
CFLAllSpcSCEOfSNewCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCE | OfS | New | CZ14 | 1.25 | 0.000339 | 0 | 1.37 | 0.000446 | -0.00313 | 1.25 | 0.000339 | 0 | 1.37 | 0.000446 | -0.00313 | CFL | AllSpc | 1250 | 0.339 | 1250 | 0.339 | 1.1 | 1.32 | -0.0025
CFLAllSpcSCEOfSNewCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCE | OfS | New | CZ15 | 1.25 | 0.000339 | 0 | 1.47 | 0.000452 | -9.35e-05 | 1.25 | 0.000339 | 0 | 1.47 | 0.000452 | -9.35e-05 | CFL | AllSpc | 1250 | 0.339 | 1250 | 0.339 | 1.18 | 1.33 | -7.48e-05
CFLAllSpcSDGOfSNewCZ15 | Com-Iltg-dWatt-CFL_OSspc | SDG | OfS | New | CZ15 | 1.25 | 0.000339 | 0 | 1.45 | 0.000445 | 0 | 1.25 | 0.000339 | 0 | 1.45 | 0.000445 | 0 | CFL | AllSpc | 1250 | 0.339 | 1250 | 0.339 | 1.16 | 1.31 | 0
CFLAllSpcPGEOfSNewCZ16 | Com-Iltg-dWatt-CFL_OSspc | PGE | OfS | New | CZ16 | 1.25 | 0.000339 | 0 | 1.24 | 0.00041 | -0.00899 | 1.25 | 0.000339 | 0 | 1.24 | 0.00041 | -0.00899 | CFL | AllSpc | 1250 | 0.339 | 1250 | 0.339 | 0.992 | 1.21 | -0.00719
CFLAllSpcSCEOfSNewCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCE | OfS | New | CZ16 | 1.25 | 0.000339 | 0 | 1.25 | 0.000425 | -0.00835 | 1.25 | 0.000339 | 0 | 1.25 | 0.000425 | -0.00835 | CFL | AllSpc | 1250 | 0.339 | 1250 | 0.339 | 1 | 1.25 | -0.00668
CFLAllSpcPGEOfSNewIOU | Com-Iltg-dWatt-CFL_OSspc | PGE | OfS | New | IOU | 1.25 | 0.000339 | 0 | 1.35 | 0.000437 | -0.00388 | 1.25 | 0.000339 | 0 | 1.35 | 0.000437 | -0.00388 | CFL | AllSpc | 1250 | 0.339 | 1250 | 0.339 | 1.08 | 1.29 | -0.0031
CFLAllSpcSDGOfSNewIOU | Com-Iltg-dWatt-CFL_OSspc | SDG | OfS | New | IOU | 1.25 | 0.000339 | 0 | 1.37 | 0.00042 | -0.000385 | 1.25 | 0.000339 | 0 | 1.37 | 0.00042 | -0.000385 | CFL | AllSpc | 1250 | 0.339 | 1250 | 0.339 | 1.1 | 1.24 | -0.000308
CFLAllSpcSCEOfSNewIOU | Com-Iltg-dWatt-CFL_OSspc | SCE | OfS | New | IOU | 1.25 | 0.000339 | 0 | 1.39 | 0.000432 | -0.000902 | 1.25 | 0.000339 | 0 | 1.39 | 0.000432 | -0.000902 | CFL | AllSpc | 1250 | 0.339 | 1250 | 0.339 | 1.11 | 1.27 | -0.000722
CFLAllSpcSCGOfSNewIOU | Com-Iltg-dWatt-CFL_OSspc | SCG | OfS | New | IOU | 1.25 | 0.000339 | 0 | 1.39 | 0.000431 | -0.000907 | 1.25 | 0.000339 | 0 | 1.39 | 0.000431 | -0.000907 | CFL | AllSpc | 1250 | 0.339 | 1250 | 0.339 | 1.11 | 1.27 | -0.000726
CFLAllSpcPGERFFExCZ01 | Com-Iltg-dWatt-CFL_OSspc | PGE | RFF | Ex | CZ01 | 3.33 | 0.00057 | 0 | 3.25 | 0.000648 | -0.0393 | 3.33 | 0.00057 | 0 | 3.25 | 0.000648 | -0.0393 | CFL | AllSpc | 3330 | 0.57 | 3330 | 0.57 | 0.976 | 1.14 | -0.0118
CFLAllSpcPGERFFExCZ02 | Com-Iltg-dWatt-CFL_OSspc | PGE | RFF | Ex | CZ02 | 3.33 | 0.00057 | 0 | 3.44 | 0.000662 | -0.0255 | 3.33 | 0.00057 | 0 | 3.44 | 0.000662 | -0.0255 | CFL | AllSpc | 3330 | 0.57 | 3330 | 0.57 | 1.03 | 1.16 | -0.00766
CFLAllSpcPGERFFExCZ03 | Com-Iltg-dWatt-CFL_OSspc | PGE | RFF | Ex | CZ03 | 3.33 | 0.00057 | 0 | 3.4 | 0.000658 | -0.027 | 3.33 | 0.00057 | 0 | 3.4 | 0.000658 | -0.027 | CFL | AllSpc | 3330 | 0.57 | 3330 | 0.57 | 1.02 | 1.15 | -0.00811
CFLAllSpcPGERFFExCZ04 | Com-Iltg-dWatt-CFL_OSspc | PGE | RFF | Ex | CZ04 | 3.33 | 0.00057 | 0 | 3.49 | 0.000661 | -0.0214 | 3.33 | 0.00057 | 0 | 3.49 | 0.000661 | -0.0214 | CFL | AllSpc | 3330 | 0.57 | 3330 | 0.57 | 1.05 | 1.16 | -0.00643
CFLAllSpcPGERFFExCZ05 | Com-Iltg-dWatt-CFL_OSspc | PGE | RFF | Ex | CZ05 | 3.33 | 0.00057 | 0 | 3.46 | 0.000675 | -0.0311 | 3.33 | 0.00057 | 0 | 3.46 | 0.000675 | -0.0311 | CFL | AllSpc | 3330 | 0.57 | 3330 | 0.57 | 1.04 | 1.18 | -0.00934
CFLAllSpcSCGRFFExCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCG | RFF | Ex | CZ05 | 3.33 | 0.00057 | 0 | 3.46 | 0.000675 | -0.0311 | 3.33 | 0.00057 | 0 | 3.46 | 0.000675 | -0.0311 | CFL | AllSpc | 3330 | 0.57 | 3330 | 0.57 | 1.04 | 1.18 | -0.00934
CFLAllSpcSCERFFExCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCE | RFF | Ex | CZ05 | 3.33 | 0.00057 | 0 | 3.46 | 0.000675 | -0.0311 | 3.33 | 0.00057 | 0 | 3.46 | 0.000675 | -0.0311 | CFL | AllSpc | 3330 | 0.57 | 3330 | 0.57 | 1.04 | 1.18 | -0.00934
CFLAllSpcSCERFFExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCE | RFF | Ex | CZ06 | 3.33 | 0.00057 | 0 | 3.7 | 0.000696 | -0.0178 | 3.33 | 0.00057 | 0 | 3.7 | 0.000696 | -0.0178 | CFL | AllSpc | 3330 | 0.57 | 3330 | 0.57 | 1.11 | 1.22 | -0.00535
CFLAllSpcSDGRFFExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SDG | RFF | Ex | CZ06 | 3.33 | 0.00057 | 0 | 3.7 | 0.000696 | -0.0178 | 3.33 | 0.00057 | 0 | 3.7 | 0.000696 | -0.0178 | CFL | AllSpc | 3330 | 0.57 | 3330 | 0.57 | 1.11 | 1.22 | -0.00535
CFLAllSpcSCGRFFExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCG | RFF | Ex | CZ06 | 3.33 | 0.00057 | 0 | 3.7 | 0.000696 | -0.0178 | 3.33 | 0.00057 | 0 | 3.7 | 0.000696 | -0.0178 | CFL | AllSpc | 3330 | 0.57 | 3330 | 0.57 | 1.11 | 1.22 | -0.00535
CFLAllSpcSDGRFFExCZ07 | Com-Iltg-dWatt-CFL_OSspc | SDG | RFF | Ex | CZ07 | 3.33 | 0.00057 | 0 | 3.7 | 0.000691 | -0.016 | 3.33 | 0.00057 | 0 | 3.7 | 0.000691 | -0.016 | CFL | AllSpc | 3330 | 0.57 | 3330 | 0.57 | 1.11 | 1.21 | -0.0048
CFLAllSpcSDGRFFExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SDG | RFF | Ex | CZ08 | 3.33 | 0.00057 | 0 | 3.73 | 0.00069 | -0.0157 | 3.33 | 0.00057 | 0 | 3.73 | 0.00069 | -0.0157 | CFL | AllSpc | 3330 | 0.57 | 3330 | 0.57 | 1.12 | 1.21 | -0.00471
CFLAllSpcSCERFFExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCE | RFF | Ex | CZ08 | 3.33 | 0.00057 | 0 | 3.73 | 0.00069 | -0.0157 | 3.33 | 0.00057 | 0 | 3.73 | 0.00069 | -0.0157 | CFL | AllSpc | 3330 | 0.57 | 3330 | 0.57 | 1.12 | 1.21 | -0.00471
CFLAllSpcSCGRFFExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCG | RFF | Ex | CZ08 | 3.33 | 0.00057 | 0 | 3.73 | 0.00069 | -0.0157 | 3.33 | 0.00057 | 0 | 3.73 | 0.00069 | -0.0157 | CFL | AllSpc | 3330 | 0.57 | 3330 | 0.57 | 1.12 | 1.21 | -0.00471
CFLAllSpcSCERFFExCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCE | RFF | Ex | CZ09 | 3.33 | 0.00057 | 0 | 3.67 | 0.000698 | -0.016 | 3.33 | 0.00057 | 0 | 3.67 | 0.000698 | -0.016 | CFL | AllSpc | 3330 | 0.57 | 3330 | 0.57 | 1.1 | 1.22 | -0.0048
CFLAllSpcSCGRFFExCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCG | RFF | Ex | CZ09 | 3.33 | 0.00057 | 0 | 3.67 | 0.000698 | -0.016 | 3.33 | 0.00057 | 0 | 3.67 | 0.000698 | -0.016 | CFL | AllSpc | 3330 | 0.57 | 3330 | 0.57 | 1.1 | 1.22 | -0.0048
CFLAllSpcSDGRFFExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SDG | RFF | Ex | CZ10 | 3.33 | 0.00057 | 0 | 3.73 | 0.000702 | -0.0174 | 3.33 | 0.00057 | 0 | 3.73 | 0.000702 | -0.0174 | CFL | AllSpc | 3330 | 0.57 | 3330 | 0.57 | 1.12 | 1.23 | -0.00523
CFLAllSpcSCGRFFExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCG | RFF | Ex | CZ10 | 3.33 | 0.00057 | 0 | 3.73 | 0.000702 | -0.0174 | 3.33 | 0.00057 | 0 | 3.73 | 0.000702 | -0.0174 | CFL | AllSpc | 3330 | 0.57 | 3330 | 0.57 | 1.12 | 1.23 | -0.00523
CFLAllSpcSCERFFExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCE | RFF | Ex | CZ10 | 3.33 | 0.00057 | 0 | 3.73 | 0.000702 | -0.0174 | 3.33 | 0.00057 | 0 | 3.73 | 0.000702 | -0.0174 | CFL | AllSpc | 3330 | 0.57 | 3330 | 0.57 | 1.12 | 1.23 | -0.00523
CFLAllSpcPGERFFExCZ11 | Com-Iltg-dWatt-CFL_OSspc | PGE | RFF | Ex | CZ11 | 3.33 | 0.00057 | 0 | 3.51 | 0.000674 | -0.021 | 3.33 | 0.00057 | 0 | 3.51 | 0.000674 | -0.021 | CFL | AllSpc | 3330 | 0.57 | 3330 | 0.57 | 1.05 | 1.18 | -0.00631
CFLAllSpcPGERFFExCZ12 | Com-Iltg-dWatt-CFL_OSspc | PGE | RFF | Ex | CZ12 | 3.33 | 0.00057 | 0 | 3.49 | 0.000667 | -0.022 | 3.33 | 0.00057 | 0 | 3.49 | 0.000667 | -0.022 | CFL | AllSpc | 3330 | 0.57 | 3330 | 0.57 | 1.05 | 1.17 | -0.00661
CFLAllSpcPGERFFExCZ13 | Com-Iltg-dWatt-CFL_OSspc | PGE | RFF | Ex | CZ13 | 3.33 | 0.00057 | 0 | 3.6 | 0.000691 | -0.0234 | 3.33 | 0.00057 | 0 | 3.6 | 0.000691 | -0.0234 | CFL | AllSpc | 3330 | 0.57 | 3330 | 0.57 | 1.08 | 1.21 | -0.00703
CFLAllSpcSCERFFExCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCE | RFF | Ex | CZ13 | 3.33 | 0.00057 | 0 | 3.6 | 0.000691 | -0.0234 | 3.33 | 0.00057 | 0 | 3.6 | 0.000691 | -0.0234 | CFL | AllSpc | 3330 | 0.57 | 3330 | 0.57 | 1.08 | 1.21 | -0.00703
CFLAllSpcSCGRFFExCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCG | RFF | Ex | CZ13 | 3.33 | 0.00057 | 0 | 3.6 | 0.000691 | -0.0234 | 3.33 | 0.00057 | 0 | 3.6 | 0.000691 | -0.0234 | CFL | AllSpc | 3330 | 0.57 | 3330 | 0.57 | 1.08 | 1.21 | -0.00703
CFLAllSpcSCGRFFExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCG | RFF | Ex | CZ14 | 3.33 | 0.00057 | 0 | 3.67 | 0.000714 | -0.0246 | 3.33 | 0.00057 | 0 | 3.67 | 0.000714 | -0.0246 | CFL | AllSpc | 3330 | 0.57 | 3330 | 0.57 | 1.1 | 1.25 | -0.00739
CFLAllSpcSCERFFExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCE | RFF | Ex | CZ14 | 3.33 | 0.00057 | 0 | 3.67 | 0.000714 | -0.0246 | 3.33 | 0.00057 | 0 | 3.67 | 0.000714 | -0.0246 | CFL | AllSpc | 3330 | 0.57 | 3330 | 0.57 | 1.1 | 1.25 | -0.00739
CFLAllSpcSDGRFFExCZ14 | Com-Iltg-dWatt-CFL_OSspc | SDG | RFF | Ex | CZ14 | 3.33 | 0.00057 | 0 | 3.67 | 0.000714 | -0.0246 | 3.33 | 0.00057 | 0 | 3.67 | 0.000714 | -0.0246 | CFL | AllSpc | 3330 | 0.57 | 3330 | 0.57 | 1.1 | 1.25 | -0.00739
CFLAllSpcSCGRFFExCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCG | RFF | Ex | CZ15 | 3.33 | 0.00057 | 0 | 3.96 | 0.000709 | -0.00809 | 3.33 | 0.00057 | 0 | 3.96 | 0.000709 | -0.00809 | CFL | AllSpc | 3330 | 0.57 | 3330 | 0.57 | 1.19 | 1.24 | -0.00243
CFLAllSpcSCERFFExCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCE | RFF | Ex | CZ15 | 3.33 | 0.00057 | 0 | 3.96 | 0.000709 | -0.00809 | 3.33 | 0.00057 | 0 | 3.96 | 0.000709 | -0.00809 | CFL | AllSpc | 3330 | 0.57 | 3330 | 0.57 | 1.19 | 1.24 | -0.00243
CFLAllSpcSDGRFFExCZ15 | Com-Iltg-dWatt-CFL_OSspc | SDG | RFF | Ex | CZ15 | 3.33 | 0.00057 | 0 | 3.96 | 0.000709 | -0.00809 | 3.33 | 0.00057 | 0 | 3.96 | 0.000709 | -0.00809 | CFL | AllSpc | 3330 | 0.57 | 3330 | 0.57 | 1.19 | 1.24 | -0.00243
CFLAllSpcSCERFFExCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCE | RFF | Ex | CZ16 | 3.33 | 0.00057 | 0 | 3.33 | 0.000677 | -0.045 | 3.33 | 0.00057 | 0 | 3.33 | 0.000677 | -0.045 | CFL | AllSpc | 3330 | 0.57 | 3330 | 0.57 | 1 | 1.19 | -0.0135
CFLAllSpcPGERFFExCZ16 | Com-Iltg-dWatt-CFL_OSspc | PGE | RFF | Ex | CZ16 | 3.33 | 0.00057 | 0 | 3.33 | 0.000677 | -0.045 | 3.33 | 0.00057 | 0 | 3.33 | 0.000677 | -0.045 | CFL | AllSpc | 3330 | 0.57 | 3330 | 0.57 | 1 | 1.19 | -0.0135
CFLAllSpcSCGRFFExCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCG | RFF | Ex | CZ16 | 3.33 | 0.00057 | 0 | 3.33 | 0.000677 | -0.045 | 3.33 | 0.00057 | 0 | 3.33 | 0.000677 | -0.045 | CFL | AllSpc | 3330 | 0.57 | 3330 | 0.57 | 1 | 1.19 | -0.0135
CFLAllSpcSCERFFExIOU | Com-Iltg-dWatt-CFL_OSspc | SCE | RFF | Ex | IOU | 3.33 | 0.00057 | 0 | 3.71 | 0.000697 | -0.0174 | 3.33 | 0.00057 | 0 | 3.71 | 0.000697 | -0.0174 | CFL | AllSpc | 3330 | 0.57 | 3330 | 0.57 | 1.11 | 1.22 | -0.00523
CFLAllSpcPGERFFExIOU | Com-Iltg-dWatt-CFL_OSspc | PGE | RFF | Ex | IOU | 3.33 | 0.00057 | 0 | 3.47 | 0.000667 | -0.0247 | 3.33 | 0.00057 | 0 | 3.47 | 0.000667 | -0.0247 | CFL | AllSpc | 3330 | 0.57 | 3330 | 0.57 | 1.04 | 1.17 | -0.00742
CFLAllSpcSCGRFFExIOU | Com-Iltg-dWatt-CFL_OSspc | SCG | RFF | Ex | IOU | 3.33 | 0.00057 | 0 | 3.71 | 0.000697 | -0.0171 | 3.33 | 0.00057 | 0 | 3.71 | 0.000697 | -0.0171 | CFL | AllSpc | 3330 | 0.57 | 3330 | 0.57 | 1.11 | 1.22 | -0.00514
CFLAllSpcSDGRFFExIOU | Com-Iltg-dWatt-CFL_OSspc | SDG | RFF | Ex | IOU | 3.33 | 0.00057 | 0 | 3.71 | 0.000694 | -0.0164 | 3.33 | 0.00057 | 0 | 3.71 | 0.000694 | -0.0164 | CFL | AllSpc | 3330 | 0.57 | 3330 | 0.57 | 1.11 | 1.22 | -0.00492
CFLAllSpcPGERFFNewCZ01 | Com-Iltg-dWatt-CFL_OSspc | PGE | RFF | New | CZ01 | 3.33 | 0.00057 | 0 | 3.13 | 0.00062 | -0.0413 | 3.33 | 0.00057 | 0 | 3.13 | 0.00062 | -0.0413 | CFL | AllSpc | 3330 | 0.57 | 3330 | 0.57 | 0.94 | 1.09 | -0.0124
CFLAllSpcPGERFFNewCZ02 | Com-Iltg-dWatt-CFL_OSspc | PGE | RFF | New | CZ02 | 3.33 | 0.00057 | 0 | 3.36 | 0.000687 | -0.0303 | 3.33 | 0.00057 | 0 | 3.36 | 0.000687 | -0.0303 | CFL | AllSpc | 3330 | 0.57 | 3330 | 0.57 | 1.01 | 1.21 | -0.0091
CFLAllSpcPGERFFNewCZ03 | Com-Iltg-dWatt-CFL_OSspc | PGE | RFF | New | CZ03 | 3.33 | 0.00057 | 0 | 3.3 | 0.000667 | -0.0308 | 3.33 | 0.00057 | 0 | 3.3 | 0.000667 | -0.0308 | CFL | AllSpc | 3330 | 0.57 | 3330 | 0.57 | 0.991 | 1.17 | -0.00925
CFLAllSpcPGERFFNewCZ04 | Com-Iltg-dWatt-CFL_OSspc | PGE | RFF | New | CZ04 | 3.33 | 0.00057 | 0 | 3.42 | 0.00068 | -0.0255 | 3.33 | 0.00057 | 0 | 3.42 | 0.00068 | -0.0255 | CFL | AllSpc | 3330 | 0.57 | 3330 | 0.57 | 1.03 | 1.19 | -0.00766
CFLAllSpcSCERFFNewCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCE | RFF | New | CZ05 | 3.33 | 0.00057 | 0 | 3.41 | 0.000685 | -0.0302 | 3.33 | 0.00057 | 0 | 3.41 | 0.000685 | -0.0302 | CFL | AllSpc | 3330 | 0.57 | 3330 | 0.57 | 1.02 | 1.2 | -0.00907
CFLAllSpcPGERFFNewCZ05 | Com-Iltg-dWatt-CFL_OSspc | PGE | RFF | New | CZ05 | 3.33 | 0.00057 | 0 | 3.29 | 0.000657 | -0.0273 | 3.33 | 0.00057 | 0 | 3.29 | 0.000657 | -0.0273 | CFL | AllSpc | 3330 | 0.57 | 3330 | 0.57 | 0.988 | 1.15 | -0.0082
CFLAllSpcSDGRFFNewCZ06 | Com-Iltg-dWatt-CFL_OSspc | SDG | RFF | New | CZ06 | 3.33 | 0.00057 | 0 | 3.57 | 0.000707 | -0.0187 | 3.33 | 0.00057 | 0 | 3.57 | 0.000707 | -0.0187 | CFL | AllSpc | 3330 | 0.57 | 3330 | 0.57 | 1.07 | 1.24 | -0.00562
CFLAllSpcSCERFFNewCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCE | RFF | New | CZ06 | 3.33 | 0.00057 | 0 | 3.58 | 0.000705 | -0.0179 | 3.33 | 0.00057 | 0 | 3.58 | 0.000705 | -0.0179 | CFL | AllSpc | 3330 | 0.57 | 3330 | 0.57 | 1.08 | 1.24 | -0.00538
CFLAllSpcSDGRFFNewCZ07 | Com-Iltg-dWatt-CFL_OSspc | SDG | RFF | New | CZ07 | 3.33 | 0.00057 | 0 | 3.55 | 0.000701 | -0.0198 | 3.33 | 0.00057 | 0 | 3.55 | 0.000701 | -0.0198 | CFL | AllSpc | 3330 | 0.57 | 3330 | 0.57 | 1.07 | 1.23 | -0.00595
CFLAllSpcSCERFFNewCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCE | RFF | New | CZ08 | 3.33 | 0.00057 | 0 | 3.58 | 0.000684 | -0.0176 | 3.33 | 0.00057 | 0 | 3.58 | 0.000684 | -0.0176 | CFL | AllSpc | 3330 | 0.57 | 3330 | 0.57 | 1.08 | 1.2 | -0.00529
CFLAllSpcSDGRFFNewCZ08 | Com-Iltg-dWatt-CFL_OSspc | SDG | RFF | New | CZ08 | 3.33 | 0.00057 | 0 | 3.58 | 0.000686 | -0.0183 | 3.33 | 0.00057 | 0 | 3.58 | 0.000686 | -0.0183 | CFL | AllSpc | 3330 | 0.57 | 3330 | 0.57 | 1.08 | 1.2 | -0.0055
CFLAllSpcSCERFFNewCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCE | RFF | New | CZ09 | 3.33 | 0.00057 | 0 | 3.65 | 0.000731 | -0.0197 | 3.33 | 0.00057 | 0 | 3.65 | 0.000731 | -0.0197 | CFL | AllSpc | 3330 | 0.57 | 3330 | 0.57 | 1.1 | 1.28 | -0.00592
CFLAllSpcSDGRFFNewCZ10 | Com-Iltg-dWatt-CFL_OSspc | SDG | RFF | New | CZ10 | 3.33 | 0.00057 | 0 | 3.66 | 0.000739 | -0.0213 | 3.33 | 0.00057 | 0 | 3.66 | 0.000739 | -0.0213 | CFL | AllSpc | 3330 | 0.57 | 3330 | 0.57 | 1.1 | 1.3 | -0.0064
CFLAllSpcSCERFFNewCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCE | RFF | New | CZ10 | 3.33 | 0.00057 | 0 | 3.67 | 0.000737 | -0.0205 | 3.33 | 0.00057 | 0 | 3.67 | 0.000737 | -0.0205 | CFL | AllSpc | 3330 | 0.57 | 3330 | 0.57 | 1.1 | 1.29 | -0.00616
CFLAllSpcPGERFFNewCZ11 | Com-Iltg-dWatt-CFL_OSspc | PGE | RFF | New | CZ11 | 3.33 | 0.00057 | 0 | 3.5 | 0.000703 | -0.023 | 3.33 | 0.00057 | 0 | 3.5 | 0.000703 | -0.023 | CFL | AllSpc | 3330 | 0.57 | 3330 | 0.57 | 1.05 | 1.23 | -0.00691
CFLAllSpcPGERFFNewCZ12 | Com-Iltg-dWatt-CFL_OSspc | PGE | RFF | New | CZ12 | 3.33 | 0.00057 | 0 | 3.46 | 0.000695 | -0.027 | 3.33 | 0.00057 | 0 | 3.46 | 0.000695 | -0.027 | CFL | AllSpc | 3330 | 0.57 | 3330 | 0.57 | 1.04 | 1.22 | -0.00811
CFLAllSpcPGERFFNewCZ13 | Com-Iltg-dWatt-CFL_OSspc | PGE | RFF | New | CZ13 | 3.33 | 0.00057 | 0 | 3.51 | 0.000694 | -0.024 | 3.33 | 0.00057 | 0 | 3.51 | 0.000694 | -0.024 | CFL | AllSpc | 3330 | 0.57 | 3330 | 0.57 | 1.05 | 1.22 | -0.00721
CFLAllSpcSCERFFNewCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCE | RFF | New | CZ13 | 3.33 | 0.00057 | 0 | 3.66 | 0.000734 | -0.0269 | 3.33 | 0.00057 | 0 | 3.66 | 0.000734 | -0.0269 | CFL | AllSpc | 3330 | 0.57 | 3330 | 0.57 | 1.1 | 1.29 | -0.00808
CFLAllSpcSCERFFNewCZ14 | Com-Iltg-dWatt-CFL_OSspc | SCE | RFF | New | CZ14 | 3.33 | 0.00057 | 0 | 3.65 | 0.000741 | -0.0286 | 3.33 | 0.00057 | 0 | 3.65 | 0.000741 | -0.0286 | CFL | AllSpc | 3330 | 0.57 | 3330 | 0.57 | 1.1 | 1.3 | -0.00859
CFLAllSpcSDGRFFNewCZ14 | Com-Iltg-dWatt-CFL_OSspc | SDG | RFF | New | CZ14 | 3.33 | 0.00057 | 0 | 3.65 | 0.000744 | -0.0297 | 3.33 | 0.00057 | 0 | 3.65 | 0.000744 | -0.0297 | CFL | AllSpc | 3330 | 0.57 | 3330 | 0.57 | 1.1 | 1.31 | -0.00892
CFLAllSpcSDGRFFNewCZ15 | Com-Iltg-dWatt-CFL_OSspc | SDG | RFF | New | CZ15 | 3.33 | 0.00057 | 0 | 3.92 | 0.000753 | -0.0106 | 3.33 | 0.00057 | 0 | 3.92 | 0.000753 | -0.0106 | CFL | AllSpc | 3330 | 0.57 | 3330 | 0.57 | 1.18 | 1.32 | -0.00318
CFLAllSpcSCERFFNewCZ15 | Com-Iltg-dWatt-CFL_OSspc | SCE | RFF | New | CZ15 | 3.33 | 0.00057 | 0 | 3.92 | 0.00075 | -0.0102 | 3.33 | 0.00057 | 0 | 3.92 | 0.00075 | -0.0102 | CFL | AllSpc | 3330 | 0.57 | 3330 | 0.57 | 1.18 | 1.32 | -0.00306
CFLAllSpcPGERFFNewCZ16 | Com-Iltg-dWatt-CFL_OSspc | PGE | RFF | New | CZ16 | 3.33 | 0.00057 | 0 | 3.24 | 0.000671 | -0.0426 | 3.33 | 0.00057 | 0 | 3.24 | 0.000671 | -0.0426 | CFL | AllSpc | 3330 | 0.57 | 3330 | 0.57 | 0.973 | 1.18 | -0.0128
CFLAllSpcSCERFFNewCZ16 | Com-Iltg-dWatt-CFL_OSspc | SCE | RFF | New | CZ16 | 3.33 | 0.00057 | 0 | 3.37 | 0.000704 | -0.0483 | 3.33 | 0.00057 | 0 | 3.37 | 0.000704 | -0.0483 | CFL | AllSpc | 3330 | 0.57 | 3330 | 0.57 | 1.01 | 1.24 | -0.0145
CFLAllSpcSCERFFNewIOU | Com-Iltg-dWatt-CFL_OSspc | SCE | RFF | New | IOU | 3.33 | 0.00057 | 0 | 3.63 | 0.000717 | -0.0196 | 3.33 | 0.00057 | 0 | 3.63 | 0.000717 | -0.0196 | CFL | AllSpc | 3330 | 0.57 | 3330 | 0.57 | 1.09 | 1.26 | -0.00589
CFLAllSpcSCGRFFNewIOU | Com-Iltg-dWatt-CFL_OSspc | SCG | RFF | New | IOU | 3.33 | 0.00057 | 0 | 3.63 | 0.000715 | -0.0195 | 3.33 | 0.00057 | 0 | 3.63 | 0.000715 | -0.0195 | CFL | AllSpc | 3330 | 0.57 | 3330 | 0.57 | 1.09 | 1.25 | -0.00586
CFLAllSpcSDGRFFNewIOU | Com-Iltg-dWatt-CFL_OSspc | SDG | RFF | New | IOU | 3.33 | 0.00057 | 0 | 3.58 | 0.000709 | -0.02 | 3.33 | 0.00057 | 0 | 3.58 | 0.000709 | -0.02 | CFL | AllSpc | 3330 | 0.57 | 3330 | 0.57 | 1.08 | 1.24 | -0.00601
CFLAllSpcPGERFFNewIOU | Com-Iltg-dWatt-CFL_OSspc | PGE | RFF | New | IOU | 3.33 | 0.00057 | 0 | 3.61 | 0.000726 | -0.0286 | 3.33 | 0.00057 | 0 | 3.61 | 0.000726 | -0.0286 | CFL | AllSpc | 3330 | 0.57 | 3330 | 0.57 | 1.08 | 1.27 | -0.00859
CFLAllSpcPGERSDExCZ01 | Com-Iltg-dWatt-CFL_OSspc | PGE | RSD | Ex | CZ01 | 3.3 | 0.000522 | 0 | 3.17 | 0.000612 | -0.0412 | 3.3 | 0.000522 | 0 | 3.17 | 0.000612 | -0.0412 | CFL | AllSpc | 3300 | 0.522 | 3300 | 0.522 | 0.961 | 1.17 | -0.0125
CFLAllSpcPGERSDExCZ02 | Com-Iltg-dWatt-CFL_OSspc | PGE | RSD | Ex | CZ02 | 3.3 | 0.000522 | 0 | 3.42 | 0.000612 | -0.0242 | 3.3 | 0.000522 | 0 | 3.42 | 0.000612 | -0.0242 | CFL | AllSpc | 3300 | 0.522 | 3300 | 0.522 | 1.04 | 1.17 | -0.00733
CFLAllSpcPGERSDExCZ03 | Com-Iltg-dWatt-CFL_OSspc | PGE | RSD | Ex | CZ03 | 3.3 | 0.000522 | 0 | 3.38 | 0.000613 | -0.0271 | 3.3 | 0.000522 | 0 | 3.38 | 0.000613 | -0.0271 | CFL | AllSpc | 3300 | 0.522 | 3300 | 0.522 | 1.02 | 1.17 | -0.00821
CFLAllSpcPGERSDExCZ04 | Com-Iltg-dWatt-CFL_OSspc | PGE | RSD | Ex | CZ04 | 3.3 | 0.000522 | 0 | 3.48 | 0.000614 | -0.0201 | 3.3 | 0.000522 | 0 | 3.48 | 0.000614 | -0.0201 | CFL | AllSpc | 3300 | 0.522 | 3300 | 0.522 | 1.05 | 1.18 | -0.00609
CFLAllSpcSCGRSDExCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCG | RSD | Ex | CZ05 | 3.3 | 0.000522 | 0 | 3.47 | 0.000635 | -0.0297 | 3.3 | 0.000522 | 0 | 3.47 | 0.000635 | -0.0297 | CFL | AllSpc | 3300 | 0.522 | 3300 | 0.522 | 1.05 | 1.22 | -0.009
CFLAllSpcSCERSDExCZ05 | Com-Iltg-dWatt-CFL_OSspc | SCE | RSD | Ex | CZ05 | 3.3 | 0.000522 | 0 | 3.47 | 0.000635 | -0.0297 | 3.3 | 0.000522 | 0 | 3.47 | 0.000635 | -0.0297 | CFL | AllSpc | 3300 | 0.522 | 3300 | 0.522 | 1.05 | 1.22 | -0.009
CFLAllSpcPGERSDExCZ05 | Com-Iltg-dWatt-CFL_OSspc | PGE | RSD | Ex | CZ05 | 3.3 | 0.000522 | 0 | 3.47 | 0.000635 | -0.0297 | 3.3 | 0.000522 | 0 | 3.47 | 0.000635 | -0.0297 | CFL | AllSpc | 3300 | 0.522 | 3300 | 0.522 | 1.05 | 1.22 | -0.009
CFLAllSpcSDGRSDExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SDG | RSD | Ex | CZ06 | 3.3 | 0.000522 | 0 | 3.73 | 0.000648 | -0.0157 | 3.3 | 0.000522 | 0 | 3.73 | 0.000648 | -0.0157 | CFL | AllSpc | 3300 | 0.522 | 3300 | 0.522 | 1.13 | 1.24 | -0.00476
CFLAllSpcSCERSDExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCE | RSD | Ex | CZ06 | 3.3 | 0.000522 | 0 | 3.73 | 0.000648 | -0.0157 | 3.3 | 0.000522 | 0 | 3.73 | 0.000648 | -0.0157 | CFL | AllSpc | 3300 | 0.522 | 3300 | 0.522 | 1.13 | 1.24 | -0.00476
CFLAllSpcSCGRSDExCZ06 | Com-Iltg-dWatt-CFL_OSspc | SCG | RSD | Ex | CZ06 | 3.3 | 0.000522 | 0 | 3.73 | 0.000648 | -0.0157 | 3.3 | 0.000522 | 0 | 3.73 | 0.000648 | -0.0157 | CFL | AllSpc | 3300 | 0.522 | 3300 | 0.522 | 1.13 | 1.24 | -0.00476
CFLAllSpcSDGRSDExCZ07 | Com-Iltg-dWatt-CFL_OSspc | SDG | RSD | Ex | CZ07 | 3.3 | 0.000522 | 0 | 3.73 | 0.000651 | -0.0138 | 3.3 | 0.000522 | 0 | 3.73 | 0.000651 | -0.0138 | CFL | AllSpc | 3300 | 0.522 | 3300 | 0.522 | 1.13 | 1.25 | -0.00418
CFLAllSpcSCGRSDExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCG | RSD | Ex | CZ08 | 3.3 | 0.000522 | 0 | 3.76 | 0.000633 | -0.0134 | 3.3 | 0.000522 | 0 | 3.76 | 0.000633 | -0.0134 | CFL | AllSpc | 3300 | 0.522 | 3300 | 0.522 | 1.14 | 1.21 | -0.00406
CFLAllSpcSDGRSDExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SDG | RSD | Ex | CZ08 | 3.3 | 0.000522 | 0 | 3.76 | 0.000633 | -0.0134 | 3.3 | 0.000522 | 0 | 3.76 | 0.000633 | -0.0134 | CFL | AllSpc | 3300 | 0.522 | 3300 | 0.522 | 1.14 | 1.21 | -0.00406
CFLAllSpcSCERSDExCZ08 | Com-Iltg-dWatt-CFL_OSspc | SCE | RSD | Ex | CZ08 | 3.3 | 0.000522 | 0 | 3.76 | 0.000633 | -0.0134 | 3.3 | 0.000522 | 0 | 3.76 | 0.000633 | -0.0134 | CFL | AllSpc | 3300 | 0.522 | 3300 | 0.522 | 1.14 | 1.21 | -0.00406
CFLAllSpcSCERSDExCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCE | RSD | Ex | CZ09 | 3.3 | 0.000522 | 0 | 3.7 | 0.000637 | -0.0148 | 3.3 | 0.000522 | 0 | 3.7 | 0.000637 | -0.0148 | CFL | AllSpc | 3300 | 0.522 | 3300 | 0.522 | 1.12 | 1.22 | -0.00448
CFLAllSpcSCGRSDExCZ09 | Com-Iltg-dWatt-CFL_OSspc | SCG | RSD | Ex | CZ09 | 3.3 | 0.000522 | 0 | 3.7 | 0.000637 | -0.0148 | 3.3 | 0.000522 | 0 | 3.7 | 0.000637 | -0.0148 | CFL | AllSpc | 3300 | 0.522 | 3300 | 0.522 | 1.12 | 1.22 | -0.00448
CFLAllSpcSCGRSDExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCG | RSD | Ex | CZ10 | 3.3 | 0.000522 | 0 | 3.74 | 0.000625 | -0.0158 | 3.3 | 0.000522 | 0 | 3.74 | 0.000625 | -0.0158 | CFL | AllSpc | 3300 | 0.522 | 3300 | 0.522 | 1.13 | 1.2 | -0.00479
CFLAllSpcSCERSDExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SCE | RSD | Ex | CZ10 | 3.3 | 0.000522 | 0 | 3.74 | 0.000625 | -0.0158 | 3.3 | 0.000522 | 0 | 3.74 | 0.000625 | -0.0158 | CFL | AllSpc | 3300 | 0.522 | 3300 | 0.522 | 1.13 | 1.2 | -0.00479
CFLAllSpcSDGRSDExCZ10 | Com-Iltg-dWatt-CFL_OSspc | SDG | RSD | Ex | CZ10 | 3.3 | 0.000522 | 0 | 3.74 | 0.000625 | -0.0158 | 3.3 | 0.000522 | 0 | 3.74 | 0.000625 | -0.0158 | CFL | AllSpc | 3300 | 0.522 | 3300 | 0.522 | 1.13 | 1.2 | -0.00479
CFLAllSpcPGERSDExCZ11 | Com-Iltg-dWatt-CFL_OSspc | PGE | RSD | Ex | CZ11 | 3.3 | 0.000522 | 0 | 3.49 | 0.000618 | -0.0209 | 3.3 | 0.000522 | 0 | 3.49 | 0.000618 | -0.0209 | CFL | AllSpc | 3300 | 0.522 | 3300 | 0.522 | 1.06 | 1.18 | -0.00633
CFLAllSpcPGERSDExCZ12 | Com-Iltg-dWatt-CFL_OSspc | PGE | RSD | Ex | CZ12 | 3.3 | 0.000522 | 0 | 3.46 | 0.000598 | -0.0216 | 3.3 | 0.000522 | 0 | 3.46 | 0.000598 | -0.0216 | CFL | AllSpc | 3300 | 0.522 | 3300 | 0.522 | 1.05 | 1.15 | -0.00655
CFLAllSpcSCERSDExCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCE | RSD | Ex | CZ13 | 3.3 | 0.000522 | 0 | 3.61 | 0.000643 | -0.0229 | 3.3 | 0.000522 | 0 | 3.61 | 0.000643 | -0.0229 | CFL | AllSpc | 3300 | 0.522 | 3300 | 0.522 | 1.09 | 1.23 | -0.00694
CFLAllSpcPGERSDExCZ13 | Com-Iltg-dWatt-CFL_OSspc | PGE | RSD | Ex | CZ13 | 3.3 | 0.000522 | 0 | 3.61 | 0.000643 | -0.0229 | 3.3 | 0.000522 | 0 | 3.61 | 0.000643 | -0.0229 | CFL | AllSpc | 3300 | 0.522 | 3300 | 0.522 | 1.09 | 1.23 | -0.00694
CFLAllSpcSCGRSDExCZ13 | Com-Iltg-dWatt-CFL_OSspc | SCG | RSD | Ex | CZ13 | 3.3 | 0.000522 | 0 | 3.61 | 0.000643 | -0.0229 | 3.3 | 0.000522 | 0 | 3.61 | 0.000643 | -0.0229 | CFL | AllSpc | 3300 | 0.522 | 3300 | 0.522 | 1.09 | 1.23 | -0.00694