## Summary
DEER2016 Commercial Boiler Update
2015-05-14
Key Changes:
Assumption for boiler draft type in baseline
For all boiler measures in DEER2014, both standard and pre-existing boilers were modeled as atmospheric draft. For DEER2016 all standard and pre-existing boilers are changed to forced draft. This change was made in accordance with the 2011 Codes and Standards Enhancement Intitiative (CASE) report titled "Commercial Boilers", which states that 88% of existing boilers are forced draft.
Expansion of measure list
Several measures were added to accomodate program offerings. Other measures were added based on equipment listings in the CEC appliance database. The measure for steam boilers 300 to 2500 kBtuh with thermal efficiency 85% were deleted due to lack of availability in the market.
Hot water loop temperature reset control for baseline simulations
Hot water loop temperature reset control was added to all simulations for vintages starting with 2006 based on Title 24 requirements that have been in place since October 2005. The baseline reset control for DEER is assumed to be an outdoor temperature based control that resets hot water temperature between 165 and 140 F. This is applied to both steam and hot water boilers. For steam boilers, it is assumed that the secondary piping loop is hot water.
Hot water loop temperature reset control for condensing boilers
For condensing boilers, measures were developed that include alternative reset controls. The first alternative is an outdoor temperature based reset control with a reduced temperature range of 140 to 115 F. The second alternative is a load based reset control with the same reduced temperature range of 140 to 115 F.
Workbook Contents:
Baseline Summary
List of key parameters for Standard and Pre-Existing cases
Measure Summary
List of new and deleted boiler measures for DEER2016
Technology Summary
List of TechIDs for boiler measures for DEER2016
Measure Definitions
Complete listing of boiler measure definitions for DEER2016
Technologies
Complete listing of boiler technologies for DEER2016

## Measure Summary
Measure Summary
This table lists the DEER2014 measure IDs that are updated for DEER2016 and the updated measure IDs.
DEER2016 includes additional tier levels and size ranges, based on review of available products.
For details on the new measure definitions, see the technology summary worksheets and the "Measure Definitions" worksheet.
Updated Boiler Efficiency Measures
DEER2014 | DEER2016
AFUE Rated Hot Water Boilers
NG-HVAC-Blr-HW-lt300kBtuh-84p5AFUE-Atm | Deleted
NG-HVAC-Blr-HW-lt300kBtuh-84p5AFUE-Drft | NG-HVAC-Blr-HW-lt300kBtuh-84p0AFUE-Drft
NG-HVAC-Blr-HW-lt300kBtuh-84p5AFUE-Drft
NG-HVAC-Blr-HW-lt300kBtuh-85p0AFUE-Drft
NG-HVAC-Blr-HW-lt300kBtuh-87p0AFUE-Drft
NG-HVAC-Blr-HW-lt300kBtuh-90p0AFUE-CndStd
NG-HVAC-Blr-HW-lt300kBtuh-90p0AFUE-CndLow
NG-HVAC-Blr-HW-lt300kBtuh-90p0AFUE-CndReset
NG-HVAC-Blr-HW-lt300kBtuh-94p0AFUE-Cnd | NG-HVAC-Blr-HW-lt300kBtuh-94p0AFUE-CndStd
NG-HVAC-Blr-HW-lt300kBtuh-94p0AFUE-CndLow
NG-HVAC-Blr-HW-lt300kBtuh-94p0AFUE-CndReset
Thermal Efficiency Rated Hot Water Boilers
NG-HVAC-Blr-HW-300to2500kBtuh-83p0Et-Drft
NG-HVAC-Blr-HW-300to2500kBtuh-85p0ET-Atm | Deleted
NG-HVAC-Blr-HW-300to2500kBtuh-85p0ET-Drft | NG-HVAC-Blr-HW-300to2500kBtuh-85p0Et-Drft
NG-HVAC-Blr-HW-300to2500kBtuh-90p0Et-CndStd
NG-HVAC-Blr-HW-300to2500kBtuh-90p0Et-CndLow
NG-HVAC-Blr-HW-300to2500kBtuh-90p0Et-CndReset
NG-HVAC-Blr-HW-300to2500kBtuh-94p0Et-CndStd
NG-HVAC-Blr-HW-300to2500kBtuh-94p0Et-CndLow
NG-HVAC-Blr-HW-300to2500kBtuh-94p0Et-CndReset
NG-HVAC-Blr-HW-gt2500kBtuh-83p0Et-Drft
NG-HVAC-Blr-HW-gt2500kBtuh-85p0Et-Drft
NG-HVAC-Blr-HW-gt2500kBtuh-90p0Et-CndStd
NG-HVAC-Blr-HW-gt2500kBtuh-90p0Et-CndLow
NG-HVAC-Blr-HW-gt2500kBtuh-90p0Et-CndReset
NG-HVAC-Blr-HW-300to2500kBtuh-94p0ET-Cnd | NG-HVAC-Blr-HW-gt2500kBtuh-94p0Et-CndStd
NG-HVAC-Blr-HW-gt2500kBtuh-94p0Et-CndLow
NG-HVAC-Blr-HW-gt2500kBtuh-94p0Et-CndReset
NG-HVAC-Blr-HW-gt2500kBtuh-85p0EC-Atm | Deleted
NG-HVAC-Blr-HW-gt2500kBtuh-85p0EC-Drft | Deleted
AFUE Rated Steam Boilers
NG-HVAC-Blr-Stm-lt300kBtuh-82p0AFUE-Atm | Deleted
NG-HVAC-Blr-Stm-lt300kBtuh-82p0AFUE-Drft | NG-HVAC-Blr-Stm-lt300kBtuh-82p0AFUE-Drft
NG-HVAC-Blr-Stm-lt300kBtuh-83p0AFUE-Drft
Thermal Efficiency Rated Steam Boilers
NG-HVAC-Blr-Stm-300to2500kBtuh-85p0ET-Atm | Deleted
NG-HVAC-Blr-Stm-300to2500kBtuh-85p0ET-Drft | NG-HVAC-Blr-Stm-300to2500kBtuh-81p0Et-Drft
NG-HVAC-Blr-Stm-300to2500kBtuh-82p0Et-Drft
NG-HVAC-Blr-Stm-gt2500kBtuh-80p0EC-Atm | Deleted
NG-HVAC-Blr-Stm-gt2500kBtuh-80p0EC-Drft | Deleted
NG-HVAC-Blr-Stm-gt2500kBtuh-80p0Et-Drft
NG-HVAC-Blr-Stm-gt2500kBtuh-81p0Et-Drft
NG-HVAC-Blr-Stm-gt2500kBtuh-82p0Et-Drft

## Baseline Summary
Baseline Summary
This table lists the standard and vintage based pre-existing baseline conditions for each boiler category.
For additional details, see the Technology Summary worksheet and the Measure Definitions worksheet.
| Size | Efficiency | Boiler Efficiency |  |  |  |  | Hot Water Temperature Control
Boiler Type | kBtuh | Units | Pre-2005 | 2006 - 2009 | 2010 - 2013 | 2014 - 2015 | Standard | Pre-2005 | 2006 - 2009 | 2010 - 2013 | 2014 - 2015 | Standard
Hot Water | < 300 | AFUE | 80 | 80 | 80 | 82 | 82 | No reset | OA Reset from 140 to 165 F
Hot Water | 300 - 2500 | Et | 75 | 75 | 75 | 80 | 80 | No reset | OA Reset from 140 to 165 F
Hot Water | > 2500 | Et | 75 | 75 | 75 | 80 | 80 | No reset | OA Reset from 140 to 165 F
Steam | < 300 | AFUE | 75 | 75 | 75 | 80 | 80 | No reset | OA Reset from 140 to 165 F
Steam | 300 - 2500 | Et | 75 | 75 | 75 | 79 | 79 | No reset | OA Reset from 140 to 165 F
Steam | > 2500 | Et | 75 | 75 | 75 | 79 | 79 | No reset | OA Reset from 140 to 165 F
Notes:
For hot water boilers > 2500 kBtuh, the code requirement is 82% combustion efficiency, which was assumed equivalent to 80% thermal efficiency.
For all boiler measures in DEER2014, both standard and pre-existing boilers were modeled as atmospheric draft. For DEER2016 standard and pre-existing boilers are changed to forced draft. This change was made in accordance with the 2011 Codes and Standards Enhancement Intitiative (CASE) report titled "Commercial Boilers", which states that 88% of existing boilers are forced draft.

## Technology Summary
DEER2016 Commercial Boiler Measure Technology Summary
This table summarizes the key parameters for the DEER2016 commercial boiler technologies.
Type | Size | Case | Efficiency |  | Condensing | Temperature Control | TechID
Hot Water | < 300 | Standard | 82% | AFUE | No | OA reset: 140 to 165 F | W-Boiler_AF-lt300k-0.82-fDraft | Hot Water | < 300 |  | AFUE | Drft
|  | Measure | 84% | AFUE | No | OA reset: 140 to 165 F | W-Boiler_AF-lt300k-0.84-fDraft | Hot Water | < 300 | 84 | AFUE | Drft
|  | Measure | 84.5% | AFUE | No | OA reset: 140 to 165 F | W-Boiler_AF-lt300k-0.845-fDraft | Hot Water | < 300 | 84.5 | AFUE | Drft
|  | Measure | 85% | AFUE | No | OA reset: 140 to 165 F | W-Boiler_AF-lt300k-0.85-fDraft | Hot Water | < 300 | 85 | AFUE | Drft
|  | Measure | 87% | AFUE | No | OA reset: 140 to 165 F | W-Boiler_AF-lt300k-0.87-fDraft | Hot Water | < 300 | 87 | AFUE | Drft
|  | Measure | 90% | AFUE | Yes | OA reset: 140 to 165 F | W-Boiler_AF-lt300k-0.9-fDraft-CndStd | Hot Water | < 300 | 90 | AFUE | CndStd
|  | Measure | 90% | AFUE | Yes | OA reset: 115 to 140 F | W-Boiler_AF-lt300k-0.9-fDraft-CndLow | Hot Water | < 300 | 90 | AFUE | CndLow
|  | Measure | 90% | AFUE | Yes | Load reset: 115 to 140 F | W-Boiler_AF-lt300k-0.9-fDraft-CndReset | Hot Water | < 300 | 90 | AFUE | CndReset
|  | Measure | 94% | AFUE | Yes | OA reset: 140 to 165 F | W-Boiler_AF-lt300k-0.94-fDraft-CndStd | Hot Water | < 300 | 94 | AFUE | CndStd
|  | Measure | 94% | AFUE | Yes | OA reset: 115 to 140 F | W-Boiler_AF-lt300k-0.94-fDraft-CndLow | Hot Water | < 300 | 94 | AFUE | CndLow
|  | Measure | 94% | AFUE | Yes | Load reset: 115 to 140 F | W-Boiler_AF-lt300k-0.94-fDraft-CndReset | Hot Water | < 300 | 94 | AFUE | CndReset
Hot Water | 300 - 2500 | Standard | 80% | Et | No | OA reset: 140 to 165 F | W-Boiler_Et-300to2500k-0.8-fDraft | Hot Water | 300 - 2500 |  | Et | Drft
|  | Measure | 83% | Et | No | OA reset: 140 to 165 F | W-Boiler_Et-300to2500k-0.83-fDraft | Hot Water | 300 - 2500 | 83 | Et | Drft
|  | Measure | 85% | Et | No | OA reset: 140 to 165 F | W-Boiler_Et-300to2500k-0.85-fDraft | Hot Water | 300 - 2500 | 85 | Et | Drft
|  | Measure | 90% | Et | Yes | OA reset: 140 to 165 F | W-Boiler_Et-300to2500k-0.9-fDraft-CndStd | Hot Water | 300 - 2500 | 90 | Et | CndStd
|  | Measure | 90% | Et | Yes | OA reset: 115 to 140 F | W-Boiler_Et-300to2500k-0.9-fDraft-CndLow | Hot Water | 300 - 2500 | 90 | Et | CndLow
|  | Measure | 90% | Et | Yes | Load reset: 115 to 140 F | W-Boiler_Et-300to2500k-0.9-fDraft-CndReset | Hot Water | 300 - 2500 | 90 | Et | CndReset
|  | Measure | 94% | Et | Yes | OA reset: 140 to 165 F | W-Boiler_Et-300to2500k-0.94-fDraft-CndStd | Hot Water | 300 - 2500 | 94 | Et | CndStd
|  | Measure | 94% | Et | Yes | OA reset: 115 to 140 F | W-Boiler_Et-300to2500k-0.94-fDraft-CndLow | Hot Water | 300 - 2500 | 94 | Et | CndLow
|  | Measure | 94% | Et | Yes | Load reset: 115 to 140 F | W-Boiler_Et-300to2500k-0.94-fDraft-CndReset | Hot Water | 300 - 2500 | 94 | Et | CndReset
Hot Water | > 2500 | Standard | 80% | Et | No | OA reset: 140 to 165 F | W-Boiler_Et-gt2500k-0.8-fDraft | Hot Water | > 2500 |  | Et | Drft
|  | Measure | 83% | Et | No | OA reset: 140 to 165 F | W-Boiler_Et-gt2500k-0.83-fDraft | Hot Water | > 2500 | 83 | Et | Drft
|  | Measure | 85% | Et | No | OA reset: 140 to 165 F | W-Boiler_Et-gt2500k-0.85-fDraft | Hot Water | > 2500 | 85 | Et | Drft
|  | Measure | 90% | Et | Yes | OA reset: 140 to 165 F | W-Boiler_Et-gt2500k-0.9-fDraft-CndStd | Hot Water | > 2500 | 90 | Et | CndStd
|  | Measure | 90% | Et | Yes | OA reset: 115 to 140 F | W-Boiler_Et-gt2500k-0.9-fDraft-CndLow | Hot Water | > 2500 | 90 | Et | CndLow
|  | Measure | 90% | Et | Yes | Load reset: 115 to 140 F | W-Boiler_Et-gt2500k-0.9-fDraft-CndReset | Hot Water | > 2500 | 90 | Et | CndReset
|  | Measure | 94% | Et | Yes | OA reset: 140 to 165 F | W-Boiler_Et-gt2500k-0.94-fDraft-CndStd | Hot Water | > 2500 | 94 | Et | CndStd
|  | Measure | 94% | Et | Yes | OA reset: 115 to 140 F | W-Boiler_Et-gt2500k-0.94-fDraft-CndLow | Hot Water | > 2500 | 94 | Et | CndLow
|  | Measure | 94% | Et | Yes | Load reset: 115 to 140 F | W-Boiler_Et-gt2500k-0.94-fDraft-CndReset | Hot Water | > 2500 | 94 | Et | CndReset
Steam | < 300 | Standard | 80% | AFUE | No | OA reset: 140 to 165 F | S-Boiler_AF-lt300k-0.8-fDraft |  | < 300 |  | AFUE | Drft
|  | Measure | 82% | AFUE | No | OA reset: 140 to 165 F | S-Boiler_AF-lt300k-0.82-fDraft |  | < 300 | 82 | AFUE | Drft
|  | Measure | 83% | AFUE | No | OA reset: 140 to 165 F | S-Boiler_AF-lt300k-0.83-fDraft |  | < 300 | 83 | AFUE | Drft
Steam | 300 - 2500 | Standard | 79% | Et | No | OA reset: 140 to 165 F | S-Boiler_Et-300to2500k-0.79-fDraft |  | 300 - 2500 |  | Et | Drft
|  | Measure | 81% | Et | No | OA reset: 140 to 165 F | S-Boiler_Et-300to2500k-0.81-fDraft |  | 300 - 2500 | 81 | Et | Drft
|  | Measure | 82% | Et | No | OA reset: 140 to 165 F | S-Boiler_Et-300to2500k-0.82-fDraft |  | 300 - 2500 | 82 | Et | Drft
Steam | > 2500 | Standard | 79% | Et | No | OA reset: 140 to 165 F | S-Boiler_Et-gt2500k-0.79-fDraft |  | > 2500 |  | Et | Drft
|  | Measure | 80% | Et | No | OA reset: 140 to 165 F | S-Boiler_Et-gt2500k-0.8-fDraft |  | > 2500 | 80 | Et | Drft
|  | Measure | 81% | Et | No | OA reset: 140 to 165 F | S-Boiler_Et-gt2500k-0.81-fDraft |  | > 2500 | 81 | Et | Drft
|  | Measure | 82% | Et | No | OA reset: 140 to 165 F | S-Boiler_Et-gt2500k-0.82-fDraft |  | > 2500 | 82 | Et | Drft

## Measure Definitions
[15 empty] | DEER Measure Definition | [24 empty] | 19 | 19 |  | 7 | 7
This table formats the DEER2015 measures in the ex ante format.
[14 empty] | Index | MeasureID | Description | Version | VersionSource | LastMod | EnergyImpactID | MeasImpactType | EnImpCalcType | ImpScaleBasis | StdScaleVal | PreScaleVal | ImpWeighting | WeightGroupID | ApplyIE | IETableName | TechBased | Sector | PA | UseCategory | UseSubCategory | TechGroup | TechType | MeasCostID | EUL_ID | PreDesc | StdDesc | MeasDesc | PreTechID | StdTechID | MeasTechID | Status | Comment | PreMultiTech | StdMultiTech | SourceDesc | SupportedAppType | StdCostID | RUL_ID | LegacyID | Qualifier | StartDate | ExpiryDate
|  |  |  | Thru 2013 | Post 2013 | Std | Msr | Units | AltStd | AltMsr | AltUnits |  |  |  | Commercial Boilers
Hot water | HW | < 300 | lt300 | 80 | 82 | 82 | 84 | AFUE |  |  |  | Drft | 2109 | 901 | NG-HVAC-Blr-HW-lt300kBtuh-84p0AFUE-Drft | Hot water boiler (< 300 kBtuh, 84.0 AFUE, OA Reset from 140 to 165 F) | DEER2016 |  | 5/15/2015 | NG-HVAC-Blr-HW-lt300kBtuh-84p0AFUE-Drft | DEER | Standard | None | 0 | 0 | None |  | f |  | f | Com | Any | HVAC | SpaceHeat | WaterHtg_eq | Boiler_AF |  | HVAC-Blr | Hot water boiler,< 300 kBtuh; Pre-2005: 80.0 Et, No reset 2006 - 2009: 80.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 80.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 82.0 Et, OA Reset from 140 to 165 F | Hot water boiler (< 300 kBtuh, 82.0 AFUE, OA Reset from 140 to 165 F) | Hot water boiler (< 300 kBtuh, 84.0 AFUE, OA Reset from 140 to 165 F) |  | W-Boiler_AF-lt300k-0.82-fDraft | W-Boiler_AF-lt300k-0.84-fDraft |  |  | f | f |  |  |  | HVAC-Blr |  | None | 1/1/2015
Hot water | HW | < 300 | lt300 | 80 | 82 | 82 | 84.5 | AFUE |  |  |  | Drft | 2110 | 902 | NG-HVAC-Blr-HW-lt300kBtuh-84p5AFUE-Drft | Hot water boiler (< 300 kBtuh, 84.5 AFUE, OA Reset from 140 to 165 F) | DEER2016 |  | 5/15/2015 | NG-HVAC-Blr-HW-lt300kBtuh-84p5AFUE-Drft | DEER | Standard | None | 0 | 0 | None |  | f |  | f | Com | Any | HVAC | SpaceHeat | WaterHtg_eq | Boiler_AF |  | HVAC-Blr | Hot water boiler,< 300 kBtuh; Pre-2005: 80.0 Et, No reset 2006 - 2009: 80.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 80.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 82.0 Et, OA Reset from 140 to 165 F | Hot water boiler (< 300 kBtuh, 82.0 AFUE, OA Reset from 140 to 165 F) | Hot water boiler (< 300 kBtuh, 84.5 AFUE, OA Reset from 140 to 165 F) |  | W-Boiler_AF-lt300k-0.82-fDraft | W-Boiler_AF-lt300k-0.845-fDraft |  |  | f | f |  |  |  | HVAC-Blr |  | None | 1/1/2015
Hot water | HW | < 300 | lt300 | 80 | 82 | 82 | 85 | AFUE |  |  |  | Drft | 2111 | 903 | NG-HVAC-Blr-HW-lt300kBtuh-85p0AFUE-Drft | Hot water boiler (< 300 kBtuh, 85.0 AFUE, OA Reset from 140 to 165 F) | DEER2016 |  | 5/15/2015 | NG-HVAC-Blr-HW-lt300kBtuh-85p0AFUE-Drft | DEER | Standard | None | 0 | 0 | None |  | f |  | f | Com | Any | HVAC | SpaceHeat | WaterHtg_eq | Boiler_AF |  | HVAC-Blr | Hot water boiler,< 300 kBtuh; Pre-2005: 80.0 Et, No reset 2006 - 2009: 80.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 80.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 82.0 Et, OA Reset from 140 to 165 F | Hot water boiler (< 300 kBtuh, 82.0 AFUE, OA Reset from 140 to 165 F) | Hot water boiler (< 300 kBtuh, 85.0 AFUE, OA Reset from 140 to 165 F) |  | W-Boiler_AF-lt300k-0.82-fDraft | W-Boiler_AF-lt300k-0.85-fDraft |  |  | f | f |  |  |  | HVAC-Blr |  | None | 1/1/2015
Hot water | HW | < 300 | lt300 | 80 | 82 | 82 | 87 | AFUE |  |  |  | Drft | 2112 | 904 | NG-HVAC-Blr-HW-lt300kBtuh-87p0AFUE-Drft | Hot water boiler (< 300 kBtuh, 87.0 AFUE, OA Reset from 140 to 165 F) | DEER2016 |  | 5/15/2015 | NG-HVAC-Blr-HW-lt300kBtuh-87p0AFUE-Drft | DEER | Standard | None | 0 | 0 | None |  | f |  | f | Com | Any | HVAC | SpaceHeat | WaterHtg_eq | Boiler_AF |  | HVAC-Blr | Hot water boiler,< 300 kBtuh; Pre-2005: 80.0 Et, No reset 2006 - 2009: 80.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 80.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 82.0 Et, OA Reset from 140 to 165 F | Hot water boiler (< 300 kBtuh, 82.0 AFUE, OA Reset from 140 to 165 F) | Hot water boiler (< 300 kBtuh, 87.0 AFUE, OA Reset from 140 to 165 F) |  | W-Boiler_AF-lt300k-0.82-fDraft | W-Boiler_AF-lt300k-0.87-fDraft |  |  | f | f |  |  |  | HVAC-Blr |  | None | 1/1/2015
Hot water | HW | < 300 | lt300 | 80 | 82 | 82 | 90 | AFUE |  |  |  | CndStd | 2113 | 905 | NG-HVAC-Blr-HW-lt300kBtuh-90p0AFUE-CndStd | Hot water boiler (< 300 kBtuh, 90.0 AFUE, condensing, OA reset from 140 to 165 F) | DEER2016 |  | 5/15/2015 | NG-HVAC-Blr-HW-lt300kBtuh-90p0AFUE-CndStd | DEER | Standard | None | 0 | 0 | None |  | f |  | f | Com | Any | HVAC | SpaceHeat | WaterHtg_eq | Boiler_AF |  | HVAC-Blr | Hot water boiler,< 300 kBtuh; Pre-2005: 80.0 Et, No reset 2006 - 2009: 80.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 80.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 82.0 Et, OA Reset from 140 to 165 F | Hot water boiler (< 300 kBtuh, 82.0 AFUE, OA Reset from 140 to 165 F) | Hot water boiler (< 300 kBtuh, 90.0 AFUE, condensing, OA reset from 140 to 165 F) |  | W-Boiler_AF-lt300k-0.82-fDraft | W-Boiler_AF-lt300k-0.9-fDraft-CndStd |  |  | f | f |  |  |  | HVAC-Blr |  | None | 1/1/2015
Hot water | HW | < 300 | lt300 | 80 | 82 | 82 | 90 | AFUE |  |  |  | CndLow | 2114 | 906 | NG-HVAC-Blr-HW-lt300kBtuh-90p0AFUE-CndLow | Hot water boiler (< 300 kBtuh, 90.0 AFUE, condensing, OA reset from 115 to 140 F) | DEER2016 |  | 5/15/2015 | NG-HVAC-Blr-HW-lt300kBtuh-90p0AFUE-CndLow | DEER | Standard | None | 0 | 0 | None |  | f |  | f | Com | Any | HVAC | SpaceHeat | WaterHtg_eq | Boiler_AF |  | HVAC-Blr | Hot water boiler,< 300 kBtuh; Pre-2005: 80.0 Et, No reset 2006 - 2009: 80.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 80.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 82.0 Et, OA Reset from 140 to 165 F | Hot water boiler (< 300 kBtuh, 82.0 AFUE, OA Reset from 140 to 165 F) | Hot water boiler (< 300 kBtuh, 90.0 AFUE, condensing, OA reset from 115 to 140 F) |  | W-Boiler_AF-lt300k-0.82-fDraft | W-Boiler_AF-lt300k-0.9-fDraft-CndLow |  |  | f | f |  |  |  | HVAC-Blr |  | None | 1/1/2015
Hot water | HW | < 300 | lt300 | 80 | 82 | 82 | 90 | AFUE |  |  |  | CndReset | 2115 | 907 | NG-HVAC-Blr-HW-lt300kBtuh-90p0AFUE-CndReset | Hot water boiler (< 300 kBtuh, 90.0 AFUE, condensing, load reset from 115 to 140 F) | DEER2016 |  | 5/15/2015 | NG-HVAC-Blr-HW-lt300kBtuh-90p0AFUE-CndReset | DEER | Standard | None | 0 | 0 | None |  | f |  | f | Com | Any | HVAC | SpaceHeat | WaterHtg_eq | Boiler_AF |  | HVAC-Blr | Hot water boiler,< 300 kBtuh; Pre-2005: 80.0 Et, No reset 2006 - 2009: 80.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 80.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 82.0 Et, OA Reset from 140 to 165 F | Hot water boiler (< 300 kBtuh, 82.0 AFUE, OA Reset from 140 to 165 F) | Hot water boiler (< 300 kBtuh, 90.0 AFUE, condensing, load reset from 115 to 140 F) |  | W-Boiler_AF-lt300k-0.82-fDraft | W-Boiler_AF-lt300k-0.9-fDraft-CndReset |  |  | f | f |  |  |  | HVAC-Blr |  | None | 1/1/2015
Hot water | HW | < 300 | lt300 | 80 | 82 | 82 | 94 | AFUE |  |  |  | CndStd | 2116 | 908 | NG-HVAC-Blr-HW-lt300kBtuh-94p0AFUE-CndStd | Hot water boiler (< 300 kBtuh, 94.0 AFUE, condensing, OA reset from 140 to 165 F) | DEER2016 |  | 5/15/2015 | NG-HVAC-Blr-HW-lt300kBtuh-94p0AFUE-CndStd | DEER | Standard | None | 0 | 0 | None |  | f |  | f | Com | Any | HVAC | SpaceHeat | WaterHtg_eq | Boiler_AF |  | HVAC-Blr | Hot water boiler,< 300 kBtuh; Pre-2005: 80.0 Et, No reset 2006 - 2009: 80.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 80.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 82.0 Et, OA Reset from 140 to 165 F | Hot water boiler (< 300 kBtuh, 82.0 AFUE, OA Reset from 140 to 165 F) | Hot water boiler (< 300 kBtuh, 94.0 AFUE, condensing, OA reset from 140 to 165 F) |  | W-Boiler_AF-lt300k-0.82-fDraft | W-Boiler_AF-lt300k-0.94-fDraft-CndStd |  |  | f | f |  |  |  | HVAC-Blr |  | None | 1/1/2015
Hot water | HW | < 300 | lt300 | 80 | 82 | 82 | 94 | AFUE |  |  |  | CndLow | 2117 | 909 | NG-HVAC-Blr-HW-lt300kBtuh-94p0AFUE-CndLow | Hot water boiler (< 300 kBtuh, 94.0 AFUE, condensing, OA reset from 115 to 140 F) | DEER2016 |  | 5/15/2015 | NG-HVAC-Blr-HW-lt300kBtuh-94p0AFUE-CndLow | DEER | Standard | None | 0 | 0 | None |  | f |  | f | Com | Any | HVAC | SpaceHeat | WaterHtg_eq | Boiler_AF |  | HVAC-Blr | Hot water boiler,< 300 kBtuh; Pre-2005: 80.0 Et, No reset 2006 - 2009: 80.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 80.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 82.0 Et, OA Reset from 140 to 165 F | Hot water boiler (< 300 kBtuh, 82.0 AFUE, OA Reset from 140 to 165 F) | Hot water boiler (< 300 kBtuh, 94.0 AFUE, condensing, OA reset from 115 to 140 F) |  | W-Boiler_AF-lt300k-0.82-fDraft | W-Boiler_AF-lt300k-0.94-fDraft-CndLow |  |  | f | f |  |  |  | HVAC-Blr |  | None | 1/1/2015
Hot water | HW | < 300 | lt300 | 80 | 82 | 82 | 94 | AFUE |  |  |  | CndReset | 2118 | 910 | NG-HVAC-Blr-HW-lt300kBtuh-94p0AFUE-CndReset | Hot water boiler (< 300 kBtuh, 94.0 AFUE, condensing, load reset from 115 to 140 F) | DEER2016 |  | 5/15/2015 | NG-HVAC-Blr-HW-lt300kBtuh-94p0AFUE-CndReset | DEER | Standard | None | 0 | 0 | None |  | f |  | f | Com | Any | HVAC | SpaceHeat | WaterHtg_eq | Boiler_AF |  | HVAC-Blr | Hot water boiler,< 300 kBtuh; Pre-2005: 80.0 Et, No reset 2006 - 2009: 80.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 80.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 82.0 Et, OA Reset from 140 to 165 F | Hot water boiler (< 300 kBtuh, 82.0 AFUE, OA Reset from 140 to 165 F) | Hot water boiler (< 300 kBtuh, 94.0 AFUE, condensing, load reset from 115 to 140 F) |  | W-Boiler_AF-lt300k-0.82-fDraft | W-Boiler_AF-lt300k-0.94-fDraft-CndReset |  |  | f | f |  |  |  | HVAC-Blr |  | None | 1/1/2015
Hot water | HW | 300 - 2500 | 300to2500 | 75 | 80 | 80 | 83 | Et |  |  |  | Drft | 2119 | 911 | NG-HVAC-Blr-HW-300to2500kBtuh-83p0Et-Drft | Hot water boiler (300 - 2500 kBtuh, 83.0 Et, OA Reset from 140 to 165 F) | DEER2016 |  | 5/15/2015 | NG-HVAC-Blr-HW-300to2500kBtuh-83p0Et-Drft | DEER | Standard | None | 0 | 0 | None |  | f |  | f | Com | Any | HVAC | SpaceHeat | WaterHtg_eq | Boiler_Et |  | HVAC-Blr | Hot water boiler,300 - 2500 kBtuh; Pre-2005: 75.0 Et, No reset 2006 - 2009: 75.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 75.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 80.0 Et, OA Reset from 140 to 165 F | Hot water boiler (300 - 2500 kBtuh, 80.0 Et, OA Reset from 140 to 165 F) | Hot water boiler (300 - 2500 kBtuh, 83.0 Et, OA Reset from 140 to 165 F) |  | W-Boiler_Et-300to2500k-0.8-fDraft | W-Boiler_Et-300to2500k-0.83-fDraft |  |  | f | f |  |  |  | HVAC-Blr |  | None | 1/1/2015
Hot water | HW | 300 - 2500 | 300to2500 | 75 | 80 | 80 | 85 | Et |  |  |  | Drft | 2120 | 912 | NG-HVAC-Blr-HW-300to2500kBtuh-85p0Et-Drft | Hot water boiler (300 - 2500 kBtuh, 85.0 Et, OA Reset from 140 to 165 F) | DEER2016 |  | 5/15/2015 | NG-HVAC-Blr-HW-300to2500kBtuh-85p0Et-Drft | DEER | Standard | None | 0 | 0 | None |  | f |  | f | Com | Any | HVAC | SpaceHeat | WaterHtg_eq | Boiler_Et |  | HVAC-Blr | Hot water boiler,300 - 2500 kBtuh; Pre-2005: 75.0 Et, No reset 2006 - 2009: 75.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 75.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 80.0 Et, OA Reset from 140 to 165 F | Hot water boiler (300 - 2500 kBtuh, 80.0 Et, OA Reset from 140 to 165 F) | Hot water boiler (300 - 2500 kBtuh, 85.0 Et, OA Reset from 140 to 165 F) |  | W-Boiler_Et-300to2500k-0.8-fDraft | W-Boiler_Et-300to2500k-0.85-fDraft |  |  | f | f |  |  |  | HVAC-Blr |  | None | 1/1/2015
Hot water | HW | 300 - 2500 | 300to2500 | 75 | 80 | 80 | 90 | Et |  |  |  | CndStd | 2121 | 913 | NG-HVAC-Blr-HW-300to2500kBtuh-90p0Et-CndStd | Hot water boiler (300 - 2500 kBtuh, 90.0 Et, condensing, OA reset from 140 to 165 F) | DEER2016 |  | 5/15/2015 | NG-HVAC-Blr-HW-300to2500kBtuh-90p0Et-CndStd | DEER | Standard | None | 0 | 0 | None |  | f |  | f | Com | Any | HVAC | SpaceHeat | WaterHtg_eq | Boiler_Et |  | HVAC-Blr | Hot water boiler,300 - 2500 kBtuh; Pre-2005: 75.0 Et, No reset 2006 - 2009: 75.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 75.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 80.0 Et, OA Reset from 140 to 165 F | Hot water boiler (300 - 2500 kBtuh, 80.0 Et, OA Reset from 140 to 165 F) | Hot water boiler (300 - 2500 kBtuh, 90.0 Et, condensing, OA reset from 140 to 165 F) |  | W-Boiler_Et-300to2500k-0.8-fDraft | W-Boiler_Et-300to2500k-0.9-fDraft-CndStd |  |  | f | f |  |  |  | HVAC-Blr |  | None | 1/1/2015
Hot water | HW | 300 - 2500 | 300to2500 | 75 | 80 | 80 | 90 | Et |  |  |  | CndLow | 2122 | 914 | NG-HVAC-Blr-HW-300to2500kBtuh-90p0Et-CndLow | Hot water boiler (300 - 2500 kBtuh, 90.0 Et, condensing, OA reset from 115 to 140 F) | DEER2016 |  | 5/15/2015 | NG-HVAC-Blr-HW-300to2500kBtuh-90p0Et-CndLow | DEER | Standard | None | 0 | 0 | None |  | f |  | f | Com | Any | HVAC | SpaceHeat | WaterHtg_eq | Boiler_Et |  | HVAC-Blr | Hot water boiler,300 - 2500 kBtuh; Pre-2005: 75.0 Et, No reset 2006 - 2009: 75.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 75.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 80.0 Et, OA Reset from 140 to 165 F | Hot water boiler (300 - 2500 kBtuh, 80.0 Et, OA Reset from 140 to 165 F) | Hot water boiler (300 - 2500 kBtuh, 90.0 Et, condensing, OA reset from 115 to 140 F) |  | W-Boiler_Et-300to2500k-0.8-fDraft | W-Boiler_Et-300to2500k-0.9-fDraft-CndLow |  |  | f | f |  |  |  | HVAC-Blr |  | None | 1/1/2015
Hot water | HW | 300 - 2500 | 300to2500 | 75 | 80 | 80 | 90 | Et |  |  |  | CndReset | 2123 | 915 | NG-HVAC-Blr-HW-300to2500kBtuh-90p0Et-CndReset | Hot water boiler (300 - 2500 kBtuh, 90.0 Et, condensing, load reset from 115 to 140 F) | DEER2016 |  | 5/15/2015 | NG-HVAC-Blr-HW-300to2500kBtuh-90p0Et-CndReset | DEER | Standard | None | 0 | 0 | None |  | f |  | f | Com | Any | HVAC | SpaceHeat | WaterHtg_eq | Boiler_Et |  | HVAC-Blr | Hot water boiler,300 - 2500 kBtuh; Pre-2005: 75.0 Et, No reset 2006 - 2009: 75.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 75.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 80.0 Et, OA Reset from 140 to 165 F | Hot water boiler (300 - 2500 kBtuh, 80.0 Et, OA Reset from 140 to 165 F) | Hot water boiler (300 - 2500 kBtuh, 90.0 Et, condensing, load reset from 115 to 140 F) |  | W-Boiler_Et-300to2500k-0.8-fDraft | W-Boiler_Et-300to2500k-0.9-fDraft-CndReset |  |  | f | f |  |  |  | HVAC-Blr |  | None | 1/1/2015
Hot water | HW | 300 - 2500 | 300to2500 | 75 | 80 | 80 | 94 | Et |  |  |  | CndStd | 2124 | 916 | NG-HVAC-Blr-HW-300to2500kBtuh-94p0Et-CndStd | Hot water boiler (300 - 2500 kBtuh, 94.0 Et, condensing, OA reset from 140 to 165 F) | DEER2016 |  | 5/15/2015 | NG-HVAC-Blr-HW-300to2500kBtuh-94p0Et-CndStd | DEER | Standard | None | 0 | 0 | None |  | f |  | f | Com | Any | HVAC | SpaceHeat | WaterHtg_eq | Boiler_Et |  | HVAC-Blr | Hot water boiler,300 - 2500 kBtuh; Pre-2005: 75.0 Et, No reset 2006 - 2009: 75.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 75.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 80.0 Et, OA Reset from 140 to 165 F | Hot water boiler (300 - 2500 kBtuh, 80.0 Et, OA Reset from 140 to 165 F) | Hot water boiler (300 - 2500 kBtuh, 94.0 Et, condensing, OA reset from 140 to 165 F) |  | W-Boiler_Et-300to2500k-0.8-fDraft | W-Boiler_Et-300to2500k-0.94-fDraft-CndStd |  |  | f | f |  |  |  | HVAC-Blr |  | None | 1/1/2015
Hot water | HW | 300 - 2500 | 300to2500 | 75 | 80 | 80 | 94 | Et |  |  |  | CndLow | 2125 | 917 | NG-HVAC-Blr-HW-300to2500kBtuh-94p0Et-CndLow | Hot water boiler (300 - 2500 kBtuh, 94.0 Et, condensing, OA reset from 115 to 140 F) | DEER2016 |  | 5/15/2015 | NG-HVAC-Blr-HW-300to2500kBtuh-94p0Et-CndLow | DEER | Standard | None | 0 | 0 | None |  | f |  | f | Com | Any | HVAC | SpaceHeat | WaterHtg_eq | Boiler_Et |  | HVAC-Blr | Hot water boiler,300 - 2500 kBtuh; Pre-2005: 75.0 Et, No reset 2006 - 2009: 75.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 75.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 80.0 Et, OA Reset from 140 to 165 F | Hot water boiler (300 - 2500 kBtuh, 80.0 Et, OA Reset from 140 to 165 F) | Hot water boiler (300 - 2500 kBtuh, 94.0 Et, condensing, OA reset from 115 to 140 F) |  | W-Boiler_Et-300to2500k-0.8-fDraft | W-Boiler_Et-300to2500k-0.94-fDraft-CndLow |  |  | f | f |  |  |  | HVAC-Blr |  | None | 1/1/2015
Hot water | HW | 300 - 2500 | 300to2500 | 75 | 80 | 80 | 94 | Et |  |  |  | CndReset | 2126 | 918 | NG-HVAC-Blr-HW-300to2500kBtuh-94p0Et-CndReset | Hot water boiler (300 - 2500 kBtuh, 94.0 Et, condensing, load reset from 115 to 140 F) | DEER2016 |  | 5/15/2015 | NG-HVAC-Blr-HW-300to2500kBtuh-94p0Et-CndReset | DEER | Standard | None | 0 | 0 | None |  | f |  | f | Com | Any | HVAC | SpaceHeat | WaterHtg_eq | Boiler_Et |  | HVAC-Blr | Hot water boiler,300 - 2500 kBtuh; Pre-2005: 75.0 Et, No reset 2006 - 2009: 75.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 75.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 80.0 Et, OA Reset from 140 to 165 F | Hot water boiler (300 - 2500 kBtuh, 80.0 Et, OA Reset from 140 to 165 F) | Hot water boiler (300 - 2500 kBtuh, 94.0 Et, condensing, load reset from 115 to 140 F) |  | W-Boiler_Et-300to2500k-0.8-fDraft | W-Boiler_Et-300to2500k-0.94-fDraft-CndReset |  |  | f | f |  |  |  | HVAC-Blr |  | None | 1/1/2015
Hot water | HW | > 2500 | gt2500 | 75 | 80 | 80 | 83 | Et | 82 | 85 | Ec | Drft | 2127 | 919 | NG-HVAC-Blr-HW-gt2500kBtuh-83p0Et-Drft | Hot water boiler (> 2500 kBtuh, 83.0 Et, 85.0Ec, OA Reset from 140 to 165 F) | DEER2016 |  | 5/15/2015 | NG-HVAC-Blr-HW-gt2500kBtuh-83p0Et-Drft | DEER | Standard | None | 0 | 0 | None |  | f |  | f | Com | Any | HVAC | SpaceHeat | WaterHtg_eq | Boiler_Et |  | HVAC-Blr | Hot water boiler,> 2500 kBtuh; Pre-2005: 75.0 Et, No reset 2006 - 2009: 75.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 75.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 80.0 Et, OA Reset from 140 to 165 F | Hot water boiler (> 2500 kBtuh, 80.0 Et, 82.0Ec, OA Reset from 140 to 165 F) | Hot water boiler (> 2500 kBtuh, 83.0 Et, 85.0Ec, OA Reset from 140 to 165 F) |  | W-Boiler_Et-gt2500k-0.8-fDraft | W-Boiler_Et-gt2500k-0.83-fDraft |  |  | f | f |  |  |  | HVAC-Blr |  | None | 1/1/2015
Hot water | HW | > 2500 | gt2500 | 75 | 80 | 80 | 85 | Et | 82 | 87 | Ec | Drft | 2128 | 920 | NG-HVAC-Blr-HW-gt2500kBtuh-85p0Et-Drft | Hot water boiler (> 2500 kBtuh, 85.0 Et, 87.0Ec, OA Reset from 140 to 165 F) | DEER2016 |  | 5/15/2015 | NG-HVAC-Blr-HW-gt2500kBtuh-85p0Et-Drft | DEER | Standard | None | 0 | 0 | None |  | f |  | f | Com | Any | HVAC | SpaceHeat | WaterHtg_eq | Boiler_Et |  | HVAC-Blr | Hot water boiler,> 2500 kBtuh; Pre-2005: 75.0 Et, No reset 2006 - 2009: 75.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 75.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 80.0 Et, OA Reset from 140 to 165 F | Hot water boiler (> 2500 kBtuh, 80.0 Et, 82.0Ec, OA Reset from 140 to 165 F) | Hot water boiler (> 2500 kBtuh, 85.0 Et, 87.0Ec, OA Reset from 140 to 165 F) |  | W-Boiler_Et-gt2500k-0.8-fDraft | W-Boiler_Et-gt2500k-0.85-fDraft |  |  | f | f |  |  |  | HVAC-Blr |  | None | 1/1/2015
Hot water | HW | > 2500 | gt2500 | 75 | 80 | 80 | 90 | Et | 82 |  | Ec | CndStd | 2129 | 921 | NG-HVAC-Blr-HW-gt2500kBtuh-90p0Et-CndStd | Hot water boiler (> 2500 kBtuh, 90.0 Et, condensing, OA reset from 140 to 165 F) | DEER2016 |  | 5/15/2015 | NG-HVAC-Blr-HW-gt2500kBtuh-90p0Et-CndStd | DEER | Standard | None | 0 | 0 | None |  | f |  | f | Com | Any | HVAC | SpaceHeat | WaterHtg_eq | Boiler_Et |  | HVAC-Blr | Hot water boiler,> 2500 kBtuh; Pre-2005: 75.0 Et, No reset 2006 - 2009: 75.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 75.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 80.0 Et, OA Reset from 140 to 165 F | Hot water boiler (> 2500 kBtuh, 80.0 Et, 82.0Ec, OA Reset from 140 to 165 F) | Hot water boiler (> 2500 kBtuh, 90.0 Et, condensing, OA reset from 140 to 165 F) |  | W-Boiler_Et-gt2500k-0.8-fDraft | W-Boiler_Et-gt2500k-0.9-fDraft-CndStd |  |  | f | f |  |  |  | HVAC-Blr |  | None | 1/1/2015
Hot water | HW | > 2500 | gt2500 | 75 | 80 | 80 | 90 | Et | 82 |  | Ec | CndLow | 2130 | 922 | NG-HVAC-Blr-HW-gt2500kBtuh-90p0Et-CndLow | Hot water boiler (> 2500 kBtuh, 90.0 Et, condensing, OA reset from 115 to 140 F) | DEER2016 |  | 5/15/2015 | NG-HVAC-Blr-HW-gt2500kBtuh-90p0Et-CndLow | DEER | Standard | None | 0 | 0 | None |  | f |  | f | Com | Any | HVAC | SpaceHeat | WaterHtg_eq | Boiler_Et |  | HVAC-Blr | Hot water boiler,> 2500 kBtuh; Pre-2005: 75.0 Et, No reset 2006 - 2009: 75.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 75.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 80.0 Et, OA Reset from 140 to 165 F | Hot water boiler (> 2500 kBtuh, 80.0 Et, 82.0Ec, OA Reset from 140 to 165 F) | Hot water boiler (> 2500 kBtuh, 90.0 Et, condensing, OA reset from 115 to 140 F) |  | W-Boiler_Et-gt2500k-0.8-fDraft | W-Boiler_Et-gt2500k-0.9-fDraft-CndLow |  |  | f | f |  |  |  | HVAC-Blr |  | None | 1/1/2015
Hot water | HW | > 2500 | gt2500 | 75 | 80 | 80 | 90 | Et | 82 |  | Ec | CndReset | 2131 | 923 | NG-HVAC-Blr-HW-gt2500kBtuh-90p0Et-CndReset | Hot water boiler (> 2500 kBtuh, 90.0 Et, condensing, load reset from 115 to 140 F) | DEER2016 |  | 5/15/2015 | NG-HVAC-Blr-HW-gt2500kBtuh-90p0Et-CndReset | DEER | Standard | None | 0 | 0 | None |  | f |  | f | Com | Any | HVAC | SpaceHeat | WaterHtg_eq | Boiler_Et |  | HVAC-Blr | Hot water boiler,> 2500 kBtuh; Pre-2005: 75.0 Et, No reset 2006 - 2009: 75.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 75.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 80.0 Et, OA Reset from 140 to 165 F | Hot water boiler (> 2500 kBtuh, 80.0 Et, 82.0Ec, OA Reset from 140 to 165 F) | Hot water boiler (> 2500 kBtuh, 90.0 Et, condensing, load reset from 115 to 140 F) |  | W-Boiler_Et-gt2500k-0.8-fDraft | W-Boiler_Et-gt2500k-0.9-fDraft-CndReset |  |  | f | f |  |  |  | HVAC-Blr |  | None | 1/1/2015
Hot water | HW | > 2500 | gt2500 | 75 | 80 | 80 | 94 | Et | 82 |  | Ec | CndStd | 2132 | 924 | NG-HVAC-Blr-HW-gt2500kBtuh-94p0Et-CndStd | Hot water boiler (> 2500 kBtuh, 94.0 Et, condensing, OA reset from 140 to 165 F) | DEER2016 |  | 5/15/2015 | NG-HVAC-Blr-HW-gt2500kBtuh-94p0Et-CndStd | DEER | Standard | None | 0 | 0 | None |  | f |  | f | Com | Any | HVAC | SpaceHeat | WaterHtg_eq | Boiler_Et |  | HVAC-Blr | Hot water boiler,> 2500 kBtuh; Pre-2005: 75.0 Et, No reset 2006 - 2009: 75.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 75.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 80.0 Et, OA Reset from 140 to 165 F | Hot water boiler (> 2500 kBtuh, 80.0 Et, 82.0Ec, OA Reset from 140 to 165 F) | Hot water boiler (> 2500 kBtuh, 94.0 Et, condensing, OA reset from 140 to 165 F) |  | W-Boiler_Et-gt2500k-0.8-fDraft | W-Boiler_Et-gt2500k-0.94-fDraft-CndStd |  |  | f | f |  |  |  | HVAC-Blr |  | None | 1/1/2015
Hot water | HW | > 2500 | gt2500 | 75 | 80 | 80 | 94 | Et | 82 |  | Ec | CndLow | 2133 | 925 | NG-HVAC-Blr-HW-gt2500kBtuh-94p0Et-CndLow | Hot water boiler (> 2500 kBtuh, 94.0 Et, condensing, OA reset from 115 to 140 F) | DEER2016 |  | 5/15/2015 | NG-HVAC-Blr-HW-gt2500kBtuh-94p0Et-CndLow | DEER | Standard | None | 0 | 0 | None |  | f |  | f | Com | Any | HVAC | SpaceHeat | WaterHtg_eq | Boiler_Et |  | HVAC-Blr | Hot water boiler,> 2500 kBtuh; Pre-2005: 75.0 Et, No reset 2006 - 2009: 75.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 75.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 80.0 Et, OA Reset from 140 to 165 F | Hot water boiler (> 2500 kBtuh, 80.0 Et, 82.0Ec, OA Reset from 140 to 165 F) | Hot water boiler (> 2500 kBtuh, 94.0 Et, condensing, OA reset from 115 to 140 F) |  | W-Boiler_Et-gt2500k-0.8-fDraft | W-Boiler_Et-gt2500k-0.94-fDraft-CndLow |  |  | f | f |  |  |  | HVAC-Blr |  | None | 1/1/2015
Hot water | HW | > 2500 | gt2500 | 75 | 80 | 80 | 94 | Et | 82 |  | Ec | CndReset | 2134 | 926 | NG-HVAC-Blr-HW-gt2500kBtuh-94p0Et-CndReset | Hot water boiler (> 2500 kBtuh, 94.0 Et, condensing, load reset from 115 to 140 F) | DEER2016 |  | 5/15/2015 | NG-HVAC-Blr-HW-gt2500kBtuh-94p0Et-CndReset | DEER | Standard | None | 0 | 0 | None |  | f |  | f | Com | Any | HVAC | SpaceHeat | WaterHtg_eq | Boiler_Et |  | HVAC-Blr | Hot water boiler,> 2500 kBtuh; Pre-2005: 75.0 Et, No reset 2006 - 2009: 75.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 75.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 80.0 Et, OA Reset from 140 to 165 F | Hot water boiler (> 2500 kBtuh, 80.0 Et, 82.0Ec, OA Reset from 140 to 165 F) | Hot water boiler (> 2500 kBtuh, 94.0 Et, condensing, load reset from 115 to 140 F) |  | W-Boiler_Et-gt2500k-0.8-fDraft | W-Boiler_Et-gt2500k-0.94-fDraft-CndReset |  |  | f | f |  |  |  | HVAC-Blr |  | None | 1/1/2015
Steam | Stm | < 300 | lt300 | 75 | 80 | 80 | 82 | AFUE |  |  |  | Drft | 2135 | 927 | NG-HVAC-Blr-Stm-lt300kBtuh-82p0AFUE-Drft | Steam boiler (< 300 kBtuh, 82.0 AFUE, OA Reset from 140 to 165 F) | DEER2016 |  | 5/15/2015 | NG-HVAC-Blr-Stm-lt300kBtuh-82p0AFUE-Drft | DEER | Standard | None | 0 | 0 | None |  | f |  | f | Com | Any | HVAC | SpaceHeat | SteamHtg_eq | Boiler_AF |  | HVAC-Blr | Steam boiler,< 300 kBtuh; Pre-2005: 75.0 Et, No reset 2006 - 2009: 75.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 75.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 80.0 Et, OA Reset from 140 to 165 F | Steam boiler (< 300 kBtuh, 80.0 AFUE, OA Reset from 140 to 165 F) | Steam boiler (< 300 kBtuh, 82.0 AFUE, OA Reset from 140 to 165 F) |  | S-Boiler_AF-lt300k-0.8-fDraft | S-Boiler_AF-lt300k-0.82-fDraft |  |  | f | f |  |  |  | HVAC-Blr |  | None | 1/1/2015
Steam | Stm | < 300 | lt300 | 75 | 80 | 80 | 83 | AFUE |  |  |  | Drft | 2136 | 928 | NG-HVAC-Blr-Stm-lt300kBtuh-83p0AFUE-Drft | Steam boiler (< 300 kBtuh, 83.0 AFUE, OA Reset from 140 to 165 F) | DEER2016 |  | 5/15/2015 | NG-HVAC-Blr-Stm-lt300kBtuh-83p0AFUE-Drft | DEER | Standard | None | 0 | 0 | None |  | f |  | f | Com | Any | HVAC | SpaceHeat | SteamHtg_eq | Boiler_AF |  | HVAC-Blr | Steam boiler,< 300 kBtuh; Pre-2005: 75.0 Et, No reset 2006 - 2009: 75.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 75.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 80.0 Et, OA Reset from 140 to 165 F | Steam boiler (< 300 kBtuh, 80.0 AFUE, OA Reset from 140 to 165 F) | Steam boiler (< 300 kBtuh, 83.0 AFUE, OA Reset from 140 to 165 F) |  | S-Boiler_AF-lt300k-0.8-fDraft | S-Boiler_AF-lt300k-0.83-fDraft |  |  | f | f |  |  |  | HVAC-Blr |  | None | 1/1/2015
Steam | Stm | 300 - 2500 | 300to2500 | 75 | 79 | 79 | 81 | Et |  |  |  | Drft | 2137 | 929 | NG-HVAC-Blr-Stm-300to2500kBtuh-81p0Et-Drft | Steam boiler (300 - 2500 kBtuh, 81.0 Et, OA Reset from 140 to 165 F) | DEER2016 |  | 5/15/2015 | NG-HVAC-Blr-Stm-300to2500kBtuh-81p0Et-Drft | DEER | Standard | None | 0 | 0 | None |  | f |  | f | Com | Any | HVAC | SpaceHeat | SteamHtg_eq | Boiler_Et |  | HVAC-Blr | Steam boiler,300 - 2500 kBtuh; Pre-2005: 75.0 Et, No reset 2006 - 2009: 75.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 75.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 79.0 Et, OA Reset from 140 to 165 F | Steam boiler (300 - 2500 kBtuh, 79.0 Et, OA Reset from 140 to 165 F) | Steam boiler (300 - 2500 kBtuh, 81.0 Et, OA Reset from 140 to 165 F) |  | S-Boiler_Et-300to2500k-0.79-fDraft | S-Boiler_Et-300to2500k-0.81-fDraft |  |  | f | f |  |  |  | HVAC-Blr |  | None | 1/1/2015
Steam | Stm | 300 - 2500 | 300to2500 | 75 | 79 | 79 | 82 | Et |  |  |  | Drft | 2138 | 930 | NG-HVAC-Blr-Stm-300to2500kBtuh-82p0Et-Drft | Steam boiler (300 - 2500 kBtuh, 82.0 Et, OA Reset from 140 to 165 F) | DEER2016 |  | 5/15/2015 | NG-HVAC-Blr-Stm-300to2500kBtuh-82p0Et-Drft | DEER | Standard | None | 0 | 0 | None |  | f |  | f | Com | Any | HVAC | SpaceHeat | SteamHtg_eq | Boiler_Et |  | HVAC-Blr | Steam boiler,300 - 2500 kBtuh; Pre-2005: 75.0 Et, No reset 2006 - 2009: 75.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 75.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 79.0 Et, OA Reset from 140 to 165 F | Steam boiler (300 - 2500 kBtuh, 79.0 Et, OA Reset from 140 to 165 F) | Steam boiler (300 - 2500 kBtuh, 82.0 Et, OA Reset from 140 to 165 F) |  | S-Boiler_Et-300to2500k-0.79-fDraft | S-Boiler_Et-300to2500k-0.82-fDraft |  |  | f | f |  |  |  | HVAC-Blr |  | None | 1/1/2015
Steam | Stm | > 2500 | gt2500 | 75 | 79 | 79 | 80 | Et |  |  |  | Drft | 2139 | 931 | NG-HVAC-Blr-Stm-gt2500kBtuh-80p0Et-Drft | Steam boiler (> 2500 kBtuh, 80.0 Et, OA Reset from 140 to 165 F) | DEER2016 |  | 5/15/2015 | NG-HVAC-Blr-Stm-gt2500kBtuh-80p0Et-Drft | DEER | Standard | None | 0 | 0 | None |  | f |  | f | Com | Any | HVAC | SpaceHeat | SteamHtg_eq | Boiler_Et |  | HVAC-Blr | Steam boiler,> 2500 kBtuh; Pre-2005: 75.0 Et, No reset 2006 - 2009: 75.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 75.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 79.0 Et, OA Reset from 140 to 165 F | Steam boiler (> 2500 kBtuh, 79.0 Et, 82.0Ec, OA Reset from 140 to 165 F) | Steam boiler (> 2500 kBtuh, 80.0 Et, OA Reset from 140 to 165 F) |  | S-Boiler_Et-gt2500k-0.79-fDraft | S-Boiler_Et-gt2500k-0.8-fDraft |  |  | f | f |  |  |  | HVAC-Blr |  | None | 1/1/2015
Steam | Stm | > 2500 | gt2500 | 75 | 79 | 79 | 81 | Et |  |  |  | Drft | 2140 | 932 | NG-HVAC-Blr-Stm-gt2500kBtuh-81p0Et-Drft | Steam boiler (> 2500 kBtuh, 81.0 Et, OA Reset from 140 to 165 F) | DEER2016 |  | 5/15/2015 | NG-HVAC-Blr-Stm-gt2500kBtuh-81p0Et-Drft | DEER | Standard | None | 0 | 0 | None |  | f |  | f | Com | Any | HVAC | SpaceHeat | SteamHtg_eq | Boiler_Et |  | HVAC-Blr | Steam boiler,> 2500 kBtuh; Pre-2005: 75.0 Et, No reset 2006 - 2009: 75.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 75.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 79.0 Et, OA Reset from 140 to 165 F | Steam boiler (> 2500 kBtuh, 79.0 Et, 82.0Ec, OA Reset from 140 to 165 F) | Steam boiler (> 2500 kBtuh, 81.0 Et, OA Reset from 140 to 165 F) |  | S-Boiler_Et-gt2500k-0.79-fDraft | S-Boiler_Et-gt2500k-0.81-fDraft |  |  | f | f |  |  |  | HVAC-Blr |  | None | 1/1/2015
Steam | Stm | > 2500 | gt2500 | 75 | 79 | 79 | 82 | Et |  |  |  | Drft | 2141 | 933 | NG-HVAC-Blr-Stm-gt2500kBtuh-82p0Et-Drft | Steam boiler (> 2500 kBtuh, 82.0 Et, OA Reset from 140 to 165 F) | DEER2016 |  | 5/15/2015 | NG-HVAC-Blr-Stm-gt2500kBtuh-82p0Et-Drft | DEER | Standard | None | 0 | 0 | None |  | f |  | f | Com | Any | HVAC | SpaceHeat | SteamHtg_eq | Boiler_Et |  | HVAC-Blr | Steam boiler,> 2500 kBtuh; Pre-2005: 75.0 Et, No reset 2006 - 2009: 75.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 75.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 79.0 Et, OA Reset from 140 to 165 F | Steam boiler (> 2500 kBtuh, 79.0 Et, 82.0Ec, OA Reset from 140 to 165 F) | Steam boiler (> 2500 kBtuh, 82.0 Et, OA Reset from 140 to 165 F) |  | S-Boiler_Et-gt2500k-0.79-fDraft | S-Boiler_Et-gt2500k-0.82-fDraft |  |  | f | f |  |  |  | HVAC-Blr |  | None | 1/1/2015

## Technologies
DEER2015 HVAC Technology Definitions
This table defines the key equipment parameters for all technologies referenced by the updated measures.
LookupID | Vint |  |  | UnitID | TechID | Version | Case | Type | CapRange | Effic | Units | AltEffic | AltUnits | Draft | Condensing | TempCtrl | Technology Description |  | Pre-existing technology Description | Pre-2005 | 2006 - 2009 | 2010 - 2013 | 2014 - 2015
StanHWlt300 | Any | Drft | lt300 |  | W-Boiler_AF-lt300k-0.82-fDraft |  | Standard | HW | < 300 | 82 | AFUE |  |  | fDraft | no | OA Reset from 140 to 165 F | Hot water boiler (< 300 kBtuh, 82.0 AFUE, OA Reset from 140 to 165 F) | HW_lt300 | Hot water boiler,< 300 kBtuh; Pre-2005: 80.0 Et, No reset 2006 - 2009: 80.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 80.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 82.0 Et, OA Reset from 140 to 165 F | Pre-2005: 80.0 Et, No reset | 2006 - 2009: 80.0 Et, OA Reset from 140 to 165 F | 2010 - 2013: 80.0 Et, OA Reset from 140 to 165 F | 2014 - 2015: 82.0 Et, OA Reset from 140 to 165 F
StanHW300to2500 | Any | Drft | 300to2500 |  | W-Boiler_Et-300to2500k-0.8-fDraft |  | Standard | HW | 300 - 2500 | 80 | Et |  |  | fDraft | no | OA Reset from 140 to 165 F | Hot water boiler (300 - 2500 kBtuh, 80.0 Et, OA Reset from 140 to 165 F) | HW_300to2500 | Hot water boiler,300 - 2500 kBtuh; Pre-2005: 75.0 Et, No reset 2006 - 2009: 75.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 75.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 80.0 Et, OA Reset from 140 to 165 F | Pre-2005: 75.0 Et, No reset | 2006 - 2009: 75.0 Et, OA Reset from 140 to 165 F | 2010 - 2013: 75.0 Et, OA Reset from 140 to 165 F | 2014 - 2015: 80.0 Et, OA Reset from 140 to 165 F
StanHWgt2500 | Any | Drft | gt2500 |  | W-Boiler_Et-gt2500k-0.8-fDraft |  | Standard | HW | > 2500 | 80 | Et | 82 | Ec | fDraft | no | OA Reset from 140 to 165 F | Hot water boiler (> 2500 kBtuh, 80.0 Et, 82.0Ec, OA Reset from 140 to 165 F) | HW_gt2500 | Hot water boiler,> 2500 kBtuh; Pre-2005: 75.0 Et, No reset 2006 - 2009: 75.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 75.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 80.0 Et, OA Reset from 140 to 165 F | Pre-2005: 75.0 Et, No reset | 2006 - 2009: 75.0 Et, OA Reset from 140 to 165 F | 2010 - 2013: 75.0 Et, OA Reset from 140 to 165 F | 2014 - 2015: 80.0 Et, OA Reset from 140 to 165 F
StanStmlt300 | Any | Drft | lt300 |  | S-Boiler_AF-lt300k-0.8-fDraft |  | Standard | Stm | < 300 | 80 | AFUE |  |  | fDraft | no | OA Reset from 140 to 165 F | Steam boiler (< 300 kBtuh, 80.0 AFUE, OA Reset from 140 to 165 F) | Stm_lt300 | Steam boiler,< 300 kBtuh; Pre-2005: 75.0 Et, No reset 2006 - 2009: 75.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 75.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 80.0 Et, OA Reset from 140 to 165 F | Pre-2005: 75.0 Et, No reset | 2006 - 2009: 75.0 Et, OA Reset from 140 to 165 F | 2010 - 2013: 75.0 Et, OA Reset from 140 to 165 F | 2014 - 2015: 80.0 Et, OA Reset from 140 to 165 F
StanStm300to2500 | Any | Drft | 300to2500 |  | S-Boiler_Et-300to2500k-0.79-fDraft |  | Standard | Stm | 300 - 2500 | 79 | Et |  |  | fDraft | no | OA Reset from 140 to 165 F | Steam boiler (300 - 2500 kBtuh, 79.0 Et, OA Reset from 140 to 165 F) | Stm_300to2500 | Steam boiler,300 - 2500 kBtuh; Pre-2005: 75.0 Et, No reset 2006 - 2009: 75.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 75.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 79.0 Et, OA Reset from 140 to 165 F | Pre-2005: 75.0 Et, No reset | 2006 - 2009: 75.0 Et, OA Reset from 140 to 165 F | 2010 - 2013: 75.0 Et, OA Reset from 140 to 165 F | 2014 - 2015: 79.0 Et, OA Reset from 140 to 165 F
StanStmgt2500 | Any | Drft | gt2500 |  | S-Boiler_Et-gt2500k-0.79-fDraft |  | Standard | Stm | > 2500 | 79 | Et | 82 | Ec | fDraft | no | OA Reset from 140 to 165 F | Steam boiler (> 2500 kBtuh, 79.0 Et, 82.0Ec, OA Reset from 140 to 165 F) | Stm_gt2500 | Steam boiler,> 2500 kBtuh; Pre-2005: 75.0 Et, No reset 2006 - 2009: 75.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 75.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 79.0 Et, OA Reset from 140 to 165 F | Pre-2005: 75.0 Et, No reset | 2006 - 2009: 75.0 Et, OA Reset from 140 to 165 F | 2010 - 2013: 75.0 Et, OA Reset from 140 to 165 F | 2014 - 2015: 79.0 Et, OA Reset from 140 to 165 F
MeasHWlt300_84Drft | Any | Drft | lt300 |  | W-Boiler_AF-lt300k-0.84-fDraft |  | Measure | HW | < 300 | 84 | AFUE |  |  | fDraft | no | OA Reset from 140 to 165 F | Hot water boiler (< 300 kBtuh, 84.0 AFUE, OA Reset from 140 to 165 F)
MeasHWlt300_84.5Drft | Any | Drft | lt300 |  | W-Boiler_AF-lt300k-0.845-fDraft |  | Measure | HW | < 300 | 84.5 | AFUE |  |  | fDraft | no | OA Reset from 140 to 165 F | Hot water boiler (< 300 kBtuh, 84.5 AFUE, OA Reset from 140 to 165 F)
MeasHWlt300_85Drft | Any | Drft | lt300 |  | W-Boiler_AF-lt300k-0.85-fDraft |  | Measure | HW | < 300 | 85 | AFUE |  |  | fDraft | no | OA Reset from 140 to 165 F | Hot water boiler (< 300 kBtuh, 85.0 AFUE, OA Reset from 140 to 165 F)
MeasHWlt300_87Drft | Any | Drft | lt300 |  | W-Boiler_AF-lt300k-0.87-fDraft |  | Measure | HW | < 300 | 87 | AFUE |  |  | fDraft | no | OA Reset from 140 to 165 F | Hot water boiler (< 300 kBtuh, 87.0 AFUE, OA Reset from 140 to 165 F)
MeasHWlt300_90CndStd | Any | CndStd | lt300 |  | W-Boiler_AF-lt300k-0.9-fDraft-CndStd |  | Measure | HW | < 300 | 90 | AFUE |  |  | fDraft | yes | condensing, OA reset from 140 to 165 F | Hot water boiler (< 300 kBtuh, 90.0 AFUE, condensing, OA reset from 140 to 165 F)
MeasHWlt300_90CndLow | Any | CndLow | lt300 |  | W-Boiler_AF-lt300k-0.9-fDraft-CndLow |  | Measure | HW | < 300 | 90 | AFUE |  |  | fDraft | yes | condensing, OA reset from 115 to 140 F | Hot water boiler (< 300 kBtuh, 90.0 AFUE, condensing, OA reset from 115 to 140 F)
MeasHWlt300_90CndReset | Any | CndReset | lt300 |  | W-Boiler_AF-lt300k-0.9-fDraft-CndReset |  | Measure | HW | < 300 | 90 | AFUE |  |  | fDraft | yes | condensing, load reset from 115 to 140 F | Hot water boiler (< 300 kBtuh, 90.0 AFUE, condensing, load reset from 115 to 140 F)
MeasHWlt300_94CndStd | Any | CndStd | lt300 |  | W-Boiler_AF-lt300k-0.94-fDraft-CndStd |  | Measure | HW | < 300 | 94 | AFUE |  |  | fDraft | yes | condensing, OA reset from 140 to 165 F | Hot water boiler (< 300 kBtuh, 94.0 AFUE, condensing, OA reset from 140 to 165 F)
MeasHWlt300_94CndLow | Any | CndLow | lt300 |  | W-Boiler_AF-lt300k-0.94-fDraft-CndLow |  | Measure | HW | < 300 | 94 | AFUE |  |  | fDraft | yes | condensing, OA reset from 115 to 140 F | Hot water boiler (< 300 kBtuh, 94.0 AFUE, condensing, OA reset from 115 to 140 F)
MeasHWlt300_94CndReset | Any | CndReset | lt300 |  | W-Boiler_AF-lt300k-0.94-fDraft-CndReset |  | Measure | HW | < 300 | 94 | AFUE |  |  | fDraft | yes | condensing, load reset from 115 to 140 F | Hot water boiler (< 300 kBtuh, 94.0 AFUE, condensing, load reset from 115 to 140 F)
MeasHW300to2500_83Drft | Any | Drft | 300to2500 |  | W-Boiler_Et-300to2500k-0.83-fDraft |  | Measure | HW | 300 - 2500 | 83 | Et |  |  | fDraft | no | OA Reset from 140 to 165 F | Hot water boiler (300 - 2500 kBtuh, 83.0 Et, OA Reset from 140 to 165 F)
MeasHW300to2500_85Drft | Any | Drft | 300to2500 |  | W-Boiler_Et-300to2500k-0.85-fDraft |  | Measure | HW | 300 - 2500 | 85 | Et |  |  | fDraft | no | OA Reset from 140 to 165 F | Hot water boiler (300 - 2500 kBtuh, 85.0 Et, OA Reset from 140 to 165 F)
MeasHW300to2500_90CndStd | Any | CndStd | 300to2500 |  | W-Boiler_Et-300to2500k-0.9-fDraft-CndStd |  | Measure | HW | 300 - 2500 | 90 | Et |  |  | fDraft | yes | condensing, OA reset from 140 to 165 F | Hot water boiler (300 - 2500 kBtuh, 90.0 Et, condensing, OA reset from 140 to 165 F)
MeasHW300to2500_90CndLow | Any | CndLow | 300to2500 |  | W-Boiler_Et-300to2500k-0.9-fDraft-CndLow |  | Measure | HW | 300 - 2500 | 90 | Et |  |  | fDraft | yes | condensing, OA reset from 115 to 140 F | Hot water boiler (300 - 2500 kBtuh, 90.0 Et, condensing, OA reset from 115 to 140 F)
MeasHW300to2500_90CndReset | Any | CndReset | 300to2500 |  | W-Boiler_Et-300to2500k-0.9-fDraft-CndReset |  | Measure | HW | 300 - 2500 | 90 | Et |  |  | fDraft | yes | condensing, load reset from 115 to 140 F | Hot water boiler (300 - 2500 kBtuh, 90.0 Et, condensing, load reset from 115 to 140 F)
MeasHW300to2500_94CndStd | Any | CndStd | 300to2500 |  | W-Boiler_Et-300to2500k-0.94-fDraft-CndStd |  | Measure | HW | 300 - 2500 | 94 | Et |  |  | fDraft | yes | condensing, OA reset from 140 to 165 F | Hot water boiler (300 - 2500 kBtuh, 94.0 Et, condensing, OA reset from 140 to 165 F)
MeasHW300to2500_94CndLow | Any | CndLow | 300to2500 |  | W-Boiler_Et-300to2500k-0.94-fDraft-CndLow |  | Measure | HW | 300 - 2500 | 94 | Et |  |  | fDraft | yes | condensing, OA reset from 115 to 140 F | Hot water boiler (300 - 2500 kBtuh, 94.0 Et, condensing, OA reset from 115 to 140 F)
MeasHW300to2500_94CndReset | Any | CndReset | 300to2500 |  | W-Boiler_Et-300to2500k-0.94-fDraft-CndReset |  | Measure | HW | 300 - 2500 | 94 | Et |  |  | fDraft | yes | condensing, load reset from 115 to 140 F | Hot water boiler (300 - 2500 kBtuh, 94.0 Et, condensing, load reset from 115 to 140 F)
MeasHWgt2500_83Drft | Any | Drft | gt2500 |  | W-Boiler_Et-gt2500k-0.83-fDraft |  | Measure | HW | > 2500 | 83 | Et | 85 | Ec | fDraft | no | OA Reset from 140 to 165 F | Hot water boiler (> 2500 kBtuh, 83.0 Et, 85.0Ec, OA Reset from 140 to 165 F)
MeasHWgt2500_85Drft | Any | Drft | gt2500 |  | W-Boiler_Et-gt2500k-0.85-fDraft |  | Measure | HW | > 2500 | 85 | Et | 87 | Ec | fDraft | no | OA Reset from 140 to 165 F | Hot water boiler (> 2500 kBtuh, 85.0 Et, 87.0Ec, OA Reset from 140 to 165 F)
MeasHWgt2500_90CndStd | Any | CndStd | gt2500 |  | W-Boiler_Et-gt2500k-0.9-fDraft-CndStd |  | Measure | HW | > 2500 | 90 | Et |  | Ec | fDraft | yes | condensing, OA reset from 140 to 165 F | Hot water boiler (> 2500 kBtuh, 90.0 Et, condensing, OA reset from 140 to 165 F)
MeasHWgt2500_90CndLow | Any | CndLow | gt2500 |  | W-Boiler_Et-gt2500k-0.9-fDraft-CndLow |  | Measure | HW | > 2500 | 90 | Et |  | Ec | fDraft | yes | condensing, OA reset from 115 to 140 F | Hot water boiler (> 2500 kBtuh, 90.0 Et, condensing, OA reset from 115 to 140 F)
MeasHWgt2500_90CndReset | Any | CndReset | gt2500 |  | W-Boiler_Et-gt2500k-0.9-fDraft-CndReset |  | Measure | HW | > 2500 | 90 | Et |  | Ec | fDraft | yes | condensing, load reset from 115 to 140 F | Hot water boiler (> 2500 kBtuh, 90.0 Et, condensing, load reset from 115 to 140 F)
MeasHWgt2500_94CndStd | Any | CndStd | gt2500 |  | W-Boiler_Et-gt2500k-0.94-fDraft-CndStd |  | Measure | HW | > 2500 | 94 | Et |  | Ec | fDraft | yes | condensing, OA reset from 140 to 165 F | Hot water boiler (> 2500 kBtuh, 94.0 Et, condensing, OA reset from 140 to 165 F)
MeasHWgt2500_94CndLow | Any | CndLow | gt2500 |  | W-Boiler_Et-gt2500k-0.94-fDraft-CndLow |  | Measure | HW | > 2500 | 94 | Et |  | Ec | fDraft | yes | condensing, OA reset from 115 to 140 F | Hot water boiler (> 2500 kBtuh, 94.0 Et, condensing, OA reset from 115 to 140 F)
MeasHWgt2500_94CndReset | Any | CndReset | gt2500 |  | W-Boiler_Et-gt2500k-0.94-fDraft-CndReset |  | Measure | HW | > 2500 | 94 | Et |  | Ec | fDraft | yes | condensing, load reset from 115 to 140 F | Hot water boiler (> 2500 kBtuh, 94.0 Et, condensing, load reset from 115 to 140 F)
MeasStmlt300_82Drft | Any | Drft | lt300 |  | S-Boiler_AF-lt300k-0.82-fDraft |  | Measure | Stm | < 300 | 82 | AFUE |  |  | fDraft | no | OA Reset from 140 to 165 F | Steam boiler (< 300 kBtuh, 82.0 AFUE, OA Reset from 140 to 165 F)
MeasStmlt300_83Drft | Any | Drft | lt300 |  | S-Boiler_AF-lt300k-0.83-fDraft |  | Measure | Stm | < 300 | 83 | AFUE |  |  | fDraft | no | OA Reset from 140 to 165 F | Steam boiler (< 300 kBtuh, 83.0 AFUE, OA Reset from 140 to 165 F)
MeasStm300to2500_81Drft | Any | Drft | 300to2500 |  | S-Boiler_Et-300to2500k-0.81-fDraft |  | Measure | Stm | 300 - 2500 | 81 | Et |  |  | fDraft | no | OA Reset from 140 to 165 F | Steam boiler (300 - 2500 kBtuh, 81.0 Et, OA Reset from 140 to 165 F)
MeasStm300to2500_82Drft | Any | Drft | 300to2500 |  | S-Boiler_Et-300to2500k-0.82-fDraft |  | Measure | Stm | 300 - 2500 | 82 | Et |  |  | fDraft | no | OA Reset from 140 to 165 F | Steam boiler (300 - 2500 kBtuh, 82.0 Et, OA Reset from 140 to 165 F)
MeasStmgt2500_80Drft | Any | Drft | gt2500 |  | S-Boiler_Et-gt2500k-0.8-fDraft |  | Measure | Stm | > 2500 | 80 | Et |  |  | fDraft | no | OA Reset from 140 to 165 F | Steam boiler (> 2500 kBtuh, 80.0 Et, OA Reset from 140 to 165 F)
MeasStmgt2500_81Drft | Any | Drft | gt2500 |  | S-Boiler_Et-gt2500k-0.81-fDraft |  | Measure | Stm | > 2500 | 81 | Et |  |  | fDraft | no | OA Reset from 140 to 165 F | Steam boiler (> 2500 kBtuh, 81.0 Et, OA Reset from 140 to 165 F)
MeasStmgt2500_82Drft | Any | Drft | gt2500 |  | S-Boiler_Et-gt2500k-0.82-fDraft |  | Measure | Stm | > 2500 | 82 | Et |  |  | fDraft | no | OA Reset from 140 to 165 F | Steam boiler (> 2500 kBtuh, 82.0 Et, OA Reset from 140 to 165 F)
Pre-HWlt300 | Pre-2005 | Drft | lt300 |  | W-Boiler_Et-lt300k-0.8-fDraft |  | Pre-2005 | HW | < 300 | 80 | Et |  |  | fDraft | no | No reset | Hot water boiler (< 300 kBtuh, 80.0 Et, No reset) | HWlt300Pre-2005 | Pre-2005: 80.0 Et, No reset
2006HWlt300 | 2006 - 2009 | Drft | lt300 |  | W-Boiler_Et-lt300k-0.8-fDraft |  | 2006 - 2009 | HW | < 300 | 80 | Et |  |  | fDraft | no | OA Reset from 140 to 165 F | Hot water boiler (< 300 kBtuh, 80.0 Et, OA Reset from 140 to 165 F) | HWlt3002006 - 2009 | 2006 - 2009: 80.0 Et, OA Reset from 140 to 165 F
2010HWlt300 | 2010 - 2013 | Drft | lt300 |  | W-Boiler_Et-lt300k-0.8-fDraft |  | 2010 - 2013 | HW | < 300 | 80 | Et |  |  | fDraft | no | OA Reset from 140 to 165 F | Hot water boiler (< 300 kBtuh, 80.0 Et, OA Reset from 140 to 165 F) | HWlt3002010 - 2013 | 2010 - 2013: 80.0 Et, OA Reset from 140 to 165 F
2014HWlt300 | 2014 - 2015 | Drft | lt300 |  | W-Boiler_Et-lt300k-0.82-fDraft |  | 2014 - 2015 | HW | < 300 | 82 | Et |  |  | fDraft | no | OA Reset from 140 to 165 F | Hot water boiler (< 300 kBtuh, 82.0 Et, OA Reset from 140 to 165 F) | HWlt3002014 - 2015 | 2014 - 2015: 82.0 Et, OA Reset from 140 to 165 F
Pre-HW300to2500 | Pre-2005 | Drft | 300to2500 |  | W-Boiler_Et-300to2500k-0.75-fDraft |  | Pre-2005 | HW | 300 - 2500 | 75 | Et |  |  | fDraft | no | No reset | Hot water boiler (300 - 2500 kBtuh, 75.0 Et, No reset) | HW300to2500Pre-2005 | Pre-2005: 75.0 Et, No reset
2006HW300to2500 | 2006 - 2009 | Drft | 300to2500 |  | W-Boiler_Et-300to2500k-0.75-fDraft |  | 2006 - 2009 | HW | 300 - 2500 | 75 | Et |  |  | fDraft | no | OA Reset from 140 to 165 F | Hot water boiler (300 - 2500 kBtuh, 75.0 Et, OA Reset from 140 to 165 F) | HW300to25002006 - 2009 | 2006 - 2009: 75.0 Et, OA Reset from 140 to 165 F
2010HW300to2500 | 2010 - 2013 | Drft | 300to2500 |  | W-Boiler_Et-300to2500k-0.75-fDraft |  | 2010 - 2013 | HW | 300 - 2500 | 75 | Et |  |  | fDraft | no | OA Reset from 140 to 165 F | Hot water boiler (300 - 2500 kBtuh, 75.0 Et, OA Reset from 140 to 165 F) | HW300to25002010 - 2013 | 2010 - 2013: 75.0 Et, OA Reset from 140 to 165 F
2014HW300to2500 | 2014 - 2015 | Drft | 300to2500 |  | W-Boiler_Et-300to2500k-0.8-fDraft |  | 2014 - 2015 | HW | 300 - 2500 | 80 | Et |  |  | fDraft | no | OA Reset from 140 to 165 F | Hot water boiler (300 - 2500 kBtuh, 80.0 Et, OA Reset from 140 to 165 F) | HW300to25002014 - 2015 | 2014 - 2015: 80.0 Et, OA Reset from 140 to 165 F
Pre-HWgt2500 | Pre-2005 | Drft | gt2500 |  | W-Boiler_Et-gt2500k-0.75-fDraft |  | Pre-2005 | HW | > 2500 | 75 | Et |  |  | fDraft | no | No reset | Hot water boiler (> 2500 kBtuh, 75.0 Et, No reset) | HWgt2500Pre-2005 | Pre-2005: 75.0 Et, No reset
2006HWgt2500 | 2006 - 2009 | Drft | gt2500 |  | W-Boiler_Et-gt2500k-0.75-fDraft |  | 2006 - 2009 | HW | > 2500 | 75 | Et |  |  | fDraft | no | OA Reset from 140 to 165 F | Hot water boiler (> 2500 kBtuh, 75.0 Et, OA Reset from 140 to 165 F) | HWgt25002006 - 2009 | 2006 - 2009: 75.0 Et, OA Reset from 140 to 165 F
2010HWgt2500 | 2010 - 2013 | Drft | gt2500 |  | W-Boiler_Et-gt2500k-0.75-fDraft |  | 2010 - 2013 | HW | > 2500 | 75 | Et |  |  | fDraft | no | OA Reset from 140 to 165 F | Hot water boiler (> 2500 kBtuh, 75.0 Et, OA Reset from 140 to 165 F) | HWgt25002010 - 2013 | 2010 - 2013: 75.0 Et, OA Reset from 140 to 165 F
2014HWgt2500 | 2014 - 2015 | Drft | gt2500 |  | W-Boiler_Et-gt2500k-0.8-fDraft |  | 2014 - 2015 | HW | > 2500 | 80 | Et |  |  | fDraft | no | OA Reset from 140 to 165 F | Hot water boiler (> 2500 kBtuh, 80.0 Et, OA Reset from 140 to 165 F) | HWgt25002014 - 2015 | 2014 - 2015: 80.0 Et, OA Reset from 140 to 165 F
Pre-Stmlt300 | Pre-2005 | Drft | lt300 |  | S-Boiler_Et-lt300k-0.75-fDraft |  | Pre-2005 | Stm | < 300 | 75 | Et |  |  | fDraft | no | No reset | Steam boiler (< 300 kBtuh, 75.0 Et, No reset) | Stmlt300Pre-2005 | Pre-2005: 75.0 Et, No reset
2006Stmlt300 | 2006 - 2009 | Drft | lt300 |  | S-Boiler_Et-lt300k-0.75-fDraft |  | 2006 - 2009 | Stm | < 300 | 75 | Et |  |  | fDraft | no | OA Reset from 140 to 165 F | Steam boiler (< 300 kBtuh, 75.0 Et, OA Reset from 140 to 165 F) | Stmlt3002006 - 2009 | 2006 - 2009: 75.0 Et, OA Reset from 140 to 165 F
2010Stmlt300 | 2010 - 2013 | Drft | lt300 |  | S-Boiler_Et-lt300k-0.75-fDraft |  | 2010 - 2013 | Stm | < 300 | 75 | Et |  |  | fDraft | no | OA Reset from 140 to 165 F | Steam boiler (< 300 kBtuh, 75.0 Et, OA Reset from 140 to 165 F) | Stmlt3002010 - 2013 | 2010 - 2013: 75.0 Et, OA Reset from 140 to 165 F
2014Stmlt300 | 2014 - 2015 | Drft | lt300 |  | S-Boiler_Et-lt300k-0.8-fDraft |  | 2014 - 2015 | Stm | < 300 | 80 | Et |  |  | fDraft | no | OA Reset from 140 to 165 F | Steam boiler (< 300 kBtuh, 80.0 Et, OA Reset from 140 to 165 F) | Stmlt3002014 - 2015 | 2014 - 2015: 80.0 Et, OA Reset from 140 to 165 F
Pre-Stm300to2500 | Pre-2005 | Drft | 300to2500 |  | S-Boiler_Et-300to2500k-0.75-fDraft |  | Pre-2005 | Stm | 300 - 2500 | 75 | Et |  |  | fDraft | no | No reset | Steam boiler (300 - 2500 kBtuh, 75.0 Et, No reset) | Stm300to2500Pre-2005 | Pre-2005: 75.0 Et, No reset
2006Stm300to2500 | 2006 - 2009 | Drft | 300to2500 |  | S-Boiler_Et-300to2500k-0.75-fDraft |  | 2006 - 2009 | Stm | 300 - 2500 | 75 | Et |  |  | fDraft | no | OA Reset from 140 to 165 F | Steam boiler (300 - 2500 kBtuh, 75.0 Et, OA Reset from 140 to 165 F) | Stm300to25002006 - 2009 | 2006 - 2009: 75.0 Et, OA Reset from 140 to 165 F
2010Stm300to2500 | 2010 - 2013 | Drft | 300to2500 |  | S-Boiler_Et-300to2500k-0.75-fDraft |  | 2010 - 2013 | Stm | 300 - 2500 | 75 | Et |  |  | fDraft | no | OA Reset from 140 to 165 F | Steam boiler (300 - 2500 kBtuh, 75.0 Et, OA Reset from 140 to 165 F) | Stm300to25002010 - 2013 | 2010 - 2013: 75.0 Et, OA Reset from 140 to 165 F
2014Stm300to2500 | 2014 - 2015 | Drft | 300to2500 |  | S-Boiler_Et-300to2500k-0.79-fDraft |  | 2014 - 2015 | Stm | 300 - 2500 | 79 | Et |  |  | fDraft | no | OA Reset from 140 to 165 F | Steam boiler (300 - 2500 kBtuh, 79.0 Et, OA Reset from 140 to 165 F) | Stm300to25002014 - 2015 | 2014 - 2015: 79.0 Et, OA Reset from 140 to 165 F
Pre-Stmgt2500 | Pre-2005 | Drft | gt2500 |  | S-Boiler_Et-gt2500k-0.75-fDraft |  | Pre-2005 | Stm | > 2500 | 75 | Et |  |  | fDraft | no | No reset | Steam boiler (> 2500 kBtuh, 75.0 Et, No reset) | Stmgt2500Pre-2005 | Pre-2005: 75.0 Et, No reset
2006Stmgt2500 | 2006 - 2009 | Drft | gt2500 |  | S-Boiler_Et-gt2500k-0.75-fDraft |  | 2006 - 2009 | Stm | > 2500 | 75 | Et |  |  | fDraft | no | OA Reset from 140 to 165 F | Steam boiler (> 2500 kBtuh, 75.0 Et, OA Reset from 140 to 165 F) | Stmgt25002006 - 2009 | 2006 - 2009: 75.0 Et, OA Reset from 140 to 165 F
2010Stmgt2500 | 2010 - 2013 | Drft | gt2500 |  | S-Boiler_Et-gt2500k-0.75-fDraft |  | 2010 - 2013 | Stm | > 2500 | 75 | Et |  |  | fDraft | no | OA Reset from 140 to 165 F | Steam boiler (> 2500 kBtuh, 75.0 Et, OA Reset from 140 to 165 F) | Stmgt25002010 - 2013 | 2010 - 2013: 75.0 Et, OA Reset from 140 to 165 F
2014Stmgt2500 | 2014 - 2015 | Drft | gt2500 |  | S-Boiler_Et-gt2500k-0.79-fDraft |  | 2014 - 2015 | Stm | > 2500 | 79 | Et |  |  | fDraft | no | OA Reset from 140 to 165 F | Steam boiler (> 2500 kBtuh, 79.0 Et, OA Reset from 140 to 165 F) | Stmgt25002014 - 2015 | 2014 - 2015: 79.0 Et, OA Reset from 140 to 165 F

## Lookups
| ID | Desc
| Drft | forced draft | OA reset: 140 to 165 F
| CndStd | condensing, OA reset from 140 to 165 F | OA reset: 140 to 165 F
| CndLow | condensing, OA reset from 115 to 140 F | OA reset: 115 to 140 F
| CndReset | condensing, load reset from 115 to 140 F | Load reset: 115 to 140 F
| Vintage | TempCtrl
4 | Pre-2005 | No reset
5 | 2006 - 2009 | OA Reset from 140 to 165 F
6 | 2010 - 2013 | OA Reset from 140 to 165 F
7 | 2014 - 2015 | OA Reset from 140 to 165 F
| Type | Size | Vintage | LookupID | Effic
4 | HW | lt300 | Pre-2005 | HWlt300Pre-2005 | 80
5 | HW | lt300 | 2006 - 2009 | HWlt3002006 - 2009 | 80
6 | HW | lt300 | 2010 - 2013 | HWlt3002010 - 2013 | 80
7 | HW | lt300 | 2014 - 2015 | HWlt3002014 - 2015 | 82
4 | HW | 300to2500 | Pre-2005 | HW300to2500Pre-2005 | 75
5 | HW | 300to2500 | 2006 - 2009 | HW300to25002006 - 2009 | 75
6 | HW | 300to2500 | 2010 - 2013 | HW300to25002010 - 2013 | 75
7 | HW | 300to2500 | 2014 - 2015 | HW300to25002014 - 2015 | 80
4 | HW | gt2500 | Pre-2005 | HWgt2500Pre-2005 | 75
5 | HW | gt2500 | 2006 - 2009 | HWgt25002006 - 2009 | 75
6 | HW | gt2500 | 2010 - 2013 | HWgt25002010 - 2013 | 75
7 | HW | gt2500 | 2014 - 2015 | HWgt25002014 - 2015 | 80
4 | Stm | lt300 | Pre-2005 | Stmlt300Pre-2005 | 75
5 | Stm | lt300 | 2006 - 2009 | Stmlt3002006 - 2009 | 75
6 | Stm | lt300 | 2010 - 2013 | Stmlt3002010 - 2013 | 75
7 | Stm | lt300 | 2014 - 2015 | Stmlt3002014 - 2015 | 80
4 | Stm | 300to2500 | Pre-2005 | Stm300to2500Pre-2005 | 75
5 | Stm | 300to2500 | 2006 - 2009 | Stm300to25002006 - 2009 | 75
6 | Stm | 300to2500 | 2010 - 2013 | Stm300to25002010 - 2013 | 75
7 | Stm | 300to2500 | 2014 - 2015 | Stm300to25002014 - 2015 | 79
4 | Stm | gt2500 | Pre-2005 | Stmgt2500Pre-2005 | 75
5 | Stm | gt2500 | 2006 - 2009 | Stmgt25002006 - 2009 | 75
6 | Stm | gt2500 | 2010 - 2013 | Stmgt25002010 - 2013 | 75
7 | Stm | gt2500 | 2014 - 2015 | Stmgt25002014 - 2015 | 79
Size ID
| < 300 | lt300
| 300 - 2500 | 300to2500
| > 2500 | gt2500