## HVAC Update
DEER2015 Packaged and Split Air Conditioner Update
2014-11-24
SEER-Rated HVAC Measures update
As of January 1, 2015, the code efficiency requirements for SEER-rated central air conditioners and heat pumps increases from SEER 13 to SEER 14. All DEER HVAC measures based on SEER-rated equipment increase the code-level technology to SEER 14. Additional efficiency tier levels are added for some measures to accommodate the higher minimum efficiency level.
EER-Rated Equipment and Measure Update
The DEER2015 update also includes an update to the larger, EER-rated packaged DX system efficiency measures. The 2014 DEER update included changes to the packaged single zone models in response to code requirements for two speed fan capabilities. For DEER2015, the larger packaged HVAC measures have been updated based on the performance characteristics of available units that meet the current code requirements and tier levels. Updates to the EER-rated equipment performance curves were also required in order to determine the IEER rating for measure technologies.
DX equipment Vintage specification update
All packaged HVAC equipment have an effective useful life (EUL) of 15 years and a remaining useful life (RUL) of 5 years. While new construction and replace-on-burnout measure application types depend only on the measure and code equipment specifications, early retirement measure applications depend on the pre-existing equipment specifications as well. In order to comply with the early-retirement measure application requirement of replacing viable equipment, all pre-existing equipment specifications are limited to be less than 15 years old. This requirement caused the equipment in the oldest building vintages to be set to the 2002-era equipment specifications.
Economizer impacts separated from fan and compressor improvements
For commercial SEER-rated measures greater than 55 kBTU/h and commercial EER-rated measures less than 110 kBTU/h, the pre-existing technologies in building vintages before 2014 do have require an economizer, while the code and measure technologies do require an economizer. A large fraction of the above pre-existing energy savings for these measures comes from the addition of an economizer in the measure technology. To address this issue, an additional set of measures are defined that include an economizer in the pre-existing equipment, such that the energy impacts are due to compressor and fan improvements only.
The evaluation of new performance maps allowed the following improvements for packaged air conditioner measures.
1 | The process of selecting typical performance maps for the analysis was updated to provide more consistent performance across tier levels for a given class and size range of equipment.
2 | For building types where packaged VAV system types are applicable, simulations were added to consider both the packaged single zone system type and the packaged VAV system type for packaged DX systems 240 kBtu/hr and larger.
3 | An analysis of unit supply fan power was conducted to establish a more rigorous approach to handling this parameter in the simulations.
4 | New measure tiers were added to reflect the ranges of efficiencies in the new performance map data sets.
5 | IEER calculations were performed for each of the new performance map data sets to enable the development of measures described in terms of IEER.
Workbook Contents:
Summary of Changes
This worksheet lists all of the categorical changes involved with the DEER2015 HVAC update.
Measure Summary
This worksheet lists all of the DEER2014 measure IDs updated by DEER2015 as well as the new DEER2015 measure IDs.
Code Update
Changes to the federal requirements for small split air conditioners
Com Technology Summary
Technology tier levels definitions for commercial split and packaged air conditioners
Res Technology Summary
Technology tier levels definitions for residential split air conditioners and heat pumps
Measure Definitions
Complete listing of DEER2015 HVAC measure definitions
Technologies
Lists all of the technologies referenced by the updated HVAC measures, including their key parameters.
Packaged AC Fan Power
Evaluation of supply fan power for packaged AC measures
Split DX Fan Power
Evaluation of supply fan power for split DX measures
Performance Map Selection
Description of process used to select performance data for DX measures
Split HP Tier Selection
Description of process used to establish heat pump HPSF levels for split HP measures
Split DX Selected Perf Maps
Complete data listings for the selected performance maps for split DX systems
Packaged DX Selected Perf Maps
Complete data listings for the selected performance maps for packaged DX systems

## Summary of Changes
Summary of changes from DEER2014 to DEER2015
SEER-rated Measure Update
For SEER-rated HVAC measures, the code case is updated from SEER-13 to SEER-14 rated equipment.
See the "Measure Summary" worksheet for all of the SEER-rated measures that are updated for DEER2015.
Capacity ranges updated
Residential and commercial split air-conditioners have additional capacity ranges based on new EER code requirements above and below 45 kBTU/h.
For residential split system AC measures:
DEER2014 has a single capacity range of less than 65 kBTU/h.
DEER2015 has two capacity ranges: less than 45 kBTU/h and 45-65 kBTU/h.
For commercial split systems AC measures:
DEER2014 has two capacity ranges: less than 55 kBTU/h and 55-65 kBTU/h (based on two-speed fan requirements).
DEER2015 has three capacity ranges: less than 45 kBTU/h, 45-55 kBTU/h (based on EER requirements) and 55-65 kBTU/h (based on two-speed fan requirements).
Tier Levels Updated
Efficiency tier levels have been expanded to reflect the equipment currently available that meets and exceeds code requirements.
Residential HP tier levels:
DEER2014 included SEER levels of 13, 14, 15 and 16. DEER2015 expands the measure SEER-rating levels to 15, 16, 17 and 18.
Commercial SEER-rated Packaged AC:
DEER2014 included SEER levels of 13 and 14. DEER2015 expands the measure SEER-rating levels to 15, 16, 17 and 18.
Commercial SEER-rated Split AC:
DEER2014 included SEER levels of 13 and 14. DEER2015 expands the measure SEER-rating levels to 15, 16, 17 and 18.
Commercial EER-rated Packaged AC
For each capacity range, an additional efficiency tier is added that reflects currently available high-efficiency equipment.
Note: to-code level measures (i.e. measures in which the high-efficiency technology is the same as code requirements, such as SEER-14 measures) are not included in DEER2015.
Economizer in Pre-existing Technologies Option for commercial measures
Commercial SEER-rated measures greater than 55 kBTU/h and Commercial EER-rated measures less than 110 kBTU/h have two options:
1. The measure and code technologies have economizers, as required by code; pre-existing technologies do not have economizer except as required by Code, which is for vintage 2014 only.
For these measures, the energy impacts are due to fan and compressor improvements associated with the various tier levels as well as the addition of an
economizer. For early-retirement measure applications, a large fraction of the RUL period savings (above pre-existing impacts) may be due to the presence of
economizer in the measure technology.
2. The measure, code and pre-existing technologies have economizers. These measures are appended with "-wPreEcono" in the measure ID.
For these measures, the energy impacts are due to fan and compressor improvements associated with the various tier levels. For early-retirement measure
applications, it is assumed an economizer was present in the pre-existing equipment.
Specification of building HVAC system type
In DEER2014, Commercial EER-rated Packaged AC measures 20 tons and larger were applied to either a packaged single-zone system (cDXGF) or a
multi-zone variable volume system (cPVVG), based on the building type. In both cases, the HVAC system type is specified as "Any" in the associated
energy impact records. For DEER2015, the measures in this category are applied to one or both of the system types, as applicable to the building type, and
"BldgHVAC" field is specified appropriately in the linked energy impact records. The following table lists which system types are associated with the packaged
AC measure larger than 20 tons in DEER2014 and DEER2015.
Packaged AC Measures greater then 20 tons
|  | DEER2014 | DEER2015
| BldgType | BldgHVAC | BldgHVAC
| Asm | cDXGF | cDXGF
| Com | cWtd | cDXGF | cPVVG
| ECC | cPVVG | cDXGF | cPVVG
| EPr | cDXGF | cDXGF
| ESe | cPVVG | cDXGF | cPVVG
| EUn | cPVVG | cDXGF | cPVVG
| ERC | cDXGF
| Gro | cDXGF | cDXGF
| Hsp | cPVVG | cDXGF | cPVVG
| Htl | cPVVG | cDXGF | cPVVG
| MBT | cDXGF | cDXGF | cPVVG
| MLI | cDXGF | cDXGF
| Nrs | cPVVG | cDXGF | cPVVG
| OfL | cPVVG | cDXGF | cPVVG
| OfS | cDXGF | cDXGF | cPVVG
| RFF | cDXGF | cDXGF
| RSD | cDXGF | cDXGF
| Rt3 | cDXGF | cDXGF | cPVVG
| RtL | cDXGF | cDXGF
| RtS | cDXGF | cDXGF
| SCn | cDXGF | cDXGF
| WRf | cDXGF
| Note: | Relocatable classroom (ERC) and refrigerated warehouse (WRf) building types are not modeled with large packaged HVAC systems in DEER2015.
Energy impacts for the commercial building type (Com) are weighted based on all buildings with the specified HVAC type.
Performance Maps
Performance maps for all of the HVAC measures in this update have been re-evaluated based on currently available equipment that meet the new
code requirements and tier definitions.
For equipment that is subject to a specified SEER level as well as a minimum EER value, the performance characteristics of multiple units were averaged to best
match both criteria.
For tier-level, SEER-rated equipment that are not limited by a minimum EER requirement, the performance characteristics of multiple units were evaluated for a range of building types and climate zones.
The performance map that best represented the group of qualifying equipment (based on the smallest deviation from the median) was chosen for the equipment size range.
DX equipment Vintage specification update
This table lists the efficiency specification of pre-existing equipment by building vintage. These represent the efficiency levels of the "Customer-average" or "Pre-existing" technology that
make up a measure definition.
Mobile homes prior to 1995 are upgraded to SEER 10 from SEER 6.5. There are no other vintage changes for residential builidngs.
Building Vintage
| Residential - SEER rating by vintage | [5 empty] | Before 1978 | 1978 - 1992 | 1993 - 2001 | 2002 - 2005 | 2006 - 2009 | 2010 - 2013 | 2014 - 2015
[5 empty] | DEER2014 | SFm, MFm | 10 | 10 | 10 | 10 | 13 | 13 | 13
| SEER-rated Air Conditioners |  |  |  | DEER2015 | SFm, MFm | 10 | 10 | 10 | 10 | 13 | 13 | 13
| SEER-rated Heat Pumps | [5 empty] | Before 1976 | 1976 - 1994 | 1995 - 2005 | After 2005
| SEER-rated Evap-cooled AC |  |  |  | DEER2014 | DMo | 6.5 | 6.5 | 10 | 13
[5 empty] | DEER2015 | DMo | 10 | 10 | 10 | 13
For SEER-rated split and packaged measures in commercial buildings, the two oldest vintages are updated to SEER 10 and SEER 9.7, respectively.
Building Vintage
| Commercial - SEER rating by vintage | [5 empty] | Before 1978 | 1978 - 1992 | 1993 - 2001 | 2002 - 2005 | 2006 - 2009 | 2010 - 2013 | 2014 - 2015
| SEER-rated Split AC & HP |  |  |  | DEER2014 |  | 8.5 | 9.5 | 10 | 10 | 13 | 13 | 13
[5 empty] | DEER2015 |  | 10 | 10 | 10 | 10 | 13 | 13 | 13
| SEER-rated Packaged AC & HP |  |  |  | DEER2014 |  | 8.3 | 9.3 | 9.7 | 9.7 | 13 | 13 | 13
[5 empty] | DEER2015 |  | 9.7 | 9.7 | 9.7 | 9.7 | 13 | 13 | 13
For commercial packaged, EER-rated measures, the pre-2002 vintages are updated to the 2002 vintage specification. In addition to the efficiency rating changes,
for units greater than 110 kBTU/hr, the oldest vintage (before 1978) includes an economizer in DEER2015.
Building Vintage
| Commercial Packaged Air Conditioners - EER rating by vintage | [5 empty] | Before 1978 | 1978 - 1992 | 1993 - 2001 | 2002 - 2005 | 2006 - 2009 | 2010 - 2013 | 2014 - 2015
|  | 65 to 110 kBTU/hr |  |  | DEER2014 |  | 7.7 | 8.9 | 8.9 | 10.1 | 10.1 | 11 | 10.8
[5 empty] | DEER2015 |  | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 11 | 11
|  | 110 to 135 kBTU/hr |  |  | DEER2014 |  | 7.7 | 8.9 | 8.9 | 10.1 | 10.1 | 11 | 10.8
[5 empty] | DEER2015 |  | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 11 | 11
|  | 135 to 240 kBTU/hr |  |  | DEER2014 |  | 7.7 | 8.3 | 8.3 | 9.5 | 9.5 | 10.8 | 10.8
[5 empty] | DEER2015 |  | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 10.8 | 10.8
|  | 240 t0 760 kBTU/hr |  |  | DEER2014 | Single-zone | 7.7 | 8.3 | 8.3 | 9.3 | 9.3 | 9.8 | 9.8
[5 empty] | DEER2015 |  | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.8 | 9.8
[5 empty] | DEER2014 | Multi-zone VAV | 7.7 | 8.5 | 8.5 | 9.5 | 9.5 | 10 | 10
[5 empty] | DEER2015 |  | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 10 | 10
|  | greater than 760 kBTU/hr |  |  | DEER2014 | Single-zone | 7.7 | 8 | 8 | 9 | 9 | 9.5 | 9.5
[5 empty] | DEER2015 |  | 9 | 9 | 9 | 9 | 9 | 9.5 | 9.5
[5 empty] | DEER2014 | Multi-zone VAV | 7.7 | 8.2 | 8.2 | 9.2 | 9.2 | 9.7 | 9.7
[5 empty] | DEER2015 |  | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.7 | 9.7

## Measure Summary
Measure Summary
This table lists the DEER2014 measure IDs that are updated for DEER2015 and the updated measure IDs.
DEER2015 includes additional tier levels and size ranges, as required by the code update.
For details on the new measure definitions, see the technology summary worksheets and the "Measure Definitions" worksheet.
Updated Residential HVAC Measures |  | Updated Commercial HVAC Measures
DEER2014 | DEER2015 | DEER2014 | DEER2015
SEER-rated Air Conditioners |  | SEER-rated Packaged Air Conditioners
RE-HV-ResAC-13S | RE-HV-ResAC-lt45kBtuh-15S | NE-HVAC-airAC-Pkg-lt55kBtuh-13p0seer | NE-HVAC-airAC-Pkg-lt55kBtuh-15p0seer
RE-HV-ResAC-14S | RE-HV-ResAC-lt45kBtuh-16S | NE-HVAC-airAC-Pkg-lt55kBtuh-14p0seer | NE-HVAC-airAC-Pkg-lt55kBtuh-16p0seer
RE-HV-ResAC-15S | RE-HV-ResAC-lt45kBtuh-17S |  | NE-HVAC-airAC-Pkg-lt55kBtuh-17p0seer
RE-HV-ResAC-16S | RE-HV-ResAC-lt45kBtuh-18S |  | NE-HVAC-airAC-Pkg-lt55kBtuh-18p0seer
RE-HV-ResAC-17S | RE-HV-ResAC-lt45kBtuh-19S | NE-HVAC-airAC-Pkg-55to65kBtuh-13p0seer | NE-HVAC-airAC-Pkg-55to65kBtuh-15p0seer
RE-HV-ResAC-18S | RE-HV-ResAC-lt45kBtuh-20S | NE-HVAC-airAC-Pkg-55to65kBtuh-14p0seer | NE-HVAC-airAC-Pkg-55to65kBtuh-16p0seer
RE-HV-ResAC-19S | RE-HV-ResAC-lt45kBtuh-21S |  | NE-HVAC-airAC-Pkg-55to65kBtuh-17p0seer
RE-HV-ResAC-20S | RE-HV-ResAC-45to65kBtuh-15S |  | NE-HVAC-airAC-Pkg-55to65kBtuh-18p0seer
RE-HV-ResAC-21S | RE-HV-ResAC-45to65kBtuh-16S |  | NE-HVAC-airAC-Pkg-55to65kBtuh-15p0seer-wPreEcono
| RE-HV-ResAC-45to65kBtuh-17S |  | NE-HVAC-airAC-Pkg-55to65kBtuh-16p0seer-wPreEcono
| RE-HV-ResAC-45to65kBtuh-18S |  | NE-HVAC-airAC-Pkg-55to65kBtuh-17p0seer-wPreEcono
| RE-HV-ResAC-45to65kBtuh-19S |  | NE-HVAC-airAC-Pkg-55to65kBtuh-18p0seer-wPreEcono
| RE-HV-ResAC-45to65kBtuh-20S | SEER-rated Split Air Conditioners
| RE-HV-ResAC-45to65kBtuh-21S | NE-HVAC-airAC-Split-lt55kBtuh-13p0seer | NE-HVAC-airAC-Split-lt45kBtuh-15p0seer
SEER-rated Heat Pumps |  | NE-HVAC-airAC-Split-lt55kBtuh-14p0seer | NE-HVAC-airAC-Split-lt45kBtuh-16p0seer
RE-HV-ResHP-13p0S-8p1H | RE-HV-ResHP-15p0S-8p7H |  | NE-HVAC-airAC-Split-lt45kBtuh-17p0seer
RE-HV-ResHP-14p0S-8p6H | RE-HV-ResHP-16p0S-9p0H |  | NE-HVAC-airAC-Split-lt45kBtuh-18p0seer
RE-HV-ResHP-15p0S-8p8H | RE-HV-ResHP-17p0S-9p4H |  | NE-HVAC-airAC-Split-45to55kBtuh-15p0seer
RE-HV-ResHP-16p0S-8p4H | RE-HV-ResHP-18p0S-9p7H |  | NE-HVAC-airAC-Split-45to55kBtuh-16p0seer
SEER-rated Evap-cooled Air Conditioners |  |  | NE-HVAC-airAC-Split-45to55kBtuh-17p0seer
RE-HV-ResEvapAC-17p4S | RE-HV-ResEvapAC-lt45kBtuh-17p4S |  | NE-HVAC-airAC-Split-45to55kBtuh-18p0seer
| RE-HV-ResEvapAC-45to65kBtuh-17p4S | NE-HVAC-airAC-Split-55to65kBtuh-13p0seer | NE-HVAC-airAC-Split-55to65kBtuh-15p0seer
|  | NE-HVAC-airAC-Split-55to65kBtuh-14p0seer | NE-HVAC-airAC-Split-55to65kBtuh-16p0seer
14 | 20 |  | NE-HVAC-airAC-Split-55to65kBtuh-17p0seer
NE-HVAC-airAC-Split-55to65kBtuh-18p0seer
NE-HVAC-airAC-Split-55to65kBtuh-15p0seer-wPreEcono
NE-HVAC-airAC-Split-55to65kBtuh-16p0seer-wPreEcono
NE-HVAC-airAC-Split-55to65kBtuh-17p0seer-wPreEcono
NE-HVAC-airAC-Split-55to65kBtuh-18p0seer-wPreEcono
EER-rated Packaged Air Conditioners
|  | NE-HVAC-airAC-SpltPkg-65to109kBtuh-11p0eer | NE-HVAC-airAC-SpltPkg-65to109kBtuh-11p5eer
|  | NE-HVAC-airAC-SpltPkg-65to109kBtuh-11p5eer | NE-HVAC-airAC-SpltPkg-65to109kBtuh-12p0eer
|  | NE-HVAC-airAC-SpltPkg-65to109kBtuh-12p0eer | NE-HVAC-airAC-SpltPkg-65to109kBtuh-13p0eer
NE-HVAC-airAC-SpltPkg-65to109kBtuh-11p5eer-wPreEcono
NE-HVAC-airAC-SpltPkg-65to109kBtuh-12p0eer-wPreEcono
NE-HVAC-airAC-SpltPkg-65to109kBtuh-13p0eer-wPreEcono
|  | NE-HVAC-airAC-SpltPkg-110to134kBtuh-11p0eer | NE-HVAC-airAC-SpltPkg-110to134kBtuh-11p5eer
|  | NE-HVAC-airAC-SpltPkg-110to134kBtuh-11p5eer | NE-HVAC-airAC-SpltPkg-110to134kBtuh-12p0eer
|  | NE-HVAC-airAC-SpltPkg-110to134kBtuh-12p0eer | NE-HVAC-airAC-SpltPkg-110to134kBtuh-12p5eer
|  | NE-HVAC-airAC-SpltPkg-135to239kBtuh-10p8eer | NE-HVAC-airAC-SpltPkg-135to239kBtuh-11p5eer
|  | NE-HVAC-airAC-SpltPkg-135to239kBtuh-11p5eer | NE-HVAC-airAC-SpltPkg-135to239kBtuh-12p0eer
|  | NE-HVAC-airAC-SpltPkg-135to239kBtuh-12p0eer | NE-HVAC-airAC-SpltPkg-135to239kBtuh-12p5eer
|  | NE-HVAC-airAC-SpltPkg-240to759kBtuh-9p8eer | NE-HVAC-airAC-SpltPkg-240to759kBtuh-10p8eer
|  | NE-HVAC-airAC-SpltPkg-240to759kBtuh-10p5eer | NE-HVAC-airAC-SpltPkg-240to759kBtuh-11p5eer
|  | NE-HVAC-airAC-SpltPkg-240to759kBtuh-10p8eer | NE-HVAC-airAC-SpltPkg-240to759kBtuh-12p5eer
|  | NE-HVAC-airAC-SpltPkg-gte760kBtuh-9p5eer | NE-HVAC-airAC-SpltPkg-gte760kBtuh-10p2eer
|  | NE-HVAC-airAC-SpltPkg-gte760kBtuh-9p7eer | NE-HVAC-airAC-SpltPkg-gte760kBtuh-11p0eer
|  | NE-HVAC-airAC-SpltPkg-gte760kBtuh-10p2eer | NE-HVAC-airAC-SpltPkg-gte760kBtuh-12p0eer
airAC-SpltPkg-gte760kBtuh-10p0eer-wtd
SEER-rated Packaged Heat Pumps
NE-HVAC-airHP-Pkg-55to65kBtuh-15p0seer-8p2hspf
|  | NE-HVAC-airHP-Pkg-55to64kBtuh-13p0seer-7p7hspf | NE-HVAC-airHP-Pkg-55to65kBtuh-16p0seer-8p5hspf
|  | NE-HVAC-airHP-Pkg-55to64kBtuh-14p0seer-8p0hspf | NE-HVAC-airHP-Pkg-55to65kBtuh-17p0seer-9p0hspf
|  | NE-HVAC-airHP-Pkg-55to64kBtuh-15p0seer-8p5hspf | NE-HVAC-airHP-Pkg-lt55kBtuh-15p0seer-8p2hspf
NE-HVAC-airHP-Pkg-lt55kBtuh-16p0seer-8p5hspf
|  | NE-HVAC-airHP-Pkg-lt55kBtuh-13p0seer-7p7hspf | NE-HVAC-airHP-Pkg-lt55kBtuh-17p0seer-9p0hspf
|  | NE-HVAC-airHP-Pkg-lt55kBtuh-14p0seer-8p0hspf | NE-HVAC-airHP-Pkg-55to65kBtuh-15p0seer-8p2hspf-wPreEcono
|  | NE-HVAC-airHP-Pkg-lt55kBtuh-15p0seer-8p5hspf | NE-HVAC-airHP-Pkg-55to65kBtuh-16p0seer-8p5hspf-wPreEcono
NE-HVAC-airHP-Pkg-55to65kBtuh-17p0seer-9p0hspf-wPreEcono
SEER-rated Split Heat Pumps
|  | NE-HVAC-airHP-Split-55to64kBtuh-13p0seer-7p7hspf | NE-HVAC-airHP-Split-55to65kBtuh-15p0seer-8p7hspf
|  | NE-HVAC-airHP-Split-55to64kBtuh-14p5seer-8p5hspf | NE-HVAC-airHP-Split-55to65kBtuh-16p0seer-9p0hspf
|  | NE-HVAC-airHP-Split-55to64kBtuh-15p0seer-9p0hspf | NE-HVAC-airHP-Split-55to65kBtuh-17p0seer-9p4hspf
NE-HVAC-airHP-Split-55to65kBtuh-18p0seer-9p7hspf
|  | NE-HVAC-airHP-Split-lt55kBtuh-13p0seer-7p7hspf | NE-HVAC-airHP-Split-lt55kBtuh-15p0seer-8p7hspf
|  | NE-HVAC-airHP-Split-lt55kBtuh-14p5seer-8p5hspf | NE-HVAC-airHP-Split-lt55kBtuh-16p0seer-9p0hspf
|  | NE-HVAC-airHP-Split-lt55kBtuh-15p0seer-9p0hspf | NE-HVAC-airHP-Split-lt55kBtuh-17p0seer-9p4hspf
NE-HVAC-airHP-Split-lt55kBtuh-18p0seer-9p7hspf
NE-HVAC-airHP-Split-55to65kBtuh-15p0seer-8p7hspf-wPreEcono
NE-HVAC-airHP-Split-55to65kBtuh-16p0seer-9p0hspf-wPreEcono
NE-HVAC-airHP-Split-55to65kBtuh-17p0seer-9p4hspf-wPreEcono
NE-HVAC-airHP-Split-55to65kBtuh-18p0seer-9p7hspf-wPreEcono
|  | 20 | 49
|  | 16 | 18

## Code Update
Split and Packaged DX Code Update in Federal Code 430.32
These requirements are applicable to split air conditioners and heat pumps less than 65 kBtu/hr in capacity
430.32 Energy and water conservation standards and their compliance dates.
(2) Central air conditioners and central air conditioning heat pumps manufactured on or after January 1, 2015, shall have a Seasonal Energy Efficiency Ratio and Heating Seasonal Performance Factor not less than:
Product class | Seasonal energy efficiency ratio (SEER) | Heating seasonal performance
factor (HSPF)
(i) Split-system air conditioners | 14 (4)
(ii) Split-system heat pumps | 14 | 8.2
(iii) Single-package air conditioners | 14
(iv) Single-package heat pumps | 14 | 8
(4) In addition to meeting the applicable requirements in paragraphs (c)(2) of this section, products in product classes (i) and (iii) of paragraph (c)(2) (i.e., split-system air conditioners and single-package air conditioners) that are manufactured on or after January 1, 2015, and installed in the States of Arizona, California, Nevada, or New Mexico shall have a Seasonal Energy Efficiency Ratio not less than 14 and have an Energy Efficiency Ratio (at a standard rating of 95 °F dry bulb outdoor temperature) not less than the following:
Product class | Energy efficiency ratio (EER)
(i) Split-system rated cooling capacity less than 45,000 Btu/hr | 12.2
(ii) Split-system rated cooling capacity equal to or greater than 45,000 Btu/hr | 11.7
(iii) Single-package systems | 11

## Com Technology Summary
DEER2015 Commercial Packaged and Split AC Measure Technology Summary
This table summarizes the key parameters for the DEER2015 commercial packaged and split AC technologies.
Rows with a green background represent new tier levels for DEER2015.
Tables to the right indicate the DEER2014 measures that are being updated and the new DEER2015 measure IDs.
HVAC performance map lookups
DEER2015 Commercial SEER-rated split Air Conditioner Code and Measure Technologies | [10 empty] | 2 | 3 | 8 | 57 | 60 | 61
Equipment Size Range | Efficiency Tier | Rated SEER | EER | Supply Fan W/CFM | Fan Control | Economizer Req'd | Econo in Pre-existing Tech | DEER 2014 Measure ID (by Size Category) | DEER2015 Measure ID | ID | SEER | EER | W/CFM | Spd
Less than 45 kBTU/hr | Code | 14 | 12.1655 | 0.294 | one speed | No |  | NE-HVAC-airAC-Split-lt55kBtuh-13p0seer NE-HVAC-airAC-Split-lt55kBtuh-14p0seer |  | 11402 | 14 | 12.1655 | 0.294 | 1
| 1 | 15 | 12.7817 | 0.251 | one speed | No | No |  | NE-HVAC-airAC-Split-lt45kBtuh-15p0seer | 11501 | 15 | 12.7817 | 0.251 | 1
| 2 | 16 | 12.48 | 0.271 | two speed | No | No |  | NE-HVAC-airAC-Split-lt45kBtuh-16p0seer | 11604 | 16 | 12.48 | 0.271 | 2
| 3 | 17 | 13.26 | 0.271 | two speed | No | No |  | NE-HVAC-airAC-Split-lt45kBtuh-17p0seer | 11704 | 17 | 13.26 | 0.271 | 2
| 4 | 18 | 14.04 | 0.271 | two speed | No | No |  | NE-HVAC-airAC-Split-lt45kBtuh-18p0seer | 11802 | 18 | 14.04 | 0.271 | 2
45 - 55 kBTU/hr | Code | 14 | 11.8179 | 0.294 | one speed | No |  |  |  | 11403 | 14 | 11.8179 | 0.294 | 1
| 1 | 15 | 12.7817 | 0.251 | one speed | No | No |  | NE-HVAC-airAC-Split-45to55kBtuh-15p0seer | 11501 | 15 | 12.7817 | 0.251 | 1
| 2 | 16 | 12.48 | 0.271 | two speed | No | No |  | NE-HVAC-airAC-Split-45to55kBtuh-16p0seer | 11604 | 16 | 12.48 | 0.271 | 2
| 3 | 17 | 13.26 | 0.271 | two speed | No | No |  | NE-HVAC-airAC-Split-45to55kBtuh-17p0seer | 11704 | 17 | 13.26 | 0.271 | 2
| 4 | 18 | 14.04 | 0.271 | two speed | No | No |  | NE-HVAC-airAC-Split-45to55kBtuh-18p0seer | 11802 | 18 | 14.04 | 0.271 | 2
55 - 65 kBTU/hr | Code | 14 | 11.1125 | 0.294 | two speed | Yes |  | NE-HVAC-airAC-Split-55to64kBtuh-13p0seer NE-HVAC-airAC-Split-55to64kBtuh-14p0seer |  | 11405 | 14 | 11.1125 | 0.294 | 2
| 1 | 15 | 11.9062 | 0.251 | two speed | Yes | No |  | NE-HVAC-airAC-Split-55to65kBtuh-15p0seer | 11505 | 15 | 11.9062 | 0.251 | 2
| 2 | 16 | 12.48 | 0.271 | two speed | Yes | No |  | NE-HVAC-airAC-Split-55to65kBtuh-16p0seer | 11605 | 16 | 12.48 | 0.271 | 2
| 3 | 17 | 13.26 | 0.271 | two speed | Yes | No |  | NE-HVAC-airAC-Split-55to65kBtuh-17p0seer | 11705 | 17 | 13.26 | 0.271 | 2
| 4 | 18 | 14.04 | 0.271 | two speed | Yes | No |  | NE-HVAC-airAC-Split-55to65kBtuh-18p0seer | 11805 | 18 | 14.04 | 0.271 | 2
| 1 | 15 | 11.9062 | 0.251 | two speed | Yes | Yes |  | NE-HVAC-airAC-Split-55to65kBtuh-15p0seer-wPreEcono | 11505 | 15 | 11.9062 | 0.251 | 2
| 2 | 16 | 12.48 | 0.271 | two speed | Yes | Yes |  | NE-HVAC-airAC-Split-55to65kBtuh-16p0seer-wPreEcono | 11605 | 16 | 12.48 | 0.271 | 2
| 3 | 17 | 13.26 | 0.271 | two speed | Yes | Yes |  | NE-HVAC-airAC-Split-55to65kBtuh-17p0seer-wPreEcono | 11705 | 17 | 13.26 | 0.271 | 2
| 4 | 18 | 14.04 | 0.271 | two speed | Yes | Yes |  | NE-HVAC-airAC-Split-55to65kBtuh-18p0seer-wPreEcono | 11805 | 18 | 14.04 | 0.271 | 2
Notes: | Federal code specifies the minimum EER based on size ranges above and below 45 kBTU/hr
Title-24 specifies the two-speed fan requirement based on size ranges above and below 55 kBTU/hr
DEER2015 Commercial SEER-rated split Heat Pump Code and Measure Technologies
Equipment Size Range | Efficiency Tier | Rated SEER | Rated HSPF | Supply Fan W/CFM | Fan Control | Economizer Req'd | Econo in Pre-existing Tech | DEER 2014 Measure ID (by Size Category) | DEER2015 Measure ID | ID | SEER | EER | W/CFM | Spd | HSPF | COP47
Less than 55 kBTU/hr | Code | 14 | 8.2 | 0.294 | one speed | No |  | NE-HVAC-airHP-Split-lt55kBtuh-13p0seer-7p7hspf NE-HVAC-airHP-Split-lt55kBtuh-14p5seer-8p5hspf NE-HVAC-airHP-Split-lt55kBtuh-15p0seer-9p0hspf |  | 21406 | 14 | 11.9296 | 0.294 | 1 | 8.2 | 3.48
| 1 | 15 | 8.7 | 0.251 | one speed | No | No |  | NE-HVAC-airHP-Split-lt55kBtuh-15p0seer-8p7hspf | 21506 | 15 | 12.7817 | 0.251 | 1 | 8.7 | 3.68
| 2 | 16 | 9 | 0.271 | two speed | No | No |  | NE-HVAC-airHP-Split-lt55kBtuh-16p0seer-9p0hspf | 21604 | 16 | 12.48 | 0.271 | 2 | 9 | 3.57
| 3 | 17 | 9.4 | 0.271 | two speed | No | No |  | NE-HVAC-airHP-Split-lt55kBtuh-17p0seer-9p4hspf | 21704 | 17 | 13.26 | 0.271 | 2 | 9.4 | 3.74
| 4 | 18 | 9.7 | 0.271 | two speed | No | No |  | NE-HVAC-airHP-Split-lt55kBtuh-18p0seer-9p7hspf | 21802 | 18 | 14.04 | 0.271 | 2 | 9.7 | 3.86
55 - 65 kBTU/hr | Code | 14 | 8.2 | 0.294 | two speed | Yes |  | NE-HVAC-airHP-Split-55to64kBtuh-13p0seer-7p7hspf NE-HVAC-airHP-Split-55to64kBtuh-14p5seer-8p5hspf NE-HVAC-airHP-Split-55to64kBtuh-15p0seer-9p0hspf |  | 21408 | 14 | 11.1125 | 0.294 | 2 | 8.2 | 3.25
| 1 | 15 | 8.7 | 0.251 | two speed | Yes | No |  | NE-HVAC-airHP-Split-55to64kBtuh-15p0seer-8p7hspf | 21508 | 15 | 11.9062 | 0.251 | 2 | 8.7 | 3.44
| 2 | 16 | 9 | 0.271 | two speed | Yes | No |  | NE-HVAC-airHP-Split-55to64kBtuh-16p0seer-9p0hspf | 21604 | 16 | 12.48 | 0.271 | 2 | 9 | 3.57
| 3 | 17 | 9.4 | 0.271 | two speed | Yes | No |  | NE-HVAC-airHP-Split-55to64kBtuh-17p0seer-9p4hspf | 21704 | 17 | 13.26 | 0.271 | 2 | 9.4 | 3.74
| 4 | 18 | 9.7 | 0.271 | two speed | Yes | No |  | NE-HVAC-airHP-Split-55to64kBtuh-18p0seer-9p7hspf | 21802 | 18 | 14.04 | 0.271 | 2 | 9.7 | 3.86
| 1 | 15 | 8.7 | 0.251 | two speed | Yes | Yes |  | NE-HVAC-airHP-Split-55to64kBtuh-15p0seer-8p7hspf-wPreEcono | 21508 | 15 | 11.9062 | 0.251 | 2 | 8.7 | 3.44
| 2 | 16 | 9 | 0.271 | two speed | Yes | Yes |  | NE-HVAC-airHP-Split-55to64kBtuh-16p0seer-9p0hspf-wPreEcono | 21604 | 16 | 12.48 | 0.271 | 2 | 9 | 3.57
| 3 | 17 | 9.4 | 0.271 | two speed | Yes | Yes |  | NE-HVAC-airHP-Split-55to64kBtuh-17p0seer-9p4hspf-wPreEcono | 21704 | 17 | 13.26 | 0.271 | 2 | 9.4 | 3.74
| 4 | 18 | 9.7 | 0.271 | two speed | Yes | Yes |  | NE-HVAC-airHP-Split-55to64kBtuh-18p0seer-9p7hspf-wPreEcono | 21802 | 18 | 14.04 | 0.271 | 2 | 9.7 | 3.86
Notes: | Title-24 specifies the two-speed fan requirement based on size ranges above and below 55 kBTU/hr
DEER2015 Commercial SEER-rated packaged Air Conditioners Technologies | [7 empty] | Associated DEER Measure IDs |  |  | 5 | 6 | 11 | 50
Equipment Size Range | Efficiency Tier | Rated SEER | EER | Supply Fan W/CFM | Fan Control | Economizer Req'd | Econo in Pre-existing Tech | DEER 2014 Measure ID (by Size Category) | DEER2015 Measure ID | ID | SEER | EER | W/CFM | Spd
Less than 55 kBTU/hr | Code | 14 | 12.0391 | 0.294 | one speed | No |  | NE-HVAC-airAC-Pkg-lt55kBtuh-13p0seer NE-HVAC-airAC-Pkg-lt55kBtuh-14p0seer |  | 30203 | 14 | 12.0391 | 0.294 | 1
| 1 | 15 | 12.9 | 0.251 | one speed | No | No |  | NE-HVAC-airAC-Pkg-lt55kBtuh-15p0seer | 30301 | 15 | 12.9 | 0.251 | 1
| 2 | 16 | 12.48 | 0.271 | two speed | No | No |  | NE-HVAC-airAC-Pkg-lt55kBtuh-16p0seer | 11610 | 16 | 12.48 | 0.271 | 2
| 3 | 17 | 13.26 | 0.271 | two speed | No | No |  | NE-HVAC-airAC-Pkg-lt55kBtuh-17p0seer | 11710 | 17 | 13.26 | 0.271 | 2
| 4 | 18 | 14.04 | 0.271 | two speed | No | No |  | NE-HVAC-airAC-Pkg-lt55kBtuh-18p0seer | 11810 | 18 | 14.04 | 0.271 | 2
55 - 64 kBTU/hr | Code | 14 | 11.1125 | 0.294 | two speed | Yes |  | NE-HVAC-airAC-Pkg-55to64kBtuh-13p0seer NE-HVAC-airAC-Pkg-55to64kBtuh-14p0seer |  | 11405 | 14 | 11.1125 | 0.294 | 2
| 1 | 15 | 11.9062 | 0.251 | two speed | Yes | No |  | NE-HVAC-airAC-Pkg-55to64kBtuh-15p0seer | 11505 | 15 | 11.9062 | 0.251 | 2
| 2 | 16 | 12.48 | 0.271 | two speed | Yes | No |  | NE-HVAC-airAC-Pkg-55to64kBtuh-16p0seer | 11610 | 16 | 12.48 | 0.271 | 2
| 3 | 17 | 13.26 | 0.271 | two speed | Yes | No |  | NE-HVAC-airAC-Pkg-55to64kBtuh-17p0seer | 11710 | 17 | 13.26 | 0.271 | 2
| 4 | 18 | 14.04 | 0.271 | two speed | Yes | No |  | NE-HVAC-airAC-Pkg-55to64kBtuh-18p0seer | 11810 | 18 | 14.04 | 0.271 | 2
| 1 | 15 | 11.9062 | 0.251 | two speed | Yes | Yes |  | NE-HVAC-airAC-Pkg-55to64kBtuh-15p0seerwPreEcono | 11505 | 15 | 11.9062 | 0.251 | 2
| 2 | 16 | 12.48 | 0.271 | two speed | Yes | Yes |  | NE-HVAC-airAC-Pkg-55to64kBtuh-16p0seerwPreEcono | 11610 | 16 | 12.48 | 0.271 | 2
| 3 | 17 | 13.26 | 0.271 | two speed | Yes | Yes |  | NE-HVAC-airAC-Pkg-55to64kBtuh-17p0seerwPreEcono | 11710 | 17 | 13.26 | 0.271 | 2
| 4 | 18 | 14.04 | 0.271 | two speed | Yes | Yes |  | NE-HVAC-airAC-Pkg-55to64kBtuh-18p0seerwPreEcono | 11810 | 18 | 14.04 | 0.271 | 2
Notes: | Title-24 specifies the two-speed fan requirement based on size ranges above and below 55 kBTU/hr
DEER2015 Commercial SEER-rated packaged Heat Pumps Technologies | [7 empty] | Associated DEER Measure IDs
Equipment Size Range | Efficiency Tier | Rated SEER | Rated HSPF | Supply Fan W/CFM | Fan Control | Economizer Req'd | Econo in Pre-existing Tech | DEER 2014 Measure ID (by Size Category) | DEER2015 Measure ID | ID | SEER | EER | W/CFM | Spd | HSPF | COP47
Less than 55 kBTU/hr | Code | 14 | 8 | 0.294 | one speed | No |  | NE-HVAC-airHP-Pkg-lt55kBtuh-13p0seer-7p7hspf NE-HVAC-airHP-Pkg-lt55kBtuh-14p0seer-8p0hspf NE-HVAC-airHP-Pkg-lt55kBtuh-15p0seer-8p5hspf | NE-HVAC-airHP-Pkg-lt55kBtuh-14p0seer-8p2hspf | 21407 | 14 | 11.9296 | 0.294 | 1 | 8 | 3.39
| 1 | 15 | 8.2 | 0.294 | one speed | No | No |  | NE-HVAC-airHP-Pkg-lt55kBtuh-15p0seer-8p2hspf | 21507 | 15 | 12.7817 | 0.294 | 1 | 8.2 | 3.48
| 2 | 16 | 8.5 | 0.271 | two speed | No | No |  | NE-HVAC-airHP-Pkg-lt55kBtuh-16p0seer-8p5hspf | 21609 | 16 | 12.48 | 0.271 | 2 | 8.5 | 3.37
| 3 | 17 | 9 | 0.271 | two speed | No | No |  | NE-HVAC-airHP-Pkg-lt55kBtuh-17p0seer-9p0hspf | 21709 | 17 | 13.26 | 0.271 | 2 | 9 | 3.57
55 - 64 kBTU/hr | Code | 14 | 8 | 0.294 | two speed | Yes |  | NE-HVAC-airHP-Pkg-55to64kBtuh-13p0seer-7p7hspf NE-HVAC-airHP-Pkg-55to64kBtuh-14p0seer-8p0hspf NE-HVAC-airHP-Pkg-55to64kBtuh-15p0seer-8p5hspf |  | 21409 | 14 | 11.1125 | 0.294 | 2 | 8 | 3.17
| 1 | 15 | 8.2 | 0.251 | two speed | Yes | No |  | NE-HVAC-airHP-Pkg-55to64kBtuh-15p0seer-8p2hspf | 21509 | 15 | 11.9062 | 0.251 | 2 | 8.2 | 3.24
| 2 | 16 | 8.5 | 0.271 | two speed | Yes | No |  | NE-HVAC-airHP-Pkg-55to64kBtuh-16p0seer-8p5hspf | 21609 | 16 | 12.48 | 0.271 | 2 | 8.5 | 3.37
| 3 | 17 | 9 | 0.271 | two speed | Yes | No |  | NE-HVAC-airHP-Pkg-55to64kBtuh-17p0seer-9p0hspf | 21709 | 17 | 13.26 | 0.271 | 2 | 9 | 3.57
| 1 | 15 | 8.2 | 0.251 | two speed | Yes | Yes |  | NE-HVAC-airHP-Pkg-55to64kBtuh-15p0seer-8p2hspf-wPreEcono | 21509 | 15 | 11.9062 | 0.251 | 2 | 8.2 | 3.24
| 2 | 16 | 8.5 | 0.271 | two speed | Yes | Yes |  | NE-HVAC-airHP-Pkg-55to64kBtuh-16p0seer-8p5hspf-wPreEcono | 21609 | 16 | 12.48 | 0.271 | 2 | 8.5 | 3.37
| 3 | 17 | 9 | 0.271 | two speed | Yes | Yes |  | NE-HVAC-airHP-Pkg-55to64kBtuh-17p0seer-9p0hspf-wPreEcono | 21709 | 17 | 13.26 | 0.271 | 2 | 9 | 3.57
Notes: | Title-24 specifies the two-speed fan requirement based on size ranges above and below 55 kBTU/hr | [8 empty] | 21006 | 10 | 8.5211 | 0.365 | 1 | 7.1 | 3.01
[10 empty] | 21306 | 13 | 11.0775 | 0.348 | 1 | 8.2 | 3.49
DEER2015 Commercial EER-rated packaged Air Conditioners Technologies | [7 empty] | Associated DEER Measure IDs
Equipment Size Range | Efficiency Tier | Rated EER | Rated IEER | Supply Fan W/CFM | System Type | Economizer Req'd | Econo in Pre-existing Tech | DEER 2014 Measure ID | DEER2015 Measure ID | ID | EER | W/CFM
65 to 110 kBTU/hr | Code | 11 | 13.4 | 0.4 | 2-speed, single zone | Yes |  | NE-HVAC-airAC-SpltPkg-65to109kBtuh-11p0eer NE-HVAC-airAC-SpltPkg-65to109kBtuh-11p5eer NE-HVAC-airAC-SpltPkg-65to109kBtuh-12p0eer |  | 31001 | 11 | 0.4
| 1 | 11.5 | 14.1 | 0.4 | 2-speed, single zone | Yes | No |  | NE-HVAC-airAC-SpltPkg-65to109kBtuh-11p5eer | 31101 | 11.5 | 0.4
| 2 | 12 | 14.8 | 0.4 | 2-speed, single zone | Yes | No |  | NE-HVAC-airAC-SpltPkg-65to109kBtuh-12p0eer | 31201 | 12 | 0.4
| 3 | 13 | 16.3 | 0.4 | 2-speed, single zone | Yes | No |  | NE-HVAC-airAC-SpltPkg-65to109kBtuh-13p0eer | 31301 | 13 | 0.4
| 1 | 11.5 | 14.1 | 0.4 | 2-speed, single zone | Yes | Yes |  | NE-HVAC-airAC-SpltPkg-65to109kBtuh-11p5eerwPreEcono | 31101 | 11.5 | 0.4
| 2 | 12 | 14.8 | 0.4 | 2-speed, single zone | Yes | Yes |  | NE-HVAC-airAC-SpltPkg-65to109kBtuh-12p0eerwPreEcono | 31201 | 12 | 0.4
| 3 | 13 | 16.3 | 0.4 | 2-speed, single zone | Yes | Yes |  | NE-HVAC-airAC-SpltPkg-65to109kBtuh-13p0eerwPreEcono | 31301 | 13 | 0.4
110 to 134 kBTU/hr | Code | 11 | 13.3 | 0.4 | 2-speed, single zone | Yes | Yes | NE-HVAC-airAC-SpltPkg-110to134kBtuh-11p0eer |  | 32001 | 11 | 0.4
| 1 | 11.5 | 14.3 | 0.4 | 2-speed, single zone | Yes | Yes | NE-HVAC-airAC-SpltPkg-110to134kBtuh-11p5eer | NE-HVAC-airAC-SpltPkg-110to134kBtuh-11p5eer | 32101 | 11.5 | 0.4
| 2 | 12 | 15.4 | 0.4 | 2-speed, single zone | Yes | Yes | NE-HVAC-airAC-SpltPkg-110to134kBtuh-12p0eer | NE-HVAC-airAC-SpltPkg-110to134kBtuh-12p0eer | 32201 | 12 | 0.4
| 3 | 12.5 | 16.5 | 0.4 | 2-speed, single zone | Yes | Yes |  | NE-HVAC-airAC-SpltPkg-110to134kBtuh-12p5eer | 32301 | 12.5 | 0.4
135 to 239 kBTU/hr | Code | 10.8 | 12.8 | 0.41 | 2-speed, single zone | Yes | Yes | NE-HVAC-airAC-SpltPkg-135to239kBtuh-10p8eer |  | 33001 | 10.8 | 0.41
| 1 | 11.5 | 14.3 | 0.41 | 2-speed, single zone | Yes | Yes | NE-HVAC-airAC-SpltPkg-135to239kBtuh-11p5eer | NE-HVAC-airAC-SpltPkg-135to239kBtuh-11p5eer | 33101 | 11.5 | 0.41
| 2 | 12 | 15.4 | 0.41 | 2-speed, single zone | Yes | Yes | NE-HVAC-airAC-SpltPkg-135to239kBtuh-12p0eer | NE-HVAC-airAC-SpltPkg-135to239kBtuh-12p0eer | 33201 | 12 | 0.41
| 3 | 12.5 | 16.5 | 0.41 | 2-speed, single zone | Yes | Yes |  | NE-HVAC-airAC-SpltPkg-135to239kBtuh-12p5eer | 33301 | 12.5 | 0.41
240 to 759 kBTU/hr | Code | 9.8 | 11.2 | 0.61 | 2-speed, single zone | Yes | Yes | NE-HVAC-airAC-SpltPkg-240to759kBtuh-9p8eer NE-HVAC-airAC-SpltPkg-240to759kBtuh-10p5eer NE-HVAC-airAC-SpltPkg-240to759kBtuh-10p8eer |  | 34002 | 9.8 | 0.61
| 1 | 10.8 | 12.8 | 0.61 | 2-speed, single zone | Yes | Yes |  | NE-HVAC-airAC-SpltPkg-240to759kBtuh-10p8eer | 34102 | 10.8 | 0.61
| 2 | 11.5 | 13.9 | 0.61 | 2-speed, single zone | Yes | Yes |  | NE-HVAC-airAC-SpltPkg-240to759kBtuh-11p5eer | 34202 | 11.5 | 0.61
| 3 | 12.5 | 15.5 | 0.61 | 2-speed, single zone | Yes | Yes |  | NE-HVAC-airAC-SpltPkg-240to759kBtuh-12p5eer | 34302 | 12.5 | 0.61
| Code | 10 | 11.4 | 0.72 | var spd, multi-zone | Yes | Yes |  |  | 34001 | 10 | 0.72
| 1 | 10.8 | 12.8 | 0.72 | var spd, multi-zone | Yes | Yes |  | NE-HVAC-airAC-SpltPkg-240to759kBtuh-10p8eer | 34101 | 10.8 | 0.72
| 2 | 11.5 | 13.9 | 0.72 | var spd, multi-zone | Yes | Yes |  | NE-HVAC-airAC-SpltPkg-240to759kBtuh-11p5eer | 34201 | 11.5 | 0.72
| 3 | 12.5 | 15.6 | 0.72 | var spd, multi-zone | Yes | Yes |  | NE-HVAC-airAC-SpltPkg-240to759kBtuh-12p5eer | 34301 | 12.5 | 0.72
> = 760 kBTU/hr | Code | 9.5 | 10.7 | 0.61 | 2-speed, single zone | Yes | Yes | NE-HVAC-airAC-SpltPkg-gte760kBtuh-9p5eer NE-HVAC-airAC-SpltPkg-gte760kBtuh-9p7eer NE-HVAC-airAC-SpltPkg-gte760kBtuh-10p2eer |  | 35002 | 9.5 | 0.61
| 1 | 10.2 | 11.8 | 0.61 | 2-speed, single zone | Yes | Yes |  | NE-HVAC-airAC-SpltPkg-gte760kBtuh-10p2eer | 35102 | 10.2 | 0.61
| 2 | 11 | 13.1 | 0.61 | 2-speed, single zone | Yes | Yes |  | NE-HVAC-airAC-SpltPkg-gte760kBtuh-11p0eer | 35202 | 11 | 0.61
| 3 | 12 | 14.7 | 0.61 | 2-speed, single zone | Yes | Yes |  | NE-HVAC-airAC-SpltPkg-gte760kBtuh-12p0eer | 35302 | 12 | 0.61
| Code | 9.7 | 10.9 | 0.72 | var spd, multi-zone | Yes | Yes |  |  | 35001 | 9.7 | 0.72
| 1 | 10.2 | 11.8 | 0.72 | var spd, multi-zone | Yes | Yes |  | NE-HVAC-airAC-SpltPkg-gte760kBtuh-10p2eer | 35101 | 10.2 | 0.72
| 2 | 11 | 13.1 | 0.72 | var spd, multi-zone | Yes | Yes |  | NE-HVAC-airAC-SpltPkg-gte760kBtuh-11p0eer | 35201 | 11 | 0.72
| 3 | 12 | 14.8 | 0.72 | var spd, multi-zone | Yes | Yes |  | NE-HVAC-airAC-SpltPkg-gte760kBtuh-12p0eer | 35301 | 12 | 0.72
Notes: | DEER2014 specified a single system type for the two largest size ranges based on the building type without explicitly assigning different BldgHVAC values to the associated energy impacts.
Created by inter-measure weighting the two system types (using IOU-specific weights)
240 to 759 kBTU/hr | 1 | 10.8 | 12.8 | wtd | weighted sys type | Yes
| 2 | 11.5 | 13.9 | wtd | weighted sys type | Yes
| 3 | 12.5 | 15.6 | wtd | weighted sys type | Yes
> = 760 kBTU/hr | 1 | 10.2 | 11.8 | wtd | weighted sys type | Yes
| 2 | 11 | 13.1 | wtd | weighted sys type | Yes
| 3 | 12 | 14.7 | wtd | weighted sys type | Yes
DEER2015 generates energy impacts based on multiple system types if applicable to a given building type and assigns the BldgHVAC types to the associated energy impacts.
Therefore, for DEER2015 the energy impacts associated with measures in the two largest size ranges include impacts for both the packaged single zone (cDXGF) and variable speed multi-zone (cPVVG) sytem types.

## Res Technology Summary
DEER2015 Residential AC an HP Measure Technology Summary
This table summarizes the key parameters for the DEER2015 residential AC and HP technologies
Rows with a green background represent new tier levels for DEER2015.
The table to the right indicates the DEER2014 measures that are being updated and the new DEER2015 measure IDs.
HVAC performance map lookups
DEER2015 Residential split-system AC and HP Technologies | [7 empty] | Associated DEER Measure IDs |  |  | 2 | 3 | 8 | 57 | 60
Size Range | Efficiency Tier | System Type | Rated SEER | Rated HSPF | EER | Supply Fan W/CFM | Fan Control | DEER2014 Measure ID | DEER2015 Measure ID | HVAC ID | SEER | EER | W/CFM | Spd | HSPF | HVAC Performance Curve Class
< 45 kBTU/hr | Code | Split AC | 14 |  | 12.1655 | 0.294 | one speed | RE-HV-ResAC-14S RE-HV-ResAC-15S RE-HV-ResAC-16S RE-HV-ResAC-17S RE-HV-ResAC-18S RE-HV-ResAC-19S RE-HV-ResAC-20S RE-HV-ResAC-21S |  | 11402 | 14 | 12.1655 | 0.294 | 1 |  | one speed, SEER 14, EER 12.2
| 1 | Split AC | 15 |  | 12.7817 | 0.251 | one speed |  | RE-HV-ResAC-lt45kBtuh-15S | 11501 | 15 | 12.7817 | 0.251 | 1 |  | one-speed, SEER 10 - 15
| 2 | Split AC | 16 |  | 12.48 | 0.271 | two speed |  | RE-HV-ResAC-lt45kBtuh-16S | 11604 | 16 | 12.48 | 0.271 | 2 |  | two-speed, SEER 16 - 21
| 3 | Split AC | 17 |  | 13.26 | 0.271 | two speed |  | RE-HV-ResAC-lt45kBtuh-17S | 11704 | 17 | 13.26 | 0.271 | 2 |  | two-speed, SEER 16 - 21
| 4 | Split AC | 18 |  | 14.04 | 0.271 | two speed |  | RE-HV-ResAC-lt45kBtuh-18S | 11802 | 18 | 14.04 | 0.271 | 2 |  | two-speed, SEER 16 - 21
| 5 | Split AC | 19 |  | 14.82 | 0.233 | two speed |  | RE-HV-ResAC-lt45kBtuh-19S | 11903 | 19 | 14.82 | 0.233 | 2 |  | two-speed, SEER 16 - 21
| 6 | Split AC | 20 |  | 15.6 | 0.233 | two speed |  | RE-HV-ResAC-lt45kBtuh-20S | 12001 | 20 | 15.6 | 0.233 | 2 |  | two-speed, SEER 16 - 21
| 7 | Split AC | 21 |  | 16.38 | 0.233 | two speed |  | RE-HV-ResAC-lt45kBtuh-21S | 12101 | 21 | 16.38 | 0.233 | 2 |  | two-speed, SEER 16 - 21
45 - 65 kBTU/hr | Code | Split AC | 14 |  | 11.8179 | 0.294 | one speed |  |  | 11403 | 14 | 11.8179 | 0.294 | 1 |  | one speed, SEER 14, EER 11.7
| 1 | Split AC | 15 |  | 12.7817 | 0.251 | one speed |  | RE-HV-ResAC-45to65kBtuh-15S | 11501 | 15 | 12.7817 | 0.251 | 1 |  | one-speed, SEER 10 - 15
| 2 | Split AC | 16 |  | 12.48 | 0.271 | two speed |  | RE-HV-ResAC-45to65kBtuh-16S | 11604 | 16 | 12.48 | 0.271 | 2 |  | two-speed, SEER 16 - 21
| 3 | Split AC | 17 |  | 13.26 | 0.271 | two speed |  | RE-HV-ResAC-45to65kBtuh-17S | 11704 | 17 | 13.26 | 0.271 | 2 |  | two-speed, SEER 16 - 21
| 4 | Split AC | 18 |  | 14.04 | 0.271 | two speed |  | RE-HV-ResAC-45to65kBtuh-18S | 11802 | 18 | 14.04 | 0.271 | 2 |  | two-speed, SEER 16 - 21
| 5 | Split AC | 19 |  | 14.82 | 0.233 | two speed |  | RE-HV-ResAC-45to65kBtuh-19S | 11903 | 19 | 14.82 | 0.233 | 2 |  | two-speed, SEER 16 - 21
| 6 | Split AC | 20 |  | 15.6 | 0.233 | two speed |  | RE-HV-ResAC-45to65kBtuh-20S | 12001 | 20 | 15.6 | 0.233 | 2 |  | two-speed, SEER 16 - 21
| 7 | Split AC | 21 |  | 16.38 | 0.233 | two speed |  | RE-HV-ResAC-45to65kBtuh-21S | 12101 | 21 | 16.38 | 0.233 | 2 |  | two-speed, SEER 16 - 21
<65 kBTU/hr | Code | Split HP | 14 | 8.2 | 11.9296 | 0.294 | one speed | RE-HV-ResHP-14p0S-8p6H |  | 21405 | 14 | 11.9296 | 0.294 | 1 | 8.2 | HP one-speed, SEER 10 - 15
| 1 | Split HP | 15 | 8.7 | 12.7817 | 0.251 | one speed | RE-HV-ResHP-15p0S-8p8H | RE-HV-ResHP-15p0S-8p7H | 21501 | 15 | 12.7817 | 0.251 | 1 | 8.7 | HP one-speed, SEER 10 - 15
| 2 | Split HP | 16 | 9 | 12.48 | 0.271 | two speed | RE-HV-ResHP-16p0S-8p4H | RE-HV-ResHP-16p0S-9p0H | 21604 | 16 | 12.48 | 0.271 | 2 | 9 | HP two-speed, SEER 16 - 18
| 3 | Split HP | 17 | 9.4 | 13.26 | 0.271 | two speed |  | RE-HV-ResHP-17p0S-9p4H | 21704 | 17 | 13.26 | 0.271 | 2 | 9.4 | HP two-speed, SEER 16 - 18
| 4 | Split HP | 18 | 9.7 | 14.04 | 0.271 | two speed |  | RE-HV-ResHP-18p0S-9p7H | 21802 | 18 | 14.04 | 0.271 | 2 | 9.7 | HP two-speed, SEER 16 - 18
Notes: | Federal code specifies the minimum EER for AC systems based on size ranges above and below 45 kBTU/hr

## Measure Definitions
DEER Measure Definition
This table formats the DEER2015 measures in the ex ante format.
Index | MeasureID | Description | Version | VersionSource | LastMod | EnergyImpactID | MeasImpactType | EnImpCalcType | ImpScaleBasis | StdScaleVal | PreScaleVal | ImpWeighting | WeightGroupID | ApplyIE | IETableName | TechBased | Sector | PA | UseCategory | UseSubCategory | TechGroup | TechType | MeasCostID | EUL_ID | PreDesc | StdDesc | MeasDesc | PreTechID | StdTechID | MeasTechID | Status | Comment | PreMultiTech | StdMultiTech | SourceDesc | SupportedAppType | StdCostID | RUL_ID | LegacyID | Qualifier | StartDate | ExpiryDate
Commercial EER-rated packaged AC
701 | NE-HVAC-airAC-SpltPkg-65to109kBtuh-11p5eer | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 11.5 (IEER = 14.1), EIR = 0.26, Fan W/CFM = 0.4, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | DEER2015 | D15 v1.0 | 2014-10-02 12:00 | NE-HVAC-airAC-SpltPkg-65to109kBtuh-11p5eer | DEER | Standard | [7 empty] | f | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER |  | HVAC-airAC | EER-Rated Pkg AC, 65-110 kBTU/h; Pre-2005: EER = 10.1, one-speed fan, no Econo; 2006 - 2009: EER = 10.1, one-speed fan, no Econo; 2010 - 2013: EER = 11, one-speed fan, no Econo; 2014 - 2015: EER = 11 (IEER = 13.4), two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 11 (IEER = 13.4), EIR = 0.273, Fan W/CFM = 0.4, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 11.5 (IEER = 14.1), EIR = 0.26, Fan W/CFM = 0.4, two-speed fan, with Econo |  | dxAC-Com-Pkg-65to110kBTUh-EER11.0 | dxAC-Com-Pkg-65to110kBTUh-EER11.5 | Review |  | f | f |  | ErRobNc |  | HVAC-airAC |  | None | 2015-01-01
702 | NE-HVAC-airAC-SpltPkg-65to109kBtuh-12p0eer | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 12 (IEER = 14.8), EIR = 0.247, Fan W/CFM = 0.4, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | DEER2015 | D15 v1.0 | 2014-10-02 12:00 | NE-HVAC-airAC-SpltPkg-65to109kBtuh-12p0eer | DEER | Standard | [7 empty] | f | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER |  | HVAC-airAC | EER-Rated Pkg AC, 65-110 kBTU/h; Pre-2005: EER = 10.1, one-speed fan, no Econo; 2006 - 2009: EER = 10.1, one-speed fan, no Econo; 2010 - 2013: EER = 11, one-speed fan, no Econo; 2014 - 2015: EER = 11 (IEER = 13.4), two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 11 (IEER = 13.4), EIR = 0.273, Fan W/CFM = 0.4, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 12 (IEER = 14.8), EIR = 0.247, Fan W/CFM = 0.4, two-speed fan, with Econo |  | dxAC-Com-Pkg-65to110kBTUh-EER11.0 | dxAC-Com-Pkg-65to110kBTUh-EER12.0 | Review |  | f | f |  | ErRobNc |  | HVAC-airAC |  | None | 2015-01-01
703 | NE-HVAC-airAC-SpltPkg-65to109kBtuh-13p0eer | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 13 (IEER = 16.3), EIR = 0.226, Fan W/CFM = 0.4, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | DEER2015 | D15 v1.0 | 2014-10-02 12:00 | NE-HVAC-airAC-SpltPkg-65to109kBtuh-13p0eer | DEER | Standard | [7 empty] | f | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER |  | HVAC-airAC | EER-Rated Pkg AC, 65-110 kBTU/h; Pre-2005: EER = 10.1, one-speed fan, no Econo; 2006 - 2009: EER = 10.1, one-speed fan, no Econo; 2010 - 2013: EER = 11, one-speed fan, no Econo; 2014 - 2015: EER = 11 (IEER = 13.4), two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 11 (IEER = 13.4), EIR = 0.273, Fan W/CFM = 0.4, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 13 (IEER = 16.3), EIR = 0.226, Fan W/CFM = 0.4, two-speed fan, with Econo |  | dxAC-Com-Pkg-65to110kBTUh-EER11.0 | dxAC-Com-Pkg-65to110kBTUh-EER13.0 | Review |  | f | f |  | ErRobNc |  | HVAC-airAC |  | None | 2015-01-01
704 | NE-HVAC-airAC-SpltPkg-65to109kBtuh-11p5eer-wPreEcono | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 11.5 (IEER = 14.1), EIR = 0.26, Fan W/CFM = 0.4, two-speed fan, with Econo (Pre-existing vintages include Economizer) | DEER2015 | D15 v1.0 | 2014-10-02 12:00 | NE-HVAC-airAC-SpltPkg-65to109kBtuh-11p5eer-wPreEcono | DEER | Standard | [7 empty] | f | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER |  | HVAC-airAC | EER-Rated Pkg AC, 65-110 kBTU/h; Pre-2005: EER = 10.1, one-speed fan, w/Econo; 2006 - 2009: EER = 10.1, one-speed fan, w/Econo; 2010 - 2013: EER = 11, one-speed fan, w/Econo; 2014 - 2015: EER = 11 (IEER = 13.4), two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 11 (IEER = 13.4), EIR = 0.273, Fan W/CFM = 0.4, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 11.5 (IEER = 14.1), EIR = 0.26, Fan W/CFM = 0.4, two-speed fan, with Econo |  | dxAC-Com-Pkg-65to110kBTUh-EER11.0 | dxAC-Com-Pkg-65to110kBTUh-EER11.5 | Review |  | f | f |  | ErRobNc |  | HVAC-airAC |  | None | 2015-01-01
705 | NE-HVAC-airAC-SpltPkg-65to109kBtuh-12p0eer-wPreEcono | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 12 (IEER = 14.8), EIR = 0.247, Fan W/CFM = 0.4, two-speed fan, with Econo (Pre-existing vintages include Economizer) | DEER2015 | D15 v1.0 | 2014-10-02 12:00 | NE-HVAC-airAC-SpltPkg-65to109kBtuh-12p0eer-wPreEcono | DEER | Standard | [7 empty] | f | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER |  | HVAC-airAC | EER-Rated Pkg AC, 65-110 kBTU/h; Pre-2005: EER = 10.1, one-speed fan, w/Econo; 2006 - 2009: EER = 10.1, one-speed fan, w/Econo; 2010 - 2013: EER = 11, one-speed fan, w/Econo; 2014 - 2015: EER = 11 (IEER = 13.4), two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 11 (IEER = 13.4), EIR = 0.273, Fan W/CFM = 0.4, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 12 (IEER = 14.8), EIR = 0.247, Fan W/CFM = 0.4, two-speed fan, with Econo |  | dxAC-Com-Pkg-65to110kBTUh-EER11.0 | dxAC-Com-Pkg-65to110kBTUh-EER12.0 | Review |  | f | f |  | ErRobNc |  | HVAC-airAC |  | None | 2015-01-01
706 | NE-HVAC-airAC-SpltPkg-65to109kBtuh-13p0eer-wPreEcono | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 13 (IEER = 16.3), EIR = 0.226, Fan W/CFM = 0.4, two-speed fan, with Econo (Pre-existing vintages include Economizer) | DEER2015 | D15 v1.0 | 2014-10-02 12:00 | NE-HVAC-airAC-SpltPkg-65to109kBtuh-13p0eer-wPreEcono | DEER | Standard | [7 empty] | f | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER |  | HVAC-airAC | EER-Rated Pkg AC, 65-110 kBTU/h; Pre-2005: EER = 10.1, one-speed fan, w/Econo; 2006 - 2009: EER = 10.1, one-speed fan, w/Econo; 2010 - 2013: EER = 11, one-speed fan, w/Econo; 2014 - 2015: EER = 11 (IEER = 13.4), two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 11 (IEER = 13.4), EIR = 0.273, Fan W/CFM = 0.4, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 13 (IEER = 16.3), EIR = 0.226, Fan W/CFM = 0.4, two-speed fan, with Econo |  | dxAC-Com-Pkg-65to110kBTUh-EER11.0 | dxAC-Com-Pkg-65to110kBTUh-EER13.0 | Review |  | f | f |  | ErRobNc |  | HVAC-airAC |  | None | 2015-01-01
707 | NE-HVAC-airAC-SpltPkg-110to134kBtuh-11p5eer | EER-rated packaged Air Conditioner, Size Range: 110 - 135 kBTU/h, EER = 11.5 (IEER = 14.3), EIR = 0.26, Fan W/CFM = 0.4, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 2014-10-02 12:00 | NE-HVAC-airAC-SpltPkg-110to134kBtuh-11p5eer | DEER | Standard | [7 empty] | f | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER |  | HVAC-airAC | EER-Rated Pkg AC, 110-135 kBTU/h; Pre-2005: EER = 10.1, one-speed fan, w/Econo; 2006 - 2009: EER = 10.1, one-speed fan, w/Econo; 2010 - 2013: EER = 11, one-speed fan, w/Econo; 2014 - 2015: EER = 11 (IEER = 13.3), two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 110 - 135 kBTU/h, EER = 11 (IEER = 13.3), EIR = 0.273, Fan W/CFM = 0.4, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 110 - 135 kBTU/h, EER = 11.5 (IEER = 14.3), EIR = 0.26, Fan W/CFM = 0.4, two-speed fan, with Econo |  | dxAC-Com-Pkg-110to135kBTUh-EER11.0 | dxAC-Com-Pkg-110to135kBTUh-EER11.5 | Review |  | f | f |  | ErRobNc |  | HVAC-airAC |  | None | 2015-01-01
708 | NE-HVAC-airAC-SpltPkg-110to134kBtuh-12p0eer | EER-rated packaged Air Conditioner, Size Range: 110 - 135 kBTU/h, EER = 12 (IEER = 15.4), EIR = 0.247, Fan W/CFM = 0.4, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 2014-10-02 12:00 | NE-HVAC-airAC-SpltPkg-110to134kBtuh-12p0eer | DEER | Standard | [7 empty] | f | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER |  | HVAC-airAC | EER-Rated Pkg AC, 110-135 kBTU/h; Pre-2005: EER = 10.1, one-speed fan, w/Econo; 2006 - 2009: EER = 10.1, one-speed fan, w/Econo; 2010 - 2013: EER = 11, one-speed fan, w/Econo; 2014 - 2015: EER = 11 (IEER = 13.3), two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 110 - 135 kBTU/h, EER = 11 (IEER = 13.3), EIR = 0.273, Fan W/CFM = 0.4, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 110 - 135 kBTU/h, EER = 12 (IEER = 15.4), EIR = 0.247, Fan W/CFM = 0.4, two-speed fan, with Econo |  | dxAC-Com-Pkg-110to135kBTUh-EER11.0 | dxAC-Com-Pkg-110to135kBTUh-EER12.0 | Review |  | f | f |  | ErRobNc |  | HVAC-airAC |  | None | 2015-01-01
709 | NE-HVAC-airAC-SpltPkg-110to134kBtuh-12p5eer | EER-rated packaged Air Conditioner, Size Range: 110 - 135 kBTU/h, EER = 12.5 (IEER = 16.5), EIR = 0.236, Fan W/CFM = 0.4, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 2014-10-02 12:00 | NE-HVAC-airAC-SpltPkg-110to134kBtuh-12p5eer | DEER | Standard | [7 empty] | f | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER |  | HVAC-airAC | EER-Rated Pkg AC, 110-135 kBTU/h; Pre-2005: EER = 10.1, one-speed fan, w/Econo; 2006 - 2009: EER = 10.1, one-speed fan, w/Econo; 2010 - 2013: EER = 11, one-speed fan, w/Econo; 2014 - 2015: EER = 11 (IEER = 13.3), two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 110 - 135 kBTU/h, EER = 11 (IEER = 13.3), EIR = 0.273, Fan W/CFM = 0.4, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 110 - 135 kBTU/h, EER = 12.5 (IEER = 16.5), EIR = 0.236, Fan W/CFM = 0.4, two-speed fan, with Econo |  | dxAC-Com-Pkg-110to135kBTUh-EER11.0 | dxAC-Com-Pkg-110to135kBTUh-EER12.5 | Review |  | f | f |  | ErRobNc |  | HVAC-airAC |  | None | 2015-01-01
710 | NE-HVAC-airAC-SpltPkg-135to239kBtuh-11p5eer | EER-rated packaged Air Conditioner, Size Range: 135 - 240 kBTU/h, EER = 11.5 (IEER = 14.3), EIR = 0.255, Fan W/CFM = 0.41, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 2014-10-02 12:00 | NE-HVAC-airAC-SpltPkg-135to239kBtuh-11p5eer | DEER | Standard | [7 empty] | f | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER |  | HVAC-airAC | EER-Rated Pkg AC, 135-240 kBTU/h; Pre-2005: EER = 9.5, one-speed fan, w/Econo; 2006 - 2009: EER = 9.5, one-speed fan, w/Econo; 2010 - 2013: EER = 10.8, one-speed fan, w/Econo; 2014 - 2015: EER = 10.8 (IEER = 12.8), two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 135 - 240 kBTU/h, EER = 10.8 (IEER = 12.8), EIR = 0.274, Fan W/CFM = 0.41, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 135 - 240 kBTU/h, EER = 11.5 (IEER = 14.3), EIR = 0.255, Fan W/CFM = 0.41, two-speed fan, with Econo |  | dxAC-Com-Pkg-135to240kBTUh-EER10.8 | dxAC-Com-Pkg-135to240kBTUh-EER11.5 | Review |  | f | f |  | ErRobNc |  | HVAC-airAC |  | None | 2015-01-01
711 | NE-HVAC-airAC-SpltPkg-135to239kBtuh-12p0eer | EER-rated packaged Air Conditioner, Size Range: 135 - 240 kBTU/h, EER = 12 (IEER = 15.4), EIR = 0.243, Fan W/CFM = 0.41, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 2014-10-02 12:00 | NE-HVAC-airAC-SpltPkg-135to239kBtuh-12p0eer | DEER | Standard | [7 empty] | f | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER |  | HVAC-airAC | EER-Rated Pkg AC, 135-240 kBTU/h; Pre-2005: EER = 9.5, one-speed fan, w/Econo; 2006 - 2009: EER = 9.5, one-speed fan, w/Econo; 2010 - 2013: EER = 10.8, one-speed fan, w/Econo; 2014 - 2015: EER = 10.8 (IEER = 12.8), two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 135 - 240 kBTU/h, EER = 10.8 (IEER = 12.8), EIR = 0.274, Fan W/CFM = 0.41, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 135 - 240 kBTU/h, EER = 12 (IEER = 15.4), EIR = 0.243, Fan W/CFM = 0.41, two-speed fan, with Econo |  | dxAC-Com-Pkg-135to240kBTUh-EER10.8 | dxAC-Com-Pkg-135to240kBTUh-EER12.0 | Review |  | f | f |  | ErRobNc |  | HVAC-airAC |  | None | 2015-01-01
712 | NE-HVAC-airAC-SpltPkg-135to239kBtuh-12p5eer | EER-rated packaged Air Conditioner, Size Range: 135 - 240 kBTU/h, EER = 12.5 (IEER = 16.5), EIR = 0.231, Fan W/CFM = 0.41, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 2014-10-02 12:00 | NE-HVAC-airAC-SpltPkg-135to239kBtuh-12p5eer | DEER | Standard | [7 empty] | f | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER |  | HVAC-airAC | EER-Rated Pkg AC, 135-240 kBTU/h; Pre-2005: EER = 9.5, one-speed fan, w/Econo; 2006 - 2009: EER = 9.5, one-speed fan, w/Econo; 2010 - 2013: EER = 10.8, one-speed fan, w/Econo; 2014 - 2015: EER = 10.8 (IEER = 12.8), two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 135 - 240 kBTU/h, EER = 10.8 (IEER = 12.8), EIR = 0.274, Fan W/CFM = 0.41, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 135 - 240 kBTU/h, EER = 12.5 (IEER = 16.5), EIR = 0.231, Fan W/CFM = 0.41, two-speed fan, with Econo |  | dxAC-Com-Pkg-135to240kBTUh-EER10.8 | dxAC-Com-Pkg-135to240kBTUh-EER12.5 | Review |  | f | f |  | ErRobNc |  | HVAC-airAC |  | None | 2015-01-01
713 | NE-HVAC-airAC-SpltPkg-240to759kBtuh-10p8eer | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 10.8 (IEER = 12.8), EIR = 0.255, Fan W/CFM = 0.61, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 2014-10-02 12:00 | NE-HVAC-airAC-SpltPkg-240to759kBtuh-10p8eer | DEER | Standard | [7 empty] | f | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER |  | HVAC-airAC | EER-Rated Pkg AC, 240-760 kBTU/h; Pre-2005: EER = 9.3, one-speed fan, w/Econo; 2006 - 2009: EER = 9.3, one-speed fan, w/Econo; 2010 - 2013: EER = 9.8, one-speed fan, w/Econo; 2014 - 2015: EER = 9.8 (IEER = 11.2), two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 9.8 (IEER = 11.2), EIR = 0.286, Fan W/CFM = 0.61, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 10.8 (IEER = 12.8), EIR = 0.255, Fan W/CFM = 0.61, two-speed fan, with Econo |  | dxAC-Com-Pkg-240to760kBTUh-EER9.8 | dxAC-Com-Pkg-240to760kBTUh-EER10.8 | Review | Std and Meas Technologies vary by system configuration | f | f |  | ErRobNc |  | HVAC-airAC |  | None | 2015-01-01
714 | NE-HVAC-airAC-SpltPkg-240to759kBtuh-11p5eer | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 11.5 (IEER = 13.9), EIR = 0.236, Fan W/CFM = 0.61, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 2014-10-02 12:00 | NE-HVAC-airAC-SpltPkg-240to759kBtuh-11p5eer | DEER | Standard | [7 empty] | f | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER |  | HVAC-airAC | EER-Rated Pkg AC, 240-760 kBTU/h; Pre-2005: EER = 9.3, one-speed fan, w/Econo; 2006 - 2009: EER = 9.3, one-speed fan, w/Econo; 2010 - 2013: EER = 9.8, one-speed fan, w/Econo; 2014 - 2015: EER = 9.8 (IEER = 11.2), two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 9.8 (IEER = 11.2), EIR = 0.286, Fan W/CFM = 0.61, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 11.5 (IEER = 13.9), EIR = 0.236, Fan W/CFM = 0.61, two-speed fan, with Econo |  | dxAC-Com-Pkg-240to760kBTUh-EER9.8 | dxAC-Com-Pkg-240to760kBTUh-EER11.5 | Review | Std and Meas Technologies vary by system configuration | f | f |  | ErRobNc |  | HVAC-airAC |  | None | 2015-01-01
715 | NE-HVAC-airAC-SpltPkg-240to759kBtuh-12p5eer | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 12.5 (IEER = 15.5), EIR = 0.213, Fan W/CFM = 0.61, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 2014-10-02 12:00 | NE-HVAC-airAC-SpltPkg-240to759kBtuh-12p5eer | DEER | Standard | [7 empty] | f | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER |  | HVAC-airAC | EER-Rated Pkg AC, 240-760 kBTU/h; Pre-2005: EER = 9.3, one-speed fan, w/Econo; 2006 - 2009: EER = 9.3, one-speed fan, w/Econo; 2010 - 2013: EER = 9.8, one-speed fan, w/Econo; 2014 - 2015: EER = 9.8 (IEER = 11.2), two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 9.8 (IEER = 11.2), EIR = 0.286, Fan W/CFM = 0.61, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 12.5 (IEER = 15.5), EIR = 0.213, Fan W/CFM = 0.61, two-speed fan, with Econo |  | dxAC-Com-Pkg-240to760kBTUh-EER9.8 | dxAC-Com-Pkg-240to760kBTUh-EER12.5 | Review | Std and Meas Technologies vary by system configuration | f | f |  | ErRobNc |  | HVAC-airAC |  | None | 2015-01-01
716 | NE-HVAC-airAC-SpltPkg-gte760kBtuh-10p2eer | EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 10.2 (IEER = 11.8), EIR = 0.273, Fan W/CFM = 0.61, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 2014-10-02 12:00 | NE-HVAC-airAC-SpltPkg-gte760kBtuh-10p2eer | DEER | Standard | [7 empty] | f | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER |  | HVAC-airAC | EER-Rated Pkg AC, 760+ kBTU/h; Pre-2005: EER = 9, one-speed fan, w/Econo; 2006 - 2009: EER = 9, one-speed fan, w/Econo; 2010 - 2013: EER = 9.5, one-speed fan, w/Econo; 2014 - 2015: EER = 9.5 (IEER = 10.7), two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 9.5 (IEER = 10.7), EIR = 0.297, Fan W/CFM = 0.61, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 10.2 (IEER = 11.8), EIR = 0.273, Fan W/CFM = 0.61, two-speed fan, with Econo |  | dxAC-Com-Pkg-760tokBTUh-EER9.5 | dxAC-Com-Pkg-760tokBTUh-EER10.2 | Review | Std and Meas Technologies vary by system configuration | f | f |  | ErRobNc |  | HVAC-airAC |  | None | 2015-01-01
717 | NE-HVAC-airAC-SpltPkg-gte760kBtuh-11p0eer | EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 11 (IEER = 13.1), EIR = 0.249, Fan W/CFM = 0.61, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 2014-10-02 12:00 | NE-HVAC-airAC-SpltPkg-gte760kBtuh-11p0eer | DEER | Standard | [7 empty] | f | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER |  | HVAC-airAC | EER-Rated Pkg AC, 760+ kBTU/h; Pre-2005: EER = 9, one-speed fan, w/Econo; 2006 - 2009: EER = 9, one-speed fan, w/Econo; 2010 - 2013: EER = 9.5, one-speed fan, w/Econo; 2014 - 2015: EER = 9.5 (IEER = 10.7), two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 9.5 (IEER = 10.7), EIR = 0.297, Fan W/CFM = 0.61, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 11 (IEER = 13.1), EIR = 0.249, Fan W/CFM = 0.61, two-speed fan, with Econo |  | dxAC-Com-Pkg-760tokBTUh-EER9.5 | dxAC-Com-Pkg-760tokBTUh-EER11.0 | Review | Std and Meas Technologies vary by system configuration | f | f |  | ErRobNc |  | HVAC-airAC |  | None | 2015-01-01
718 | NE-HVAC-airAC-SpltPkg-gte760kBtuh-12p0eer | EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 12 (IEER = 14.7), EIR = 0.224, Fan W/CFM = 0.61, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 2014-10-02 12:00 | NE-HVAC-airAC-SpltPkg-gte760kBtuh-12p0eer | DEER | Standard | [7 empty] | f | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER |  | HVAC-airAC | EER-Rated Pkg AC, 760+ kBTU/h; Pre-2005: EER = 9, one-speed fan, w/Econo; 2006 - 2009: EER = 9, one-speed fan, w/Econo; 2010 - 2013: EER = 9.5, one-speed fan, w/Econo; 2014 - 2015: EER = 9.5 (IEER = 10.7), two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 9.5 (IEER = 10.7), EIR = 0.297, Fan W/CFM = 0.61, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 12 (IEER = 14.7), EIR = 0.224, Fan W/CFM = 0.61, two-speed fan, with Econo |  | dxAC-Com-Pkg-760tokBTUh-EER9.5 | dxAC-Com-Pkg-760tokBTUh-EER12.0 | Review | Std and Meas Technologies vary by system configuration | f | f |  | ErRobNc |  | HVAC-airAC |  | None | 2015-01-01
Commercial SEER-rated Packaged AC
719 | NE-HVAC-airAC-Pkg-lt55kBtuh-15p0seer | Commercial SEER-rated Packaged Air Conditioners, Size Range: 18 - 55 kBTU/h, SEER = 15 (EER = 12.9), EIR = 0.234, Fan W/CFM = 0.25, one-speed fan, without Econo | DEER2015 | D15 v1.0 | 2014-10-08 | NE-HVAC-airAC-Pkg-lt55kBtuh-15p0seer | DEER | Standard | [7 empty] | f | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgSEER |  | HVAC-airAC | Com SEER-Rated Pkg AC, 18-65 kBTU/h; pre-2001: SEER = 9.7 (EER = 9.21), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.06), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.04), one-speed fan, no Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 18 - 55 kBTU/h, SEER = 14 (EER = 12), EIR = 0.246, Fan W/CFM = 0.29, one-speed fan, without Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 18 - 55 kBTU/h, SEER = 15 (EER = 12.9), EIR = 0.234, Fan W/CFM = 0.25, one-speed fan, without Econo |  | dxAC-Com-Pkg-lt55kBTUh-SEER-14.0 | dxAC-Com-Pkg-lt55kBTUh-SEER-15.0 | Review |  | f | f |  | ErRobNc |  | HVAC-airAC |  | None | 2015-01-01
720 | NE-HVAC-airAC-Pkg-lt55kBtuh-16p0seer | Commercial SEER-rated Packaged Air Conditioners, Size Range: 18 - 55 kBTU/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, without Econo | DEER2015 | D15 v1.0 | 2014-10-08 | NE-HVAC-airAC-Pkg-lt55kBtuh-16p0seer | DEER | Standard | [7 empty] | f | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgSEER |  | HVAC-airAC | Com SEER-Rated Pkg AC, 18-65 kBTU/h; pre-2001: SEER = 9.7 (EER = 9.21), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.06), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.04), one-speed fan, no Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 18 - 55 kBTU/h, SEER = 14 (EER = 12), EIR = 0.246, Fan W/CFM = 0.29, one-speed fan, without Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 18 - 55 kBTU/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, without Econo |  | dxAC-Com-Pkg-lt55kBTUh-SEER-14.0 | dxAC-Com-Pkg-lt55kBTUh-SEER-16.0 | Review |  | f | f |  | ErRobNc |  | HVAC-airAC |  | None | 2015-01-01
721 | NE-HVAC-airAC-Pkg-lt55kBtuh-17p0seer | Commercial SEER-rated Packaged Air Conditioners, Size Range: 18 - 55 kBTU/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, without Econo | DEER2015 | D15 v1.0 | 2014-10-08 | NE-HVAC-airAC-Pkg-lt55kBtuh-17p0seer | DEER | Standard | [7 empty] | f | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgSEER |  | HVAC-airAC | Com SEER-Rated Pkg AC, 18-65 kBTU/h; pre-2001: SEER = 9.7 (EER = 9.21), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.06), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.04), one-speed fan, no Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 18 - 55 kBTU/h, SEER = 14 (EER = 12), EIR = 0.246, Fan W/CFM = 0.29, one-speed fan, without Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 18 - 55 kBTU/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, without Econo |  | dxAC-Com-Pkg-lt55kBTUh-SEER-14.0 | dxAC-Com-Pkg-lt55kBTUh-SEER-17.0 | Review |  | f | f |  | ErRobNc |  | HVAC-airAC |  | None | 2015-01-01
722 | NE-HVAC-airAC-Pkg-lt55kBtuh-18p0seer | Commercial SEER-rated Packaged Air Conditioners, Size Range: 18 - 55 kBTU/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, without Econo | DEER2015 | D15 v1.0 | 2014-10-08 | NE-HVAC-airAC-Pkg-lt55kBtuh-18p0seer | DEER | Standard | [7 empty] | f | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgSEER |  | HVAC-airAC | Com SEER-Rated Pkg AC, 18-65 kBTU/h; pre-2001: SEER = 9.7 (EER = 9.21), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.06), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.04), one-speed fan, no Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 18 - 55 kBTU/h, SEER = 14 (EER = 12), EIR = 0.246, Fan W/CFM = 0.29, one-speed fan, without Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 18 - 55 kBTU/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, without Econo |  | dxAC-Com-Pkg-lt55kBTUh-SEER-14.0 | dxAC-Com-Pkg-lt55kBTUh-SEER-18.0 | Review |  | f | f |  | ErRobNc |  | HVAC-airAC |  | None | 2015-01-01
723 | NE-HVAC-airAC-Pkg-55to65kBtuh-15p0seer | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | DEER2015 | D15 v1.0 | 2014-10-08 | NE-HVAC-airAC-Pkg-55to65kBtuh-15p0seer | DEER | Standard | [7 empty] | f | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgSEER |  | HVAC-airAC | Com SEER-Rated Pkg AC, 18-65 kBTU/h; pre-2001: SEER = 9.7 (EER = 9.21), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.06), one-speed fan, no Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo |  | dxAC-Com-Pkg-55to65kBTUh-SEER-14.0 | dxAC-Com-Pkg-55to65kBTUh-SEER-15.0 | Review |  | f | f |  | ErRobNc |  | HVAC-airAC |  | None | 2015-01-01
724 | NE-HVAC-airAC-Pkg-55to65kBtuh-16p0seer | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | DEER2015 | D15 v1.0 | 2014-10-08 | NE-HVAC-airAC-Pkg-55to65kBtuh-16p0seer | DEER | Standard | [7 empty] | f | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgSEER |  | HVAC-airAC | Com SEER-Rated Pkg AC, 18-65 kBTU/h; pre-2001: SEER = 9.7 (EER = 9.21), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.06), one-speed fan, no Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxAC-Com-Pkg-55to65kBTUh-SEER-14.0 | dxAC-Com-Pkg-55to65kBTUh-SEER-16.0 | Review |  | f | f |  | ErRobNc |  | HVAC-airAC |  | None | 2015-01-01
725 | NE-HVAC-airAC-Pkg-55to65kBtuh-17p0seer | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | DEER2015 | D15 v1.0 | 2014-10-08 | NE-HVAC-airAC-Pkg-55to65kBtuh-17p0seer | DEER | Standard | [7 empty] | f | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgSEER |  | HVAC-airAC | Com SEER-Rated Pkg AC, 18-65 kBTU/h; pre-2001: SEER = 9.7 (EER = 9.21), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.06), one-speed fan, no Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxAC-Com-Pkg-55to65kBTUh-SEER-14.0 | dxAC-Com-Pkg-55to65kBTUh-SEER-17.0 | Review |  | f | f |  | ErRobNc |  | HVAC-airAC |  | None | 2015-01-01
726 | NE-HVAC-airAC-Pkg-55to65kBtuh-18p0seer | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | DEER2015 | D15 v1.0 | 2014-10-08 | NE-HVAC-airAC-Pkg-55to65kBtuh-18p0seer | DEER | Standard | [7 empty] | f | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgSEER |  | HVAC-airAC | Com SEER-Rated Pkg AC, 18-65 kBTU/h; pre-2001: SEER = 9.7 (EER = 9.21), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.06), one-speed fan, no Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxAC-Com-Pkg-55to65kBTUh-SEER-14.0 | dxAC-Com-Pkg-55to65kBTUh-SEER-18.0 | Review |  | f | f |  | ErRobNc |  | HVAC-airAC |  | None | 2015-01-01
727 | NE-HVAC-airAC-Pkg-55to65kBtuh-15p0seer-wPreEcono | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages include Economizer) | DEER2015 | D15 v1.0 | 2014-10-08 | NE-HVAC-airAC-Pkg-55to65kBtuh-15p0seer-wPreEcono | DEER | Standard | [7 empty] | f | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgSEER |  | HVAC-airAC | Com SEER-Rated Pkg AC, 18-65 kBTU/h; pre-2001: SEER = 9.7 (EER = 9.21), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.06), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo |  | dxAC-Com-Pkg-55to65kBTUh-SEER-14.0 | dxAC-Com-Pkg-55to65kBTUh-SEER-15.0 | Review |  | f | f |  | ErRobNc |  | HVAC-airAC |  | None | 2015-01-01
728 | NE-HVAC-airAC-Pkg-55to65kBtuh-16p0seer-wPreEcono | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, with Econo (Pre-existing vintages include Economizer) | DEER2015 | D15 v1.0 | 2014-10-08 | NE-HVAC-airAC-Pkg-55to65kBtuh-16p0seer-wPreEcono | DEER | Standard | [7 empty] | f | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgSEER |  | HVAC-airAC | Com SEER-Rated Pkg AC, 18-65 kBTU/h; pre-2001: SEER = 9.7 (EER = 9.21), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.06), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxAC-Com-Pkg-55to65kBTUh-SEER-14.0 | dxAC-Com-Pkg-55to65kBTUh-SEER-16.0 | Review |  | f | f |  | ErRobNc |  | HVAC-airAC |  | None | 2015-01-01
729 | NE-HVAC-airAC-Pkg-55to65kBtuh-17p0seer-wPreEcono | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, with Econo (Pre-existing vintages include Economizer) | DEER2015 | D15 v1.0 | 2014-10-08 | NE-HVAC-airAC-Pkg-55to65kBtuh-17p0seer-wPreEcono | DEER | Standard | [7 empty] | f | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgSEER |  | HVAC-airAC | Com SEER-Rated Pkg AC, 18-65 kBTU/h; pre-2001: SEER = 9.7 (EER = 9.21), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.06), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxAC-Com-Pkg-55to65kBTUh-SEER-14.0 | dxAC-Com-Pkg-55to65kBTUh-SEER-17.0 | Review |  | f | f |  | ErRobNc |  | HVAC-airAC |  | None | 2015-01-01
730 | NE-HVAC-airAC-Pkg-55to65kBtuh-18p0seer-wPreEcono | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, with Econo (Pre-existing vintages include Economizer) | DEER2015 | D15 v1.0 | 2014-10-08 | NE-HVAC-airAC-Pkg-55to65kBtuh-18p0seer-wPreEcono | DEER | Standard | [7 empty] | f | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgSEER |  | HVAC-airAC | Com SEER-Rated Pkg AC, 18-65 kBTU/h; pre-2001: SEER = 9.7 (EER = 9.21), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.06), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxAC-Com-Pkg-55to65kBTUh-SEER-14.0 | dxAC-Com-Pkg-55to65kBTUh-SEER-18.0 | Review |  | f | f |  | ErRobNc |  | HVAC-airAC |  | None | 2015-01-01
Commercial SEER-rated Split AC
731 | NE-HVAC-airAC-Split-lt45kBtuh-15p0seer | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo | DEER2015 | D15 v1.0 | 2014-10-08 | NE-HVAC-airAC-Split-lt45kBtuh-15p0seer | DEER | Standard | [7 empty] | f | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER |  | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo |  | dxAC-Com-Split-lt45kBTUh-SEER-14.0 | dxAC-Com-Split-lt45kBTUh-SEER-15.0 | Review |  | f | f |  | ErRobNc |  | HVAC-airAC |  | None | 2015-01-01
732 | NE-HVAC-airAC-Split-lt45kBtuh-16p0seer | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, without Econo | DEER2015 | D15 v1.0 | 2014-10-08 | NE-HVAC-airAC-Split-lt45kBtuh-16p0seer | DEER | Standard | [7 empty] | f | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER |  | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, without Econo |  | dxAC-Com-Split-lt45kBTUh-SEER-14.0 | dxAC-Com-Split-lt45kBTUh-SEER-16.0 | Review |  | f | f |  | ErRobNc |  | HVAC-airAC |  | None | 2015-01-01
733 | NE-HVAC-airAC-Split-lt45kBtuh-17p0seer | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, without Econo | DEER2015 | D15 v1.0 | 2014-10-08 | NE-HVAC-airAC-Split-lt45kBtuh-17p0seer | DEER | Standard | [7 empty] | f | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER |  | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, without Econo |  | dxAC-Com-Split-lt45kBTUh-SEER-14.0 | dxAC-Com-Split-lt45kBTUh-SEER-17.0 | Review |  | f | f |  | ErRobNc |  | HVAC-airAC |  | None | 2015-01-01
734 | NE-HVAC-airAC-Split-lt45kBtuh-18p0seer | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, without Econo | DEER2015 | D15 v1.0 | 2014-10-08 | NE-HVAC-airAC-Split-lt45kBtuh-18p0seer | DEER | Standard | [7 empty] | f | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER |  | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, without Econo |  | dxAC-Com-Split-lt45kBTUh-SEER-14.0 | dxAC-Com-Split-lt45kBTUh-SEER-18.0 | Review |  | f | f |  | ErRobNc |  | HVAC-airAC |  | None | 2015-01-01
735 | NE-HVAC-airAC-Split-45to55kBtuh-15p0seer | Commercial SEER-rated split Air Conditioners, Size Range: 45 - 55 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo | DEER2015 | D15 v1.0 | 2014-10-08 | NE-HVAC-airAC-Split-45to55kBtuh-15p0seer | DEER | Standard | [7 empty] | f | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER |  | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 11.82), one-speed fan, no Econo | Commercial SEER-rated split Air Conditioners, Size Range: 45 - 55 kBTU/h, SEER = 14 (EER = 11.8), EIR = 0.247, Fan W/CFM = 0.29, one-speed fan, without Econo | Commercial SEER-rated split Air Conditioners, Size Range: 45 - 55 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo |  | dxAC-Com-Split-45to55kBTUh-SEER-14.0 | dxAC-Com-Split-45to55kBTUh-SEER-15.0 | Review |  | f | f |  | ErRobNc |  | HVAC-airAC |  | None | 2015-01-01
736 | NE-HVAC-airAC-Split-45to55kBtuh-16p0seer | Commercial SEER-rated split Air Conditioners, Size Range: 45 - 55 kBTU/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, without Econo | DEER2015 | D15 v1.0 | 2014-10-08 | NE-HVAC-airAC-Split-45to55kBtuh-16p0seer | DEER | Standard | [7 empty] | f | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER |  | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 11.82), one-speed fan, no Econo | Commercial SEER-rated split Air Conditioners, Size Range: 45 - 55 kBTU/h, SEER = 14 (EER = 11.8), EIR = 0.247, Fan W/CFM = 0.29, one-speed fan, without Econo | Commercial SEER-rated split Air Conditioners, Size Range: 45 - 55 kBTU/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, without Econo |  | dxAC-Com-Split-45to55kBTUh-SEER-14.0 | dxAC-Com-Split-45to55kBTUh-SEER-16.0 | Review |  | f | f |  | ErRobNc |  | HVAC-airAC |  | None | 2015-01-01
737 | NE-HVAC-airAC-Split-45to55kBtuh-17p0seer | Commercial SEER-rated split Air Conditioners, Size Range: 45 - 55 kBTU/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, without Econo | DEER2015 | D15 v1.0 | 2014-10-08 | NE-HVAC-airAC-Split-45to55kBtuh-17p0seer | DEER | Standard | [7 empty] | f | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER |  | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 11.82), one-speed fan, no Econo | Commercial SEER-rated split Air Conditioners, Size Range: 45 - 55 kBTU/h, SEER = 14 (EER = 11.8), EIR = 0.247, Fan W/CFM = 0.29, one-speed fan, without Econo | Commercial SEER-rated split Air Conditioners, Size Range: 45 - 55 kBTU/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, without Econo |  | dxAC-Com-Split-45to55kBTUh-SEER-14.0 | dxAC-Com-Split-45to55kBTUh-SEER-17.0 | Review |  | f | f |  | ErRobNc |  | HVAC-airAC |  | None | 2015-01-01
738 | NE-HVAC-airAC-Split-45to55kBtuh-18p0seer | Commercial SEER-rated split Air Conditioners, Size Range: 45 - 55 kBTU/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, without Econo | DEER2015 | D15 v1.0 | 2014-10-08 | NE-HVAC-airAC-Split-45to55kBtuh-18p0seer | DEER | Standard | [7 empty] | f | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER |  | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 11.82), one-speed fan, no Econo | Commercial SEER-rated split Air Conditioners, Size Range: 45 - 55 kBTU/h, SEER = 14 (EER = 11.8), EIR = 0.247, Fan W/CFM = 0.29, one-speed fan, without Econo | Commercial SEER-rated split Air Conditioners, Size Range: 45 - 55 kBTU/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, without Econo |  | dxAC-Com-Split-45to55kBTUh-SEER-14.0 | dxAC-Com-Split-45to55kBTUh-SEER-18.0 | Review |  | f | f |  | ErRobNc |  | HVAC-airAC |  | None | 2015-01-01
739 | NE-HVAC-airAC-Split-55to65kBtuh-15p0seer | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | DEER2015 | D15 v1.0 | 2014-10-08 | NE-HVAC-airAC-Split-55to65kBtuh-15p0seer | DEER | Standard | [7 empty] | f | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER |  | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo |  | dxAC-Com-Split-55to65kBTUh-SEER-14.0 | dxAC-Com-Split-55to65kBTUh-SEER-15.0 | Review |  | f | f |  | ErRobNc |  | HVAC-airAC |  | None | 2015-01-01
740 | NE-HVAC-airAC-Split-55to65kBtuh-16p0seer | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | DEER2015 | D15 v1.0 | 2014-10-08 | NE-HVAC-airAC-Split-55to65kBtuh-16p0seer | DEER | Standard | [7 empty] | f | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER |  | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxAC-Com-Split-55to65kBTUh-SEER-14.0 | dxAC-Com-Split-55to65kBTUh-SEER-16.0 | Review |  | f | f |  | ErRobNc |  | HVAC-airAC |  | None | 2015-01-01
741 | NE-HVAC-airAC-Split-55to65kBtuh-17p0seer | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | DEER2015 | D15 v1.0 | 2014-10-08 | NE-HVAC-airAC-Split-55to65kBtuh-17p0seer | DEER | Standard | [7 empty] | f | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER |  | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxAC-Com-Split-55to65kBTUh-SEER-14.0 | dxAC-Com-Split-55to65kBTUh-SEER-17.0 | Review |  | f | f |  | ErRobNc |  | HVAC-airAC |  | None | 2015-01-01
742 | NE-HVAC-airAC-Split-55to65kBtuh-18p0seer | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | DEER2015 | D15 v1.0 | 2014-10-08 | NE-HVAC-airAC-Split-55to65kBtuh-18p0seer | DEER | Standard | [7 empty] | f | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER |  | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxAC-Com-Split-55to65kBTUh-SEER-14.0 | dxAC-Com-Split-55to65kBTUh-SEER-18.0 | Review |  | f | f |  | ErRobNc |  | HVAC-airAC |  | None | 2015-01-01
743 | NE-HVAC-airAC-Split-55to65kBtuh-15p0seer-wPreEcono | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages include Economizer) | DEER2015 | D15 v1.0 | 2014-10-08 | NE-HVAC-airAC-Split-55to65kBtuh-15p0seer-wPreEcono | DEER | Standard | [7 empty] | f | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER |  | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo |  | dxAC-Com-Split-55to65kBTUh-SEER-14.0 | dxAC-Com-Split-55to65kBTUh-SEER-15.0 | Review |  | f | f |  | ErRobNc |  | HVAC-airAC |  | None | 2015-01-01
744 | NE-HVAC-airAC-Split-55to65kBtuh-16p0seer-wPreEcono | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, with Econo (Pre-existing vintages include Economizer) | DEER2015 | D15 v1.0 | 2014-10-08 | NE-HVAC-airAC-Split-55to65kBtuh-16p0seer-wPreEcono | DEER | Standard | [7 empty] | f | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER |  | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxAC-Com-Split-55to65kBTUh-SEER-14.0 | dxAC-Com-Split-55to65kBTUh-SEER-16.0 | Review |  | f | f |  | ErRobNc |  | HVAC-airAC |  | None | 2015-01-01
745 | NE-HVAC-airAC-Split-55to65kBtuh-17p0seer-wPreEcono | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, with Econo (Pre-existing vintages include Economizer) | DEER2015 | D15 v1.0 | 2014-10-08 | NE-HVAC-airAC-Split-55to65kBtuh-17p0seer-wPreEcono | DEER | Standard | [7 empty] | f | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER |  | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxAC-Com-Split-55to65kBTUh-SEER-14.0 | dxAC-Com-Split-55to65kBTUh-SEER-17.0 | Review |  | f | f |  | ErRobNc |  | HVAC-airAC |  | None | 2015-01-01
746 | NE-HVAC-airAC-Split-55to65kBtuh-18p0seer-wPreEcono | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, with Econo (Pre-existing vintages include Economizer) | DEER2015 | D15 v1.0 | 2014-10-08 | NE-HVAC-airAC-Split-55to65kBtuh-18p0seer-wPreEcono | DEER | Standard | [7 empty] | f | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER |  | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxAC-Com-Split-55to65kBTUh-SEER-14.0 | dxAC-Com-Split-55to65kBTUh-SEER-18.0 | Review |  | f | f |  | ErRobNc |  | HVAC-airAC |  | None | 2015-01-01
Residential Split AC
747 | RE-HV-ResAC-lt45kBtuh-15S | Residential SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan | DEER2015 | D15 v1.0 | 2014-10-08 | RE-HV-ResAC-lt45kBtuh-15S | DEER | Standard | None | 0 | 0 | None |  | f |  | f | Res | Any | HVAC | SpaceCool | dxAC_equip | spltSEER |  | HV-ResAC | Residential SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan; post-2001: SEER = 13 (EER = 11.08), one-speed fan; 2014: SEER = 14 (EER = 12.17), one-speed fan | Residential SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan | Residential SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan |  | dxAC-Res-Split-lt45kBTUh-SEER-14.0 | dxAC-Res-Split-SEER-15.0 | Review |  | f | f |  | ErRobNc |  | HV-ResAC |  | None | 2015-01-01
748 | RE-HV-ResAC-lt45kBtuh-16S | Residential SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan | DEER2015 | D15 v1.0 | 2014-10-08 | RE-HV-ResAC-lt45kBtuh-16S | DEER | Standard | None | 0 | 0 | None |  | f |  | f | Res | Any | HVAC | SpaceCool | dxAC_equip | spltSEER |  | HV-ResAC | Residential SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan; post-2001: SEER = 13 (EER = 11.08), one-speed fan; 2014: SEER = 14 (EER = 12.17), one-speed fan | Residential SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan | Residential SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan |  | dxAC-Res-Split-lt45kBTUh-SEER-14.0 | dxAC-Res-Split-SEER-16.0 | Review |  | f | f |  | ErRobNc |  | HV-ResAC |  | None | 2015-01-01
749 | RE-HV-ResAC-lt45kBtuh-17S | Residential SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan | DEER2015 | D15 v1.0 | 2014-10-08 | RE-HV-ResAC-lt45kBtuh-17S | DEER | Standard | None | 0 | 0 | None |  | f |  | f | Res | Any | HVAC | SpaceCool | dxAC_equip | spltSEER |  | HV-ResAC | Residential SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan; post-2001: SEER = 13 (EER = 11.08), one-speed fan; 2014: SEER = 14 (EER = 12.17), one-speed fan | Residential SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan | Residential SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan |  | dxAC-Res-Split-lt45kBTUh-SEER-14.0 | dxAC-Res-Split-SEER-17.0 | Review |  | f | f |  | ErRobNc |  | HV-ResAC |  | None | 2015-01-01
750 | RE-HV-ResAC-lt45kBtuh-18S | Residential SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan | DEER2015 | D15 v1.0 | 2014-10-08 | RE-HV-ResAC-lt45kBtuh-18S | DEER | Standard | None | 0 | 0 | None |  | f |  | f | Res | Any | HVAC | SpaceCool | dxAC_equip | spltSEER |  | HV-ResAC | Residential SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan; post-2001: SEER = 13 (EER = 11.08), one-speed fan; 2014: SEER = 14 (EER = 12.17), one-speed fan | Residential SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan | Residential SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan |  | dxAC-Res-Split-lt45kBTUh-SEER-14.0 | dxAC-Res-Split-SEER-18.0 | Review |  | f | f |  | ErRobNc |  | HV-ResAC |  | None | 2015-01-01
751 | RE-HV-ResAC-lt45kBtuh-19S | Residential SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 19 (EER = 14.8), EIR = 0.201, Fan W/CFM = 0.23, two-speed fan | DEER2015 | D15 v1.0 | 2014-10-08 | RE-HV-ResAC-lt45kBtuh-19S | DEER | Standard | None | 0 | 0 | None |  | f |  | f | Res | Any | HVAC | SpaceCool | dxAC_equip | spltSEER |  | HV-ResAC | Residential SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan; post-2001: SEER = 13 (EER = 11.08), one-speed fan; 2014: SEER = 14 (EER = 12.17), one-speed fan | Residential SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan | Residential SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 19 (EER = 14.8), EIR = 0.201, Fan W/CFM = 0.23, two-speed fan |  | dxAC-Res-Split-lt45kBTUh-SEER-14.0 | dxAC-Res-Split-SEER-19.0 | Review |  | f | f |  | ErRobNc |  | HV-ResAC |  | None | 2015-01-01
752 | RE-HV-ResAC-lt45kBtuh-20S | Residential SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 20 (EER = 15.6), EIR = 0.19, Fan W/CFM = 0.23, two-speed fan | DEER2015 | D15 v1.0 | 2014-10-08 | RE-HV-ResAC-lt45kBtuh-20S | DEER | Standard | None | 0 | 0 | None |  | f |  | f | Res | Any | HVAC | SpaceCool | dxAC_equip | spltSEER |  | HV-ResAC | Residential SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan; post-2001: SEER = 13 (EER = 11.08), one-speed fan; 2014: SEER = 14 (EER = 12.17), one-speed fan | Residential SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan | Residential SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 20 (EER = 15.6), EIR = 0.19, Fan W/CFM = 0.23, two-speed fan |  | dxAC-Res-Split-lt45kBTUh-SEER-14.0 | dxAC-Res-Split-SEER-20.0 | Review |  | f | f |  | ErRobNc |  | HV-ResAC |  | None | 2015-01-01
753 | RE-HV-ResAC-lt45kBtuh-21S | Residential SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 21 (EER = 16.4), EIR = 0.18, Fan W/CFM = 0.23, two-speed fan | DEER2015 | D15 v1.0 | 2014-10-08 | RE-HV-ResAC-lt45kBtuh-21S | DEER | Standard | None | 0 | 0 | None |  | f |  | f | Res | Any | HVAC | SpaceCool | dxAC_equip | spltSEER |  | HV-ResAC | Residential SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan; post-2001: SEER = 13 (EER = 11.08), one-speed fan; 2014: SEER = 14 (EER = 12.17), one-speed fan | Residential SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan | Residential SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 21 (EER = 16.4), EIR = 0.18, Fan W/CFM = 0.23, two-speed fan |  | dxAC-Res-Split-lt45kBTUh-SEER-14.0 | dxAC-Res-Split-SEER-21.0 | Review |  | f | f |  | ErRobNc |  | HV-ResAC |  | None | 2015-01-01
754 | RE-HV-ResEvapAC-lt45kBtuh-17p4S | Residential SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 17.4, one-speed fan, evaporative cooled condenser | DEER2015 | D15 v1.0 | 2014-10-08 | RE-HV-ResEvapAC-lt45kBtuh-17p4S | DEER | Standard | None | 0 | 0 | None |  | f |  | f | Res | Any | HVAC | SpaceCool | dxAC_equip | spltSEER |  | HV-ResAC | Residential SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan; post-2001: SEER = 13 (EER = 11.08), one-speed fan; 2014: SEER = 14 (EER = 12.17), one-speed fan | Residential SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan | Residential SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 17.4, one-speed fan, evaporative cooled condenser |  | dxAC-Res-Split-lt45kBTUh-SEER-14.0 | dxAC-Res-EvapAC-SEER-17.4 | Review
755 | RE-HV-ResAC-45to65kBtuh-15S | Residential SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan | DEER2015 | D15 v1.0 | 2014-10-08 | RE-HV-ResAC-45to65kBtuh-15S | DEER | Standard | None | 0 | 0 | None |  | f |  | f | Res | Any | HVAC | SpaceCool | dxAC_equip | spltSEER |  | HV-ResAC | Residential SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan; post-2001: SEER = 13 (EER = 11.08), one-speed fan; 2014: SEER = 14 (EER = 11.82), one-speed fan | Residential SEER-rated split Air Conditioners, Size Range: 45 - 65 kBTU/h, SEER = 14 (EER = 11.8), EIR = 0.247, Fan W/CFM = 0.29, one-speed fan | Residential SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan |  | dxAC-Res-Split-45to65kBTUh-SEER-14.0 | dxAC-Res-Split-SEER-15.0 | Review |  | f | f |  | ErRobNc |  | HV-ResAC |  | None | 2015-01-01
756 | RE-HV-ResAC-45to65kBtuh-16S | Residential SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan | DEER2015 | D15 v1.0 | 2014-10-08 | RE-HV-ResAC-45to65kBtuh-16S | DEER | Standard | None | 0 | 0 | None |  | f |  | f | Res | Any | HVAC | SpaceCool | dxAC_equip | spltSEER |  | HV-ResAC | Residential SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan; post-2001: SEER = 13 (EER = 11.08), one-speed fan; 2014: SEER = 14 (EER = 11.82), one-speed fan | Residential SEER-rated split Air Conditioners, Size Range: 45 - 65 kBTU/h, SEER = 14 (EER = 11.8), EIR = 0.247, Fan W/CFM = 0.29, one-speed fan | Residential SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan |  | dxAC-Res-Split-45to65kBTUh-SEER-14.0 | dxAC-Res-Split-SEER-16.0 | Review |  | f | f |  | ErRobNc |  | HV-ResAC |  | None | 2015-01-01
757 | RE-HV-ResAC-45to65kBtuh-17S | Residential SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan | DEER2015 | D15 v1.0 | 2014-10-08 | RE-HV-ResAC-45to65kBtuh-17S | DEER | Standard | None | 0 | 0 | None |  | f |  | f | Res | Any | HVAC | SpaceCool | dxAC_equip | spltSEER |  | HV-ResAC | Residential SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan; post-2001: SEER = 13 (EER = 11.08), one-speed fan; 2014: SEER = 14 (EER = 11.82), one-speed fan | Residential SEER-rated split Air Conditioners, Size Range: 45 - 65 kBTU/h, SEER = 14 (EER = 11.8), EIR = 0.247, Fan W/CFM = 0.29, one-speed fan | Residential SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan |  | dxAC-Res-Split-45to65kBTUh-SEER-14.0 | dxAC-Res-Split-SEER-17.0 | Review |  | f | f |  | ErRobNc |  | HV-ResAC |  | None | 2015-01-01
758 | RE-HV-ResAC-45to65kBtuh-18S | Residential SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan | DEER2015 | D15 v1.0 | 2014-10-08 | RE-HV-ResAC-45to65kBtuh-18S | DEER | Standard | None | 0 | 0 | None |  | f |  | f | Res | Any | HVAC | SpaceCool | dxAC_equip | spltSEER |  | HV-ResAC | Residential SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan; post-2001: SEER = 13 (EER = 11.08), one-speed fan; 2014: SEER = 14 (EER = 11.82), one-speed fan | Residential SEER-rated split Air Conditioners, Size Range: 45 - 65 kBTU/h, SEER = 14 (EER = 11.8), EIR = 0.247, Fan W/CFM = 0.29, one-speed fan | Residential SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan |  | dxAC-Res-Split-45to65kBTUh-SEER-14.0 | dxAC-Res-Split-SEER-18.0 | Review |  | f | f |  | ErRobNc |  | HV-ResAC |  | None | 2015-01-01
759 | RE-HV-ResAC-45to65kBtuh-19S | Residential SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 19 (EER = 14.8), EIR = 0.201, Fan W/CFM = 0.23, two-speed fan | DEER2015 | D15 v1.0 | 2014-10-08 | RE-HV-ResAC-45to65kBtuh-19S | DEER | Standard | None | 0 | 0 | None |  | f |  | f | Res | Any | HVAC | SpaceCool | dxAC_equip | spltSEER |  | HV-ResAC | Residential SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan; post-2001: SEER = 13 (EER = 11.08), one-speed fan; 2014: SEER = 14 (EER = 11.82), one-speed fan | Residential SEER-rated split Air Conditioners, Size Range: 45 - 65 kBTU/h, SEER = 14 (EER = 11.8), EIR = 0.247, Fan W/CFM = 0.29, one-speed fan | Residential SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 19 (EER = 14.8), EIR = 0.201, Fan W/CFM = 0.23, two-speed fan |  | dxAC-Res-Split-45to65kBTUh-SEER-14.0 | dxAC-Res-Split-SEER-19.0 | Review |  | f | f |  | ErRobNc |  | HV-ResAC |  | None | 2015-01-01
760 | RE-HV-ResAC-45to65kBtuh-20S | Residential SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 20 (EER = 15.6), EIR = 0.19, Fan W/CFM = 0.23, two-speed fan | DEER2015 | D15 v1.0 | 2014-10-08 | RE-HV-ResAC-45to65kBtuh-20S | DEER | Standard | None | 0 | 0 | None |  | f |  | f | Res | Any | HVAC | SpaceCool | dxAC_equip | spltSEER |  | HV-ResAC | Residential SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan; post-2001: SEER = 13 (EER = 11.08), one-speed fan; 2014: SEER = 14 (EER = 11.82), one-speed fan | Residential SEER-rated split Air Conditioners, Size Range: 45 - 65 kBTU/h, SEER = 14 (EER = 11.8), EIR = 0.247, Fan W/CFM = 0.29, one-speed fan | Residential SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 20 (EER = 15.6), EIR = 0.19, Fan W/CFM = 0.23, two-speed fan |  | dxAC-Res-Split-45to65kBTUh-SEER-14.0 | dxAC-Res-Split-SEER-20.0 | Review |  | f | f |  | ErRobNc |  | HV-ResAC |  | None | 2015-01-01
761 | RE-HV-ResAC-45to65kBtuh-21S | Residential SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 21 (EER = 16.4), EIR = 0.18, Fan W/CFM = 0.23, two-speed fan | DEER2015 | D15 v1.0 | 2014-10-08 | RE-HV-ResAC-45to65kBtuh-21S | DEER | Standard | None | 0 | 0 | None |  | f |  | f | Res | Any | HVAC | SpaceCool | dxAC_equip | spltSEER |  | HV-ResAC | Residential SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan; post-2001: SEER = 13 (EER = 11.08), one-speed fan; 2014: SEER = 14 (EER = 11.82), one-speed fan | Residential SEER-rated split Air Conditioners, Size Range: 45 - 65 kBTU/h, SEER = 14 (EER = 11.8), EIR = 0.247, Fan W/CFM = 0.29, one-speed fan | Residential SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 21 (EER = 16.4), EIR = 0.18, Fan W/CFM = 0.23, two-speed fan |  | dxAC-Res-Split-45to65kBTUh-SEER-14.0 | dxAC-Res-Split-SEER-21.0 | Review |  | f | f |  | ErRobNc |  | HV-ResAC |  | None | 2015-01-01
762 | RE-HV-ResEvapAC-45to65kBtuh-17p4S | Residential SEER-rated split Heat Pumps, SEER = 17 (EER = 13.3), HSPF = 9.4 (COP = 3.74), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan | DEER2015 | D15 v1.0 | 2014-10-08 | RE-HV-ResEvapAC-45to65kBtuh-17p4S | DEER | Standard | None | 0 | 0 | None |  | f |  | f | Res | Any | HVAC | SpaceCool | dxAC_equip | spltSEER |  | HV-ResAC | Residential SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan; post-2001: SEER = 13 (EER = 11.08), one-speed fan; 2014: SEER = 14 (EER = 11.82), one-speed fan | Residential SEER-rated split Air Conditioners, Size Range: 45 - 65 kBTU/h, SEER = 14 (EER = 11.8), EIR = 0.247, Fan W/CFM = 0.29, one-speed fan | Residential SEER-rated split Heat Pumps, SEER = 17 (EER = 13.3), HSPF = 9.4 (COP = 3.74), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan |  | dxAC-Res-Split-45to65kBTUh-SEER-14.0 | dxHP-Res-Split-SEER-17.0 | Review
Residential Split HP
763 | RE-HV-ResHP-15p0S-8p7H | Residential SEER-rated split Heat Pumps, SEER = 15 (EER = 12.8), HSPF = 8.7 (COP = 3.68), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan | DEER2015 | D15 v1.0 | 2014-10-08 | RE-HV-ResHP-15p0S-8p7H | DEER | Standard | None | 0 | 0 | None |  | f |  | f | Res | Any | HVAC | HeatCool | dxHP_equip | spltSEER |  | HVAC-airHP | Res SEER-Rated Splt HP, 7.1-3.01 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan; 2014: SEER = 14 (HSPF = 8.2), one-speed fan | Residential SEER-rated split Heat Pumps, SEER = 14 (EER = 11.9), HSPF = 8.2 (COP = 3.48), EIR = 0.245, Fan W/CFM = 0.29, one-speed fan | Residential SEER-rated split Heat Pumps, SEER = 15 (EER = 12.8), HSPF = 8.7 (COP = 3.68), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan |  | dxHP-Res-Split-SEER-14.0 | dxHP-Res-Split-SEER-15.0 | Review |  | f | f |  | ErRobNc |  | HVAC-airHP |  | None | 2015-01-01
764 | RE-HV-ResHP-16p0S-9p0H | Residential SEER-rated split Heat Pumps, SEER = 16 (EER = 12.5), HSPF = 9 (COP = 3.57), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan | DEER2015 | D15 v1.0 | 2014-10-08 | RE-HV-ResHP-16p0S-9p0H | DEER | Standard | None | 0 | 0 | None |  | f |  | f | Res | Any | HVAC | HeatCool | dxHP_equip | spltSEER |  | HVAC-airHP | Res SEER-Rated Splt HP, 7.1-3.01 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan; 2014: SEER = 14 (HSPF = 8.2), one-speed fan | Residential SEER-rated split Heat Pumps, SEER = 14 (EER = 11.9), HSPF = 8.2 (COP = 3.48), EIR = 0.245, Fan W/CFM = 0.29, one-speed fan | Residential SEER-rated split Heat Pumps, SEER = 16 (EER = 12.5), HSPF = 9 (COP = 3.57), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan |  | dxHP-Res-Split-SEER-14.0 | dxHP-Res-Split-SEER-16.0 | Review |  | f | f |  | ErRobNc |  | HVAC-airHP |  | None | 2015-01-01
765 | RE-HV-ResHP-17p0S-9p4H | Residential SEER-rated split Heat Pumps, SEER = 17 (EER = 13.3), HSPF = 9.4 (COP = 3.74), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan | DEER2015 | D15 v1.0 | 2014-10-08 | RE-HV-ResHP-17p0S-9p4H | DEER | Standard | None | 0 | 0 | None |  | f |  | f | Res | Any | HVAC | HeatCool | dxHP_equip | spltSEER |  | HVAC-airHP | Res SEER-Rated Splt HP, 7.1-3.01 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan; 2014: SEER = 14 (HSPF = 8.2), one-speed fan | Residential SEER-rated split Heat Pumps, SEER = 14 (EER = 11.9), HSPF = 8.2 (COP = 3.48), EIR = 0.245, Fan W/CFM = 0.29, one-speed fan | Residential SEER-rated split Heat Pumps, SEER = 17 (EER = 13.3), HSPF = 9.4 (COP = 3.74), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan |  | dxHP-Res-Split-SEER-14.0 | dxHP-Res-Split-SEER-17.0 | Review |  | f | f |  | ErRobNc |  | HVAC-airHP |  | None | 2015-01-01
766 | RE-HV-ResHP-18p0S-9p7H | Residential SEER-rated split Heat Pumps, SEER = 18 (EER = 14), HSPF = 9.7 (COP = 3.86), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan | DEER2015 | D15 v1.0 | 2014-10-08 | RE-HV-ResHP-18p0S-9p7H | DEER | Standard | None | 0 | 0 | None |  | f |  | f | Res | Any | HVAC | HeatCool | dxHP_equip | spltSEER |  | HVAC-airHP | Res SEER-Rated Splt HP, 7.1-3.01 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan; 2014: SEER = 14 (HSPF = 8.2), one-speed fan | Residential SEER-rated split Heat Pumps, SEER = 14 (EER = 11.9), HSPF = 8.2 (COP = 3.48), EIR = 0.245, Fan W/CFM = 0.29, one-speed fan | Residential SEER-rated split Heat Pumps, SEER = 18 (EER = 14), HSPF = 9.7 (COP = 3.86), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan |  | dxHP-Res-Split-SEER-14.0 | dxHP-Res-Split-SEER-18.0 | Review |  | f | f |  | ErRobNc |  | HVAC-airHP |  | None | 2015-01-01
Commercial SEER-rated Packaged HP
767 | NE-HVAC-airHP-Pkg-lt55kBtuh-15p0seer-8p2hspf | Commercial SEER-rated Packaged Heat Pumps, Size Range: 18 - 65 kBTU/h, SEER = 15 (HSPF = 8.2), EIR = 0.226, Fan W/CFM = 0.29, one-speed fan, without Econo | DEER2015 | D15 v1.0 | 2014-10-21 | NE-HVAC-airHP-Pkg-lt55kBtuh-15p0seer-8p2hspf | DEER | Standard | None | 0 | 0 | None |  | f |  | f | Com | Any | HVAC | HeatCool | dxHP_equip | pkgSEER |  | HVAC-airHP | Com SEER-Rated Pkg HP, 18-65 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan, no Econo; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan, no Econo; 2014: SEER = 14 (HSPF = 8), one-speed fan, no Econo | Commercial SEER-rated Packaged Heat Pumps, Size Range: 18 - 55 kBTU/h, SEER = 14 (HSPF = 8.0), EIR = 0.245, Fan W/CFM = 0.29, one-speed fan, without Econo | Commercial SEER-rated Packaged Heat Pumps, Size Range: 18 - 65 kBTU/h, SEER = 15 (HSPF = 8.2), EIR = 0.226, Fan W/CFM = 0.29, one-speed fan, without Econo |  | dxHP-Com-Pkg-lt55kBTUh-SEER-14.0 | dxHP-Com-Pkg-lt55kBTUh-SEER-15.0 | Review |  | f | f |  | ErRobNc |  | HVAC-airHP |  | None | 2015-01-01
768 | NE-HVAC-airHP-Pkg-lt55kBtuh-16p0seer-8p5hspf | Commercial SEER-rated Packaged Heat Pumps, Size Range: 18 - 65 kBTU/h, SEER = 16 (HSPF = 8.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, without Econo | DEER2015 | D15 v1.0 | 2014-10-21 | NE-HVAC-airHP-Pkg-lt55kBtuh-16p0seer-8p5hspf | DEER | Standard | None | 0 | 0 | None |  | f |  | f | Com | Any | HVAC | HeatCool | dxHP_equip | pkgSEER |  | HVAC-airHP | Com SEER-Rated Pkg HP, 18-65 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan, no Econo; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan, no Econo; 2014: SEER = 14 (HSPF = 8), one-speed fan, no Econo | Commercial SEER-rated Packaged Heat Pumps, Size Range: 18 - 55 kBTU/h, SEER = 14 (HSPF = 8.0), EIR = 0.245, Fan W/CFM = 0.29, one-speed fan, without Econo | Commercial SEER-rated Packaged Heat Pumps, Size Range: 18 - 65 kBTU/h, SEER = 16 (HSPF = 8.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, without Econo |  | dxHP-Com-Pkg-lt55kBTUh-SEER-14.0 | dxHP-Com-Pkg-lt55kBTUh-SEER-16.0 | Review |  | f | f |  | ErRobNc |  | HVAC-airHP |  | None | 2015-01-01
769 | NE-HVAC-airHP-Pkg-lt55kBtuh-17p0seer-9p0hspf | Commercial SEER-rated Packaged Heat Pumps, Size Range: 18 - 65 kBTU/h, SEER = 17 (HSPF = 9.0), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, without Econo | DEER2015 | D15 v1.0 | 2014-10-21 | NE-HVAC-airHP-Pkg-lt55kBtuh-17p0seer-9p0hspf | DEER | Standard | None | 0 | 0 | None |  | f |  | f | Com | Any | HVAC | HeatCool | dxHP_equip | pkgSEER |  | HVAC-airHP | Com SEER-Rated Pkg HP, 18-65 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan, no Econo; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan, no Econo; 2014: SEER = 14 (HSPF = 8), one-speed fan, no Econo | Commercial SEER-rated Packaged Heat Pumps, Size Range: 18 - 55 kBTU/h, SEER = 14 (HSPF = 8.0), EIR = 0.245, Fan W/CFM = 0.29, one-speed fan, without Econo | Commercial SEER-rated Packaged Heat Pumps, Size Range: 18 - 65 kBTU/h, SEER = 17 (HSPF = 9.0), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, without Econo |  | dxHP-Com-Pkg-lt55kBTUh-SEER-14.0 | dxHP-Com-Pkg-lt55kBTUh-SEER-17.0 | Review |  | f | f |  | ErRobNc |  | HVAC-airHP |  | None | 2015-01-01
770 | NE-HVAC-airHP-Pkg-55to65kBtuh-15p0seer-8p2hspf | Commercial SEER-rated Packaged Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 15 (HSPF = 8.2), EIR = 0.256, Fan W/CFM = 0.25, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 2014-10-21 | NE-HVAC-airHP-Pkg-55to65kBtuh-15p0seer-8p2hspf | DEER | Standard | None | 0 | 0 | None |  | f |  | f | Com | Any | HVAC | HeatCool | dxHP_equip | pkgSEER |  | HVAC-airHP | Com SEER-Rated Pkg HP, 18-65 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan, no Econo; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan, no Econo; 2014: SEER = 14 (HSPF = 8), two-speed fan, w/Econo | Commercial SEER-rated Packaged Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 14 (HSPF = 8.0), EIR = 0.27, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated Packaged Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 15 (HSPF = 8.2), EIR = 0.256, Fan W/CFM = 0.25, two-speed fan, with Econo |  | dxHP-Com-Pkg-55to65kBTUh-SEER-14.0 | dxHP-Com-Pkg-55to65kBTUh-SEER-15.0 | Review |  | f | f |  | ErRobNc |  | HVAC-airHP |  | None | 2015-01-01
771 | NE-HVAC-airHP-Pkg-55to65kBtuh-16p0seer-8p5hspf | Commercial SEER-rated Packaged Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 16 (HSPF = 8.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 2014-10-21 | NE-HVAC-airHP-Pkg-55to65kBtuh-16p0seer-8p5hspf | DEER | Standard | None | 0 | 0 | None |  | f |  | f | Com | Any | HVAC | HeatCool | dxHP_equip | pkgSEER |  | HVAC-airHP | Com SEER-Rated Pkg HP, 18-65 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan, no Econo; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan, no Econo; 2014: SEER = 14 (HSPF = 8), two-speed fan, w/Econo | Commercial SEER-rated Packaged Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 14 (HSPF = 8.0), EIR = 0.27, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated Packaged Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 16 (HSPF = 8.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxHP-Com-Pkg-55to65kBTUh-SEER-14.0 | dxHP-Com-Pkg-55to65kBTUh-SEER-16.0 | Review |  | f | f |  | ErRobNc |  | HVAC-airHP |  | None | 2015-01-01
772 | NE-HVAC-airHP-Pkg-55to65kBtuh-17p0seer-9p0hspf | Commercial SEER-rated Packaged Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 17 (HSPF = 9.0), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 2014-10-21 | NE-HVAC-airHP-Pkg-55to65kBtuh-17p0seer-9p0hspf | DEER | Standard | None | 0 | 0 | None |  | f |  | f | Com | Any | HVAC | HeatCool | dxHP_equip | pkgSEER |  | HVAC-airHP | Com SEER-Rated Pkg HP, 18-65 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan, no Econo; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan, no Econo; 2014: SEER = 14 (HSPF = 8), two-speed fan, w/Econo | Commercial SEER-rated Packaged Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 14 (HSPF = 8.0), EIR = 0.27, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated Packaged Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 17 (HSPF = 9.0), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxHP-Com-Pkg-55to65kBTUh-SEER-14.0 | dxHP-Com-Pkg-55to65kBTUh-SEER-17.0 | Review |  | f | f |  | ErRobNc |  | HVAC-airHP |  | None | 2015-01-01
773 | NE-HVAC-airHP-Pkg-55to65kBtuh-15p0seer-8p2hspf-wPreEcono | Commercial SEER-rated Packaged Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 15 (HSPF = 8.2), EIR = 0.256, Fan W/CFM = 0.25, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 2014-10-21 | NE-HVAC-airHP-Pkg-55to65kBtuh-15p0seer-8p2hspf-wPreEcono | DEER | Standard | None | 0 | 0 | None |  | f |  | f | Com | Any | HVAC | HeatCool | dxHP_equip | pkgSEER |  | HVAC-airHP | Com SEER-Rated Pkg HP, 18-65 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan, w/Econo; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan, w/Econo; 2014: SEER = 14 (HSPF = 8), two-speed fan, w/Econo | Commercial SEER-rated Packaged Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 14 (HSPF = 8.0), EIR = 0.27, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated Packaged Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 15 (HSPF = 8.2), EIR = 0.256, Fan W/CFM = 0.25, two-speed fan, with Econo |  | dxHP-Com-Pkg-55to65kBTUh-SEER-14.0 | dxHP-Com-Pkg-55to65kBTUh-SEER-15.0 | Review |  | f | f |  | ErRobNc |  | HVAC-airHP |  | None | 2015-01-01
774 | NE-HVAC-airHP-Pkg-55to65kBtuh-16p0seer-8p5hspf-wPreEcono | Commercial SEER-rated Packaged Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 16 (HSPF = 8.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 2014-10-21 | NE-HVAC-airHP-Pkg-55to65kBtuh-16p0seer-8p5hspf-wPreEcono | DEER | Standard | None | 0 | 0 | None |  | f |  | f | Com | Any | HVAC | HeatCool | dxHP_equip | pkgSEER |  | HVAC-airHP | Com SEER-Rated Pkg HP, 18-65 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan, w/Econo; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan, w/Econo; 2014: SEER = 14 (HSPF = 8), two-speed fan, w/Econo | Commercial SEER-rated Packaged Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 14 (HSPF = 8.0), EIR = 0.27, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated Packaged Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 16 (HSPF = 8.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxHP-Com-Pkg-55to65kBTUh-SEER-14.0 | dxHP-Com-Pkg-55to65kBTUh-SEER-16.0 | Review |  | f | f |  | ErRobNc |  | HVAC-airHP |  | None | 2015-01-01
775 | NE-HVAC-airHP-Pkg-55to65kBtuh-17p0seer-9p0hspf-wPreEcono | Commercial SEER-rated Packaged Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 17 (HSPF = 9.0), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 2014-10-21 | NE-HVAC-airHP-Pkg-55to65kBtuh-17p0seer-9p0hspf-wPreEcono | DEER | Standard | None | 0 | 0 | None |  | f |  | f | Com | Any | HVAC | HeatCool | dxHP_equip | pkgSEER |  | HVAC-airHP | Com SEER-Rated Pkg HP, 18-65 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan, w/Econo; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan, w/Econo; 2014: SEER = 14 (HSPF = 8), two-speed fan, w/Econo | Commercial SEER-rated Packaged Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 14 (HSPF = 8.0), EIR = 0.27, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated Packaged Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 17 (HSPF = 9.0), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxHP-Com-Pkg-55to65kBTUh-SEER-14.0 | dxHP-Com-Pkg-55to65kBTUh-SEER-17.0 | Review |  | f | f |  | ErRobNc |  | HVAC-airHP |  | None | 2015-01-01
Commercial SEER-rated Split HP
776 | NE-HVAC-airHP-Split-lt55kBtuh-15p0seer-8p7hspf | Commercial SEER-rated Split Heat Pumps, Size Range: 18 - 65 kBTU/h, SEER = 15 (HSPF = 8.7), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo | DEER2015 | D15 v1.0 | 2014-10-21 | NE-HVAC-airHP-Split-lt55kBtuh-15p0seer-8p7hspf | DEER | Standard | None | 0 | 0 | None |  | f |  | f | Com | Any | HVAC | HeatCool | dxHP_equip | spltSEER |  | HVAC-airHP | Com SEER-Rated Split HP, 18-65 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan, no Econo; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan, no Econo; 2014: SEER = 14 (HSPF = 8.2), one-speed fan, no Econo | Commercial SEER-rated Split Heat Pumps, Size Range: 18 - 55 kBTU/h, SEER = 14 (HSPF = 8.2), EIR = 0.245, Fan W/CFM = 0.29, one-speed fan, without Econo | Commercial SEER-rated Split Heat Pumps, Size Range: 18 - 65 kBTU/h, SEER = 15 (HSPF = 8.7), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo |  | dxHP-Com-Split-lt55kBTUh-SEER-14.0 | dxHP-Com-Split-lt55kBTUh-SEER-15.0 | Review |  | f | f |  | ErRobNc |  | HVAC-airHP |  | None | 2015-01-01
777 | NE-HVAC-airHP-Split-lt55kBtuh-16p0seer-9p0hspf | Commercial SEER-rated Split Heat Pumps, Size Range: 18 - 65 kBTU/h, SEER = 16 (HSPF = 9.0), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, without Econo | DEER2015 | D15 v1.0 | 2014-10-21 | NE-HVAC-airHP-Split-lt55kBtuh-16p0seer-9p0hspf | DEER | Standard | None | 0 | 0 | None |  | f |  | f | Com | Any | HVAC | HeatCool | dxHP_equip | spltSEER |  | HVAC-airHP | Com SEER-Rated Split HP, 18-65 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan, no Econo; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan, no Econo; 2014: SEER = 14 (HSPF = 8.2), one-speed fan, no Econo | Commercial SEER-rated Split Heat Pumps, Size Range: 18 - 55 kBTU/h, SEER = 14 (HSPF = 8.2), EIR = 0.245, Fan W/CFM = 0.29, one-speed fan, without Econo | Commercial SEER-rated Split Heat Pumps, Size Range: 18 - 65 kBTU/h, SEER = 16 (HSPF = 9.0), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, without Econo |  | dxHP-Com-Split-lt55kBTUh-SEER-14.0 | dxHP-Com-Split-lt55kBTUh-SEER-16.0 | Review |  | f | f |  | ErRobNc |  | HVAC-airHP |  | None | 2015-01-01
778 | NE-HVAC-airHP-Split-lt55kBtuh-17p0seer-9p4hspf | Commercial SEER-rated Split Heat Pumps, Size Range: 18 - 65 kBTU/h, SEER = 17 (HSPF = 9.4), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, without Econo | DEER2015 | D15 v1.0 | 2014-10-21 | NE-HVAC-airHP-Split-lt55kBtuh-17p0seer-9p4hspf | DEER | Standard | None | 0 | 0 | None |  | f |  | f | Com | Any | HVAC | HeatCool | dxHP_equip | spltSEER |  | HVAC-airHP | Com SEER-Rated Split HP, 18-65 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan, no Econo; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan, no Econo; 2014: SEER = 14 (HSPF = 8.2), one-speed fan, no Econo | Commercial SEER-rated Split Heat Pumps, Size Range: 18 - 55 kBTU/h, SEER = 14 (HSPF = 8.2), EIR = 0.245, Fan W/CFM = 0.29, one-speed fan, without Econo | Commercial SEER-rated Split Heat Pumps, Size Range: 18 - 65 kBTU/h, SEER = 17 (HSPF = 9.4), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, without Econo |  | dxHP-Com-Split-lt55kBTUh-SEER-14.0 | dxHP-Com-Split-lt55kBTUh-SEER-17.0 | Review |  | f | f |  | ErRobNc |  | HVAC-airHP |  | None | 2015-01-01
779 | NE-HVAC-airHP-Split-lt55kBtuh-18p0seer-9p7hspf | Commercial SEER-rated Split Heat Pumps, Size Range: 18 - 65 kBTU/h, SEER = 18 (HSPF = 9.7), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, without Econo | DEER2015 | D15 v1.0 | 2014-10-21 | NE-HVAC-airHP-Split-lt55kBtuh-18p0seer-9p7hspf | DEER | Standard | None | 0 | 0 | None |  | f |  | f | Com | Any | HVAC | HeatCool | dxHP_equip | spltSEER |  | HVAC-airHP | Com SEER-Rated Split HP, 18-65 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan, no Econo; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan, no Econo; 2014: SEER = 14 (HSPF = 8.2), one-speed fan, no Econo | Commercial SEER-rated Split Heat Pumps, Size Range: 18 - 55 kBTU/h, SEER = 14 (HSPF = 8.2), EIR = 0.245, Fan W/CFM = 0.29, one-speed fan, without Econo | Commercial SEER-rated Split Heat Pumps, Size Range: 18 - 65 kBTU/h, SEER = 18 (HSPF = 9.7), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, without Econo |  | dxHP-Com-Split-lt55kBTUh-SEER-14.0 | dxHP-Com-Split-lt55kBTUh-SEER-18.0 | Review |  | f | f |  | ErRobNc |  | HVAC-airHP |  | None | 2015-01-01
780 | NE-HVAC-airHP-Split-55to65kBtuh-15p0seer-8p7hspf | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 15 (HSPF = 8.7), EIR = 0.256, Fan W/CFM = 0.25, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 2014-10-21 | NE-HVAC-airHP-Split-55to65kBtuh-15p0seer-8p7hspf | DEER | Standard | None | 0 | 0 | None |  | f |  | f | Com | Any | HVAC | HeatCool | dxHP_equip | spltSEER |  | HVAC-airHP | Com SEER-Rated Split HP, 18-65 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan, no Econo; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan, no Econo; 2014: SEER = 14 (HSPF = 8.2), two-speed fan, w/Econo | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 14 (HSPF = 8.2), EIR = 0.27, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 15 (HSPF = 8.7), EIR = 0.256, Fan W/CFM = 0.25, two-speed fan, with Econo |  | dxHP-Com-Split-55to65kBTUh-SEER-14.0 | dxHP-Com-Split-55to65kBTUh-SEER-15.0 | Review |  | f | f |  | ErRobNc |  | HVAC-airHP |  | None | 2015-01-01
781 | NE-HVAC-airHP-Split-55to65kBtuh-16p0seer-9p0hspf | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 16 (HSPF = 9.0), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 2014-10-21 | NE-HVAC-airHP-Split-55to65kBtuh-16p0seer-9p0hspf | DEER | Standard | None | 0 | 0 | None |  | f |  | f | Com | Any | HVAC | HeatCool | dxHP_equip | spltSEER |  | HVAC-airHP | Com SEER-Rated Split HP, 18-65 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan, no Econo; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan, no Econo; 2014: SEER = 14 (HSPF = 8.2), two-speed fan, w/Econo | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 14 (HSPF = 8.2), EIR = 0.27, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 16 (HSPF = 9.0), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxHP-Com-Split-55to65kBTUh-SEER-14.0 | dxHP-Com-Split-55to65kBTUh-SEER-16.0 | Review |  | f | f |  | ErRobNc |  | HVAC-airHP |  | None | 2015-01-01
782 | NE-HVAC-airHP-Split-55to65kBtuh-17p0seer-9p4hspf | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 17 (HSPF = 9.4), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 2014-10-21 | NE-HVAC-airHP-Split-55to65kBtuh-17p0seer-9p4hspf | DEER | Standard | None | 0 | 0 | None |  | f |  | f | Com | Any | HVAC | HeatCool | dxHP_equip | spltSEER |  | HVAC-airHP | Com SEER-Rated Split HP, 18-65 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan, no Econo; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan, no Econo; 2014: SEER = 14 (HSPF = 8.2), two-speed fan, w/Econo | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 14 (HSPF = 8.2), EIR = 0.27, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 17 (HSPF = 9.4), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxHP-Com-Split-55to65kBTUh-SEER-14.0 | dxHP-Com-Split-55to65kBTUh-SEER-17.0 | Review |  | f | f |  | ErRobNc |  | HVAC-airHP |  | None | 2015-01-01
783 | NE-HVAC-airHP-Split-55to65kBtuh-18p0seer-9p7hspf | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 18 (HSPF = 9.7), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 2014-10-21 | NE-HVAC-airHP-Split-55to65kBtuh-18p0seer-9p7hspf | DEER | Standard | None | 0 | 0 | None |  | f |  | f | Com | Any | HVAC | HeatCool | dxHP_equip | spltSEER |  | HVAC-airHP | Com SEER-Rated Split HP, 18-65 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan, no Econo; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan, no Econo; 2014: SEER = 14 (HSPF = 8.2), two-speed fan, w/Econo | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 14 (HSPF = 8.2), EIR = 0.27, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 18 (HSPF = 9.7), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxHP-Com-Split-55to65kBTUh-SEER-14.0 | dxHP-Com-Split-55to65kBTUh-SEER-18.0 | Review |  | f | f |  | ErRobNc |  | HVAC-airHP |  | None | 2015-01-01
784 | NE-HVAC-airHP-Split-55to65kBtuh-15p0seer-8p7hspf-wPreEcono | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 15 (HSPF = 8.7), EIR = 0.256, Fan W/CFM = 0.25, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 2014-10-21 | NE-HVAC-airHP-Split-55to65kBtuh-15p0seer-8p7hspf-wPreEcono | DEER | Standard | None | 0 | 0 | None |  | f |  | f | Com | Any | HVAC | HeatCool | dxHP_equip | spltSEER |  | HVAC-airHP | Com SEER-Rated Split HP, 18-65 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan, w/Econo; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan, w/Econo; 2014: SEER = 14 (HSPF = 8.2), two-speed fan, w/Econo | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 14 (HSPF = 8.2), EIR = 0.27, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 15 (HSPF = 8.7), EIR = 0.256, Fan W/CFM = 0.25, two-speed fan, with Econo |  | dxHP-Com-Split-55to65kBTUh-SEER-14.0 | dxHP-Com-Split-55to65kBTUh-SEER-15.0 | Review |  | f | f |  | ErRobNc |  | HVAC-airHP |  | None | 2015-01-01
785 | NE-HVAC-airHP-Split-55to65kBtuh-16p0seer-9p0hspf-wPreEcono | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 16 (HSPF = 9.0), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 2014-10-21 | NE-HVAC-airHP-Split-55to65kBtuh-16p0seer-9p0hspf-wPreEcono | DEER | Standard | None | 0 | 0 | None |  | f |  | f | Com | Any | HVAC | HeatCool | dxHP_equip | spltSEER |  | HVAC-airHP | Com SEER-Rated Split HP, 18-65 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan, w/Econo; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan, w/Econo; 2014: SEER = 14 (HSPF = 8.2), two-speed fan, w/Econo | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 14 (HSPF = 8.2), EIR = 0.27, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 16 (HSPF = 9.0), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxHP-Com-Split-55to65kBTUh-SEER-14.0 | dxHP-Com-Split-55to65kBTUh-SEER-16.0 | Review |  | f | f |  | ErRobNc |  | HVAC-airHP |  | None | 2015-01-01
786 | NE-HVAC-airHP-Split-55to65kBtuh-17p0seer-9p4hspf-wPreEcono | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 17 (HSPF = 9.4), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 2014-10-21 | NE-HVAC-airHP-Split-55to65kBtuh-17p0seer-9p4hspf-wPreEcono | DEER | Standard | None | 0 | 0 | None |  | f |  | f | Com | Any | HVAC | HeatCool | dxHP_equip | spltSEER |  | HVAC-airHP | Com SEER-Rated Split HP, 18-65 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan, w/Econo; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan, w/Econo; 2014: SEER = 14 (HSPF = 8.2), two-speed fan, w/Econo | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 14 (HSPF = 8.2), EIR = 0.27, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 17 (HSPF = 9.4), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxHP-Com-Split-55to65kBTUh-SEER-14.0 | dxHP-Com-Split-55to65kBTUh-SEER-17.0 | Review |  | f | f |  | ErRobNc |  | HVAC-airHP |  | None | 2015-01-01
787 | NE-HVAC-airHP-Split-55to65kBtuh-18p0seer-9p7hspf-wPreEcono | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 18 (HSPF = 9.7), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 2014-10-21 | NE-HVAC-airHP-Split-55to65kBtuh-18p0seer-9p7hspf-wPreEcono | DEER | Standard | None | 0 | 0 | None |  | f |  | f | Com | Any | HVAC | HeatCool | dxHP_equip | spltSEER |  | HVAC-airHP | Com SEER-Rated Split HP, 18-65 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan, w/Econo; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan, w/Econo; 2014: SEER = 14 (HSPF = 8.2), two-speed fan, w/Econo | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 14 (HSPF = 8.2), EIR = 0.27, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 18 (HSPF = 9.7), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxHP-Com-Split-55to65kBTUh-SEER-14.0 | dxHP-Com-Split-55to65kBTUh-SEER-18.0 | Review |  | f | f |  | ErRobNc |  | HVAC-airHP |  | None | 2015-01-01

## Technologies
DEER2015 HVAC Technology Definitions
This table defines the key equipment parameters for all technologies referenced by the updated measures.
| EER-Rated Pkg AC |  |  |  | 5 |  |  |  | 8 | 9 | 10 | 11
UnitID | EER-rated packaged Air Conditioner | Version | Case | IEER | EER | Min_CoolCap | Max_CoolCap | CondType | SensCapRatio | COOLING-EIR | CFMperTon | WperCFM | CrankRatio | CRANKCASE-MAX-T | Economizer | Fan_spd | BldgHVAC | PerfCurveID | Technology Description | Pre-existing technology Description (lookup is based on Code ID)
31001 | dxAC-Com-Pkg-65to110kBTUh-EER11.0 | DEER2015 | Code/Standard | 13.4 | 11 | 65 | 110 | Air | 0.663 | 0.27299 | 318 | 0.4 | 0 | 100 | TRUE | two-speed | cDXGF |  | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 11 (IEER = 13.4), EIR = 0.273, Fan W/CFM = 0.4, two-speed fan, with Econo | EER-Rated Pkg AC, 65-110 kBTU/h; Pre-2005: EER = 10.1, one-speed fan, no Econo; 2006 - 2009: EER = 10.1, one-speed fan, no Econo; 2010 - 2013: EER = 11, one-speed fan, no Econo; 2014 - 2015: EER = 11 (IEER = 13.4), two-speed fan, w/Econo |  | EER-Rated Pkg AC, 65-110 kBTU/h; Pre-2005: EER = 10.1, one-speed fan, w/Econo; 2006 - 2009: EER = 10.1, one-speed fan, w/Econo; 2010 - 2013: EER = 11, one-speed fan, w/Econo; 2014 - 2015: EER = 11 (IEER = 13.4), two-speed fan, w/Econo
31101 | dxAC-Com-Pkg-65to110kBTUh-EER11.5 | DEER2015 | Measure | 14.1 | 11.5 | 65 | 110 | Air | 0.663 | 0.25964 | 318 | 0.4 | 0 | 100 | TRUE | two-speed | cDXGF |  | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 11.5 (IEER = 14.1), EIR = 0.26, Fan W/CFM = 0.4, two-speed fan, with Econo
31201 | dxAC-Com-Pkg-65to110kBTUh-EER12.0 | DEER2015 | Measure | 14.8 | 12 | 65 | 110 | Air | 0.663 | 0.24716 | 318 | 0.4 | 0 | 100 | TRUE | two-speed | cDXGF |  | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 12 (IEER = 14.8), EIR = 0.247, Fan W/CFM = 0.4, two-speed fan, with Econo
31301 | dxAC-Com-Pkg-65to110kBTUh-EER13.0 | DEER2015 | Measure | 16.3 | 13 | 65 | 110 | Air | 0.663 | 0.22552 | 318 | 0.4 | 0 | 100 | TRUE | two-speed | cDXGF |  | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 13 (IEER = 16.3), EIR = 0.226, Fan W/CFM = 0.4, two-speed fan, with Econo
32001 | dxAC-Com-Pkg-110to135kBTUh-EER11.0 | DEER2015 | Code/Standard | 13.3 | 11 | 110 | 135 | Air | 0.663 | 0.27299 | 318 | 0.4 | 0 | 100 | TRUE | two-speed | cDXGF |  | EER-rated packaged Air Conditioner, Size Range: 110 - 135 kBTU/h, EER = 11 (IEER = 13.3), EIR = 0.273, Fan W/CFM = 0.4, two-speed fan, with Econo | EER-Rated Pkg AC, 110-135 kBTU/h; Pre-2005: EER = 10.1, one-speed fan, w/Econo; 2006 - 2009: EER = 10.1, one-speed fan, w/Econo; 2010 - 2013: EER = 11, one-speed fan, w/Econo; 2014 - 2015: EER = 11 (IEER = 13.3), two-speed fan, w/Econo
32101 | dxAC-Com-Pkg-110to135kBTUh-EER11.5 | DEER2015 | Measure | 14.3 | 11.5 | 110 | 135 | Air | 0.663 | 0.25964 | 318 | 0.4 | 0 | 100 | TRUE | two-speed | cDXGF |  | EER-rated packaged Air Conditioner, Size Range: 110 - 135 kBTU/h, EER = 11.5 (IEER = 14.3), EIR = 0.26, Fan W/CFM = 0.4, two-speed fan, with Econo
32201 | dxAC-Com-Pkg-110to135kBTUh-EER12.0 | DEER2015 | Measure | 15.4 | 12 | 110 | 135 | Air | 0.663 | 0.24716 | 318 | 0.4 | 0 | 100 | TRUE | two-speed | cDXGF |  | EER-rated packaged Air Conditioner, Size Range: 110 - 135 kBTU/h, EER = 12 (IEER = 15.4), EIR = 0.247, Fan W/CFM = 0.4, two-speed fan, with Econo
32301 | dxAC-Com-Pkg-110to135kBTUh-EER12.5 | DEER2015 | Measure | 16.5 | 12.5 | 110 | 135 | Air | 0.663 | 0.23591 | 318 | 0.4 | 0 | 100 | TRUE | two-speed | cDXGF |  | EER-rated packaged Air Conditioner, Size Range: 110 - 135 kBTU/h, EER = 12.5 (IEER = 16.5), EIR = 0.236, Fan W/CFM = 0.4, two-speed fan, with Econo
33001 | dxAC-Com-Pkg-135to240kBTUh-EER10.8 | DEER2015 | Code/Standard | 12.8 | 10.8 | 135 | 240 | Air | 0.696 | 0.27372 | 326.4 | 0.41 | 0 | 100 | TRUE | two-speed | cDXGF |  | EER-rated packaged Air Conditioner, Size Range: 135 - 240 kBTU/h, EER = 10.8 (IEER = 12.8), EIR = 0.274, Fan W/CFM = 0.41, two-speed fan, with Econo | EER-Rated Pkg AC, 135-240 kBTU/h; Pre-2005: EER = 9.5, one-speed fan, w/Econo; 2006 - 2009: EER = 9.5, one-speed fan, w/Econo; 2010 - 2013: EER = 10.8, one-speed fan, w/Econo; 2014 - 2015: EER = 10.8 (IEER = 12.8), two-speed fan, w/Econo
33101 | dxAC-Com-Pkg-135to240kBTUh-EER11.5 | DEER2015 | Measure | 14.3 | 11.5 | 135 | 240 | Air | 0.696 | 0.25481 | 326.4 | 0.41 | 0 | 100 | TRUE | two-speed | cDXGF |  | EER-rated packaged Air Conditioner, Size Range: 135 - 240 kBTU/h, EER = 11.5 (IEER = 14.3), EIR = 0.255, Fan W/CFM = 0.41, two-speed fan, with Econo
33201 | dxAC-Com-Pkg-135to240kBTUh-EER12.0 | DEER2015 | Measure | 15.4 | 12 | 135 | 240 | Air | 0.696 | 0.24278 | 326.4 | 0.41 | 0 | 100 | TRUE | two-speed | cDXGF |  | EER-rated packaged Air Conditioner, Size Range: 135 - 240 kBTU/h, EER = 12 (IEER = 15.4), EIR = 0.243, Fan W/CFM = 0.41, two-speed fan, with Econo
33301 | dxAC-Com-Pkg-135to240kBTUh-EER12.5 | DEER2015 | Measure | 16.5 | 12.5 | 135 | 240 | Air | 0.696 | 0.23149 | 326.4 | 0.41 | 0 | 100 | TRUE | two-speed | cDXGF |  | EER-rated packaged Air Conditioner, Size Range: 135 - 240 kBTU/h, EER = 12.5 (IEER = 16.5), EIR = 0.231, Fan W/CFM = 0.41, two-speed fan, with Econo
34002 | dxAC-Com-Pkg-240to760kBTUh-EER9.8 | DEER2015 | Code/Standard | 11.2 | 9.8 | 240 | 760 | Air | 0.705 | 0.28622 | 320.4 | 0.61 | 0 | 100 | TRUE | two-speed | cDXGF |  | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 9.8 (IEER = 11.2), EIR = 0.286, Fan W/CFM = 0.61, two-speed fan, with Econo | EER-Rated Pkg AC, 240-760 kBTU/h; Pre-2005: EER = 9.3, one-speed fan, w/Econo; 2006 - 2009: EER = 9.3, one-speed fan, w/Econo; 2010 - 2013: EER = 9.8, one-speed fan, w/Econo; 2014 - 2015: EER = 9.8 (IEER = 11.2), two-speed fan, w/Econo
34102 | dxAC-Com-Pkg-240to760kBTUh-EER10.8 | DEER2015 | Measure | 12.8 | 10.8 | 240 | 760 | Air | 0.705 | 0.25464 | 320.4 | 0.61 | 0 | 100 | TRUE | two-speed | cDXGF |  | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 10.8 (IEER = 12.8), EIR = 0.255, Fan W/CFM = 0.61, two-speed fan, with Econo
34202 | dxAC-Com-Pkg-240to760kBTUh-EER11.5 | DEER2015 | Measure | 13.9 | 11.5 | 240 | 760 | Air | 0.705 | 0.23585 | 320.4 | 0.61 | 0 | 100 | TRUE | two-speed | cDXGF |  | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 11.5 (IEER = 13.9), EIR = 0.236, Fan W/CFM = 0.61, two-speed fan, with Econo
34302 | dxAC-Com-Pkg-240to760kBTUh-EER12.5 | DEER2015 | Measure | 15.5 | 12.5 | 240 | 760 | Air | 0.705 | 0.21257 | 320.4 | 0.61 | 0 | 100 | TRUE | two-speed | cDXGF |  | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 12.5 (IEER = 15.5), EIR = 0.213, Fan W/CFM = 0.61, two-speed fan, with Econo
34001 | dxAC-Com-Pkg-240to760kBTUh-EER10.0 | DEER2015 | Code/Standard | 11.4 | 10 | 240 | 760 | Air | 0.708 | 0.28182 | 321.6 | 0.72 | 0 | 100 | TRUE | var-speed | cPVVT |  | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 10 (IEER = 11.4), EIR = 0.282, Fan W/CFM = 0.72, var-speed fan, with Econo | EER-Rated Pkg AC, 240-760 kBTU/h; Pre-2005: EER = 9.5, var-speed fan, w/Econo; 2006 - 2009: EER = 9.5, var-speed fan, w/Econo; 2010 - 2013: EER = 10, var-speed fan, w/Econo; 2014 - 2015: EER = 10 (IEER = 11.4), var-speed fan, w/Econo
34101 | dxAC-Com-Pkg-240to760kBTUh-EER10.8 | DEER2015 | Measure | 12.8 | 10.8 | 240 | 760 | Air | 0.708 | 0.25619 | 321.6 | 0.72 | 0 | 100 | TRUE | var-speed | cPVVT |  | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 10.8 (IEER = 12.8), EIR = 0.256, Fan W/CFM = 0.72, var-speed fan, with Econo
34201 | dxAC-Com-Pkg-240to760kBTUh-EER11.5 | DEER2015 | Measure | 13.9 | 11.5 | 240 | 760 | Air | 0.708 | 0.23663 | 321.6 | 0.72 | 0 | 100 | TRUE | var-speed | cPVVT |  | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 11.5 (IEER = 13.9), EIR = 0.237, Fan W/CFM = 0.72, var-speed fan, with Econo
34301 | dxAC-Com-Pkg-240to760kBTUh-EER12.5 | DEER2015 | Measure | 15.6 | 12.5 | 240 | 760 | Air | 0.708 | 0.21235 | 321.6 | 0.72 | 0 | 100 | TRUE | var-speed | cPVVT |  | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 12.5 (IEER = 15.6), EIR = 0.212, Fan W/CFM = 0.72, var-speed fan, with Econo
35002 | dxAC-Com-Pkg-760tokBTUh-EER9.5 | DEER2015 | Code/Standard | 10.7 | 9.5 | 760 |  | Air | 0.705 | 0.29707 | 320.4 | 0.61 | 0 | 100 | TRUE | two-speed | cDXGF |  | EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 9.5 (IEER = 10.7), EIR = 0.297, Fan W/CFM = 0.61, two-speed fan, with Econo | EER-Rated Pkg AC, 760+ kBTU/h; Pre-2005: EER = 9, one-speed fan, w/Econo; 2006 - 2009: EER = 9, one-speed fan, w/Econo; 2010 - 2013: EER = 9.5, one-speed fan, w/Econo; 2014 - 2015: EER = 9.5 (IEER = 10.7), two-speed fan, w/Econo
35102 | dxAC-Com-Pkg-760tokBTUh-EER10.2 | DEER2015 | Measure | 11.8 | 10.2 | 760 |  | Air | 0.705 | 0.27298 | 320.4 | 0.61 | 0 | 100 | TRUE | two-speed | cDXGF |  | EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 10.2 (IEER = 11.8), EIR = 0.273, Fan W/CFM = 0.61, two-speed fan, with Econo
35202 | dxAC-Com-Pkg-760tokBTUh-EER11.0 | DEER2015 | Measure | 13.1 | 11 | 760 |  | Air | 0.705 | 0.24907 | 320.4 | 0.61 | 0 | 100 | TRUE | two-speed | cDXGF |  | EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 11 (IEER = 13.1), EIR = 0.249, Fan W/CFM = 0.61, two-speed fan, with Econo
35302 | dxAC-Com-Pkg-760tokBTUh-EER12.0 | DEER2015 | Measure | 14.7 | 12 | 760 |  | Air | 0.705 | 0.22373 | 320.4 | 0.61 | 0 | 100 | TRUE | two-speed | cDXGF |  | EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 12 (IEER = 14.7), EIR = 0.224, Fan W/CFM = 0.61, two-speed fan, with Econo
35001 | dxAC-Com-Pkg-760tokBTUh-EER9.7 | DEER2015 | Code/Standard | 10.9 | 9.7 | 760 |  | Air | 0.708 | 0.29277 | 321.6 | 0.72 | 0 | 100 | TRUE | var-speed | cPVVT |  | EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 9.7 (IEER = 10.9), EIR = 0.293, Fan W/CFM = 0.72, var-speed fan, with Econo | EER-Rated Pkg AC, 760+ kBTU/h; Pre-2005: EER = 9.2, var-speed fan, w/Econo; 2006 - 2009: EER = 9.2, var-speed fan, w/Econo; 2010 - 2013: EER = 9.7, var-speed fan, w/Econo; 2014 - 2015: EER = 9.7 (IEER = 10.9), var-speed fan, w/Econo
35101 | dxAC-Com-Pkg-760tokBTUh-EER10.2 | DEER2015 | Measure | 11.8 | 10.2 | 760 |  | Air | 0.708 | 0.27513 | 321.6 | 0.72 | 0 | 100 | TRUE | var-speed | cPVVT |  | EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 10.2 (IEER = 11.8), EIR = 0.275, Fan W/CFM = 0.72, var-speed fan, with Econo
35201 | dxAC-Com-Pkg-760tokBTUh-EER11.0 | DEER2015 | Measure | 13.1 | 11 | 760 |  | Air | 0.708 | 0.25044 | 321.6 | 0.72 | 0 | 100 | TRUE | var-speed | cPVVT |  | EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 11 (IEER = 13.1), EIR = 0.25, Fan W/CFM = 0.72, var-speed fan, with Econo
35301 | dxAC-Com-Pkg-760tokBTUh-EER12.0 | DEER2015 | Measure | 14.8 | 12 | 760 |  | Air | 0.708 | 0.22398 | 321.6 | 0.72 | 0 | 100 | TRUE | var-speed | cPVVT |  | EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 12 (IEER = 14.8), EIR = 0.224, Fan W/CFM = 0.72, var-speed fan, with Econo
7900473 | dxAC-Com-Pkg-65to110kBTUh-EER10.1 | DEER2015 | Pre-2005 | na | 10.1 | 65 | 110 | Air |  |  |  | 0.4 | 0 | 100 | FALSE | one-speed | cDXGF |  | Pre-2005: EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 10.1, one-speed fan, without Econo | EER-Rated Pkg AC, 65-110 kBTU/h | Pre-2005: EER = 10.1, one-speed fan, no Econo | Pre-2005: EER = 10.1, one-speed fan, w/Econo
7900573 | dxAC-Com-Pkg-65to110kBTUh-EER10.1 | DEER2015 | 2006 - 2009 | na | 10.1 | 65 | 110 | Air |  |  |  | 0.4 | 0 | 100 | FALSE | one-speed | cDXGF |  | 2006 - 2009: EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 10.1, one-speed fan, without Econo |  | 2006 - 2009: EER = 10.1, one-speed fan, no Econo | 2006 - 2009: EER = 10.1, one-speed fan, w/Econo
7900673 | dxAC-Com-Pkg-65to110kBTUh-EER11.0 | DEER2015 | 2010 - 2013 | na | 11 | 65 | 110 | Air |  |  |  | 0.4 | 0 | 100 | FALSE | one-speed | cDXGF |  | 2010 - 2013: EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 11, one-speed fan, without Econo |  | 2010 - 2013: EER = 11, one-speed fan, no Econo | 2010 - 2013: EER = 11, one-speed fan, w/Econo
7900773 | dxAC-Com-Pkg-65to110kBTUh-EER11.0 | DEER2015 | 2014 - 2015 | 13.4 | 11 | 65 | 110 | Air |  |  |  | 0.4 | 0 | 100 | TRUE | two-speed | cDXGF |  | 2014 - 2015: EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 11 (IEER = 13.4), two-speed fan, with Economizer |  | 2014 - 2015: EER = 11 (IEER = 13.4), two-speed fan, w/Econo | 2014 - 2015: EER = 11 (IEER = 13.4), two-speed fan, w/Econo
13600473 | dxAC-Com-Pkg-110to135kBTUh-EER10.1 | DEER2015 | Pre-2005 | na | 10.1 | 110 | 135 | Air |  |  |  | 0.4 | 0 | 100 | TRUE | one-speed | cDXGF |  | Pre-2005: EER-rated packaged Air Conditioner, Size Range: 110 - 135 kBTU/h, EER = 10.1, one-speed fan, with Economizer | EER-Rated Pkg AC, 110-135 kBTU/h | Pre-2005: EER = 10.1, one-speed fan, w/Econo | Pre-2005: EER = 10.1, one-speed fan, w/Econo
13600573 | dxAC-Com-Pkg-110to135kBTUh-EER10.1 | DEER2015 | 2006 - 2009 | na | 10.1 | 110 | 135 | Air |  |  |  | 0.4 | 0 | 100 | TRUE | one-speed | cDXGF |  | 2006 - 2009: EER-rated packaged Air Conditioner, Size Range: 110 - 135 kBTU/h, EER = 10.1, one-speed fan, with Economizer |  | 2006 - 2009: EER = 10.1, one-speed fan, w/Econo
13600673 | dxAC-Com-Pkg-110to135kBTUh-EER11.0 | DEER2015 | 2010 - 2013 | na | 11 | 110 | 135 | Air |  |  |  | 0.4 | 0 | 100 | TRUE | one-speed | cDXGF |  | 2010 - 2013: EER-rated packaged Air Conditioner, Size Range: 110 - 135 kBTU/h, EER = 11, one-speed fan, with Economizer |  | 2010 - 2013: EER = 11, one-speed fan, w/Econo
13600773 | dxAC-Com-Pkg-110to135kBTUh-EER11.0 | DEER2015 | 2014 - 2015 | 13.3 | 11 | 110 | 135 | Air |  |  |  | 0.4 | 0 | 100 | TRUE | two-speed | cDXGF |  | 2014 - 2015: EER-rated packaged Air Conditioner, Size Range: 110 - 135 kBTU/h, EER = 11 (IEER = 13.3), two-speed fan, with Economizer |  | 2014 - 2015: EER = 11 (IEER = 13.3), two-speed fan, w/Econo
13900473 | dxAC-Com-Pkg-135to240kBTUh-EER9.5 | DEER2015 | Pre-2005 | na | 9.5 | 135 | 240 | Air |  |  |  | 0.41 | 0 | 100 | TRUE | one-speed | cDXGF |  | Pre-2005: EER-rated packaged Air Conditioner, Size Range: 135 - 240 kBTU/h, EER = 9.5, one-speed fan, with Economizer | EER-Rated Pkg AC, 135-240 kBTU/h | Pre-2005: EER = 9.5, one-speed fan, w/Econo
13900573 | dxAC-Com-Pkg-135to240kBTUh-EER9.5 | DEER2015 | 2006 - 2009 | na | 9.5 | 135 | 240 | Air |  |  |  | 0.41 | 0 | 100 | TRUE | one-speed | cDXGF |  | 2006 - 2009: EER-rated packaged Air Conditioner, Size Range: 135 - 240 kBTU/h, EER = 9.5, one-speed fan, with Economizer |  | 2006 - 2009: EER = 9.5, one-speed fan, w/Econo
13900673 | dxAC-Com-Pkg-135to240kBTUh-EER10.8 | DEER2015 | 2010 - 2013 | na | 10.8 | 135 | 240 | Air |  |  |  | 0.41 | 0 | 100 | TRUE | one-speed | cDXGF |  | 2010 - 2013: EER-rated packaged Air Conditioner, Size Range: 135 - 240 kBTU/h, EER = 10.8, one-speed fan, with Economizer |  | 2010 - 2013: EER = 10.8, one-speed fan, w/Econo
13900773 | dxAC-Com-Pkg-135to240kBTUh-EER10.8 | DEER2015 | 2014 - 2015 | 12.8 | 10.8 | 135 | 240 | Air |  |  |  | 0.41 | 0 | 100 | TRUE | two-speed | cDXGF |  | 2014 - 2015: EER-rated packaged Air Conditioner, Size Range: 135 - 240 kBTU/h, EER = 10.8 (IEER = 12.8), two-speed fan, with Economizer |  | 2014 - 2015: EER = 10.8 (IEER = 12.8), two-speed fan, w/Econo
10400473 | dxAC-Com-Pkg-240to760kBTUh-EER9.3 | DEER2015 | Pre-2005 | na | 9.3 | 240 | 760 | Air |  |  |  | 0.61 | 0 | 100 | TRUE | one-speed | cDXGF |  | Pre-2005: EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 9.3, one-speed fan, with Economizer | EER-Rated Pkg AC, 240-760 kBTU/h | Pre-2005: EER = 9.3, one-speed fan, w/Econo
10400573 | dxAC-Com-Pkg-240to760kBTUh-EER9.3 | DEER2015 | 2006 - 2009 | na | 9.3 | 240 | 760 | Air |  |  |  | 0.61 | 0 | 100 | TRUE | one-speed | cDXGF |  | 2006 - 2009: EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 9.3, one-speed fan, with Economizer |  | 2006 - 2009: EER = 9.3, one-speed fan, w/Econo
10400673 | dxAC-Com-Pkg-240to760kBTUh-EER9.8 | DEER2015 | 2010 - 2013 | na | 9.8 | 240 | 760 | Air |  |  |  | 0.61 | 0 | 100 | TRUE | one-speed | cDXGF |  | 2010 - 2013: EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 9.8, one-speed fan, with Economizer |  | 2010 - 2013: EER = 9.8, one-speed fan, w/Econo
10400773 | dxAC-Com-Pkg-240to760kBTUh-EER9.8 | DEER2015 | 2014 - 2015 | 11.2 | 9.8 | 240 | 760 | Air |  |  |  | 0.61 | 0 | 100 | TRUE | two-speed | cDXGF |  | 2014 - 2015: EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 9.8 (IEER = 11.2), two-speed fan, with Economizer |  | 2014 - 2015: EER = 9.8 (IEER = 11.2), two-speed fan, w/Econo
10400460 | dxAC-Com-Pkg-240to760kBTUh-EER9.5 | DEER2015 | Pre-2005 | na | 9.5 | 240 | 760 | Air |  |  |  | 0.72 | 0 | 100 | TRUE | var-speed | cPVVT |  | Pre-2005: EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 9.5, var-speed fan, with Economizer | EER-Rated Pkg AC, 240-760 kBTU/h | Pre-2005: EER = 9.5, var-speed fan, w/Econo
10400560 | dxAC-Com-Pkg-240to760kBTUh-EER9.5 | DEER2015 | 2006 - 2009 | na | 9.5 | 240 | 760 | Air |  |  |  | 0.72 | 0 | 100 | TRUE | var-speed | cPVVT |  | 2006 - 2009: EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 9.5, var-speed fan, with Economizer |  | 2006 - 2009: EER = 9.5, var-speed fan, w/Econo
10400660 | dxAC-Com-Pkg-240to760kBTUh-EER10.0 | DEER2015 | 2010 - 2013 | na | 10 | 240 | 760 | Air |  |  |  | 0.72 | 0 | 100 | TRUE | var-speed | cPVVT |  | 2010 - 2013: EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 10, var-speed fan, with Economizer |  | 2010 - 2013: EER = 10, var-speed fan, w/Econo
10400760 | dxAC-Com-Pkg-240to760kBTUh-EER10.0 | DEER2015 | 2014 - 2015 | 11.4 | 10 | 240 | 760 | Air |  |  |  | 0.72 | 0 | 100 | TRUE | var-speed | cPVVT |  | 2014 - 2015: EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 10 (IEER = 11.4), var-speed fan, with Economizer |  | 2014 - 2015: EER = 10 (IEER = 11.4), var-speed fan, w/Econo
10500473 | dxAC-Com-Pkg-760tokBTUh-EER9.0 | DEER2015 | Pre-2005 | na | 9 | 760 |  | Air |  |  |  | 0.61 | 0 | 100 | TRUE | one-speed | cPVVT |  | Pre-2005: EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 9, one-speed fan, with Economizer | EER-Rated Pkg AC, 760+ kBTU/h | Pre-2005: EER = 9, one-speed fan, w/Econo
10500573 | dxAC-Com-Pkg-760tokBTUh-EER9.0 | DEER2015 | 2006 - 2009 | na | 9 | 760 |  | Air |  |  |  | 0.61 | 0 | 100 | TRUE | one-speed | cDXGF |  | 2006 - 2009: EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 9, one-speed fan, with Economizer |  | 2006 - 2009: EER = 9, one-speed fan, w/Econo
10500673 | dxAC-Com-Pkg-760tokBTUh-EER9.5 | DEER2015 | 2010 - 2013 | na | 9.5 | 760 |  | Air |  |  |  | 0.61 | 0 | 100 | TRUE | one-speed | cDXGF |  | 2010 - 2013: EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 9.5, one-speed fan, with Economizer |  | 2010 - 2013: EER = 9.5, one-speed fan, w/Econo
10500773 | dxAC-Com-Pkg-760tokBTUh-EER9.5 | DEER2015 | 2014 - 2015 | 10.7 | 9.5 | 760 |  | Air |  |  |  | 0.61 | 0 | 100 | TRUE | two-speed | cDXGF |  | 2014 - 2015: EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 9.5 (IEER = 10.7), two-speed fan, with Economizer |  | 2014 - 2015: EER = 9.5 (IEER = 10.7), two-speed fan, w/Econo
10500460 | dxAC-Com-Pkg-760tokBTUh-EER9.2 | DEER2015 | Pre-2005 | na | 9.2 | 760 |  | Air |  |  |  | 0.72 | 0 | 100 | TRUE | var-speed | cPVVT |  | Pre-2005: EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 9.2, var-speed fan, with Economizer | EER-Rated Pkg AC, 760+ kBTU/h | Pre-2005: EER = 9.2, var-speed fan, w/Econo
10500560 | dxAC-Com-Pkg-760tokBTUh-EER9.2 | DEER2015 | 2006 - 2009 | na | 9.2 | 760 |  | Air |  |  |  | 0.72 | 0 | 100 | TRUE | var-speed | cPVVT |  | 2006 - 2009: EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 9.2, var-speed fan, with Economizer |  | 2006 - 2009: EER = 9.2, var-speed fan, w/Econo
10500660 | dxAC-Com-Pkg-760tokBTUh-EER9.7 | DEER2015 | 2010 - 2013 | na | 9.7 | 760 |  | Air |  |  |  | 0.72 | 0 | 100 | TRUE | var-speed | cPVVT |  | 2010 - 2013: EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 9.7, var-speed fan, with Economizer |  | 2010 - 2013: EER = 9.7, var-speed fan, w/Econo
10500760 | dxAC-Com-Pkg-760tokBTUh-EER9.7 | DEER2015 | 2014 - 2015 | 10.9 | 9.7 | 760 |  | Air |  |  |  | 0.72 | 0 | 100 | TRUE | var-speed | cPVVT |  | 2014 - 2015: EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 9.7 (IEER = 10.9), var-speed fan, with Economizer |  | 2014 - 2015: EER = 9.7 (IEER = 10.9), var-speed fan, w/Econo
| Com SEER-Rated Splt AC |  |  | 2 | 3 |  |  |  | 5 | 6 | 7 | 8 |  |  |  | 57
| Commercial SEER-rated split Air Conditioners | Version | Case | SEER | EER | Min_CoolCap | Max_CoolCap | CondType | SensCapRatio | COOLING-EIR | CFMperTon | WperCFM | CrankRatio | CRANKCASE-MAX-T | Econo_req | Fan_spd | BldgHVAC | PerfCurveID
11402 | dxAC-Com-Split-lt45kBTUh-SEER-14.0 | DEER2015 | Code/Standard | 14 | 12.1655 | 18 | 45 | Air | 0.75406 | 0.2393 | 385.2 | 0.294 | 0 | 100 | FALSE | one-speed | cDXGF |  | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo | 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo
11501 | dxAC-Com-Split-lt45kBTUh-SEER-15.0 | DEER2015 | Measure | 15 | 12.7817 | 18 | 45 | Air | 0.744 | 0.23218 | 385.2 | 0.251 | 0 | 100 | FALSE | one-speed | cDXGF |  | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo
11604 | dxAC-Com-Split-lt45kBTUh-SEER-16.0 | DEER2015 | Measure | 16 | 12.48 | 18 | 45 | Air | 0.724 | 0.23814 | 360 | 0.271 | 0 | 100 | FALSE | two-speed | cDXGF |  | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, without Econo
11704 | dxAC-Com-Split-lt45kBTUh-SEER-17.0 | DEER2015 | Measure | 17 | 13.26 | 18 | 45 | Air | 0.724 | 0.2225 | 360 | 0.271 | 0 | 100 | FALSE | two-speed | cDXGF |  | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, without Econo
11802 | dxAC-Com-Split-lt45kBTUh-SEER-18.0 | DEER2015 | Measure | 18 | 14.04 | 18 | 45 | Air | 0.724 | 0.2086 | 360 | 0.271 | 0 | 100 | FALSE | two-speed | cDXGF |  | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, without Econo
11403 | dxAC-Com-Split-45to55kBTUh-SEER-14.0 | DEER2015 | Code/Standard | 14 | 11.8179 | 45 | 55 | Air | 0.75922 | 0.2466 | 391.56 | 0.294 | 0 | 100 | FALSE | one-speed | cDXGF |  | Commercial SEER-rated split Air Conditioners, Size Range: 45 - 55 kBTU/h, SEER = 14 (EER = 11.8), EIR = 0.247, Fan W/CFM = 0.29, one-speed fan, without Econo | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 11.82), one-speed fan, no Econo | 2014: SEER = 14 (EER = 11.82), one-speed fan, no Econo
11501 | dxAC-Com-Split-45to55kBTUh-SEER-15.0 | DEER2015 | Measure | 15 | 12.7817 | 45 | 55 | Air | 0.744 | 0.23218 | 385.2 | 0.251 | 0 | 100 | FALSE | one-speed | cDXGF |  | Commercial SEER-rated split Air Conditioners, Size Range: 45 - 55 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo
11604 | dxAC-Com-Split-45to55kBTUh-SEER-16.0 | DEER2015 | Measure | 16 | 12.48 | 45 | 55 | Air | 0.724 | 0.23814 | 360 | 0.271 | 0 | 100 | FALSE | two-speed | cDXGF |  | Commercial SEER-rated split Air Conditioners, Size Range: 45 - 55 kBTU/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, without Econo
11704 | dxAC-Com-Split-45to55kBTUh-SEER-17.0 | DEER2015 | Measure | 17 | 13.26 | 45 | 55 | Air | 0.724 | 0.2225 | 360 | 0.271 | 0 | 100 | FALSE | two-speed | cDXGF |  | Commercial SEER-rated split Air Conditioners, Size Range: 45 - 55 kBTU/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, without Econo
11802 | dxAC-Com-Split-45to55kBTUh-SEER-18.0 | DEER2015 | Measure | 18 | 14.04 | 45 | 55 | Air | 0.724 | 0.2086 | 360 | 0.271 | 0 | 100 | FALSE | two-speed | cDXGF |  | Commercial SEER-rated split Air Conditioners, Size Range: 45 - 55 kBTU/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, without Econo
11405 | dxAC-Com-Split-55to65kBTUh-SEER-14.0 | DEER2015 | Code/Standard | 14 | 11.7458 | 55 | 65 | Air | 0.732 | 0.249 | 385.2 | 0.294 | 0 | 100 | TRUE | two-speed | cDXGF |  | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo
11505 | dxAC-Com-Split-55to65kBTUh-SEER-15.0 | DEER2015 | Measure | 15 | 12.5847 | 55 | 65 | Air | 0.732 | 0.23624 | 385.2 | 0.251 | 0 | 100 | TRUE | two-speed | cDXGF |  | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo
11605 | dxAC-Com-Split-55to65kBTUh-SEER-16.0 | DEER2015 | Measure | 16 | 12.48 | 55 | 65 | Air | 0.724 | 0.23814 | 360 | 0.271 | 0 | 100 | TRUE | two-speed | cDXGF |  | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, with Econo
11705 | dxAC-Com-Split-55to65kBTUh-SEER-17.0 | DEER2015 | Measure | 17 | 13.26 | 55 | 65 | Air | 0.724 | 0.2225 | 360 | 0.271 | 0 | 100 | TRUE | two-speed | cDXGF |  | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, with Econo
11805 | dxAC-Com-Split-55to65kBTUh-SEER-18.0 | DEER2015 | Measure | 18 | 14.04 | 55 | 65 | Air | 0.724 | 0.2086 | 360 | 0.271 | 0 | 100 | TRUE | two-speed | cDXGF |  | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, with Econo
11009 | dxAC-Com-Split-SEER-10.0 | DEER2015 | pre-2001 | 10 | 8.5211 | 18 | 65 | Air | 0.744 | 0.34453 | 385.2 | 0.365 | 0 | 100 | FALSE | one-speed | cDXGF |  | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 10 (EER = 8.5), EIR = 0.345, Fan W/CFM = 0.37, one-speed fan, without Econo | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h | pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo | pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo
11304 | dxAC-Com-Split-SEER-13.0 | DEER2015 | post-2001 | 13 | 11.0775 | 18 | 65 | Air | 0.744 | 0.25823 | 385.2 | 0.348 | 0 | 100 | FALSE | one-speed | cDXGF |  | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 13 (EER = 11.1), EIR = 0.258, Fan W/CFM = 0.35, one-speed fan, without Econo |  | post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo | post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo
Res SEER-Rated Splt AC
| Residential SEER-rated split Air Conditioners | Version |  | SEER | EER | Min_CoolCap | Max_CoolCap | CondType | SensCapRatio | COOLING-EIR | CFMperTon | WperCFM | CrankRatio | CRANKCASE-MAX-T | Econo_req | Fan_spd | BldgHVAC | PerfCurveID
11402 | dxAC-Res-Split-lt45kBTUh-SEER-14.0 | DEER2015 | Code/Standard | 14 | 12.1655 | 18 | 45 | Air | 0.75406 | 0.2393 | 385.2 | 0.294 | 0 | 100 |  | one-speed | rDXGF |  | Residential SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan | Residential SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan; post-2001: SEER = 13 (EER = 11.08), one-speed fan; 2014: SEER = 14 (EER = 12.17), one-speed fan | 2014: SEER = 14 (EER = 12.17), one-speed fan
11501 | dxAC-Res-Split-SEER-15.0 | DEER2015 | Measure | 15 | 12.7817 | 18 | 65 | Air | 0.744 | 0.23218 | 385.2 | 0.251 | 0 | 100 |  | one-speed | rDXGF |  | Residential SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan
11604 | dxAC-Res-Split-SEER-16.0 | DEER2015 | Measure | 16 | 12.48 | 18 | 65 | Air | 0.724 | 0.23814 | 360 | 0.271 | 0 | 100 |  | two-speed | rDXGF |  | Residential SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan
11704 | dxAC-Res-Split-SEER-17.0 | DEER2015 | Measure | 17 | 13.26 | 18 | 65 | Air | 0.724 | 0.2225 | 360 | 0.271 | 0 | 100 |  | two-speed | rDXGF |  | Residential SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan
11802 | dxAC-Res-Split-SEER-18.0 | DEER2015 | Measure | 18 | 14.04 | 18 | 65 | Air | 0.724 | 0.2086 | 360 | 0.271 | 0 | 100 |  | two-speed | rDXGF |  | Residential SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan
11903 | dxAC-Res-Split-SEER-19.0 | DEER2015 | Measure | 19 | 14.82 | 18 | 65 | Air | 0.724 | 0.20095 | 360 | 0.233 | 0 | 100 |  | two-speed | rDXGF |  | Residential SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 19 (EER = 14.8), EIR = 0.201, Fan W/CFM = 0.23, two-speed fan
12001 | dxAC-Res-Split-SEER-20.0 | DEER2015 | Measure | 20 | 15.6 | 18 | 65 | Air | 0.724 | 0.18971 | 360 | 0.233 | 0 | 100 |  | two-speed | rDXGF |  | Residential SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 20 (EER = 15.6), EIR = 0.19, Fan W/CFM = 0.23, two-speed fan
12101 | dxAC-Res-Split-SEER-21.0 | DEER2015 | Measure | 21 | 16.38 | 18 | 65 | Air | 0.724 | 0.17954 | 360 | 0.233 | 0 | 100 |  | two-speed | rDXGF |  | Residential SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 21 (EER = 16.4), EIR = 0.18, Fan W/CFM = 0.23, two-speed fan
11403 | dxAC-Res-Split-45to65kBTUh-SEER-14.0 | DEER2015 | Code/Standard | 14 | 11.8179 | 45 | 65 | Air | 0.75922 | 0.2466 | 391.56 | 0.294 | 0 | 100 |  | one-speed | rDXGF |  | Residential SEER-rated split Air Conditioners, Size Range: 45 - 65 kBTU/h, SEER = 14 (EER = 11.8), EIR = 0.247, Fan W/CFM = 0.29, one-speed fan | Residential SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan; post-2001: SEER = 13 (EER = 11.08), one-speed fan; 2014: SEER = 14 (EER = 11.82), one-speed fan | 2014: SEER = 14 (EER = 11.82), one-speed fan
11009 | dxAC-Res-Split-SEER-10.0 | DEER2015 | pre-2001 | 10 | 8.5211 | 18 | 65 | Air | 0.744 | 0.34453 | 385.2 | 0.365 | 0 | 100 |  | one-speed | rDXGF |  | Residential SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 10 (EER = 8.5), EIR = 0.345, Fan W/CFM = 0.37, one-speed fan | Residential SEER-rated split Air Conditioners, 18-65 kBTU/h | pre-2001: SEER = 10 (EER = 8.52), one-speed fan
11304 | dxAC-Res-Split-SEER-13.0 | DEER2015 | post-2001 | 13 | 11.0775 | 18 | 65 | Air | 0.744 | 0.25823 | 385.2 | 0.348 | 0 | 100 |  | one-speed | rDXGF |  | Residential SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 13 (EER = 11.1), EIR = 0.258, Fan W/CFM = 0.35, one-speed fan |  | post-2001: SEER = 13 (EER = 11.08), one-speed fan
| dxAC-Res-EvapAC-SEER-17.4 | DEER2015 | Measure | 17.4 |  | 18 | 45 | Evap |  |  |  |  | 0 | 100 |  | one-speed | rDXGF |  | Residential SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 17.4, one-speed fan, evaporative cooled condenser
| Res SEER-Rated Splt HP |  |  | 2 | 3 | 60 | 61 |  |  |  | 5 | 6 | 7 | 8 |  | 57
| Residential SEER-rated split Heat Pumps | Version | Case | SEER | EER | HSPF | COP | Min_CoolCap | Max_CoolCap | CondType | SensCapRatio | COOLING-EIR | CFMperTon | WperCFM | Econo_req | Fan_spd | BldgHVAC | PerfCurveID
21405 | dxHP-Res-Split-SEER-14.0 | DEER2015 | Code/Standard | 14 | 11.9296 | 8.2 | 3.48 | 18 | 65 | Air | 0.744 | 0.24467 | 385.2 | 0.294 |  | one-speed | rDXHP |  | Residential SEER-rated split Heat Pumps, SEER = 14 (EER = 11.9), HSPF = 8.2 (COP = 3.48), EIR = 0.245, Fan W/CFM = 0.29, one-speed fan | Res SEER-Rated Splt HP, 7.1-3.01 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan; 2014: SEER = 14 (HSPF = 8.2), one-speed fan | 2014: SEER = 14 (HSPF = 8.2), one-speed fan
21501 | dxHP-Res-Split-SEER-15.0 | DEER2015 | Measure | 15 | 12.7817 | 8.7 | 3.68 | 18 | 65 | Air | 0.744 | 0.23218 | 385.2 | 0.251 |  | one-speed | rDXHP |  | Residential SEER-rated split Heat Pumps, SEER = 15 (EER = 12.8), HSPF = 8.7 (COP = 3.68), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan
21604 | dxHP-Res-Split-SEER-16.0 | DEER2015 | Measure | 16 | 12.48 | 9 | 3.57 | 18 | 65 | Air | 0.724 | 0.23814 | 360 | 0.271 |  | two-speed | rDXHP |  | Residential SEER-rated split Heat Pumps, SEER = 16 (EER = 12.5), HSPF = 9 (COP = 3.57), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan
21704 | dxHP-Res-Split-SEER-17.0 | DEER2015 | Measure | 17 | 13.26 | 9.4 | 3.74 | 18 | 65 | Air | 0.724 | 0.2225 | 360 | 0.271 |  | two-speed | rDXHP |  | Residential SEER-rated split Heat Pumps, SEER = 17 (EER = 13.3), HSPF = 9.4 (COP = 3.74), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan
21802 | dxHP-Res-Split-SEER-18.0 | DEER2015 | Measure | 18 | 14.04 | 9.7 | 3.86 | 18 | 65 | Air | 0.724 | 0.2086 | 360 | 0.271 |  | two-speed | rDXHP |  | Residential SEER-rated split Heat Pumps, SEER = 18 (EER = 14), HSPF = 9.7 (COP = 3.86), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan
21005 | dxHP-Res-Split-SEER-10.0 | DEER2015 | pre-2001 | 10 | 8.5211 | 7.1 | 3.01 | 18 | 65 | Air | 0.744 | 0.34453 | 385.2 | 0.365 |  | one-speed | rDXHP |  | Residential SEER-rated split Heat Pumps, SEER = 10 (EER = 8.5), HSPF = 7.1 (COP = 3.01), EIR = 0.345, Fan W/CFM = 0.37, one-speed fan | Res SEER-Rated Splt HP, 7.1-3.01 kBTU/h | pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan
21305 | dxHP-Res-Split-SEER-13.0 | DEER2015 | post-2001 | 13 | 11.0775 | 8.2 | 3.49 | 18 | 65 | Air | 0.744 | 0.25823 | 385.2 | 0.348 |  | one-speed | rDXHP |  | Residential SEER-rated split Heat Pumps, SEER = 13 (EER = 11.1), HSPF = 8.2 (COP = 3.49), EIR = 0.258, Fan W/CFM = 0.35, one-speed fan |  | post-2001: SEER = 13 (HSPF = 8.2), one-speed fan
| Com SEER-Rated Pkg AC |  |  | 5 | 6 |  |  |  | 8 | 9 | 10 | 11
| Commercial SEER-rated Packaged Air Conditioners | Version | Case | SEER | EER | Min_CoolCap | Max_CoolCap | CondType | SensCapRatio | COOLING-EIR | CFMperTon | WperCFM | CrankRatio | CRANKCASE-MAX-T | Econo_req | Fan_spd | BldgHVAC | PerfCurveID
30203 | dxAC-Com-Pkg-lt55kBTUh-SEER-14.0 | DEER2015 | Code/Standard | 14 | 12.0391 | 18 | 55 | Air | 0.6932 | 0.2456 | 338.28 | 0.294 | 0 | 100 | FALSE | one-speed | cDXGF |  | Commercial SEER-rated Packaged Air Conditioners, Size Range: 18 - 55 kBTU/h, SEER = 14 (EER = 12), EIR = 0.246, Fan W/CFM = 0.29, one-speed fan, without Econo | Com SEER-Rated Pkg AC, 18-65 kBTU/h; pre-2001: SEER = 9.7 (EER = 9.21), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.06), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.04), one-speed fan, no Econo | 2014: SEER = 14 (EER = 12.04), one-speed fan, no Econo
30301 | dxAC-Com-Pkg-lt55kBTUh-SEER-15.0 | DEER2015 | Measure | 15 | 12.9 | 18 | 55 | Air | 0.6932 | 0.23404 | 338.28 | 0.251 | 0 | 100 | FALSE | one-speed | cDXGF |  | Commercial SEER-rated Packaged Air Conditioners, Size Range: 18 - 55 kBTU/h, SEER = 15 (EER = 12.9), EIR = 0.234, Fan W/CFM = 0.25, one-speed fan, without Econo
11610 | dxAC-Com-Pkg-lt55kBTUh-SEER-16.0 | DEER2015 | Measure | 16 | 12.48 | 18 | 55 | Air | 0.724 | 0.23814 | 360 | 0.271 | 0 | 100 | FALSE | two-speed | cDXGF |  | Commercial SEER-rated Packaged Air Conditioners, Size Range: 18 - 55 kBTU/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, without Econo
11710 | dxAC-Com-Pkg-lt55kBTUh-SEER-17.0 | DEER2015 | Measure | 17 | 13.26 | 18 | 55 | Air | 0.724 | 0.2225 | 360 | 0.271 | 0 | 100 | FALSE | two-speed | cDXGF |  | Commercial SEER-rated Packaged Air Conditioners, Size Range: 18 - 55 kBTU/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, without Econo
11810 | dxAC-Com-Pkg-lt55kBTUh-SEER-18.0 | DEER2015 | Measure | 18 | 14.04 | 18 | 55 | Air | 0.724 | 0.2086 | 360 | 0.271 | 0 | 100 | FALSE | two-speed | cDXGF |  | Commercial SEER-rated Packaged Air Conditioners, Size Range: 18 - 55 kBTU/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, without Econo
11405 | dxAC-Com-Pkg-55to65kBTUh-SEER-14.0 | DEER2015 | Code/Standard | 14 | 11.7458 | 55 | 65 | Air | 0.732 | 0.249 | 385.2 | 0.294 | 0 | 100 | TRUE | two-speed | cDXGF |  | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | Com SEER-Rated Pkg AC, 18-65 kBTU/h; pre-2001: SEER = 9.7 (EER = 9.21), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.06), one-speed fan, no Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Com SEER-Rated Pkg AC, 18-65 kBTU/h; pre-2001: SEER = 9.7 (EER = 9.21), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.06), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo
11505 | dxAC-Com-Pkg-55to65kBTUh-SEER-15.0 | DEER2015 | Measure | 15 | 12.5847 | 55 | 65 | Air | 0.732 | 0.23624 | 385.2 | 0.251 | 0 | 100 | TRUE | two-speed | cDXGF |  | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo
11610 | dxAC-Com-Pkg-55to65kBTUh-SEER-16.0 | DEER2015 | Measure | 16 | 12.48 | 55 | 65 | Air | 0.724 | 0.23814 | 360 | 0.271 | 0 | 100 | TRUE | two-speed | cDXGF |  | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, with Econo
11710 | dxAC-Com-Pkg-55to65kBTUh-SEER-17.0 | DEER2015 | Measure | 17 | 13.26 | 55 | 65 | Air | 0.724 | 0.2225 | 360 | 0.271 | 0 | 100 | TRUE | two-speed | cDXGF |  | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, with Econo
11810 | dxAC-Com-Pkg-55to65kBTUh-SEER-18.0 | DEER2015 | Measure | 18 | 14.04 | 55 | 65 | Air | 0.724 | 0.2086 | 360 | 0.271 | 0 | 100 | TRUE | two-speed | cDXGF |  | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, with Econo
30007 | dxAC-Com-Pkg-SEER-10.0 | DEER2015 | pre-2001 | 9.7 | 9.2131 | 18 | 65 | Air | 0.6975 | 0.2971 | 372.36 | 0.4325 | 0 | 100 | FALSE | one-speed | cDXGF |  | Commercial SEER-rated Packaged Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 9.7 (EER = 9.2), EIR = 0.297, Fan W/CFM = 0.43, one-speed fan, without Econo | Com SEER-Rated Pkg AC, 18-65 kBTU/h | pre-2001: SEER = 9.7 (EER = 9.21), one-speed fan, no Econo | pre-2001: SEER = 9.7 (EER = 9.21), one-speed fan, w/Econo
30103 | dxAC-Com-Pkg-SEER-13.0 | DEER2015 | post-2001 | 13 | 11.0559 | 18 | 65 | Air | 0.732 | 0.2557 | 376.2 | 0.3785 | 0 | 100 | FALSE | one-speed | cDXGF |  | Commercial SEER-rated Packaged Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 13 (EER = 11.1), EIR = 0.256, Fan W/CFM = 0.38, one-speed fan, withpit Econo |  | post-2001: SEER = 13 (EER = 11.06), one-speed fan, no Econo | post-2001: SEER = 13 (EER = 11.06), one-speed fan, w/Econo
| Com SEER-Rated Pkg HP |  |  | 2 | 3 | 60 | 61 |  |  |  | 5 | 6 | 7 | 8 |  | 57
| Commercial SEER-rated Packaged Heat Pumps | Version | Case | SEER | EER | HSPF | COP | Min_CoolCap | Max_CoolCap | CondType | SensCapRatio | COOLING-EIR | CFMperTon | WperCFM | Econo_req | Fan_spd | BldgHVAC | PerfCurveID
| dxHP-Com-Pkg-lt55kBTUh-SEER-14.0 | DEER2015 | Code/Standard | 14 | 11.9296 | 8 | 3.39 | 18 | 55 | Air | 0.744 | 0.24467 | 385.2 | 0.294 | FALSE | one-speed | cDXHP | 21407 | Commercial SEER-rated Packaged Heat Pumps, Size Range: 18 - 55 kBTU/h, SEER = 14 (HSPF = 8.0), EIR = 0.245, Fan W/CFM = 0.29, one-speed fan, without Econo | Com SEER-Rated Pkg HP, 18-65 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan, no Econo; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan, no Econo; 2014: SEER = 14 (HSPF = 8), one-speed fan, no Econo | 2014: SEER = 14 (HSPF = 8), one-speed fan, no Econo
| dxHP-Com-Pkg-lt55kBTUh-SEER-15.0 | DEER2015 | Measure | 15 | 12.7817 | 8.2 | 3.48 | 18 | 65 | Air | 0.744 | 0.22621 | 385.2 | 0.294 | FALSE | one-speed | cDXHP | 21507 | Commercial SEER-rated Packaged Heat Pumps, Size Range: 18 - 65 kBTU/h, SEER = 15 (HSPF = 8.2), EIR = 0.226, Fan W/CFM = 0.29, one-speed fan, without Econo
| dxHP-Com-Pkg-lt55kBTUh-SEER-16.0 | DEER2015 | Measure | 16 | 12.48 | 8.5 | 3.37 | 18 | 65 | Air | 0.724 | 0.23814 | 360 | 0.271 | FALSE | two-speed | cDXHP | 21609 | Commercial SEER-rated Packaged Heat Pumps, Size Range: 18 - 65 kBTU/h, SEER = 16 (HSPF = 8.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, without Econo
| dxHP-Com-Pkg-lt55kBTUh-SEER-17.0 | DEER2015 | Measure | 17 | 13.26 | 9 | 3.57 | 18 | 65 | Air | 0.724 | 0.2225 | 360 | 0.271 | FALSE | two-speed | cDXHP | 21709 | Commercial SEER-rated Packaged Heat Pumps, Size Range: 18 - 65 kBTU/h, SEER = 17 (HSPF = 9.0), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, without Econo
| dxHP-Com-Pkg-55to65kBTUh-SEER-14.0 | DEER2015 | Code/Standard | 14 | 11.1125 | 8 | 3.17 | 55 | 65 | Air | 0.717 | 0.27047 | 335.4 | 0.294 | TRUE | two-speed | cDXHP | 21409 | Commercial SEER-rated Packaged Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 14 (HSPF = 8.0), EIR = 0.27, Fan W/CFM = 0.29, two-speed fan, with Econo | Com SEER-Rated Pkg HP, 18-65 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan, no Econo; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan, no Econo; 2014: SEER = 14 (HSPF = 8), two-speed fan, w/Econo | 2014: SEER = 14 (HSPF = 8), two-speed fan, w/Econo | Com SEER-Rated Pkg HP, 18-65 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan, w/Econo; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan, w/Econo; 2014: SEER = 14 (HSPF = 8), two-speed fan, w/Econo
| dxHP-Com-Pkg-55to65kBTUh-SEER-15.0 | DEER2015 | Measure | 15 | 11.9062 | 8.2 | 3.24 | 55 | 65 | Air | 0.717 | 0.25585 | 335.4 | 0.251 | TRUE | two-speed | cDXHP | 21509 | Commercial SEER-rated Packaged Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 15 (HSPF = 8.2), EIR = 0.256, Fan W/CFM = 0.25, two-speed fan, with Econo
| dxHP-Com-Pkg-55to65kBTUh-SEER-16.0 | DEER2015 | Measure | 16 | 12.48 | 8.5 | 3.37 | 55 | 65 | Air | 0.724 | 0.23814 | 360 | 0.271 | TRUE | two-speed | cDXHP | 21609 | Commercial SEER-rated Packaged Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 16 (HSPF = 8.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, with Econo
| dxHP-Com-Pkg-55to65kBTUh-SEER-17.0 | DEER2015 | Measure | 17 | 13.26 | 9 | 3.57 | 55 | 65 | Air | 0.724 | 0.2225 | 360 | 0.271 | TRUE | two-speed | cDXHP | 21709 | Commercial SEER-rated Packaged Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 17 (HSPF = 9.0), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, with Econo
| dxHP-Com-Pkg-lt65kBTUh-SEER-10.0 | DEER2015 | pre-2001 | 10 | 8.5211 | 7.1 | 3.01 | 18 | 65 | Air | 0.744 | 0.34453 | 385.2 | 0.365 | FALSE | one-speed | cDXHP | 21006 | Commercial SEER-rated Packaged Heat Pumps, Size Range: 18 - 65 kBTU/h, SEER = 10 (HSPF = 7.1), EIR = 0.345, Fan W/CFM = 0.37, one-speed fan, without Econo | Com SEER-Rated Pkg HP, 18-65 kBTU/h | pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan, no Econo | pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan, w/Econo
| dxHP-Com-Pkg-lt65kBTUh-SEER-13.0 | DEER2015 | post-2001 | 13 | 11.0775 | 8.2 | 3.49 | 18 | 65 | Air | 0.744 | 0.25823 | 385.2 | 0.348 | FALSE | one-speed | cDXHP | 21306 | Commercial SEER-rated Packaged Heat Pumps, Size Range: 18 - 65 kBTU/h, SEER = 13 (HSPF = 8.2), EIR = 0.258, Fan W/CFM = 0.35, one-speed fan, without Econo |  | post-2001: SEER = 13 (HSPF = 8.2), one-speed fan, no Econo | post-2001: SEER = 13 (HSPF = 8.2), one-speed fan, w/Econo
Com SEER-Rated Split HP
| Commercial SEER-rated Split Heat Pumps | Version | Case | SEER | EER | HSPF | COP | Min_CoolCap | Max_CoolCap | CondType | SensCapRatio | COOLING-EIR | CFMperTon | WperCFM | Econo_req | Fan_spd | BldgHVAC | PerfCurveID
| dxHP-Com-Split-lt55kBTUh-SEER-14.0 | DEER2015 | Code/Standard | 14 | 11.9296 | 8.2 | 3.48 | 18 | 55 | Air | 0.744 | 0.24467 | 385.2 | 0.294 | FALSE | one-speed | cDXHP | 21406 | Commercial SEER-rated Split Heat Pumps, Size Range: 18 - 55 kBTU/h, SEER = 14 (HSPF = 8.2), EIR = 0.245, Fan W/CFM = 0.29, one-speed fan, without Econo | Com SEER-Rated Split HP, 18-65 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan, no Econo; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan, no Econo; 2014: SEER = 14 (HSPF = 8.2), one-speed fan, no Econo | 2014: SEER = 14 (HSPF = 8.2), one-speed fan, no Econo
| dxHP-Com-Split-lt55kBTUh-SEER-15.0 | DEER2015 | Measure | 15 | 12.7817 | 8.7 | 3.68 | 18 | 65 | Air | 0.744 | 0.23218 | 385.2 | 0.251 | FALSE | one-speed | cDXHP | 21506 | Commercial SEER-rated Split Heat Pumps, Size Range: 18 - 65 kBTU/h, SEER = 15 (HSPF = 8.7), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo
| dxHP-Com-Split-lt55kBTUh-SEER-16.0 | DEER2015 | Measure | 16 | 12.48 | 9 | 3.57 | 18 | 65 | Air | 0.724 | 0.23814 | 360 | 0.271 | FALSE | two-speed | cDXHP | 21604 | Commercial SEER-rated Split Heat Pumps, Size Range: 18 - 65 kBTU/h, SEER = 16 (HSPF = 9.0), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, without Econo
| dxHP-Com-Split-lt55kBTUh-SEER-17.0 | DEER2015 | Measure | 17 | 13.26 | 9.4 | 3.74 | 18 | 65 | Air | 0.724 | 0.2225 | 360 | 0.271 | FALSE | two-speed | cDXHP | 21704 | Commercial SEER-rated Split Heat Pumps, Size Range: 18 - 65 kBTU/h, SEER = 17 (HSPF = 9.4), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, without Econo
| dxHP-Com-Split-lt55kBTUh-SEER-18.0 | DEER2015 | Measure | 18 | 14.04 | 9.7 | 3.86 | 18 | 65 | Air | 0.724 | 0.2086 | 360 | 0.271 | FALSE | two-speed | cDXHP | 21802 | Commercial SEER-rated Split Heat Pumps, Size Range: 18 - 65 kBTU/h, SEER = 18 (HSPF = 9.7), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, without Econo
| dxHP-Com-Split-55to65kBTUh-SEER-14.0 | DEER2015 | Code/Standard | 14 | 11.1125 | 8.2 | 3.25 | 55 | 65 | Air | 0.717 | 0.27047 | 335.4 | 0.294 | TRUE | two-speed | cDXHP | 21408 | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 14 (HSPF = 8.2), EIR = 0.27, Fan W/CFM = 0.29, two-speed fan, with Econo | Com SEER-Rated Split HP, 18-65 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan, no Econo; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan, no Econo; 2014: SEER = 14 (HSPF = 8.2), two-speed fan, w/Econo | 2014: SEER = 14 (HSPF = 8.2), two-speed fan, w/Econo | Com SEER-Rated Split HP, 18-65 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan, w/Econo; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan, w/Econo; 2014: SEER = 14 (HSPF = 8.2), two-speed fan, w/Econo
| dxHP-Com-Split-55to65kBTUh-SEER-15.0 | DEER2015 | Measure | 15 | 11.9062 | 8.7 | 3.44 | 55 | 65 | Air | 0.717 | 0.25585 | 335.4 | 0.251 | TRUE | two-speed | cDXHP | 21508 | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 15 (HSPF = 8.7), EIR = 0.256, Fan W/CFM = 0.25, two-speed fan, with Econo
| dxHP-Com-Split-55to65kBTUh-SEER-16.0 | DEER2015 | Measure | 16 | 12.48 | 9 | 3.57 | 55 | 65 | Air | 0.724 | 0.23814 | 360 | 0.271 | TRUE | two-speed | cDXHP | 21604 | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 16 (HSPF = 9.0), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, with Econo
| dxHP-Com-Split-55to65kBTUh-SEER-17.0 | DEER2015 | Measure | 17 | 13.26 | 9.4 | 3.74 | 55 | 65 | Air | 0.724 | 0.2225 | 360 | 0.271 | TRUE | two-speed | cDXHP | 21704 | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 17 (HSPF = 9.4), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, with Econo
| dxHP-Com-Split-55to65kBTUh-SEER-18.0 | DEER2015 | Measure | 18 | 14.04 | 9.7 | 3.86 | 55 | 65 | Air | 0.724 | 0.2086 | 360 | 0.271 | TRUE | two-speed | cDXHP | 21802 | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 18 (HSPF = 9.7), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, with Econo
| dxHP-Com-Split-SEER-10.0 | DEER2015 | pre-2001 | 10 | 8.5211 | 7.1 | 3.01 | 18 | 65 | Air | 0.744 | 0.34453 | 385.2 | 0.365 | FALSE | one-speed | cDXHP | 21006 | Commercial SEER-rated Split Heat Pumps, Size Range: 18 - 65 kBTU/h, SEER = 10 (HSPF = 7.1), EIR = 0.345, Fan W/CFM = 0.37, one-speed fan, without Econo | Com SEER-Rated Split HP, 18-65 kBTU/h | pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan, no Econo | pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan, w/Econo
| dxHP-Com-Split-SEER-13.0 | DEER2015 | post-2001 | 13 | 11.0775 | 8.2 | 3.49 | 18 | 65 | Air | 0.744 | 0.25823 | 385.2 | 0.348 | FALSE | one-speed | cDXHP | 21306 | Commercial SEER-rated Split Heat Pumps, Size Range: 18 - 65 kBTU/h, SEER = 13 (HSPF = 8.2), EIR = 0.258, Fan W/CFM = 0.35, one-speed fan, without Econo |  | post-2001: SEER = 13 (HSPF = 8.2), one-speed fan, no Econo | post-2001: SEER = 13 (HSPF = 8.2), one-speed fan, w/Econo
Note on D117: different lookup references

## Packaged AC Fan Power
Fan Power Evaluation for Packaged Air Conditioners
Bi-Variable Regression of Supply Fan W/cfm vs Capacity and Rated EER |  |  |  |  | Average Supply Fan W/CFM for each Equipment Type and Size Range
[5 empty] | System Description |  |  |  |  | Fan W/cfm
The statistical analysis shown below indicates that EER is not a significant variable in determing the fan power for the various equipment size groups (the T-stat for EER is below the critical T-value for all cases). |  |  |  |  | Packaged Single Zone: 65 to 134 kBtuh (6 to 11 tons) |  |  |  |  | 0.40296
[5 empty] | Packaged Single Zone: 135 to 239 kBtuh (12 to 19 tons) |  |  |  |  | 0.4071
The conclusion of this excercise is that supply fan W/cfm should be treated as constant within a given capacity range. Thus, averages were calculated for each equipment type and range. |  |  |  |  | Packaged Single Zone: 240 to 759 kBtuh (20 to 65 tons) |  |  |  |  | 0.60866
[5 empty] | Packaged VAV: 240 to 759 kBtuh (20 to 65 tons) |  |  |  |  | 0.72063
Packaged Single Zone: 65 to 134 kBtuh (6 to 11 tons) |  |  |  |  | Packaged AC equipment Unit Data used for the determination of Fan W/CFM
Weak relationships for both EER and Cap, low R2 |  |  |  |  | Unit Type | Mfgr | Model # | Cap^2 | Cap, tons | Rated EER | Fan W/cfm
Coefficient Description | EER | Cap | Const | T-critical | PSZ | York | ZXG07 (R410A) | 36 | 6 | 11 | 0.458 | 6
Coefficient Value | -0.017528 | 0.0083938 | 0.53816 |  | PSZ | Ruud | RLNL-C073 (R410A) | 36 | 6 | 11.2 | 0.427 | 6
Std Err of coef | 0.023816 | 0.0096649 | 0.2891 |  | PSZ | McQuay | MPS 006B (R410A) | 36 | 6 | 11.5 | 0.409 | 6
R2, Std Err of Y | 0.049437 | 0.074057 | #N/A |  | PSZ | York | ZYG07 (R410A) | 36 | 6 | 12 | 0.411 | 6
F, deg freedom | 0.6501 | 25 | #N/A |  | PSZ | Carrier | 48PG07 (R410A) | 36 | 6 | 12 | 0.292 | 6
Sum of Squares: regr, resid. | 0.0071309 | 0.13711 | #N/A |  | PSZ | McQuay | MPS 007B (R410A) | 49 | 7 | 11.2 | 0.344 | 7
T-stat | 0.736 | 0.86848 | 1.8615 | 2.0595 | PSZ | Lennox | KGA092S4B | 56.25 | 7.5 | 11 | 0.316 | 7.5
[5 empty] | PSZ | York | ZXG08 (R410A) | 56.25 | 7.5 | 11 | 0.433 | 7.5
Packaged Single Zone: 135 to 239 kBtuh (12 to 19 tons) |  |  |  |  | PSZ | Ruud | RKNL-C090 (R410A) | 56.25 | 7.5 | 11.2 | 0.466 | 7.5
Moderate relation ship for Capacity; weak relationship for EER |  |  |  |  | PSZ | York | ZYG08 (R410A) | 56.25 | 7.5 | 12 | 0.409 | 7.5
Coefficient Description | EER | Cap | Const | T-critical | PSZ | Carrier | 48PG08 (R410A) | 56.25 | 7.5 | 12.5 | 0.274 | 7.5
Coefficient Value | -0.043109 | -0.017834 | 1.1629 |  | PSZ | Lennox | KGA092H4B | 56.25 | 7.5 | 12.5 | 0.338 | 7.5
Std Err of coef | 0.036142 | 0.0084849 | 0.39661 |  | PSZ | Ruud | RLRL-C090 (R410A) | 56.25 | 7.5 | 13 | 0.505 | 7.5
R2, Std Err of Y | 0.30041 | 0.075082 | #N/A |  | PSZ | McQuay | MPS 008B (R410A) | 64 | 8 | 11.2 | 0.45 | 8
F, deg freedom | 3.8647 | 18 | #N/A |  | PSZ | Lennox | KGA102S4B | 72.25 | 8.5 | 11 | 0.313 | 8.5
Sum of Squares: regr, resid. | 0.043573 | 0.10147 | #N/A |  | PSZ | York | ZXG09 (R410A) | 72.25 | 8.5 | 11 | 0.416 | 8.5
T-stat | 1.1928 | 2.1018 | 2.9321 | 2.1009 | PSZ | York | ZYG09 (R410A) | 72.25 | 8.5 | 12 | 0.421 | 8.5
[5 empty] | PSZ | Carrier | 48PG09 (R410A) | 72.25 | 8.5 | 12.2 | 0.368 | 8.5
Packaged Single Zone: 240 to 759 kBtuh (20 to 65 tons) |  |  |  |  | PSZ | Lennox | KGA102H4B | 72.25 | 8.5 | 12.2 | 0.403 | 8.5
Moderate relationship for Capacity; very weak for EER |  |  |  |  | PSZ | Lennox | KGA120S4B | 100 | 10 | 11 | 0.338 | 10
Coefficient Description | EER | Cap | Const | T-critical | PSZ | York | ZXG12 (R410A) | 100 | 10 | 11 | 0.506 | 10
Coefficient Value | -0.03485 | 0.0087033 | 0.67807 |  | PSZ | McQuay | MPS 010B (R410A) | 100 | 10 | 11.2 | 0.375 | 10
Std Err of coef | 0.029413 | 0.0017402 | 0.35008 |  | PSZ | Ruud | RKKL-B120 (R410A) | 100 | 10 | 11.2 | 0.577 | 10
R2, Std Err of Y | 0.67641 | 0.0901 | #N/A |  | PSZ | York | ZYG12 (R410A) | 100 | 10 | 11.5 | 0.51 | 10
F, deg freedom | 27.1746 | 26 | #N/A |  | PSZ | Carrier | 50PG12 (R410A) | 100 | 10 | 12 | 0.323 | 10
Sum of Squares: regr, resid. | 0.44121 | 0.21107 | #N/A |  | PSZ | Carrier | 48PG12 (R410A) | 100 | 10 | 12 | 0.35 | 10
T-stat | 1.1849 | 5.0012 | 1.9369 | 2.0555 | PSZ | Lennox | KGA120H4B | 100 | 10 | 12 | 0.399 | 10
[5 empty] | PSZ | Ruud | RLRL-C120 (R410A) | 100 | 10 | 12.5 | 0.452 | 10
Packaged VAV: 240 to 759 kBtuh (20 to 65 tons)
Moderate relationship for Capacity; very weak for EER |  |  |  |  | PSZ | McQuay | MPS 012B (R410A) | 144 | 12 | 11 | 0.5 | 12
Coefficient Description | EER | Cap | Const | T-critical | PSZ | Lennox | KGA150S4B | 156.25 | 12.5 | 11 | 0.508 | 12.5
Coefficient Value | 0.014874 | 0.0085156 | 0.23919 |  | PSZ | Ruud | RLNL-G151 (R410A) | 156.25 | 12.5 | 11 | 0.533 | 12.5
Std Err of coef | 0.048461 | 0.00185 | 0.5282 |  | PSZ | Ruud | RLKL-B151 (R410A) | 156.25 | 12.5 | 11 | 0.557 | 12.5
R2, Std Err of Y | 0.52827 | 0.095114 | #N/A |  | PSZ | Ruud | RKKL-C151 (R410A) | 156.25 | 12.5 | 11.1 | 0.557 | 12.5
F, deg freedom | 11.7587 | 21 | #N/A |  | PSZ | Carrier | 48PG14 (R410A) | 156.25 | 12.5 | 11.4 | 0.45 | 12.5
Sum of Squares: regr, resid. | 0.21275 | 0.18998 | #N/A |  | PSZ | Lennox | KGA156H4B | 169 | 13 | 12 | 0.288 | 13
T-stat | 0.30693 | 4.6029 | 0.45284 | 2.0796 | PSZ | Lennox | KGA180S4B | 225 | 15 | 10.8 | 0.317 | 15
[5 empty] | PSZ | Ruud | RKKL-B180 (R410A) | 225 | 15 | 10.9 | 0.35 | 15
[5 empty] | PSZ | York | ZF180N (R410A) | 225 | 15 | 11 | 0.449 | 15
[5 empty] | PSZ | McQuay | MPS 015B (R410A) | 225 | 15 | 11.1 | 0.342 | 15
[5 empty] | PSZ | Carrier | 48PG16 (R410A) | 225 | 15 | 11.4 | 0.344 | 15
[5 empty] | PSZ | Carrier | 50PG16 (R410A) | 225 | 15 | 11.6 | 0.307 | 15
[5 empty] | PSZ | Lennox | KGA180H4B | 225 | 15 | 12 | 0.315 | 15
[5 empty] | PSZ | York | ZJ180N (R410A) | 225 | 15 | 12.4 | 0.403 | 15
[5 empty] | PSZ | Lennox | KGA210S4B | 306.25 | 17.5 | 10.8 | 0.347 | 17.5
[5 empty] | PSZ | York | ZF210N (R410A) | 306.25 | 17.5 | 11 | 0.385 | 17.5
[5 empty] | PSZ | Ruud | RKNL-C210 (R410A) | 306.25 | 17.5 | 11.6 | 0.429 | 17.5
[5 empty] | PSZ | Lennox | KGA210H4B | 306.25 | 17.5 | 12 | 0.361 | 17.5
[5 empty] | PSZ | York | ZJ210N (R410A) | 306.25 | 17.5 | 12 | 0.366 | 17.5
[5 empty] | PSZ | Carrier | 48PG20 (R410A) | 324 | 18 | 11.6 | 0.441 | 18
[5 empty] | PSZ | Carrier | 48A2-020 | 400 | 20 | 10.1 | 0.423 | 20
[5 empty] | PSZ | Lennox | KGA240S4B | 400 | 20 | 10.8 | 0.417 | 20
[5 empty] | PSZ | McQuay | MPS 020B (R410A) | 400 | 20 | 11.1 | 0.381 | 20
[5 empty] | PSZ | York | ZJ240N (R410A) | 400 | 20 | 11.5 | 0.43 | 20
[5 empty] | PSZ | Carrier | 48PG24 (R410A) | 400 | 20 | 11.6 | 0.475 | 20
[5 empty] | PSZ | Lennox | KGA240H4B | 400 | 20 | 12 | 0.423 | 20
[5 empty] | PSZ | Lennox | SGC240H4B | 400 | 20 | 12.6 | 0.375 | 20
[5 empty] | PSZ | Carrier | 48A2-025 | 625 | 25 | 10 | 0.482 | 25
[5 empty] | PSZ | York | Z42+C0(2,4,5) | 625 | 25 | 10.5 | 0.561 | 25
[5 empty] | PSZ | Lennox | LGH300H4V | 625 | 25 | 11.6 | 0.447 | 25
[5 empty] | PSZ | Carrier | 48A2-027 | 729 | 27 | 10.1 | 0.5 | 27
[5 empty] | PSZ | Carrier | 48A2-030 | 900 | 30 | 10 | 0.543 | 30
[5 empty] | PSZ | York | Z33+C0(2,4,5) | 900 | 30 | 10.1 | 0.662 | 30
[5 empty] | PSZ | Lennox | LGH360H4V | 900 | 30 | 10.6 | 0.535 | 30
[5 empty] | PSZ | Carrier | 48A2-035 | 1225 | 35 | 10 | 0.737 | 35
[5 empty] | PSZ | Lennox | LGH420S4V | 1225 | 35 | 10 | 0.65 | 35
[5 empty] | PSZ | Lennox | LGH420H4V | 1225 | 35 | 10.8 | 0.654 | 35
[5 empty] | PSZ | Lennox | LCH420H4V | 1225 | 35 | 10.8 | 0.678 | 35
[5 empty] | PSZ | Lennox | LGH480S4V | 1600 | 40 | 9.8 | 0.728 | 40
[5 empty] | PSZ | York | Z34+C0(2,4,5) | 1600 | 40 | 10 | 0.741 | 40
[5 empty] | PSZ | Carrier | 48A2-040 | 1600 | 40 | 10.3 | 0.824 | 40
[5 empty] | PSZ | Lennox | LGH480H4V | 1600 | 40 | 10.8 | 0.721 | 40
[5 empty] | PSZ | Lennox | LCH480H4V | 1600 | 40 | 10.8 | 0.775 | 40
[5 empty] | PSZ | Lennox | LGH540S4 | 2025 | 45 | 10 | 0.823 | 45
[5 empty] | PSZ | Lennox | LGH600S4V | 2500 | 50 | 9.8 | 0.858 | 50
[5 empty] | PSZ | York | YPAL050N | 2500 | 50 | 10 | 0.625 | 50
[5 empty] | PSZ | York | YPAL051N | 3025 | 55 | 9.9 | 0.688 | 55
[5 empty] | PSZ | York | YPAL060N | 3600 | 60 | 9.8 | 0.636 | 60
[5 empty] | PSZ | Carrier | 48A2-060 | 3600 | 60 | 10.1 | 0.859 | 60
[5 empty] | PVAV | Carrier | 48A2-020 | 400 | 20 | 10.1 | 0.467 | 20
[5 empty] | PVAV | Carrier | 48A2-025 | 625 | 25 | 10 | 0.52 | 25
[5 empty] | PVAV | Carrier | 48A2-027 | 729 | 27 | 10.1 | 0.535 | 27
[5 empty] | PVAV | Carrier | 48A2-030 | 900 | 30 | 10 | 0.576 | 30
[5 empty] | PVAV | Carrier | 48A2-035 | 1225 | 35 | 10 | 0.78 | 35
[5 empty] | PVAV | Carrier | 48A2-040 | 1600 | 40 | 10.3 | 0.87 | 40
[5 empty] | PVAV | Carrier | 48A2-060 | 3600 | 60 | 10.1 | 0.916 | 60
[5 empty] | PVAV | Lennox | LGH300H4V | 625 | 25 | 11.6 | 0.533 | 25
[5 empty] | PVAV | Lennox | LGH360H4V | 900 | 30 | 10.6 | 0.586 | 30
[5 empty] | PVAV | Lennox | LGH420H4V | 1225 | 35 | 10.8 | 0.732 | 35
[5 empty] | PVAV | Lennox | LGH420S4V | 1225 | 35 | 10 | 0.728 | 35
[5 empty] | PVAV | Lennox | LGH480H4V | 1600 | 40 | 10.8 | 0.79 | 40
[5 empty] | PVAV | Lennox | LGH480S4V | 1600 | 40 | 9.8 | 0.799 | 40
[5 empty] | PVAV | Lennox | LGH540S4 | 2025 | 45 | 10 | 0.888 | 45
[5 empty] | PVAV | Lennox | LGH600S4V | 2500 | 50 | 9.8 | 0.922 | 50
[5 empty] | PVAV | Lennox | LCH420H4V | 1225 | 35 | 10.8 | 0.751 | 35
[5 empty] | PVAV | Lennox | LCH480H4V | 1600 | 40 | 10.8 | 0.843 | 40
[5 empty] | PVAV | York | Z42+C0(2,4,5) | 625 | 25 | 10.5 | 0.615 | 25
[5 empty] | PVAV | York | Z33+C0(2,4,5) | 900 | 30 | 10.1 | 0.712 | 30
[5 empty] | PVAV | York | Z34+C0(2,4,5 | 1600 | 40 | 10 | 0.797 | 40
[5 empty] | PVAV | York | YPAL050N | 2500 | 50 | 10 | 0.672 | 50
[5 empty] | PVAV | York | YPAL051N | 3025 | 55 | 9.9 | 0.734 | 55
[5 empty] | PVAV | York | YPAL051E | 3025 | 55 | 10.2 | 0.708 | 55
[5 empty] | PVAV | York | YPAL060N | 3600 | 60 | 9.8 | 0.821 | 60

## Split DX Fan Power
Fan Power Evaluation for Split DX Systems
For the Split DX performance data, there is a trend of decreasing fan power with increasing SEER. Based on the statistical analysis of all the data, SEER is determined to be the only important variable when assessing fan power based on Size (capacity), SEER and EER levels.
The data was processed into bins as summarized below.
DX Split Unit data | [5 empty] | Bin Average Summary
Tot Cap | Tons | SEER | EER | Fan W/cfm |  | SEER | Avg
23397 | 1.9498 | 10 | 8.87 | 0.365 |  | Bin | W/cfm
30000 | 2.5 | 10 | 9.29 | 0.365 |  | 10 | 0.365
24120 | 2.01 | 10 | 9.51 | 0.365 |  | 13 | 0.34833
17947 | 1.4956 | 10 | 8.77 | 0.365 |  | 14 | 0.29367
35495 | 2.9579 | 10 | 9.08 | 0.365 |  | 15 | 0.25133
18840 | 1.57 | 10 | 9.83 | 0.365 |  | 16 to 18 | 0.27061
47993 | 3.9994 | 10 | 8.46 | 0.365 |  | 19 to 20 | 0.23275
48893 | 4.0744 | 10 | 8.79 | 0.365
41713 | 3.4761 | 10 | 9.31 | 0.365
43994.894 | 3.6662 | 13 | 11.36 | 0.365
49930 | 4.1608 | 13 | 12.04 | 0.365
26120 | 2.1767 | 13 | 12.5 | 0.365
44700 | 3.725 | 13 | 11.09 | 0.364
43544.043 | 3.6287 | 13 | 11.3 | 0.365
30545.745 | 2.5455 | 13 | 11.72 | 0.365
43400 | 3.6167 | 13 | 10.74 | 0.288
62102 | 5.1752 | 13 | 10.98 | 0.329
41570 | 3.4642 | 13 | 11.35 | 0.329
36500 | 3.0417 | 14 | 11.99 | 0.383
37680 | 3.14 | 14 | 13.08 | 0.263
41520 | 3.46 | 14 | 13.22 | 0.24
31167.925 | 2.5973 | 14 | 11.7 | 0.225
29100 | 2.425 | 14 | 11.84 | 0.345
25300 | 2.1083 | 14 | 12.17 | 0.306
45047.791 | 3.754 | 15 | 12.72 | 0.256
36100 | 3.0083 | 15 | 12.99 | 0.233
29600 | 2.4667 | 15 | 13.11 | 0.19
51934.1453 | 4.3278 | 15 | 12.39 | 0.318
30874 | 2.5728 | 15 | 13.01 | 0.256
23967 | 1.9972 | 15 | 12.85 | 0.255
36720.291 | 3.06 | 16 | 11.74 | 0.256
36192.361 | 3.016 | 16 | 11.77 | 0.179
36955.7197 | 3.0796 | 16 | 12.2 | 0.255
37000 | 3.0833 | 16 | 11.61 | 0.274
50500 | 4.2083 | 16 | 12.17 | 0.258
37600 | 3.1333 | 16 | 12.2 | 0.367
36910 | 3.0758 | 16 | 12.42 | 0.255
47293.871 | 3.9412 | 16 | 11.1 | 0.292
35847.791 | 2.9873 | 16 | 11.33 | 0.256
35751.184 | 2.9793 | 17 | 12.4 | 0.255
36479.053 | 3.0399 | 17 | 12.47 | 0.255
36117.884 | 3.0098 | 17 | 12.68 | 0.255
38000 | 3.1667 | 17 | 12.28 | 0.202
37600 | 3.1333 | 17 | 12.47 | 0.162
36800 | 3.0667 | 17 | 12.67 | 0.292
61342.341 | 5.1119 | 17 | 11.41 | 0.365
51504.454 | 4.292 | 17 | 12.16 | 0.328
33842.341 | 2.8202 | 17 | 12.95 | 0.365
37800 | 3.15 | 18 | 12.97 | 0.287
37600 | 3.1333 | 18 | 13.22 | 0.223
37347.791 | 3.1123 | 18 | 12.73 | 0.256
33259.053 | 2.7716 | 18 | 13.37 | 0.255
34047.791 | 2.8373 | 18 | 13.75 | 0.256
36300 | 3.025 | 18 | 13.38 | 0.366
38933.116 | 3.2444 | 19 | 13.12 | 0.255
25966.252 | 2.1639 | 19 | 14 | 0.255
38000 | 3.1667 | 19 | 13.82 | 0.166
26498.252 | 2.2082 | 20 | 14.43 | 0.255
| Coefficient Description | Tons | SEER | EER | Constant | T-critical
| Coefficient Value | -0.0073095 | -0.01094 | 0.009611 | 0.51518
| Std Err of coef | 0.0093189 | 0.0048462 | 0.0088043 | 0.068558
| R2, Std Err of Y | 0.41485 | 0.048845 | #N/A | #N/A
| F, deg freedom | 12.7613 | 54 | #N/A | #N/A
| Sum of Squares: regr, resid. | 0.091339 | 0.12884 | #N/A | #N/A
| T-stat | 0.78437 | 2.2574 | 1.0916 | 7.5145 | 2.0049

## Performance Map Selection
Performance Map Selection Process
Several new performance map data sets were developed and analyzed to update the packaged and split air conditioning system efficiency measures. The data sets span a broad range of manufacturer, model, unit capacity and efficiency level. Each data set inlcudes operational data such as fan power consumption and coil bypass factor as well as a full set of performance curves for simulation.
Commercial EER-rated Packaged Performance curves
The performance maps for commercial EER-rate packaged AC units were grouped by system size and fan control type as shown in the table below. For each group a series of simulations were run to select the most typical set of performance curves in the group. The simulations included all California climate zones and the small office and large retail building types. The performance curves for the selected unit were then used for all simulations of measures for that group.
Run Group Categories for Performance Map Selection
| Size Range, kBtu/hr | Fan Control | Number of Performance Maps
| 65 to 134 | Two Speed | 28
| 135 to 239 | Two Speed | 27
| 240 to 759 | Two Speed | 29
| 240 to 759 | Variable Speed | 24
For each test run on each of the performance maps described in the table above, annual cooling and fan energy values were collected. These data were evaluated to select the performance map for which the deviation from the median was lowest across all test conditions (climate zone, building type and energy end-use).

## Split HP Tier Selection
Split Heat Pump Tier Level Selection
This worksheet illustrates the process that was used to establish the HSPF tier levels for split heat pump measures.
Since the DEER2014 performance data are based on equipment selections made several years ago, available efficiency levels were collected from recent manufacturer literature for comparison.
The measure levels were based on a curve fit to the recent manufacturer data.
Recent Product Data from Manufacturer Literature
Mfg | SEER | HSPF
Carrier | 13 | 8.3
Goodman | 14 | 8.1
Trane | 14 | 8.2
Carrier | 14 | 8.5
Carrier | 14.5 | 8.5
Lennox | 15 | 8.2
Goodman | 15 | 8.1
Carrier | 15 | 9
Carrier | 15 | 8.2
Lennox | 15.2 | 9.2
Lennox | 15.2 | 9.2
Carrier | 15.3 | 9
Carrier | 15.3 | 9
Carrier | 15.5 | 9.5
Carrier | 15.5 | 9
Lennox | 15.7 | 9.2
Lennox | 15.7 | 8.7
Lennox | 16 | 9.5
Trane | 16 | 9.5
Lennox | 16.2 | 8.7
Lennox | 16.2 | 9.5 | Split HP Measure Tier Levels
Lennox | 16.2 | 9 | Tier | SEER | HSPF
Trane | 16.25 | 9.7 | 0 | 14 | 8.4
Lennox | 16.5 | 9.2 | 1 | 15 | 8.7
Lennox | 16.5 | 9 | 2 | 16 | 9
Lennox | 16.5 | 9 | 3 | 17 | 9.4
Goodman | 16.5 | 9 | 4 | 18 | 9.7
Goodman | 16.75 | 9.25
Lennox | 17 | 8.5
Goodman | 17 | 9.3
Lennox | 17.2 | 9.2
Carrier | 17.2 | 9.5
Carrier | 17.2 | 9.5
Goodman | 17.5 | 9.25
Lennox | 17.7 | 9.5
Goodman | 18 | 9.5
Trane | 18 | 10
Trane | 18 | 9.5
Trane | 18 | 9.5
Carrier | 18 | 11
Lennox | 18.5 | 9.7
Trane | 19 | 10
Carrier | 19 | 10
Lennox | 19.2 | 9.2
Lennox | 19.5 | 10.2
Lennox | 20.5 | 10.2
Carrier | 20.5 | 13
Lennox | 21.5 | 10
Lennox | 23.5 | 10.2
Values from DEER 2014 Performance Map Data
| SEER | HSPF
| 10 | 6.8
| 10 | 7
| 10 | 7.2
| 10 | 6.9
| 10 | 7.2
| 10 | 7.2
| 10 | 7.2
| 10 | 7.3
| 10 | 7.2
| 13 | 8.3
| 13 | 8
| 13 | 8
| 13 | 8.3
| 13 | 8.1
| 13 | 8.55
| 13 | 8.1
| 13 | 8.5
| 13 | 8
| 14 | 8.2
| 14 | 8.5
| 14 | 8.5
| 14 | 8.2
| 14 | 8.6
| 14 | 8.3
| 15 | 8.8
| 15 | 8.2
| 15 | 9
| 15 | 9.4
| 15 | 9
| 15 | 8
| 16 | 8.8
| 16 | 8.3
| 16 | 8.5
| 16 | 8.4
| 16 | 8.9
| 16 | 8.15
| 16 | 8.2
| 16 | 8.25
| 17 | 9.5
| 17 | 9
| 17 | 8.75
| 17 | 8.55
| 18 | 8.45
| 18 | 9.2
| 18 | 8.75
| 18 | 8.4

## Split DX Selected Perf Maps
Split DX Selected Performance Maps
This table lists the complete performance data sets used for the split DX measures for the DEER2015 update.
Indep. | Dependents
1 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78
Equip ID | SEER | EER | Tot Cap | Sen/Total | EIR | cfm/Btuh | Fan W/cfm | Coil-BF | Crnk/Tot kW | Crnk Off | Total Capacity Curve Fit Coefficients | [5 empty] | Sensible Capacity Curve Fit Coefficients | [5 empty] | EIR Curve Fit Coefficients | [5 empty] | Coil-BF Curve Fit Coefficients | [5 empty] | Temperate EIR_PLR Curve Fit Coefficients |  |  |  | Moderate EIR_PLR Curve Fit Coefficients |  |  |  | Hot EIR_PLR Curve Fit Coefficients |  |  |  | Temp C-Loss Curve Fit Coefficients |  |  | Mod C-Loss Curve Fit Coefficients |  |  | Hot C-Loss Curve Fit Coefficients |  |  | Cmp Spd | Low Speed Ratios |  | HSPF | COP47 | Heat Cap | H-EIR | Total Capacity Curve Fit Coefficients | [5 empty] | HIR Curve Fit Coefficients | [5 empty] | BF-FFLOW Curve Coeffients
11402 | 14 | 12.1655 | 30924.8571 | 0.75406 | 0.2393 | 0.0321 | 0.294 | 0.12 | 0.0109 | 100 | 1.8945 | -0.039201 | 0.00046953 | 0.0040681 | -1.3357e-05 | -0.00010081 | -0.1319 | 0.091027 | -0.0010761 | -0.0096549 | -1.6898e-05 | 0.00014665 | -1.4196 | 0.065634 | -0.00044695 | -0.002831 | 0.00019172 | -0.00022513 | 80.3536 | -2.4634 | 0.019553 | 0.096934 | 0.00023569 | -0.0021081 | -0.0001 | 1.1176 | -0.14004 | 0.02252 | 8e-05 | 1.1481 | -0.18252 | 0.0343 | 0 | 1.1763 | -0.2231 | 0.04682 | 0.89347 | 0.11776 | -0.01123 | 0.8687 | 0.14851 | -0.01721 | 0.84664 | 0.17682 | -0.02346 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1
11403 | 14 | 11.8179 | 52519.3636 | 0.75922 | 0.2466 | 0.03263 | 0.294 | 0.10652 | 0.0090909 | 100 | 2.3004 | -0.05275 | 0.00057866 | 0.0052398 | -1.7642e-05 | -0.00011033 | 1.0053 | 0.060879 | -0.00087668 | -0.013109 | -1.783e-05 | 0.00019756 | -1.6279 | 0.081247 | -0.00059318 | -0.0092213 | 0.00020694 | -0.00017981 | 58.7088 | -1.8847 | 0.015572 | 0.15884 | 0.00015075 | -0.0027944 | -0.0001 | 1.1176 | -0.14004 | 0.02252 | 8e-05 | 1.1481 | -0.18252 | 0.0343 | 0 | 1.1763 | -0.2231 | 0.04682 | 0.89347 | 0.11776 | -0.01123 | 0.8687 | 0.14851 | -0.01721 | 0.84664 | 0.17682 | -0.02346 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1
11405 | 14 | 11.1125 | 58310 | 0.717 | 0.26503 | 0.0321 | 0.294 | 0.12 | 0.0109 | 100 | 3.4906 | -0.091345 | 0.00095659 | 0.0062175 | -7.875e-06 | -0.00018605 | 2.9971 | 0.0018497 | -0.00038268 | -0.017138 | -1.2463e-05 | 0.00021013 | -3.4577 | 0.15512 | -0.0011438 | -0.021251 | 0.00029839 | -0.00023171 | 29.7842 | -0.96569 | 0.0078708 | 0.23115 | 0.00019408 | -0.0036332 | 0.00284 | 1.0607 | -0.06874 | 0.00523 | -0.00146 | 1.1032 | -0.1193 | 0.01755 | -0.00016 | 1.1224 | -0.14282 | 0.02058 | 0.88889 | 0.06952 | -0.00646 | 0.87243 | 0.09413 | -0.00752 | 0.85625 | 0.12115 | -0.01241 | 2 | 0.773 | 0.682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.745 | -0.745 | 1 | 1.189
11501 | 15 | 12.7817 | 34895 | 0.744 | 0.23218 | 0.0321 | 0.251 | 0.12 | 0.0109 | 100 | 0.33897 | 0.00041807 | 0.00021371 | 0.0089003 | -2.5963e-05 | -0.0001473 | 4.678 | -0.073712 | 0.00028931 | 0.0064477 | -2.7952e-05 | -6.2571e-05 | 0.9275 | -0.00046154 | 3.96e-05 | -0.0068688 | 0.0002048 | -0.00019954 | 25.5462 | -0.65922 | 0.0051164 | -0.027638 | 0.00033263 | -0.00058485 | -7e-05 | 1.1695 | -0.21321 | 0.04377 | 0.00012 | 1.2018 | -0.26145 | 0.05955 | 7e-05 | 1.2314 | -0.30703 | 0.07557 | 0.85187 | 0.17007 | -0.02194 | 0.82723 | 0.20273 | -0.02996 | 0.8053 | 0.2327 | -0.038 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1
11505 | 15 | 11.9062 | 58310 | 0.717 | 0.25127 | 0.0321 | 0.251 | 0.12 | 0.0109 | 100 | 3.4906 | -0.091345 | 0.00095659 | 0.0062175 | -7.875e-06 | -0.00018605 | 2.9971 | 0.0018497 | -0.00038268 | -0.017138 | -1.2463e-05 | 0.00021013 | -3.4577 | 0.15512 | -0.0011438 | -0.021251 | 0.00029839 | -0.00023171 | 29.7842 | -0.96569 | 0.0078708 | 0.23115 | 0.00019408 | -0.0036332 | 0.00284 | 1.0607 | -0.06874 | 0.00523 | -0.00146 | 1.1032 | -0.1193 | 0.01755 | -0.00016 | 1.1224 | -0.14282 | 0.02058 | 0.88889 | 0.06952 | -0.00646 | 0.87243 | 0.09413 | -0.00752 | 0.85625 | 0.12115 | -0.01241 | 2 | 0.773 | 0.682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.745 | -0.745 | 1 | 1.189
11604 | 16 | 12.48 | 58805 | 0.724 | 0.23814 | 0.03 | 0.271 | 0.102 | 0.01 | 100 | 3.4462 | -0.09133 | 0.000924 | 0.0070176 | -2.0119e-05 | -0.00015082 | 0.25994 | 0.074843 | -0.00091895 | -0.0096756 | -3.0969e-05 | 0.00016487 | -3.0223 | 0.13455 | -0.0010034 | -0.015978 | 0.00023792 | -0.00017556 | 66.8974 | -2.0132 | 0.01588 | 0.10092 | 0.00035451 | -0.0023705 | -0.0072625 | 1.1134 | -0.13234 | 0.026242 | -0.00144 | 1.1191 | -0.13966 | 0.021968 | 0.0063475 | 1.1162 | -0.13862 | 0.016045 | 0.9595 | 0.093423 | -0.006875 | 0.94032 | 0.12407 | -0.010928 | 0.92296 | 0.15259 | -0.015618 | 2 | 0.739 | 0.686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.745 | -0.745 | 1 | 1.189
11605 | 16 | 12.48 | 58805 | 0.724 | 0.23814 | 0.03 | 0.271 | 0.102 | 0.01 | 100 | 3.4462 | -0.09133 | 0.000924 | 0.0070176 | -2.0119e-05 | -0.00015082 | 0.25994 | 0.074843 | -0.00091895 | -0.0096756 | -3.0969e-05 | 0.00016487 | -3.0223 | 0.13455 | -0.0010034 | -0.015978 | 0.00023792 | -0.00017556 | 66.8974 | -2.0132 | 0.01588 | 0.10092 | 0.00035451 | -0.0023705 | -0.0072625 | 1.1134 | -0.13234 | 0.026242 | -0.00144 | 1.1191 | -0.13966 | 0.021968 | 0.0063475 | 1.1162 | -0.13862 | 0.016045 | 0.9595 | 0.093423 | -0.006875 | 0.94032 | 0.12407 | -0.010928 | 0.92296 | 0.15259 | -0.015618 | 2 | 0.739 | 0.686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.745 | -0.745 | 1 | 1.189
11610 | 16 | 12.48 | 58805 | 0.724 | 0.23814 | 0.03 | 0.271 | 0.102 | 0.01 | 100 | 3.4462 | -0.09133 | 0.000924 | 0.0070176 | -2.0119e-05 | -0.00015082 | 0.25994 | 0.074843 | -0.00091895 | -0.0096756 | -3.0969e-05 | 0.00016487 | -3.0223 | 0.13455 | -0.0010034 | -0.015978 | 0.00023792 | -0.00017556 | 66.8974 | -2.0132 | 0.01588 | 0.10092 | 0.00035451 | -0.0023705 | -0.0072625 | 1.1134 | -0.13234 | 0.026242 | -0.00144 | 1.1191 | -0.13966 | 0.021968 | 0.0063475 | 1.1162 | -0.13862 | 0.016045 | 0.9595 | 0.093423 | -0.006875 | 0.94032 | 0.12407 | -0.010928 | 0.92296 | 0.15259 | -0.015618 | 2 | 0.739 | 0.686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.745 | -0.745 | 1 | 1.189
11704 | 17 | 13.26 | 58805 | 0.724 | 0.2225 | 0.03 | 0.271 | 0.102 | 0.01 | 100 | 3.4462 | -0.09133 | 0.000924 | 0.0070176 | -2.0119e-05 | -0.00015082 | 0.25994 | 0.074843 | -0.00091895 | -0.0096756 | -3.0969e-05 | 0.00016487 | -3.0223 | 0.13455 | -0.0010034 | -0.015978 | 0.00023792 | -0.00017556 | 66.8974 | -2.0132 | 0.01588 | 0.10092 | 0.00035451 | -0.0023705 | -0.0072625 | 1.1134 | -0.13234 | 0.026242 | -0.00144 | 1.1191 | -0.13966 | 0.021968 | 0.0063475 | 1.1162 | -0.13862 | 0.016045 | 0.9595 | 0.093423 | -0.006875 | 0.94032 | 0.12407 | -0.010928 | 0.92296 | 0.15259 | -0.015618 | 2 | 0.739 | 0.686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.745 | -0.745 | 1 | 1.189
11705 | 17 | 13.26 | 58805 | 0.724 | 0.2225 | 0.03 | 0.271 | 0.102 | 0.01 | 100 | 3.4462 | -0.09133 | 0.000924 | 0.0070176 | -2.0119e-05 | -0.00015082 | 0.25994 | 0.074843 | -0.00091895 | -0.0096756 | -3.0969e-05 | 0.00016487 | -3.0223 | 0.13455 | -0.0010034 | -0.015978 | 0.00023792 | -0.00017556 | 66.8974 | -2.0132 | 0.01588 | 0.10092 | 0.00035451 | -0.0023705 | -0.0072625 | 1.1134 | -0.13234 | 0.026242 | -0.00144 | 1.1191 | -0.13966 | 0.021968 | 0.0063475 | 1.1162 | -0.13862 | 0.016045 | 0.9595 | 0.093423 | -0.006875 | 0.94032 | 0.12407 | -0.010928 | 0.92296 | 0.15259 | -0.015618 | 2 | 0.739 | 0.686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.745 | -0.745 | 1 | 1.189
11710 | 17 | 13.26 | 58805 | 0.724 | 0.2225 | 0.03 | 0.271 | 0.102 | 0.01 | 100 | 3.4462 | -0.09133 | 0.000924 | 0.0070176 | -2.0119e-05 | -0.00015082 | 0.25994 | 0.074843 | -0.00091895 | -0.0096756 | -3.0969e-05 | 0.00016487 | -3.0223 | 0.13455 | -0.0010034 | -0.015978 | 0.00023792 | -0.00017556 | 66.8974 | -2.0132 | 0.01588 | 0.10092 | 0.00035451 | -0.0023705 | -0.0072625 | 1.1134 | -0.13234 | 0.026242 | -0.00144 | 1.1191 | -0.13966 | 0.021968 | 0.0063475 | 1.1162 | -0.13862 | 0.016045 | 0.9595 | 0.093423 | -0.006875 | 0.94032 | 0.12407 | -0.010928 | 0.92296 | 0.15259 | -0.015618 | 2 | 0.739 | 0.686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.745 | -0.745 | 1 | 1.189
11802 | 18 | 14.04 | 58805 | 0.724 | 0.2086 | 0.03 | 0.271 | 0.102 | 0.01 | 100 | 3.4462 | -0.09133 | 0.000924 | 0.0070176 | -2.0119e-05 | -0.00015082 | 0.25994 | 0.074843 | -0.00091895 | -0.0096756 | -3.0969e-05 | 0.00016487 | -3.0223 | 0.13455 | -0.0010034 | -0.015978 | 0.00023792 | -0.00017556 | 66.8974 | -2.0132 | 0.01588 | 0.10092 | 0.00035451 | -0.0023705 | -0.0072625 | 1.1134 | -0.13234 | 0.026242 | -0.00144 | 1.1191 | -0.13966 | 0.021968 | 0.0063475 | 1.1162 | -0.13862 | 0.016045 | 0.9595 | 0.093423 | -0.006875 | 0.94032 | 0.12407 | -0.010928 | 0.92296 | 0.15259 | -0.015618 | 2 | 0.739 | 0.686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.745 | -0.745 | 1 | 1.189
11805 | 18 | 14.04 | 58805 | 0.724 | 0.2086 | 0.03 | 0.271 | 0.102 | 0.01 | 100 | 3.4462 | -0.09133 | 0.000924 | 0.0070176 | -2.0119e-05 | -0.00015082 | 0.25994 | 0.074843 | -0.00091895 | -0.0096756 | -3.0969e-05 | 0.00016487 | -3.0223 | 0.13455 | -0.0010034 | -0.015978 | 0.00023792 | -0.00017556 | 66.8974 | -2.0132 | 0.01588 | 0.10092 | 0.00035451 | -0.0023705 | -0.0072625 | 1.1134 | -0.13234 | 0.026242 | -0.00144 | 1.1191 | -0.13966 | 0.021968 | 0.0063475 | 1.1162 | -0.13862 | 0.016045 | 0.9595 | 0.093423 | -0.006875 | 0.94032 | 0.12407 | -0.010928 | 0.92296 | 0.15259 | -0.015618 | 2 | 0.739 | 0.686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.745 | -0.745 | 1 | 1.189
11810 | 18 | 14.04 | 58805 | 0.724 | 0.2086 | 0.03 | 0.271 | 0.102 | 0.01 | 100 | 3.4462 | -0.09133 | 0.000924 | 0.0070176 | -2.0119e-05 | -0.00015082 | 0.25994 | 0.074843 | -0.00091895 | -0.0096756 | -3.0969e-05 | 0.00016487 | -3.0223 | 0.13455 | -0.0010034 | -0.015978 | 0.00023792 | -0.00017556 | 66.8974 | -2.0132 | 0.01588 | 0.10092 | 0.00035451 | -0.0023705 | -0.0072625 | 1.1134 | -0.13234 | 0.026242 | -0.00144 | 1.1191 | -0.13966 | 0.021968 | 0.0063475 | 1.1162 | -0.13862 | 0.016045 | 0.9595 | 0.093423 | -0.006875 | 0.94032 | 0.12407 | -0.010928 | 0.92296 | 0.15259 | -0.015618 | 2 | 0.739 | 0.686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.745 | -0.745 | 1 | 1.189
11903 | 19 | 14.82 | 58805 | 0.724 | 0.20095 | 0.03 | 0.233 | 0.102 | 0.01 | 100 | 3.4462 | -0.09133 | 0.000924 | 0.0070176 | -2.0119e-05 | -0.00015082 | 0.25994 | 0.074843 | -0.00091895 | -0.0096756 | -3.0969e-05 | 0.00016487 | -3.0223 | 0.13455 | -0.0010034 | -0.015978 | 0.00023792 | -0.00017556 | 66.8974 | -2.0132 | 0.01588 | 0.10092 | 0.00035451 | -0.0023705 | -0.0072625 | 1.1134 | -0.13234 | 0.026242 | -0.00144 | 1.1191 | -0.13966 | 0.021968 | 0.0063475 | 1.1162 | -0.13862 | 0.016045 | 0.9595 | 0.093423 | -0.006875 | 0.94032 | 0.12407 | -0.010928 | 0.92296 | 0.15259 | -0.015618 | 2 | 0.739 | 0.686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.745 | -0.745 | 1 | 1.189
12001 | 20 | 15.6 | 58805 | 0.724 | 0.18971 | 0.03 | 0.233 | 0.102 | 0.01 | 100 | 3.4462 | -0.09133 | 0.000924 | 0.0070176 | -2.0119e-05 | -0.00015082 | 0.25994 | 0.074843 | -0.00091895 | -0.0096756 | -3.0969e-05 | 0.00016487 | -3.0223 | 0.13455 | -0.0010034 | -0.015978 | 0.00023792 | -0.00017556 | 66.8974 | -2.0132 | 0.01588 | 0.10092 | 0.00035451 | -0.0023705 | -0.0072625 | 1.1134 | -0.13234 | 0.026242 | -0.00144 | 1.1191 | -0.13966 | 0.021968 | 0.0063475 | 1.1162 | -0.13862 | 0.016045 | 0.9595 | 0.093423 | -0.006875 | 0.94032 | 0.12407 | -0.010928 | 0.92296 | 0.15259 | -0.015618 | 2 | 0.739 | 0.686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.745 | -0.745 | 1 | 1.189
12101 | 21 | 16.38 | 58805 | 0.724 | 0.17954 | 0.03 | 0.233 | 0.102 | 0.01 | 100 | 3.4462 | -0.09133 | 0.000924 | 0.0070176 | -2.0119e-05 | -0.00015082 | 0.25994 | 0.074843 | -0.00091895 | -0.0096756 | -3.0969e-05 | 0.00016487 | -3.0223 | 0.13455 | -0.0010034 | -0.015978 | 0.00023792 | -0.00017556 | 66.8974 | -2.0132 | 0.01588 | 0.10092 | 0.00035451 | -0.0023705 | -0.0072625 | 1.1134 | -0.13234 | 0.026242 | -0.00144 | 1.1191 | -0.13966 | 0.021968 | 0.0063475 | 1.1162 | -0.13862 | 0.016045 | 0.9595 | 0.093423 | -0.006875 | 0.94032 | 0.12407 | -0.010928 | 0.92296 | 0.15259 | -0.015618 | 2 | 0.739 | 0.686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.745 | -0.745 | 1 | 1.189
21405 | 14 | 11.9296 | 34895 | 0.744 | 0.24467 | 0.0321 | 0.294 | 0.12 | 0.0109 | 100 | 0.33897 | 0.00041807 | 0.00021371 | 0.0089003 | -2.5963e-05 | -0.0001473 | 4.678 | -0.073712 | 0.00028931 | 0.0064477 | -2.7952e-05 | -6.2571e-05 | 0.9275 | -0.00046154 | 3.96e-05 | -0.0068688 | 0.0002048 | -0.00019954 | 25.5462 | -0.65922 | 0.0051164 | -0.027638 | 0.00033263 | -0.00058485 | -7e-05 | 1.1695 | -0.21321 | 0.04377 | 0.00012 | 1.2018 | -0.26145 | 0.05955 | 7e-05 | 1.2314 | -0.30703 | 0.07557 | 0.85187 | 0.17007 | -0.02194 | 0.82723 | 0.20273 | -0.02996 | 0.8053 | 0.2327 | -0.038 | 1 | 1 | 1 | 8.2 | 3.48 | 33754 | 0.28764 | 0.48334 | -0.0018833 | 5.4506e-06 | 0.017815 | -1.6965e-06 | -6.4368e-05 | 1.3857 | 0.0056717 | 5.247e-05 | -0.028076 | 0.00026023 | -8.9704e-05 | 1 | 0 | 0 | 1
21406 | 14 | 11.9296 | 34895 | 0.744 | 0.24467 | 0.0321 | 0.294 | 0.12 | 0.0109 | 100 | 0.33897 | 0.00041807 | 0.00021371 | 0.0089003 | -2.5963e-05 | -0.0001473 | 4.678 | -0.073712 | 0.00028931 | 0.0064477 | -2.7952e-05 | -6.2571e-05 | 0.9275 | -0.00046154 | 3.96e-05 | -0.0068688 | 0.0002048 | -0.00019954 | 25.5462 | -0.65922 | 0.0051164 | -0.027638 | 0.00033263 | -0.00058485 | -7e-05 | 1.1695 | -0.21321 | 0.04377 | 0.00012 | 1.2018 | -0.26145 | 0.05955 | 7e-05 | 1.2314 | -0.30703 | 0.07557 | 0.85187 | 0.17007 | -0.02194 | 0.82723 | 0.20273 | -0.02996 | 0.8053 | 0.2327 | -0.038 | 1 | 1 | 1 | 8.2 | 3.48 | 33754 | 0.28764 | 0.5325 | -0.00049956 | -1.912e-06 | 0.0079586 | 0.00012731 | -4.3601e-05 | 0.86181 | 0.0084487 | 3.6449e-05 | -0.010183 | 6.86e-05 | -9.2633e-05 | 1 | 0 | 0 | 1
21407 | 14 | 11.9296 | 34895 | 0.744 | 0.24467 | 0.0321 | 0.294 | 0.12 | 0.0109 | 100 | 0.33897 | 0.00041807 | 0.00021371 | 0.0089003 | -2.5963e-05 | -0.0001473 | 4.678 | -0.073712 | 0.00028931 | 0.0064477 | -2.7952e-05 | -6.2571e-05 | 0.9275 | -0.00046154 | 3.96e-05 | -0.0068688 | 0.0002048 | -0.00019954 | 25.5462 | -0.65922 | 0.0051164 | -0.027638 | 0.00033263 | -0.00058485 | -7e-05 | 1.1695 | -0.21321 | 0.04377 | 0.00012 | 1.2018 | -0.26145 | 0.05955 | 7e-05 | 1.2314 | -0.30703 | 0.07557 | 0.85187 | 0.17007 | -0.02194 | 0.82723 | 0.20273 | -0.02996 | 0.8053 | 0.2327 | -0.038 | 1 | 1 | 1 | 8 | 3.39 | 33754 | 0.29507 | 0.5325 | -0.00049956 | -1.912e-06 | 0.0079586 | 0.00012731 | -4.3601e-05 | 0.86181 | 0.0084487 | 3.6449e-05 | -0.010183 | 6.86e-05 | -9.2633e-05 | 1 | 0 | 0 | 1
21408 | 14 | 11.1125 | 58310 | 0.717 | 0.27047 | 0.02795 | 0.294 | 0.0694 | 0.01 | 100 | 3.4906 | -0.091345 | 0.00095659 | 0.0062175 | -7.875e-06 | -0.00018605 | 2.9971 | 0.0018497 | -0.00038268 | -0.017138 | -1.2463e-05 | 0.00021013 | -3.4577 | 0.15512 | -0.0011438 | -0.021251 | 0.00029839 | -0.00023171 | 29.7842 | -0.96569 | 0.0078708 | 0.23115 | 0.00019408 | -0.0036332 | 0.00284 | 1.0607 | -0.06874 | 0.00523 | -0.00146 | 1.1032 | -0.1193 | 0.01755 | -0.00016 | 1.1224 | -0.14282 | 0.02058 | 0.88889 | 0.06952 | -0.00646 | 0.87243 | 0.09413 | -0.00752 | 0.85625 | 0.12115 | -0.01241 | 2 | 0.773 | 0.682 | 8.2 | 3.25 | 31641 | 0.30794 | 0.42851 | -0.00097813 | 5.0142e-15 | 0.015309 | 3.9018e-05 | -5.0381e-05 | 1.366 | 0.0034688 | 6.2209e-05 | -0.02346 | 0.00022502 | -9.3635e-05 | 1.745 | -0.745 | 1 | 1.189
21409 | 14 | 11.1125 | 58310 | 0.717 | 0.27047 | 0.02795 | 0.294 | 0.0694 | 0.01 | 100 | 3.4906 | -0.091345 | 0.00095659 | 0.0062175 | -7.875e-06 | -0.00018605 | 2.9971 | 0.0018497 | -0.00038268 | -0.017138 | -1.2463e-05 | 0.00021013 | -3.4577 | 0.15512 | -0.0011438 | -0.021251 | 0.00029839 | -0.00023171 | 29.7842 | -0.96569 | 0.0078708 | 0.23115 | 0.00019408 | -0.0036332 | 0.00284 | 1.0607 | -0.06874 | 0.00523 | -0.00146 | 1.1032 | -0.1193 | 0.01755 | -0.00016 | 1.1224 | -0.14282 | 0.02058 | 0.88889 | 0.06952 | -0.00646 | 0.87243 | 0.09413 | -0.00752 | 0.85625 | 0.12115 | -0.01241 | 2 | 0.773 | 0.682 | 8 | 3.17 | 31641 | 0.31585 | 0.42851 | -0.00097813 | 5.0142e-15 | 0.015309 | 3.9018e-05 | -5.0381e-05 | 1.366 | 0.0034688 | 6.2209e-05 | -0.02346 | 0.00022502 | -9.3635e-05 | 1.745 | -0.745 | 1 | 1.189
21501 | 15 | 12.7817 | 34895 | 0.744 | 0.23218 | 0.0321 | 0.251 | 0.12 | 0.0109 | 100 | 0.33897 | 0.00041807 | 0.00021371 | 0.0089003 | -2.5963e-05 | -0.0001473 | 4.678 | -0.073712 | 0.00028931 | 0.0064477 | -2.7952e-05 | -6.2571e-05 | 0.9275 | -0.00046154 | 3.96e-05 | -0.0068688 | 0.0002048 | -0.00019954 | 25.5462 | -0.65922 | 0.0051164 | -0.027638 | 0.00033263 | -0.00058485 | -7e-05 | 1.1695 | -0.21321 | 0.04377 | 0.00012 | 1.2018 | -0.26145 | 0.05955 | 7e-05 | 1.2314 | -0.30703 | 0.07557 | 0.85187 | 0.17007 | -0.02194 | 0.82723 | 0.20273 | -0.02996 | 0.8053 | 0.2327 | -0.038 | 1 | 1 | 1 | 8.7 | 3.68 | 33754 | 0.27157 | 0.48334 | -0.0018833 | 5.4506e-06 | 0.017815 | -1.6965e-06 | -6.4368e-05 | 1.3857 | 0.0056717 | 5.247e-05 | -0.028076 | 0.00026023 | -8.9704e-05 | 1 | 0 | 0 | 1
21506 | 15 | 12.7817 | 34895 | 0.744 | 0.23218 | 0.0321 | 0.251 | 0.12 | 0.0109 | 100 | 0.33897 | 0.00041807 | 0.00021371 | 0.0089003 | -2.5963e-05 | -0.0001473 | 4.678 | -0.073712 | 0.00028931 | 0.0064477 | -2.7952e-05 | -6.2571e-05 | 0.9275 | -0.00046154 | 3.96e-05 | -0.0068688 | 0.0002048 | -0.00019954 | 25.5462 | -0.65922 | 0.0051164 | -0.027638 | 0.00033263 | -0.00058485 | -7e-05 | 1.1695 | -0.21321 | 0.04377 | 0.00012 | 1.2018 | -0.26145 | 0.05955 | 7e-05 | 1.2314 | -0.30703 | 0.07557 | 0.85187 | 0.17007 | -0.02194 | 0.82723 | 0.20273 | -0.02996 | 0.8053 | 0.2327 | -0.038 | 1 | 1 | 1 | 8.7 | 3.68 | 33754 | 0.27157 | 0.5325 | -0.00049956 | -1.912e-06 | 0.0079586 | 0.00012731 | -4.3601e-05 | 0.86181 | 0.0084487 | 3.6449e-05 | -0.010183 | 6.86e-05 | -9.2633e-05 | 1 | 0 | 0 | 1
21507 | 15 | 12.7817 | 34895 | 0.744 | 0.22621 | 0.0321 | 0.294 | 0.12 | 0.0109 | 100 | 0.33897 | 0.00041807 | 0.00021371 | 0.0089003 | -2.5963e-05 | -0.0001473 | 4.678 | -0.073712 | 0.00028931 | 0.0064477 | -2.7952e-05 | -6.2571e-05 | 0.9275 | -0.00046154 | 3.96e-05 | -0.0068688 | 0.0002048 | -0.00019954 | 25.5462 | -0.65922 | 0.0051164 | -0.027638 | 0.00033263 | -0.00058485 | -7e-05 | 1.1695 | -0.21321 | 0.04377 | 0.00012 | 1.2018 | -0.26145 | 0.05955 | 7e-05 | 1.2314 | -0.30703 | 0.07557 | 0.85187 | 0.17007 | -0.02194 | 0.82723 | 0.20273 | -0.02996 | 0.8053 | 0.2327 | -0.038 | 1 | 1 | 1 | 8.2 | 3.48 | 33754 | 0.28764 | 0.5325 | -0.00049956 | -1.912e-06 | 0.0079586 | 0.00012731 | -4.3601e-05 | 0.86181 | 0.0084487 | 3.6449e-05 | -0.010183 | 6.86e-05 | -9.2633e-05 | 1 | 0 | 0 | 1
21508 | 15 | 11.9062 | 58310 | 0.717 | 0.25585 | 0.02795 | 0.251 | 0.0694 | 0.01 | 100 | 3.4906 | -0.091345 | 0.00095659 | 0.0062175 | -7.875e-06 | -0.00018605 | 2.9971 | 0.0018497 | -0.00038268 | -0.017138 | -1.2463e-05 | 0.00021013 | -3.4577 | 0.15512 | -0.0011438 | -0.021251 | 0.00029839 | -0.00023171 | 29.7842 | -0.96569 | 0.0078708 | 0.23115 | 0.00019408 | -0.0036332 | 0.00284 | 1.0607 | -0.06874 | 0.00523 | -0.00146 | 1.1032 | -0.1193 | 0.01755 | -0.00016 | 1.1224 | -0.14282 | 0.02058 | 0.88889 | 0.06952 | -0.00646 | 0.87243 | 0.09413 | -0.00752 | 0.85625 | 0.12115 | -0.01241 | 2 | 0.773 | 0.682 | 8.7 | 3.44 | 31641 | 0.29062 | 0.42851 | -0.00097813 | 5.0142e-15 | 0.015309 | 3.9018e-05 | -5.0381e-05 | 1.366 | 0.0034688 | 6.2209e-05 | -0.02346 | 0.00022502 | -9.3635e-05 | 1.745 | -0.745 | 1 | 1.189
21509 | 15 | 11.9062 | 58310 | 0.717 | 0.25585 | 0.02795 | 0.251 | 0.0694 | 0.01 | 100 | 3.4906 | -0.091345 | 0.00095659 | 0.0062175 | -7.875e-06 | -0.00018605 | 2.9971 | 0.0018497 | -0.00038268 | -0.017138 | -1.2463e-05 | 0.00021013 | -3.4577 | 0.15512 | -0.0011438 | -0.021251 | 0.00029839 | -0.00023171 | 29.7842 | -0.96569 | 0.0078708 | 0.23115 | 0.00019408 | -0.0036332 | 0.00284 | 1.0607 | -0.06874 | 0.00523 | -0.00146 | 1.1032 | -0.1193 | 0.01755 | -0.00016 | 1.1224 | -0.14282 | 0.02058 | 0.88889 | 0.06952 | -0.00646 | 0.87243 | 0.09413 | -0.00752 | 0.85625 | 0.12115 | -0.01241 | 2 | 0.773 | 0.682 | 8.2 | 3.24 | 31641 | 0.30877 | 0.42851 | -0.00097813 | 5.0142e-15 | 0.015309 | 3.9018e-05 | -5.0381e-05 | 1.366 | 0.0034688 | 6.2209e-05 | -0.02346 | 0.00022502 | -9.3635e-05 | 1.745 | -0.745 | 1 | 1.189
21604 | 16 | 12.48 | 58805 | 0.724 | 0.23814 | 0.03 | 0.271 | 0.102 | 0.01 | 100 | 3.4462 | -0.09133 | 0.000924 | 0.0070176 | -2.0119e-05 | -0.00015082 | 0.25994 | 0.074843 | -0.00091895 | -0.0096756 | -3.0969e-05 | 0.00016487 | -3.0223 | 0.13455 | -0.0010034 | -0.015978 | 0.00023792 | -0.00017556 | 66.8974 | -2.0132 | 0.01588 | 0.10092 | 0.00035451 | -0.0023705 | -0.0072625 | 1.1134 | -0.13234 | 0.026242 | -0.00144 | 1.1191 | -0.13966 | 0.021968 | 0.0063475 | 1.1162 | -0.13862 | 0.016045 | 0.9595 | 0.093423 | -0.006875 | 0.94032 | 0.12407 | -0.010928 | 0.92296 | 0.15259 | -0.015618 | 2 | 0.739 | 0.686 | 9 | 3.57 | 31641 | 0.2799 | 0.42851 | -0.00097813 | 5.0142e-15 | 0.015309 | 3.9018e-05 | -5.0381e-05 | 1.366 | 0.0034688 | 6.2209e-05 | -0.02346 | 0.00022502 | -9.3635e-05 | 1.745 | -0.745 | 1 | 1.189
21609 | 16 | 12.48 | 58805 | 0.724 | 0.23814 | 0.03 | 0.271 | 0.102 | 0.01 | 100 | 3.4462 | -0.09133 | 0.000924 | 0.0070176 | -2.0119e-05 | -0.00015082 | 0.25994 | 0.074843 | -0.00091895 | -0.0096756 | -3.0969e-05 | 0.00016487 | -3.0223 | 0.13455 | -0.0010034 | -0.015978 | 0.00023792 | -0.00017556 | 66.8974 | -2.0132 | 0.01588 | 0.10092 | 0.00035451 | -0.0023705 | -0.0072625 | 1.1134 | -0.13234 | 0.026242 | -0.00144 | 1.1191 | -0.13966 | 0.021968 | 0.0063475 | 1.1162 | -0.13862 | 0.016045 | 0.9595 | 0.093423 | -0.006875 | 0.94032 | 0.12407 | -0.010928 | 0.92296 | 0.15259 | -0.015618 | 2 | 0.739 | 0.686 | 8.5 | 3.37 | 31641 | 0.29685 | 0.42851 | -0.00097813 | 5.0142e-15 | 0.015309 | 3.9018e-05 | -5.0381e-05 | 1.366 | 0.0034688 | 6.2209e-05 | -0.02346 | 0.00022502 | -9.3635e-05 | 1.745 | -0.745 | 1 | 1.189
21704 | 17 | 13.26 | 58805 | 0.724 | 0.2225 | 0.03 | 0.271 | 0.102 | 0.01 | 100 | 3.4462 | -0.09133 | 0.000924 | 0.0070176 | -2.0119e-05 | -0.00015082 | 0.25994 | 0.074843 | -0.00091895 | -0.0096756 | -3.0969e-05 | 0.00016487 | -3.0223 | 0.13455 | -0.0010034 | -0.015978 | 0.00023792 | -0.00017556 | 66.8974 | -2.0132 | 0.01588 | 0.10092 | 0.00035451 | -0.0023705 | -0.0072625 | 1.1134 | -0.13234 | 0.026242 | -0.00144 | 1.1191 | -0.13966 | 0.021968 | 0.0063475 | 1.1162 | -0.13862 | 0.016045 | 0.9595 | 0.093423 | -0.006875 | 0.94032 | 0.12407 | -0.010928 | 0.92296 | 0.15259 | -0.015618 | 2 | 0.739 | 0.686 | 9.4 | 3.74 | 31641 | 0.26765 | 0.42851 | -0.00097813 | 5.0142e-15 | 0.015309 | 3.9018e-05 | -5.0381e-05 | 1.366 | 0.0034688 | 6.2209e-05 | -0.02346 | 0.00022502 | -9.3635e-05 | 1.745 | -0.745 | 1 | 1.189
21709 | 17 | 13.26 | 58805 | 0.724 | 0.2225 | 0.03 | 0.271 | 0.102 | 0.01 | 100 | 3.4462 | -0.09133 | 0.000924 | 0.0070176 | -2.0119e-05 | -0.00015082 | 0.25994 | 0.074843 | -0.00091895 | -0.0096756 | -3.0969e-05 | 0.00016487 | -3.0223 | 0.13455 | -0.0010034 | -0.015978 | 0.00023792 | -0.00017556 | 66.8974 | -2.0132 | 0.01588 | 0.10092 | 0.00035451 | -0.0023705 | -0.0072625 | 1.1134 | -0.13234 | 0.026242 | -0.00144 | 1.1191 | -0.13966 | 0.021968 | 0.0063475 | 1.1162 | -0.13862 | 0.016045 | 0.9595 | 0.093423 | -0.006875 | 0.94032 | 0.12407 | -0.010928 | 0.92296 | 0.15259 | -0.015618 | 2 | 0.739 | 0.686 | 9 | 3.57 | 31641 | 0.2799 | 0.42851 | -0.00097813 | 5.0142e-15 | 0.015309 | 3.9018e-05 | -5.0381e-05 | 1.366 | 0.0034688 | 6.2209e-05 | -0.02346 | 0.00022502 | -9.3635e-05 | 1.745 | -0.745 | 1 | 1.189
21802 | 18 | 14.04 | 58805 | 0.724 | 0.2086 | 0.03 | 0.271 | 0.102 | 0.01 | 100 | 3.4462 | -0.09133 | 0.000924 | 0.0070176 | -2.0119e-05 | -0.00015082 | 0.25994 | 0.074843 | -0.00091895 | -0.0096756 | -3.0969e-05 | 0.00016487 | -3.0223 | 0.13455 | -0.0010034 | -0.015978 | 0.00023792 | -0.00017556 | 66.8974 | -2.0132 | 0.01588 | 0.10092 | 0.00035451 | -0.0023705 | -0.0072625 | 1.1134 | -0.13234 | 0.026242 | -0.00144 | 1.1191 | -0.13966 | 0.021968 | 0.0063475 | 1.1162 | -0.13862 | 0.016045 | 0.9595 | 0.093423 | -0.006875 | 0.94032 | 0.12407 | -0.010928 | 0.92296 | 0.15259 | -0.015618 | 2 | 0.739 | 0.686 | 9.7 | 3.86 | 31641 | 0.25912 | 0.42851 | -0.00097813 | 5.0142e-15 | 0.015309 | 3.9018e-05 | -5.0381e-05 | 1.366 | 0.0034688 | 6.2209e-05 | -0.02346 | 0.00022502 | -9.3635e-05 | 1.745 | -0.745 | 1 | 1.189
21006 | 10 | 8.5211 | 34895 | 0.744 | 0.34453 | 0.0321 | 0.365 | 0.12 | 0.0109 | 100 | 0.33897 | 0.00041807 | 0.00021371 | 0.0089003 | -2.5963e-05 | -0.0001473 | 4.678 | -0.073712 | 0.00028931 | 0.0064477 | -2.7952e-05 | -6.2571e-05 | 0.9275 | -0.00046154 | 3.96e-05 | -0.0068688 | 0.0002048 | -0.00019954 | 25.5462 | -0.65922 | 0.0051164 | -0.027638 | 0.00033263 | -0.00058485 | -7e-05 | 1.1695 | -0.21321 | 0.04377 | 0.00012 | 1.2018 | -0.26145 | 0.05955 | 7e-05 | 1.2314 | -0.30703 | 0.07557 | 0.85187 | 0.17007 | -0.02194 | 0.82723 | 0.20273 | -0.02996 | 0.8053 | 0.2327 | -0.038 | 1 | 1 | 1 | 7.1 | 3.01 | 33754 | 0.33217 | 0.5325 | -0.00049956 | -1.912e-06 | 0.0079586 | 0.00012731 | -4.3601e-05 | 0.86181 | 0.0084487 | 3.6449e-05 | -0.010183 | 6.86e-05 | -9.2633e-05 | 1 | 0 | 0 | 1
21306 | 13 | 11.0775 | 34895 | 0.744 | 0.25823 | 0.0321 | 0.348 | 0.12 | 0.0109 | 100 | 0.33897 | 0.00041807 | 0.00021371 | 0.0089003 | -2.5963e-05 | -0.0001473 | 4.678 | -0.073712 | 0.00028931 | 0.0064477 | -2.7952e-05 | -6.2571e-05 | 0.9275 | -0.00046154 | 3.96e-05 | -0.0068688 | 0.0002048 | -0.00019954 | 25.5462 | -0.65922 | 0.0051164 | -0.027638 | 0.00033263 | -0.00058485 | -7e-05 | 1.1695 | -0.21321 | 0.04377 | 0.00012 | 1.2018 | -0.26145 | 0.05955 | 7e-05 | 1.2314 | -0.30703 | 0.07557 | 0.85187 | 0.17007 | -0.02194 | 0.82723 | 0.20273 | -0.02996 | 0.8053 | 0.2327 | -0.038 | 1 | 1 | 1 | 8.2 | 3.49 | 33754 | 0.28642 | 0.5325 | -0.00049956 | -1.912e-06 | 0.0079586 | 0.00012731 | -4.3601e-05 | 0.86181 | 0.0084487 | 3.6449e-05 | -0.010183 | 6.86e-05 | -9.2633e-05 | 1 | 0 | 0 | 1
Data Key:
Dep Col(s) | Usage
1 | SEER
2 | Unit's rated EER.
3 | Actual unit total capacity. Value is for reference only and not used in simulations.
Data used as DOE-2 simulation inputs. Fields are used as follows:
4 | Ratio of sensible to total capacity (sensible heat ratio) is used to establish COOL-SH-CAP from design cooling load.
COOL-SH-CAP = COOLING-CAPACITY * Sen/Total
5 | Value is DOE-2 keyword COOLING-EIR
6 | cfm/Btuh is used to calculate design air flow as SUPPLY-CFM = cfm/Btuh * unit design capacity.
7 | Fan W/cfm is used to set the fan power input and fan Delta T via the following keywords:
SUPPLY-KW = (Fan W/cfm)/1,000
SUPPLY-DELTA-T = (Fan W/cfm)* 3.160
8 | Coil-BF is the design coil by-pass factor. The DOE-2 keyword COIL-BF = Coil-BF
9 | Crkn/Tot kW is used to set the keyword CRANKCASE-HEAT, and is the ratio of crankcase load heat to the design compressor load.
10 | Crnk Off is the temperature above which crankcase heat is deactivated and is the value used for the keyword CRANKCASE-MAX-T.
11 - 16 | The coefficients for the bi-quadratic total capacity off-design curve set by the keyword COOL-CAP-FT
17 - 22 | The coefficients for the bi-quadratic sensible capacity off-design curve set by the keyword COOL-SH-FT
23 - 28 | The coefficients for the bi-quadratic EIR off-design curve set by the keyword COOL-EIR-FT
29 - 34 | The coefficients for the bi-quadratic coil by-pass factor off-design curve set by the keyword COIL-BF-FT
For this curve set, the following should be set: OUTPUT-MAX = 0.4/CoilBF, where the Coil-BF is specified in column 8.
35 - 38 | The coefficients for the qubic equation that determines the EIR as a function of the part-load ratio for houses in temperate climate zones
39 - 42 | The coefficients for the qubic equation that determines the EIR as a function of the part-load ratio for houses in moderate climate zones
43 - 46 | The coefficients for the qubic equation that determines the EIR as a function of the part-load ratio for houses in hot climate zones
47 - 49 | The coefficients for the quadratic equation of the C-LOSS curve for houses in temperate climate zones
50 - 52 | The coefficients for the quadratic equation of the C-LOSS curve for houses in moderate climate zones
53 - 55 | The coefficients for the quadratic equation of the C-LOSS curve for houses in hot climate zones
56 | Number of compressor speeds (1 or 2). This is used as a flag to notify simulation when 2-speed equipment is to be simulated
57 | Low speed cfm ratio for 2-speed units (ratio of low speed to high speed cfm) used by keyword MIN-FLOW-RATIO
58 | Low speed capacity ratio for 2-speed units (ratio of lowspeed to high speed cooling capacity) used by keyword COOL-STAGES
Columns for heat pumps only. Colums BL and BN are descriptive only and not used in simulations
59 | For heat pumps only - rated HSPF
60 | For heat pumps only - rated COP at 47 outdoor temperature. Keyword HEATING-EIR = 1/(COP at 47 ODB)
61 | For heat pumps only - Actual unit rated heating capacity. Value is for reference only and not used in simulations.
62 | Heating EIR from manufacturers expanded ratings chart. Used only as a check with the rated COP at 47 ODB.
63 - 68 | For heat pumps only - the coefficients of the bi-quadratic heating capacity off-design curve set by keyword HEAT-CAP-FT
69 - 74 | For heat pumps only - the coefficients of the bi-quadratic heating EIR off-design curve set by keyword HEAT-EIR-FT
75 - 78 | The coefficients C0 & C1 and the Min and Max values of the linear curve-fit command assigned to keyword COIL-BF-FFLOW

## Packaged AC Selected Perf Maps
Packaged AC Selected Performance Maps
This table lists the complete performance data sets used for the packaged AC measures for the DEER2015 update.
Indep. | Dependents
1 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58
Equip ID | Tier | Nom Cap | Heat Source | Rated SEER/EER | Calc EER | Tot Cap | Sen/Total | EIR | cfm/Btuh | Fan W/cfm | CF W/Bth | Coil-BF | Crnk/Tot kW | Crnk Off | Total Capacity Curve Fit Coefficients | [5 empty] | Sensible Capacity Curve Fit Coefficients | [5 empty] | EIR Curve Fit Coefficients | [5 empty] | Coil-BF Curve Fit Coefficients | [5 empty] | EIR_PLR Curve Fit Coefficients |  |  |  | CLoss Curve Fit Coefficients |  |  |  | C_Loss Min, Max |  | Cmp Spd | Low Speed Ratios |  | Tot Cap_f(cfm) |  | Sen Cap_f(cfm) |  |  | SF Exp | SF_Mult
SEER Rated A/C Units - Up to 5 tons
30007 | 0 | 2 | 1 | 10 | 9.4981 | 25800 | 0.6975 | 0.2971 | 0.03103 | 0.4325 | 0 | 0.2143 | 0 | 55 | -0.35078 | 0.032251 | -0.000154 | -0.0027733 | -3.8833e-05 | 7.78e-05 | 2.8739 | -0.002921 | -0.000361 | -0.0074043 | -1.8583e-05 | 0.0001278 | 1.3045 | -0.028713 | 0.000312 | 0.011817 | 9.675e-05 | -0.0002792 | 8.5771 | -0.34275 | 0.0036658 | 0.081184 | 5.5738e-05 | -0.0014586 | 2.141e-05 | 1.1383 | -0.16866 | 0.030369 | 0.8764 | 0.1407 | -0.020849 | 0.0037539 | 0.85 | 1 | 1 | 1 | 1 | 0.80746 | 0.19254 | 0.34576 | 0.83221 | -0.17797 | 0.13849 | 1.2289
30103 | 1 | 5 | 1 | 13 | 11.0559 | 63800 | 0.732 | 0.2557 | 0.03135 | 0.3785 | 0 | 0.1304 | 0 | 55 | -0.94186 | 0.053996 | -0.00032 | -0.0064383 | -1.6095e-05 | 8.13e-05 | 0.74101 | 0.066734 | -0.000942 | -0.010653 | -2.5048e-05 | 0.0001971 | 2.0296 | -0.064611 | 0.000656 | 0.020324 | 0.00013157 | -0.0004342 | 47.1113 | -1.5077 | 0.013015 | 0.079071 | 0.0003567 | -0.002239 | 3.1428e-08 | 1.0172 | -0.017804 | 0.00057405 | 0.98306 | 0.017236 | -0.00030168 | 9.727e-06 | 0.979 | 1 | 1 | 1 | 1 | 0.87282 | 0.12718 | 0.36331 | 0.79657 | -0.15989 | 2.5824 | 1.2607
30203 | 2 | 5 | 1 | 14 | 12.0391 | 60300 | 0.6932 | 0.2456 | 0.02819 | 0.294 | 0 | 0.1482 | 0 | 55 | 0.27139 | 0.0042667 | 0.00015433 | 0.0058883 | -2.406e-05 | -9.3057e-05 | 2.8637 | -0.008743 | -0.000264 | -0.0024261 | -2.0054e-05 | 5.0057e-05 | 0.67902 | -0.0018999 | 9.5333e-05 | 0.00085893 | 0.0001854 | -0.00027251 | 15.5043 | -0.47623 | 0.0042994 | 0.030314 | 0.00018497 | -0.0010127 | 7.1271e-06 | 1.0979 | -0.11402 | 0.016141 | 0.91 | 0.098808 | -0.010262 | 0.0014527 | 0.89 | 1 | 1 | 1 | 1 | 0.83381 | 0.16619 | 1.2847 | -0.99912 | 0.71443 | 2.1702 | 1.3371
30301 | 3 | 5 | 1 | 15 | 12.9 | 60300 | 0.6932 | 0.23404 | 0.02819 | 0.251 | 0 | 0.1482 | 0 | 55 | 0.27139 | 0.0042667 | 0.00015433 | 0.0058883 | -2.406e-05 | -9.3057e-05 | 2.8637 | -0.008743 | -0.000264 | -0.0024261 | -2.0054e-05 | 5.0057e-05 | 0.67902 | -0.0018999 | 9.5333e-05 | 0.00085893 | 0.0001854 | -0.00027251 | 15.5043 | -0.47623 | 0.0042994 | 0.030314 | 0.00018497 | -0.0010127 | 7.1271e-06 | 1.0979 | -0.11402 | 0.016141 | 0.91 | 0.098808 | -0.010262 | 0.0014527 | 0.89 | 1 | 1 | 1 | 1 | 0.83381 | 0.16619 | 1.2847 | -0.99912 | 0.71443 | 2.1702 | 1.364
EER Rated Units 65 to 110 kBtuh
31001 | 0 | 15 | 1 | 11 | 10.64 | 184140 | 0.663 | 0.27299 | 0.0265 | 0.4 | 0 | 0.114 | 0.02 | 100 | 1.9543 | -0.036502 | 0.00035617 | 0.0062696 | -4.1442e-05 | -5.1697e-05 | 0.24557 | 0.090507 | -0.0011888 | -0.010263 | -4.2723e-05 | 0.00021802 | 0.13023 | 0.036993 | -0.00027783 | -0.020132 | 0.0002154 | -6.1743e-05 | 57.0342 | -1.7701 | 0.014453 | 0.013433 | 0.00029803 | -0.00098747 | 0.01844 | 1.1476 | -0.20833 | 0.04227 | 0.88228 | 0.21053 | -0.04389 | 0.0098 | 0.8323 | 1.1087 | 2 | 0.5 | 0.5 | 0.87855 | 0.12145 | -1.5914 | 4.2054 | -1.614 | 2.2325 | 0
31101 | 1 | 15 | 1 | 11.5 | 11.12 | 184140 | 0.663 | 0.25964 | 0.0265 | 0.4 | 0 | 0.114 | 0.02 | 100 | 1.9543 | -0.036502 | 0.00035617 | 0.0062696 | -4.1442e-05 | -5.1697e-05 | 0.24557 | 0.090507 | -0.0011888 | -0.010263 | -4.2723e-05 | 0.00021802 | 0.13023 | 0.036993 | -0.00027783 | -0.020132 | 0.0002154 | -6.1743e-05 | 57.0342 | -1.7701 | 0.014453 | 0.013433 | 0.00029803 | -0.00098747 | 0.01844 | 1.1476 | -0.20833 | 0.04227 | 0.88228 | 0.21053 | -0.04389 | 0.0098 | 0.8323 | 1.1087 | 2 | 0.5 | 0.5 | 0.87855 | 0.12145 | -1.5914 | 4.2054 | -1.614 | 2.2325 | 0
31201 | 2 | 15 | 1 | 12 | 11.61 | 184140 | 0.663 | 0.24716 | 0.0265 | 0.4 | 0 | 0.114 | 0.02 | 100 | 1.9543 | -0.036502 | 0.00035617 | 0.0062696 | -4.1442e-05 | -5.1697e-05 | 0.24557 | 0.090507 | -0.0011888 | -0.010263 | -4.2723e-05 | 0.00021802 | 0.13023 | 0.036993 | -0.00027783 | -0.020132 | 0.0002154 | -6.1743e-05 | 57.0342 | -1.7701 | 0.014453 | 0.013433 | 0.00029803 | -0.00098747 | 0.01844 | 1.1476 | -0.20833 | 0.04227 | 0.88228 | 0.21053 | -0.04389 | 0.0098 | 0.8323 | 1.1087 | 2 | 0.5 | 0.5 | 0.87855 | 0.12145 | -1.5914 | 4.2054 | -1.614 | 2.2325 | 0
31301 | 3 | 15 | 1 | 13 | 12.57 | 184140 | 0.663 | 0.22552 | 0.0265 | 0.4 | 0 | 0.114 | 0.02 | 100 | 1.9543 | -0.036502 | 0.00035617 | 0.0062696 | -4.1442e-05 | -5.1697e-05 | 0.24557 | 0.090507 | -0.0011888 | -0.010263 | -4.2723e-05 | 0.00021802 | 0.13023 | 0.036993 | -0.00027783 | -0.020132 | 0.0002154 | -6.1743e-05 | 57.0342 | -1.7701 | 0.014453 | 0.013433 | 0.00029803 | -0.00098747 | 0.01844 | 1.1476 | -0.20833 | 0.04227 | 0.88228 | 0.21053 | -0.04389 | 0.0098 | 0.8323 | 1.1087 | 2 | 0.5 | 0.5 | 0.87855 | 0.12145 | -1.5914 | 4.2054 | -1.614 | 2.2325 | 0
EER Rated Units 110 to 135 kBtuh
32001 | 0 | 15 | 1 | 11 | 10.64 | 184140 | 0.663 | 0.27299 | 0.0265 | 0.4 | 0 | 0.114 | 0.02 | 100 | 1.9543 | -0.036502 | 0.00035617 | 0.0062696 | -4.1442e-05 | -5.1697e-05 | 0.24557 | 0.090507 | -0.0011888 | -0.010263 | -4.2723e-05 | 0.00021802 | 0.13023 | 0.036993 | -0.00027783 | -0.020132 | 0.0002154 | -6.1743e-05 | 57.0342 | -1.7701 | 0.014453 | 0.013433 | 0.00029803 | -0.00098747 | 0.01844 | 1.1476 | -0.20833 | 0.04227 | 0.88228 | 0.21053 | -0.04389 | 0.0098 | 0.8323 | 1.1087 | 2 | 0.5 | 0.5 | 0.87855 | 0.12145 | -1.5914 | 4.2054 | -1.614 | 2.2325 | 0
32101 | 1 | 15 | 1 | 11.5 | 11.12 | 184140 | 0.663 | 0.25964 | 0.0265 | 0.4 | 0 | 0.114 | 0.02 | 100 | 1.9543 | -0.036502 | 0.00035617 | 0.0062696 | -4.1442e-05 | -5.1697e-05 | 0.24557 | 0.090507 | -0.0011888 | -0.010263 | -4.2723e-05 | 0.00021802 | 0.13023 | 0.036993 | -0.00027783 | -0.020132 | 0.0002154 | -6.1743e-05 | 57.0342 | -1.7701 | 0.014453 | 0.013433 | 0.00029803 | -0.00098747 | 0.01844 | 1.1476 | -0.20833 | 0.04227 | 0.88228 | 0.21053 | -0.04389 | 0.0098 | 0.8323 | 1.1087 | 2 | 0.5 | 0.5 | 0.87855 | 0.12145 | -1.5914 | 4.2054 | -1.614 | 2.2325 | 0
32201 | 2 | 15 | 1 | 12 | 11.61 | 184140 | 0.663 | 0.24716 | 0.0265 | 0.4 | 0 | 0.114 | 0.02 | 100 | 1.9543 | -0.036502 | 0.00035617 | 0.0062696 | -4.1442e-05 | -5.1697e-05 | 0.24557 | 0.090507 | -0.0011888 | -0.010263 | -4.2723e-05 | 0.00021802 | 0.13023 | 0.036993 | -0.00027783 | -0.020132 | 0.0002154 | -6.1743e-05 | 57.0342 | -1.7701 | 0.014453 | 0.013433 | 0.00029803 | -0.00098747 | 0.01844 | 1.1476 | -0.20833 | 0.04227 | 0.88228 | 0.21053 | -0.04389 | 0.0098 | 0.8323 | 1.1087 | 2 | 0.5 | 0.5 | 0.87855 | 0.12145 | -1.5914 | 4.2054 | -1.614 | 2.2325 | 0
32301 | 3 | 15 | 1 | 12.5 | 12.09 | 184140 | 0.663 | 0.23591 | 0.0265 | 0.4 | 0 | 0.114 | 0.02 | 100 | 1.9543 | -0.036502 | 0.00035617 | 0.0062696 | -4.1442e-05 | -5.1697e-05 | 0.24557 | 0.090507 | -0.0011888 | -0.010263 | -4.2723e-05 | 0.00021802 | 0.13023 | 0.036993 | -0.00027783 | -0.020132 | 0.0002154 | -6.1743e-05 | 57.0342 | -1.7701 | 0.014453 | 0.013433 | 0.00029803 | -0.00098747 | 0.01844 | 1.1476 | -0.20833 | 0.04227 | 0.88228 | 0.21053 | -0.04389 | 0.0098 | 0.8323 | 1.1087 | 2 | 0.5 | 0.5 | 0.87855 | 0.12145 | -1.5914 | 4.2054 | -1.614 | 2.2325 | 0
EER Rated Units 135 to 240 kBtuh
33001 | 0 | 15 | 1 | 10.8 | 10.53 | 179280 | 0.696 | 0.27372 | 0.0272 | 0.41 | 0 | 0.099 | 0.02 | 100 | 3.5046 | -0.080819 | 0.00080267 | 0.00036515 | 8.2232e-06 | -0.00012597 | -4.8754 | 0.25179 | -0.0023868 | -0.017726 | -1.2759e-05 | 0.00023861 | -2.0067 | 0.084379 | -0.0006675 | -0.0032537 | 0.00012652 | -7.588e-05 | 172.1845 | -5.5221 | 0.045803 | 0.14324 | 0.00065847 | -0.0041417 | 0.01843 | 1.1476 | -0.20833 | 0.04227 | 0.85236 | 0.20333 | -0.04226 | 0.00938 | 0.8024 | 1.0728 | 2 | 0.5 | 0.5 | 0.84615 | 0.15385 | 0.19661 | 1.1131 | -0.30974 | 2.9094 | 0
33101 | 1 | 15 | 1 | 11.5 | 11.21 | 179280 | 0.696 | 0.25481 | 0.0272 | 0.41 | 0 | 0.099 | 0.02 | 100 | 3.5046 | -0.080819 | 0.00080267 | 0.00036515 | 8.2232e-06 | -0.00012597 | -4.8754 | 0.25179 | -0.0023868 | -0.017726 | -1.2759e-05 | 0.00023861 | -2.0067 | 0.084379 | -0.0006675 | -0.0032537 | 0.00012652 | -7.588e-05 | 172.1845 | -5.5221 | 0.045803 | 0.14324 | 0.00065847 | -0.0041417 | 0.01843 | 1.1476 | -0.20833 | 0.04227 | 0.85236 | 0.20333 | -0.04226 | 0.00938 | 0.8024 | 1.0728 | 2 | 0.5 | 0.5 | 0.84615 | 0.15385 | 0.19661 | 1.1131 | -0.30974 | 2.9094 | 0
33201 | 2 | 15 | 1 | 12 | 11.69 | 179280 | 0.696 | 0.24278 | 0.0272 | 0.41 | 0 | 0.099 | 0.02 | 100 | 3.5046 | -0.080819 | 0.00080267 | 0.00036515 | 8.2232e-06 | -0.00012597 | -4.8754 | 0.25179 | -0.0023868 | -0.017726 | -1.2759e-05 | 0.00023861 | -2.0067 | 0.084379 | -0.0006675 | -0.0032537 | 0.00012652 | -7.588e-05 | 172.1845 | -5.5221 | 0.045803 | 0.14324 | 0.00065847 | -0.0041417 | 0.01843 | 1.1476 | -0.20833 | 0.04227 | 0.85236 | 0.20333 | -0.04226 | 0.00938 | 0.8024 | 1.0728 | 2 | 0.5 | 0.5 | 0.84615 | 0.15385 | 0.19661 | 1.1131 | -0.30974 | 2.9094 | 0
33301 | 3 | 15 | 1 | 12.5 | 12.18 | 179280 | 0.696 | 0.23149 | 0.0272 | 0.41 | 0 | 0.099 | 0.02 | 100 | 3.5046 | -0.080819 | 0.00080267 | 0.00036515 | 8.2232e-06 | -0.00012597 | -4.8754 | 0.25179 | -0.0023868 | -0.017726 | -1.2759e-05 | 0.00023861 | -2.0067 | 0.084379 | -0.0006675 | -0.0032537 | 0.00012652 | -7.588e-05 | 172.1845 | -5.5221 | 0.045803 | 0.14324 | 0.00065847 | -0.0041417 | 0.01843 | 1.1476 | -0.20833 | 0.04227 | 0.85236 | 0.20333 | -0.04226 | 0.00938 | 0.8024 | 1.0728 | 2 | 0.5 | 0.5 | 0.84615 | 0.15385 | 0.19661 | 1.1131 | -0.30974 | 2.9094 | 0
EER Rated PVAV Units 240 to 760 kBtuh
34001 | 0 | 40 | 1 | 10 | 9.17 | 485760 | 0.708 | 0.28182 | 0.0268 | 0.72 | 0 | 0.125 | 0.01 | 100 | 1.4771 | -0.028736 | 0.0003802 | 0.0022055 | -1.3982e-05 | -5.37e-05 | 1.5063 | 0.04313 | -0.0007206 | -0.012658 | -9.9821e-06 | 0.00017774 | -0.55587 | 0.032991 | -0.0001478 | 0.0059216 | 0.00016175 | -0.00031632 | 36.5605 | -1.3553 | 0.010827 | 0.1936 | -0.00068253 | -0.00087867 | 0.12412 | 0.37624 | 1.2935 | -0.79382 | 0 | 1 | 0 | 0 | 0.1 | 1 | 1 | 0.17 | 0.24 | 0.78306 | 0.21694 | 0.42236 | 0.68944 | -0.1118 | 2.4182 | 0
34101 | 1 | 40 | 1 | 10.8 | 9.9 | 485760 | 0.708 | 0.25619 | 0.0268 | 0.72 | 0 | 0.125 | 0.01 | 100 | 1.4771 | -0.028736 | 0.0003802 | 0.0022055 | -1.3982e-05 | -5.37e-05 | 1.5063 | 0.04313 | -0.0007206 | -0.012658 | -9.9821e-06 | 0.00017774 | -0.55587 | 0.032991 | -0.0001478 | 0.0059216 | 0.00016175 | -0.00031632 | 36.5605 | -1.3553 | 0.010827 | 0.1936 | -0.00068253 | -0.00087867 | 0.12412 | 0.37624 | 1.2935 | -0.79382 | 0 | 1 | 0 | 0 | 0.1 | 1 | 1 | 0.17 | 0.24 | 0.78306 | 0.21694 | 0.42236 | 0.68944 | -0.1118 | 2.4182 | 0
34201 | 2 | 40 | 1 | 11.5 | 10.54 | 485760 | 0.708 | 0.23663 | 0.0268 | 0.72 | 0 | 0.125 | 0.01 | 100 | 1.4771 | -0.028736 | 0.0003802 | 0.0022055 | -1.3982e-05 | -5.37e-05 | 1.5063 | 0.04313 | -0.0007206 | -0.012658 | -9.9821e-06 | 0.00017774 | -0.55587 | 0.032991 | -0.0001478 | 0.0059216 | 0.00016175 | -0.00031632 | 36.5605 | -1.3553 | 0.010827 | 0.1936 | -0.00068253 | -0.00087867 | 0.12412 | 0.37624 | 1.2935 | -0.79382 | 0 | 1 | 0 | 0 | 0.1 | 1 | 1 | 0.17 | 0.24 | 0.78306 | 0.21694 | 0.42236 | 0.68944 | -0.1118 | 2.4182 | 0
34301 | 3 | 40 | 1 | 12.5 | 11.46 | 485760 | 0.708 | 0.21235 | 0.0268 | 0.72 | 0 | 0.125 | 0.01 | 100 | 1.4771 | -0.028736 | 0.0003802 | 0.0022055 | -1.3982e-05 | -5.37e-05 | 1.5063 | 0.04313 | -0.0007206 | -0.012658 | -9.9821e-06 | 0.00017774 | -0.55587 | 0.032991 | -0.0001478 | 0.0059216 | 0.00016175 | -0.00031632 | 36.5605 | -1.3553 | 0.010827 | 0.1936 | -0.00068253 | -0.00087867 | 0.12412 | 0.37624 | 1.2935 | -0.79382 | 0 | 1 | 0 | 0 | 0.1 | 1 | 1 | 0.17 | 0.24 | 0.78306 | 0.21694 | 0.42236 | 0.68944 | -0.1118 | 2.4182 | 0
EER Rated PVAV Units 760 to 800 kBtuh
35001 | 0 | 65 | 1 | 9.7 | 8.89 | 789360 | 0.708 | 0.29277 | 0.0268 | 0.72 | 0 | 0.125 | 0.01 | 100 | 1.4771 | -0.028736 | 0.0003802 | 0.0022055 | -1.3982e-05 | -5.37e-05 | 1.5063 | 0.04313 | -0.0007206 | -0.012658 | -9.9821e-06 | 0.00017774 | -0.55587 | 0.032991 | -0.0001478 | 0.0059216 | 0.00016175 | -0.00031632 | 36.5605 | -1.3553 | 0.010827 | 0.1936 | -0.00068253 | -0.00087867 | 0.12412 | 0.37624 | 1.2935 | -0.79382 | 0 | 1 | 0 | 0 | 0.1 | 1 | 1 | 0.17 | 0.24 | 0.78306 | 0.21694 | 0.42236 | 0.68944 | -0.1118 | 2.4182 | 0
35101 | 1 | 65 | 1 | 10.2 | 9.35 | 789360 | 0.708 | 0.27513 | 0.0268 | 0.72 | 0 | 0.125 | 0.01 | 100 | 1.4771 | -0.028736 | 0.0003802 | 0.0022055 | -1.3982e-05 | -5.37e-05 | 1.5063 | 0.04313 | -0.0007206 | -0.012658 | -9.9821e-06 | 0.00017774 | -0.55587 | 0.032991 | -0.0001478 | 0.0059216 | 0.00016175 | -0.00031632 | 36.5605 | -1.3553 | 0.010827 | 0.1936 | -0.00068253 | -0.00087867 | 0.12412 | 0.37624 | 1.2935 | -0.79382 | 0 | 1 | 0 | 0 | 0.1 | 1 | 1 | 0.17 | 0.24 | 0.78306 | 0.21694 | 0.42236 | 0.68944 | -0.1118 | 2.4182 | 0
35201 | 2 | 65 | 1 | 11 | 10.08 | 789360 | 0.708 | 0.25044 | 0.0268 | 0.72 | 0 | 0.125 | 0.01 | 100 | 1.4771 | -0.028736 | 0.0003802 | 0.0022055 | -1.3982e-05 | -5.37e-05 | 1.5063 | 0.04313 | -0.0007206 | -0.012658 | -9.9821e-06 | 0.00017774 | -0.55587 | 0.032991 | -0.0001478 | 0.0059216 | 0.00016175 | -0.00031632 | 36.5605 | -1.3553 | 0.010827 | 0.1936 | -0.00068253 | -0.00087867 | 0.12412 | 0.37624 | 1.2935 | -0.79382 | 0 | 1 | 0 | 0 | 0.1 | 1 | 1 | 0.17 | 0.24 | 0.78306 | 0.21694 | 0.42236 | 0.68944 | -0.1118 | 2.4182 | 0
35301 | 3 | 65 | 1 | 12 | 11 | 789360 | 0.708 | 0.22398 | 0.0268 | 0.72 | 0 | 0.125 | 0.01 | 100 | 1.4771 | -0.028736 | 0.0003802 | 0.0022055 | -1.3982e-05 | -5.37e-05 | 1.5063 | 0.04313 | -0.0007206 | -0.012658 | -9.9821e-06 | 0.00017774 | -0.55587 | 0.032991 | -0.0001478 | 0.0059216 | 0.00016175 | -0.00031632 | 36.5605 | -1.3553 | 0.010827 | 0.1936 | -0.00068253 | -0.00087867 | 0.12412 | 0.37624 | 1.2935 | -0.79382 | 0 | 1 | 0 | 0 | 0.1 | 1 | 1 | 0.17 | 0.24 | 0.78306 | 0.21694 | 0.42236 | 0.68944 | -0.1118 | 2.4182 | 0
EER Rated 2 Speed Units 240 to 760 kBtuh
34002 | 0 | 40 | 1 | 9.8 | 9.43 | 487200 | 0.705 | 0.28622 | 0.0267 | 0.61 | 0 | 0.123 | 0.01 | 100 | 2.2459 | -0.045908 | 0.00051641 | 0.0026469 | -9.5833e-06 | -0.00010262 | 3.84 | -0.027141 | -0.00014531 | -0.0076466 | -8.9167e-06 | 6.875e-05 | -0.79627 | 0.056948 | -0.00035859 | -0.0098866 | 0.000209 | -0.00021313 | 58.1396 | -1.7385 | 0.0127 | 0.0065284 | 8.6136e-05 | 0.0001466 | 2.6306 | -9.5 | 14.2718 | -6.4024 | 0.96409 | 0.28948 | 0.18252 | -0.13119 | 0.96 | 1.3 | 2 | 0.5 | 0.66 | 0.84171 | 0.15829 | 0.028822 | 1.3011 | -0.32991 | 2.6081 | 0
34102 | 1 | 40 | 1 | 10.8 | 10.39 | 487200 | 0.705 | 0.25464 | 0.0267 | 0.61 | 0 | 0.123 | 0.01 | 100 | 2.2459 | -0.045908 | 0.00051641 | 0.0026469 | -9.5833e-06 | -0.00010262 | 3.84 | -0.027141 | -0.00014531 | -0.0076466 | -8.9167e-06 | 6.875e-05 | -0.79627 | 0.056948 | -0.00035859 | -0.0098866 | 0.000209 | -0.00021313 | 58.1396 | -1.7385 | 0.0127 | 0.0065284 | 8.6136e-05 | 0.0001466 | 2.6306 | -9.5 | 14.2718 | -6.4024 | 0.96409 | 0.28948 | 0.18252 | -0.13119 | 0.96 | 1.3 | 2 | 0.5 | 0.66 | 0.84171 | 0.15829 | 0.028822 | 1.3011 | -0.32991 | 2.6081 | 0
34202 | 2 | 40 | 1 | 11.5 | 11.06 | 487200 | 0.705 | 0.23585 | 0.0267 | 0.61 | 0 | 0.123 | 0.01 | 100 | 2.2459 | -0.045908 | 0.00051641 | 0.0026469 | -9.5833e-06 | -0.00010262 | 3.84 | -0.027141 | -0.00014531 | -0.0076466 | -8.9167e-06 | 6.875e-05 | -0.79627 | 0.056948 | -0.00035859 | -0.0098866 | 0.000209 | -0.00021313 | 58.1396 | -1.7385 | 0.0127 | 0.0065284 | 8.6136e-05 | 0.0001466 | 2.6306 | -9.5 | 14.2718 | -6.4024 | 0.96409 | 0.28948 | 0.18252 | -0.13119 | 0.96 | 1.3 | 2 | 0.5 | 0.66 | 0.84171 | 0.15829 | 0.028822 | 1.3011 | -0.32991 | 2.6081 | 0
34302 | 3 | 40 | 1 | 12.5 | 12.02 | 487200 | 0.705 | 0.21257 | 0.0267 | 0.61 | 0 | 0.123 | 0.01 | 100 | 2.2459 | -0.045908 | 0.00051641 | 0.0026469 | -9.5833e-06 | -0.00010262 | 3.84 | -0.027141 | -0.00014531 | -0.0076466 | -8.9167e-06 | 6.875e-05 | -0.79627 | 0.056948 | -0.00035859 | -0.0098866 | 0.000209 | -0.00021313 | 58.1396 | -1.7385 | 0.0127 | 0.0065284 | 8.6136e-05 | 0.0001466 | 2.6306 | -9.5 | 14.2718 | -6.4024 | 0.96409 | 0.28948 | 0.18252 | -0.13119 | 0.96 | 1.3 | 2 | 0.5 | 0.66 | 0.84171 | 0.15829 | 0.028822 | 1.3011 | -0.32991 | 2.6081 | 0
EER Rated 2 Speed Units 760 to 800 kBtuh
35002 | 0 | 65 | 1 | 9.5 | 9.14 | 791700 | 0.705 | 0.29707 | 0.0267 | 0.61 | 0 | 0.123 | 0.01 | 100 | 2.2459 | -0.045908 | 0.00051641 | 0.0026469 | -9.5833e-06 | -0.00010262 | 3.84 | -0.027141 | -0.00014531 | -0.0076466 | -8.9167e-06 | 6.875e-05 | -0.79627 | 0.056948 | -0.00035859 | -0.0098866 | 0.000209 | -0.00021313 | 58.1396 | -1.7385 | 0.0127 | 0.0065284 | 8.6136e-05 | 0.0001466 | 2.6306 | -9.5 | 14.2718 | -6.4024 | 0.96409 | 0.28948 | 0.18252 | -0.13119 | 0.96 | 1.3 | 2 | 0.5 | 0.66 | 0.84171 | 0.15829 | 0.028822 | 1.3011 | -0.32991 | 2.6081 | 0
35102 | 1 | 65 | 1 | 10.2 | 9.81 | 791700 | 0.705 | 0.27298 | 0.0267 | 0.61 | 0 | 0.123 | 0.01 | 100 | 2.2459 | -0.045908 | 0.00051641 | 0.0026469 | -9.5833e-06 | -0.00010262 | 3.84 | -0.027141 | -0.00014531 | -0.0076466 | -8.9167e-06 | 6.875e-05 | -0.79627 | 0.056948 | -0.00035859 | -0.0098866 | 0.000209 | -0.00021313 | 58.1396 | -1.7385 | 0.0127 | 0.0065284 | 8.6136e-05 | 0.0001466 | 2.6306 | -9.5 | 14.2718 | -6.4024 | 0.96409 | 0.28948 | 0.18252 | -0.13119 | 0.96 | 1.3 | 2 | 0.5 | 0.66 | 0.84171 | 0.15829 | 0.028822 | 1.3011 | -0.32991 | 2.6081 | 0
35202 | 2 | 65 | 1 | 11 | 10.58 | 791700 | 0.705 | 0.24907 | 0.0267 | 0.61 | 0 | 0.123 | 0.01 | 100 | 2.2459 | -0.045908 | 0.00051641 | 0.0026469 | -9.5833e-06 | -0.00010262 | 3.84 | -0.027141 | -0.00014531 | -0.0076466 | -8.9167e-06 | 6.875e-05 | -0.79627 | 0.056948 | -0.00035859 | -0.0098866 | 0.000209 | -0.00021313 | 58.1396 | -1.7385 | 0.0127 | 0.0065284 | 8.6136e-05 | 0.0001466 | 2.6306 | -9.5 | 14.2718 | -6.4024 | 0.96409 | 0.28948 | 0.18252 | -0.13119 | 0.96 | 1.3 | 2 | 0.5 | 0.66 | 0.84171 | 0.15829 | 0.028822 | 1.3011 | -0.32991 | 2.6081 | 0
35302 | 3 | 65 | 1 | 12 | 11.54 | 791700 | 0.705 | 0.22373 | 0.0267 | 0.61 | 0 | 0.123 | 0.01 | 100 | 2.2459 | -0.045908 | 0.00051641 | 0.0026469 | -9.5833e-06 | -0.00010262 | 3.84 | -0.027141 | -0.00014531 | -0.0076466 | -8.9167e-06 | 6.875e-05 | -0.79627 | 0.056948 | -0.00035859 | -0.0098866 | 0.000209 | -0.00021313 | 58.1396 | -1.7385 | 0.0127 | 0.0065284 | 8.6136e-05 | 0.0001466 | 2.6306 | -9.5 | 14.2718 | -6.4024 | 0.96409 | 0.28948 | 0.18252 | -0.13119 | 0.96 | 1.3 | 2 | 0.5 | 0.66 | 0.84171 | 0.15829 | 0.028822 | 1.3011 | -0.32991 | 2.6081 | 0
Data Key:
Columns labeled 1 - 6 are unit descriptors and are not uses as DOE-2 input fields. | [10 empty] | Col. 3 - Heat Source Values
Column(s) | Usage | [9 empty] | None | 0
2 | Nominal cooling capacity (tons) | [9 empty] | Gas | 1
3 | Unit heat source, or for heat pumps, supplemental heat source (gas, electric, or none) | [9 empty] | Elec | 2
4 | Unit EER rating for units over 65,000 Btuh cooling output
5 | Calculated EER based on expanded ratings tables and assumed SA fan power.
6 | Unit rated gross cooling capacity
Colums I through BF are used as DOE-2 simulation inputs. Fields are used as follows:
7 | Ratio of sensible to total capacity (sensible heat ratio) is used to establish COOL-SH-CAP from design cooling load.
COOL-SH-CAP = COOLING-CAPACITY * Sen/Total
8 | Value is DOE-2 keyword COOLING-EIR
9 | cfm/Btuh is used to calculate design air flow as SUPPLY-CFM = cfm/Btuh * unit design capacity.
10 | Fan W/cfm is used to set the fan power input and fan Delta T via the following keywords:
11 | Condenser fan Watt/gross total cooling capacity. Value is the DOE-2 keyword OUTSIDE-FAN-ELEC.
12 | Coil-BF is the design coil by-pass factor. The DOE-2 keyword COIL-BF = Coil-BF
13 | Crkn/Tot kW is used to set the keyword CRANKCASE-HEAT, and is the ratio of crankcase load heat to the design compressor power.
14 | Crnk Off is the temperature above which crankcase heat is deactivated and is the value used for the keyword CRANKCASE-MAX-T.
15 - 20 | The coefficients for the bi-quadratic total capacity off-design curve set by the keyword COOL-CAP-FT
21 - 26 | The coefficients for the bi-quadratic sensible capacity off-design curve set by the keyword COOL-SH-FT
27 - 32 | The coefficients for the bi-quadratic EIR off-design curve set by the keyword COOL-EIR-FT
33 - 38 | The coefficients for the bi-quadratic coil by-pass factor off-design curve set by the keyword COIL-BF-FT
39 - 42 | The coefficients for the qubic equation that determines the EIR as a function of the part-load ratio.
43 - 46 | The coefficients for the cubic equation of the C-LOSS curve.
47 | Minimum value for the C-LOSS curve - value is the DOE-2 curve fit keyword OUTPUT-MIN | [5 empty] | Need to property to define CURVE TYPE!
48 | Maximum value for the C-LOSS curve - value is the DOE-2 curve fit keyword OUTPUT-MAX
49 | Number of cooling stages - (Used only for proper outdoor fan simulation.)
50 | Low speed cfm ratio for 2-speed units (ratio of low speed to high speed cfm) used by keyword MIN-FLOW-RATIO
51 | Low speed capacity ratio for 2-speed units (ratio of lowspeed to high speed cooling capacity) used by keyword COOL-STAGES
52, 53 | The coefficients for the linear curve that relates total capacity to cfm ratio
cfm ratio is defined as operating cfm/rated cfm.
54 - 56 | The coefficients for the quadratic curve that relates sensible capacity to cfm ratio
57 | Fan power exponent used to adjust supply fan power for non-rated flow conditions.
Supply fan power calculated as: Fan power = Rated fan power *(cfm ratio)(fan power exponent)
58 | Supply Fan kW Multiplier, based on typical external static pressure and presence of an economizer.
ignore