## Package AC Performance
;-------------------------------------------------------------------------
; DEER - eQUEST Wizard Defaults: Packaged DX Equipment Details
; October 4, 2008 - kjm
;-------------------------------------------------------------------------
;
; |  | Detailed AC and HP Unit Performance Data
; |  | The performance curves are for all unique packaged units (<=20 tons) for which expanded ratings data sufficient to
; |  | generate performance curves were found.
;
;
; |  | Data Key & Implmentation Notes:
; |  | Columns A through E are unit descriptors and are not uses as DOE-2 input fields.
; |  | Column(s) | Usage
; |  | 1 | Dataset key
; |  | 2 | Nominal cooling capacity (tons)
; |  | 3 | Unit heat source, or for heat pumps, supplemental heat source (gas, electric, or none)
; |  |  | Heat Source Values
; |  |  | None | 0
; |  |  | Gas | 1
; |  |  | Elec | 2
; |  | 4 | Unit EER rating for units over 65,000 Btuh cooling output
; |  | 5 | Calculated EER based on expanded ratings tables and assumed SA fan power.
; |  | 6 | Unit rated gross cooling capacity
; |  | Colums I through BF are used as DOE-2 simulation inputs. Fields are used as follows:
; |  | 7 | Ratio of sensible to total capacity (sensible heat ratio) is used to establish COOL-SH-CAP from design cooling load.
; |  |  | COOL-SH-CAP = COOLING-CAPACITY * Sen/Total
; |  |  | DEER Sizing Procedure:
; |  |  |  | (1) Set SYSTEM:COOLING-CAPACITY based on SV-A of design run
; |  |  |  | (2) Multiply CoolCap by this value (Sens/Total) and post to SYSTEM:COOL-SH-CAP
; |  | 8 | Value is DOE-2 keyword COOLING-EIR
; |  | 9 | cfm/Btuh is used to calculate design air flow as SUPPLY-CFM = cfm/Btuh * unit design capacity.
; |  |  |  | SUPPLY-FLOW = <this value> * SYSTEM:COOLING-CAPACITY
; |  | 10 | Fan W/cfm is used to set the fan power input and fan Delta T via the following keywords:
; |  |  |  | SUPPLY-KW/FLOW = <this value> / 1000
; |  |  |  | SUPPLY-DELTA-T = <this value> * 3.16
; |  | 11 | Condenser fan Watt/gross total cooling capacity. Value is the DOE-2 keyword OUTSIDE-FAN-ELEC.
; |  | 12 | Coil-BF is the design coil by-pass factor. The DOE-2 keyword COIL-BF = Coil-BF
; |  | 13 | Crkn/Tot kW is used to set the keyword CRANKCASE-HEAT, and is the ratio of crankcase load heat to the design compressor power.
; |  |  |  | CRANKCASE-HEAT = 0 ***For all DEER simulations***
; |  | 14 | Crnk Off is the temperature above which crankcase heat is deactivated and is the value used for the keyword CRANKCASE-MAX-T.
; |  | 15 - 20 | The coefficients for the bi-quadratic total capacity off-design curve set by the keyword COOL-CAP-FT | [11 empty] | REFRIGERATION (DOE2.2R) BDL REQUIRED KEYWORDS
; |  |  |  | TYPE = BI-QUADRATIC-T, INPUT-TYPE = COEFFICIENTS, COEFFICIENTS = <these values> | [10 empty] | Grocery Building Type
; |  | 21 - 26 | The coefficients for the bi-quadratic sensible capacity off-design curve set by the keyword COOL-SH-FT
; |  |  |  | TYPE = BI-QUADRATIC-T, INPUT-TYPE = COEFFICIENTS, COEFFICIENTS = <these values> | [10 empty] | Keyword | MIN-INPUT-1 | MAX-INPUT-1 | MIN-INPUT-2 | MAX-INPUT-2
; |  | 27 - 32 | The coefficients for the bi-quadratic EIR off-design curve set by the keyword COOL-EIR-FT | [11 empty] | COOL-CAP-FT | 55 | 70 | 55 | 120
; |  |  |  | TYPE = BI-QUADRATIC-T, INPUT-TYPE = COEFFICIENTS, COEFFICIENTS = <these values> | [10 empty] | COOL-SH-FT | 55 | 70 | 55 | 120
; |  | 33 - 38 | The coefficients for the bi-quadratic coil by-pass factor off-design curve set by the keyword COIL-BF-FT | [11 empty] | COOL-EIR-FT | 55 | 70 | 55 | 120
; |  |  |  | TYPE = BI-QUADRATIC-T, INPUT-TYPE = COEFFICIENTS, COEFFICIENTS = <these values> | [10 empty] | COIL-BF-FT | 55 | 70 | 55 | 120
; |  |  |  | Keyword OUTPUT-MIN must be set to zero for this curve as small negative values can occur! | [10 empty] | COOL-EIR-FPLR | 0 | 1.1
; |  |  |  | set DetDXCoilBFFTMin = 0 & DetDXCoilBFFTMax = -999 | [10 empty] | COOL-CLOSS-FPLR | 0 | 1.1
; |  | 39 - 42 | The coefficients for the qubic equation that determines the EIR as a function of the part-load ratio, COOL-EIR-FPLR | [11 empty] | OUTSIDE-FAN-CFLT | 0 | 5 | 0 | 200
; |  |  |  | TYPE = CUBIC, INPUT-TYPE = COEFFICIENTS, COEFFICIENTS = <these values>
; |  | 43 - 46 | The coefficients for the cubic equation of the C-LOSS curve, COOL-CLOSS-FPLR
; |  |  |  | TYPE = CUBIC, INPUT-TYPE = COEFFICIENTS, COEFFICIENTS = <these values>
; |  | 47 | Minimum value for the C-LOSS curve - value is the DOE-2 curve fit keyword OUTPUT-MIN
; |  | 48 | Maximum value for the C-LOSS curve - value is the DOE-2 curve fit keyword OUTPUT-MAX
; |  | 49 | Number of cooling stages - (Used only for proper outdoor fan simulation.)
; |  |  |  | Keywords MIN-HGB-RATIO and MIN-UNLOAD-RATIO must be set to zero (not 1/cooling stages) for dual
; |  |  |  | compressor cooling as modeled by the EIR_f(PLR) curves and C-LOSS_f(PLR) curves provided above.
; |  | 50 | Low speed cfm ratio for 2-speed units (ratio of low speed to high speed cfm) used by keyword MIN-FLOW-RATIO
; |  |  |  | MIN-FLOW-RATIO not used in nonres (PSZ) system models
; |  | 51 | Low speed capacity ratio for 2-speed units (ratio of lowspeed to high speed cooling capacity) used by keyword COOL-STAGES
; |  |  |  | COOL-STAGES not used in nonres (PSZ) system models
; |  |  |  | if <comp spd> = 2, then MIN-UNLOAD-RATIO = 0.0 AND MIN-HGB-RATIO = 0.0, (otherwise set each to 1.0)
; |  |  |  | if <comp spd> = 2, then populate SYSTEM:OUTSIDE-FAN-CFLT as follows:
; | [5 empty] | "DEER08 Outside Fan CFLT" | = CURVE-FIT
; | [5 empty] | TYPE | = BI-LINEAR
; | [5 empty] | INPUT-TYPE | = COEFFICIENTS
; | [5 empty] | OUTPUT-MIN | = 0.0
; | [5 empty] | OUTPUT-MAX | = 1.0
; | [5 empty] | COEFFICIENTS | = { 0, 1/<this value>, 0, 0 )
; |  | 52, 53 | The coefficients for the linear curve that relates total capacity to cfm ratio | [8 empty] | not used
; |  |  | cfm ratio is defined as operating cfm/rated cfm.
; |  |  | Compressor electric input is not significantly affected by cfm, thus EIR impact = 1/(total capacity impact)
; |  | 54 - 56 | The coefficients for the quadratic curve that relates sensible capacity to cfm ratio | [8 empty] | not used
; |  | 57 | Fan power exponent used to adjust supply fan power for non-rated flow conditions. | [8 empty] | not used
; |  |  | Supply fan power calculated as: Fan power = Rated fan power *(cfm ratio)(fan power exponent)
; |  | 58 | Supply Fan kW Multiplier, based on typical external static pressure and presence of an economizer. | [8 empty] | not used
;
;
;
;
; | Mapping of detailed equipment data to efficiency levels in DEER Measures
; | Typical DX Equipment by (AC/HP(3/4) * 100) + (SizeCateg(0-2) * 10) + Tier
; |  | Equip ID | Generic Data Name |  |  | Capacity | CEE Tier | Measure Efficiency | Units | Notes
; | 300 | 30007 | PkgDX T0 Mfg1 110 2t 10seer |  |  | <= 65 | - n/a - | 10 | SEER
; | 301 | 30103 | PkgDX T1 Mfg1 167 5t 13seer |  |  | <= 65 | - n/a - | 12 | SEER | Scale 13 SEER properties down to represent 12 SEER
; | 302 | 30103 | PkgDX T1 Mfg1 167 5t 13seer |  |  | <= 65 | - n/a - | 13 | SEER
; | 303 | 30203 | PkgDX T2 Mfg1 195 5t 14seer |  |  | <= 65 | - n/a - | 14 | SEER
; | 310 | 31005 | PkgDX T0 Mfg1 202 10t 10.1eer |  |  | 65-135 | 0 | 10.1 | EER
; | 311 | 31102 | PkgDX T1 Mfg1 243 10t 11eer |  |  | 65-135 | 1 | 11 | EER
; | 312 | 31305 | PkgDX T3 Mfg1 274 7.4t 12.5eer |  |  | 65-135 | 2 | 11.5 | EER | Scale 12.5 EER properties down to represent 11.5 EER
; | 313 | 31305 | PkgDX T3 Mfg1 274 7.4t 12.5eer |  |  | 65-135 | 3 | 12 | EER | Scale 12.5 EER properties down to represent 12.0 EER
; | 320 | 32020 | PkgDX T0 Mfg3 297 12.5t 9.5eer |  |  | 135-240 | 0 | 9.5 | EER
; | 321 | 32103 | PkgDX T1 Mfg3 323 21t 10.5eer |  |  | 135-240 | 1 | 10.8 | EER | Scale 10.5 EER properties up to represent 10.8 EER
; | 322 | 32203 | PkgDX T2 Mfg3 341 18t 11.5eer |  |  | 135-240 | 2 | 11.5 | EER
; | 323 | 32306 | PkgDX T3 Mfg3 356 12.5t 12.2eer |  |  | 135-240 | 3 | 12 | EER | Scale 12.2 EER properties down to represent 12.0 EER
;
;
; Indep. | Dependents
; 1 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58
; Indep. ; 1: ; Equip ID; Dependents 1: Tier; Dependents 2: Nom Cap; Dependents 3: Heat Source; Dependents 4: Rated SEER/EER; Dependents 5: Calc EER; Dependents 6: Tot Cap; Dependents 7: Sen/Total; Dependents 8: EIR; Dependents 9: cfm/Btuh; Dependents 10: Fan W/cfm; Dependents 11: CF W/Bth; Dependents 12: Coil-BF; Dependents 13: Crnk/Tot kW; Dependents 14: Crnk Off; Dependents 15: Total Capacity Curve Fit Coefficients; Dependents 21: Sensible Capacity Curve Fit Coefficients; Dependents 27: EIR Curve Fit Coefficients; Dependents 33: Coil-BF Curve Fit Coefficients; Dependents 39: EIR_PLR Curve Fit Coefficients; Dependents 43: CLoss Curve Fit Coefficients; Dependents 47: C_Loss Min, Max; Dependents 49: Cmp Spd; Dependents 50: Low Speed Ratios; Dependents 52: Tot Cap_f(cfm); Dependents 54: Sen Cap_f(cfm); Dependents 57: SF Exp; Dependents 58: SF_Mult |  | Mfgr | Model # | Heat Source |  | Equip Abbreviation | Wizard Long Name | DX Equip Label
; | SEER Rated A/C Units - Up to 5 tons, from: "All SEER-Rated Pkg Unit Perf Curves (2008 DEER Rev 2).xls"
30001 | 0 | 3 | 1 | 9.7 | 8.9326 | 36600 | 0.7104 | 0.3371 | 0.03279 | 0.29083 | 0 | 0.2231 | 0 | 55 | 0.3694 | 0.0080874 | 0.0001304 | -0.00069868 | -7.1905e-06 | -5.74e-05 | 1.9743 | 0.031185 | -0.0006152 | -0.010898 | 0 | 0.0001152 | 0.88223 | -0.016084 | 0.0001628 | 0.01057 | 7.7738e-05 | -0.000195 | 28.0393 | -0.93885 | 0.0081123 | 0.07722 | 2.2083e-05 | -0.0012706 | 9.9468e-06 | 1.1087 | -0.12828 | 0.019584 | 0.90084 | 0.10995 | -0.012722 | 0.0019421 | 0.879 | 1 | 1 | 1 | 1 | 0.85246 | 0.14754 | 0.45385 | 0.63846 | -0.092308 | 0.48321 | 1.3099 | ; | Mfg1 | 104 | Gas | Mfg1 | Mfg1_104 | Pkg DX, Tier 0, Mfg1 104 (3 ton, 9.7 rated SEER) | PkgDX T0 Mfg1 104 3t 9.7seer
30002 | 0 | 4 | 1 | 9.7 | 8.8169 | 50500 | 0.705 | 0.3349 | 0.03168 | 0.34813 | 0 | 0.2104 | 0 | 55 | 0.0037953 | 0.025675 | -6.36e-05 | -0.0045861 | -9.9762e-06 | 1.37e-05 | 1.8288 | 0.03566 | -0.000674 | -0.01078 | -1.081e-05 | 0.000146 | 1.2536 | -0.030826 | 0.0002912 | 0.012769 | 7.1714e-05 | -0.000213 | 30.9406 | -1.0011 | 0.0085981 | 0.057789 | 0.0001216 | -0.0012644 | 4.2834e-06 | 1.0834 | -0.095345 | 0.011979 | 0.9225 | 0.083961 | -0.0073892 | 0.00092835 | 0.905 | 1 | 1 | 1 | 1 | 0.84554 | 0.15446 | 0.45506 | 0.6573 | -0.11236 | 1.1201 | 1.2782 | ; | Mfg1 | 105 | Gas | Mfg1 | Mfg1_105 | Pkg DX, Tier 0, Mfg1 105 (4 ton, 9.7 rated SEER) | PkgDX T0 Mfg1 105 4t 9.7seer
30003 | 0 | 5 | 1 | 9.7 | 8.6413 | 60900 | 0.7438 | 0.341 | 0.03284 | 0.345 | 0 | 0.1405 | 0 | 55 | 0.89007 | -0.023072 | 0.0004068 | 0.0066113 | -3.9881e-05 | -6.89e-05 | 0.21968 | 0.079955 | -0.0010248 | -0.010653 | -3.7786e-05 | 0.0002163 | -0.44167 | 0.020106 | -6.52e-05 | 0.015912 | 8.8833e-05 | -0.0003026 | 60.4643 | -1.9802 | 0.017037 | 0.13641 | 0.00037599 | -0.0030834 | 2.0792e-06 | 1.0663 | -0.074131 | 0.007797 | 0.9375 | 0.066646 | -0.0046332 | 0.00048731 | 0.923 | 1 | 1 | 1 | 1 | 0.77997 | 0.22003 | 0.30684 | 0.8521 | -0.15894 | 1.0368 | 1.2719 | ; | Mfg1 | 106 | Gas | Mfg1 | Mfg1_106 | Pkg DX, Tier 0, Mfg1 106 (5 ton, 9.7 rated SEER) | PkgDX T0 Mfg1 106 5t 9.7seer
30004 | 0 | 2.5 | 2 | 9.7 | 8.5997 | 29300 | 0.76 | 0.3157 | 0.03413 | 0.499 | 0 | 0.1348 | 0 | 55 | 1.3785 | -0.02322 | 0.00034766 | 0.0024844 | -1.1417e-05 | -8.1125e-05 | 2.5354 | 0.019064 | -0.00052578 | -0.013025 | 1.7417e-05 | 9.8625e-05 | 1.0573 | -0.0090109 | 5.8594e-05 | 0.00024437 | 9.5917e-05 | -9.5125e-05 | 49.4561 | -1.6046 | 0.012557 | 0.13181 | -0.00024367 | -0.0011996 | 3.2792e-07 | 1.0368 | -0.039333 | 0.0025263 | 0.96444 | 0.036864 | -0.0013985 | 8.9823e-05 | 0.956 | 1 | 1 | 1 | 1 | 0.87201 | 0.12799 | 0.59314 | 0.32491 | 0.081956 | 1.002 | 1.1581 | ; | Mfg3 | 107 | Elec | Mfg3 | Mfg3_107 | Pkg DX, Tier 0, Mfg3 107 (2.5 ton, 9.7 rated SEER) | PkgDX T0 Mfg3 107 2.5t 9.7seer
30005 | 0 | 2.5 | 2 | 9.9 | 9.2 | 30853.594 | 0.731 | 0.3199 | 0.03241 | 0.338 | 0 | 0.1614 | 0 | 55 | 3.8475 | -0.091934 | 0.000778 | 0.0012766 | -4.9786e-05 | 2.32e-05 | -4.9422 | 0.26552 | -0.0026338 | -0.026411 | -4.6714e-05 | 0.00045656 | -2.0803 | 0.10432 | -0.0005992 | -0.014346 | 0.00027671 | -0.00036984 | 126.2149 | -4.0822 | 0.033496 | 0.15103 | 0.00023203 | -0.0029087 | 2.3905e-07 | 1.0333 | -0.035326 | 0.002075 | 0.96778 | 0.033294 | -0.0011383 | 6.6862e-05 | 0.96 | 1 | 1 | 1 | 1 | 0.85324 | 0.14676 | 2.6044 | -3.7487 | 2.1443 | 1 | 1.2798 | ; | Mfg6 | 108 | Elec | Mfg6 | Mfg6_108 | Pkg DX, Tier 0, Mfg6 108 (2.5 ton, 9.9 rated SEER) | PkgDX T0 Mfg6 108 2.5t 9.9seer
30006 | 0 | 1.5 | 1 | 10 | 9.5238 | 18600 | 0.6928 | 0.3178 | 0.03234 | 0.27 | 0 | 0.2585 | 0 | 55 | -0.60642 | 0.034924 | -8.1e-05 | -0.0038957 | -2.6917e-05 | 3.82e-05 | 2.2649 | 0.019182 | -0.000583 | -0.012178 | -4.55e-05 | 0.0002568 | 2.1846 | -0.053817 | 0.000528 | 0.016996 | 0.00012408 | -0.0004216 | 13.4193 | -0.44573 | 0.0047478 | 0.039996 | 0.0003686 | -0.0017273 | 3.7615e-05 | 1.165 | -0.20674 | 0.041702 | 0.85502 | 0.16893 | -0.029978 | 0.0060468 | 0.825 | 1 | 1 | 1 | 1 | 0.71457 | 0.28543 | 0.081548 | 1.1759 | -0.25747 | 0.17151 | 1.3274 | ; | Mfg1 | 109 | Gas | Mfg1 | Mfg1_109 | Pkg DX, Tier 0, Mfg1 109 (1.5 ton, 10 rated SEER) | PkgDX T0 Mfg1 109 1.5t 10seer
30007 | 0 | 2 | 1 | 10 | 9.4981 | 25800 | 0.6975 | 0.2971 | 0.03103 | 0.4325 | 0 | 0.2143 | 0 | 55 | -0.35078 | 0.032251 | -0.000154 | -0.0027733 | -3.8833e-05 | 7.78e-05 | 2.8739 | -0.002921 | -0.000361 | -0.0074043 | -1.8583e-05 | 0.0001278 | 1.3045 | -0.028713 | 0.000312 | 0.011817 | 9.675e-05 | -0.0002792 | 8.5771 | -0.34275 | 0.0036658 | 0.081184 | 5.5738e-05 | -0.0014586 | 2.141e-05 | 1.1383 | -0.16866 | 0.030369 | 0.8764 | 0.1407 | -0.020849 | 0.0037539 | 0.85 | 1 | 1 | 1 | 1 | 0.80746 | 0.19254 | 0.34576 | 0.83221 | -0.17797 | 0.13849 | 1.2289 | ; | Mfg1 | 110 | Gas | Mfg1 | Mfg1_110 | Pkg DX, Tier 0, Mfg1 110 (2 ton, 10 rated SEER) | PkgDX T0 Mfg1 110 2t 10seer
30008 | 0 | 2.5 | 1 | 10 | 9.505 | 30000 | 0.7302 | 0.3038 | 0.03331 | 0.358 | 0 | 0.186 | 0 | 55 | 2.7229 | -0.076629 | 0.000616 | 0.011403 | -0.00011658 | 9.66e-05 | 3.4741 | -0.023662 | -0.0002515 | -0.004324 | -5.3333e-05 | 0.0001779 | -0.82315 | 0.044154 | -0.000196 | 0.0031782 | 0.00015167 | -0.0003026 | 11.7853 | -0.42577 | 0.0039072 | 0.086121 | -2.8463e-05 | -0.0012133 | 3.8389e-05 | 1.1661 | -0.20828 | 0.042179 | 0.85419 | 0.17005 | -0.030374 | 0.0061511 | 0.824 | 1 | 1 | 1 | 1 | 0.81633 | 0.18367 | 0.34206 | 0.80889 | -0.15096 | 0.25614 | 1.2595 | ; | Mfg1 | 111 | Gas | Mfg1 | Mfg1_111 | Pkg DX, Tier 0, Mfg1 111 (2.5 ton, 10 rated SEER) | PkgDX T0 Mfg1 111 2.5t 10seer
30009 | 0 | 3 | 1 | 10 | 9.3243 | 36300 | 0.7244 | 0.2988 | 0.03307 | 0.43583 | 0 | 0.1945 | 0 | 55 | 0.95146 | -0.017582 | 0.0003585 | 0.0052621 | -4.5e-06 | -0.0001323 | 3.2878 | -0.01935 | -0.0001905 | -0.004096 | -9.4167e-06 | 5.31e-05 | 1.1813 | -0.004444 | -3.9e-05 | -0.0048538 | 8.875e-05 | -7.6e-06 | 3.1246 | -0.13498 | 0.0019485 | 0.059321 | 0.00015458 | -0.0013917 | 1.115e-05 | 1.1127 | -0.13359 | 0.020918 | 0.8975 | 0.11405 | -0.013693 | 0.0021441 | 0.875 | 1 | 1 | 1 | 1 | 0.92844 | 0.071561 | 0.57748 | 0.54841 | -0.1259 | 0.55733 | 1.2091 | ; | Mfg1 | 112 | Gas | Mfg1 | Mfg1_112 | Pkg DX, Tier 0, Mfg1 112 (3 ton, 10 rated SEER) | PkgDX T0 Mfg1 112 3t 10seer
30010 | 0 | 3.5 | 1 | 10 | 9.5078 | 45600 | 0.7568 | 0.2656 | 0.03068 | 0.65643 | 0 | 0.0459 | 0 | 55 | 0.77995 | -0.0081585 | 0.0002415 | 0.0014866 | -2e-05 | -4.37e-05 | 1.7124 | 0.045156 | -0.0008395 | -0.017213 | -3.6083e-05 | 0.0003129 | -0.34425 | 0.014899 | -7.65e-05 | 0.013612 | 6.9583e-05 | -0.0001935 | 95.1387 | -3.3228 | 0.031416 | 0.47993 | 0.0013576 | -0.011058 | 4.8009e-05 | 1.1781 | -0.22594 | 0.047771 | 0.84475 | 0.18294 | -0.035083 | 0.0074178 | 0.813 | 1 | 1 | 1 | 1 | 0.73995 | 0.26005 | -0.012414 | 1.3685 | -0.35608 | 1.1252 | 1.1005 | ; | Mfg1 | 113 | Gas | Mfg1 | Mfg1_113 | Pkg DX, Tier 0, Mfg1 113 (3.5 ton, 10 rated SEER) | PkgDX T0 Mfg1 113 3.5t 10seer
30011 | 0 | 4 | 1 | 10 | 9.0038 | 49500 | 0.7516 | 0.3088 | 0.03231 | 0.4625 | 0 | 0.1068 | 0 | 55 | 0.29217 | 0.0074325 | 0.0001325 | 0.00023283 | -6.6667e-06 | -5.45e-05 | 1.9756 | 0.018171 | -0.0005635 | -0.0029465 | -6.0417e-05 | 0.0001825 | 0.37699 | -0.006845 | 0.00014 | 0.013409 | 0.00011317 | -0.0002894 | 54.0519 | -1.5736 | 0.013951 | 0.016223 | 0.0010424 | -0.0033303 | 1.0238e-05 | 1.1097 | -0.12961 | 0.019913 | 0.9 | 0.11097 | -0.012961 | 0.0019913 | 0.878 | 1 | 1 | 1 | 1 | 0.76947 | 0.23053 | 0.28791 | 0.79512 | -0.083028 | 1.1959 | 1.1986 | ; | Mfg1 | 114 | Gas | Mfg1 | Mfg1_114 | Pkg DX, Tier 0, Mfg1 114 (4 ton, 10 rated SEER) | PkgDX T0 Mfg1 114 4t 10seer
30012 | 0 | 5 | 1 | 10 | 8.9021 | 63300 | 0.7328 | 0.3122 | 0.03162 | 0.4775 | 0 | 0.1355 | 0 | 55 | -0.030564 | 0.019897 | 3.2e-05 | -0.0011409 | -4e-06 | -4.74e-05 | 1.6031 | 0.034616 | -0.000689 | -0.0063575 | -4.5083e-05 | 0.0001856 | 1.0299 | -0.012661 | 9.35e-05 | 0.0059 | 8.1583e-05 | -0.0001411 | 42.1202 | -1.3229 | 0.012017 | 0.066812 | 0.00062719 | -0.0028967 | 4.9061e-07 | 1.0419 | -0.045123 | 0.0032413 | 0.95972 | 0.041965 | -0.0018174 | 0.00013055 | 0.95 | 1 | 1 | 1 | 1 | 0.9113 | 0.088698 | 0.77767 | 0.32364 | -0.1013 | 1.7642 | 1.1955 | ; | Mfg1 | 115 | Gas | Mfg1 | Mfg1_115 | Pkg DX, Tier 0, Mfg1 115 (5 ton, 10 rated SEER) | PkgDX T0 Mfg1 115 5t 10seer
30013 | 0 | 1.5 | 2 | 10 | 9.5238 | 18600 | 0.6932 | 0.316 | 0.03229 | 0.28333 | 0 | 0.2563 | 0 | 55 | -0.60309 | 0.034795 | -8e-05 | -0.0038603 | -2.6917e-05 | 3.78e-05 | 2.2615 | 0.019237 | -0.0005825 | -0.012203 | -4.5167e-05 | 0.0002563 | 2.1284 | -0.052402 | 0.0005175 | 0.017096 | 0.00012333 | -0.0004207 | 15.478 | -0.55666 | 0.0057978 | 0.075355 | 0.00029954 | -0.0020535 | 3.7615e-05 | 1.165 | -0.20674 | 0.041702 | 0.85502 | 0.16893 | -0.029978 | 0.0060468 | 0.825 | 1 | 1 | 1 | 1 | 0.69882 | 0.30118 | -0.092452 | 1.502 | -0.40955 | 0.69293 | 1.3183 | ; | Mfg1 | 116 | Elec | Mfg1 | Mfg1_116 | Pkg DX, Tier 0, Mfg1 116 (1.5 ton, 10 rated SEER) | PkgDX T0 Mfg1 116 1.5t 10seer
30014 | 0 | 2 | 2 | 10 | 9.4981 | 25800 | 0.6977 | 0.2962 | 0.03101 | 0.43875 | 0 | 0.2133 | 0 | 55 | -0.35425 | 0.032356 | -0.0001545 | -0.0027691 | -3.8667e-05 | 7.73e-05 | 2.8695 | -0.0028265 | -0.0003615 | -0.0074076 | -1.8583e-05 | 0.0001279 | 1.3025 | -0.02859 | 0.0003105 | 0.011741 | 9.6833e-05 | -0.0002781 | 8.4252 | -0.33807 | 0.0036319 | 0.081565 | 5.6463e-05 | -0.0014669 | 1.9454e-05 | 1.1342 | -0.16296 | 0.028761 | 0.87973 | 0.13642 | -0.0196 | 0.0034593 | 0.854 | 1 | 1 | 1 | 1 | 0.76631 | 0.23369 | -0.18611 | 1.8372 | -0.65112 | 1.0962 | 1.2252 | ; | Mfg1 | 117 | Elec | Mfg1 | Mfg1_117 | Pkg DX, Tier 0, Mfg1 117 (2 ton, 10 rated SEER) | PkgDX T0 Mfg1 117 2t 10seer
30015 | 0 | 2.5 | 2 | 10 | 9.505 | 30300 | 0.7328 | 0.291 | 0.03298 | 0.445 | 0 | 0.1713 | 0 | 55 | 2.7053 | -0.07588 | 0.00061 | 0.011308 | -0.0001155 | 9.56e-05 | 3.4445 | -0.023422 | -0.0002475 | -0.0042885 | -5.25e-05 | 0.0001755 | -0.81651 | 0.043248 | -0.000192 | 0.0032555 | 0.00014992 | -0.0002956 | 6.0885 | -0.24607 | 0.0024834 | 0.089179 | -3.1957e-05 | -0.0012464 | 3.8389e-05 | 1.1661 | -0.20828 | 0.042179 | 0.85419 | 0.17005 | -0.030374 | 0.0061511 | 0.824 | 1 | 1 | 1 | 1 | 0.78301 | 0.21699 | -0.070647 | 1.5932 | -0.52251 | 0.94851 | 1.2038 | ; | Mfg1 | 118 | Elec | Mfg1 | Mfg1_118 | Pkg DX, Tier 0, Mfg1 118 (2.5 ton, 10 rated SEER) | PkgDX T0 Mfg1 118 2.5t 10seer
30016 | 0 | 3 | 2 | 10 | 9.3243 | 36600 | 0.7269 | 0.2872 | 0.03278 | 0.51583 | 0 | 0.181 | 0 | 55 | 0.94995 | -0.01744 | 0.0003555 | 0.0052684 | -4.6667e-06 | -0.0001313 | 3.26 | -0.019148 | -0.000188 | -0.0040312 | -9.4167e-06 | 5.26e-05 | 1.1457 | -0.003936 | -4.1e-05 | -0.0049584 | 8.975e-05 | -5.8e-06 | -2.5828 | 0.0458 | 0.00052539 | 0.060335 | 0.00015638 | -0.001412 | 1.115e-05 | 1.1127 | -0.13359 | 0.020918 | 0.8975 | 0.11405 | -0.013693 | 0.0021441 | 0.875 | 1 | 1 | 1 | 1 | 0.90372 | 0.096276 | 0.20307 | 1.266 | -0.46908 | 0.94257 | 1.1605 | ; | Mfg1 | 119 | Elec | Mfg1 | Mfg1_119 | Pkg DX, Tier 0, Mfg1 119 (3 ton, 10 rated SEER) | PkgDX T0 Mfg1 119 3t 10seer
30017 | 0 | 3.5 | 2 | 10 | 9.5078 | 45700 | 0.7572 | 0.2635 | 0.03063 | 0.67214 | 0 | 0.0433 | 0 | 55 | 0.78054 | -0.008159 | 0.000241 | 0.0014921 | -2.0083e-05 | -4.34e-05 | 1.7078 | 0.045067 | -0.0008375 | -0.017122 | -3.6167e-05 | 0.0003119 | -0.35991 | 0.015018 | -7.7e-05 | 0.013751 | 6.9e-05 | -0.0001932 | 88.8396 | -3.2158 | 0.035052 | 0.51588 | 0.0030141 | -0.016644 | 4.8009e-05 | 1.1781 | -0.22594 | 0.047771 | 0.84475 | 0.18294 | -0.035083 | 0.0074178 | 0.813 | 1 | 1 | 1 | 1 | 0.72963 | 0.27037 | 0.032382 | 1.2661 | -0.29851 | 1.2497 | 1.0924 | ; | Mfg1 | 120 | Elec | Mfg1 | Mfg1_120 | Pkg DX, Tier 0, Mfg1 120 (3.5 ton, 10 rated SEER) | PkgDX T0 Mfg1 120 3.5t 10seer
30018 | 0 | 4 | 2 | 10 | 9.0038 | 49600 | 0.7521 | 0.3062 | 0.03224 | 0.48 | 0 | 0.1038 | 0 | 55 | 0.29276 | 0.007432 | 0.000132 | 0.0002384 | -6.75e-06 | -5.42e-05 | 1.9772 | 0.018063 | -0.000562 | -0.0029799 | -6.025e-05 | 0.0001826 | 0.34749 | -0.006174 | 0.000136 | 0.013444 | 0.0001135 | -0.00029 | 40.9913 | -1.1332 | 0.012106 | -0.026098 | 0.0018274 | -0.0050938 | 1.0238e-05 | 1.1097 | -0.12961 | 0.019913 | 0.9 | 0.11097 | -0.012961 | 0.0019913 | 0.878 | 1 | 1 | 1 | 1 | 0.76606 | 0.23394 | 0.26706 | 0.83332 | -0.10037 | 1.2285 | 1.1881 | ; | Mfg1 | 121 | Elec | Mfg1 | Mfg1_121 | Pkg DX, Tier 0, Mfg1 121 (4 ton, 10 rated SEER) | PkgDX T0 Mfg1 121 4t 10seer
30019 | 0 | 5 | 2 | 10 | 8.9021 | 63300 | 0.7457 | 0.311 | 0.03159 | 0.4855 | 0 | 0.1016 | 0 | 55 | 0.52795 | -0.0052655 | 0.0002845 | 0.0030981 | -9.1667e-06 | -0.0001043 | 1.3553 | 0.050145 | -0.000815 | -0.01398 | -2.8083e-05 | 0.0002396 | 0.42897 | 0.0076975 | -3.75e-05 | 0.005352 | 0.00010533 | -0.0001941 | 26.7595 | -0.97485 | 0.010097 | 0.17738 | 0.0006201 | -0.0044329 | 9.0577e-07 | 1.0509 | -0.05566 | 0.0047198 | 0.95139 | 0.051087 | -0.0027057 | 0.00022943 | 0.94 | 1 | 1 | 1 | 1 | 0.70354 | 0.29646 | 0.032478 | 1.1986 | -0.23109 | 1.7003 | 1.1908 | ; | Mfg1 | 122 | Elec | Mfg1 | Mfg1_122 | Pkg DX, Tier 0, Mfg1 122 (5 ton, 10 rated SEER) | PkgDX T0 Mfg1 122 5t 10seer
30020 | 0 | 3 | 2 | 10 | 8.9326 | 36600 | 0.7104 | 0.3371 | 0.03279 | 0.29083 | 0 | 0.2231 | 0 | 55 | 0.3694 | 0.0080874 | 0.0001304 | -0.00069868 | -7.1905e-06 | -5.74e-05 | 1.9743 | 0.031185 | -0.0006152 | -0.010898 | 0 | 0.0001152 | 0.88223 | -0.016084 | 0.0001628 | 0.01057 | 7.7738e-05 | -0.000195 | 28.0393 | -0.93885 | 0.0081123 | 0.07722 | 2.2083e-05 | -0.0012706 | 1.068e-06 | 1.0537 | -0.058902 | 0.0052171 | 0.94889 | 0.053855 | -0.0030105 | 0.00026665 | 0.937 | 1 | 1 | 1 | 1 | 0.85246 | 0.14754 | 0.45385 | 0.63846 | -0.092308 | 0.48321 | 1.3099 | ; | Mfg1 | 123 | Elec | Mfg1 | Mfg1_123 | Pkg DX, Tier 0, Mfg1 123 (3 ton, 10 rated SEER) | PkgDX T0 Mfg1 123 3t 10seer
30021 | 0 | 4 | 2 | 10 | 8.8169 | 50500 | 0.705 | 0.3349 | 0.03168 | 0.34813 | 0 | 0.2104 | 0 | 55 | 0.0037953 | 0.025675 | -6.36e-05 | -0.0045861 | -9.9762e-06 | 1.37e-05 | 1.8288 | 0.03566 | -0.000674 | -0.01078 | -1.081e-05 | 0.000146 | 1.2536 | -0.030826 | 0.0002912 | 0.012769 | 7.1714e-05 | -0.000213 | 30.9406 | -1.0011 | 0.0085981 | 0.057789 | 0.0001216 | -0.0012644 | 1.6866e-07 | 1.0297 | -0.031385 | 0.0016681 | 0.97111 | 0.029747 | -0.00090667 | 4.819e-05 | 0.964 | 1 | 1 | 1 | 1 | 0.84554 | 0.15446 | 0.45506 | 0.6573 | -0.11236 | 1.1201 | 1.2782 | ; | Mfg1 | 124 | Elec | Mfg1 | Mfg1_124 | Pkg DX, Tier 0, Mfg1 124 (4 ton, 10 rated SEER) | PkgDX T0 Mfg1 124 4t 10seer
30022 | 0 | 5 | 2 | 10 | 8.6413 | 60900 | 0.7438 | 0.341 | 0.03284 | 0.345 | 0 | 0.1405 | 0 | 55 | 0.89007 | -0.023072 | 0.0004068 | 0.0066113 | -3.9881e-05 | -6.89e-05 | 0.21968 | 0.079955 | -0.0010248 | -0.010653 | -3.7786e-05 | 0.0002163 | -0.44167 | 0.020106 | -6.52e-05 | 0.015912 | 8.8833e-05 | -0.0003026 | 60.4643 | -1.9802 | 0.017037 | 0.13641 | 0.00037599 | -0.0030834 | 1.5914e-08 | 1.0138 | -0.014166 | 0.00037044 | 0.98639 | 0.013799 | -0.00019282 | 5.0421e-06 | 0.983 | 1 | 1 | 1 | 1 | 0.77997 | 0.22003 | 0.30684 | 0.8521 | -0.15894 | 1.0368 | 1.2719 | ; | Mfg1 | 125 | Elec | Mfg1 | Mfg1_125 | Pkg DX, Tier 0, Mfg1 125 (5 ton, 10 rated SEER) | PkgDX T0 Mfg1 125 5t 10seer
30023 | 0 | 2 | 2 | 10 | 8.9922 | 24000 | 0.7339 | 0.3308 | 0.03214 | 0.32212 | 0 | 0.147 | 0 | 55 | 3.4851 | -0.086062 | 0.0008398 | 0.0034897 | -2.9464e-06 | -0.0001247 | -4.4972 | 0.228 | -0.0021306 | -0.015352 | -1.3107e-05 | 0.00021404 | -0.22903 | 0.028611 | -0.0002218 | -0.0029617 | 7.9607e-05 | -2.032e-05 | 107.0114 | -3.3054 | 0.026146 | 0.103 | 0.00020098 | -0.0021244 | 1.6528e-06 | 1.0617 | -0.068471 | 0.0067935 | 0.94167 | 0.061931 | -0.0039942 | 0.00039628 | 0.928 | 1 | 1 | 1 | 1 | 0.43869 | 0.56131 | -0.11512 | 1.371 | -0.25589 | 1.3867 | 1.2925 | ; | Mfg2 | 126 | Elec | Mfg2 | Mfg2_126 | Pkg DX, Tier 0, Mfg2 126 (2 ton, 10 rated SEER) | PkgDX T0 Mfg2 126 2t 10seer
30024 | 0 | 2.5 | 2 | 10 | 8.9873 | 29300 | 0.7341 | 0.3359 | 0.03229 | 0.28828 | 0 | 0.1503 | 0 | 55 | 3.4862 | -0.086493 | 0.0008456 | 0.0036974 | -2.9464e-06 | -0.00012754 | -4.4595 | 0.22639 | -0.002118 | -0.015016 | -1.4929e-05 | 0.00021376 | -0.19721 | 0.027069 | -0.0002122 | -0.0023891 | 7.5411e-05 | -1.846e-05 | 104.4584 | -3.2164 | 0.025404 | 0.093639 | 0.00021563 | -0.0020175 | 1.4532e-06 | 1.0592 | -0.065494 | 0.0062864 | 0.94389 | 0.059433 | -0.0036749 | 0.00035274 | 0.931 | 1 | 1 | 1 | 1 | 0.46437 | 0.53563 | -0.023476 | 1.2089 | -0.18541 | 0.75311 | 1.3148 | ; | Mfg2 | 127 | Elec | Mfg2 | Mfg2_127 | Pkg DX, Tier 0, Mfg2 127 (2.5 ton, 10 rated SEER) | PkgDX T0 Mfg2 127 2.5t 10seer
30025 | 0 | 3 | 2 | 10 | 8.9974 | 36400 | 0.7415 | 0.3278 | 0.0321 | 0.34105 | 0 | 0.1266 | 0 | 55 | 3.4278 | -0.08544 | 0.0008362 | 0.004302 | -6.3393e-06 | -0.00012702 | -4.4769 | 0.22632 | -0.0021146 | -0.014771 | -1.5214e-05 | 0.00021156 | -0.016816 | 0.023467 | -0.0001836 | -0.00408 | 8.4286e-05 | -1.64e-05 | 124.5848 | -3.823 | 0.029969 | 0.11075 | 0.00022128 | -0.0022774 | 1.8149e-06 | 1.0635 | -0.070723 | 0.0071866 | 0.94 | 0.063812 | -0.0042434 | 0.0004312 | 0.926 | 1 | 1 | 1 | 1 | 0.44169 | 0.55831 | -0.22239 | 1.5928 | -0.37045 | 1.2759 | 1.2799 | ; | Mfg2 | 128 | Elec | Mfg2 | Mfg2_128 | Pkg DX, Tier 0, Mfg2 128 (3 ton, 10 rated SEER) | PkgDX T0 Mfg2 128 3t 10seer
30026 | 0 | 3.5 | 2 | 10 | 8.9936 | 43500 | 0.7699 | 0.3329 | 0.03221 | 0.30714 | 0 | 0.0586 | 0 | 55 | 3.3761 | -0.083814 | 0.0008234 | 0.0042525 | -6.1607e-06 | -0.0001265 | -4.4793 | 0.22702 | -0.0021214 | -0.014961 | -1.4393e-05 | 0.000211 | -0.046222 | 0.023811 | -0.000183 | -0.0034971 | 8.2946e-05 | -2.262e-05 | 225.555 | -6.9779 | 0.05475 | 0.26163 | 0.00046232 | -0.0050016 | 1.7325e-06 | 1.0626 | -0.069595 | 0.0069887 | 0.94083 | 0.062871 | -0.0041177 | 0.0004135 | 0.927 | 1 | 1 | 1 | 1 | 0.43674 | 0.56326 | -0.16969 | 1.4783 | -0.30865 | 1.4972 | 1.3023 | ; | Mfg2 | 129 | Elec | Mfg2 | Mfg2_129 | Pkg DX, Tier 0, Mfg2 129 (3.5 ton, 10 rated SEER) | PkgDX T0 Mfg2 129 3.5t 10seer
30027 | 0 | 4 | 2 | 10 | 9.002 | 48000 | 0.7874 | 0.3221 | 0.03195 | 0.37965 | 0 | 0.0075 | 0 | 55 | 3.4035 | -0.08384 | 0.000821 | 0.0037096 | -4.3929e-06 | -0.00012324 | -4.3998 | 0.22447 | -0.002101 | -0.015175 | -1.3714e-05 | 0.0002132 | -0.071794 | 0.023266 | -0.000175 | -0.002893 | 8.1393e-05 | -2.532e-05 | 1569.4897 | -48.2118 | 0.37691 | 1.9039 | 0.0044029 | -0.03941 | 1.7325e-06 | 1.0626 | -0.069595 | 0.0069887 | 0.94083 | 0.062871 | -0.0041177 | 0.0004135 | 0.927 | 1 | 1 | 1 | 1 | 0.47477 | 0.52523 | -0.25873 | 1.7005 | -0.44179 | 0.43592 | 1.2553 | ; | Mfg2 | 130 | Elec | Mfg2 | Mfg2_130 | Pkg DX, Tier 0, Mfg2 130 (4 ton, 10 rated SEER) | PkgDX T0 Mfg2 130 4t 10seer
30028 | 0 | 5 | 2 | 10 | 9.0062 | 60500 | 0.7604 | 0.3213 | 0.03194 | 0.38334 | 0 | 0.0742 | 0 | 55 | 3.435 | -0.084871 | 0.0008292 | 0.0037706 | -4.4107e-06 | -0.00012402 | -4.4274 | 0.22481 | -0.002099 | -0.014892 | -1.3214e-05 | 0.00020768 | -0.018131 | 0.022443 | -0.0001724 | -0.0035502 | 8.2893e-05 | -1.924e-05 | 187.1042 | -5.7835 | 0.045568 | 0.21879 | 0.00043761 | -0.004383 | 1.7325e-06 | 1.0626 | -0.069595 | 0.0069887 | 0.94083 | 0.062871 | -0.0041177 | 0.0004135 | 0.927 | 1 | 1 | 1 | 1 | 0.45092 | 0.54908 | -0.36088 | 1.8839 | -0.52298 | 0.94021 | 1.2529 | ; | Mfg2 | 131 | Elec | Mfg2 | Mfg2_131 | Pkg DX, Tier 0, Mfg2 131 (5 ton, 10 rated SEER) | PkgDX T0 Mfg2 131 5t 10seer
30029 | 0 | 2 | 2 | 10 | 9.2114 | 24530 | 0.72 | 0.3075 | 0.03261 | 0.4132 | 0 | 0.1944 | 0 | 55 | -0.37287 | 0.0066984 | 0.00016016 | 0.021387 | -0.00010533 | -0.00013762 | 0.64647 | 0.10962 | -0.0015672 | -0.034444 | -6.025e-05 | 0.0006065 | 2.4123 | -0.011878 | 0.00013281 | -0.028508 | 0.0002805 | -0.00016275 | 30.0176 | -1.2087 | 0.011926 | 0.22434 | 0.0001629 | -0.0038263 | 9.109e-06 | 1.1057 | -0.12435 | 0.018613 | 0.90333 | 0.10689 | -0.01202 | 0.0017992 | 0.882 | 1 | 1 | 1 | 1 | 0.85324 | 0.14676 | 2.6044 | -3.7487 | 2.1443 | 0.99088 | 1.2278 | ; | Mfg3 | 132 | Elec | Mfg3 | Mfg3_132 | Pkg DX, Tier 0, Mfg3 132 (2 ton, 10 rated SEER) | PkgDX T0 Mfg3 132 2t 10seer
30030 | 0 | 2.5 | 2 | 10 | 9.207 | 30090 | 0.74 | 0.321 | 0.03323 | 0.3197 | 0 | 0.16 | 0 | 55 | -0.29143 | -0.0051734 | 0.00025859 | 0.027674 | -0.00013308 | -0.00014938 | 1.7408 | 0.08803 | -0.0014273 | -0.041937 | -3.5833e-05 | 0.00064037 | 1.696 | 0.0048844 | -2.0313e-05 | -0.02476 | 0.00024375 | -0.0001225 | 33.3572 | -1.4321 | 0.013605 | 0.32069 | -0.00018283 | -0.004131 | 1.115e-05 | 1.1127 | -0.13359 | 0.020918 | 0.8975 | 0.11405 | -0.013693 | 0.0021441 | 0.875 | 1 | 1 | 1 | 1 | 0.86707 | 0.13293 | 2.478 | -3.4706 | 1.9926 | 1 | 1.2867 | ; | Mfg3 | 133 | Elec | Mfg3 | Mfg3_133 | Pkg DX, Tier 0, Mfg3 133 (2.5 ton, 10 rated SEER) | PkgDX T0 Mfg3 133 2.5t 10seer
30031 | 0 | 3 | 2 | 10 | 9.0902 | 36420 | 0.73 | 0.3219 | 0.03295 | 0.3463 | 0 | 0.1776 | 0 | 55 | 0.98023 | -0.0093156 | 0.00025781 | 0.0030247 | -1.6083e-05 | -0.000103 | 0.81474 | 0.094977 | -0.0014195 | -0.028858 | -6.9583e-05 | 0.00055988 | -0.061694 | 0.00025 | 1.5625e-05 | 0.016131 | 2.725e-05 | -0.00012625 | 37.9347 | -1.2586 | 0.011817 | 0.098524 | 0.00062969 | -0.0032517 | 3.5537e-06 | 1.0786 | -0.089321 | 0.010728 | 0.92667 | 0.079097 | -0.0065502 | 0.00078671 | 0.91 | 1 | 1 | 1 | 1 | 0.8682 | 0.1318 | 2.5418 | -3.6024 | 2.0606 | 1 | 1.2702 | ; | Mfg3 | 134 | Elec | Mfg3 | Mfg3_134 | Pkg DX, Tier 0, Mfg3 134 (3 ton, 10 rated SEER) | PkgDX T0 Mfg3 134 3t 10seer
30032 | 0 | 3.5 | 2 | 10 | 9.1927 | 42980 | 0.74 | 0.3081 | 0.03257 | 0.4143 | 0 | 0.143 | 0 | 55 | -0.53776 | -0.011553 | 0.00028906 | 0.035063 | -0.00017067 | -0.000122 | 0.15825 | 0.099711 | -0.001468 | -0.018488 | -0.00012375 | 0.00056938 | 2.6869 | 0.0035766 | -1.9531e-05 | -0.042036 | 0.00031675 | -0.00011063 | 54.132 | -1.8655 | 0.017136 | 0.18175 | 0.00056537 | -0.0043101 | 2.3701e-06 | 1.0691 | -0.077576 | 0.0084321 | 0.935 | 0.069494 | -0.0050424 | 0.00054809 | 0.92 | 1 | 1 | 1 | 1 | 0.84799 | 0.15201 | 3.203 | -5.0035 | 2.8005 | 0.99769 | 1.2275 | ; | Mfg3 | 135 | Elec | Mfg3 | Mfg3_135 | Pkg DX, Tier 0, Mfg3 135 (3.5 ton, 10 rated SEER) | PkgDX T0 Mfg3 135 3.5t 10seer
30033 | 0 | 4 | 2 | 10 | 9.3073 | 49660 | 0.74 | 0.2935 | 0.03222 | 0.4873 | 0 | 0.1336 | 0 | 55 | 2.1286 | -0.028858 | 0.00015703 | -0.011822 | -7.05e-05 | 0.00029213 | 0.72929 | 0.13788 | -0.0019937 | -0.059892 | -4.325e-05 | 0.0009525 | 0.3117 | 0.014128 | 0.00033906 | 0.0026253 | 0.00033367 | -0.000792 | 47.1791 | -1.9436 | 0.019137 | 0.39976 | 0.00022305 | -0.0065756 | 1.084e-05 | 1.1117 | -0.13226 | 0.02058 | 0.89833 | 0.11302 | -0.013446 | 0.0020923 | 0.876 | 1 | 1 | 1 | 1 | 0.87112 | 0.12888 | 2.5668 | -3.6445 | 2.0777 | 0.99968 | 1.1837 | ; | Mfg3 | 136 | Elec | Mfg3 | Mfg3_136 | Pkg DX, Tier 0, Mfg3 136 (4 ton, 10 rated SEER) | PkgDX T0 Mfg3 136 4t 10seer
30034 | 0 | 5 | 2 | 10 | 8.9999 | 61630 | 0.74 | 0.2979 | 0.03245 | 0.5321 | 0 | 0.1398 | 0 | 55 | 3.6878 | -0.070972 | 0.00045781 | -0.013007 | -6.7667e-05 | 0.000292 | 2.9165 | 0.075905 | -0.0015586 | -0.060562 | -5.0667e-05 | 0.00097488 | -1.6058 | 0.071869 | -8.75e-05 | -0.00041167 | 0.00034892 | -0.000774 | 37.0342 | -1.5835 | 0.016127 | 0.35391 | 0.00031145 | -0.0060907 | 1.383e-06 | 1.0583 | -0.064385 | 0.0061013 | 0.94472 | 0.0585 | -0.0035591 | 0.00033727 | 0.932 | 1 | 1 | 1 | 1 | 0.8637 | 0.1363 | 2.5343 | -3.587 | 2.0527 | 0.99986 | 1.1537 | ; | Mfg3 | 137 | Elec | Mfg3 | Mfg3_137 | Pkg DX, Tier 0, Mfg3 137 (5 ton, 10 rated SEER) | PkgDX T0 Mfg3 137 5t 10seer
30035 | 0 | 2 | 2 | 10 | 8.6924 | 23200 | 0.75 | 0.3339 | 0.03448 | 0.3581 | 0 | 0.167 | 0 | 55 | 2.1107 | -0.043105 | 0.00050547 | 0.0012948 | -3.6667e-06 | -9.1375e-05 | 2.52 | 0.0075281 | -0.00044844 | -0.0053365 | -2.725e-05 | 0.0001165 | -0.68509 | 0.032097 | -0.00025469 | 0.0074778 | 5.4583e-05 | -8.25e-05 | 37.29 | -1.1165 | 0.0091501 | 0.0404 | 0.00025372 | -0.001365 | 2.3905e-07 | 1.0333 | -0.035326 | 0.002075 | 0.96778 | 0.033294 | -0.0011383 | 6.6862e-05 | 0.96 | 1 | 1 | 1 | 1 | 0.85991 | 0.14009 | 0.52011 | 0.48707 | -0.0071839 | 0.99644 | 1.2508 | ; | Mfg3 | 138 | Elec | Mfg3 | Mfg3_138 | Pkg DX, Tier 0, Mfg3 138 (2 ton, 10 rated SEER) | PkgDX T0 Mfg3 138 2t 10seer
30036 | 0 | 3 | 2 | 10 | 8.734 | 37100 | 0.74 | 0.3165 | 0.03235 | 0.484 | 0 | 0.137 | 0 | 55 | 1.5122 | -0.026255 | 0.00033672 | 0.0010284 | -6.9167e-06 | -4.7125e-05 | 5.2561 | -0.081134 | 0.00022344 | 0.00051633 | -3.45e-05 | 6.9e-05 | 0.69602 | 0.0021828 | 5.2344e-05 | 9.4042e-05 | 0.00015275 | -0.00023012 | 41.9166 | -1.2179 | 0.0099774 | 0.003467 | 0.00038854 | -0.001248 | 2.3701e-06 | 1.0691 | -0.077576 | 0.0084321 | 0.935 | 0.069494 | -0.0050424 | 0.00054809 | 0.92 | 1 | 1 | 1 | 1 | 0.86523 | 0.13477 | 0.24383 | 1.0089 | -0.2527 | 0.99825 | 1.1846 | ; | Mfg3 | 139 | Elec | Mfg3 | Mfg3_139 | Pkg DX, Tier 0, Mfg3 139 (3 ton, 10 rated SEER) | PkgDX T0 Mfg3 139 3t 10seer
30037 | 0 | 4 | 2 | 10 | 9.1604 | 47600 | 0.74 | 0.3011 | 0.03361 | 0.4537 | 0 | 0.1695 | 0 | 55 | 1.4692 | -0.027759 | 0.00036094 | 0.0033197 | -1.225e-05 | -6.825e-05 | 4.2481 | -0.037887 | -0.00010625 | -0.008497 | 4.4167e-06 | 8.4e-05 | 0.2985 | 0.018719 | -0.00010312 | -0.0041687 | 0.00015383 | -0.00017 | 32.8115 | -1.0581 | 0.0085461 | 0.080126 | -7.9753e-05 | -0.00096996 | 1.677e-05 | 1.1281 | -0.15452 | 0.026431 | 0.88472 | 0.13004 | -0.017813 | 0.0030469 | 0.86 | 1 | 1 | 1 | 1 | 0.87395 | 0.12605 | 0.61305 | 0.27694 | 0.11001 | 0.9986 | 1.1926 | ; | Mfg3 | 140 | Elec | Mfg3 | Mfg3_140 | Pkg DX, Tier 0, Mfg3 140 (4 ton, 10 rated SEER) | PkgDX T0 Mfg3 140 4t 10seer
30038 | 0 | 2 | 1 | 10 | 8.7252 | 24100 | 0.75 | 0.3356 | 0.0332 | 0.3523 | 0 | 0.1347 | 0 | 55 | 1.6981 | -0.031834 | 0.00042031 | 0.0017873 | -6.8333e-06 | -8.8e-05 | 2.0829 | 0.025063 | -0.00055313 | -0.0085583 | -8.3333e-08 | 8.4e-05 | -0.53515 | 0.025508 | -0.00019453 | 0.0090834 | 5.1083e-05 | -9.8125e-05 | 35.0393 | -1.1621 | 0.0096732 | 0.12283 | -2.7855e-05 | -0.0017315 | 2.1981e-07 | 1.0324 | -0.034334 | 0.0019691 | 0.96861 | 0.032405 | -0.0010777 | 6.1809e-05 | 0.961 | 1 | 1 | 1 | 1 | 0.85477 | 0.14523 | 0.4675 | 0.58783 | -0.055325 | 0.99279 | 1.2643 | ; | Mfg3 | 141 | Gas | Mfg3 | Mfg3_141 | Pkg DX, Tier 0, Mfg3 141 (2 ton, 10 rated SEER) | PkgDX T0 Mfg3 141 2t 10seer
30039 | 0 | 2.5 | 1 | 10 | 8.682 | 28900 | 0.76 | 0.3224 | 0.0346 | 0.4297 | 0 | 0.1466 | 0 | 55 | 1.5224 | -0.029317 | 0.00040547 | 0.0038016 | -1.15e-05 | -9.9875e-05 | 2.7396 | 0.010991 | -0.00044844 | -0.011569 | 1.9e-05 | 7.3e-05 | 0.16762 | 0.020538 | -0.00019375 | -0.0019585 | 9.025e-05 | -4.75e-05 | 34.297 | -1.1596 | 0.0092812 | 0.13398 | -0.00024717 | -0.00122 | 7.2622e-09 | 1.0107 | -0.010889 | 0.0002228 | 0.98944 | 0.010668 | -0.00011494 | 2.3518e-06 | 0.987 | 1 | 1 | 1 | 1 | 0.87024 | 0.12976 | 0.59024 | 0.32895 | 0.080814 | 1 | 1.2001 | ; | Mfg3 | 142 | Gas | Mfg3 | Mfg3_142 | Pkg DX, Tier 0, Mfg3 142 (2.5 ton, 10 rated SEER) | PkgDX T0 Mfg3 142 2.5t 10seer
30040 | 0 | 5 | 1 | 10 | 8.8787 | 61200 | 0.76 | 0.3257 | 0.03268 | 0.3803 | 0 | 0.0964 | 0 | 55 | 1.6001 | -0.030869 | 0.00040938 | 0.0031366 | -1.0667e-05 | -8.975e-05 | 1.6472 | 0.027433 | -0.00052266 | -0.0015155 | -1.2583e-05 | 1.8625e-05 | 0.075119 | 0.014012 | -0.00013125 | 0.0042993 | 5.2333e-05 | -4.8e-05 | 75.0661 | -2.2008 | 0.016537 | 0.038451 | 0.00013697 | -0.00090127 | 2.5943e-07 | 1.0341 | -0.036322 | 0.0021837 | 0.96694 | 0.034184 | -0.0012006 | 7.2183e-05 | 0.959 | 1 | 1 | 1 | 1 | 0.87337 | 0.12663 | 0.48529 | 0.57517 | -0.060468 | 1.0026 | 1.2491 | ; | Mfg3 | 143 | Gas | Mfg3 | Mfg3_143 | Pkg DX, Tier 0, Mfg3 143 (5 ton, 10 rated SEER) | PkgDX T0 Mfg3 143 5t 10seer
30041 | 0 | 3.5 | 2 | 10 | 9.13 | 43900 | 0.77221 | 0.314 | 0.03189 | 0.4 | 0 | 0.0435 | 0 | 55 | -3.2769 | 0.099131 | -0.00065563 | 0.016506 | -0.00010957 | 0 | 8.8682 | -0.19117 | 0.0010325 | 0.0014917 | -7.2333e-05 | 0.000129 | -2.7421 | 0.1012 | -0.00061187 | -0.0068038 | 0.000228 | -0.0002705 | -42.8575 | 0.8169 | -0.0024044 | 0.38691 | 0.00039609 | -0.0062973 | 5.5118e-05 | 1.186 | -0.23763 | 0.05157 | 0.83864 | 0.19141 | -0.03835 | 0.0083228 | 0.83864 | 1 | 1 | 1 | 1 | 0.81774 | 0.18226 | 0.54866 | 0.43371 | 0.01763 | 1.8788 | 1.2424 | ; | Mfg5 | 144 | Elec | Mfg5 | Mfg5_144 | Pkg DX, Tier 0, Mfg5 144 (3.5 ton, 10 rated SEER) | PkgDX T0 Mfg5 144 3.5t 10seer
30042 | 0 | 1.5 | 2 | 10 | 8.8 | 18248.47 | 0.6931 | 0.3385 | 0.03288 | 0.317 | 0 | 0.2698 | 0 | 55 | 2.9925 | -0.065495 | 0.000592 | 0.0014957 | -3.6214e-05 | -1.212e-05 | -5.6068 | 0.2734 | -0.002688 | -0.015698 | -6.6304e-05 | 0.00038418 | -3.385 | 0.14716 | -0.0010734 | -0.014737 | 0.00021571 | -0.00018896 | 79.0618 | -2.4509 | 0.019046 | 0.017743 | -3.0457e-05 | -0.00011901 | 1.0118e-06 | 1.0528 | -0.057817 | 0.0050486 | 0.94972 | 0.052931 | -0.0029069 | 0.00025383 | 0.938 | 1 | 1 | 1 | 1 | 0.85324 | 0.14676 | 2.6044 | -3.7487 | 2.1443 | 1 | 1.291 | ; | Mfg6 | 145 | Elec | Mfg6 | Mfg6_145 | Pkg DX, Tier 0, Mfg6 145 (1.5 ton, 10 rated SEER) | PkgDX T0 Mfg6 145 1.5t 10seer
30043 | 0 | 4 | 2 | 10 | 9.04 | 48191.146 | 0.7199 | 0.315 | 0.0332 | 0.401 | 0 | 0.209 | 0 | 55 | 4.36 | -0.1177 | 0.001075 | 0.0063728 | -3.4393e-05 | -9.34e-05 | -2.7291 | 0.18346 | -0.001822 | -0.017257 | -1.1357e-05 | 0.00021336 | -4.7785 | 0.19345 | -0.0014578 | -0.019053 | 0.00024484 | -0.00016314 | 73.8005 | -2.3373 | 0.018289 | 0.063795 | -8.2286e-05 | -0.00056818 | 2.7134e-05 | 1.1489 | -0.18369 | 0.03472 | 0.86779 | 0.15192 | -0.024288 | 0.0045907 | 0.84 | 1 | 1 | 1 | 1 | 0.85324 | 0.14676 | 2.6044 | -3.7487 | 2.1443 | 1 | 1.2311 | ; | Mfg6 | 146 | Elec | Mfg6 | Mfg6_146 | Pkg DX, Tier 0, Mfg6 146 (4 ton, 10 rated SEER) | PkgDX T0 Mfg6 146 4t 10seer
30044 | 0 | 3 | 1 | 10 | 9.48 | 38000 | 0.7368 | 0.2874 | 0.03158 | 0.495 | 0 | 0.1242 | 0 | 55 | 4.8293 | -0.12348 | 0.00098675 | 0.00024908 | -4.9312e-05 | 6.846e-05 | -2.153 | 0.17458 | -0.0018752 | -0.022647 | -2.2437e-05 | 0.0003501 | -4.293 | 0.16814 | -0.001133 | -0.011532 | 0.00025075 | -0.00032264 | 117.9973 | -3.9094 | 0.032047 | 0.20595 | -6.9118e-05 | -0.0028071 | 3.3917e-05 | 1.1597 | -0.19913 | 0.039356 | 0.85918 | 0.16333 | -0.028044 | 0.0055427 | 0.83 | 1 | 1 | 1 | 1 | 0.85324 | 0.14676 | 2.6044 | -3.7487 | 2.1443 | 1 | 1.1851 | ; | Mfg6 | 147 | Gas | Mfg6 | Mfg6_147 | Pkg DX, Tier 0, Mfg6 147 (3 ton, 10 rated SEER) | PkgDX T0 Mfg6 147 3t 10seer
30045 | 0 | 4 | 1 | 10 | 8.74 | 48000 | 0.75 | 0.32 | 0.03333 | 0.446 | 0 | 0.1383 | 0 | 55 | 6.223 | -0.15541 | 0.00125 | -0.011135 | 0 | 9.996e-05 | -4.2144 | 0.21921 | -0.0021525 | -0.013516 | -5.2125e-05 | 0.00030548 | -6.231 | 0.17979 | -0.0011805 | 0.024424 | 9.225e-05 | -0.00041924 | 136.1259 | -4.0648 | 0.032405 | -0.063967 | 0.00089653 | -0.0016124 | 3.5537e-06 | 1.0786 | -0.089321 | 0.010728 | 0.92667 | 0.079097 | -0.0065502 | 0.00078671 | 0.91 | 1 | 1 | 1 | 1 | 0.85324 | 0.14676 | 2.6044 | -3.7487 | 2.1443 | 1 | 1.2001 | ; | Mfg6 | 148 | Gas | Mfg6 | Mfg6_148 | Pkg DX, Tier 0, Mfg6 148 (4 ton, 10 rated SEER) | PkgDX T0 Mfg6 148 4t 10seer
30046 | 0 | 5 | 1 | 10 | 9.09 | 58000 | 0.7414 | 0.3001 | 0.03448 | 0.466 | 0 | 0.1872 | 0 | 55 | 3.3098 | -0.078634 | 0.0006895 | -0.0015203 | -4.3125e-05 | 6.24e-05 | -5.6813 | 0.28309 | -0.0027327 | -0.025671 | -4.3562e-05 | 0.00044202 | -1.6927 | 0.07949 | -0.000342 | -0.003397 | 0.00029425 | -0.000539 | 96.0896 | -3.1118 | 0.026067 | 0.11282 | 0.00039008 | -0.0028047 | 3.5537e-06 | 1.0786 | -0.089321 | 0.010728 | 0.92667 | 0.079097 | -0.0065502 | 0.00078671 | 0.91 | 1 | 1 | 1 | 1 | 0.85324 | 0.14676 | 2.6044 | -3.7487 | 2.1443 | 1 | 1.1766 | ; | Mfg6 | 149 | Gas | Mfg6 | Mfg6_149 | Pkg DX, Tier 0, Mfg6 149 (5 ton, 10 rated SEER) | PkgDX T0 Mfg6 149 5t 10seer
30047 | 0 | 1.5 | 1 | 10 | 8.72 | 17837.208 | 0.7421 | 0.3337 | 0.03364 | 0.36 | 0 | 0.165 | 0 | 55 | 3.9154 | -0.094164 | 0.0007846 | 0.0017382 | -4.9036e-05 | 2.34e-05 | -3.1257 | 0.20235 | -0.0021156 | -0.022905 | -4.5821e-05 | 0.00041704 | -2.6934 | 0.10887 | -0.0007004 | -0.0039919 | 0.00018652 | -0.0002767 | 77.2313 | -2.4632 | 0.020404 | 0.11653 | 0.00025783 | -0.0025435 | 9.0577e-07 | 1.0509 | -0.05566 | 0.0047198 | 0.95139 | 0.051087 | -0.0027057 | 0.00022943 | 0.94 | 1 | 1 | 1 | 1 | 0.85324 | 0.14676 | 2.6044 | -3.7487 | 2.1443 | 1 | 1.2557 | ; | Mfg6 | 150 | Gas | Mfg6 | Mfg6_150 | Pkg DX, Tier 0, Mfg6 150 (1.5 ton, 10 rated SEER) | PkgDX T0 Mfg6 150 1.5t 10seer
30048 | 0 | 2.5 | 1 | 10 | 9.19 | 31050.525 | 0.7617 | 0.3072 | 0.03221 | 0.425 | 0 | 0.079 | 0 | 55 | 3.1 | -0.075055 | 0.0007086 | 0.0017352 | -2.9304e-05 | -2.398e-05 | -5.5588 | 0.2632 | -0.0024696 | -0.018564 | -3.5446e-05 | 0.00032898 | -15.8421 | 0.42685 | -0.0026504 | 0.06579 | 7.5107e-05 | -0.0010664 | 174.888 | -5.4251 | 0.043423 | 0.19601 | 0.0005484 | -0.0045409 | 9.6615e-06 | 1.1077 | -0.12697 | 0.019258 | 0.90167 | 0.10892 | -0.012485 | 0.0018937 | 0.88 | 1 | 1 | 1 | 1 | 0.85324 | 0.14676 | 2.6044 | -3.7487 | 2.1443 | 1 | 1.2235 | ; | Mfg6 | 151 | Gas | Mfg6 | Mfg6_151 | Pkg DX, Tier 0, Mfg6 151 (2.5 ton, 10 rated SEER) | PkgDX T0 Mfg6 151 2.5t 10seer
30049 | 0 | 3 | 1 | 10 | 8.95 | 36606.5 | 0.7569 | 0.317 | 0.03278 | 0.417 | 0 | 0.1069 | 0 | 55 | 0.28832 | 0.0088912 | 8.18e-05 | 0.0047119 | -1.6643e-05 | -8.62e-05 | -6.8822 | 0.30784 | -0.0028438 | -0.020048 | -1.5429e-05 | 0.00032468 | 2.0908 | -0.043733 | 0.0003318 | 0.001599 | 7.2714e-05 | -7.2e-05 | 112.8838 | -3.8458 | 0.033812 | 0.36101 | 0.00025945 | -0.006698 | 3.5537e-06 | 1.0786 | -0.089321 | 0.010728 | 0.92667 | 0.079097 | -0.0065502 | 0.00078671 | 0.91 | 1 | 1 | 1 | 1 | 0.85324 | 0.14676 | 2.6044 | -3.7487 | 2.1443 | 1 | 1.2239 | ; | Mfg6 | 152 | Gas | Mfg6 | Mfg6_152 | Pkg DX, Tier 0, Mfg6 152 (3 ton, 10 rated SEER) | PkgDX T0 Mfg6 152 3t 10seer
30050 | 0 | 3.5 | 1 | 10 | 9.05 | 43168.278 | 0.7707 | 0.311 | 0.03243 | 0.433 | 0 | 0.0633 | 0 | 55 | 4.0774 | -0.11194 | 0.0010286 | 0.0082926 | -4.1821e-05 | -9.504e-05 | -3.2937 | 0.20331 | -0.0020318 | -0.023711 | -1.8875e-05 | 0.0003481 | -3.2336 | 0.14117 | -0.0010578 | -0.012579 | 0.0001762 | -0.0001369 | 161.0901 | -5.3489 | 0.043754 | 0.49635 | -9.2445e-05 | -0.0069826 | 3.5537e-06 | 1.0786 | -0.089321 | 0.010728 | 0.92667 | 0.079097 | -0.0065502 | 0.00078671 | 0.91 | 1 | 1 | 1 | 1 | 0.85324 | 0.14676 | 2.6044 | -3.7487 | 2.1443 | 1 | 1.2164 | ; | Mfg6 | 153 | Gas | Mfg6 | Mfg6_153 | Pkg DX, Tier 0, Mfg6 153 (3.5 ton, 10 rated SEER) | PkgDX T0 Mfg6 153 3.5t 10seer
30051 | 0 | 4 | 1 | 10 | 9.55 | 49692.857 | 0.7666 | 0.2837 | 0.0322 | 0.493 | 0 | 0.0666 | 0 | 55 | 3.4023 | -0.088416 | 0.0008486 | 0.0067803 | -2.4089e-05 | -0.00011226 | -4.9515 | 0.24889 | -0.0023626 | -0.018095 | -1.9732e-05 | 0.00027946 | 0.17969 | 0.09785 | -0.0007908 | -0.055343 | 0.00038846 | -6.82e-05 | 215.2979 | -6.9811 | 0.0572 | 0.37745 | 0.00028879 | -0.0065674 | 3.5537e-06 | 1.0786 | -0.089321 | 0.010728 | 0.92667 | 0.079097 | -0.0065502 | 0.00078671 | 0.91 | 1 | 1 | 1 | 1 | 0.85324 | 0.14676 | 2.6044 | -3.7487 | 2.1443 | 1 | 1.1804 | ; | Mfg6 | 154 | Gas | Mfg6 | Mfg6_154 | Pkg DX, Tier 0, Mfg6 154 (4 ton, 10 rated SEER) | PkgDX T0 Mfg6 154 4t 10seer
30052 | 0 | 5 | 1 | 10 | 8.8 | 60134.845 | 0.7971 | 0.3039 | 0.03326 | 0.533 | 0 | 0.0237 | 0 | 55 | 2.1595 | -0.029536 | 0.0002624 | -0.0065604 | -2.5821e-05 | 7.82e-05 | -5.493 | 0.27362 | -0.002624 | -0.02664 | -3.575e-05 | 0.00043884 | 0.095985 | -0.0020412 | 0.0003192 | 0.0093716 | 0.00022504 | -0.00052056 | 453.1315 | -13.8299 | 0.10882 | 0.61573 | 0.0019464 | -0.014153 | 2.141e-05 | 1.1383 | -0.16866 | 0.030369 | 0.8764 | 0.1407 | -0.020849 | 0.0037539 | 0.85 | 1 | 1 | 1 | 1 | 0.85324 | 0.14676 | 2.6044 | -3.7487 | 2.1443 | 1 | 1.145 | ; | Mfg6 | 155 | Gas | Mfg6 | Mfg6_155 | Pkg DX, Tier 0, Mfg6 155 (5 ton, 10 rated SEER) | PkgDX T0 Mfg6 155 5t 10seer
30053 | 0 | 3 | 1 | 10.1 | 9.1949 | 36765 | 0.8 | 0.3203 | 0.03264 | 0.3333 | 0 | -0.0017 | 0 | 55 | 1.9275 | -0.040484 | 0.00044844 | 0.0025362 | -1.1417e-05 | -5.75e-05 | 1.9605 | 0.026166 | -0.00058906 | -0.0066787 | -1.425e-05 | 0.000109 | -0.33944 | 0.032528 | -0.00020469 | -0.00076192 | 0.00013683 | -0.00017025 | -4682.8478 | 139.7412 | -1.0569 | -3.899 | -0.011616 | 0.08499 | 1.1467e-05 | 1.1137 | -0.13493 | 0.021258 | 0.89667 | 0.11508 | -0.013943 | 0.0021966 | 0.874 | 1 | 1 | 1 | 1 | 0.8776 | 0.1224 | 0.66392 | 0.20618 | 0.1299 | 1 | 1.2814 | ; | Mfg3 | 156 | Gas | Mfg3 | Mfg3_156 | Pkg DX, Tier 0, Mfg3 156 (3 ton, 10.1 rated SEER) | PkgDX T0 Mfg3 156 3t 10.1seer
30054 | 0 | 5 | 2 | 10.1 | 9.35 | 63000 | 0.74603 | 0.3034 | 0.03175 | 0.4175 | 0 | 0.1053 | 0 | 55 | -0.009442 | 0.0023687 | 8.0625e-05 | 0.01483 | -0.00010169 | 0 | 2.8449 | -0.016513 | -0.000215 | 0.0074096 | -5.8238e-05 | 7.875e-06 | -3.3885 | 0.11734 | -0.00068562 | -0.00080739 | 0.0002211 | -0.00036512 | 21.2692 | -0.45381 | 0.0020738 | -0.12183 | 8.053e-05 | 0.0018316 | 4.6194e-05 | 1.176 | -0.22279 | 0.046759 | 0.84641 | 0.18064 | -0.034223 | 0.0071828 | 0.84641 | 1 | 1 | 1 | 1 | 0.81774 | 0.18226 | 0.54866 | 0.43371 | 0.01763 | 1.8788 | 1.2323 | ; | Mfg5 | 157 | Elec | Mfg5 | Mfg5_157 | Pkg DX, Tier 0, Mfg5 157 (5 ton, 10.1 rated SEER) | PkgDX T0 Mfg5 157 5t 10.1seer
30055 | 0 | 2 | 2 | 10.1 | 8.98 | 24006.835 | 0.7251 | 0.322 | 0.03332 | 0.369 | 0 | 0.1989 | 0 | 55 | 3.9556 | -0.10391 | 0.0009576 | 0.006534 | -4.4696e-05 | -8.01e-05 | -3.6878 | 0.2373 | -0.0024012 | -0.032104 | -8.1607e-06 | 0.00042278 | -3.5052 | 0.15745 | -0.0011588 | -0.018261 | 0.00022625 | -0.0001806 | 81.8857 | -2.8854 | 0.024413 | 0.24569 | -0.00027157 | -0.0028349 | 1.5013e-06 | 1.0598 | -0.066236 | 0.0064113 | 0.94333 | 0.060057 | -0.0037534 | 0.00036331 | 0.93 | 1 | 1 | 1 | 1 | 0.85324 | 0.14676 | 2.6044 | -3.7487 | 2.1443 | 1 | 1.2519 | ; | Mfg6 | 158 | Elec | Mfg6 | Mfg6_158 | Pkg DX, Tier 0, Mfg6 158 (2 ton, 10.1 rated SEER) | PkgDX T0 Mfg6 158 2t 10.1seer
30056 | 0 | 3 | 2 | 10.15 | 9.07 | 35491.481 | 0.7042 | 0.3186 | 0.03381 | 0.364 | 0 | 0.2621 | 0 | 55 | 1.9056 | -0.042361 | 0.000496 | 0.0070173 | -4.0839e-05 | -9.302e-05 | -5.1201 | 0.27339 | -0.002657 | -0.025575 | -2.2107e-05 | 0.00037064 | -1.3426 | 0.08257 | -0.000539 | -0.01329 | 0.00022834 | -0.00024638 | 68.69 | -2.2829 | 0.018399 | 0.10564 | -0.00019484 | -0.00088109 | 3.5537e-06 | 1.0786 | -0.089321 | 0.010728 | 0.92667 | 0.079097 | -0.0065502 | 0.00078671 | 0.91 | 1 | 1 | 1 | 1 | 0.85324 | 0.14676 | 2.6044 | -3.7487 | 2.1443 | 1 | 1.2516 | ; | Mfg6 | 159 | Elec | Mfg6 | Mfg6_159 | Pkg DX, Tier 0, Mfg6 159 (3 ton, 10.15 rated SEER) | PkgDX T0 Mfg6 159 3t 10.15seer
30057 | 0 | 3 | 2 | 10.2 | 9.4 | 37600 | 0.74734 | 0.305 | 0.03191 | 0.3917 | 0 | 0.1067 | 0 | 55 | 0.24325 | 0.0044425 | 4.9375e-05 | 0.0091496 | -7.2167e-05 | 3.25e-06 | 4.7919 | -0.06388 | 0.00015563 | -0.00074127 | -9.3095e-06 | -8.75e-06 | -5.7153 | 0.19265 | -0.0013081 | -0.0072593 | 0.00021526 | -0.0002505 | -14.7061 | 0.5468 | -0.0057016 | -0.025307 | -0.00038774 | 0.0017041 | 5.115e-05 | 1.1817 | -0.23123 | 0.04948 | 0.84197 | 0.18677 | -0.036547 | 0.0078206 | 0.84197 | 1 | 1 | 1 | 1 | 0.81774 | 0.18226 | 0.54866 | 0.43371 | 0.01763 | 1.8788 | 1.2477 | ; | Mfg5 | 160 | Elec | Mfg5 | Mfg5_160 | Pkg DX, Tier 0, Mfg5 160 (3 ton, 10.2 rated SEER) | PkgDX T0 Mfg5 160 3t 10.2seer
30058 | 0 | 5 | 2 | 10.25 | 9.4088 | 60800 | 0.76 | 0.2767 | 0.03289 | 0.5621 | 0 | 0.1023 | 0 | 55 | -0.72056 | 0.052047 | -0.00029531 | -0.0038133 | 1.3333e-06 | -1.425e-05 | 3.281 | -0.0045594 | -0.00042344 | -0.011309 | -1.6e-05 | 0.00017975 | 3.6647 | -0.12209 | 0.00091875 | 0.021395 | -1.075e-05 | -8.55e-05 | 54.0404 | -1.6641 | 0.013672 | 0.1018 | 0.0002945 | -0.0023962 | 4.1295e-06 | 1.0824 | -0.094132 | 0.011723 | 0.92333 | 0.082984 | -0.0072168 | 0.00089876 | 0.906 | 1 | 1 | 1 | 1 | 0.80263 | 0.19737 | -0.24489 | 2.0323 | -0.7874 | 0.99969 | 1.1307 | ; | Mfg3 | 161 | Elec | Mfg3 | Mfg3_161 | Pkg DX, Tier 0, Mfg3 161 (5 ton, 10.25 rated SEER) | PkgDX T0 Mfg3 161 5t 10.25seer
30059 | 0 | 4 | 1 | 10.35 | 9.5091 | 48787 | 0.75 | 0.2952 | 0.0328 | 0.4188 | 0 | 0.1241 | 0 | 55 | 1.4838 | -0.027731 | 0.00035313 | 0.0035252 | -1.3583e-05 | -6.65e-05 | 1.7861 | 0.028539 | -0.00057891 | -0.0043947 | -8.5833e-06 | 6.2125e-05 | 0.46251 | 0.016214 | -9.7656e-05 | -0.0063055 | 0.00015525 | -0.00014338 | 40.9642 | -1.2939 | 0.010476 | 0.087243 | 3.3925e-05 | -0.0013978 | 1.3508e-05 | 1.1197 | -0.14303 | 0.023356 | 0.89167 | 0.1213 | -0.015495 | 0.0025302 | 0.868 | 1 | 1 | 1 | 1 | 0.88214 | 0.11786 | 0.51225 | 0.52532 | -0.037578 | 1 | 1.2226 | ; | Mfg3 | 162 | Gas | Mfg3 | Mfg3_162 | Pkg DX, Tier 0, Mfg3 162 (4 ton, 10.35 rated SEER) | PkgDX T0 Mfg3 162 4t 10.35seer
30060 | 0 | 5 | 2 | 10.35 | 8.86 | 63661.461 | 0.7989 | 0.3186 | 0.03142 | 0.449 | 0 | 0.05 | 0 | 55 | 4.3022 | -0.10583 | 0.0009864 | -0.00057056 | -5.0714e-06 | -8.472e-05 | -4.5765 | 0.24267 | -0.0022924 | -0.022833 | -1.3018e-05 | 0.0002977 | -3.6634 | 0.14034 | -0.0009748 | -0.0075142 | 0.00022282 | -0.00026088 | 231.0926 | -7.0544 | 0.054573 | 0.2232 | 0.00070277 | -0.0047091 | 9.0577e-07 | 1.0509 | -0.05566 | 0.0047198 | 0.95139 | 0.051087 | -0.0027057 | 0.00022943 | 0.94 | 1 | 1 | 1 | 1 | 0.85324 | 0.14676 | 2.6044 | -3.7487 | 2.1443 | 1 | 1.2151 | ; | Mfg6 | 163 | Elec | Mfg6 | Mfg6_163 | Pkg DX, Tier 0, Mfg6 163 (5 ton, 10.35 rated SEER) | PkgDX T0 Mfg6 163 5t 10.35seer
30061 | 0 | 4 | 2 | 10.4 | 9.64 | 50100 | 0.7505 | 0.2998 | 0.03194 | 0.3688 | 0 | 0.0993 | 0 | 55 | -1.6063 | 0.047982 | -0.00029938 | 0.017809 | -0.00010593 | 1.25e-07 | -0.51126 | 0.095691 | -0.0010806 | -0.0030936 | 3.8571e-06 | 3.3375e-05 | -1.7001 | 0.084661 | -0.0006175 | -0.013866 | 0.00017112 | -6.7375e-05 | 97.672 | -3.5665 | 0.029161 | 0.50892 | -0.0014664 | -0.0037989 | 8.324e-06 | 1.1028 | -0.12044 | 0.017665 | 0.90584 | 0.10384 | -0.011342 | 0.0016635 | 0.90584 | 1 | 1 | 1 | 1 | 0.81774 | 0.18226 | 0.54866 | 0.43371 | 0.01763 | 1.8788 | 1.2625 | ; | Mfg5 | 164 | Elec | Mfg5 | Mfg5_164 | Pkg DX, Tier 0, Mfg5 164 (4 ton, 10.4 rated SEER) | PkgDX T0 Mfg5 164 4t 10.4seer
30101 | 1 | 3 | 1 | 13 | 11.1482 | 37800 | 0.7196 | 0.2758 | 0.03175 | 0.21417 | 0 | 0.1735 | 0 | 55 | 0.15885 | 0.017274 | -2.12e-05 | -0.0013044 | -1.831e-05 | 1.07e-05 | 1.582 | 0.0357 | -0.000648 | -0.0056716 | -1.4857e-05 | 9.55e-05 | 0.9061 | -0.018137 | 0.0002324 | 0.0088223 | 0.00013343 | -0.0002791 | 31.3525 | -0.96925 | 0.0079677 | 0.037732 | 9.4253e-05 | -0.00088208 | 2.3905e-07 | 1.0333 | -0.035326 | 0.002075 | 0.96778 | 0.033294 | -0.0011383 | 6.6862e-05 | 0.96 | 1 | 1 | 1 | 1 | 0.85185 | 0.14815 | 0.45588 | 0.66176 | -0.11765 | 2.106 | 1.3702 | ; | Mfg1 | 165 | Gas | Mfg1 | Mfg1_165 | Pkg DX, Tier 1, Mfg1 165 (3 ton, 13 rated SEER) | PkgDX T1 Mfg1 165 3t 13seer
30102 | 1 | 4 | 1 | 13 | 11.0305 | 48400 | 0.6942 | 0.2779 | 0.02996 | 0.23586 | 0 | 0.1955 | 0 | 55 | -1.8425 | 0.082088 | -0.0005612 | -0.0062771 | -3.4929e-05 | 0.0001215 | 0.68995 | 0.071238 | -0.0009636 | -0.013184 | -1.4952e-05 | 0.0001964 | 3.1659 | -0.099451 | 0.0010072 | 0.019975 | 0.00019395 | -0.0005769 | 30.2015 | -0.9919 | 0.0082655 | 0.069787 | -3.2019e-05 | -0.00097231 | 4.9061e-07 | 1.0419 | -0.045123 | 0.0032413 | 0.95972 | 0.041965 | -0.0018174 | 0.00013055 | 0.95 | 1 | 1 | 1 | 1 | 0.88464 | 0.11536 | 0.38014 | 0.8474 | -0.22754 | 2.375 | 1.3642 | ; | Mfg1 | 166 | Gas | Mfg1 | Mfg1_166 | Pkg DX, Tier 1, Mfg1 166 (4 ton, 13 rated SEER) | PkgDX T1 Mfg1 166 4t 13seer
30103 | 1 | 5 | 1 | 13 | 11.0559 | 63800 | 0.732 | 0.2557 | 0.03135 | 0.3785 | 0 | 0.1304 | 0 | 55 | -0.94186 | 0.053997 | -0.00032 | -0.0064383 | -1.6095e-05 | 8.13e-05 | 0.74101 | 0.066734 | -0.000942 | -0.010653 | -2.5048e-05 | 0.0001971 | 2.0296 | -0.064611 | 0.000656 | 0.020324 | 0.00013157 | -0.0004342 | 47.1113 | -1.5077 | 0.013015 | 0.079071 | 0.0003567 | -0.002239 | 3.1428e-08 | 1.0172 | -0.017804 | 0.00057405 | 0.98306 | 0.017236 | -0.00030168 | 9.727e-06 | 0.979 | 1 | 1 | 1 | 1 | 0.87282 | 0.12718 | 0.36331 | 0.79657 | -0.15989 | 2.5824 | 1.2607 | ; | Mfg1 | 167 | Gas | Mfg1 | Mfg1_167 | Pkg DX, Tier 1, Mfg1 167 (5 ton, 13 rated SEER) | PkgDX T1 Mfg1 167 5t 13seer
30104 | 1 | 3 | 2 | 13 | 11.1482 | 37800 | 0.7196 | 0.2758 | 0.03175 | 0.21417 | 0 | 0.1735 | 0 | 55 | 0.15885 | 0.017274 | -2.12e-05 | -0.0013044 | -1.831e-05 | 1.07e-05 | 1.582 | 0.0357 | -0.000648 | -0.0056716 | -1.4857e-05 | 9.55e-05 | 0.9061 | -0.018137 | 0.0002324 | 0.0088223 | 0.00013343 | -0.0002791 | 31.3525 | -0.96925 | 0.0079677 | 0.037732 | 9.4253e-05 | -0.00088208 | 2.3905e-07 | 1.0333 | -0.035326 | 0.002075 | 0.96778 | 0.033294 | -0.0011383 | 6.6862e-05 | 0.96 | 1 | 1 | 1 | 1 | 0.85185 | 0.14815 | 0.45588 | 0.66176 | -0.11765 | 2.106 | 1.3702 | ; | Mfg1 | 168 | Elec | Mfg1 | Mfg1_168 | Pkg DX, Tier 1, Mfg1 168 (3 ton, 13 rated SEER) | PkgDX T1 Mfg1 168 3t 13seer
30105 | 1 | 4 | 2 | 13 | 11.0305 | 48400 | 0.6942 | 0.2779 | 0.02996 | 0.23586 | 0 | 0.1955 | 0 | 55 | -1.8425 | 0.082088 | -0.0005612 | -0.0062771 | -3.4929e-05 | 0.0001215 | 0.68995 | 0.071238 | -0.0009636 | -0.013184 | -1.4952e-05 | 0.0001964 | 3.1659 | -0.099451 | 0.0010072 | 0.019975 | 0.00019395 | -0.0005769 | 30.2015 | -0.9919 | 0.0082655 | 0.069787 | -3.2019e-05 | -0.00097231 | 4.9061e-07 | 1.0419 | -0.045123 | 0.0032413 | 0.95972 | 0.041965 | -0.0018174 | 0.00013055 | 0.95 | 1 | 1 | 1 | 1 | 0.88464 | 0.11536 | 0.38014 | 0.8474 | -0.22754 | 2.375 | 1.3642 | ; | Mfg1 | 169 | Elec | Mfg1 | Mfg1_169 | Pkg DX, Tier 1, Mfg1 169 (4 ton, 13 rated SEER) | PkgDX T1 Mfg1 169 4t 13seer
30106 | 1 | 5 | 2 | 13 | 11.0559 | 63800 | 0.732 | 0.2557 | 0.03135 | 0.3785 | 0 | 0.1304 | 0 | 55 | -0.94186 | 0.053997 | -0.00032 | -0.0064383 | -1.6095e-05 | 8.13e-05 | 0.74101 | 0.066734 | -0.000942 | -0.010653 | -2.5048e-05 | 0.0001971 | 2.0296 | -0.064611 | 0.000656 | 0.020324 | 0.00013157 | -0.0004342 | 47.1113 | -1.5077 | 0.013015 | 0.079071 | 0.0003567 | -0.002239 | 3.1428e-08 | 1.0172 | -0.017804 | 0.00057405 | 0.98306 | 0.017236 | -0.00030168 | 9.727e-06 | 0.979 | 1 | 1 | 1 | 1 | 0.87282 | 0.12718 | 0.36331 | 0.79657 | -0.15989 | 2.5824 | 1.2607 | ; | Mfg1 | 170 | Elec | Mfg1 | Mfg1_170 | Pkg DX, Tier 1, Mfg1 170 (5 ton, 13 rated SEER) | PkgDX T1 Mfg1 170 5t 13seer
30107 | 1 | 3 | 2 | 13 | 11.0639 | 37700 | 0.74 | 0.2616 | 0.03183 | 0.3295 | 0 | 0.123 | 0 | 55 | 1.5456 | -0.031759 | 0.00041406 | 0.0032886 | -9e-06 | -7.975e-05 | 0.36172 | 0.11242 | -0.0014555 | -0.033829 | 1.725e-05 | 0.00042387 | -0.18466 | 0.029889 | -0.00018203 | 0.0013531 | 0.00015308 | -0.00023738 | 40.6754 | -1.8258 | 0.01815 | 0.4483 | -0.00022624 | -0.006185 | 5.6403e-09 | 1.0098 | -0.010006 | 0.00018901 | 0.99028 | 0.0098177 | -9.7276e-05 | 1.8376e-06 | 0.988 | 1 | 1 | 1 | 1 | 0.86074 | 0.13926 | 1.3952 | -1.1699 | 0.7747 | 2.5007 | 1.2896 | ; | Mfg3 | 171 | Elec | Mfg3 | Mfg3_171 | Pkg DX, Tier 1, Mfg3 171 (3 ton, 13 rated SEER) | PkgDX T1 Mfg3 171 3t 13seer
30108 | 1 | 3.5 | 2 | 13 | 11.1547 | 45272 | 0.73 | 0.2548 | 0.03092 | 0.3711 | 0 | 0.1237 | 0 | 55 | 1.0758 | -0.016136 | 0.00028672 | 0.0024206 | -7.4167e-06 | -6.9875e-05 | 1.756 | 0.070656 | -0.0011406 | -0.034296 | 1.925e-05 | 0.0004265 | 0.35663 | 0.0090187 | -1.25e-05 | 0.0041187 | 0.00014633 | -0.000254 | 16.2593 | -1.1014 | 0.012743 | 0.46436 | -0.00025578 | -0.0063588 | 8.5699e-08 | 1.0239 | -0.024963 | 0.0010884 | 0.97667 | 0.02389 | -0.00058246 | 2.5396e-05 | 0.971 | 1 | 1 | 1 | 1 | 0.85642 | 0.14358 | 1.7844 | -1.9584 | 1.174 | 2.4966 | 1.2689 | ; | Mfg3 | 172 | Elec | Mfg3 | Mfg3_172 | Pkg DX, Tier 1, Mfg3 172 (3.5 ton, 13 rated SEER) | PkgDX T1 Mfg3 172 3.5t 13seer
30109 | 1 | 3 | 1 | 13 | 11.0305 | 37799 | 0.72 | 0.2609 | 0.03175 | 0.3416 | 0 | 0.1724 | 0 | 55 | 1.5525 | -0.031853 | 0.00041406 | 0.0032324 | -8.8333e-06 | -7.925e-05 | 5.6428 | -0.089078 | 0.00032031 | -0.001709 | -5.75e-06 | 1.6e-05 | -0.18463 | 0.029811 | -0.00018047 | 0.0013931 | 0.00015317 | -0.00023838 | 15.7129 | -0.56257 | 0.0052523 | 0.071648 | 2.4747e-05 | -0.0011985 | 3.4572e-10 | 1.0039 | -0.0039342 | 3.0245e-05 | 0.99611 | 0.0039041 | -1.53e-05 | 1.1762e-07 | 0.995 | 1 | 1 | 1 | 1 | 0.86111 | 0.13889 | 0.60648 | 0.26676 | 0.12676 | 2.4982 | 1.282 | ; | Mfg3 | 173 | Gas | Mfg3 | Mfg3_173 | Pkg DX, Tier 1, Mfg3 173 (3 ton, 13 rated SEER) | PkgDX T1 Mfg3 173 3t 13seer
30110 | 1 | 3.5 | 1 | 13 | 11.1537 | 45275 | 0.73 | 0.2548 | 0.03026 | 0.3796 | 0 | 0.1045 | 0 | 55 | 1.0513 | -0.015355 | 0.00028047 | 0.0023717 | -7.4167e-06 | -6.9125e-05 | 6.1387 | -0.1109 | 0.00053203 | 0.0016576 | -5.6667e-06 | -3.1875e-05 | 0.36362 | 0.0083562 | -6.25e-06 | 0.004446 | 0.00014533 | -0.000256 | 7.0817 | -0.24934 | 0.0025979 | 0.073892 | 4.7169e-05 | -0.0013328 | 7.6416e-08 | 1.023 | -0.024015 | 0.0010121 | 0.9775 | 0.023018 | -0.00054034 | 2.2771e-05 | 0.972 | 1 | 1 | 1 | 1 | 0.86036 | 0.13964 | 0.39031 | 0.70574 | -0.096054 | 2.5021 | 1.2686 | ; | Mfg3 | 174 | Gas | Mfg3 | Mfg3_174 | Pkg DX, Tier 1, Mfg3 174 (3.5 ton, 13 rated SEER) | PkgDX T1 Mfg3 174 3.5t 13seer
30111 | 1 | 5 | 1 | 13 | 11.3599 | 63900 | 0.74 | 0.259 | 0.0313 | 0.298 | 0 | 0.1081 | 0 | 55 | 1.5743 | -0.030098 | 0.00038047 | 0.0029085 | -9e-06 | -7.2375e-05 | 6.8993 | -0.12764 | 0.00059063 | 0.000464 | -1.675e-05 | 1.7e-05 | -0.51307 | 0.035767 | -0.00022109 | 0.00032896 | 0.00014325 | -0.00019088 | 30.1836 | -0.97745 | 0.0086587 | 0.061148 | 0.00021953 | -0.0016267 | 2.3701e-06 | 1.0691 | -0.077576 | 0.0084321 | 0.935 | 0.069494 | -0.0050424 | 0.00054809 | 0.92 | 1 | 1 | 1 | 1 | 0.87089 | 0.12911 | 0.4216 | 0.62386 | -0.045468 | 2.7712 | 1.3144 | ; | Mfg3 | 175 | Gas | Mfg3 | Mfg3_175 | Pkg DX, Tier 1, Mfg3 175 (5 ton, 13 rated SEER) | PkgDX T1 Mfg3 175 5t 13seer
30112 | 1 | 2 | 2 | 13 | 11.49 | 24923.2111 | 0.7312 | 0.2801 | 0.0321 | 0.118 | 0 | 0.1528 | 0 | 55 | 2.7553 | -0.058004 | 0.0005376 | 0.0027074 | -4.7286e-05 | -1.772e-05 | -1.1947 | 0.1632 | -0.0018546 | -0.03418 | -9.8036e-06 | 0.0004589 | -1.1185 | 0.082918 | -0.0005944 | -0.022358 | 0.00025498 | -0.00014862 | 55.755 | -2.0151 | 0.017519 | 0.2511 | -0.00013733 | -0.0032998 | 7.3557e-06 | 1.0988 | -0.1153 | 0.016441 | 0.90917 | 0.099812 | -0.010473 | 0.0014934 | 0.889 | 1 | 1 | 1 | 1 | 0.85324 | 0.14676 | 2.6044 | -3.7487 | 2.1443 | 1 | 1.4397 | ; | Mfg6 | 176 | Elec | Mfg6 | Mfg6_176 | Pkg DX, Tier 1, Mfg6 176 (2 ton, 13 rated SEER) | PkgDX T1 Mfg6 176 2t 13seer
30113 | 1 | 2.5 | 2 | 13 | 11.75 | 31403.4175 | 0.7134 | 0.2698 | 0.03184 | 0.148 | 0 | 0.1921 | 0 | 55 | 4.074 | -0.089612 | 0.0007004 | -0.0021322 | -4.4893e-05 | 6.184e-05 | -3.3546 | 0.22528 | -0.0024014 | -0.028047 | -4.7768e-05 | 0.00049278 | -2.1632 | 0.095338 | -0.0005634 | -0.010542 | 0.00022536 | -0.00027144 | 104.7739 | -3.425 | 0.027859 | 0.13464 | -4.3481e-05 | -0.0018473 | 7.1271e-06 | 1.0979 | -0.11402 | 0.016141 | 0.91 | 0.098808 | -0.010262 | 0.0014527 | 0.89 | 1 | 1 | 1 | 1 | 0.85324 | 0.14676 | 2.6044 | -3.7487 | 2.1443 | 1 | 1.418 | ; | Mfg6 | 177 | Elec | Mfg6 | Mfg6_177 | Pkg DX, Tier 1, Mfg6 177 (2.5 ton, 13 rated SEER) | PkgDX T1 Mfg6 177 2.5t 13seer
30114 | 1 | 3 | 2 | 13 | 11.14 | 37155.2996 | 0.747 | 0.2692 | 0.0323 | 0.258 | 0 | 0.1181 | 0 | 55 | 4.5792 | -0.10955 | 0.0008662 | -0.0025475 | -4.0804e-05 | 7.586e-05 | -2.3869 | 0.18482 | -0.0020104 | -0.024954 | -3.5393e-05 | 0.00042712 | -5.0702 | 0.16848 | -0.0010938 | 0.0025428 | 0.00020623 | -0.00037878 | 107.2838 | -3.5529 | 0.030269 | 0.21301 | 0.00032792 | -0.0042916 | 2.4733e-06 | 1.0701 | -0.078732 | 0.0086493 | 0.93417 | 0.070447 | -0.0051832 | 0.00056942 | 0.919 | 1 | 1 | 1 | 1 | 0.85324 | 0.14676 | 2.6044 | -3.7487 | 2.1443 | 1 | 1.3361 | ; | Mfg6 | 178 | Elec | Mfg6 | Mfg6_178 | Pkg DX, Tier 1, Mfg6 178 (3 ton, 13 rated SEER) | PkgDX T1 Mfg6 178 3t 13seer
30115 | 1 | 3.5 | 2 | 13 | 11.14 | 44060.0778 | 0.7095 | 0.2749 | 0.02951 | 0.239 | 0 | 0.1392 | 0 | 55 | 4.6392 | -0.11392 | 0.0010078 | -0.0019783 | -4.0714e-06 | -4.808e-05 | -3.6306 | 0.21152 | -0.002079 | -0.016056 | -1.825e-05 | 0.00023272 | -5.1747 | 0.17411 | -0.001241 | -0.00031768 | 0.00017457 | -0.00023016 | 161.7292 | -5.1152 | 0.040274 | 0.063516 | -2.6144e-05 | -0.00072282 | 5.1162e-06 | 1.0882 | -0.10147 | 0.013298 | 0.91834 | 0.088867 | -0.0082867 | 0.001086 | 0.9 | 1 | 1 | 1 | 1 | 0.85324 | 0.14676 | 2.6044 | -3.7487 | 2.1443 | 1 | 1.3645 | ; | Mfg6 | 179 | Elec | Mfg6 | Mfg6_179 | Pkg DX, Tier 1, Mfg6 179 (3.5 ton, 13 rated SEER) | PkgDX T1 Mfg6 179 3.5t 13seer
30116 | 1 | 4 | 2 | 13 | 10.98 | 48995.238 | 0.753 | 0.2629 | 0.03266 | 0.329 | 0 | 0.1129 | 0 | 55 | 5.4172 | -0.14114 | 0.0012126 | -0.00070425 | -1.8661e-05 | -2.65e-05 | -4.0055 | 0.20254 | -0.0019512 | -0.0066689 | -6.5321e-05 | 0.00022268 | -5.7468 | 0.19169 | -0.0012952 | 0.0034797 | 0.00020654 | -0.00038912 | 158.3602 | -4.4465 | 0.033136 | -0.2147 | 0.001052 | 0.0004261 | 1.5854e-07 | 1.0291 | -0.030734 | 0.0016046 | 0.97167 | 0.029159 | -0.0008708 | 4.5463e-05 | 0.965 | 1 | 1 | 1 | 1 | 0.85324 | 0.14676 | 2.6044 | -3.7487 | 2.1443 | 1 | 1.2842 | ; | Mfg6 | 180 | Elec | Mfg6 | Mfg6_180 | Pkg DX, Tier 1, Mfg6 180 (4 ton, 13 rated SEER) | PkgDX T1 Mfg6 180 4t 13seer
30117 | 1 | 4 | 2 | 13.25 | 11.3952 | 50294 | 0.71 | 0.2661 | 0.02883 | 0.2614 | 0 | 0.1176 | 0 | 55 | 0.80959 | -0.0076844 | 0.00021719 | 0.0023425 | -1.1167e-05 | -6.15e-05 | 1.1302 | 0.094981 | -0.0013437 | -0.037268 | 2.675e-05 | 0.00044575 | 0.67636 | 8.5937e-05 | 6.0156e-05 | 0.00092496 | 0.00015275 | -0.00022288 | 35.0723 | -1.8967 | 0.020071 | 0.59006 | -0.00045319 | -0.0077069 | 4.0828e-07 | 1.0395 | -0.042382 | 0.0028938 | 0.96194 | 0.039558 | -0.0016129 | 0.00011012 | 0.953 | 1 | 1 | 1 | 1 | 0.87964 | 0.12036 | 2.107 | -2.3226 | 1.2157 | 2.5078 | 1.3537 | ; | Mfg3 | 181 | Elec | Mfg3 | Mfg3_181 | Pkg DX, Tier 1, Mfg3 181 (4 ton, 13.25 rated SEER) | PkgDX T1 Mfg3 181 4t 13.25seer
30118 | 1 | 4 | 1 | 13.25 | 11.3952 | 50294 | 0.71 | 0.2661 | 0.02883 | 0.2614 | 0 | 0.1176 | 0 | 55 | 0.80959 | -0.0076844 | 0.00021719 | 0.0023425 | -1.1167e-05 | -6.15e-05 | 7.275 | -0.1418 | 0.00079844 | 0.0014484 | 1.5e-05 | -9.925e-05 | 0.67636 | 8.5937e-05 | 6.0156e-05 | 0.00092496 | 0.00015275 | -0.00022288 | 6.3295 | -0.261 | 0.0019114 | 0.049245 | -0.00032598 | 0.00028927 | 4.0828e-07 | 1.0395 | -0.042382 | 0.0028938 | 0.96194 | 0.039558 | -0.0016129 | 0.00011012 | 0.953 | 1 | 1 | 1 | 1 | 0.87964 | 0.12036 | -0.18391 | 1.7661 | -0.58215 | 2.5078 | 1.3537 | ; | Mfg3 | 182 | Gas | Mfg3 | Mfg3_182 | Pkg DX, Tier 1, Mfg3 182 (4 ton, 13.25 rated SEER) | PkgDX T1 Mfg3 182 4t 13.25seer
30119 | 1 | 5 | 2 | 13.3 | 11.5216 | 63900 | 0.74 | 0.259 | 0.0313 | 0.2685 | 0 | 0.1081 | 0 | 55 | 1.5743 | -0.030098 | 0.00038047 | 0.0029085 | -9e-06 | -7.2375e-05 | 6.8993 | -0.12764 | 0.00059062 | 0.000464 | -1.675e-05 | 1.7e-05 | -0.51307 | 0.035767 | -0.00022109 | 0.00032896 | 0.00014325 | -0.00019087 | 30.0621 | -0.975 | 0.0086452 | 0.061923 | 0.00021781 | -0.001633 | 9.0577e-07 | 1.0509 | -0.05566 | 0.0047198 | 0.95139 | 0.051087 | -0.0027057 | 0.00022943 | 0.94 | 1 | 1 | 1 | 1 | 0.87089 | 0.12911 | 0.4216 | 0.62386 | -0.045468 | 2.5074 | 1.3345 | ; | Mfg3 | 183 | Elec | Mfg3 | Mfg3_183 | Pkg DX, Tier 1, Mfg3 183 (5 ton, 13.3 rated SEER) | PkgDX T1 Mfg3 183 5t 13.3seer
30120 | 1 | 5 | 1 | 13.4 | 11.12 | 59000 | 0.7288 | 0.2545 | 0.03051 | 0.386 | 0 | 0.115 | 0 | 55 | 3.4892 | -0.084881 | 0.000983 | 0.0023818 | 3.6321e-05 | -0.00027792 | -5.1114 | 0.2579 | -0.0024188 | -0.015055 | -3.3232e-05 | 0.00022314 | -2.8493 | 0.11019 | -0.0008576 | -0.0041863 | 0.00018843 | -0.00015504 | 210.6596 | -6.4525 | 0.049972 | -0.096808 | 0.00054779 | 0.00040593 | 8.0737e-06 | 1.1018 | -0.11915 | 0.017355 | 0.90667 | 0.10283 | -0.011121 | 0.0016198 | 0.886 | 1 | 1 | 1 | 1 | 0.85324 | 0.14676 | 2.6044 | -3.7487 | 2.1443 | 2.5 | 1.2626 | ; | Mfg6 | 184 | Gas | Mfg6 | Mfg6_184 | Pkg DX, Tier 1, Mfg6 184 (5 ton, 13.4 rated SEER) | PkgDX T1 Mfg6 184 5t 13.4seer
30121 | 1 | 4 | 1 | 13.45 | 11.59 | 49000 | 0.7143 | 0.2368 | 0.03265 | 0.399 | 0 | 0.2099 | 0 | 55 | 4.4065 | -0.096599 | 0.0007346 | -0.0072954 | -5.8286e-05 | 0.00015508 | -2.481 | 0.21094 | -0.0023998 | -0.035387 | -8.1661e-05 | 0.00066294 | -4.3405 | 0.15215 | -0.000907 | 0.00016264 | 0.00027814 | -0.00051964 | 92.9341 | -2.9639 | 0.023798 | 0.03559 | 0.000228 | -0.00088273 | 3.6918e-06 | 1.0795 | -0.090518 | 0.010973 | 0.92583 | 0.080066 | -0.0067134 | 0.0008138 | 0.909 | 1 | 1 | 1 | 1 | 0.85324 | 0.14676 | 2.6044 | -3.7487 | 2.1443 | 2.5 | 1.2369 | ; | Mfg6 | 185 | Gas | Mfg6 | Mfg6_185 | Pkg DX, Tier 1, Mfg6 185 (4 ton, 13.45 rated SEER) | PkgDX T1 Mfg6 185 4t 13.45seer
30122 | 1 | 3 | 1 | 13.5 | 11.74 | 37000 | 0.7027 | 0.2491 | 0.03243 | 0.291 | 0 | 0.2345 | 0 | 55 | 4.6904 | -0.10645 | 0.0008648 | -0.0066644 | -4.3429e-05 | 9.192e-05 | -1.216 | 0.17141 | -0.0020002 | -0.03418 | -4.1214e-05 | 0.00052312 | -3.7995 | 0.13305 | -0.0008548 | 0.0042134 | 0.00021848 | -0.00041626 | 76.5102 | -2.4303 | 0.019291 | 0.021501 | 9.6313e-05 | -0.00034366 | 7.1271e-06 | 1.0979 | -0.11402 | 0.016141 | 0.91 | 0.098808 | -0.010262 | 0.0014527 | 0.89 | 1 | 1 | 1 | 1 | 0.85324 | 0.14676 | 2.6044 | -3.7487 | 2.1443 | 2.5 | 1.3121 | ; | Mfg6 | 186 | Gas | Mfg6 | Mfg6_186 | Pkg DX, Tier 1, Mfg6 186 (3 ton, 13.5 rated SEER) | PkgDX T1 Mfg6 186 3t 13.5seer
30123 | 1 | 3 | 2 | 13 | 11.8 | 37500 | 0.744 | 0.2366 | 0.032 | 0.3733 | 0 | 0.1175 | 0 | 55 | 3.4845 | -0.088379 | 0.00071563 | 0.0037093 | -8.4452e-05 | 9.9875e-05 | 3.9847 | -0.045742 | -0.00015625 | 0.0002339 | -0.0001399 | 0.000318 | -4.1054 | 0.12164 | -0.00060125 | 0.017797 | 0.00020479 | -0.00060975 | 17.6991 | 0.011207 | 6.3397e-05 | -0.33183 | 0.0022732 | -0.0010314 | 1.8527e-05 | 1.1321 | -0.16013 | 0.027974 | 0.8814 | 0.13428 | -0.018993 | 0.003318 | 0.8814 | 1 | 1 | 1 | 1 | 0.81867 | 0.18133 | 0.50538 | 0.5233 | -0.028674 | 0.97264 | 1.2591 | ; | Mfg4 | 187 | Elec | Mfg4 | Mfg4_187 | Pkg DX, Tier 1, Mfg4 187 (3 ton, 13 rated SEER) | PkgDX T1 Mfg4 187 3t 13seer
30124 | 1 | 4 | 2 | 13.1 | 11.5 | 49100 | 0.72709 | 0.2433 | 0.03157 | 0.3819 | 0 | 0.1492 | 0 | 55 | 10.7687 | -0.28276 | 0.00224 | -0.013204 | 4.5548e-05 | -5.25e-06 | 12.1228 | -0.26458 | 0.0016638 | -0.014882 | 6.1357e-05 | -3.75e-07 | -11.9221 | 0.33576 | -0.0023375 | 0.029468 | 4.7143e-05 | -0.0003625 | -14.3774 | 0.4796 | -0.0047281 | 0.0065783 | -0.00042294 | 0.00123 | 8.324e-06 | 1.1028 | -0.12044 | 0.017665 | 0.90584 | 0.10384 | -0.011342 | 0.0016635 | 0.90584 | 1 | 1 | 1 | 1 | 0.81788 | 0.18212 | 0.56012 | 0.41776 | 0.022123 | 1.1004 | 1.2568 | ; | Mfg4 | 188 | Elec | Mfg4 | Mfg4_188 | Pkg DX, Tier 1, Mfg4 188 (4 ton, 13.1 rated SEER) | PkgDX T1 Mfg4 188 4t 13.1seer
30125 | 1 | 5 | 2 | 13 | 11.44 | 60000 | 0.73333 | 0.2503 | 0.03167 | 0.3426 | 0 | 0.1356 | 0 | 55 | 2.8809 | -0.066985 | 0.00062313 | 0.00049535 | -2.8929e-05 | 4.25e-06 | 3.7865 | -0.037254 | -2.8125e-05 | -0.00027762 | -1.5048e-05 | 0 | -3.4686 | 0.10503 | -0.00064187 | 0.014409 | 0.00011817 | -0.00033462 | 16.5482 | -0.34828 | 0.0015373 | -0.078063 | 7.6226e-07 | 0.001311 | 2.3701e-06 | 1.0691 | -0.077576 | 0.0084321 | 0.935 | 0.069494 | -0.0050424 | 0.00054809 | 0.935 | 1 | 1 | 1 | 1 | 0.81858 | 0.18142 | 0.5545 | 0.42769 | 0.017805 | 1.9597 | 1.282 | ; | Mfg4 | 189 | Elec | Mfg4 | Mfg4_189 | Pkg DX, Tier 1, Mfg4 189 (5 ton, 13 rated SEER) | PkgDX T1 Mfg4 189 5t 13seer
30126 | 1 | 0.25 | 1 | 13 | 11.8 | 37500 | 0.744 | 0.2366 | 0.032 | 0.3733 | 0 | 0.1175 | 0 | 55 | 3.4845 | -0.088379 | 0.00071563 | 0.0037093 | -8.4452e-05 | 9.9875e-05 | 3.9847 | -0.045742 | -0.00015625 | 0.0002339 | -0.0001399 | 0.000318 | -4.1054 | 0.12164 | -0.00060125 | 0.017797 | 0.00020479 | -0.00060975 | 17.6991 | 0.011207 | 6.3397e-05 | -0.33183 | 0.0022732 | -0.0010314 | 1.8527e-05 | 1.1321 | -0.16013 | 0.027974 | 0.8814 | 0.13428 | -0.018993 | 0.003318 | 0.8814 | 1 | 1 | 1 | 1 | 0.81867 | 0.18133 | 0.50538 | 0.5233 | -0.028674 | 0.97264 | 1.2591 | ; | Mfg4 | 190 | Gas | Mfg4 | Mfg4_190 | Pkg DX, Tier 1, Mfg4 190 (0.25 ton, 13 rated SEER) | PkgDX T1 Mfg4 190 0.25t 13seer
30127 | 1 | 0.33 | 1 | 13.1 | 11.5 | 49100 | 0.72709 | 0.2433 | 0.03157 | 0.3819 | 0 | 0.1492 | 0 | 55 | 10.7687 | -0.28276 | 0.00224 | -0.013204 | 4.5548e-05 | -5.25e-06 | 12.1228 | -0.26458 | 0.0016638 | -0.014882 | 6.1357e-05 | -3.75e-07 | -11.9221 | 0.33576 | -0.0023375 | 0.029468 | 4.7143e-05 | -0.0003625 | -14.3774 | 0.4796 | -0.0047281 | 0.0065783 | -0.00042294 | 0.00123 | 8.324e-06 | 1.1028 | -0.12044 | 0.017665 | 0.90584 | 0.10384 | -0.011342 | 0.0016635 | 0.90584 | 1 | 1 | 1 | 1 | 0.81788 | 0.18212 | 0.56012 | 0.41776 | 0.022123 | 1.1004 | 1.2568 | ; | Mfg4 | 191 | Gas | Mfg4 | Mfg4_191 | Pkg DX, Tier 1, Mfg4 191 (0.33 ton, 13.1 rated SEER) | PkgDX T1 Mfg4 191 0.33t 13.1seer
30128 | 1 | 0.42 | 1 | 13 | 11.44 | 60000 | 0.73333 | 0.2503 | 0.03167 | 0.3426 | 0 | 0.1356 | 0 | 55 | 2.8809 | -0.066985 | 0.00062313 | 0.00049535 | -2.8929e-05 | 4.25e-06 | 3.7865 | -0.037254 | -2.8125e-05 | -0.00027762 | -1.5048e-05 | 0 | -3.4686 | 0.10503 | -0.00064187 | 0.014409 | 0.00011817 | -0.00033462 | 16.5482 | -0.34828 | 0.0015373 | -0.078063 | 7.6226e-07 | 0.001311 | 2.3701e-06 | 1.0691 | -0.077576 | 0.0084321 | 0.935 | 0.069494 | -0.0050424 | 0.00054809 | 0.935 | 1 | 1 | 1 | 1 | 0.81858 | 0.18142 | 0.5545 | 0.42769 | 0.017805 | 1.9597 | 1.282 | ; | Mfg4 | 192 | Gas | Mfg4 | Mfg4_192 | Pkg DX, Tier 1, Mfg4 192 (0.42 ton, 13 rated SEER) | PkgDX T1 Mfg4 192 0.42t 13seer
30201 | 2 | 2 | 1 | 14 | 12.0177 | 24900 | 0.7189 | 0.2481 | 0.03213 | 0.255 | 0 | 0.1851 | 0 | 55 | 0.69045 | -0.0038087 | 0.00021367 | 0.002382 | -8.869e-06 | -8.4943e-05 | 3.2479 | -0.011505 | -0.000298 | -0.007342 | -1.4607e-05 | 0.0001084 | 0.085415 | 0.0071172 | 8.1e-05 | 0.0051965 | 0.00020461 | -0.00035603 | 15.5841 | -0.53276 | 0.0050035 | 0.065276 | 0.00013784 | -0.0013819 | 4.188e-05 | 1.1707 | -0.21497 | 0.044277 | 0.85058 | 0.17495 | -0.032126 | 0.0066169 | 0.82 | 1 | 1 | 1 | 1 | 0.81526 | 0.18474 | 0.68715 | 0.13408 | 0.17877 | 1.0946 | 1.3392 | ; | Mfg1 | 193 | Gas | Mfg1 | Mfg1_193 | Pkg DX, Tier 2, Mfg1 193 (2 ton, 14 rated SEER) | PkgDX T2 Mfg1 193 2t 14seer
30202 | 2 | 3 | 1 | 14 | 11.7688 | 36000 | 0.725 | 0.2551 | 0.03333 | 0.23833 | 0 | 0.1994 | 0 | 55 | 0.77481 | -0.0097725 | 0.000277 | 0.0048806 | -1.4375e-05 | -0.00010957 | 35.0656 | -0.6732 | 0.00332 | -0.18352 | 0.00030673 | 0.001697 | 0.4913 | 0.0032467 | 5.4333e-05 | 0.0016858 | 0.00018035 | -0.00027346 | -43.2502 | 0.71534 | -0.0027113 | 0.38791 | -0.00073204 | -0.0034174 | 3.5537e-06 | 1.0786 | -0.089321 | 0.010728 | 0.92667 | 0.079097 | -0.0065502 | 0.00078671 | 0.91 | 1 | 1 | 1 | 1 | 0.82778 | 0.17222 | 0.7931 | -0.068966 | 0.27586 | 1.4429 | 1.3447 | ; | Mfg1 | 194 | Gas | Mfg1 | Mfg1_194 | Pkg DX, Tier 2, Mfg1 194 (3 ton, 14 rated SEER) | PkgDX T2 Mfg1 194 3t 14seer
30203 | 2 | 5 | 1 | 14 | 12.0391 | 60300 | 0.6932 | 0.2456 | 0.02819 | 0.30647 | 0 | 0.1482 | 0 | 55 | 0.27139 | 0.0042667 | 0.00015433 | 0.0058883 | -2.406e-05 | -9.3057e-05 | 2.8637 | -0.008743 | -0.000264 | -0.0024261 | -2.0054e-05 | 5.0057e-05 | 0.67902 | -0.0018999 | 9.5333e-05 | 0.00085893 | 0.0001854 | -0.00027251 | 15.5043 | -0.47623 | 0.0042994 | 0.030314 | 0.00018497 | -0.0010127 | 7.1271e-06 | 1.0979 | -0.11402 | 0.016141 | 0.91 | 0.098808 | -0.010262 | 0.0014527 | 0.89 | 1 | 1 | 1 | 1 | 0.83381 | 0.16619 | 1.2847 | -0.99912 | 0.71443 | 2.1702 | 1.3294 | ; | Mfg1 | 195 | Gas | Mfg1 | Mfg1_195 | Pkg DX, Tier 2, Mfg1 195 (5 ton, 14 rated SEER) | PkgDX T2 Mfg1 195 5t 14seer
30204 | 2 | 4 | 1 | 14.1 | 12.0121 | 48900 | 0.726 | 0.2457 | 0.03272 | 0.26813 | 0 | 0.1819 | 0 | 55 | -0.099543 | 0.014793 | 9.5667e-05 | 0.0064803 | -1.9619e-05 | -0.00011934 | 2.0621 | 0.023924 | -0.00056267 | -0.007842 | -1.7113e-05 | 0.00011943 | 0.99012 | -0.0097197 | 0.00015267 | -0.0010567 | 0.00019402 | -0.00026314 | 16.3515 | -0.56147 | 0.0051737 | 0.080058 | 0.00010847 | -0.0014992 | 3.5537e-06 | 1.0786 | -0.089321 | 0.010728 | 0.92667 | 0.079097 | -0.0065502 | 0.00078671 | 0.91 | 1 | 1 | 1 | 1 | 0.84049 | 0.15951 | 0.46479 | 0.60282 | -0.067606 | 2.0547 | 1.3265 | ; | Mfg1 | 196 | Gas | Mfg1 | Mfg1_196 | Pkg DX, Tier 2, Mfg1 196 (4 ton, 14.1 rated SEER) | PkgDX T2 Mfg1 196 4t 14.1seer
; Indep. ; 1: ;; Dependents 1: Mult Compressor A/C, 6 - 10 ton Units, from: "All 2 Comp Pkg Unit Perf Curves (2008 DEER Rev 1).xls" | ;
31001 | 0 | 7.5 | 1 | 10.1 | 10.1 | 89000 | 0.7685 | 0.25512 | 0.03371 | 0.376 | 0.0073034 | 0.1038 | 0 | 55 | 1.0371 | -0.018772 | 0.0001756 | 0.0066389 | -8.8548e-05 | 9.44e-05 | -1.6494 | 0.11705 | -0.0013328 | 0.0036202 | -0.00011136 | 0.000228 | 0.37292 | 0.009442 | 6.2e-05 | -0.0015771 | 0.00021648 | -0.000328 | 85.5178 | -2.4113 | 0.019662 | -0.048514 | 0.001253 | -0.0028167 | 0.0046725 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.7236 | 0.2764 | -0.3538 | 2.2544 | -0.90058 | 2.2748 | 1.2441 | ; | Mfg1 | 198 | Gas | Mfg1 | Mfg1_198 | Pkg DX, Tier 0, Mfg1 198 (7.5 ton, 10.1 rated EER) | PkgDX T0 Mfg1 198 7.5t 10.1eer
31002 | 0 | 10 | 1 | 10.1 | 10.1 | 122100 | 0.7117 | 0.29185 | 0.02621 | 0.23312 | 0.0053235 | 0.0238 | 0 | 55 | 1.4157 | -0.019494 | 0.0001628 | -0.0014185 | -6.6905e-05 | 0.0001411 | 4.5507 | -0.050516 | -7.76e-05 | -0.0054824 | -5.2929e-05 | 0.0001855 | -0.42881 | 0.018822 | 8.36e-05 | 0.0092324 | 0.00021376 | -0.0004735 | 172.3022 | -5.6101 | 0.048731 | 0.1333 | 0.002049 | -0.0071226 | 0.0046725 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.83807 | 0.16193 | -1.5132 | 4.2513 | -1.7381 | 2.8497 | 1.3858 | ; | Mfg1 | 199 | Gas | Mfg1 | Mfg1_199 | Pkg DX, Tier 0, Mfg1 199 (10 ton, 10.1 rated EER) | PkgDX T0 Mfg1 199 10t 10.1eer
31003 | 0 | 7.5 | 2 | 10.1 | 10.1 | 89000 | 0.7685 | 0.25676 | 0.03371 | 0.36533 | 0.0073034 | 0.1038 | 0 | 55 | 1.0371 | -0.018772 | 0.0001756 | 0.0066389 | -8.8548e-05 | 9.44e-05 | -1.6494 | 0.11705 | -0.0013328 | 0.0036202 | -0.00011136 | 0.000228 | 0.37292 | 0.009442 | 6.2e-05 | -0.0015771 | 0.00021648 | -0.000328 | 85.5178 | -2.4113 | 0.019662 | -0.048514 | 0.001253 | -0.0028167 | 0.0046725 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.7236 | 0.2764 | -0.3538 | 2.2544 | -0.90058 | 2.3263 | 1.2515 | ; | Mfg1 | 200 | Elec | Mfg1 | Mfg1_200 | Pkg DX, Tier 0, Mfg1 200 (7.5 ton, 10.1 rated EER) | PkgDX T0 Mfg1 200 7.5t 10.1eer
31004 | 0 | 10 | 2 | 10.1 | 10.1 | 122100 | 0.7117 | 0.29365 | 0.02621 | 0.21813 | 0.0053235 | 0.0238 | 0 | 55 | 1.4157 | -0.019494 | 0.0001628 | -0.0014185 | -6.6905e-05 | 0.0001411 | 4.5507 | -0.050516 | -7.76e-05 | -0.0054824 | -5.2929e-05 | 0.0001855 | -0.42881 | 0.018822 | 8.36e-05 | 0.0092324 | 0.00021376 | -0.0004735 | 172.3022 | -5.6101 | 0.048731 | 0.1333 | 0.002049 | -0.0071226 | 0.0046725 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.83807 | 0.16193 | -1.5132 | 4.2513 | -1.7381 | 2.8936 | 1.3948 | ; | Mfg1 | 201 | Elec | Mfg1 | Mfg1_201 | Pkg DX, Tier 0, Mfg1 201 (10 ton, 10.1 rated EER) | PkgDX T0 Mfg1 201 10t 10.1eer
31005 | 0 | 10 | 1 | 10.1 | 10.1 | 121000 | 0.7554 | 0.26155 | 0.03306 | 0.3845 | 0.0053719 | 0.118 | 0 | 55 | 1.3757 | -0.0061983 | 0.0001292 | -0.012041 | 2.7619e-06 | 9.09e-05 | 0.56031 | 0.08998 | -0.0012168 | -0.023545 | -2.081e-05 | 0.000361 | -0.45426 | -0.0091137 | 0.0002568 | 0.035514 | 2.1262e-05 | -0.0004169 | 69.0046 | -2.3092 | 0.020134 | 0.20723 | 0.00039715 | -0.0042329 | 0.0046725 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.8595 | 0.1405 | 0.42013 | 0.67615 | -0.09628 | 2.6023 | 1.2433 | ; | Mfg1 | 202 | Gas | Mfg1 | Mfg1_202 | Pkg DX, Tier 0, Mfg1 202 (10 ton, 10.1 rated EER) | PkgDX T0 Mfg1 202 10t 10.1eer
31006 | 0 | 8 | 2 | 10.2 | 10.2 | 99700 | 0.681 | 0.26467 | 0.03009 | 0.34792 | 0.0065196 | 0.237 | 0 | 55 | 2.3014 | -0.058681 | 0.0006376 | 0.0014285 | -2.0357e-05 | -2.89e-05 | 7.125 | -0.1398 | 0.0007476 | -0.0016553 | -1.1905e-05 | 2.36e-05 | -1.1919 | 0.032655 | -7.28e-05 | 0.021642 | 0.00014681 | -0.0004792 | 2.5033 | -0.11944 | 0.0015729 | 0.045421 | 3.1655e-05 | -0.000811 | 0.0046725 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.82528 | 0.17472 | -0.030928 | 1.5507 | -0.5198 | 2.4269 | 1.29 | ; | Mfg1 | 203 | Elec | Mfg1 | Mfg1_203 | Pkg DX, Tier 0, Mfg1 203 (8 ton, 10.2 rated EER) | PkgDX T0 Mfg1 203 8t 10.2eer
31007 | 0 | 8 | 1 | 10.2 | 10.2 | 99700 | 0.681 | 0.26379 | 0.03009 | 0.35433 | 0.0065196 | 0.237 | 0 | 55 | 2.3014 | -0.058681 | 0.0006376 | 0.0014285 | -2.0357e-05 | -2.89e-05 | 7.125 | -0.1398 | 0.0007476 | -0.0016553 | -1.1905e-05 | 2.36e-05 | -1.1919 | 0.032655 | -7.28e-05 | 0.021642 | 0.00014681 | -0.0004792 | 2.5033 | -0.11944 | 0.0015729 | 0.045421 | 3.1655e-05 | -0.000811 | 0.0046725 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.82528 | 0.17472 | -0.030928 | 1.5507 | -0.5198 | 2.3854 | 1.2859 | ; | Mfg1 | 204 | Gas | Mfg1 | Mfg1_204 | Pkg DX, Tier 0, Mfg1 204 (8 ton, 10.2 rated EER) | PkgDX T0 Mfg1 204 8t 10.2eer
31008 | 0 | 8 | 2 | 10.3 | 10.3 | 91000 | 0.7308 | 0.26281 | 0.03077 | 0.31589 | 0.0071429 | 0.1172 | 0 | 55 | 0.16628 | 0.016117 | 2.2e-05 | -0.00089904 | -2.4095e-05 | -6.6e-06 | 1.6257 | 0.042339 | -0.0007752 | -0.010662 | -3.6548e-05 | 0.0002137 | 0.61233 | -0.014064 | 0.0002128 | 0.013393 | 8.9333e-05 | -0.0002677 | 65.4501 | -2.1757 | 0.019271 | 0.15687 | 0.00051577 | -0.0038873 | 0.0046725 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.83476 | 0.16524 | 0.43158 | 0.64702 | -0.078596 | 2.3322 | 1.306 | ; | Mfg1 | 205 | Elec | Mfg1 | Mfg1_205 | Pkg DX, Tier 0, Mfg1 205 (8 ton, 10.3 rated EER) | PkgDX T0 Mfg1 205 8t 10.3eer
31009 | 0 | 10 | 2 | 10.3 | 10.3 | 121000 | 0.7554 | 0.26518 | 0.03306 | 0.3185 | 0.0053719 | 0.118 | 0 | 55 | 1.3757 | -0.0061983 | 0.0001292 | -0.012041 | 2.7619e-06 | 9.09e-05 | 0.56031 | 0.08998 | -0.0012168 | -0.023545 | -2.081e-05 | 0.000361 | -0.45426 | -0.0091137 | 0.0002568 | 0.035514 | 2.1262e-05 | -0.0004169 | 69.0046 | -2.3092 | 0.020134 | 0.20723 | 0.00039715 | -0.0042329 | 0.0046725 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.8595 | 0.1405 | 0.42013 | 0.67615 | -0.09628 | 2.5302 | 1.2887 | ; | Mfg1 | 206 | Elec | Mfg1 | Mfg1_206 | Pkg DX, Tier 0, Mfg1 206 (10 ton, 10.3 rated EER) | PkgDX T0 Mfg1 206 10t 10.3eer
31010 | 0 | 8 | 1 | 10.3 | 10.3 | 91000 | 0.7308 | 0.26189 | 0.03077 | 0.3225 | 0.0071429 | 0.1172 | 0 | 55 | 0.16628 | 0.016117 | 2.2e-05 | -0.00089904 | -2.4095e-05 | -6.6e-06 | 1.6257 | 0.042339 | -0.0007752 | -0.010662 | -3.6548e-05 | 0.0002137 | 0.61233 | -0.014064 | 0.0002128 | 0.013393 | 8.9333e-05 | -0.0002677 | 65.4501 | -2.1757 | 0.019271 | 0.15687 | 0.00051577 | -0.0038873 | 0.0046725 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.83476 | 0.16524 | 0.43158 | 0.64702 | -0.078596 | 2.2869 | 1.3016 | ; | Mfg1 | 207 | Gas | Mfg1 | Mfg1_207 | Pkg DX, Tier 0, Mfg1 207 (8 ton, 10.3 rated EER) | PkgDX T0 Mfg1 207 8t 10.3eer
31011 | 0 | 7.5 | 1 | 10.3 | 10.3 | 90600 | 0.75276 | 0.23093 | 0.03311 | 0.4547 | 0.0093819 | 0.1912 | 0 | 55 | 2.0247 | -0.042473 | 0.00051667 | -0.00022128 | 1.2743e-05 | -9.3067e-05 | 1.4252 | 0.047714 | -0.00072603 | -0.011724 | 1.5029e-05 | 9.6667e-05 | 0.1978 | 0.0085814 | -0.00012984 | 0.0054006 | 6.7143e-05 | -4.8533e-05 | 50.0723 | -1.6741 | 0.013843 | 0.15224 | -8.1372e-05 | -0.0020079 | 0.0046844 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.84786 | 0.15214 | 0.42595 | -0.090476 | 0.66452 | 2.5 | 1.1964 | ; | Mfg2 | 208 | Gas | Mfg2 | Mfg2_208 | Pkg DX, Tier 0, Mfg2 208 (7.5 ton, 10.3 rated EER) | PkgDX T0 Mfg2 208 7.5t 10.3eer
31012 | 0 | 10 | 1 | 10.3 | 10.3 | 124200 | 0.73913 | 0.22031 | 0.0306 | 0.6308 | 0.0068438 | 0.1885 | 0 | 55 | 2.02 | -0.042014 | 0.00051349 | -0.00042801 | 1.3943e-05 | -9.3533e-05 | 1.4553 | 0.046719 | -0.00071921 | -0.011627 | 1.4286e-05 | 9.72e-05 | 0.077646 | 0.007437 | -7.4127e-05 | 0.0076907 | 7.9543e-05 | -0.00010867 | 83.9738 | -2.7997 | 0.023043 | 0.21547 | -0.00013109 | -0.0028463 | 0.0046844 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.84786 | 0.15214 | 0.42595 | -0.090476 | 0.66452 | 2.5 | 1.1157 | ; | Mfg2 | 209 | Gas | Mfg2 | Mfg2_209 | Pkg DX, Tier 0, Mfg2 209 (10 ton, 10.3 rated EER) | PkgDX T0 Mfg2 209 10t 10.3eer
31013 | 0 | 7.5 | 2 | 10.3 | 10.3 | 90600 | 0.75276 | 0.23103 | 0.03311 | 0.454 | 0.0093819 | 0.1912 | 0 | 55 | 2.0247 | -0.042473 | 0.00051667 | -0.00022128 | 1.2743e-05 | -9.3067e-05 | 1.4252 | 0.047714 | -0.00072603 | -0.011724 | 1.5029e-05 | 9.6667e-05 | 0.21393 | 0.0081072 | -0.00012698 | 0.0054057 | 6.6743e-05 | -4.76e-05 | 50.0723 | -1.6741 | 0.013843 | 0.15224 | -8.1372e-05 | -0.0020079 | 0.0046844 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.84786 | 0.15214 | 0.42595 | -0.090476 | 0.66452 | 2.5 | 1.1968 | ; | Mfg2 | 210 | Elec | Mfg2 | Mfg2_210 | Pkg DX, Tier 0, Mfg2 210 (7.5 ton, 10.3 rated EER) | PkgDX T0 Mfg2 210 7.5t 10.3eer
31014 | 0 | 10 | 2 | 10.3 | 10.3 | 124200 | 0.73913 | 0.22031 | 0.0306 | 0.6308 | 0.0068438 | 0.1885 | 0 | 55 | 2.02 | -0.042014 | 0.00051349 | -0.00042801 | 1.3943e-05 | -9.3533e-05 | 1.4553 | 0.046719 | -0.00071921 | -0.011627 | 1.4286e-05 | 9.72e-05 | 0.077646 | 0.007437 | -7.4127e-05 | 0.0076907 | 7.9543e-05 | -0.00010867 | 83.9738 | -2.7997 | 0.023043 | 0.21547 | -0.00013109 | -0.0028463 | 0.0046844 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.84786 | 0.15214 | 0.42595 | -0.090476 | 0.66452 | 2.5 | 1.1157 | ; | Mfg2 | 211 | Elec | Mfg2 | Mfg2_211 | Pkg DX, Tier 0, Mfg2 211 (10 ton, 10.3 rated EER) | PkgDX T0 Mfg2 211 10t 10.3eer
31015 | 0 | 7.5 | 1 | 10.1 | 10.1 | 93000 | 0.68 | 0.28189 | 0.03226 | 0.206 | 0.0075269 | 0.2911 | 0 | 55 | 1.1268 | -0.01717 | 0.00028516 | 0.0032745 | -1.1667e-05 | -7.2625e-05 | 12.6405 | -0.29621 | 0.001843 | 0.0020968 | -8.8333e-06 | -2.9375e-05 | 0.38929 | 0.014267 | -5.5469e-05 | -0.0058476 | 0.00017158 | -0.00017113 | 15.6763 | -0.54061 | 0.0049906 | 0.032329 | 3.7001e-05 | -0.00066985 | 0.0046844 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.87097 | 0.12903 | 0.59503 | 0.27728 | 0.12769 | 2.194 | 1.3737 | ; | Mfg3 | 212 | Gas | Mfg3 | Mfg3_212 | Pkg DX, Tier 0, Mfg3 212 (7.5 ton, 10.1 rated EER) | PkgDX T0 Mfg3 212 7.5t 10.1eer
31016 | 0 | 8.5 | 1 | 10.1 | 10.1 | 104000 | 0.71 | 0.27802 | 0.03269 | 0.2474 | 0.0067308 | 0.2218 | 0 | 55 | 1.4648 | -0.028639 | 0.00037578 | 0.0046078 | -1.6917e-05 | -8.1375e-05 | 14.7702 | -0.35498 | 0.0022406 | 0.00093783 | -1.5167e-05 | 5e-07 | -0.10974 | 0.029203 | -0.00016719 | -0.0056557 | 0.00016875 | -0.00017 | 23.4441 | -0.783 | 0.0068853 | 0.028222 | 6.2087e-05 | -0.00064925 | 0.0046844 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.8774 | 0.1226 | 0.74919 | -0.043405 | 0.29422 | 2.3238 | 1.3415 | ; | Mfg3 | 213 | Gas | Mfg3 | Mfg3_213 | Pkg DX, Tier 0, Mfg3 213 (8.5 ton, 10.1 rated EER) | PkgDX T0 Mfg3 213 8.5t 10.1eer
31017 | 0 | 10 | 1 | 10.1 | 10.1 | 125875 | 0.705 | 0.26979 | 0.03019 | 0.3566 | 0.0055611 | 0.1712 | 0 | 55 | 1.5672 | -0.028947 | 0.00036719 | 0.0024485 | -1.0167e-05 | -6.55e-05 | 11.9873 | -0.26997 | 0.0016023 | -0.0032234 | -9.5e-06 | 4.7125e-05 | -0.12118 | 0.027602 | -0.00016328 | -0.0027501 | 0.000147 | -0.00016662 | 27.762 | -0.95161 | 0.0084798 | 0.058949 | 6.4128e-05 | -0.0011389 | 0.0046844 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.8804 | 0.1196 | 0.55667 | 0.33451 | 0.10882 | 2.384 | 1.2837 | ; | Mfg3 | 214 | Gas | Mfg3 | Mfg3_214 | Pkg DX, Tier 0, Mfg3 214 (10 ton, 10.1 rated EER) | PkgDX T0 Mfg3 214 10t 10.1eer
31018 | 0 | 7.5 | 2 | 10.3 | 10.3 | 96200 | 0.71 | 0.27733 | 0.03119 | 0.206 | 0.0072765 | 0.1842 | 0 | 55 | 1.1971 | -0.019652 | 0.00030703 | 0.0038895 | -1.2917e-05 | -8.0375e-05 | 11.2749 | -0.26109 | 0.0015969 | 0.0045964 | -2.2917e-05 | -2.825e-05 | 0.424 | 0.015806 | -7.1875e-05 | -0.0078805 | 0.00017908 | -0.0001615 | 26.1356 | -0.80801 | 0.0069192 | 0.0086125 | 0.00016709 | -0.00068899 | 0.0046844 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.87526 | 0.12474 | 0.60836 | 0.27195 | 0.11969 | 2.194 | 1.3787 | ; | Mfg3 | 215 | Elec | Mfg3 | Mfg3_215 | Pkg DX, Tier 0, Mfg3 215 (7.5 ton, 10.3 rated EER) | PkgDX T0 Mfg3 215 7.5t 10.3eer
31019 | 0 | 8.5 | 2 | 10.3 | 10.3 | 102000 | 0.71 | 0.27047 | 0.03333 | 0.2474 | 0.0068627 | 0.2368 | 0 | 55 | 1.6251 | -0.033433 | 0.00041328 | 0.0048703 | -1.7333e-05 | -8.5875e-05 | 12.0152 | -0.26715 | 0.0015898 | -0.0039944 | 5.5e-06 | 1.2125e-05 | -0.20423 | 0.034025 | -0.00020938 | -0.007296 | 0.00017392 | -0.000159 | 23.3708 | -0.81374 | 0.0070475 | 0.059705 | -8.198e-05 | -0.00069412 | 0.0046844 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.87745 | 0.12255 | 0.78376 | -0.11309 | 0.32933 | 2.3238 | 1.338 | ; | Mfg3 | 216 | Elec | Mfg3 | Mfg3_216 | Pkg DX, Tier 0, Mfg3 216 (8.5 ton, 10.3 rated EER) | PkgDX T0 Mfg3 216 8.5t 10.3eer
31020 | 0 | 10 | 1 | 10.3 | 10.3 | 125850 | 0.745 | 0.26345 | 0.03019 | 0.3566 | 0.0055622 | 0.0621 | 0 | 55 | 1.425 | -0.025197 | 0.00033906 | 0.0026506 | -1.0917e-05 | -6.475e-05 | 4.1328 | -0.041987 | -4.6875e-05 | -0.0033118 | -9.3333e-06 | 4.55e-05 | -0.0069502 | 0.025283 | -0.00015078 | -0.0034146 | 0.00014775 | -0.00016013 | 115.5853 | -3.5226 | 0.027317 | 0.09357 | 0.00014108 | -0.0017841 | 0.0046844 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.88061 | 0.11939 | 0.44913 | 0.59072 | -0.039851 | 2.384 | 1.2837 | ; | Mfg3 | 217 | Gas | Mfg3 | Mfg3_217 | Pkg DX, Tier 0, Mfg3 217 (10 ton, 10.3 rated EER) | PkgDX T0 Mfg3 217 10t 10.3eer
31021 | 0 | 10 | 1 | 10.3 | 10.3 | 127600 | 0.655 | 0.26538 | 0.02821 | 0.3686 | 0.0054859 | 0.2702 | 0 | 55 | 1.2303 | -0.021603 | 0.00033906 | 0.005237 | -2.05e-05 | -9.7e-05 | 15.1626 | -0.37008 | 0.0024266 | 0.0028543 | 4.1667e-07 | -8.4e-05 | -0.4212 | 0.03578 | -0.00017422 | -0.0047209 | 0.00021183 | -0.00026038 | 15.4985 | -0.61694 | 0.0060821 | 0.060652 | -2.0696e-05 | -0.00094914 | 0.0046844 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.88172 | 0.11828 | 0.78614 | -0.084639 | 0.2985 | 2.6309 | 1.2915 | ; | Mfg3 | 218 | Gas | Mfg3 | Mfg3_218 | Pkg DX, Tier 0, Mfg3 218 (10 ton, 10.3 rated EER) | PkgDX T0 Mfg3 218 10t 10.3eer
31022 | 0 | 7.5 | 2 | 10.4 | 10.4 | 96200 | 0.71 | 0.27422 | 0.03119 | 0.206 | 0.0072765 | 0.1842 | 0 | 55 | 1.1971 | -0.019652 | 0.00030703 | 0.0038895 | -1.2917e-05 | -8.0375e-05 | 11.2749 | -0.26109 | 0.0015969 | 0.0045964 | -2.2917e-05 | -2.825e-05 | 0.424 | 0.015806 | -7.1875e-05 | -0.0078805 | 0.00017908 | -0.0001615 | 26.1356 | -0.80801 | 0.0069192 | 0.0086125 | 0.00016709 | -0.00068899 | 0.0046844 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.87526 | 0.12474 | 0.60836 | 0.27195 | 0.11969 | 2.194 | 1.3787 | ; | Mfg3 | 219 | Elec | Mfg3 | Mfg3_219 | Pkg DX, Tier 0, Mfg3 219 (7.5 ton, 10.4 rated EER) | PkgDX T0 Mfg3 219 7.5t 10.4eer
31023 | 0 | 8.5 | 2 | 10.4 | 10.4 | 102000 | 0.71 | 0.26738 | 0.03333 | 0.2474 | 0.0068627 | 0.2368 | 0 | 55 | 1.6251 | -0.033433 | 0.00041328 | 0.0048703 | -1.7333e-05 | -8.5875e-05 | 12.0152 | -0.26715 | 0.0015898 | -0.0039944 | 5.5e-06 | 1.2125e-05 | -0.20423 | 0.034025 | -0.00020938 | -0.007296 | 0.00017392 | -0.000159 | 23.3708 | -0.81374 | 0.0070475 | 0.059705 | -8.198e-05 | -0.00069412 | 0.0046844 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.87745 | 0.12255 | 0.78376 | -0.11309 | 0.32933 | 2.3238 | 1.338 | ; | Mfg3 | 220 | Elec | Mfg3 | Mfg3_220 | Pkg DX, Tier 0, Mfg3 220 (8.5 ton, 10.4 rated EER) | PkgDX T0 Mfg3 220 8.5t 10.4eer
31024 | 0 | 10 | 2 | 10.4 | 10.4 | 125850 | 0.745 | 0.26435 | 0.03019 | 0.3276 | 0.0055622 | 0.0621 | 0 | 55 | 1.425 | -0.025197 | 0.00033906 | 0.0026506 | -1.0917e-05 | -6.475e-05 | 4.1328 | -0.041987 | -4.6875e-05 | -0.0033118 | -9.3333e-06 | 4.55e-05 | -0.0069502 | 0.025283 | -0.00015078 | -0.0034146 | 0.00014775 | -0.00016013 | 115.5853 | -3.5226 | 0.027317 | 0.09357 | 0.00014108 | -0.0017841 | 0.0046844 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.88061 | 0.11939 | 0.44913 | 0.59072 | -0.039851 | 2.3715 | 1.3023 | ; | Mfg3 | 221 | Elec | Mfg3 | Mfg3_221 | Pkg DX, Tier 0, Mfg3 221 (10 ton, 10.4 rated EER) | PkgDX T0 Mfg3 221 10t 10.4eer
31025 | 0 | 10 | 2 | 10.4 | 10.4 | 127600 | 0.655 | 0.27062 | 0.02821 | 0.3036 | 0.0054859 | 0.2702 | 0 | 55 | 1.2303 | -0.021603 | 0.00033906 | 0.005237 | -2.05e-05 | -9.7e-05 | 15.1626 | -0.37008 | 0.0024266 | 0.0028543 | 4.1667e-07 | -8.4e-05 | -0.4212 | 0.03578 | -0.00017422 | -0.0047209 | 0.00021183 | -0.00026038 | 15.4985 | -0.61694 | 0.0060821 | 0.060652 | -2.0696e-05 | -0.00094914 | 0.0046844 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.88172 | 0.11828 | 0.78614 | -0.084639 | 0.2985 | 2.3379 | 1.331 | ; | Mfg3 | 222 | Elec | Mfg3 | Mfg3_222 | Pkg DX, Tier 0, Mfg3 222 (10 ton, 10.4 rated EER) | PkgDX T0 Mfg3 222 10t 10.4eer
31026 | 0 | 7.5 | 2 | 10.4 | 10.4 | 93000 | 0.68 | 0.27236 | 0.03226 | 0.206 | 0.0075269 | 0.2911 | 0 | 55 | 1.1268 | -0.01717 | 0.00028516 | 0.0032745 | -1.1667e-05 | -7.2625e-05 | 12.6405 | -0.29621 | 0.001843 | 0.0020968 | -8.8333e-06 | -2.9375e-05 | 0.38929 | 0.014267 | -5.5469e-05 | -0.0058476 | 0.00017158 | -0.00017113 | 15.6763 | -0.54061 | 0.0049906 | 0.032329 | 3.7001e-05 | -0.00066985 | 0.0046844 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.87097 | 0.12903 | 0.59503 | 0.27728 | 0.12769 | 2.194 | 1.3737 | ; | Mfg3 | 223 | Elec | Mfg3 | Mfg3_223 | Pkg DX, Tier 0, Mfg3 223 (7.5 ton, 10.4 rated EER) | PkgDX T0 Mfg3 223 7.5t 10.4eer
31027 | 0 | 8.5 | 2 | 10.4 | 10.4 | 104000 | 0.71 | 0.26854 | 0.03269 | 0.2474 | 0.0067308 | 0.2218 | 0 | 55 | 1.4648 | -0.028639 | 0.00037578 | 0.0046078 | -1.6917e-05 | -8.1375e-05 | 14.7702 | -0.35498 | 0.0022406 | 0.00093783 | -1.5167e-05 | 5e-07 | -0.10974 | 0.029203 | -0.00016719 | -0.0056557 | 0.00016875 | -0.00017 | 23.4441 | -0.783 | 0.0068853 | 0.028222 | 6.2087e-05 | -0.00064925 | 0.0046844 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.8774 | 0.1226 | 0.74919 | -0.043405 | 0.29422 | 2.3238 | 1.3415 | ; | Mfg3 | 224 | Elec | Mfg3 | Mfg3_224 | Pkg DX, Tier 0, Mfg3 224 (8.5 ton, 10.4 rated EER) | PkgDX T0 Mfg3 224 8.5t 10.4eer
31028 | 0 | 10 | 2 | 10.4 | 10.4 | 125875 | 0.705 | 0.26436 | 0.03019 | 0.3276 | 0.0055611 | 0.1712 | 0 | 55 | 1.5672 | -0.028947 | 0.00036719 | 0.0024485 | -1.0167e-05 | -6.55e-05 | 11.9873 | -0.26997 | 0.0016023 | -0.0032234 | -9.5e-06 | 4.7125e-05 | -0.12118 | 0.027602 | -0.00016328 | -0.0027501 | 0.000147 | -0.00016662 | 27.762 | -0.95161 | 0.0084798 | 0.058949 | 6.4128e-05 | -0.0011389 | 0.0046844 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.8804 | 0.1196 | 0.55667 | 0.33451 | 0.10882 | 2.3715 | 1.3023 | ; | Mfg3 | 225 | Elec | Mfg3 | Mfg3_225 | Pkg DX, Tier 0, Mfg3 225 (10 ton, 10.4 rated EER) | PkgDX T0 Mfg3 225 10t 10.4eer
31029 | 0 | 6 | 2 | 10.3 | 10.3 | 75300 | 0.74369 | 0.25877 | 0.03187 | 0.3917 | 0.0046481 | 0.1148 | 0 | 55 | -4.8197 | 0.14472 | -0.0010031 | 0.017028 | -0.00010998 | 2.5e-07 | 2.2955 | 0.0049469 | -0.00039188 | 0.003135 | -4.1714e-05 | 3.3125e-05 | -1.2895 | 0.06215 | -0.00037187 | -0.0055112 | 0.00019731 | -0.00022975 | 31.6013 | -0.92124 | 0.0064136 | 0.033984 | -0.00013855 | 5.5488e-05 | 0.0046844 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.81939 | 0.18061 | 0.53571 | 0.46429 | 0 | 2.0424 | 1.248 | ; | Mfg5 | 226 | Elec | Mfg5 | Mfg5_226 | Pkg DX, Tier 0, Mfg5 226 (6 ton, 10.3 rated EER) | PkgDX T0 Mfg5 226 6t 10.3eer
31030 | 0 | 7.5 | 2 | 10.3 | 10.3 | 93400 | 0.76445 | 0.25195 | 0.03426 | 0.3528 | 0.0071734 | 0.1277 | 0 | 55 | -2.0135 | 0.074545 | -0.00048875 | 0.01002 | -8.081e-05 | -1.5e-06 | -3.8628 | 0.18116 | -0.0017244 | 0.0093138 | -7.8714e-05 | 4.575e-05 | 4.9954 | -0.13152 | 0.001075 | -0.0027259 | 0.00018064 | -0.00021688 | 85.9624 | -2.4775 | 0.019322 | -0.040604 | 0.00061285 | -0.0011598 | 0.0046844 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.81799 | 0.18201 | 0.51681 | 0.5007 | -0.017507 | 1.8569 | 1.2562 | ; | Mfg5 | 227 | Elec | Mfg5 | Mfg5_227 | Pkg DX, Tier 0, Mfg5 227 (7.5 ton, 10.3 rated EER) | PkgDX T0 Mfg5 227 7.5t 10.3eer
31031 | 0 | 8.5 | 2 | 10.3 | 10.3 | 104000 | 0.76923 | 0.26004 | 0.03269 | 0.3321 | 0.0064423 | 0.0742 | 0 | 55 | -0.1861 | 0.018478 | -5.375e-05 | 0.0088879 | -7.2571e-05 | 0 | -0.074557 | 0.068848 | -0.00085063 | 0.0056542 | -5.4738e-05 | 3.725e-05 | 1.1644 | -0.015697 | 0.00020688 | -0.0014074 | 0.0001676 | -0.00022312 | 72.0686 | -2.028 | 0.015654 | 0.031271 | 0.00057475 | -0.0021396 | 0.0046844 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.81731 | 0.18269 | 0.55 | 0.43438 | 0.015625 | 1.8569 | 1.2818 | ; | Mfg5 | 228 | Elec | Mfg5 | Mfg5_228 | Pkg DX, Tier 0, Mfg5 228 (8.5 ton, 10.3 rated EER) | PkgDX T0 Mfg5 228 8.5t 10.3eer
31032 | 0 | 10 | 2 | 10.3 | 10.3 | 125700 | 0.74543 | 0.24734 | 0.03182 | 0.4553 | 0.0053302 | 0.1089 | 0 | 55 | 2.4828 | -0.043065 | 0.00035688 | 0.00094142 | -3.1833e-05 | -2.5e-07 | -0.7329 | 0.090133 | -0.0010213 | 0.0087046 | -6.1929e-05 | 1.625e-06 | 1.6152 | -0.037601 | 0.0003175 | 2.3494e-05 | 9.8381e-05 | -6.4625e-05 | 92.9918 | -2.3982 | 0.016923 | -0.24364 | 0.00086004 | 0.0012736 | 0.0046844 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.81702 | 0.18298 | 0.53575 | 0.46425 | 0 | 2.0098 | 1.2076 | ; | Mfg5 | 229 | Elec | Mfg5 | Mfg5_229 | Pkg DX, Tier 0, Mfg5 229 (10 ton, 10.3 rated EER) | PkgDX T0 Mfg5 229 10t 10.3eer
31033 | 0 | 10 | 2 | 10.11 | 10.11 | 119200 | 0.7307 | 0.20417 | 0.03356 | 0.591 | 0.012584 | 0.1907 | 0 | 55 | 2.637 | -0.061226 | 0.0005434 | 0.0053432 | -3.1964e-05 | -3.036e-05 | -5.5459 | 0.28795 | -0.0028264 | -0.029517 | -1.4929e-05 | 0.00045244 | -0.74188 | 0.050374 | -0.0004618 | -0.006342 | 8.0839e-05 | 4.914e-05 | 90.1825 | -3.0873 | 0.026757 | 0.23266 | 0.0001577 | -0.0040802 | 0.0046725 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.87919 | 0.12081 | 0.16418 | 1.2767 | -0.44087 | 1.2181 | 1.106 | ; | Mfg6 | 230 | Elec | Mfg6 | Mfg6_230 | Pkg DX, Tier 0, Mfg6 230 (10 ton, 10.11 rated EER) | PkgDX T0 Mfg6 230 10t 10.11eer
31034 | 0 | 6.5 | 1 | 10.4 | 10.4 | 77600 | 0.7513 | 0.25246 | 0.03351 | 0.296 | 0.0090206 | 0.1396 | 0 | 55 | 4.7276 | -0.12397 | 0.0011804 | 0.0019378 | -1.3714e-05 | -0.00012264 | -3.4102 | 0.22223 | -0.0022404 | -0.031052 | -1.8732e-05 | 0.00042374 | -4.875 | 0.18727 | -0.0013042 | -0.010646 | 0.00026995 | -0.00035234 | 101.8385 | -3.3536 | 0.028331 | 0.18795 | 0.00042162 | -0.0039251 | 0.0046725 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.81443 | 0.18557 | 0.10463 | 1.2384 | -0.34305 | 1.8727 | 1.3017 | ; | Mfg6 | 231 | Gas | Mfg6 | Mfg6_231 | Pkg DX, Tier 0, Mfg6 231 (6.5 ton, 10.4 rated EER) | PkgDX T0 Mfg6 231 6.5t 10.4eer
31035 | 0 | 8.5 | 1 | 10.4 | 10.4 | 103100 | 0.7216 | 0.21783 | 0.03298 | 0.583 | 0.0067895 | 0.1992 | 0 | 55 | 4.9424 | -0.12591 | 0.0011252 | 0.0014177 | -2.5321e-05 | -7.284e-05 | -2.9299 | 0.20769 | -0.00225 | -0.024504 | -6.6714e-05 | 0.00047844 | -5.2585 | 0.20434 | -0.0014994 | -0.016964 | 0.00025518 | -0.00021884 | 98.3141 | -3.1681 | 0.025764 | 0.067156 | 0.00019691 | -0.0013928 | 0.0046725 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.84814 | 0.15186 | 0.23118 | 1.0412 | -0.2724 | 2.4269 | 1.1171 | ; | Mfg6 | 232 | Gas | Mfg6 | Mfg6_232 | Pkg DX, Tier 0, Mfg6 232 (8.5 ton, 10.4 rated EER) | PkgDX T0 Mfg6 232 8.5t 10.4eer
31036 | 0 | 10 | 1 | 10.4 | 10.4 | 119200 | 0.7307 | 0.20422 | 0.03356 | 0.533 | 0.012584 | 0.1907 | 0 | 55 | 2.637 | -0.061226 | 0.0005434 | 0.0053432 | -3.1964e-05 | -3.036e-05 | -5.5459 | 0.28795 | -0.0028264 | -0.029517 | -1.4929e-05 | 0.00045244 | -0.74188 | 0.050374 | -0.0004618 | -0.006342 | 8.0839e-05 | 4.914e-05 | 90.1825 | -3.0873 | 0.026757 | 0.23266 | 0.0001577 | -0.0040802 | 0.0046725 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.87919 | 0.12081 | 0.16418 | 1.2767 | -0.44087 | 1.0185 | 1.142 | ; | Mfg6 | 233 | Gas | Mfg6 | Mfg6_233 | Pkg DX, Tier 0, Mfg6 233 (10 ton, 10.4 rated EER) | PkgDX T0 Mfg6 233 10t 10.4eer
31037 | 0 | 6 | 2 | 10.3 | 10.3 | 75300 | 0.74369 | 0.25114 | 0.03187 | 0.435 | 0.0050465 | 0.1148 | 0 | 55 | -4.8187 | 0.14472 | -0.0010031 | 0.017028 | -0.00010998 | 2.5e-07 | 4.6538 | -0.067564 | 0.00016563 | 0.0031064 | -4.169e-05 | 3.35e-05 | -3.2014 | 0.12653 | -0.00083875 | -0.012126 | 0.00023231 | -0.00022937 | -19.5416 | 0.61016 | -0.004862 | 0.055674 | -0.000116 | -0.00039668 | 0.0046725 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.81939 | 0.18061 | 0.53571 | 0.46429 | 0 | 2.0534 | 1.22 | ; | Mfg4 | 234 | Elec | Mfg4 | Mfg4_234 | Pkg DX, Tier 0, Mfg4 234 (6 ton, 10.3 rated EER) | PkgDX T0 Mfg4 234 6t 10.3eer
31038 | 0 | 7.5 | 2 | 10.3 | 10.3 | 93400 | 0.76445 | 0.24579 | 0.03426 | 0.3713 | 0.008137 | 0.1277 | 0 | 55 | -2.0119 | 0.074545 | -0.00048875 | 0.01002 | -8.081e-05 | -1.5e-06 | -3.8605 | 0.18116 | -0.0017244 | 0.0093138 | -7.8714e-05 | 4.575e-05 | 3.4873 | -0.080943 | 0.00071 | -0.0079706 | 0.0002096 | -0.0002185 | 63.1464 | -1.7106 | 0.012791 | -0.10554 | 0.00052791 | 2.4141e-05 | 0.0046725 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.81799 | 0.18201 | 0.51681 | 0.5007 | -0.017507 | 1.7089 | 1.2431 | ; | Mfg4 | 235 | Elec | Mfg4 | Mfg4_235 | Pkg DX, Tier 0, Mfg4 235 (7.5 ton, 10.3 rated EER) | PkgDX T0 Mfg4 235 7.5t 10.3eer
31039 | 0 | 8.5 | 2 | 10.3 | 10.3 | 104000 | 0.76923 | 0.24879 | 0.03269 | 0.3879 | 0.0073077 | 0.0742 | 0 | 55 | -0.53499 | 0.0297 | -0.0001375 | 0.0083264 | -6.9381e-05 | 0 | -0.071849 | 0.068848 | -0.00085063 | 0.0056542 | -5.4738e-05 | 3.725e-05 | 0.72709 | -0.00016187 | 9.875e-05 | -0.004073 | 0.00018198 | -0.00022337 | 65.4416 | -1.5899 | 0.011118 | -0.1395 | 0.00078091 | -0.00022009 | 0.0046725 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.81731 | 0.18269 | 0.55 | 0.43438 | 0.015625 | 1.9832 | 1.244 | ; | Mfg4 | 236 | Elec | Mfg4 | Mfg4_236 | Pkg DX, Tier 0, Mfg4 236 (8.5 ton, 10.3 rated EER) | PkgDX T0 Mfg4 236 8.5t 10.3eer
31040 | 0 | 10 | 2 | 10.3 | 10.3 | 125700 | 0.74543 | 0.23951 | 0.03182 | 0.4925 | 0.0060461 | 0.1089 | 0 | 55 | 2.486 | -0.043065 | 0.00035688 | 0.00094142 | -3.1833e-05 | -2.5e-07 | -0.73161 | 0.090133 | -0.0010213 | 0.0087046 | -6.1929e-05 | 1.625e-06 | 0.53232 | -0.0014656 | 5.75e-05 | -0.0036936 | 0.0001191 | -6.6625e-05 | 91.2774 | -2.3455 | 0.016384 | -0.2487 | 0.00081093 | 0.0014836 | 0.0046725 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.81702 | 0.18298 | 0.53575 | 0.46425 | 0 | 2.1488 | 1.1843 | ; | Mfg4 | 237 | Elec | Mfg4 | Mfg4_237 | Pkg DX, Tier 0, Mfg4 237 (10 ton, 10.3 rated EER) | PkgDX T0 Mfg4 237 10t 10.3eer
31041 | 0 | 6 | 1 | 10.3 | 10.3 | 75300 | 0.74369 | 0.25114 | 0.03187 | 0.435 | 0.0050465 | 0.1148 | 0 | 55 | -4.8187 | 0.14472 | -0.0010031 | 0.017028 | -0.00010998 | 2.5e-07 | 4.6538 | -0.067564 | 0.00016563 | 0.0031064 | -4.169e-05 | 3.35e-05 | -3.2014 | 0.12653 | -0.00083875 | -0.012126 | 0.00023231 | -0.00022937 | -19.5416 | 0.61016 | -0.004862 | 0.055674 | -0.000116 | -0.00039668 | 0.0046725 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.81939 | 0.18061 | 0.53571 | 0.46429 | 0 | 2.0534 | 1.22 | ; | Mfg4 | 238 | Gas | Mfg4 | Mfg4_238 | Pkg DX, Tier 0, Mfg4 238 (6 ton, 10.3 rated EER) | PkgDX T0 Mfg4 238 6t 10.3eer
31042 | 0 | 7.5 | 1 | 10.3 | 10.3 | 93400 | 0.76445 | 0.24579 | 0.03426 | 0.3713 | 0.008137 | 0.1277 | 0 | 55 | -2.0119 | 0.074545 | -0.00048875 | 0.01002 | -8.081e-05 | -1.5e-06 | -3.8605 | 0.18116 | -0.0017244 | 0.0093138 | -7.8714e-05 | 4.575e-05 | 3.4873 | -0.080943 | 0.00071 | -0.0079706 | 0.0002096 | -0.0002185 | 63.1464 | -1.7106 | 0.012791 | -0.10554 | 0.00052791 | 2.4141e-05 | 0.0046725 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.81799 | 0.18201 | 0.51681 | 0.5007 | -0.017507 | 1.7089 | 1.2431 | ; | Mfg4 | 239 | Gas | Mfg4 | Mfg4_239 | Pkg DX, Tier 0, Mfg4 239 (7.5 ton, 10.3 rated EER) | PkgDX T0 Mfg4 239 7.5t 10.3eer
31043 | 0 | 8.5 | 1 | 10.3 | 10.3 | 104000 | 0.76923 | 0.24879 | 0.03269 | 0.3879 | 0.0073077 | 0.0742 | 0 | 55 | -0.53499 | 0.0297 | -0.0001375 | 0.0083264 | -6.9381e-05 | 0 | -0.071849 | 0.068848 | -0.00085063 | 0.0056542 | -5.4738e-05 | 3.725e-05 | 0.72709 | -0.00016187 | 9.875e-05 | -0.004073 | 0.00018198 | -0.00022337 | 65.4416 | -1.5899 | 0.011118 | -0.1395 | 0.00078091 | -0.00022009 | 0.0046725 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.81731 | 0.18269 | 0.55 | 0.43438 | 0.015625 | 1.9832 | 1.244 | ; | Mfg4 | 240 | Gas | Mfg4 | Mfg4_240 | Pkg DX, Tier 0, Mfg4 240 (8.5 ton, 10.3 rated EER) | PkgDX T0 Mfg4 240 8.5t 10.3eer
31044 | 0 | 10 | 1 | 10.3 | 10.3 | 125700 | 0.74543 | 0.23951 | 0.03182 | 0.4925 | 0.0060461 | 0.1089 | 0 | 55 | 2.486 | -0.043065 | 0.00035688 | 0.00094142 | -3.1833e-05 | -2.5e-07 | -0.73161 | 0.090133 | -0.0010213 | 0.0087046 | -6.1929e-05 | 1.625e-06 | 0.53232 | -0.0014656 | 5.75e-05 | -0.0036936 | 0.0001191 | -6.6625e-05 | 91.2774 | -2.3455 | 0.016384 | -0.2487 | 0.00081093 | 0.0014836 | 0.0046725 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.81702 | 0.18298 | 0.53575 | 0.46425 | 0 | 2.1488 | 1.1843 | ; | Mfg4 | 241 | Gas | Mfg4 | Mfg4_241 | Pkg DX, Tier 0, Mfg4 241 (10 ton, 10.3 rated EER) | PkgDX T0 Mfg4 241 10t 10.3eer
31101 | 1 | 8 | 1 | 11 | 11 | 92900 | 0.7234 | 0.23521 | 0.03229 | 0.35442 | 0.0069968 | 0.1778 | 0 | 55 | -0.5264 | 0.032926 | -0.00010467 | -0.00032844 | -1.8702e-05 | -1.5429e-06 | 0.84846 | 0.062956 | -0.00090867 | -0.0094341 | -2.4202e-05 | 0.00017709 | 1.4679 | -0.041954 | 0.00046233 | 0.015563 | 0.00014848 | -0.00040077 | 37.7107 | -1.2268 | 0.0104 | 0.072822 | 0.00012566 | -0.0014541 | 0.0046725 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.96 | 1 | 2 | 0.5 | 0.5 | 0.88805 | 0.11195 | 0.79464 | 0.0029762 | 0.20238 | 2.3717 | 1.2695 | ; | Mfg1 | 242 | Gas | Mfg1 | Mfg1_242 | Pkg DX, Tier 1, Mfg1 242 (8 ton, 11 rated EER) | PkgDX T1 Mfg1 242 8t 11eer
31102 | 1 | 10 | 1 | 11 | 11 | 121900 | 0.6727 | 0.25704 | 0.02625 | 0.29844 | 0.0053322 | 0.1537 | 0 | 55 | -0.82834 | 0.051006 | -0.000317 | -0.0090596 | -2.6429e-05 | 0.0001466 | 2.4059 | 0.015506 | -0.00054067 | -0.010982 | -2.2345e-05 | 0.0001928 | 2.5275 | -0.090915 | 0.0010107 | 0.030759 | 0.00017397 | -0.00070154 | 32.5254 | -1.1432 | 0.010555 | 0.090537 | 0.00018097 | -0.0019705 | 0.0046725 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.96 | 1 | 2 | 0.5 | 0.5 | 0.86781 | 0.13219 | 0.51707 | 0.49854 | -0.01561 | 2.4573 | 1.3471 | ; | Mfg1 | 243 | Gas | Mfg1 | Mfg1_243 | Pkg DX, Tier 1, Mfg1 243 (10 ton, 11 rated EER) | PkgDX T1 Mfg1 243 10t 11eer
31103 | 1 | 8 | 2 | 11 | 11 | 92900 | 0.7234 | 0.23615 | 0.03229 | 0.34792 | 0.0069968 | 0.1778 | 0 | 55 | -0.5264 | 0.032926 | -0.00010467 | -0.00032844 | -1.8702e-05 | -1.5429e-06 | 0.84846 | 0.062956 | -0.00090867 | -0.0094341 | -2.4202e-05 | 0.00017709 | 1.4679 | -0.041954 | 0.00046233 | 0.015563 | 0.00014848 | -0.00040077 | 37.7107 | -1.2268 | 0.0104 | 0.072822 | 0.00012566 | -0.0014541 | 0.0046725 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.96 | 1 | 2 | 0.5 | 0.5 | 0.88805 | 0.11195 | 0.79464 | 0.0029762 | 0.20238 | 2.4156 | 1.2739 | ; | Mfg1 | 244 | Elec | Mfg1 | Mfg1_244 | Pkg DX, Tier 1, Mfg1 244 (8 ton, 11 rated EER) | PkgDX T1 Mfg1 244 8t 11eer
31104 | 1 | 10 | 2 | 11 | 11 | 121900 | 0.6727 | 0.26313 | 0.02625 | 0.24656 | 0.0053322 | 0.1537 | 0 | 55 | -0.82834 | 0.051006 | -0.000317 | -0.0090596 | -2.6429e-05 | 0.0001466 | 2.4059 | 0.015506 | -0.00054067 | -0.010982 | -2.2345e-05 | 0.0001928 | 2.5275 | -0.090915 | 0.0010107 | 0.030759 | 0.00017397 | -0.00070154 | 32.5254 | -1.1432 | 0.010555 | 0.090537 | 0.00018097 | -0.0019705 | 0.0046725 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.96 | 1 | 2 | 0.5 | 0.5 | 0.86781 | 0.13219 | 0.51707 | 0.49854 | -0.01561 | 2.447 | 1.3776 | ; | Mfg1 | 245 | Elec | Mfg1 | Mfg1_245 | Pkg DX, Tier 1, Mfg1 245 (10 ton, 11 rated EER) | PkgDX T1 Mfg1 245 10t 11eer
31105 | 1 | 10 | 2 | 11 | 11 | 126050 | 0.685 | 0.25254 | 0.02856 | 0.3036 | 0.0055534 | 0.184 | 0 | 55 | 1.2687 | -0.021564 | 0.00031953 | 0.0029923 | -1.0833e-05 | -6.9875e-05 | 10.6378 | -0.23757 | 0.0014125 | 0.0011924 | -1.2833e-05 | -9.25e-06 | -0.21467 | 0.027625 | -0.00014375 | -0.0016213 | 0.000169 | -0.000214 | 28.5691 | -0.94648 | 0.0082748 | 0.031439 | 9.3479e-05 | -0.00080613 | 0.0046844 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.88191 | 0.11809 | 0.70173 | 0.11339 | 0.18488 | 2.3379 | 1.3287 | ; | Mfg3 | 246 | Elec | Mfg3 | Mfg3_246 | Pkg DX, Tier 1, Mfg3 246 (10 ton, 11 rated EER) | PkgDX T1 Mfg3 246 10t 11eer
31106 | 1 | 10 | 1 | 11 | 11 | 126050 | 0.685 | 0.24424 | 0.02856 | 0.3686 | 0.0055534 | 0.184 | 0 | 55 | 1.2687 | -0.021564 | 0.00031953 | 0.0029923 | -1.0833e-05 | -6.9875e-05 | 10.6378 | -0.23757 | 0.0014125 | 0.0011924 | -1.2833e-05 | -9.25e-06 | -0.21467 | 0.027625 | -0.00014375 | -0.0016213 | 0.000169 | -0.000214 | 28.5691 | -0.94648 | 0.0082748 | 0.031439 | 9.3479e-05 | -0.00080613 | 0.0046844 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.88191 | 0.11809 | 0.70173 | 0.11339 | 0.18488 | 2.6309 | 1.2888 | ; | Mfg3 | 247 | Gas | Mfg3 | Mfg3_247 | Pkg DX, Tier 1, Mfg3 247 (10 ton, 11 rated EER) | PkgDX T1 Mfg3 247 10t 11eer
31107 | 1 | 8 | 2 | 11 | 11 | 93000 | 0.71 | 0.25487 | 0.03226 | 0.206 | 0.0075269 | 0.2113 | 0 | 55 | 1.477 | -0.02803 | 0.00036797 | 0.0030072 | -1.175e-05 | -6.7625e-05 | 9.9387 | -0.21022 | 0.0011664 | -0.0028856 | -8.4167e-06 | 4.0875e-05 | -0.47133 | 0.034966 | -0.00019531 | -0.00064942 | 0.00017158 | -0.00023275 | 27.657 | -0.91752 | 0.0079172 | 0.048214 | 3.4466e-05 | -0.0008821 | 0.0046844 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.86828 | 0.13172 | 0.61381 | 0.25386 | 0.13233 | 2.194 | 1.3737 | ; | Mfg3 | 248 | Elec | Mfg3 | Mfg3_248 | Pkg DX, Tier 1, Mfg3 248 (8 ton, 11 rated EER) | PkgDX T1 Mfg3 248 8t 11eer
31108 | 1 | 9 | 2 | 11 | 11 | 106000 | 0.71 | 0.25225 | 0.03208 | 0.2474 | 0.0066038 | 0.2068 | 0 | 55 | 1.5482 | -0.031223 | 0.00039922 | 0.0044267 | -1.2667e-05 | -8.7125e-05 | 12.2822 | -0.279 | 0.0016688 | -0.0018461 | -1.0083e-05 | 2.925e-05 | -0.36281 | 0.035627 | -0.00021641 | -0.0046234 | 0.00017392 | -0.00018588 | 26.6275 | -0.89677 | 0.0078544 | 0.045035 | 4.4861e-05 | -0.00086179 | 0.0046844 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.87736 | 0.12264 | 0.78647 | -0.11866 | 0.33218 | 2.3238 | 1.3448 | ; | Mfg3 | 249 | Elec | Mfg3 | Mfg3_249 | Pkg DX, Tier 1, Mfg3 249 (9 ton, 11 rated EER) | PkgDX T1 Mfg3 249 9t 11eer
31109 | 1 | 10 | 2 | 11 | 11 | 125850 | 0.6975 | 0.24705 | 0.03019 | 0.3276 | 0.0055622 | 0.1924 | 0 | 55 | 1.4907 | -0.027455 | 0.00036172 | 0.0030271 | -1.0583e-05 | -7.3375e-05 | 11.6692 | -0.26219 | 0.0015578 | -0.0016208 | -1.0083e-05 | 2.35e-05 | -0.27666 | 0.031122 | -0.00017656 | -0.0029632 | 0.00017083 | -0.0002005 | 27.7519 | -0.93639 | 0.0082232 | 0.04347 | 6.057e-05 | -0.0008804 | 0.0046844 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.8766 | 0.1234 | 0.72352 | 0.039286 | 0.23719 | 2.3715 | 1.3023 | ; | Mfg3 | 250 | Elec | Mfg3 | Mfg3_250 | Pkg DX, Tier 1, Mfg3 250 (10 ton, 11 rated EER) | PkgDX T1 Mfg3 250 10t 11eer
31110 | 1 | 8 | 1 | 11 | 11 | 93000 | 0.71 | 0.25487 | 0.03226 | 0.206 | 0.0075269 | 0.2113 | 0 | 55 | 1.477 | -0.02803 | 0.00036797 | 0.0030072 | -1.175e-05 | -6.7625e-05 | 9.9387 | -0.21022 | 0.0011664 | -0.0028856 | -8.4167e-06 | 4.0875e-05 | -0.47133 | 0.034966 | -0.00019531 | -0.00064942 | 0.00017158 | -0.00023275 | 27.657 | -0.91752 | 0.0079172 | 0.048214 | 3.4466e-05 | -0.0008821 | 0.0046844 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.86828 | 0.13172 | 0.61381 | 0.25386 | 0.13233 | 2.194 | 1.3737 | ; | Mfg3 | 251 | Gas | Mfg3 | Mfg3_251 | Pkg DX, Tier 1, Mfg3 251 (8 ton, 11 rated EER) | PkgDX T1 Mfg3 251 8t 11eer
31111 | 1 | 9 | 1 | 11 | 11 | 106000 | 0.71 | 0.25225 | 0.03208 | 0.2474 | 0.0066038 | 0.2068 | 0 | 55 | 1.5482 | -0.031223 | 0.00039922 | 0.0044267 | -1.2667e-05 | -8.7125e-05 | 12.2822 | -0.279 | 0.0016688 | -0.0018461 | -1.0083e-05 | 2.925e-05 | -0.36281 | 0.035627 | -0.00021641 | -0.0046234 | 0.00017392 | -0.00018588 | 26.6275 | -0.89677 | 0.0078544 | 0.045035 | 4.4861e-05 | -0.00086179 | 0.0046844 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.87736 | 0.12264 | 0.78647 | -0.11866 | 0.33218 | 2.3238 | 1.3448 | ; | Mfg3 | 252 | Gas | Mfg3 | Mfg3_252 | Pkg DX, Tier 1, Mfg3 252 (9 ton, 11 rated EER) | PkgDX T1 Mfg3 252 9t 11eer
31112 | 1 | 10 | 1 | 11 | 11 | 125850 | 0.6975 | 0.24314 | 0.03019 | 0.3566 | 0.0055622 | 0.1924 | 0 | 55 | 1.4907 | -0.027455 | 0.00036172 | 0.0030271 | -1.0583e-05 | -7.3375e-05 | 11.6692 | -0.26219 | 0.0015578 | -0.0016208 | -1.0083e-05 | 2.35e-05 | -0.27666 | 0.031122 | -0.00017656 | -0.0029632 | 0.00017083 | -0.0002005 | 27.7519 | -0.93639 | 0.0082232 | 0.04347 | 6.057e-05 | -0.0008804 | 0.0046844 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.8766 | 0.1234 | 0.72352 | 0.039286 | 0.23719 | 2.384 | 1.2837 | ; | Mfg3 | 253 | Gas | Mfg3 | Mfg3_253 | Pkg DX, Tier 1, Mfg3 253 (10 ton, 11 rated EER) | PkgDX T1 Mfg3 253 10t 11eer
31113 | 1 | 9 | 2 | 11.2 | 11.2 | 105900 | 0.72 | 0.24681 | 0.03211 | 0.2474 | 0.00661 | 0.1816 | 0 | 55 | 1.492 | -0.030577 | 0.00039766 | 0.0047776 | -1.575e-05 | -8.4875e-05 | 9.9557 | -0.21312 | 0.0011992 | -0.0015784 | -1.3417e-05 | 3.3125e-05 | -0.42636 | 0.034609 | -0.00020469 | -0.0012567 | 0.00016567 | -0.000212 | 30.7459 | -0.99313 | 0.0083967 | 0.041911 | 6.4469e-05 | -0.00085825 | 0.0046844 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.87252 | 0.12748 | 0.59494 | 0.30161 | 0.10345 | 2.3238 | 1.3447 | ; | Mfg3 | 254 | Elec | Mfg3 | Mfg3_254 | Pkg DX, Tier 1, Mfg3 254 (9 ton, 11.2 rated EER) | PkgDX T1 Mfg3 254 9t 11.2eer
31114 | 1 | 9 | 1 | 11.2 | 11.2 | 105900 | 0.72 | 0.24681 | 0.03211 | 0.2474 | 0.00661 | 0.1816 | 0 | 55 | 1.492 | -0.030577 | 0.00039766 | 0.0047776 | -1.575e-05 | -8.4875e-05 | 9.9557 | -0.21312 | 0.0011992 | -0.0015784 | -1.3417e-05 | 3.3125e-05 | -0.42636 | 0.034609 | -0.00020469 | -0.0012567 | 0.00016567 | -0.000212 | 30.7459 | -0.99313 | 0.0083967 | 0.041911 | 6.4469e-05 | -0.00085825 | 0.0046844 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.87252 | 0.12748 | 0.59494 | 0.30161 | 0.10345 | 2.3238 | 1.3447 | ; | Mfg3 | 255 | Gas | Mfg3 | Mfg3_255 | Pkg DX, Tier 1, Mfg3 255 (9 ton, 11.2 rated EER) | PkgDX T1 Mfg3 255 9t 11.2eer
31115 | 1 | 8 | 2 | 11.3 | 11.3 | 93800 | 0.72 | 0.24729 | 0.03198 | 0.206 | 0.0074627 | 0.1785 | 0 | 55 | 1.5429 | -0.02993 | 0.00038359 | 0.0032007 | -1.1583e-05 | -7.2125e-05 | 9.245 | -0.19368 | 0.0010766 | 0.00043025 | -8.1667e-06 | -1.075e-05 | -0.5596 | 0.038342 | -0.00022422 | -0.00090771 | 0.00016925 | -0.00022688 | 39.4577 | -1.2594 | 0.010365 | 0.0327 | 3.5655e-05 | -0.00063403 | 0.0046844 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.96 | 1 | 2 | 0.5 | 0.5 | 0.87207 | 0.12793 | 0.40387 | 0.64943 | -0.053305 | 2.194 | 1.375 | ; | Mfg3 | 256 | Elec | Mfg3 | Mfg3_256 | Pkg DX, Tier 1, Mfg3 256 (8 ton, 11.3 rated EER) | PkgDX T1 Mfg3 256 8t 11.3eer
31116 | 1 | 8 | 1 | 11.3 | 11.3 | 93800 | 0.72 | 0.24729 | 0.03198 | 0.206 | 0.0074627 | 0.1785 | 0 | 55 | 1.5429 | -0.02993 | 0.00038359 | 0.0032007 | -1.1583e-05 | -7.2125e-05 | 9.245 | -0.19368 | 0.0010766 | 0.00043025 | -8.1667e-06 | -1.075e-05 | -0.5596 | 0.038342 | -0.00022422 | -0.00090771 | 0.00016925 | -0.00022688 | 39.4577 | -1.2594 | 0.010365 | 0.0327 | 3.5655e-05 | -0.00063403 | 0.0046844 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.87207 | 0.12793 | 0.40387 | 0.64943 | -0.053305 | 2.194 | 1.375 | ; | Mfg3 | 257 | Gas | Mfg3 | Mfg3_257 | Pkg DX, Tier 1, Mfg3 257 (8 ton, 11.3 rated EER) | PkgDX T1 Mfg3 257 8t 11.3eer
31117 | 1 | 10 | 2 | 11 | 11 | 124300 | 0.70233 | 0.2446 | 0.02735 | 0.3865 | 0.0053902 | 0.0935 | 0 | 55 | 1.423 | -0.029961 | 0.00035125 | 0.0049155 | -5.081e-05 | -1.25e-07 | 5.492 | -0.079206 | 0.00016375 | -0.0048597 | -4.0071e-05 | 0.00014187 | -1.0767 | 0.032299 | -9.125e-05 | 0.015174 | 0.00013702 | -0.00037013 | 31.0497 | -1.2069 | 0.011945 | 0.14377 | 0.00034559 | -0.0030765 | 0.0046844 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.81861 | 0.18139 | 0.53265 | 0.46735 | 0 | 2.1277 | 1.2879 | ; | Mfg5 | 258 | Elec | Mfg5 | Mfg5_258 | Pkg DX, Tier 1, Mfg5 258 (10 ton, 11 rated EER) | PkgDX T1 Mfg5 258 10t 11eer
31118 | 1 | 7.5 | 2 | 11.3 | 11.3 | 89300 | 0.74244 | 0.23766 | 0.0294 | 0.2968 | 0.0075028 | 0.0436 | 0 | 55 | -2.3706 | 0.078009 | -0.00048938 | 0.013592 | -0.00010531 | 0 | 0.89795 | 0.045317 | -0.00070625 | 0.0053697 | -7.1524e-05 | 5.8375e-05 | 5.6284 | -0.14725 | 0.0012606 | -0.003891 | 0.00024507 | -0.00035562 | 159.1383 | -4.5568 | 0.03363 | -0.13477 | 0.00098589 | 1.7293e-05 | 0.0046844 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.81884 | 0.18116 | 0.50052 | 0.52613 | -0.026649 | 2.0018 | 1.3275 | ; | Mfg5 | 259 | Elec | Mfg5 | Mfg5_259 | Pkg DX, Tier 1, Mfg5 259 (7.5 ton, 11.3 rated EER) | PkgDX T1 Mfg5 259 7.5t 11.3eer
31119 | 1 | 8.5 | 1 | 11 | 11 | 106200 | 0.7072 | 0.2043 | 0.03202 | 0.583 | 0.0065913 | 0.2128 | 0 | 55 | 4.9312 | -0.12387 | 0.0010622 | 0.00011348 | -3.125e-05 | -2.024e-05 | -1.4918 | 0.17575 | -0.0020476 | -0.033273 | -4.0875e-05 | 0.00054014 | -4.7157 | 0.17311 | -0.0012176 | -0.0074338 | 0.00021993 | -0.00026636 | 76.8003 | -2.6578 | 0.022424 | 0.18023 | -7.9351e-05 | -0.0023249 | 0.0046725 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.80091 | 0.19909 | 0.16378 | 1.2197 | -0.38349 | 2.4269 | 1.1274 | ; | Mfg6 | 260 | Gas | Mfg6 | Mfg6_260 | Pkg DX, Tier 1, Mfg6 260 (8.5 ton, 11 rated EER) | PkgDX T1 Mfg6 260 8.5t 11eer
31120 | 1 | 10 | 1 | 11 | 11 | 121000 | 0.7521 | 0.19241 | 0.03174 | 0.532 | 0.012397 | 0.0896 | 0 | 55 | 2.9828 | -0.081901 | 0.0008426 | 0.0098334 | -3.9821e-05 | -0.00013396 | -5.638 | 0.26505 | -0.0024834 | -0.013673 | -5.2964e-05 | 0.00028348 | 0.66515 | 0.027057 | -0.0002258 | -0.015946 | 0.00018852 | -0.00010226 | 208.5874 | -6.4651 | 0.052113 | 0.065483 | 0.0010398 | -0.0037654 | 0.0046725 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.74795 | 0.25205 | 0.44526 | 0.48253 | 0.07221 | 1.0029 | 1.1609 | ; | Mfg6 | 261 | Gas | Mfg6 | Mfg6_261 | Pkg DX, Tier 1, Mfg6 261 (10 ton, 11 rated EER) | PkgDX T1 Mfg6 261 10t 11eer
31121 | 1 | 10 | 2 | 11.13 | 11.13 | 127800 | 0.741 | 0.18384 | 0.0313 | 0.593 | 0.011737 | 0.1055 | 0 | 55 | 2.3075 | -0.061886 | 0.00071333 | 0.010479 | -2.8451e-05 | -0.00017315 | -4.0434 | 0.23215 | -0.0022932 | -0.021761 | -2.5045e-05 | 0.00032623 | -1.9707 | 0.092879 | -0.000654 | -0.011707 | 0.0002541 | -0.00023528 | 159.0871 | -5.3653 | 0.044917 | 0.29699 | 0.00010437 | -0.0046194 | 0.0046725 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.80282 | 0.19718 | 0.22703 | 0.94192 | -0.16895 | 2.5237 | 1.1294 | ; | Mfg6 | 262 | Elec | Mfg6 | Mfg6_262 | Pkg DX, Tier 1, Mfg6 262 (10 ton, 11.13 rated EER) | PkgDX T1 Mfg6 262 10t 11.13eer
31122 | 1 | 10 | 0 | 11.32 | 11.32 | 120720 | 0.7518 | 0.19309 | 0.03181 | 0.467 | 0.012425 | 0.0923 | 0 | 55 | 2.9617 | -0.080017 | 0.0008292 | 0.0091547 | -3.5732e-05 | -0.0001367 | -5.6905 | 0.26557 | -0.0024856 | -0.012874 | -5.6375e-05 | 0.00028078 | 0.69559 | 0.023419 | -0.0002002 | -0.014443 | 0.00017925 | -9.608e-05 | 205.4775 | -6.3131 | 0.050745 | 0.026688 | 0.0011389 | -0.0034738 | 0.0046725 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.74553 | 0.25447 | 0.63204 | 0.1218 | 0.24616 | 0.6545 | 1.2003 | ; | Mfg6 | 263 | None | Mfg6 | Mfg6_263 | Pkg DX, Tier 1, Mfg6 263 (10 ton, 11.32 rated EER) | PkgDX T1 Mfg6 263 10t 11.32eer
31201 | 2 | 9 | 1 | 11.6 | 11.6 | 106200 | 0.6874 | 0.2411 | 0.02825 | 0.25833 | 0.0061205 | 0.1676 | 0 | 55 | 0.98552 | -0.0033441 | 3.7333e-05 | -0.0067015 | -5.5113e-05 | 0.00018931 | 2.9518 | 0.008576 | -0.00062067 | -0.0138 | -5.4452e-05 | 0.000324 | -0.10982 | -0.0051791 | 0.00040467 | 0.024727 | 0.00022051 | -0.00073823 | 56.7095 | -2.0002 | 0.018323 | 0.14853 | 0.00033817 | -0.0033165 | 0.0046725 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.96 | 1 | 2 | 0.5 | 0.5 | 0.82009 | 0.17991 | 0.48402 | 0.49987 | 0.016116 | 2.4344 | 1.359 | ; | Mfg1 | 264 | Gas | Mfg1 | Mfg1_264 | Pkg DX, Tier 2, Mfg1 264 (9 ton, 11.6 rated EER) | PkgDX T2 Mfg1 264 9t 11.6eer
31202 | 2 | 9 | 2 | 11.8 | 11.8 | 106200 | 0.6874 | 0.24183 | 0.02825 | 0.21333 | 0.0061205 | 0.1676 | 0 | 55 | 0.98552 | -0.0033441 | 3.7333e-05 | -0.0067015 | -5.5113e-05 | 0.00018931 | 2.9518 | 0.008576 | -0.00062067 | -0.0138 | -5.4452e-05 | 0.000324 | -0.10982 | -0.0051791 | 0.00040467 | 0.024727 | 0.00022051 | -0.00073823 | 56.7095 | -2.0002 | 0.018323 | 0.14853 | 0.00033817 | -0.0033165 | 0.0046725 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.96 | 1 | 2 | 0.5 | 0.5 | 0.82009 | 0.17991 | 0.48402 | 0.49987 | 0.016116 | 2.4246 | 1.3877 | ; | Mfg1 | 265 | Elec | Mfg1 | Mfg1_265 | Pkg DX, Tier 2, Mfg1 265 (9 ton, 11.8 rated EER) | PkgDX T2 Mfg1 265 9t 11.8eer
31203 | 2 | 8.5 | 2 | 11.6 | 11.6 | 104000 | 0.80769 | 0.20895 | 0.0351 | 0.4082 | 0.0064423 | 0.0513 | 0 | 55 | -1.7902 | 0.050661 | -0.00030625 | 0.020678 | -0.00013236 | 1.25e-07 | -2.6727 | 0.14405 | -0.001555 | 0.0084771 | -0.00013781 | 0.00022625 | 2.4661 | -0.042663 | 0.000415 | -0.011937 | 0.00022029 | -0.00020813 | 199.7011 | -5.6356 | 0.045046 | -0.10168 | 0.0026908 | -0.0059622 | 0.0046844 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.81673 | 0.18327 | 0.52758 | 0.48037 | -0.0079499 | 1.9789 | 1.2107 | ; | Mfg5 | 266 | Elec | Mfg5 | Mfg5_266 | Pkg DX, Tier 2, Mfg5 266 (8.5 ton, 11.6 rated EER) | PkgDX T2 Mfg5 266 8.5t 11.6eer
31204 | 2 | 6.5 | 1 | 11.5 | 11.5 | 78800 | 0.7348 | 0.22327 | 0.03299 | 0.296 | 0.0088832 | 0.1669 | 0 | 55 | 4.0816 | -0.097981 | 0.0008936 | 0.00097866 | -2.0821e-05 | -6.808e-05 | -3.8666 | 0.23938 | -0.0024284 | -0.028292 | -2.6839e-05 | 0.00041778 | -2.6805 | 0.1149 | -0.0007988 | -0.01156 | 0.00022537 | -0.0002149 | 111.7657 | -3.7495 | 0.031694 | 0.19083 | 0.00023759 | -0.0034713 | 0.0046725 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.82487 | 0.17513 | 0.11572 | 1.2712 | -0.38687 | 1.8727 | 1.305 | ; | Mfg6 | 267 | Gas | Mfg6 | Mfg6_267 | Pkg DX, Tier 2, Mfg6 267 (6.5 ton, 11.5 rated EER) | PkgDX T2 Mfg6 267 6.5t 11.5eer
31205 | 2 | 7.5 | 1 | 11.5 | 11.5 | 91500 | 0.7399 | 0.2012 | 0.03279 | 0.479 | 0.0076503 | 0.1489 | 0 | 55 | 3.8762 | -0.080375 | 0.0006952 | -0.0058029 | -7.625e-06 | 1.3e-06 | -3.5882 | 0.22951 | -0.002352 | -0.028581 | -2.3214e-05 | 0.0004232 | -2.6103 | 0.093308 | -0.0005964 | 0.0014403 | 0.00016655 | -0.00025202 | 110.6983 | -3.6033 | 0.031061 | 0.14777 | 0.00071559 | -0.0044315 | 0.0046725 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.83825 | 0.16175 | 0.26736 | 0.96898 | -0.23634 | 2.4011 | 1.1836 | ; | Mfg6 | 268 | Gas | Mfg6 | Mfg6_268 | Pkg DX, Tier 2, Mfg6 268 (7.5 ton, 11.5 rated EER) | PkgDX T2 Mfg6 268 7.5t 11.5eer
31206 | 2 | 10 | 1 | 11.5 | 11.5 | 127800 | 0.741 | 0.18367 | 0.0313 | 0.527 | 0.011737 | 0.1055 | 0 | 55 | 2.3075 | -0.061886 | 0.00071333 | 0.010479 | -2.8451e-05 | -0.00017315 | -4.0434 | 0.23215 | -0.0022932 | -0.021761 | -2.5045e-05 | 0.00032623 | -1.9707 | 0.092879 | -0.000654 | -0.011707 | 0.0002541 | -0.00023528 | 159.0871 | -5.3653 | 0.044917 | 0.29699 | 0.00010437 | -0.0046194 | 0.0046725 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.80282 | 0.19718 | 0.22703 | 0.94192 | -0.16895 | 2.5943 | 1.1684 | ; | Mfg6 | 269 | Gas | Mfg6 | Mfg6_269 | Pkg DX, Tier 2, Mfg6 269 (10 ton, 11.5 rated EER) | PkgDX T2 Mfg6 269 10t 11.5eer
31301 | 3 | 10 | 1 | 12 | 12 | 122800 | 0.7191 | 0.22282 | 0.0285 | 0.29171 | 0.0073697 | 0.0809 | 0 | 55 | 1.6167 | -0.04174 | 0.00054701 | 0.0091425 | -2.2362e-05 | -0.00014805 | -2.7216 | 0.16222 | -0.0015761 | -0.0070183 | -2.3635e-05 | 0.00012695 | -1.2476 | 0.057195 | -0.00042124 | 0.00027201 | 0.00015816 | -0.00018016 | 132.1118 | -4.1085 | 0.031891 | 0.13979 | -6.2733e-05 | -0.0018404 | 0.0046725 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.96 | 1 | 2 | 0.5 | 0.5 | 0.81189 | 0.18811 | 0.38165 | 0.67384 | -0.055493 | 2.4765 | 1.3365 | ; | Mfg1 | 270 | Gas | Mfg1 | Mfg1_270 | Pkg DX, Tier 3, Mfg1 270 (10 ton, 12 rated EER) | PkgDX T3 Mfg1 270 10t 12eer
31302 | 3 | 8.5 | 1 | 12.2 | 12.2 | 104800 | 0.6966 | 0.23492 | 0.02863 | 0.22833 | 0.004771 | 0.151 | 0 | 55 | 1.2083 | -0.029129 | 0.00045293 | 0.007951 | -1.7713e-05 | -0.00013911 | -1.5245 | 0.12326 | -0.001247 | -0.0061851 | -1.3768e-05 | 9.0451e-05 | -0.91139 | 0.046046 | -0.00035271 | 0.0033689 | 0.00013901 | -0.00018303 | 51.0819 | -1.5768 | 0.012076 | 0.071654 | -0.00014934 | -0.0006442 | 0.0046725 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.955 | 1 | 2 | 0.5 | 0.5 | 0.80094 | 0.19906 | 0.40297 | 0.69776 | -0.10073 | 2.2376 | 1.3761 | ; | Mfg1 | 271 | Gas | Mfg1 | Mfg1_271 | Pkg DX, Tier 3, Mfg1 271 (8.5 ton, 12.2 rated EER) | PkgDX T3 Mfg1 271 8.5t 12.2eer
31303 | 3 | 10 | 2 | 12.2 | 12.2 | 122800 | 0.7191 | 0.21829 | 0.0285 | 0.29171 | 0.0073697 | 0.0809 | 0 | 55 | 1.6167 | -0.04174 | 0.00054701 | 0.0091425 | -2.2362e-05 | -0.00014805 | -2.7216 | 0.16222 | -0.0015761 | -0.0070183 | -2.3635e-05 | 0.00012695 | -1.2476 | 0.057195 | -0.00042124 | 0.00027201 | 0.00015816 | -0.00018016 | 132.1118 | -4.1085 | 0.031891 | 0.13979 | -6.2733e-05 | -0.0018404 | 0.0046725 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.96 | 1 | 2 | 0.5 | 0.5 | 0.81189 | 0.18811 | 0.38165 | 0.67384 | -0.055493 | 2.4765 | 1.3365 | ; | Mfg1 | 272 | Elec | Mfg1 | Mfg1_272 | Pkg DX, Tier 3, Mfg1 272 (10 ton, 12.2 rated EER) | PkgDX T3 Mfg1 272 10t 12.2eer
31304 | 3 | 8.6 | 2 | 12.4 | 12.4 | 104800 | 0.6966 | 0.23321 | 0.02863 | 0.20667 | 0.004771 | 0.151 | 0 | 55 | 1.2083 | -0.029129 | 0.00045293 | 0.007951 | -1.7713e-05 | -0.00013911 | -1.5245 | 0.12326 | -0.001247 | -0.0061851 | -1.3768e-05 | 9.0451e-05 | -0.91139 | 0.046046 | -0.00035271 | 0.0033689 | 0.00013901 | -0.00018303 | 51.0819 | -1.5768 | 0.012076 | 0.071654 | -0.00014934 | -0.0006442 | 0.0046725 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.955 | 1 | 2 | 0.5 | 0.5 | 0.80094 | 0.19906 | 0.40297 | 0.69776 | -0.10073 | 2.5183 | 1.3902 | ; | Mfg1 | 273 | Elec | Mfg1 | Mfg1_273 | Pkg DX, Tier 3, Mfg1 273 (8.6 ton, 12.4 rated EER) | PkgDX T3 Mfg1 273 8.6t 12.4eer
31305 | 3 | 7.4 | 1 | 12.5 | 12.5 | 90700 | 0.7806 | 0.22141 | 0.03308 | 0.22833 | 0.0055127 | 0.0577 | 0 | 55 | 2.0406 | -0.056816 | 0.00066844 | 0.010513 | -2.5378e-05 | -0.00015778 | -5.359 | 0.23546 | -0.0021103 | -0.006385 | -3.6316e-05 | 0.0001556 | -2.0067 | 0.086239 | -0.00066228 | -0.0036201 | 0.00017805 | -0.00016673 | 187.0364 | -5.5884 | 0.043744 | 0.1869 | 0.00089336 | -0.0053098 | 0.0046725 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.96 | 1 | 2 | 0.5 | 0.5 | 0.81918 | 0.18082 | 0.45198 | 0.52542 | 0.022599 | 2.4059 | 1.3533 | ; | Mfg1 | 274 | Gas | Mfg1 | Mfg1_274 | Pkg DX, Tier 3, Mfg1 274 (7.4 ton, 12.5 rated EER) | PkgDX T3 Mfg1 274 7.4t 12.5eer
31306 | 3 | 7.4 | 2 | 12.7 | 12.7 | 90700 | 0.7806 | 0.22033 | 0.03308 | 0.20667 | 0.0055127 | 0.0577 | 0 | 55 | 2.0406 | -0.056816 | 0.00066844 | 0.010513 | -2.5378e-05 | -0.00015778 | -5.359 | 0.23546 | -0.0021103 | -0.006385 | -3.6316e-05 | 0.0001556 | -2.0067 | 0.086239 | -0.00066228 | -0.0036201 | 0.00017805 | -0.00016673 | 187.0364 | -5.5884 | 0.043744 | 0.1869 | 0.00089336 | -0.0053098 | 0.0046725 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.96 | 1 | 2 | 0.5 | 0.5 | 0.81918 | 0.18082 | 0.45198 | 0.52542 | 0.022599 | 2.3798 | 1.3694 | ; | Mfg1 | 275 | Elec | Mfg1 | Mfg1_275 | Pkg DX, Tier 3, Mfg1 275 (7.4 ton, 12.7 rated EER) | PkgDX T3 Mfg1 275 7.4t 12.7eer
31307 | 3 | 10 | 0 | 11.94 | 11.94 | 127800 | 0.741 | 0.18369 | 0.0313 | 0.452 | 0.011737 | 0.1055 | 0 | 55 | 2.3075 | -0.061886 | 0.00071333 | 0.010479 | -2.8451e-05 | -0.00017315 | -4.0434 | 0.23215 | -0.0022932 | -0.021761 | -2.5045e-05 | 0.00032623 | -1.9707 | 0.092879 | -0.000654 | -0.011707 | 0.0002541 | -0.00023528 | 159.0871 | -5.3653 | 0.044917 | 0.29699 | 0.00010437 | -0.0046194 | 0.0046725 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.80282 | 0.19718 | 0.22703 | 0.94192 | -0.16895 | 2.6878 | 1.2143 | ; | Mfg6 | 276 | None | Mfg6 | Mfg6_276 | Pkg DX, Tier 3, Mfg6 276 (10 ton, 11.94 rated EER) | PkgDX T3 Mfg6 276 10t 11.94eer
; Indep. ; 1: ;; Dependents 1: Dual Compressor A/C, 10 - 20 ton Units, from: "12-20 ton Pkg Unit Perf Curves (2008 DEER).xls" | ;
32001 | 0 | 15 | 2 | 8.4 | 8.4 | 179900 | 0.72207 | 0.29274 | 0.02724 | 0.651 | 0.008338 | 0.0291 | 0 | 55 | 0.14133 | 0.012779 | -2.4375e-05 | 0.0066796 | -5.8357e-05 | 6.25e-07 | 3.3824 | -0.030643 | -0.00010187 | 0.0052361 | -4.2167e-05 | 1.75e-06 | 0.53499 | -0.004145 | 0.00011875 | 0.0017147 | 0.00012543 | -0.0001705 | 68.0845 | -1.5356 | 0.0098582 | -0.27296 | 0.0012431 | 0.00098297 | 0.0046844 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.81795 | 0.18205 | 0.52271 | 0.48691 | -0.0096228 | 2.9063 | 1.1449 | ; | Mfg5 | 278 | Elec | Mfg5 | Mfg5_278 | Pkg DX, Tier 0, Mfg5 278 (15 ton, 8.4 rated EER) | PkgDX T0 Mfg5 278 15t 8.4eer
32002 | 0 | 15 | 2 | 8.4 | 8.4 | 184000 | 0.7663 | 0.28159 | 0.03261 | 0.56 | 0.01087 | 0.079 | 0 | 55 | 3.6486 | -0.095641 | 0.0009375 | 0.0053953 | -1.6875e-05 | -0.00012716 | -4.3204 | 0.22864 | -0.002181 | -0.017463 | -2.2125e-05 | 0.00025936 | -1.2944 | 0.063137 | -0.0004935 | -0.0010759 | 9.4e-05 | -7.332e-05 | 177.1978 | -5.5893 | 0.044656 | 0.1935 | 0.00038524 | -0.0037763 | 0.0034466 | 1.0125 | 0.059111 | -0.072068 | 0.91241 | 0.24998 | -0.35145 | 0.1856 | 0.925 | 1 | 2 | 0.33 | 0.33 | 0.74252 | 0.25748 | 0.18913 | 0.98424 | -0.17336 | 2.1316 | 1.135 | ; | Mfg6 | 279 | Elec | Mfg6 | Mfg6_279 | Pkg DX, Tier 0, Mfg6 279 (15 ton, 8.4 rated EER) | PkgDX T0 Mfg6 279 15t 8.4eer
32003 | 0 | 20 | 2 | 8.4 | 8.4 | 250000 | 0.752 | 0.29165 | 0.032 | 0.569 | 0.008 | 0.0973 | 0 | 55 | 2.782 | -0.08028 | 0.00092 | 0.010254 | 0 | -0.0002368 | -3.8367 | 0.20344 | -0.0017952 | -0.013348 | 2.9937e-05 | 4.134e-05 | -0.98141 | 0.06172 | -0.00064125 | -0.0047988 | 4.2563e-05 | 0.00012514 | 115.0609 | -3.5459 | 0.025392 | 0.12482 | -0.00062208 | 0.00051573 | 0.0046725 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.74356 | 0.25644 | 0.85482 | -0.45557 | 0.60075 | 2.8464 | 1.136 | ; | Mfg6 | 280 | Elec | Mfg6 | Mfg6_280 | Pkg DX, Tier 0, Mfg6 280 (20 ton, 8.4 rated EER) | PkgDX T0 Mfg6 280 20t 8.4eer
32004 | 0 | 15 | 1 | 8.5 | 8.5 | 184000 | 0.7663 | 0.28153 | 0.03261 | 0.532 | 0.01087 | 0.079 | 0 | 55 | 3.6486 | -0.095641 | 0.0009375 | 0.0053953 | -1.6875e-05 | -0.00012716 | -4.3204 | 0.22864 | -0.002181 | -0.017463 | -2.2125e-05 | 0.00025936 | -1.2944 | 0.063137 | -0.0004935 | -0.0010759 | 9.4e-05 | -7.332e-05 | 177.1978 | -5.5893 | 0.044656 | 0.1935 | 0.00038524 | -0.0037763 | 0.0034466 | 1.0125 | 0.059111 | -0.072068 | 0.91241 | 0.24998 | -0.35145 | 0.1856 | 0.925 | 1 | 2 | 0.33 | 0.33 | 0.74252 | 0.25748 | 0.18913 | 0.98424 | -0.17336 | 2.195 | 1.1521 | ; | Mfg6 | 281 | Gas | Mfg6 | Mfg6_281 | Pkg DX, Tier 0, Mfg6 281 (15 ton, 8.5 rated EER) | PkgDX T0 Mfg6 281 15t 8.5eer
32005 | 0 | 20 | 1 | 8.5 | 8.5 | 250000 | 0.752 | 0.29578 | 0.032 | 0.513 | 0.008 | 0.0973 | 0 | 55 | 2.782 | -0.08028 | 0.00092 | 0.010254 | 0 | -0.0002368 | -3.8367 | 0.20344 | -0.0017952 | -0.013348 | 2.9937e-05 | 4.134e-05 | -0.98141 | 0.06172 | -0.00064125 | -0.0047988 | 4.2563e-05 | 0.00012514 | 115.0609 | -3.5459 | 0.025392 | 0.12482 | -0.00062208 | 0.00051573 | 0.0046725 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.74356 | 0.25644 | 0.85482 | -0.45557 | 0.60075 | 2.6568 | 1.1699 | ; | Mfg6 | 282 | Gas | Mfg6 | Mfg6_282 | Pkg DX, Tier 0, Mfg6 282 (20 ton, 8.5 rated EER) | PkgDX T0 Mfg6 282 20t 8.5eer
32006 | 0 | 20 | 2 | 8.7 | 8.7 | 245000 | 0.7184 | 0.26887 | 0.03265 | 0.49025 | 0.013878 | 0.1995 | 0 | 55 | 1.7367 | -0.043706 | 0.0005228 | 0.0078583 | -1.9452e-05 | -0.0001141 | 0.82657 | 0.050142 | -0.0007044 | -0.0054374 | -2.1667e-05 | 0.0001081 | -0.50542 | 0.031379 | -0.0002176 | 0.0034301 | 0.00010288 | -0.0001374 | 11.7328 | -0.34793 | 0.0031731 | 0.06738 | 0.00019103 | -0.0015382 | 0.0046725 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.86939 | 0.13061 | 0.38636 | 0.79545 | -0.18182 | 2.1125 | 1.1778 | ; | Mfg1 | 283 | Elec | Mfg1 | Mfg1_283 | Pkg DX, Tier 0, Mfg1 283 (20 ton, 8.7 rated EER) | PkgDX T0 Mfg1 283 20t 8.7eer
32007 | 0 | 18 | 2 | 8.8 | 8.8 | 216800 | 0.7279 | 0.30183 | 0.03321 | 0.43667 | 0.0050738 | 0.1893 | 0 | 55 | 1.4774 | -0.031341 | 0.0004164 | 0.0055428 | -1.1643e-05 | -0.000105 | 0.11663 | 0.078332 | -0.0009432 | -0.010209 | -1.2405e-05 | 0.0001494 | -0.53322 | 0.031696 | -0.0002316 | 0.0031763 | 9.3429e-05 | -0.0001093 | 12.4298 | -0.34992 | 0.0027504 | 0.063372 | 6.3704e-05 | -0.0010884 | 0.0040028 | 0.9901 | 0.095998 | -0.086528 | 0.92022 | 0.2688 | -0.4089 | 0.21568 | 0.925 | 1 | 2 | 0.4 | 0.5 | 0.86716 | 0.13284 | 0.43726 | 0.69962 | -0.13688 | 2.0598 | 1.2073 | ; | Mfg1 | 284 | Elec | Mfg1 | Mfg1_284 | Pkg DX, Tier 0, Mfg1 284 (18 ton, 8.8 rated EER) | PkgDX T0 Mfg1 284 18t 8.8eer
32008 | 0 | 12.5 | 2 | 8.8 | 8.8 | 152800 | 0.7644 | 0.2787 | 0.03141 | 0.6254 | 0.004712 | 0.0488 | 0 | 55 | 2.639 | -0.073265 | 0.00063313 | 0.015384 | -0.00011402 | -7.5e-07 | 6.9169 | -0.12091 | 0.00040187 | -0.0030301 | -8.4571e-05 | 0.00022487 | 3.8253 | -0.085995 | 0.00078125 | -0.0089938 | 0.0002335 | -0.0002865 | 57.3438 | -1.8866 | 0.017596 | 0.16718 | 0.0013181 | -0.0057675 | 0.0046844 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.81839 | 0.18161 | 0.53339 | 0.46661 | 0 | 2.7069 | 1.1095 | ; | Mfg5 | 285 | Elec | Mfg5 | Mfg5_285 | Pkg DX, Tier 0, Mfg5 285 (12.5 ton, 8.8 rated EER) | PkgDX T0 Mfg5 285 12.5t 8.8eer
32009 | 0 | 15 | 2 | 8.9 | 8.9 | 186000 | 0.6989 | 0.30679 | 0.03226 | 0.371 | 0.005914 | 0.2403 | 0 | 55 | 1.257 | -0.023847 | 0.0003644 | 0.0040942 | -7.6667e-06 | -9.66e-05 | 2.6912 | 0.0004981 | -0.0003384 | -0.0090284 | -3.6905e-06 | 0.0001077 | -0.38911 | 0.024654 | -0.0001696 | 0.0056059 | 9.1024e-05 | -0.0001344 | -0.26151 | 0.014458 | 6.2765e-05 | 0.0513 | 6.0911e-06 | -0.00077258 | 0.0046725 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.85561 | 0.14439 | 0.66154 | 0.25641 | 0.082051 | 2.1458 | 1.2586 | ; | Mfg1 | 286 | Elec | Mfg1 | Mfg1_286 | Pkg DX, Tier 0, Mfg1 286 (15 ton, 8.9 rated EER) | PkgDX T0 Mfg1 286 15t 8.9eer
32010 | 0 | 12.5 | 2 | 9 | 9 | 150000 | 0.75 | 0.3027 | 0.032 | 0.3192 | 0.0083333 | 0.1024 | 0 | 55 | 1.5084 | -0.027855 | 0.00035547 | 0.003138 | -1.275e-05 | -6.6125e-05 | 4.0955 | -0.036827 | -0.00011484 | -0.0050436 | -8.6667e-06 | 6.9875e-05 | -0.17848 | 0.027828 | -0.00015156 | -0.0035024 | 0.00015667 | -0.00017075 | 50.6159 | -1.642 | 0.013563 | 0.10822 | 5.9916e-05 | -0.0017762 | 0.0046844 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.87 | 0.13 | 0.4072 | 0.65747 | -0.064667 | 2.5673 | 1.2954 | ; | Mfg3 | 287 | Elec | Mfg3 | Mfg3_287 | Pkg DX, Tier 0, Mfg3 287 (12.5 ton, 9 rated EER) | PkgDX T0 Mfg3 287 12.5t 9eer
32011 | 0 | 15 | 2 | 9 | 9 | 183200 | 0.75 | 0.32043 | 0.03275 | 0.2363 | 0.0065502 | 0.1229 | 0 | 55 | 1.6748 | -0.028213 | 0.0003875 | 0.0012845 | 0 | -0.0001015 | 5.1817 | -0.064575 | 0.00010937 | -0.0075428 | 6.8333e-06 | 4.85e-05 | 0.43135 | 0.0067859 | -8.0469e-05 | -0.0015054 | 8.675e-05 | -2.5875e-05 | 54.5982 | -1.7305 | 0.013727 | 0.092063 | -6.7539e-05 | -0.0011643 | 0.00046003 | 1.0125 | 0.059111 | -0.072068 | 0.91241 | 0.24998 | -0.35145 | 0.1856 | 0.925 | 1 | 2 | 0.33 | 0.33 | 0.87855 | 0.12145 | 0.43985 | 0.60027 | -0.04012 | 2.5769 | 1.3492 | ; | Mfg3 | 288 | Elec | Mfg3 | Mfg3_288 | Pkg DX, Tier 0, Mfg3 288 (15 ton, 9 rated EER) | PkgDX T0 Mfg3 288 15t 9eer
32012 | 0 | 20 | 2 | 9 | 9 | 226600 | 0.75 | 0.29479 | 0.03177 | 0.3581 | 0.0090468 | 0.096 | 0 | 55 | 1.5062 | -0.026786 | 0.00034609 | 0.0030987 | -1.1833e-05 | -7.1125e-05 | 5.2104 | -0.072092 | 0.00013984 | -0.003232 | -1.9667e-05 | 7.4875e-05 | 0.16125 | 0.017206 | -7.5e-05 | -0.005135 | 0.000156 | -0.000141 | 72.9978 | -2.2232 | 0.017747 | 0.052237 | 0.00026541 | -0.0015817 | 0.00046003 | 1.0125 | 0.059111 | -0.072068 | 0.91241 | 0.24998 | -0.35145 | 0.1856 | 0.925 | 1 | 2 | 0.33 | 0.33 | 0.87864 | 0.12136 | 0.41862 | 0.64316 | -0.061783 | 2.6217 | 1.2709 | ; | Mfg3 | 289 | Elec | Mfg3 | Mfg3_289 | Pkg DX, Tier 0, Mfg3 289 (20 ton, 9 rated EER) | PkgDX T0 Mfg3 289 20t 9eer
32013 | 0 | 15 | 1 | 9 | 9 | 183200 | 0.75 | 0.32138 | 0.03275 | 0.2302 | 0.0065502 | 0.1229 | 0 | 55 | 1.6748 | -0.028213 | 0.0003875 | 0.0012845 | 0 | -0.0001015 | 5.1817 | -0.064575 | 0.00010937 | -0.0075428 | 6.8333e-06 | 4.85e-05 | 0.43135 | 0.0067859 | -8.0469e-05 | -0.0015054 | 8.675e-05 | -2.5875e-05 | 34.1122 | -1.1632 | 0.0098013 | 0.12181 | -6.9376e-05 | -0.0015899 | 0.00046003 | 1.0125 | 0.059111 | -0.072068 | 0.91241 | 0.24998 | -0.35145 | 0.1856 | 0.925 | 1 | 2 | 0.33 | 0.33 | 0.87855 | 0.12145 | 0.43985 | 0.60027 | -0.04012 | 2.4545 | 1.3536 | ; | Mfg3 | 290 | Gas | Mfg3 | Mfg3_290 | Pkg DX, Tier 0, Mfg3 290 (15 ton, 9 rated EER) | PkgDX T0 Mfg3 290 15t 9eer
32014 | 0 | 18 | 1 | 9 | 9 | 226600 | 0.75 | 0.30094 | 0.03177 | 0.3169 | 0.0090468 | 0.096 | 0 | 55 | 1.5062 | -0.026786 | 0.00034609 | 0.0030987 | -1.1833e-05 | -7.1125e-05 | 5.2104 | -0.072092 | 0.00013984 | -0.003232 | -1.9667e-05 | 7.4875e-05 | 0.16125 | 0.017206 | -7.5e-05 | -0.005135 | 0.000156 | -0.000141 | 43.5342 | -1.3983 | 0.011996 | 0.088823 | 0.00027238 | -0.0021356 | 0.00046003 | 1.0125 | 0.059111 | -0.072068 | 0.91241 | 0.24998 | -0.35145 | 0.1856 | 0.925 | 1 | 2 | 0.33 | 0.33 | 0.87864 | 0.12136 | 0.41862 | 0.64316 | -0.061783 | 2.5129 | 1.2985 | ; | Mfg3 | 291 | Gas | Mfg3 | Mfg3_291 | Pkg DX, Tier 0, Mfg3 291 (18 ton, 9 rated EER) | PkgDX T0 Mfg3 291 18t 9eer
32015 | 0 | 12.5 | 2 | 9.2 | 9.2 | 153500 | 0.7238 | 0.2989 | 0.02932 | 0.42822 | 0.0039088 | 0.0931 | 0 | 55 | -0.16228 | 0.029381 | -0.0001032 | -0.0039071 | -1.5286e-05 | 2.61e-05 | 2.7131 | 0.0097704 | -0.0005076 | -0.011265 | -2.0786e-05 | 0.0001836 | 1.5104 | -0.039979 | 0.0003772 | 0.013442 | 8.131e-05 | -0.0002413 | 72.9303 | -2.3772 | 0.020212 | 0.15923 | 0.00034377 | -0.0033965 | 0.0046725 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.83892 | 0.16108 | 0.54095 | 0.42016 | 0.038884 | 2.7611 | 1.2465 | ; | Mfg1 | 292 | Elec | Mfg1 | Mfg1_292 | Pkg DX, Tier 0, Mfg1 292 (12.5 ton, 9.2 rated EER) | PkgDX T0 Mfg1 292 12.5t 9.2eer
32016 | 0 | 12.5 | 1 | 9.5 | 9.5 | 147600 | 0.7622 | 0.2457 | 0.03388 | 0.627 | 0.0044038 | 0.1231 | 0 | 55 | 1.8589 | -0.048611 | 0.000488 | 0.0092315 | -7.0738e-05 | -4.9e-06 | 0.37155 | 0.084449 | -0.0011808 | -0.01526 | -6.0905e-05 | 0.0003567 | -1.4751 | 0.061075 | -0.0003232 | 0.0028776 | 0.00017467 | -0.0003167 | 63.5067 | -2.1177 | 0.018567 | 0.19325 | 0.00043089 | -0.0041188 | 0.0046725 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.87263 | 0.12737 | 0.42044 | 0.66489 | -0.085333 | 2.732 | 1.0807 | ; | Mfg1 | 293 | Gas | Mfg1 | Mfg1_293 | Pkg DX, Tier 0, Mfg1 293 (12.5 ton, 9.5 rated EER) | PkgDX T0 Mfg1 293 12.5t 9.5eer
32017 | 0 | 15 | 1 | 9.5 | 9.5 | 189000 | 0.7143 | 0.28042 | 0.03175 | 0.4005 | 0.0058201 | 0.1873 | 0 | 55 | -0.63017 | 0.026606 | 0 | 0.010358 | -2.8952e-05 | -0.0001375 | 0.84035 | 0.064093 | -0.0008592 | -0.0075503 | -3.5476e-06 | 7.41e-05 | 1.3083 | -0.018967 | 0.0001396 | -0.0001834 | 0.0001041 | -9.21e-05 | 42.822 | -1.3798 | 0.010908 | 0.060901 | -0.0001062 | -0.00049759 | 0.0040028 | 0.9901 | 0.095998 | -0.086528 | 0.92022 | 0.2688 | -0.4089 | 0.21568 | 0.925 | 1 | 2 | 0.4 | 0.5 | 0.86999 | 0.13001 | 0.55556 | 0.36543 | 0.079012 | 2.268 | 1.2432 | ; | Mfg1 | 294 | Gas | Mfg1 | Mfg1_294 | Pkg DX, Tier 0, Mfg1 294 (15 ton, 9.5 rated EER) | PkgDX T0 Mfg1 294 15t 9.5eer
32018 | 0 | 20 | 1 | 9.5 | 9.5 | 249000 | 0.755 | 0.25198 | 0.03213 | 0.61862 | 0.0044177 | 0.0934 | 0 | 55 | 0.63476 | -0.010165 | 0.0002732 | 0.0077283 | -2.4857e-05 | -0.0001084 | 1.2429 | 0.053748 | -0.0007868 | -0.010635 | 2.4762e-06 | 0.0001062 | 0.37909 | 0.0057118 | -2.92e-05 | 0.004461 | 7.8452e-05 | -0.0001198 | 86.5903 | -2.744 | 0.02104 | 0.14304 | -0.00025893 | -0.0011697 | 0.0040028 | 0.9901 | 0.095998 | -0.086528 | 0.92022 | 0.2688 | -0.4089 | 0.21568 | 0.925 | 1 | 2 | 0.4 | 0.5 | 0.90361 | 0.096386 | 0.34043 | 0.82979 | -0.17021 | 1.8751 | 1.1052 | ; | Mfg1 | 295 | Gas | Mfg1 | Mfg1_295 | Pkg DX, Tier 0, Mfg1 295 (20 ton, 9.5 rated EER) | PkgDX T0 Mfg1 295 20t 9.5eer
32019 | 0 | 20 | 1 | 9.5 | 9.5 | 243000 | 0.73 | 0.29395 | 0.03292 | 0.2994 | 0.0057407 | 0.1769 | 0 | 55 | 1.7324 | -0.032984 | 0.00039844 | 0.0017872 | -5.5e-06 | -6.775e-05 | 11.2552 | -0.25436 | 0.001525 | 0.0013277 | -1.325e-05 | -1.025e-05 | -0.30177 | 0.031611 | -0.00020547 | -0.0019165 | 0.00013658 | -0.00014837 | 33.7916 | -1.0391 | 0.0084462 | 0.0062567 | 0.00010566 | -0.00041431 | 0.0046844 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.87654 | 0.12346 | 0.7545 | -0.043407 | 0.28891 | 2.5722 | 1.3031 | ; | Mfg3 | 296 | Gas | Mfg3 | Mfg3_296 | Pkg DX, Tier 0, Mfg3 296 (20 ton, 9.5 rated EER) | PkgDX T0 Mfg3 296 20t 9.5eer
32020 | 0 | 12.5 | 1 | 9.5 | 9.5 | 145100 | 0.67 | 0.27533 | 0.02929 | 0.4186 | 0.0079256 | 0.2497 | 0 | 55 | 1.1225 | -0.018123 | 0.00029609 | 0.003713 | -1.2583e-05 | -7.4875e-05 | 13.6216 | -0.31894 | 0.0020477 | -0.0044153 | 2.6917e-05 | -4.2125e-05 | 0.11723 | 0.019688 | -0.00011563 | -0.0027662 | 0.00014725 | -0.0001545 | -0.031461 | -0.13512 | 0.0018152 | 0.082439 | -0.00023006 | -0.00060003 | 0.0046844 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.87228 | 0.12772 | 0.9184 | -0.31194 | 0.39354 | 3.0516 | 1.2526 | ; | Mfg3 | 297 | Gas | Mfg3 | Mfg3_297 | Pkg DX, Tier 0, Mfg3 297 (12.5 ton, 9.5 rated EER) | PkgDX T0 Mfg3 297 12.5t 9.5eer
32021 | 0 | 12 | 1 | 9.6 | 9.6 | 146800 | 0.7228 | 0.27527 | 0.02929 | 0.4807 | 0.0044278 | 0.0952 | 0 | 55 | 1.2609 | -0.01528 | 0.00015933 | -0.0034025 | -5.9095e-05 | 0.00014206 | 1.3921 | 0.055884 | -0.00097733 | -0.017441 | -6.0315e-05 | 0.00038526 | -1.401 | 0.034186 | 9.0333e-05 | 0.02299 | 0.00020112 | -0.00067466 | 52.7287 | -1.8109 | 0.01664 | 0.18976 | 0.00058968 | -0.0044686 | 0.0046725 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.96 | 1 | 2 | 0.5 | 0.5 | 0.85783 | 0.14217 | 0.46156 | 0.59819 | -0.05975 | 3.7353 | 1.2157 | ; | Mfg1 | 298 | Gas | Mfg1 | Mfg1_298 | Pkg DX, Tier 0, Mfg1 298 (12 ton, 9.6 rated EER) | PkgDX T0 Mfg1 298 12t 9.6eer
32022 | 0 | 12.5 | 2 | 9.6 | 9.6 | 153100 | 0.72567 | 0.27452 | 0.02809 | 0.493 | 0.0049641 | 0.0478 | 0 | 55 | 5.4331 | -0.14503 | 0.0011788 | 0.0041882 | -4.5119e-05 | 2.5e-07 | 6.0933 | -0.10358 | 0.00041625 | 0.0019766 | -2.4e-05 | 1.125e-06 | -6.6966 | 0.20179 | -0.0013956 | 0.010304 | 0.0001075 | -0.00023687 | 121.6755 | -3.7874 | 0.029919 | -0.011961 | 0.00024729 | -0.00036493 | 0.0046844 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.81874 | 0.18126 | 0.54046 | 0.454 | 0.0055476 | 2.7503 | 1.2203 | ; | Mfg5 | 299 | Elec | Mfg5 | Mfg5_299 | Pkg DX, Tier 0, Mfg5 299 (12.5 ton, 9.6 rated EER) | PkgDX T0 Mfg5 299 12.5t 9.6eer
32023 | 0 | 20 | 2 | 9.6 | 9.6 | 233100 | 0.7825 | 0.26707 | 0.03003 | 0.479 | 0.006435 | 0.01 | 0 | 55 | 2.5254 | -0.05576 | 0.00057 | 0.0057133 | -1.875e-05 | -0.0001134 | -4.0807 | 0.21214 | -0.0020355 | -0.010612 | -3.725e-05 | 0.00021192 | -0.81438 | 0.046998 | -0.000442 | -0.0046073 | 7.1875e-05 | 6.892e-05 | 1080.7493 | -32.7633 | 0.25734 | 0.9531 | 0.0049327 | -0.027471 | 0.0046725 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.8845 | 0.1155 | 0.32806 | 0.84247 | -0.17053 | 2.303 | 1.2096 | ; | Mfg6 | 300 | Elec | Mfg6 | Mfg6_300 | Pkg DX, Tier 0, Mfg6 300 (20 ton, 9.6 rated EER) | PkgDX T0 Mfg6 300 20t 9.6eer
32024 | 0 | 18 | 1 | 9.7 | 9.7 | 233000 | 0.7339 | 0.26891 | 0.03004 | 0.48214 | 0.004721 | 0.0874 | 0 | 55 | 0.67349 | -0.0086332 | 0.0002568 | 0.005852 | -1.9381e-05 | -9.88e-05 | 2.7422 | 0.001045 | -0.000374 | -0.005157 | -1.3952e-05 | 7.58e-05 | 0.5269 | 0.0020565 | -4e-06 | 0.0039618 | 8.3976e-05 | -0.0001227 | 69.955 | -2.2208 | 0.017924 | 0.11466 | 0.00012587 | -0.0019879 | 0.0040028 | 0.9901 | 0.095998 | -0.086528 | 0.92022 | 0.2688 | -0.4089 | 0.21568 | 0.925 | 1 | 2 | 0.4 | 0.5 | 0.87983 | 0.12017 | 0.67251 | 0.18421 | 0.14327 | 2.0712 | 1.2077 | ; | Mfg1 | 301 | Gas | Mfg1 | Mfg1_301 | Pkg DX, Tier 0, Mfg1 301 (18 ton, 9.7 rated EER) | PkgDX T0 Mfg1 301 18t 9.7eer
32025 | 0 | 20 | 2 | 9.7 | 9.7 | 243000 | 0.73 | 0.29176 | 0.03292 | 0.2666 | 0.0057407 | 0.1769 | 0 | 55 | 1.7324 | -0.032984 | 0.00039844 | 0.0017872 | -5.5e-06 | -6.775e-05 | 11.2552 | -0.25436 | 0.001525 | 0.0013277 | -1.325e-05 | -1.025e-05 | -0.30177 | 0.031611 | -0.00020547 | -0.0019165 | 0.00013658 | -0.00014837 | 33.7916 | -1.0391 | 0.0084462 | 0.0062567 | 0.00010566 | -0.00041431 | 0.0046844 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.87654 | 0.12346 | 0.7545 | -0.043407 | 0.28891 | 2.6038 | 1.3264 | ; | Mfg3 | 302 | Elec | Mfg3 | Mfg3_302 | Pkg DX, Tier 0, Mfg3 302 (20 ton, 9.7 rated EER) | PkgDX T0 Mfg3 302 20t 9.7eer
32026 | 0 | 12.5 | 2 | 9.7 | 9.7 | 145100 | 0.67 | 0.27705 | 0.02929 | 0.3534 | 0.0079256 | 0.2497 | 0 | 55 | 1.1225 | -0.018123 | 0.00029609 | 0.003713 | -1.2583e-05 | -7.4875e-05 | 13.6216 | -0.31894 | 0.0020477 | -0.0044153 | 2.6917e-05 | -4.2125e-05 | 0.11723 | 0.019688 | -0.00011563 | -0.0027662 | 0.00014725 | -0.0001545 | -0.031461 | -0.13512 | 0.0018152 | 0.082439 | -0.00023006 | -0.00060003 | 0.0046844 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.87228 | 0.12772 | 0.9184 | -0.31194 | 0.39354 | 2.9878 | 1.2925 | ; | Mfg3 | 303 | Elec | Mfg3 | Mfg3_303 | Pkg DX, Tier 0, Mfg3 303 (12.5 ton, 9.7 rated EER) | PkgDX T0 Mfg3 303 12.5t 9.7eer
32027 | 0 | 12.5 | 2 | 9.7 | 9.7 | 153100 | 0.72567 | 0.2725 | 0.02809 | 0.4816 | 0.0049641 | 0.0478 | 0 | 55 | 5.4353 | -0.14503 | 0.0011788 | 0.0041882 | -4.5119e-05 | 2.5e-07 | 6.095 | -0.10358 | 0.00041625 | 0.0019766 | -2.4e-05 | 1.125e-06 | -7.9727 | 0.24475 | -0.0017069 | 0.0057982 | 0.00013121 | -0.00023687 | 83.4614 | -2.4893 | 0.018411 | -0.14662 | -6.1957e-06 | 0.0023017 | 0.0046725 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.81874 | 0.18126 | 0.54046 | 0.454 | 0.0055476 | 2.9943 | 1.2268 | ; | Mfg4 | 304 | Elec | Mfg4 | Mfg4_304 | Pkg DX, Tier 0, Mfg4 304 (12.5 ton, 9.7 rated EER) | PkgDX T0 Mfg4 304 12.5t 9.7eer
32028 | 0 | 20 | 2 | 9.7 | 9.7 | 245600 | 0.73941 | 0.24009 | 0.03013 | 0.652 | 0.0061889 | 0.0751 | 0 | 55 | 1.0224 | -0.020723 | 0.0002375 | 0.0097969 | -6.9429e-05 | -5e-07 | 6.3675 | -0.11622 | 0.00053 | 0.0029294 | -2.6214e-05 | -1.25e-07 | -4.9386 | 0.1655 | -0.0011538 | -0.0015863 | 0.00015529 | -0.00019288 | -44.2368 | 1.4538 | -0.012263 | -0.038913 | -0.00027327 | 0.0014769 | 0.0046725 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.81881 | 0.18119 | 0.52643 | 0.48045 | -0.0068833 | 2.5174 | 1.1094 | ; | Mfg4 | 305 | Elec | Mfg4 | Mfg4_305 | Pkg DX, Tier 0, Mfg4 305 (20 ton, 9.7 rated EER) | PkgDX T0 Mfg4 305 20t 9.7eer
32029 | 0 | 12.5 | 1 | 9.7 | 9.7 | 153100 | 0.72567 | 0.2725 | 0.02809 | 0.4816 | 0.0049641 | 0.0478 | 0 | 55 | 5.4353 | -0.14503 | 0.0011788 | 0.0041882 | -4.5119e-05 | 2.5e-07 | 6.095 | -0.10358 | 0.00041625 | 0.0019766 | -2.4e-05 | 1.125e-06 | -7.9727 | 0.24475 | -0.0017069 | 0.0057982 | 0.00013121 | -0.00023687 | 83.4614 | -2.4893 | 0.018411 | -0.14662 | -6.1957e-06 | 0.0023017 | 0.0046725 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.81874 | 0.18126 | 0.54046 | 0.454 | 0.0055476 | 2.9943 | 1.2268 | ; | Mfg4 | 306 | Gas | Mfg4 | Mfg4_306 | Pkg DX, Tier 0, Mfg4 306 (12.5 ton, 9.7 rated EER) | PkgDX T0 Mfg4 306 12.5t 9.7eer
32030 | 0 | 20 | 1 | 9.7 | 9.7 | 245600 | 0.73941 | 0.24009 | 0.03013 | 0.652 | 0.0061889 | 0.0751 | 0 | 55 | 1.0224 | -0.020723 | 0.0002375 | 0.0097969 | -6.9429e-05 | -5e-07 | 6.3675 | -0.11622 | 0.00053 | 0.0029294 | -2.6214e-05 | -1.25e-07 | -4.9386 | 0.1655 | -0.0011538 | -0.0015863 | 0.00015529 | -0.00019288 | -44.2368 | 1.4538 | -0.012263 | -0.038913 | -0.00027327 | 0.0014769 | 0.0046725 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.81881 | 0.18119 | 0.52643 | 0.48045 | -0.0068833 | 2.5174 | 1.1094 | ; | Mfg4 | 307 | Gas | Mfg4 | Mfg4_307 | Pkg DX, Tier 0, Mfg4 307 (20 ton, 9.7 rated EER) | PkgDX T0 Mfg4 307 20t 9.7eer
32031 | 0 | 20 | 1 | 9.7 | 9.7 | 233100 | 0.7825 | 0.26804 | 0.03003 | 0.446 | 0.006435 | 0.01 | 0 | 55 | 2.5254 | -0.05576 | 0.00057 | 0.0057133 | -1.875e-05 | -0.0001134 | -4.0807 | 0.21214 | -0.0020355 | -0.010612 | -3.725e-05 | 0.00021192 | -0.81438 | 0.046998 | -0.000442 | -0.0046073 | 7.1875e-05 | 6.892e-05 | 1080.7493 | -32.7633 | 0.25734 | 0.9531 | 0.0049327 | -0.027471 | 0.0046725 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.8845 | 0.1155 | 0.32806 | 0.84247 | -0.17053 | 2.409 | 1.2295 | ; | Mfg6 | 308 | Gas | Mfg6 | Mfg6_308 | Pkg DX, Tier 0, Mfg6 308 (20 ton, 9.7 rated EER) | PkgDX T0 Mfg6 308 20t 9.7eer
32032 | 0 | 12.5 | 2 | 9.8 | 9.8 | 149800 | 0.7623 | 0.255 | 0.03338 | 0.5108 | 0.0043391 | 0.1097 | 0 | 55 | 2.5862 | -0.060949 | 0.00053133 | 0.0018842 | -6.3095e-05 | 7.8971e-05 | -0.34872 | 0.11324 | -0.0014533 | -0.02081 | -6.269e-05 | 0.0004444 | -3.1103 | 0.096519 | -0.00044967 | 0.01363 | 0.00019982 | -0.00053986 | 73.9879 | -2.4059 | 0.020315 | 0.18474 | 0.00037534 | -0.003759 | 0.0046725 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.96 | 1 | 2 | 0.5 | 0.5 | 0.89266 | 0.10734 | 0.41889 | 0.66771 | -0.086603 | 2.7779 | 1.1578 | ; | Mfg1 | 309 | Elec | Mfg1 | Mfg1_309 | Pkg DX, Tier 0, Mfg1 309 (12.5 ton, 9.8 rated EER) | PkgDX T0 Mfg1 309 12.5t 9.8eer
32033 | 0 | 12.5 | 2 | 9.8 | 9.8 | 153000 | 0.6797 | 0.25462 | 0.0268 | 0.488 | 0.0098039 | 0.1475 | 0 | 55 | 0.63453 | 0.011313 | -1.34e-05 | -0.004134 | -1.1643e-05 | 2.6e-05 | -8.4436 | 0.36641 | -0.0033654 | -0.021779 | -3.0964e-05 | 0.00036916 | 0.54075 | -0.017262 | 0.0003294 | 0.011955 | 0.00015907 | -0.00038244 | 168.3436 | -5.1802 | 0.040136 | -0.0022952 | 0.00019122 | -0.00030535 | 0.0046725 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.94078 | 0.059225 | 0.45122 | 0.65618 | -0.1074 | 2.1144 | 1.2359 | ; | Mfg6 | 310 | Elec | Mfg6 | Mfg6_310 | Pkg DX, Tier 0, Mfg6 310 (12.5 ton, 9.8 rated EER) | PkgDX T0 Mfg6 310 12.5t 9.8eer
32034 | 0 | 15 | 2 | 9.9 | 9.9 | 185700 | 0.7286 | 0.23898 | 0.03104 | 0.549 | 0.0080775 | 0.1308 | 0 | 55 | 2.3435 | -0.028662 | 0.000351 | -0.008522 | 5.625e-05 | -0.00010948 | -0.055212 | -0.00127 | -0.000453 | 0.049689 | -0.00039213 | 0.000313 | 0.37867 | -0.0079467 | -2.375e-05 | 0.0068574 | -8.125e-07 | 9.682e-05 | 88.0303 | -0.50863 | 6.7427e-05 | -1.3832 | 0.0062098 | 0.0034724 | 0.0046725 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.86264 | 0.13736 | 0.4192 | 0.70349 | -0.12269 | 2.2768 | 1.158 | ; | Mfg6 | 311 | Elec | Mfg6 | Mfg6_311 | Pkg DX, Tier 0, Mfg6 311 (15 ton, 9.9 rated EER) | PkgDX T0 Mfg6 311 15t 9.9eer
32035 | 0 | 15 | 2 | 10 | 10 | 186400 | 0.73 | 0.2904 | 0.03219 | 0.1752 | 0.0073498 | 0.1581 | 0 | 55 | 1.4652 | -0.025458 | 0.00034766 | 0.0018769 | -5.4167e-06 | -7.0625e-05 | 7.8939 | -0.15066 | 0.00075 | -0.0037779 | -1.75e-06 | 3.275e-05 | 0.054843 | 0.02123 | -0.00012109 | -0.0023805 | 0.00014217 | -0.00015562 | 35.8748 | -1.1442 | 0.009379 | 0.057022 | 4.4737e-06 | -0.00090653 | 0.00046003 | 1.0125 | 0.059111 | -0.072068 | 0.91241 | 0.24998 | -0.35145 | 0.1856 | 0.96 | 1 | 2 | 0.33 | 0.33 | 0.8699 | 0.1301 | 0.7394 | -0.019769 | 0.28037 | 2.2411 | 1.3966 | ; | Mfg3 | 312 | Elec | Mfg3 | Mfg3_312 | Pkg DX, Tier 0, Mfg3 312 (15 ton, 10 rated EER) | PkgDX T0 Mfg3 312 15t 10eer
32036 | 0 | 17.5 | 2 | 10 | 10 | 211400 | 0.72 | 0.28866 | 0.03217 | 0.2044 | 0.0066036 | 0.1832 | 0 | 55 | 1.4565 | -0.027698 | 0.00036797 | 0.0042228 | -1.575e-05 | -8.0375e-05 | 10.3831 | -0.23071 | 0.0014375 | 0.0020101 | 1.75e-05 | -0.00011425 | -0.60411 | 0.044206 | -0.00027187 | -0.0062824 | 0.00017417 | -0.00017475 | 28.6289 | -0.92167 | 0.0071263 | 0.040476 | -0.00021596 | 3.7182e-05 | 0.0046844 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.88394 | 0.11606 | 0.80432 | -0.11499 | 0.31067 | 2.4385 | 1.3752 | ; | Mfg3 | 313 | Elec | Mfg3 | Mfg3_313 | Pkg DX, Tier 0, Mfg3 313 (17.5 ton, 10 rated EER) | PkgDX T0 Mfg3 313 17.5t 10eer
32037 | 0 | 15 | 1 | 10 | 10 | 186400 | 0.73 | 0.28824 | 0.03219 | 0.1898 | 0.0073498 | 0.1581 | 0 | 55 | 1.4652 | -0.025458 | 0.00034766 | 0.0018769 | -5.4167e-06 | -7.0625e-05 | 7.8939 | -0.15066 | 0.00075 | -0.0037779 | -1.75e-06 | 3.275e-05 | 0.054843 | 0.02123 | -0.00012109 | -0.0023805 | 0.00014217 | -0.00015562 | 35.8748 | -1.1442 | 0.009379 | 0.057022 | 4.4737e-06 | -0.00090653 | 0.00046003 | 1.0125 | 0.059111 | -0.072068 | 0.91241 | 0.24998 | -0.35145 | 0.1856 | 0.96 | 1 | 2 | 0.33 | 0.33 | 0.8699 | 0.1301 | 0.7394 | -0.019769 | 0.28037 | 2.2211 | 1.3858 | ; | Mfg3 | 314 | Gas | Mfg3 | Mfg3_314 | Pkg DX, Tier 0, Mfg3 314 (15 ton, 10 rated EER) | PkgDX T0 Mfg3 314 15t 10eer
32038 | 0 | 17.5 | 1 | 10 | 10 | 211400 | 0.72 | 0.28331 | 0.03217 | 0.2407 | 0.0066036 | 0.1832 | 0 | 55 | 1.4565 | -0.027698 | 0.00036797 | 0.0042228 | -1.575e-05 | -8.0375e-05 | 10.3831 | -0.23071 | 0.0014375 | 0.0020101 | 1.75e-05 | -0.00011425 | -0.60411 | 0.044206 | -0.00027187 | -0.0062824 | 0.00017417 | -0.00017475 | 28.6289 | -0.92167 | 0.0071263 | 0.040476 | -0.00021596 | 3.7182e-05 | 0.0046844 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.88394 | 0.11606 | 0.80432 | -0.11499 | 0.31067 | 2.4283 | 1.3491 | ; | Mfg3 | 315 | Gas | Mfg3 | Mfg3_315 | Pkg DX, Tier 0, Mfg3 315 (17.5 ton, 10 rated EER) | PkgDX T0 Mfg3 315 17.5t 10eer
32039 | 0 | 15 | 1 | 10 | 10 | 185745.826 | 0.7287 | 0.23975 | 0.03104 | 0.521 | 0.0080756 | 0.1304 | 0 | 55 | 2.3428 | -0.028671 | 0.000351 | -0.0085017 | 5.6125e-05 | -0.0001094 | -0.053647 | -0.0013135 | -0.0004525 | 0.049676 | -0.000392 | 0.00031288 | 0.25755 | -0.0016485 | -7.25e-05 | 0.0072172 | -7.75e-06 | 8.84e-05 | 87.8487 | -0.50291 | 3.2751e-05 | -1.3827 | 0.006215 | 0.003451 | 0.0046725 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.86267 | 0.13733 | 0.41939 | 0.70325 | -0.12265 | 2.3535 | 1.1746 | ; | Mfg6 | 316 | Gas | Mfg6 | Mfg6_316 | Pkg DX, Tier 0, Mfg6 316 (15 ton, 10 rated EER) | PkgDX T0 Mfg6 316 15t 10eer
32040 | 0 | 12.5 | 1 | 10 | 10 | 153000 | 0.6797 | 0.25326 | 0.0268 | 0.445 | 0.0098039 | 0.1475 | 0 | 55 | 0.63453 | 0.011313 | -1.34e-05 | -0.004134 | -1.1643e-05 | 2.6e-05 | -8.4436 | 0.36641 | -0.0033654 | -0.021779 | -3.0964e-05 | 0.00036916 | 0.54075 | -0.017262 | 0.0003294 | 0.011955 | 0.00015907 | -0.00038244 | 168.3436 | -5.1802 | 0.040136 | -0.0022952 | 0.00019122 | -0.00030535 | 0.0046725 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.94078 | 0.059225 | 0.45122 | 0.65618 | -0.1074 | 2.0254 | 1.2595 | ; | Mfg6 | 317 | Gas | Mfg6 | Mfg6_317 | Pkg DX, Tier 0, Mfg6 317 (12.5 ton, 10 rated EER) | PkgDX T0 Mfg6 317 12.5t 10eer
32041 | 0 | 15 | 2 | 10.2 | 10.2 | 188700 | 0.75623 | 0.24196 | 0.0318 | 0.4498 | 0.0080551 | 0.0808 | 0 | 55 | 2.6613 | -0.064348 | 0.00057563 | 0.0047533 | -4.2548e-05 | 1.25e-07 | 5.9688 | -0.10257 | 0.00042 | 0.0023713 | -2.2833e-05 | 0 | 1.8578 | -0.045883 | 0.00042188 | 0.0080608 | 0.00010176 | -0.00021475 | -4.0335 | 0.2474 | -0.0026821 | -0.074613 | 2.0792e-05 | 0.0011668 | 0.0046725 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.81849 | 0.18151 | 0.53399 | 0.46601 | 0 | 3.5134 | 1.2112 | ; | Mfg4 | 318 | Elec | Mfg4 | Mfg4_318 | Pkg DX, Tier 0, Mfg4 318 (15 ton, 10.2 rated EER) | PkgDX T0 Mfg4 318 15t 10.2eer
32042 | 0 | 15 | 1 | 10.2 | 10.2 | 188700 | 0.75623 | 0.24196 | 0.0318 | 0.4498 | 0.0080551 | 0.0808 | 0 | 55 | 2.6613 | -0.064348 | 0.00057563 | 0.0047533 | -4.2548e-05 | 1.25e-07 | 5.9688 | -0.10257 | 0.00042 | 0.0023713 | -2.2833e-05 | 0 | 1.8578 | -0.045883 | 0.00042188 | 0.0080608 | 0.00010176 | -0.00021475 | -4.0335 | 0.2474 | -0.0026821 | -0.074613 | 2.0792e-05 | 0.0011668 | 0.0046725 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.81849 | 0.18151 | 0.53399 | 0.46601 | 0 | 3.5134 | 1.2112 | ; | Mfg4 | 319 | Gas | Mfg4 | Mfg4_319 | Pkg DX, Tier 0, Mfg4 319 (15 ton, 10.2 rated EER) | PkgDX T0 Mfg4 319 15t 10.2eer
32043 | 0 | 12.5 | 0 | 10.2 | 10.2 | 153000 | 0.6797 | 0.25214 | 0.0268 | 0.401 | 0.0098039 | 0.1475 | 0 | 55 | 0.63453 | 0.011313 | -1.34e-05 | -0.004134 | -1.1643e-05 | 2.6e-05 | -8.4436 | 0.36641 | -0.0033654 | -0.021779 | -3.0964e-05 | 0.00036916 | 0.54075 | -0.017262 | 0.0003294 | 0.011955 | 0.00015907 | -0.00038244 | 168.3436 | -5.1802 | 0.040136 | -0.0022952 | 0.00019122 | -0.00030535 | 0.0046725 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.94078 | 0.059225 | 0.45122 | 0.65618 | -0.1074 | 1.9851 | 1.2841 | ; | Mfg6 | 320 | None | Mfg6 | Mfg6_320 | Pkg DX, Tier 0, Mfg6 320 (12.5 ton, 10.2 rated EER) | PkgDX T0 Mfg6 320 12.5t 10.2eer
32101 | 1 | 10 | 2 | 10.4 | 10.4 | 127600 | 0.655 | 0.27062 | 0.02821 | 0.3036 | 0.0054859 | 0.2702 | 0 | 55 | 1.2303 | -0.021603 | 0.00033906 | 0.005237 | -2.05e-05 | -9.7e-05 | 15.1626 | -0.37008 | 0.0024266 | 0.0028543 | 4.1667e-07 | -8.4e-05 | -0.4212 | 0.03578 | -0.00017422 | -0.0047209 | 0.00021183 | -0.00026038 | 15.4985 | -0.61694 | 0.0060821 | 0.060652 | -2.0696e-05 | -0.00094914 | 0.0046844 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.88172 | 0.11828 | 0.78614 | -0.084639 | 0.2985 | 2.3379 | 1.331 | ; | Mfg3 | 321 | Elec | Mfg3 | Mfg3_321 | Pkg DX, Tier 1, Mfg3 321 (10 ton, 10.4 rated EER) | PkgDX T1 Mfg3 321 10t 10.4eer
32102 | 1 | 20 | 2 | 10.5 | 10.5 | 254900 | 0.72 | 0.27207 | 0.02942 | 0.2577 | 0.0054727 | 0.107 | 0 | 55 | 1.1323 | -0.017669 | 0.00030625 | 0.0045561 | -1.9417e-05 | -9.125e-05 | 8.5508 | -0.17446 | 0.00099141 | -0.00030021 | 7.5833e-06 | -5.5375e-05 | -0.49853 | 0.034883 | -0.00015391 | -0.002642 | 0.00020742 | -0.00027788 | 50.5314 | -1.6949 | 0.013881 | 0.12347 | -0.0002443 | -0.0012268 | 0.0046844 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.8768 | 0.1232 | 0.42092 | 0.63024 | -0.051165 | 2.6112 | 1.3527 | ; | Mfg3 | 322 | Elec | Mfg3 | Mfg3_322 | Pkg DX, Tier 1, Mfg3 322 (20 ton, 10.5 rated EER) | PkgDX T1 Mfg3 322 20t 10.5eer
32103 | 1 | 21 | 1 | 10.5 | 10.5 | 254900 | 0.72 | 0.26947 | 0.02942 | 0.2773 | 0.0054727 | 0.107 | 0 | 55 | 1.1323 | -0.017669 | 0.00030625 | 0.0045561 | -1.9417e-05 | -9.125e-05 | 8.5508 | -0.17446 | 0.00099141 | -0.00030021 | 7.5833e-06 | -5.5375e-05 | -0.49853 | 0.034883 | -0.00015391 | -0.002642 | 0.00020742 | -0.00027788 | 50.5314 | -1.6949 | 0.013881 | 0.12347 | -0.0002443 | -0.0012268 | 0.0046844 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.8768 | 0.1232 | 0.42092 | 0.63024 | -0.051165 | 2.5952 | 1.3399 | ; | Mfg3 | 323 | Gas | Mfg3 | Mfg3_323 | Pkg DX, Tier 1, Mfg3 323 (21 ton, 10.5 rated EER) | PkgDX T1 Mfg3 323 21t 10.5eer
32104 | 1 | 12.5 | 2 | 10.5 | 10.5 | 155900 | 0.6793 | 0.21348 | 0.02646 | 0.658 | 0.0096216 | 0.1382 | 0 | 55 | 3.9034 | -0.097222 | 0.00089583 | 0.0016288 | -1.4942e-05 | -6.7686e-05 | -4.4869 | 0.23938 | -0.0023545 | -0.01709 | -4.2433e-05 | 0.00031801 | -3.5747 | 0.12598 | -0.00086917 | 0.0001725 | 0.0001815 | -0.00025427 | 164.7584 | -5.0378 | 0.039098 | -0.031888 | 0.00034957 | -0.00029248 | 0.0046725 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.81351 | 0.18649 | 0.47174 | 0.53805 | -0.0097936 | 2.4052 | 1.1509 | ; | Mfg6 | 324 | Elec | Mfg6 | Mfg6_324 | Pkg DX, Tier 1, Mfg6 324 (12.5 ton, 10.5 rated EER) | PkgDX T1 Mfg6 324 12.5t 10.5eer
32105 | 1 | 12.5 | 1 | 10.8 | 10.8 | 160000 | 0.7313 | 0.26575 | 0.02734 | 0.21829 | 0.006875 | 0.0052 | 0 | 55 | 1.0071 | -0.014956 | 0.000292 | 0.0039846 | -6.375e-06 | -0.00010006 | 2.6509 | 0.0048864 | -0.00041267 | -0.0064958 | -1.1256e-05 | 9.3143e-05 | -0.090316 | 0.019279 | -0.00010467 | 0.0011497 | 0.0001288 | -0.0001576 | 491.9415 | -17.249 | 0.16066 | 2.0277 | 0.0061111 | -0.047801 | 0.0040028 | 0.9901 | 0.095998 | -0.086528 | 0.92022 | 0.2688 | -0.4089 | 0.21568 | 0.925 | 1 | 2 | 0.4 | 0.5 | 0.82419 | 0.17581 | 0.48911 | 0.48677 | 0.024125 | 2.508 | 1.389 | ; | Mfg1 | 325 | Gas | Mfg1 | Mfg1_325 | Pkg DX, Tier 1, Mfg1 325 (12.5 ton, 10.8 rated EER) | PkgDX T1 Mfg1 325 12.5t 10.8eer
32106 | 1 | 15 | 1 | 10.8 | 10.8 | 155000 | 0.6839 | 0.26412 | 0.02323 | 0.26528 | 0.0070968 | 0.01 | 0 | 55 | 0.69682 | -0.0056996 | 0.00021467 | 0.002918 | -9.6369e-06 | -7.3657e-05 | 3.0892 | -0.01577 | -0.00019167 | -0.0026785 | -6.3452e-06 | 2.1914e-05 | 0.37348 | 0.0021985 | 4.8e-05 | 0.0042982 | 0.00012882 | -0.00020537 | 366.6858 | -11.9457 | 0.09831 | 0.69436 | 0.00083801 | -0.012594 | 0.0040028 | 0.9901 | 0.095998 | -0.086528 | 0.92022 | 0.2688 | -0.4089 | 0.21568 | 0.925 | 1 | 2 | 0.4 | 0.5 | 0.85067 | 0.14933 | 0.53987 | 0.4421 | 0.01803 | 1.5919 | 1.3846 | ; | Mfg1 | 326 | Gas | Mfg1 | Mfg1_326 | Pkg DX, Tier 1, Mfg1 326 (15 ton, 10.8 rated EER) | PkgDX T1 Mfg1 326 15t 10.8eer
32107 | 1 | 18 | 1 | 10.8 | 10.8 | 205000 | 0.7024 | 0.25573 | 0.02634 | 0.31259 | 0.0068293 | 0.0584 | 0 | 55 | 0.2678 | 0.0040828 | 0.00014567 | 0.0052817 | -1.9137e-05 | -8.2371e-05 | 3.141 | -0.01411 | -0.00023267 | -0.0040062 | -8.2738e-06 | 4.7771e-05 | 0.73055 | -0.0030294 | 5.5333e-05 | 0.002127 | 0.00012676 | -0.00017629 | 31.6553 | -1.1317 | 0.010174 | 0.14622 | 5.5736e-05 | -0.0023404 | 0.0046725 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.86829 | 0.13171 | 0.35417 | 0.77083 | -0.125 | 2.3191 | 1.3383 | ; | Mfg1 | 327 | Gas | Mfg1 | Mfg1_327 | Pkg DX, Tier 1, Mfg1 327 (18 ton, 10.8 rated EER) | PkgDX T1 Mfg1 327 18t 10.8eer
32108 | 1 | 20 | 1 | 10.8 | 10.8 | 241000 | 0.6929 | 0.25754 | 0.0249 | 0.34567 | 0.0058091 | 0.0363 | 0 | 55 | 0.20119 | 0.0071137 | 0.00011033 | 0.0050222 | -2.197e-05 | -7.1e-05 | 3.2416 | -0.018209 | -0.00019933 | -0.0034669 | -1.1405e-05 | 4.8e-05 | 0.89204 | -0.010253 | 0.00010767 | 0.001958 | 0.00012045 | -0.00015106 | 39.3409 | -1.4185 | 0.013121 | 0.19095 | 0.0002208 | -0.0035085 | 0.0046725 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.87552 | 0.12448 | 0.40719 | 0.7006 | -0.10778 | 2.3597 | 1.3301 | ; | Mfg1 | 328 | Gas | Mfg1 | Mfg1_328 | Pkg DX, Tier 1, Mfg1 328 (20 ton, 10.8 rated EER) | PkgDX T1 Mfg1 328 20t 10.8eer
32109 | 1 | 12 | 2 | 10.8 | 10.8 | 164600 | 0.7813 | 0.25045 | 0.03159 | 0.30135 | 0.0066829 | 0.0117 | 0 | 55 | 1.8125 | -0.039797 | 0.000468 | 0.0055725 | -1.3607e-05 | -0.00010269 | 0.44582 | 0.076941 | -0.0010057 | -0.010402 | -1.572e-05 | 0.00016397 | -0.63658 | 0.040875 | -0.00029067 | -0.0032776 | 0.0001339 | -0.00010909 | 706.831 | -21.7122 | 0.16821 | 0.90374 | 0.0013204 | -0.016337 | 0.0046725 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.86666 | 0.13334 | 0.30892 | 0.83672 | -0.14564 | 2.1694 | 1.3103 | ; | Mfg1 | 329 | Elec | Mfg1 | Mfg1_329 | Pkg DX, Tier 1, Mfg1 329 (12 ton, 10.8 rated EER) | PkgDX T1 Mfg1 329 12t 10.8eer
32110 | 1 | 15 | 2 | 10.8 | 10.8 | 190000 | 0.7158 | 0.2473 | 0.03158 | 0.34517 | 0.0057895 | 0.179 | 0 | 55 | -0.087576 | 0.016776 | 7.0667e-05 | 0.0056185 | -5.0298e-06 | -0.00013229 | 1.4257 | 0.043668 | -0.00070833 | -0.0051632 | -1.7298e-05 | 7.46e-05 | 1.1106 | -0.0057161 | 3.8667e-05 | -0.0054585 | 0.00013208 | -9.0286e-05 | 48.9128 | -1.4272 | 0.010582 | -0.034858 | 0.00012223 | 0.00037923 | 0.0040028 | 0.9901 | 0.095998 | -0.086528 | 0.92022 | 0.2688 | -0.4089 | 0.21568 | 0.925 | 1 | 2 | 0.4 | 0.5 | 0.90376 | 0.096241 | 0.40196 | 0.67647 | -0.078431 | 2.2553 | 1.2809 | ; | Mfg1 | 330 | Elec | Mfg1 | Mfg1_330 | Pkg DX, Tier 1, Mfg1 330 (15 ton, 10.8 rated EER) | PkgDX T1 Mfg1 330 15t 10.8eer
32111 | 1 | 12.5 | 0 | 10.9 | 10.9 | 155900 | 0.6793 | 0.21129 | 0.02646 | 0.582 | 0.0096216 | 0.1382 | 0 | 55 | 3.9034 | -0.097222 | 0.00089583 | 0.0016288 | -1.4942e-05 | -6.7686e-05 | -4.4869 | 0.23938 | -0.0023545 | -0.01709 | -4.2433e-05 | 0.00031801 | -3.5747 | 0.12598 | -0.00086917 | 0.0001725 | 0.0001815 | -0.00025427 | 164.7584 | -5.0378 | 0.039098 | -0.031888 | 0.00034957 | -0.00029248 | 0.0046725 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.81351 | 0.18649 | 0.47174 | 0.53805 | -0.0097936 | 2.4857 | 1.1896 | ; | Mfg6 | 331 | None | Mfg6 | Mfg6_331 | Pkg DX, Tier 1, Mfg6 331 (12.5 ton, 10.9 rated EER) | PkgDX T1 Mfg6 331 12.5t 10.9eer
32112 | 1 | 20 | 2 | 11 | 11 | 250300 | 0.72 | 0.25672 | 0.02996 | 0.2577 | 0.0055733 | 0.1231 | 0 | 55 | 1.2765 | -0.021756 | 0.00031875 | 0.0029351 | -1.325e-05 | -6.425e-05 | 9.4794 | -0.21145 | 0.0012789 | 0.0075083 | -1.2417e-05 | -0.00010287 | -0.29628 | 0.03078 | -0.00016484 | -0.0021412 | 0.00017508 | -0.00022038 | 60.5894 | -1.8512 | 0.014644 | -0.011516 | 0.00010184 | -0.00017595 | 0.0046844 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.87816 | 0.12184 | 0.52777 | 0.40083 | 0.071394 | 2.6112 | 1.3496 | ; | Mfg3 | 332 | Elec | Mfg3 | Mfg3_332 | Pkg DX, Tier 1, Mfg3 332 (20 ton, 11 rated EER) | PkgDX T1 Mfg3 332 20t 11eer
32113 | 1 | 20 | 1 | 11 | 11 | 250300 | 0.72 | 0.25409 | 0.02996 | 0.2773 | 0.0055733 | 0.1231 | 0 | 55 | 1.2765 | -0.021756 | 0.00031875 | 0.0029351 | -1.325e-05 | -6.425e-05 | 9.4794 | -0.21145 | 0.0012789 | 0.0075083 | -1.2417e-05 | -0.00010287 | -0.29628 | 0.03078 | -0.00016484 | -0.0021412 | 0.00017508 | -0.00022038 | 60.5894 | -1.8512 | 0.014644 | -0.011516 | 0.00010184 | -0.00017595 | 0.0046844 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.87816 | 0.12184 | 0.52777 | 0.40083 | 0.071394 | 2.5952 | 1.3366 | ; | Mfg3 | 333 | Gas | Mfg3 | Mfg3_333 | Pkg DX, Tier 1, Mfg3 333 (20 ton, 11 rated EER) | PkgDX T1 Mfg3 333 20t 11eer
32114 | 1 | 20 | 2 | 11 | 11 | 259000 | 0.7336 | 0.20886 | 0.03089 | 0.639 | 0.003861 | 0.1132 | 0 | 55 | 3.5104 | -0.073368 | 0.00065 | -0.010055 | 2.4308e-05 | 3.5063e-05 | -5.598 | 0.19772 | -0.0016138 | 0.035346 | -0.00012922 | -0.00025083 | -2.3986 | 0.071541 | -0.00041517 | 0.017196 | 8.1844e-05 | -0.00029901 | 153.3705 | -3.8865 | 0.024905 | -0.59128 | 0.0011798 | 0.0065594 | 0.0046725 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.82129 | 0.17871 | -0.51579 | 2.6386 | -1.1228 | 2.7627 | 1.1077 | ; | Mfg6 | 334 | Elec | Mfg6 | Mfg6_334 | Pkg DX, Tier 1, Mfg6 334 (20 ton, 11 rated EER) | PkgDX T1 Mfg6 334 20t 11eer
32115 | 1 | 12.5 | 2 | 11.2 | 11.2 | 154000 | 0.6688 | 0.21637 | 0.02435 | 0.508 | 0.0097403 | 0.1019 | 0 | 55 | 3.3488 | -0.09064 | 0.00087 | 0.0082971 | -3.1339e-05 | -0.0001079 | -2.6261 | 0.18874 | -0.0019804 | -0.02381 | -2.2571e-05 | 0.000367 | -2.6162 | 0.11691 | -0.0008542 | -0.012404 | 0.00021066 | -0.00017366 | 176.6764 | -5.9473 | 0.048341 | 0.33693 | -0.00044332 | -0.0034909 | 0.0046725 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.91095 | 0.089054 | 0.79612 | 0.029126 | 0.17476 | 2.3158 | 1.2503 | ; | Mfg6 | 335 | Elec | Mfg6 | Mfg6_335 | Pkg DX, Tier 1, Mfg6 335 (12.5 ton, 11.2 rated EER) | PkgDX T1 Mfg6 335 12.5t 11.2eer
32116 | 1 | 12.5 | 1 | 11.2 | 11.2 | 155900 | 0.6793 | 0.21242 | 0.02646 | 0.505 | 0.0096216 | 0.1382 | 0 | 55 | 3.9034 | -0.097222 | 0.00089583 | 0.0016288 | -1.4942e-05 | -6.7686e-05 | -4.4869 | 0.23938 | -0.0023545 | -0.01709 | -4.2433e-05 | 0.00031801 | -3.5747 | 0.12598 | -0.00086917 | 0.0001725 | 0.0001815 | -0.00025427 | 164.7584 | -5.0378 | 0.039098 | -0.031888 | 0.00034957 | -0.00029248 | 0.0046725 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.81351 | 0.18649 | 0.47174 | 0.53805 | -0.0097936 | 2.5477 | 1.2301 | ; | Mfg6 | 336 | Gas | Mfg6 | Mfg6_336 | Pkg DX, Tier 1, Mfg6 336 (12.5 ton, 11.2 rated EER) | PkgDX T1 Mfg6 336 12.5t 11.2eer
32117 | 1 | 20 | 1 | 11.2 | 11.2 | 259000 | 0.7336 | 0.21023 | 0.03089 | 0.591 | 0.003861 | 0.1132 | 0 | 55 | 3.5104 | -0.073368 | 0.00065 | -0.010055 | 2.4308e-05 | 3.5063e-05 | -5.598 | 0.19772 | -0.0016138 | 0.035346 | -0.00012922 | -0.00025083 | -2.3986 | 0.071541 | -0.00041517 | 0.017196 | 8.1844e-05 | -0.00029901 | 153.3705 | -3.8865 | 0.024905 | -0.59128 | 0.0011798 | 0.0065594 | 0.0046725 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.82129 | 0.17871 | -0.51579 | 2.6386 | -1.1228 | 2.608 | 1.1351 | ; | Mfg6 | 337 | Gas | Mfg6 | Mfg6_337 | Pkg DX, Tier 1, Mfg6 337 (20 ton, 11.2 rated EER) | PkgDX T1 Mfg6 337 20t 11.2eer
32118 | 1 | 20 | 0 | 11.3 | 11.3 | 259000 | 0.7336 | 0.20976 | 0.03089 | 0.576 | 0.003861 | 0.1132 | 0 | 55 | 3.5104 | -0.073368 | 0.00065 | -0.010055 | 2.4308e-05 | 3.5063e-05 | -5.598 | 0.19772 | -0.0016138 | 0.035346 | -0.00012922 | -0.00025083 | -2.3986 | 0.071541 | -0.00041517 | 0.017196 | 8.1844e-05 | -0.00029901 | 153.3705 | -3.8865 | 0.024905 | -0.59128 | 0.0011798 | 0.0065594 | 0.0046725 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.82129 | 0.17871 | -0.51579 | 2.6386 | -1.1228 | 2.6933 | 1.1437 | ; | Mfg6 | 338 | None | Mfg6 | Mfg6_338 | Pkg DX, Tier 1, Mfg6 338 (20 ton, 11.3 rated EER) | PkgDX T1 Mfg6 338 20t 11.3eer
32201 | 2 | 12.5 | 2 | 11.5 | 11.5 | 159900 | 0.7261 | 0.22597 | 0.03127 | 0.342 | 0.0068793 | 0.1437 | 0 | 55 | 2.39 | -0.067989 | 0.00075565 | 0.012286 | -3.2771e-05 | -0.00017254 | -4.6458 | 0.22536 | -0.0020857 | -0.011367 | -1.5912e-05 | 0.000178 | -2.1836 | 0.091083 | -0.00070344 | -0.0054838 | 0.00016001 | -0.00010752 | 81.9514 | -2.5428 | 0.019377 | 0.12064 | -0.0003049 | -0.00098622 | 0.0046725 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.96 | 1 | 2 | 0.5 | 0.5 | 0.8374 | 0.1626 | 0.35056 | 0.7528 | -0.10336 | 2.7299 | 1.2852 | ; | Mfg1 | 339 | Elec | Mfg1 | Mfg1_339 | Pkg DX, Tier 2, Mfg1 339 (12.5 ton, 11.5 rated EER) | PkgDX T2 Mfg1 339 12.5t 11.5eer
32202 | 2 | 18 | 2 | 11.5 | 11.5 | 218600 | 0.73 | 0.24672 | 0.03019 | 0.2117 | 0.0063815 | 0.1025 | 0 | 55 | 1.052 | -0.016398 | 0.00029922 | 0.0037126 | -1.0667e-05 | -8.6875e-05 | 8.5211 | -0.17937 | 0.0010234 | 0.0032576 | -9.3333e-06 | -5.075e-05 | -0.056565 | 0.022625 | -0.00010625 | -0.00025583 | 0.00016792 | -0.0002315 | 61.8594 | -1.899 | 0.015078 | 0.028963 | 9.4173e-05 | -0.00077132 | 0.0046844 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.87283 | 0.12717 | 0.50208 | 0.4769 | 0.021014 | 2.4116 | 1.3794 | ; | Mfg3 | 340 | Elec | Mfg3 | Mfg3_340 | Pkg DX, Tier 2, Mfg3 340 (18 ton, 11.5 rated EER) | PkgDX T2 Mfg3 340 18t 11.5eer
32203 | 2 | 18 | 1 | 11.5 | 11.5 | 218600 | 0.73 | 0.24386 | 0.03019 | 0.233 | 0.0063815 | 0.1025 | 0 | 55 | 1.052 | -0.016398 | 0.00029922 | 0.0037126 | -1.0667e-05 | -8.6875e-05 | 8.5211 | -0.17937 | 0.0010234 | 0.0032576 | -9.3333e-06 | -5.075e-05 | -0.056565 | 0.022625 | -0.00010625 | -0.00025583 | 0.00016792 | -0.0002315 | 61.8594 | -1.899 | 0.015078 | 0.028963 | 9.4173e-05 | -0.00077132 | 0.0046844 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.87283 | 0.12717 | 0.50208 | 0.4769 | 0.021014 | 2.3899 | 1.3649 | ; | Mfg3 | 341 | Gas | Mfg3 | Mfg3_341 | Pkg DX, Tier 2, Mfg3 341 (18 ton, 11.5 rated EER) | PkgDX T2 Mfg3 341 18t 11.5eer
32204 | 2 | 12.5 | 0 | 11.5 | 11.5 | 154000 | 0.6688 | 0.21569 | 0.02435 | 0.444 | 0.0097403 | 0.1019 | 0 | 55 | 3.3488 | -0.09064 | 0.00087 | 0.0082971 | -3.1339e-05 | -0.0001079 | -2.6261 | 0.18874 | -0.0019804 | -0.02381 | -2.2571e-05 | 0.000367 | -2.6162 | 0.11691 | -0.0008542 | -0.012404 | 0.00021066 | -0.00017366 | 176.6764 | -5.9473 | 0.048341 | 0.33693 | -0.00044332 | -0.0034909 | 0.0046725 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.91095 | 0.089054 | 0.79612 | 0.029126 | 0.17476 | 2.0182 | 1.2828 | ; | Mfg6 | 342 | None | Mfg6 | Mfg6_342 | Pkg DX, Tier 2, Mfg6 342 (12.5 ton, 11.5 rated EER) | PkgDX T2 Mfg6 342 12.5t 11.5eer
32205 | 2 | 18 | 1 | 11.6 | 11.6 | 205700 | 0.7443 | 0.24907 | 0.035 | 0.14181 | 0.006806 | 0.1925 | 0 | 55 | -0.99616 | 0.052843 | -0.00021192 | -0.00060613 | 3.7477e-07 | -8.465e-05 | -6.8583 | 0.26617 | -0.0021791 | 0.0050054 | -3.2964e-05 | -5.8248e-05 | 1.7229 | -0.0602 | 0.00056607 | 0.018074 | 0.0001249 | -0.00032599 | 64.4283 | -1.562 | 0.0094901 | -0.20645 | 0.00037738 | 0.0023305 | 0.0046725 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.96 | 1 | 2 | 0.5 | 0.5 | 0.43218 | 0.56782 | -2.7596 | 6.8321 | -3.0725 | 2.5388 | 1.4122 | ; | Mfg1 | 343 | Gas | Mfg1 | Mfg1_343 | Pkg DX, Tier 2, Mfg1 343 (18 ton, 11.6 rated EER) | PkgDX T2 Mfg1 343 18t 11.6eer
32206 | 2 | 20 | 1 | 11.6 | 11.6 | 252000 | 0.7143 | 0.21984 | 0.03175 | 0.39525 | 0.0055556 | 0.1873 | 0 | 55 | -1.2089 | 0.058714 | -0.00025946 | -0.0044846 | -5.7703e-09 | -2.108e-05 | -6.6345 | 0.25691 | -0.0020818 | 0.0038064 | -3.0068e-05 | -5.0782e-05 | 2.4989 | -0.10227 | 0.0010305 | 0.036432 | 0.00013439 | -0.00062009 | 50.4396 | -1.2219 | 0.0071437 | -0.15846 | 0.00024732 | 0.0020705 | 0.0046725 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.96 | 1 | 2 | 0.5 | 0.5 | 0.90476 | 0.095238 | 0.28889 | 1.0667 | -0.35556 | 3.0273 | 1.2467 | ; | Mfg1 | 344 | Gas | Mfg1 | Mfg1_344 | Pkg DX, Tier 2, Mfg1 344 (20 ton, 11.6 rated EER) | PkgDX T2 Mfg1 344 20t 11.6eer
32207 | 2 | 15 | 2 | 11.6 | 11.6 | 187300 | 0.7421 | 0.24607 | 0.03203 | 0.19867 | 0.0058729 | 0.1232 | 0 | 55 | 2.3154 | -0.061464 | 0.00069482 | 0.0091184 | -2.1635e-05 | -0.00015512 | -3.4846 | 0.18847 | -0.0018015 | -0.0085058 | -2.9129e-05 | 0.00015948 | -1.8883 | 0.080019 | -0.00060583 | -0.0029144 | 0.00016209 | -0.0001476 | 92.02 | -2.8116 | 0.021558 | 0.068599 | 2.197e-05 | -0.00096277 | 0.0034466 | 1.0125 | 0.059111 | -0.072068 | 0.91241 | 0.24998 | -0.35145 | 0.1856 | 0.925 | 1 | 2 | 0.33 | 0.5 | 0.84517 | 0.15483 | 0.37554 | 0.71655 | -0.092086 | 2.4773 | 1.3801 | ; | Mfg1 | 345 | Elec | Mfg1 | Mfg1_345 | Pkg DX, Tier 2, Mfg1 345 (15 ton, 11.6 rated EER) | PkgDX T2 Mfg1 345 15t 11.6eer
32208 | 2 | 21 | 2 | 11.6 | 11.6 | 252000 | 0.7143 | 0.2262 | 0.03175 | 0.34987 | 0.0055556 | 0.1873 | 0 | 55 | -1.2089 | 0.058714 | -0.00025946 | -0.0044846 | -5.7703e-09 | -2.108e-05 | -6.6345 | 0.25691 | -0.0020818 | 0.0038064 | -3.0068e-05 | -5.0782e-05 | 2.4989 | -0.10227 | 0.0010305 | 0.036432 | 0.00013439 | -0.00062009 | 50.4396 | -1.2219 | 0.0071437 | -0.15846 | 0.00024732 | 0.0020705 | 0.0046725 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.96 | 1 | 2 | 0.5 | 0.5 | 0.90476 | 0.095238 | 0.28889 | 1.0667 | -0.35556 | 2.5179 | 1.2765 | ; | Mfg1 | 346 | Elec | Mfg1 | Mfg1_346 | Pkg DX, Tier 2, Mfg1 346 (21 ton, 11.6 rated EER) | PkgDX T2 Mfg1 346 21t 11.6eer
32209 | 2 | 18 | 2 | 11.8 | 11.8 | 205700 | 0.7443 | 0.24417 | 0.035 | 0.14181 | 0.006806 | 0.1925 | 0 | 55 | -0.99616 | 0.052843 | -0.00021192 | -0.00060613 | 3.7477e-07 | -8.465e-05 | -6.8583 | 0.26617 | -0.0021791 | 0.0050054 | -3.2964e-05 | -5.8248e-05 | 1.7229 | -0.0602 | 0.00056607 | 0.018074 | 0.0001249 | -0.00032599 | 64.4283 | -1.562 | 0.0094901 | -0.20645 | 0.00037738 | 0.0023305 | 0.0046725 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.96 | 1 | 2 | 0.5 | 0.5 | 0.43218 | 0.56782 | -2.7596 | 6.8321 | -3.0725 | 2.5104 | 1.4122 | ; | Mfg1 | 347 | Elec | Mfg1 | Mfg1_347 | Pkg DX, Tier 2, Mfg1 347 (18 ton, 11.8 rated EER) | PkgDX T2 Mfg1 347 18t 11.8eer
32210 | 2 | 15 | 2 | 11.8 | 11.8 | 187100 | 0.71 | 0.24234 | 0.03046 | 0.16 | 0.0074559 | 0.1649 | 0 | 55 | 1.1934 | -0.018914 | 0.00029766 | 0.0023663 | -1.0333e-05 | -6.1875e-05 | 7.2848 | -0.12833 | 0.00056094 | -0.0062854 | 3.0833e-06 | 5.725e-05 | 0.12376 | 0.017228 | -4.8437e-05 | -0.0003175 | 0.000174 | -0.0002515 | 39.1536 | -1.3275 | 0.011279 | 0.093042 | -6.7747e-05 | -0.0012675 | 0.00046003 | 1.0125 | 0.059111 | -0.072068 | 0.91241 | 0.24998 | -0.35145 | 0.1856 | 0.96 | 1 | 2 | 0.33 | 0.33 | 0.87524 | 0.12476 | 0.45094 | 0.59528 | -0.046221 | 2.2032 | 1.4143 | ; | Mfg3 | 348 | Elec | Mfg3 | Mfg3_348 | Pkg DX, Tier 2, Mfg3 348 (15 ton, 11.8 rated EER) | PkgDX T2 Mfg3 348 15t 11.8eer
32211 | 2 | 15 | 1 | 11.8 | 11.8 | 187100 | 0.71 | 0.2402 | 0.03046 | 0.176 | 0.0074559 | 0.1649 | 0 | 55 | 1.1934 | -0.018914 | 0.00029766 | 0.0023663 | -1.0333e-05 | -6.1875e-05 | 7.2848 | -0.12833 | 0.00056094 | -0.0062854 | 3.0833e-06 | 5.725e-05 | 0.12376 | 0.017228 | -4.8437e-05 | -0.0003175 | 0.000174 | -0.0002515 | 39.1536 | -1.3275 | 0.011279 | 0.093042 | -6.7747e-05 | -0.0012675 | 0.00046003 | 1.0125 | 0.059111 | -0.072068 | 0.91241 | 0.24998 | -0.35145 | 0.1856 | 0.96 | 1 | 2 | 0.33 | 0.33 | 0.87524 | 0.12476 | 0.45094 | 0.59528 | -0.046221 | 2.168 | 1.403 | ; | Mfg3 | 349 | Gas | Mfg3 | Mfg3_349 | Pkg DX, Tier 2, Mfg3 349 (15 ton, 11.8 rated EER) | PkgDX T2 Mfg3 349 15t 11.8eer
32212 | 2 | 20 | 2 | 11 | 11 | 250300 | 0.72 | 0.25672 | 0.02996 | 0.2577 | 0.0055733 | 0.1231 | 0 | 55 | 1.2765 | -0.021756 | 0.00031875 | 0.0029351 | -1.325e-05 | -6.425e-05 | 9.4794 | -0.21145 | 0.0012789 | 0.0075083 | -1.2417e-05 | -0.00010287 | -0.29628 | 0.03078 | -0.00016484 | -0.0021412 | 0.00017508 | -0.00022038 | 60.5894 | -1.8512 | 0.014644 | -0.011516 | 0.00010184 | -0.00017595 | 0.0046844 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.87816 | 0.12184 | 0.52777 | 0.40083 | 0.071394 | 2.6112 | 1.3496 | ; | Mfg3 | 350 | Elec | Mfg3 | Mfg3_350 | Pkg DX, Tier 2, Mfg3 350 (20 ton, 11 rated EER) | PkgDX T2 Mfg3 350 20t 11eer
32301 | 3 | 15 | 2 | 12 | 12 | 191000 | 0.733 | 0.1892 | 0.03141 | 0.562 | 0.0052356 | 0.1296 | 0 | 55 | 3.5692 | -0.078766 | 0.000733 | -0.0075446 | 2.8777e-05 | -1.968e-05 | -5.7679 | 0.20645 | -0.0016785 | 0.033811 | -0.00012213 | -0.00025759 | -2.604 | 0.077222 | -0.00049317 | 0.016866 | 7.621e-05 | -0.00025863 | 128.7776 | -3.3592 | 0.02205 | -0.43428 | 0.0008667 | 0.004987 | 0.0046725 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.72775 | 0.27225 | 0.44286 | 0.5 | 0.057143 | 2.2176 | 1.1464 | ; | Mfg6 | 351 | Elec | Mfg6 | Mfg6_351 | Pkg DX, Tier 3, Mfg6 351 (15 ton, 12 rated EER) | PkgDX T3 Mfg6 351 15t 12eer
32302 | 3 | 15 | 1 | 12 | 12 | 191000 | 0.733 | 0.18989 | 0.03141 | 0.557 | 0.0052356 | 0.1296 | 0 | 55 | 3.5692 | -0.078766 | 0.000733 | -0.0075446 | 2.8777e-05 | -1.968e-05 | -5.7679 | 0.20645 | -0.0016785 | 0.033811 | -0.00012213 | -0.00025759 | -2.604 | 0.077222 | -0.00049317 | 0.016866 | 7.621e-05 | -0.00025863 | 128.7776 | -3.3592 | 0.02205 | -0.43428 | 0.0008667 | 0.004987 | 0.0046725 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.72775 | 0.27225 | 0.44286 | 0.5 | 0.057143 | 2.2131 | 1.1493 | ; | Mfg6 | 352 | Gas | Mfg6 | Mfg6_352 | Pkg DX, Tier 3, Mfg6 352 (15 ton, 12 rated EER) | PkgDX T3 Mfg6 352 15t 12eer
32303 | 3 | 12.5 | 2 | 12.2 | 12.2 | 160000 | 0.72 | 0.2289 | 0.0325 | 0.1487 | 0.0087188 | 0.1916 | 0 | 55 | 1.4046 | -0.029317 | 0.00040547 | 0.0052217 | -1.3917e-05 | -9.9125e-05 | 11.0768 | -0.24327 | 0.0014477 | -0.0031757 | 9.0833e-06 | -8.875e-06 | -0.55081 | 0.038117 | -0.00022422 | -0.00021904 | 0.00016975 | -0.00023687 | 28.6078 | -0.97617 | 0.0082271 | 0.070311 | -0.0001214 | -0.00074151 | 0.00046003 | 1.0125 | 0.059111 | -0.072068 | 0.91241 | 0.24998 | -0.35145 | 0.1856 | 0.96 | 1 | 2 | 0.33 | 0.33 | 0.86094 | 0.13906 | 0.73064 | -0.016992 | 0.28635 | 1.9472 | 1.4152 | ; | Mfg3 | 353 | Elec | Mfg3 | Mfg3_353 | Pkg DX, Tier 3, Mfg3 353 (12.5 ton, 12.2 rated EER) | PkgDX T3 Mfg3 353 12.5t 12.2eer
32304 | 3 | 12.5 | 1 | 12.2 | 12.2 | 160000 | 0.72 | 0.22698 | 0.0325 | 0.1621 | 0.0087188 | 0.1916 | 0 | 55 | 1.4046 | -0.029317 | 0.00040547 | 0.0052217 | -1.3917e-05 | -9.9125e-05 | 11.0768 | -0.24327 | 0.0014477 | -0.0031757 | 9.0833e-06 | -8.875e-06 | -0.55081 | 0.038117 | -0.00022422 | -0.00021904 | 0.00016975 | -0.00023687 | 28.6078 | -0.97617 | 0.0082271 | 0.070311 | -0.0001214 | -0.00074151 | 0.00046003 | 1.0125 | 0.059111 | -0.072068 | 0.91241 | 0.24998 | -0.35145 | 0.1856 | 0.96 | 1 | 2 | 0.33 | 0.33 | 0.86094 | 0.13906 | 0.73064 | -0.016992 | 0.28635 | 1.9682 | 1.4051 | ; | Mfg3 | 354 | Gas | Mfg3 | Mfg3_354 | Pkg DX, Tier 3, Mfg3 354 (12.5 ton, 12.2 rated EER) | PkgDX T3 Mfg3 354 12.5t 12.2eer
32305 | 3 | 15 | 0 | 12.3 | 12.3 | 191000 | 0.733 | 0.18974 | 0.03141 | 0.542 | 0.0052356 | 0.1296 | 0 | 55 | 3.5692 | -0.078766 | 0.000733 | -0.0075446 | 2.8777e-05 | -1.968e-05 | -5.7679 | 0.20645 | -0.0016785 | 0.033811 | -0.00012213 | -0.00025759 | -2.604 | 0.077222 | -0.00049317 | 0.016866 | 7.621e-05 | -0.00025863 | 128.7776 | -3.3592 | 0.02205 | -0.43428 | 0.0008667 | 0.004987 | 0.0046725 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.925 | 1 | 2 | 0.5 | 0.5 | 0.72775 | 0.27225 | 0.44286 | 0.5 | 0.057143 | 2.1821 | 1.1583 | ; | Mfg6 | 355 | None | Mfg6 | Mfg6_355 | Pkg DX, Tier 3, Mfg6 355 (15 ton, 12.3 rated EER) | PkgDX T3 Mfg6 355 15t 12.3eer
32306 | 3 | 12.5 | 1 | 12.2 | 12.2 | 160000 | 0.72 | 0.22698 | 0.0325 | 0.1621 | 0.0087188 | 0.1916 | 0 | 55 | 3.5692 | -0.078766 | 0.000733 | -0.0075446 | 2.8777e-05 | -1.968e-05 | -5.7679 | 0.20645 | -0.0016785 | 0.033811 | -0.00012213 | -0.00025759 | -2.604 | 0.077222 | -0.00049317 | 0.016866 | 7.621e-05 | -0.00025863 | 128.7776 | -3.3592 | 0.02205 | -0.43428 | 0.0008667 | 0.004987 | 0.0046725 | 0.94113 | 0.2642 | -0.21002 | 0.93158 | 0.32329 | -0.67635 | 0.42329 | 0.96 | 1 | 2 | 0.5 | 0.5 | 0.72775 | 0.27225 | 0.44286 | 0.5 | 0.057143 | 1.9682 | 1.4051 | ; | Mfg3 | 356 | Gas | Mfg3 | Mfg3_356 | Pkg DX, Tier 3, Mfg3 356 (12.5 ton, 12.2 rated EER) | PkgDX T3 Mfg3 356 12.5t 12.2eer
; ERROR - No Match Found
-99 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1