## DEERDXEquipDetails
;-------------------------------------------------------------------------
; DEER - eQUEST Wizard Defaults: DX Equipment Details (based on SEER/EER research)
;-------------------------------------------------------------------------
;
; |  | Detailed AC and HP Unit Performance Data
;
; |  | Dec 2007: Updated by PRC with new values from John Hill for Two-Speed Units. Added SEER 19, 20, 21 for AC (not HP)
;
; |  | The performance of 500+ units examined were distilled down to 99 units, identified by the slope of the EER curve and the value of the
; |  | cycling degradation coefficient. The table below (starting at row 64) contains the data used to simulate the units examined in this study.
; | kjm 03/22/05 - Highlighted Rows/Columns are populated to DEER input files
; | [14 empty] | eQ Wizard Bdbase Property
; Data Key: |  | Data Key: | [11 empty] | Equipment Symbol Selection: | DetDXEquipType
; Dep Col(s) |  | Dep Col(s) | Usage | [14 empty] | BDL Keyword |  | Notes
; 1 |  | 1 | SEER | [11 empty] | DetDXCoolSEER |  |  | *** SEE NOTES *** |  | <SEER from this table> (see rule for setting COOLING-EIR)
; 2 |  | 2 | Unit's rated EER. | [11 empty] | DetDXCoolEER
; 3 |  | 3 | Actual unit total capacity. Value is for reference only and not used in simulations. | [11 empty] | DetDXCoolCap
; |  | Data used as DOE-2 simulation inputs. Fields are used as follows: | [27 empty] | Previous Version that held COOL-SH-CAP constant across runs - replaced 4/6/05
; 4 |  | 4 | Ratio of sensible to total capacity (sensible heat ratio) is used to establish COOL-SH-CAP from design cooling load. | [11 empty] | DetDXClSensTotRat |  |  | COOLING-CAPACITY |  | Sizing proc: | (1) Set SYSTEM:COOLING-CAPACITY based on SV-A of design run | [8 empty] | COOL-SH-CAP |  | Sizing procedure: (1) Capture (cooling capacity * sens heat ratio) from SV-A of design run and post to SYSTEM:COOL-SH-CAP
; |  |  | COOL-SH-CAP = COOLING-CAPACITY * Sen/Total | [14 empty] | (& COOL-SH-CAP) |  |  | (2) Multiply CoolCap by this value (Sens/Total) and post to SYSTEM:COOL-SH-CAP | [8 empty] | (& COOLING-CAPACITY) |  |  |  | (2) Divide by this value and post to SYSTEM:COOLING-CAPACITY
; 5 |  | 5 | Value is DOE-2 keyword COOLING-EIR | [11 empty] | DetDXCoolEIR |  |  | COOLING-EIR |  | COOLING-EIR = <SEER from this table>/<DEER Proto SEER> * <this value>
; 6 |  | 6 | cfm/Btuh is used to calculate design air flow as SUPPLY-CFM = cfm/Btuh * unit design capacity. | [11 empty] | DetDXCFMPerBTUH |  |  | SUPPLY-FLOW |  | SUPPLY-FLOW = <this value> * SYSTEM:COOLING-CAPACITY
; 7 |  | 7 | Fan W/cfm is used to set the fan power input and fan Delta T via the following keywords: | [11 empty] | DetDXFanWPerCFM |  |  | SUPPLY-KW/FLOW |  | SUPPLY-KW/FLOW = <this value> / 1000
; |  |  | SUPPLY-KW = (Fan W/cfm)/1,000 | [14 empty] | SUPPLY-DELTA-T |  | SUPPLY-DELTA-T = <this value> * 3.16
; |  |  | SUPPLY-DELTA-T = (Fan W/cfm)* 3.160
; 8 |  | 8 | Coil-BF is the design coil by-pass factor. The DOE-2 keyword COIL-BF = Coil-BF | [11 empty] | SysCoilBF |  |  | COIL-BF
; 9 |  | 9 | Crkn/Tot kW is used to set the keyword CRANKCASE-HEAT, and is the ratio of crankcase load heat to the design compressor load. | [14 empty] | CRANKCASE-HEAT |  | CRANKCASE-HEAT = 0 ***For all DEER simulations***
; 10 |  | 10 | Crnk Off is the temperature above which crankcase heat is deactivated and is the value used for the keyword CRANKCASE-MAX-T.
; 11 - 16 |  | 11 - 16 | The coefficients for the bi-quadratic total capacity off-design curve set by the keyword COOL-CAP-FT | [11 empty] | DetDXCoilCapFTCoef |  |  | COOL-CAP-FT |  | TYPE = BI-QUADRATIC-T, INPUT-TYPE = COEFFICIENTS, COEFFICIENTS = <these values>
; 17 - 22 |  | 17 - 22 | The coefficients for the bi-quadratic sensible capacity off-design curve set by the keyword COOL-SH-FT | [11 empty] | DetDXCoolSHFTCoef |  |  | COOL-SH-FT |  | TYPE = BI-QUADRATIC-T, INPUT-TYPE = COEFFICIENTS, COEFFICIENTS = <these values>
; 23 - 28 |  | 23 - 28 | The coefficients for the bi-quadratic EIR off-design curve set by the keyword COOL-EIR-FT | [11 empty] | DetDXCoolEIRFTCoef |  |  | COOL-EIR-FT |  | TYPE = BI-QUADRATIC-T, INPUT-TYPE = COEFFICIENTS, COEFFICIENTS = <these values>
; 29 - 34 |  | 29 - 34 | The coefficients for the bi-quadratic coil by-pass factor off-design curve set by the keyword COIL-BF-FT | [11 empty] | DetDXCoilBFFTCoef |  |  | COIL-BF-FT |  | TYPE = BI-QUADRATIC-T, INPUT-TYPE = COEFFICIENTS, COEFFICIENTS = <these values>
; |  |  | PRC (06-02-14): For this curve set, the following should be set: OUTPUT-MAX = 0.4/CoilBF, where the Coil-BF is specified in column 8. | [11 empty] | DetDXCoilBFFTMin / …Max
; |  |  | 06-02-14 Update includes all Coil-CF-FT coefficients along with random other fixes.
; 35 - 38 |  | 35 - 38 | The coefficients for the qubic equation that determines the EIR as a function of the part-load ratio for houses in temperate climate zones
; 39 - 42 |  | 39 - 42 | The coefficients for the qubic equation that determines the EIR as a function of the part-load ratio for houses in moderate climate zones | [11 empty] | DetDXClEIRFPLRCoef |  |  | COOL-EIR-FPLR & HEAT-" |  | TYPE = CUBIC, INPUT-TYPE = COEFFICIENTS, COEFFICIENTS = <these values>
; 43 - 46 |  | 43 - 46 | The coefficients for the qubic equation that determines the EIR as a function of the part-load ratio for houses in hot climate zones
; 47 - 49 |  | 47 - 49 | The coefficients for the quadratic equation of the C-LOSS curve for houses in temperate climate zones
; 50 - 52 |  | 50 - 52 | The coefficients for the quadratic equation of the C-LOSS curve for houses in moderate climate zones | [11 empty] | DetDXClClsFPLRCoef |  |  | COOL-CLOSS-FPLR |  | TYPE = QUADRATIC, INPUT-TYPE = COEFFICIENTS, COEFFICIENTS = <these values>
; 53 - 55 |  | 53 - 55 | The coefficients for the quadratic equation of the C-LOSS curve for houses in hot climate zones
; 56 |  | 56 | Number of compressor speeds (1 or 2). This is used as a flag to notify simulation when 2-speed equipment is to be simulated | [11 empty] | DetDXNumCompSpds |  |  | AIR/TEMP-CONTROL |  | ALWAYS set AIR/TEMP-CONTROL = TWO-SPEED
; 57 |  | 57 | Low speed cfm ratio for 2-speed units (ratio of low speed to high speed cfm) used by keyword MIN-FLOW-RATIO | [11 empty] | DetDXLoSpdCFMRat |  |  | *** SEE NOTES *** |  | if <comp spd> = 2, then MIN-FLOW-RATIO = <this value> AND (for HEAT-SOURCE = HEAT-PUMP) HMIN-FLOW-RATIO = <this value> | [9 empty] | HMIN-FLOW-RATIO for NON-HeatPump: = 1.0
; 58 |  | 58 | Low speed capacity ratio for 2-speed units (ratio of lowspeed to high speed cooling capacity) used by keyword COOL-STAGES | [11 empty] | DetDXLoSpdCapRat |  |  | *** SEE NOTES *** |  | if <comp spd> = 2, then COOL-STAGES = ( <this value>, 1.0 ) AND (for HEAT-SOURCE = HEAT-PUMP) HEAT-STAGES = ( <this value>, 1.0 ) | [9 empty] | HEAT-STAGES for NON-HeatPump: = (0.9989, 1.0)
; | [19 empty] | if <comp spd> = 2, then MIN-UNLOAD-RATIO = <this value> AND MIN-HGB-RATIO = <this value>,
; | [19 empty] | if <comp spd> = 2, then FAN-EIR-FPLR = "Residential Var Vol-Fan EIR"
; |  | Columns for heat pumps only. Colums BL and BN are descriptive only and not used in simulations
; 59 |  | 59 | For heat pumps only - rated HSPF | [11 empty] | DetHPHeatHSPF |  |  | *** SEE NOTES *** |  | <HSPF from this table> (see rule for setting HEATING-EIR)
; 60 |  | 60 | For heat pumps only - rated COP at 47 outdoor temperature. Keyword HEATING-EIR = 1/(COP at 47 ODB)
; 61 |  | 61 | For heat pumps only - Actual unit rated heating capacity. Value is for reference only and not used in simulations.
; 62 |  | 62 | Heating EIR from manufacturers expanded ratings chart. Used only as a check with the rated COP at 47 ODB. | [11 empty] | DetHPHeatEIR |  |  | HEATING-EIR |  | HEATING-EIR = <HSPF from this table>/<DEER Proto HSPF> * <this value>
; 63 - 68 |  | 63 - 68 | For heat pumps only - the coefficients of the bi-quadratic heating capacity off-design curve set by keyword HEAT-CAP-FT | [11 empty] | DetHPHeatCapFTCoef |  |  | HEAT-CAP-FT |  | TYPE = BI-QUADRATIC-T, INPUT-TYPE = COEFFICIENTS, COEFFICIENTS = <these values>
; 69 - 74 |  | 69 - 74 | For heat pumps only - the coefficients of the bi-quadratic heating EIR off-design curve set by keyword HEAT-EIR-FT | [11 empty] | DetHPHeatEIRFTCoef |  |  | HEAT-EIR-FT |  | TYPE = BI-QUADRATIC-T, INPUT-TYPE = COEFFICIENTS, COEFFICIENTS = <these values>
; 75 - 78 |  | 75 - 78 | The coefficients C0 & C1 and the Min and Max values of the linear curve-fit command assigned to keyword COIL-BF-FFLOW | [11 empty] | DetDXBFFFlowCoef |  |  | COIL-BF-FFLOW |  | TYPE = LINEAR, INPUT-TYPE = COEFFICIENTS, COEFFICIENTS = <these values> | [8 empty] | COIL-BF-FFLOW-SPEC = CURVE-FIT
; |  | Added by PRC June 9 2005 | [12 empty] | DetDXBFFFlowMin // …Max |  |  | Min/Max of above curve | [10 empty] | TYPE = LINEAR
; | [28 empty] | INPUT-TYPE = COEFFICIENTS
; |  | Other Information not used as DOE-2 input fields. | [26 empty] | COEFFICIENTS = (col75,col76)
; BY. |  | BY. | eQUEST Wizard Symbol String | [25 empty] | OUTPUT-MIN = col77
; BZ. |  | BZ. | Evaporator configuration. Split-R indicates split-system residential units. | [25 empty] | OUTPUT-MAX = col78 ..
; CA. |  | CA. | Type of cooling unit -- AC is air conditioner and HP is heat pump. | [5 empty] | Columns CB through CE are needed for two-speed units only | [19 empty] | and for each SYSTEM:
; CB. |  | CB. | Sensitivity of units' EER to temperature. Values are Low, Median, and High. | [5 empty] | CB & CC | The coefficients C0 and C1 of the linear curve-fit command assigned to keyword COIL-BF-FFLOW | [18 empty] | COIL-BF-FFLOW = COIL-BF-FFLOW-SPEC
; CC. |  | CC. | Unit cycling degradation coefficient description. Values are Low, Median, and High. | [5 empty] | CD thru CE | The min and max values used in the same curve-fit command referenced above.
;
;
; | Typical DX Equipment by (AC/HP(1/2) * 100) + (SizeCateg(0) * 10) + Tier | [6 empty] | <<== Make sure any changes in default/typical unit IDs are also made to this table
; | 100 | 11009 | Split AC, SEER 10, High EER Slope, High Degrad. Coef | [5 empty] | Changes to these values may result in changes in DX Equip Map tab (via VLOOKUPs)
; | 101 | 11304 | Split AC, SEER 13, Med EER Slope, Low Degrad. Coef
; | 102 | 11501 | Split AC, SEER 15, Med EER Slope, Low Degrad. Coef
; | 103 | 11704 | Split AC, SEER 17, Mfg2 EER Slope, Low Degrad. Coef
; | 104 | 11802 | Split AC, SEER 18, Mfg2 EER Slope, High Degrad. Coef |  |  |  |  | <<-- SAC 6/27/08 - added per Paul's request
; | 200 | 21005 | Split HP, SEER 10, Med EER Slope, Med Degrad. Coef
; | 201 | 21305 | Split HP, SEER 13, Med EER Slope, Med Degrad. Coef
; | 202 | 21501 | Split HP, SEER 15, Med EER Slope, Low Degrad. Coef
; | 203 | 21704 | Split HP, SEER 17, Mfg4 EER Slope, High Degrad. Coef
;
;
;
; Indep. | Dependents
; 1 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78
; Indep. ; 1: ; Equip ID; Dependents 1: SEER; Dependents 2: EER; Dependents 3: Tot Cap; Dependents 4: Sen/Total; Dependents 5: EIR; Dependents 6: cfm/Btuh; Dependents 7: Fan W/cfm; Dependents 8: Coil-BF; Dependents 9: Crnk/Tot kW; Dependents 10: Crnk Off; Dependents 11: Total Capacity Curve Fit Coefficients; Dependents 17: Sensible Capacity Curve Fit Coefficients; Dependents 23: EIR Curve Fit Coefficients; Dependents 29: Coil-BF Curve Fit Coefficients; Dependents 35: Temperate EIR_PLR Curve Fit Coefficients; Dependents 39: Moderate EIR_PLR Curve Fit Coefficients; Dependents 43: Hot EIR_PLR Curve Fit Coefficients; Dependents 47: Temp C-Loss Curve Fit Coefficients; Dependents 50: Mod C-Loss Curve Fit Coefficients; Dependents 53: Hot C-Loss Curve Fit Coefficients; Dependents 56: Cmp Spd; Dependents 57: Low Speed Ratios; Dependents 59: HSPF; Dependents 60: COP47; Dependents 61: Heat Cap; Dependents 62: H-EIR; Dependents 63: Total Capacity Curve Fit Coefficients; Dependents 69: HIR Curve Fit Coefficients; Dependents 75: BF-FFLOW Curve Coeffients |  | eQUEST Wizard Symbol String | ID | Evap Config | Cool Type | EER Slope | CD
11001 | 10 | 8.87 | 23397 | 0.735 | 0.32576 | 0.03419 | 0.365 | 0.2127 | 0 | 100 | 2.1366 | -0.049513 | 0.00060311 | 0.0051714 | -6.3929e-06 | -0.00015086 | -1.6066 | 0.14422 | -0.001486 | -0.017898 | -2.381e-08 | 0.00020662 | -0.20834 | 0.029968 | -0.00027444 | -0.00042858 | 6.7994e-05 | -2.2073e-05 | 37.7193 | -1.0576 | 0.0076048 | 1e-12 | 1e-12 | 1e-12 | 2.4385e-06 | 1.0698 | -0.078346 | 0.0085766 | 7.2789e-06 | 1.0985 | -0.11487 | 0.016341 | 1.5536e-05 | 1.125 | -0.15035 | 0.025302 | 0.93446 | 0.069814 | -0.0042974 | 0.9095 | 0.098648 | -0.0081949 | 0.88732 | 0.12528 | -0.0127 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | ; | Split AC, SEER 10, Low EER Slope, Low Degrad. Coef | SA-10-LL | Split-R | AC | Low | Low
11002 | 10 | 9.29 | 30000 | 0.7667 | 0.30336 | 0.0375 | 0.365 | 0.2206 | 0 | 100 | 1.1609 | -0.028145 | 0.0004005 | 0.0095336 | -4.7167e-05 | -8.69e-05 | 0.5179 | 0.055771 | -0.000739 | -0.0031257 | -3.9833e-05 | 0.000113 | 0.44422 | 0.00787 | -4e-05 | 0.0012025 | 9.3333e-05 | -0.0001176 | 6.7763 | -0.086213 | 0 | 1e-12 | 1e-12 | 1e-12 | 2.1242e-05 | 1.1379 | -0.16819 | 0.030233 | 4.0782e-05 | 1.1692 | -0.21291 | 0.043626 | 6.7211e-05 | 1.1979 | -0.25553 | 0.057533 | 0.8768 | 0.13825 | -0.015181 | 0.8519 | 0.16981 | -0.021928 | 0.8298 | 0.19881 | -0.028946 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | ; | Split AC, SEER 10, Low EER Slope, Med Degrad. Coef | SA-10-LM | Split-R | AC | Low | Med
11003 | 10 | 9.51 | 24120 | 0.7803 | 0.2959 | 0.03731 | 0.365 | 0.1888 | 0 | 100 | 1.1473 | -0.028911 | 0.000414 | 0.010872 | -5.1667e-05 | -9.98e-05 | 0.36475 | 0.061711 | -0.000849 | -0.0046315 | -6.65e-05 | 0.0002124 | 0.83534 | 0.0017305 | -9.5e-06 | -0.002555 | 0.000111 | -0.0001049 | 8.8858 | -0.1177 | 0 | 1e-12 | 1e-12 | 1e-12 | 4.1054e-05 | 1.1696 | -0.21342 | 0.043788 | 7.1648e-05 | 1.2019 | -0.2616 | 0.059591 | 0.0001108 | 1.2315 | -0.30724 | 0.075607 | 0.85162 | 0.17017 | -0.02201 | 0.82677 | 0.20287 | -0.029985 | 0.80472 | 0.23287 | -0.038082 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | ; | Split AC, SEER 10, Low EER Slope, High Degrad. Coef | SA-10-LH | Split-R | AC | Low | High
11004 | 10 | 8.77 | 17947 | 0.7103 | 0.3311 | 0.03343 | 0.365 | 0.2537 | 0 | 100 | 1.8143 | -0.040224 | 0.00054456 | 0.0049525 | -4.5833e-06 | -0.000156 | -0.41194 | 0.10962 | -0.0012322 | -0.01885 | -1.1548e-06 | 0.00021991 | -0.055224 | 0.024173 | -0.00023156 | 0.00045781 | 7.3988e-05 | -3.7102e-05 | 23.6551 | -0.6431 | 0.0045517 | 1e-12 | 1e-12 | 1e-12 | 3.5993e-06 | 1.0789 | -0.08972 | 0.010809 | 9.756e-06 | 1.108 | -0.12741 | 0.019366 | 1.977e-05 | 1.1349 | -0.1639 | 0.029026 | 0.92642 | 0.078973 | -0.0054175 | 0.90146 | 0.10819 | -0.0097151 | 0.87929 | 0.13516 | -0.014573 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | ; | Split AC, SEER 10, Med EER Slope, Low Degrad. Coef | SA-10-ML | Split-R | AC | Med | Low
11005 | 10 | 9.08 | 35495 | 0.7662 | 0.31786 | 0.03381 | 0.365 | 0.1319 | 0 | 100 | -0.58806 | 0.032113 | 3.0888e-06 | 0.0044513 | 4.5818e-07 | -0.0001578 | 5.3907 | -0.061339 | -8.2689e-07 | -0.017483 | -9.6288e-06 | 0.00023103 | 0.6212 | 0.00017973 | -9.9627e-06 | 0.0021263 | 7.9472e-05 | -7.9771e-05 | 52.4841 | -1.5055 | 0.011002 | 1e-12 | 1e-12 | 1e-12 | 1.663e-05 | 1.1277 | -0.15405 | 0.026304 | 3.3211e-05 | 1.1587 | -0.19761 | 0.038895 | 5.6145e-05 | 1.1871 | -0.23924 | 0.052099 | 0.88511 | 0.12799 | -0.013204 | 0.86019 | 0.15916 | -0.019543 | 0.83808 | 0.18783 | -0.026202 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | ; | Split AC, SEER 10, Med EER Slope, Med Degrad. Coef | SA-10-MM | Split-R | AC | Med | Med
11006 | 10 | 9.83 | 18840 | 0.7612 | 0.2869 | 0.03583 | 0.365 | 0.1961 | 0 | 100 | 1.2756 | -0.034465 | 0.0004505 | 0.010942 | -5.7583e-05 | -7.99e-05 | 0.65755 | 0.047882 | -0.000663 | -0.00048887 | -4.65e-05 | 9.06e-05 | 0.34873 | 0.010851 | -6.45e-05 | 0.0025882 | 9.85e-05 | -0.0001447 | 7.6786 | -0.099681 | 0 | 1e-12 | 1e-12 | 1e-12 | 0.00021601 | 1.2854 | -0.39389 | 0.10824 | 0.00031399 | 1.3209 | -0.45319 | 0.13194 | 0.00042614 | 1.3532 | -0.5084 | 0.15482 | 0.76597 | 0.28782 | -0.054621 | 0.74134 | 0.32421 | -0.06666 | 0.71951 | 0.3574 | -0.078308 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | ; | Split AC, SEER 10, Med EER Slope, High Degrad. Coef | SA-10-MH | Split-R | AC | Med | High
11007 | 10 | 8.46 | 47993 | 0.7229 | 0.34522 | 0.03334 | 0.365 | 0.2213 | 0 | 100 | 1.8334 | -0.040389 | 0.00050267 | 0.0045755 | -8.1905e-06 | -0.00011698 | -1.1685 | 0.12379 | -0.0013098 | -0.013198 | -6.5238e-06 | 0.00016766 | -0.59695 | 0.038944 | -0.00029044 | -0.0024521 | 0.0001425 | -0.00011966 | 31.5863 | -0.87712 | 0.0062778 | 1e-12 | 1e-12 | 1e-12 | 7.1271e-06 | 1.0979 | -0.11402 | 0.016141 | 1.663e-05 | 1.1277 | -0.15405 | 0.026304 | 3.0936e-05 | 1.1552 | -0.1926 | 0.037377 | 0.91005 | 0.097994 | -0.0080948 | 0.88511 | 0.12799 | -0.013204 | 0.86296 | 0.15564 | -0.018779 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | ; | Split AC, SEER 10, High EER Slope, Low Degrad. Coef | SA-10-HL | Split-R | AC | High | Low
11008 | 10 | 8.79 | 48893 | 0.7239 | 0.33153 | 0.03272 | 0.365 | 0.2154 | 0 | 100 | 1.8967 | -0.043158 | 0.00052567 | 0.0048137 | -8.5833e-06 | -0.000117 | -1.2607 | 0.12654 | -0.0013233 | -0.013335 | -2.25e-06 | 0.00015866 | -0.36023 | 0.034808 | -0.00027133 | -0.0029425 | 0.00012808 | -9.9029e-05 | 27.2567 | -0.73746 | 0.0051578 | 1e-12 | 1e-12 | 1e-12 | 1.663e-05 | 1.1277 | -0.15405 | 0.026304 | 3.3211e-05 | 1.1587 | -0.19761 | 0.038895 | 5.6145e-05 | 1.1871 | -0.23924 | 0.052099 | 0.88511 | 0.12799 | -0.013204 | 0.86019 | 0.15916 | -0.019543 | 0.83808 | 0.18783 | -0.026202 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | ; | Split AC, SEER 10, High EER Slope, Med Degrad. Coef | SA-10-HM | Split-R | AC | High | Med
11009 | 10 | 9.31 | 41713 | 0.7411 | 0.31029 | 0.03296 | 0.365 | 0.18 | 0 | 55 | 2.4319 | -0.056537 | 0.0006515 | 0.0039245 | -2.1667e-06 | -0.00014481 | -1.8122 | 0.15026 | -0.0015367 | -0.017657 | -2.6667e-06 | 0.00021126 | -0.5725 | 0.040069 | -0.00034967 | -0.00039087 | 8.1083e-05 | -3.7257e-05 | 40.3001 | -1.1145 | 0.00788 | 1e-12 | 1e-12 | 1e-12 | 7.2478e-05 | 1.2027 | -0.26271 | 0.059969 | 0.00011782 | 1.236 | -0.31431 | 0.078168 | 0.00017345 | 1.2665 | -0.3629 | 0.096274 | 0.82622 | 0.20361 | -0.030176 | 0.80141 | 0.23745 | -0.039377 | 0.77942 | 0.26843 | -0.048548 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | ; | Split AC, SEER 10, High EER Slope, High Degrad. Coef | SA-10-HH | Split-R | AC | High | High
11301 | 13 | 11.36 | 43994.894 | 0.7022 | 0.2562 | 0.02728 | 0.365 | 0.1226 | 0 | 55 | 1.1675 | -0.024899 | 0.00035684 | 0.0054285 | -2.4052e-05 | -6.2812e-05 | 0.33332 | 0.066177 | -0.00080937 | -0.002306 | -4.6667e-06 | 2e-05 | -0.10321 | 0.026928 | -0.00018477 | -0.0007664 | 0.00013867 | -0.000165 | 42.5735 | -1.2354 | 0.0091779 | 1e-12 | 1e-12 | 1e-12 | 3.5993e-06 | 1.0789 | -0.08972 | 0.010809 | 9.756e-06 | 1.108 | -0.12741 | 0.019366 | 1.977e-05 | 1.1349 | -0.1639 | 0.029026 | 0.92642 | 0.078973 | -0.0054175 | 0.90146 | 0.10819 | -0.0097151 | 0.87929 | 0.13516 | -0.014573 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | ; | Split AC, SEER 13, Low EER Slope, Low Degrad. Coef | SA-13-LL | Split-R | AC | Low | Low
11302 | 13 | 12.04 | 49930 | 0.7416 | 0.23394 | 0.03104 | 0.365 | 0.1211 | 0 | 55 | 1.058 | -0.022649 | 0.000341 | 0.0058047 | -3.5e-05 | -4.82e-05 | 2.2518 | -0.0066825 | -0.0002025 | 0.0041301 | -3.375e-05 | 2.7e-06 | 0.97322 | -0.0023395 | 0.0001155 | -0.001479 | 0.00018517 | -0.0002931 | 11.2136 | -0.15244 | 0 | 1e-12 | 1e-12 | 1e-12 | 4.1054e-05 | 1.1696 | -0.21342 | 0.043788 | 7.1648e-05 | 1.2019 | -0.2616 | 0.059591 | 0.0001108 | 1.2315 | -0.30724 | 0.075607 | 0.85162 | 0.17017 | -0.02201 | 0.82677 | 0.20287 | -0.029985 | 0.80472 | 0.23287 | -0.038082 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | ; | Split AC, SEER 13, Low EER Slope, Med Degrad. Coef | SA-13-LM | Split-R | AC | Low | Med
11303 | 13 | 12.5 | 26120 | 0.7703 | 0.2184 | 0.03445 | 0.365 | 0.1437 | 0 | 55 | 2.0708 | -0.064319 | 0.000671 | 0.012967 | -5.4417e-05 | -8.08e-05 | 1.1698 | 0.013783 | -0.0003475 | 0.011487 | -6.2083e-05 | -1.01e-05 | -0.75939 | 0.051959 | -0.000331 | -0.0021968 | 0.00016525 | -0.0002386 | 9.8983 | -0.13281 | 0 | 1e-12 | 1e-12 | 1e-12 | 8.6274e-05 | 1.2141 | -0.28011 | 0.065975 | 0.00013749 | 1.2477 | -0.33284 | 0.08497 | 0.00019956 | 1.2784 | -0.3824 | 0.10377 | 0.81767 | 0.21514 | -0.033211 | 0.79289 | 0.24935 | -0.042821 | 0.77091 | 0.28066 | -0.05235 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | ; | Split AC, SEER 13, Low EER Slope, High Degrad. Coef | SA-13-LH | Split-R | AC | Low | High
11304 | 13 | 11.09 | 44700 | 0.75 | 0.25674 | 0.03132 | 0.364 | 0.1148 | 0 | 55 | 1.1914 | -0.01965 | 0.00031563 | 0.0030587 | -9.3333e-06 | -7.825e-05 | 2.9212 | -0.0010016 | -0.00032734 | -0.0068234 | 1.6417e-05 | 1.8125e-05 | -0.068189 | 0.022284 | -0.00011719 | 0.0010593 | 0.00014817 | -0.00021 | 8.2569 | -0.19403 | 0.0012794 | 1e-12 | 1e-12 | 1e-12 | 1.5738e-06 | 1.0607 | -0.067322 | 0.006596 | 5.2912e-06 | 1.0891 | -0.10267 | 0.013563 | 1.2001e-05 | 1.1153 | -0.13713 | 0.021822 | 0.94256 | 0.060678 | -0.0032424 | 0.91762 | 0.088968 | -0.0066159 | 0.89551 | 0.11501 | -0.01057 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | ; | Split AC, SEER 13, Med EER Slope, Low Degrad. Coef | SA-13-ML | Split-R | AC | Med | Low
11305 | 13 | 11.3 | 43544.043 | 0.729 | 0.25 | 0.03215 | 0.365 | 0.1888 | 0 | 55 | 3.5009 | -0.090336 | 0.00087051 | 0.0029382 | 3.6458e-07 | -0.00010031 | 0.48245 | 0.069346 | -0.00084785 | -0.0073919 | 1.451e-05 | 3.9062e-05 | -2.9365 | 0.10373 | -0.00079922 | 0.0030636 | 0.00010629 | -0.00010625 | 27.4956 | -0.76471 | 0.0055112 | 1e-12 | 1e-12 | 1e-12 | 1.28e-05 | 1.1177 | -0.14031 | 0.022646 | 2.6734e-05 | 1.1482 | -0.18271 | 0.03443 | 4.6493e-05 | 1.1763 | -0.22331 | 0.046927 | 0.89342 | 0.11786 | -0.011364 | 0.86849 | 0.14864 | -0.017294 | 0.84637 | 0.17698 | -0.023593 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | ; | Split AC, SEER 13, Med EER Slope, Med Degrad. Coef | SA-13-MM | Split-R | AC | Med | Med
11306 | 13 | 11.72 | 30545.745 | 0.7381 | 0.2386 | 0.03274 | 0.365 | 0.1815 | 0 | 55 | 3.0075 | -0.070888 | 0.00070215 | -0.00081068 | 6.0937e-06 | -6.0937e-05 | -2.6484 | 0.16813 | -0.0016205 | -0.010065 | 1.8948e-05 | 6.9687e-05 | -3.0666 | 0.087898 | -0.00057734 | 0.019142 | 8.1646e-05 | -0.00028062 | 40.1366 | -1.1412 | 0.0083139 | 1e-12 | 1e-12 | 1e-12 | 6.0394e-05 | 1.1914 | -0.24571 | 0.054241 | 0.00010034 | 1.2244 | -0.29617 | 0.071638 | 0.00014998 | 1.2546 | -0.34377 | 0.089044 | 0.83477 | 0.19221 | -0.027284 | 0.80995 | 0.22567 | -0.036074 | 0.78794 | 0.25632 | -0.044885 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | ; | Split AC, SEER 13, Med EER Slope, High Degrad. Coef | SA-13-MH | Split-R | AC | Med | High
11307 | 13 | 10.74 | 43400 | 0.77 | 0.2752 | 0.03283 | 0.288 | 0.1087 | 0 | 55 | 1.3186 | -0.025167 | 0.00037734 | 0.0061013 | -1.725e-05 | -0.00011788 | 3.0045 | 0.0047656 | -0.00047969 | -0.012061 | -9e-06 | 0.000166 | 0.35078 | 0.025947 | -0.00016406 | -0.012954 | 0.00021875 | -0.00017225 | 38.9421 | -1.1017 | 0.0079909 | 1e-12 | 1e-12 | 1e-12 | 7.1792e-07 | 1.0473 | -0.051396 | 0.0040952 | 3.0792e-06 | 1.0751 | -0.084968 | 0.0098542 | 7.8289e-06 | 1.1008 | -0.11786 | 0.017048 | 0.95473 | 0.047315 | -0.0020505 | 0.92975 | 0.075168 | -0.0049383 | 0.90755 | 0.10094 | -0.0085501 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | ; | Split AC, SEER 13, High EER Slope, Low Degrad. Coef | SA-13-HL | Split-R | AC | High | Low
11308 | 13 | 10.98 | 62102 | 0.7693 | 0.2634 | 0.0322 | 0.329 | 0.0813 | 0 | 100 | 2.389 | -0.060045 | 0.000656 | 0.0091894 | -2.7101e-05 | -0.00014756 | -1.546 | 0.13361 | -0.0013876 | -0.013416 | -1.8685e-05 | 0.00019886 | -1.242 | 0.07635 | -0.00060556 | -0.015157 | 0.00019547 | -7.5314e-05 | 88.6979 | -2.3876 | 0.0161 | 1e-12 | 1e-12 | 1e-12 | 5.1756e-06 | 1.0885 | -0.10188 | 0.013388 | 1.2916e-05 | 1.118 | -0.14077 | 0.022763 | 2.4988e-05 | 1.1451 | -0.17831 | 0.033143 | 0.91809 | 0.08858 | -0.0067121 | 0.89314 | 0.1182 | -0.011423 | 0.87099 | 0.14551 | -0.016646 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | ; | Split AC, SEER 13, High EER Slope, Med Degrad. Coef | SA-13-HM | Split-R | AC | High | Med
11309 | 13 | 11.35 | 41570 | 0.7643 | 0.2515 | 0.03368 | 0.329 | 0.1329 | 0 | 100 | 1.8327 | -0.044845 | 0.00050533 | 0.0093478 | -4.3107e-05 | -9.3559e-05 | -4.1057 | 0.213 | -0.002043 | -0.013024 | -3.1304e-05 | 0.00023969 | -1.2152 | 0.079179 | -0.00057567 | -0.017619 | 0.00023964 | -0.00015625 | 87.8714 | -2.5509 | 0.018721 | 1e-12 | 1e-12 | 1e-12 | 3.3211e-05 | 1.1587 | -0.19761 | 0.038895 | 5.967e-05 | 1.1907 | -0.24463 | 0.053881 | 9.4115e-05 | 1.22 | -0.28925 | 0.069183 | 0.86019 | 0.15916 | -0.019543 | 0.83532 | 0.19148 | -0.027102 | 0.81326 | 0.22114 | -0.034833 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | ; | Split AC, SEER 13, High EER Slope, High Degrad. Coef | SA-13-HH | Split-R | AC | High | High
11401 | 14 | 11.99 | 36500 | 0.78 | 0.22932 | 0.03288 | 0.383 | 0.0866 | 0 | 100 | 1.631 | -0.03418 | 0.00042734 | 0.003849 | -1.15e-05 | -8.1875e-05 | 1.0575 | 0.055406 | -0.00080938 | -0.0077255 | -7.5e-06 | 0.0001045 | -0.67296 | 0.044013 | -0.000275 | 0.00034433 | 0.00016317 | -0.000243 | 31.2787 | -0.83452 | 0.0057104 | 1e-12 | 1e-12 | 1e-12 | 5.1756e-06 | 1.0885 | -0.10188 | 0.013388 | 1.2916e-05 | 1.118 | -0.14077 | 0.022763 | 2.4988e-05 | 1.1451 | -0.17831 | 0.033143 | 0.91809 | 0.08858 | -0.0067121 | 0.89314 | 0.1182 | -0.011423 | 0.87099 | 0.14551 | -0.016646 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | ; | Split AC, SEER 14, Med EER Slope, Low Degrad. Coef | SA-14-ML | Split-R | AC | Med | Low
11402 | 14 | 13.08 | 37680 | 0.7478 | 0.22503 | 0.03185 | 0.263 | 0.1282 | 0 | 100 | 0.70697 | -0.007713 | 0.000132 | 0.0030629 | -6.4167e-05 | 7.94e-05 | 1.0885 | 0.027737 | -0.000533 | 0.0039964 | -6.8e-05 | 0.0001068 | 0.79053 | -0.0097785 | 0.0002915 | 0.0078246 | 0.00020042 | -0.0004707 | 10.2541 | -0.13812 | 0 | 1e-12 | 1e-12 | 1e-12 | 4.9876e-05 | 1.1803 | -0.22911 | 0.048793 | 8.486e-05 | 1.2129 | -0.27841 | 0.065382 | 0.00012897 | 1.2428 | -0.32502 | 0.082084 | 0.84333 | 0.18094 | -0.024534 | 0.81849 | 0.21402 | -0.032911 | 0.79646 | 0.24434 | -0.04136 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | ; | Split AC, SEER 14, Med EER Slope, Med Degrad. Coef | SA-14-MM | Split-R | AC | Med | Med
11403 | 14 | 13.22 | 41520 | 0.711 | 0.22709 | 0.0301 | 0.24 | 0.1744 | 0 | 100 | 0.80636 | -0.018401 | 0.000349 | 0.0074827 | -2.8e-05 | -9.4e-05 | 1.8938 | -0.0014855 | -0.0001855 | 0.0064776 | -2.8167e-05 | -5.07e-05 | 1.1105 | -0.006073 | 0.000117 | -0.00062367 | 0.00017233 | -0.000271 | 7.8818 | -0.10271 | 0 | 1e-12 | 1e-12 | 1e-12 | 7.2478e-05 | 1.2027 | -0.26271 | 0.059969 | 0.00011782 | 1.236 | -0.31431 | 0.078168 | 0.00017345 | 1.2665 | -0.3629 | 0.096274 | 0.82622 | 0.20361 | -0.030176 | 0.80141 | 0.23745 | -0.039377 | 0.77942 | 0.26843 | -0.048548 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | ; | Split AC, SEER 14, Med EER Slope, High Degrad. Coef | SA-14-MH | Split-R | AC | Med | High
11404 | 14 | 11.7 | 31167.925 | 0.7722 | 0.25992 | 0.03208 | 0.225 | 0.0826 | 0 | 100 | 2.9298 | -0.073729 | 0.0007663 | 0.0041592 | -1.8617e-06 | -0.00012698 | -4.2897 | 0.21439 | -0.0020881 | -0.0057032 | -4.9151e-05 | 0.00020182 | -1.7975 | 0.087146 | -0.00078912 | -0.0078009 | 0.00012471 | 1.8319e-05 | 139.2851 | -4.0513 | 0.029663 | 1e-12 | 1e-12 | 1e-12 | 1.5758e-06 | 1.0607 | -0.067351 | 0.006601 | 5.2959e-06 | 1.0891 | -0.10271 | 0.01357 | 1.2009e-05 | 1.1153 | -0.13716 | 0.021831 | 0.94251 | 0.06078 | -0.0033065 | 0.91754 | 0.089226 | -0.0068034 | 0.89536 | 0.11552 | -0.010954 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | ; | Split AC, SEER 14, High EER Slope, Low Degrad. Coef | SA-14-HL | Split-R | AC | High | Low
11405 | 14 | 11.84 | 29100 | 0.79 | 0.23689 | 0.03436 | 0.345 | 0.104 | 0 | 100 | 1.8979 | -0.041081 | 0.00050938 | 0.0029553 | 2.8333e-06 | -0.000116 | 0.52066 | 0.072658 | -0.00094453 | -0.0094176 | -5.4167e-06 | 0.00012487 | -0.7592 | 0.037092 | -0.00026797 | 0.0073089 | 0.00011458 | -0.00019663 | 63.2009 | -1.8127 | 0.013199 | 1e-12 | 1e-12 | 1e-12 | 3.5993e-06 | 1.0789 | -0.08972 | 0.010809 | 9.756e-06 | 1.108 | -0.12741 | 0.019366 | 1.977e-05 | 1.1349 | -0.1639 | 0.029026 | 0.92642 | 0.078973 | -0.0054175 | 0.90146 | 0.10819 | -0.0097151 | 0.87929 | 0.13516 | -0.014573 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | ; | Split AC, SEER 14, High EER Slope, Med Degrad. Coef | SA-14-HM | Split-R | AC | High | Med
11406 | 14 | 12.17 | 25300 | 0.75 | 0.24507 | 0.03162 | 0.306 | 0.1232 | 0 | 100 | 1.3696 | -0.02588 | 0.00040234 | 0.0026539 | 3.25e-06 | -0.00011363 | 1.7984 | 0.022356 | -0.00047188 | -0.0010312 | -3.5833e-06 | -7.5e-06 | -1.1928 | 0.048469 | -0.00035313 | 0.009335 | 0.00010933 | -0.000211 | 8.1581 | -0.18753 | 0.0012043 | 1e-12 | 1e-12 | 1e-12 | 1.663e-05 | 1.1277 | -0.15405 | 0.026304 | 3.3211e-05 | 1.1587 | -0.19761 | 0.038895 | 5.6145e-05 | 1.1871 | -0.23924 | 0.052099 | 0.88511 | 0.12799 | -0.013204 | 0.86019 | 0.15916 | -0.019543 | 0.83808 | 0.18783 | -0.026202 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | ; | Split AC, SEER 14, High EER Slope, High Degrad. Coef | SA-14-HH | Split-R | AC | High | High
11501 | 15 | 12.72 | 45047.791 | 0.7025 | 0.2389 | 0.02664 | 0.256 | 0.1007 | 0 | 55 | 1.612 | -0.034129 | 0.00044551 | 0.0027867 | -2.1146e-06 | -8.9687e-05 | 0.42252 | 0.073602 | -0.00089453 | -0.0084029 | 1.6146e-05 | 4.9375e-05 | -0.68032 | 0.034102 | -0.0002502 | 0.0055919 | 0.00010461 | -0.00015031 | 56.6744 | -1.6656 | 0.012457 | 1e-12 | 1e-12 | 1e-12 | 2.4385e-06 | 1.0698 | -0.078346 | 0.0085766 | 7.2789e-06 | 1.0985 | -0.11487 | 0.016341 | 1.5536e-05 | 1.125 | -0.15035 | 0.025302 | 0.93446 | 0.069814 | -0.0042974 | 0.9095 | 0.098648 | -0.0081949 | 0.88732 | 0.12528 | -0.0127 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | ; | Split AC, SEER 15, Med EER Slope, Low Degrad. Coef | SA-15-ML | Split-R | AC | Med | Low
11502 | 15 | 12.99 | 36100 | 0.78 | 0.2297 | 0.03324 | 0.233 | 0.0966 | 0 | 100 | 1.7038 | -0.037103 | 0.00045469 | 0.0041866 | -1.1583e-05 | -8.675e-05 | 2.7021 | -0.0057594 | -0.00031094 | -0.00016333 | -2.825e-05 | 5.5e-05 | -0.85172 | 0.049228 | -0.00030469 | 0.0008295 | 0.00016767 | -0.0002625 | 30.6324 | -0.83497 | 0.0058611 | 1e-12 | 1e-12 | 1e-12 | 5.1756e-06 | 1.0885 | -0.10188 | 0.013388 | 1.2916e-05 | 1.118 | -0.14077 | 0.022763 | 2.4988e-05 | 1.1451 | -0.17831 | 0.033143 | 0.91809 | 0.08858 | -0.0067121 | 0.89314 | 0.1182 | -0.011423 | 0.87099 | 0.14551 | -0.016646 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | ; | Split AC, SEER 15, Med EER Slope, Med Degrad. Coef | SA-15-MM | Split-R | AC | Med | Med
11503 | 15 | 13.11 | 29600 | 0.79 | 0.23488 | 0.03378 | 0.19 | 0.0886 | 0 | 100 | 1.5132 | -0.028142 | 0.00042109 | 0.0019705 | 1.1167e-05 | -0.00012663 | 2.1808 | 0.020644 | -0.0005625 | -0.0073817 | -1.9e-05 | 0.000131 | -0.46971 | 0.021738 | -0.00014063 | 0.011561 | 9.7833e-05 | -0.00021 | 19.0247 | -0.45342 | 0.0027522 | 1e-12 | 1e-12 | 1e-12 | 4.1054e-05 | 1.1696 | -0.21342 | 0.043788 | 7.1648e-05 | 1.2019 | -0.2616 | 0.059591 | 0.0001108 | 1.2315 | -0.30724 | 0.075607 | 0.85162 | 0.17017 | -0.02201 | 0.82677 | 0.20287 | -0.029985 | 0.80472 | 0.23287 | -0.038082 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | ; | Split AC, SEER 15, Med EER Slope, High Degrad. Coef | SA-15-MH | Split-R | AC | Med | High
11504 | 15 | 12.39 | 51934.1453 | 0.7766 | 0.2328 | 0.03081 | 0.318 | 0.0336 | 0 | 55 | 3.7471 | -0.099512 | 0.00095195 | 0.005716 | -9.8125e-06 | -0.00012687 | -6.1903 | 0.27495 | -0.0025369 | -0.0085626 | -3.4656e-05 | 0.00020156 | -3.6661 | 0.12222 | -0.00089687 | 0.0045344 | 0.00013588 | -0.00018125 | 368.4902 | -10.7817 | 0.079056 | 1e-12 | 1e-12 | 1e-12 | 3.5993e-06 | 1.0789 | -0.08972 | 0.010809 | 9.756e-06 | 1.108 | -0.12741 | 0.019366 | 1.977e-05 | 1.1349 | -0.1639 | 0.029026 | 0.92642 | 0.078973 | -0.0054175 | 0.90146 | 0.10819 | -0.0097151 | 0.87929 | 0.13516 | -0.014573 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | ; | Split AC, SEER 15, High EER Slope, Low Degrad. Coef | SA-15-HL | Split-R | AC | High | Low
11505 | 15 | 13.01 | 30874 | 0.7636 | 0.2267 | 0.03239 | 0.256 | 0.1001 | 0 | 100 | 1.8768 | -0.038132 | 0.00048922 | 0.0067273 | -8.8869e-06 | -0.0001692 | -2.6365 | 0.17652 | -0.0017579 | -0.016188 | -7.0536e-06 | 0.00020456 | -0.55408 | 0.059005 | -0.00051111 | -0.018903 | 0.00019695 | -1.3608e-05 | 109.5573 | -3.1838 | 0.023336 | 1e-12 | 1e-12 | 1e-12 | 2.6734e-05 | 1.1482 | -0.18271 | 0.03443 | 4.9561e-05 | 1.1799 | -0.22858 | 0.048622 | 7.9822e-05 | 1.2089 | -0.27221 | 0.063229 | 0.86849 | 0.14864 | -0.017294 | 0.84361 | 0.18058 | -0.024448 | 0.82153 | 0.20992 | -0.031823 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | ; | Split AC, SEER 15, High EER Slope, Med Degrad. Coef | SA-15-HM | Split-R | AC | High | Med
11506 | 15 | 12.85 | 23967 | 0.7819 | 0.2288 | 0.03338 | 0.255 | 0.0847 | 0 | 100 | 2.9829 | -0.076834 | 0.00078589 | 0.007719 | -2.2036e-05 | -0.00014098 | -2.137 | 0.15234 | -0.0015286 | -0.014449 | -1.5113e-05 | 0.00020436 | -2.2648 | 0.10387 | -0.00080911 | -0.014056 | 0.00021446 | -0.00010408 | 96.5246 | -2.6377 | 0.018089 | 1e-12 | 1e-12 | 1e-12 | 6.0394e-05 | 1.1914 | -0.24571 | 0.054241 | 0.00010034 | 1.2244 | -0.29617 | 0.071638 | 0.00014998 | 1.2546 | -0.34377 | 0.089044 | 0.83477 | 0.19221 | -0.027284 | 0.80995 | 0.22567 | -0.036074 | 0.78794 | 0.25632 | -0.044885 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | ; | Split AC, SEER 15, High EER Slope, High Degrad. Coef | SA-15-HH | Split-R | AC | High | High
11601 | 16 | 11.74 | 36720.291 | 0.7718 | 0.2539 | 0.03268 | 0.256 | 0.0668 | 0 | 125 | 4.3024 | -0.1134 | 0.0011145 | 0.0068311 | -7.1339e-06 | -0.00020296 | -10.4442 | 0.40321 | -0.0034015 | -0.021172 | -1.7812e-05 | 0.00029384 | -3.5949 | 0.13604 | -0.0010457 | -0.0062155 | 0.00015847 | -0.00010457 | 298.3001 | -9.3837 | 0.07507 | 0.58504 | 0.00069794 | -0.010599 | -4.4039e-15 | 0.62971 | 0.37029 | 1e-12 | -4.4039e-15 | 0.62971 | 0.37029 | 1e-12 | -4.4039e-15 | 0.62971 | 0.37029 | 1e-12 | 0.91043 | 0.096408 | -0.006841 | 0.88565 | 0.12581 | -0.011459 | 0.86305 | 0.15568 | -0.018734 | 2 | 0.66667 | 0.59572 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3715 | -0.37154 | 1 | 1.1238 | ; | Split AC, SEER 16, Mfg1 EER Slope, Low Degrad. Coef | SA-16-ML | Split-TS | AC | Mfg1 | Low
11602 | 16 | 11.77 | 36192.361 | 0.7459 | 0.266 | 0.03039 | 0.179 | 0.0631 | 0 | 125 | 4.56 | -0.12341 | 0.0012315 | 0.0080205 | 2.75e-06 | -0.00025244 | -10.0327 | 0.3919 | -0.0033223 | -0.02172 | -1.8146e-05 | 0.00030109 | -3.6704 | 0.13952 | -0.0010888 | -0.0064763 | 0.00015252 | -8.6557e-05 | 359.7883 | -11.3928 | 0.091692 | 0.69723 | 0.00079233 | -0.012642 | 2.5287e-13 | 0.66429 | 0.33571 | 1e-12 | 2.5287e-13 | 0.66429 | 0.33571 | 1e-12 | 2.5287e-13 | 0.66429 | 0.33571 | 1e-12 | 0.92736 | 0.075027 | -0.0023896 | 0.90178 | 0.1065 | -0.0082807 | 0.87891 | 0.13743 | -0.016338 | 2 | 0.72727 | 0.59787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8151 | -2.8151 | 1 | 1.7678 | ; | Split AC, SEER 16, Mfg1 EER Slope, Med Degrad. Coef | SA-16-MM | Split-TS | AC | Mfg1 | Med
11603 | 16 | 12.2 | 36955.7197 | 0.7465 | 0.24659 | 0.02977 | 0.255 | 0.0419 | 0 | 125 | 2.2343 | -0.054915 | 0.00071917 | 0.0056006 | 6.3304e-06 | -0.00021564 | -8.3213 | 0.34618 | -0.0029906 | -0.025399 | -3.1131e-06 | 0.00031304 | -1.8572 | 0.072403 | -0.00056218 | 0.0069044 | 9.233e-05 | -0.00015072 | 284.3684 | -10.0755 | 0.087897 | 1.3302 | 0.00060085 | -0.021159 | -2.3291e-13 | 0.77905 | 0.22095 | 1e-12 | -2.3291e-13 | 0.77905 | 0.22095 | 1e-12 | -2.3291e-13 | 0.77905 | 0.22095 | 1e-12 | 0.93532 | 0.066385 | -0.0017047 | 0.91027 | 0.094506 | -0.0047797 | 0.88785 | 0.12275 | -0.010596 | 2 | 0.6 | 0.55873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0088161 | 0.99118 | 0.60353 | 1 | ; | Split AC, SEER 16, Mfg1 EER Slope, High Degrad. Coef | SA-16-MH | Split-TS | AC | Mfg1 | High
11604 | 16 | 11.61 | 37000 | 0.81 | 0.2527 | 0.03405 | 0.274 | 0.0515 | 0.02 | 55 | 0.087384 | 0.010108 | 0.00012969 | 0.0076712 | -1.9381e-05 | -0.0001415 | 1.2628 | 0.046857 | -0.00075844 | -0.0080865 | -3.569e-05 | 0.00017169 | 0.28876 | -0.0017163 | 3.75e-05 | 0.0074902 | 0.00010883 | -0.00016275 | 18.3808 | -0.47973 | 0.0038702 | 0.15627 | 0.00045113 | -0.0033826 | -1.6676e-13 | 0.69439 | 0.30561 | 1e-12 | -1.6676e-13 | 0.69439 | 0.30561 | 1e-12 | -1.6676e-13 | 0.69439 | 0.30561 | 1e-12 | 0.89659 | 0.11422 | -0.010806 | 0.86193 | 0.1565 | -0.018432 | 0.83114 | 0.19674 | -0.027879 | 2 | 0.71429 | 0.71892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5812 | 0.4188 | 0.88034 | 1 | ; | Split AC, SEER 16, Mfg2 EER Slope, Low Degrad. Coef | SA-16-ML | Split-TS | AC | Mfg2 | Low
11605 | 16 | 12.17 | 50500 | 0.78 | 0.24415 | 0.03228 | 0.258 | 0.0696 | 0.02 | 55 | 0.00089933 | 0.017192 | 3.4375e-05 | 0.0032858 | -1.7345e-05 | -7.2688e-05 | 2.2101 | 0.007115 | -0.00035875 | -0.00056695 | -2.0131e-05 | 2.5e-05 | 1.0949 | -0.024369 | 0.00019813 | 0.0088446 | 0.00010085 | -0.00017312 | -48.1585 | 1.6817 | -0.014042 | -0.0094751 | 4.7459e-05 | -1.6377e-06 | 1.0591e-12 | 0.83613 | 0.16387 | 1e-12 | 1.0591e-12 | 0.83613 | 0.16387 | 1e-12 | 1.0591e-12 | 0.83613 | 0.16387 | 1e-12 | 0.90388 | 0.10513 | -0.0090171 | 0.86818 | 0.14945 | -0.017631 | 0.83684 | 0.18938 | -0.026212 | 2 | 0.69939 | 0.70891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.39451 | 0.60549 | 0.81798 | 1 | ; | Split AC, SEER 16, Mfg2 EER Slope, Med Degrad. Coef | SA-16-MM | Split-TS | AC | Mfg2 | Med
11606 | 16 | 12.2 | 37600 | 0.76 | 0.2287 | 0.03191 | 0.367 | 0.1071 | 0.02 | 55 | 0.42105 | 0.00064469 | 0.0002025 | 0.0066453 | -1.6583e-05 | -0.00013431 | 3.5155 | -0.030896 | -6.4688e-05 | 0.00087226 | -1.6845e-05 | -1.35e-05 | 0.0097852 | 0.0014234 | 1.875e-05 | 0.0113 | 9.681e-05 | -0.00017856 | -24.4173 | 1.1537 | -0.010112 | -0.21817 | 0.00076837 | 0.0011471 | 1.8585e-12 | 0.69973 | 0.30027 | 1e-12 | 1.8585e-12 | 0.69973 | 0.30027 | 1e-12 | 1.8585e-12 | 0.69973 | 0.30027 | 1e-12 | 0.7904 | 0.25223 | -0.042629 | 0.75798 | 0.29831 | -0.056295 | 0.72983 | 0.33865 | -0.068479 | 2 | 0.75 | 0.7409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10429 | 0.89571 | 0.77607 | 1 | ; | Split AC, SEER 16, Mfg2 EER Slope, High Degrad. Coef | SA-16-MH | Split-TS | AC | Mfg2 | High
11607 | 16 | 12.42 | 36910 | 0.7047 | 0.2433 | 0.02844 | 0.255 | 0.1442 | 0 | 55 | 0.90944 | -0.01415 | 0.0003153 | 0.0058039 | -1.6057e-05 | -0.00012305 | 4.9807 | -0.084755 | 0.00035784 | 0.0086154 | -3.5136e-05 | -6.4395e-05 | 0.80076 | -1.1735e-05 | 3.1919e-05 | -0.0043234 | 0.00013103 | -0.00011235 | -6.2786 | 0.27567 | -0.0017994 | -0.049854 | 0.00024497 | -9.2417e-05 | 7.2749e-13 | 0.85344 | 0.14656 | 1e-12 | 7.2749e-13 | 0.85344 | 0.14656 | 1e-12 | 0.015822 | 0.81835 | 0.16583 | 9.9996e-13 | 0.93801 | 0.067068 | -0.0050751 | 0.91316 | 0.094727 | -0.0078824 | 0.89198 | 0.1191 | -0.011079 | 2 | 0.69048 | 0.69431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72213 | 0.27787 | 0.91399 | 1 | ; | Split AC, SEER 16, Mfg3 EER Slope, Med Degrad. Coef | SA-16-MM | Split-TS | AC | Mfg3 | Med
11608 | 16 | 11.1 | 47293.871 | 0.7399 | 0.2635 | 0.03383 | 0.292 | 0.2037 | 0 | 55 | 2.542 | -0.063185 | 0.00071146 | 0.0064081 | 7.9167e-07 | -0.00017568 | -0.64125 | 0.1223 | -0.0013773 | -0.01915 | 6.8333e-06 | 0.00021804 | -3.2918 | 0.088132 | -0.00061862 | 0.021751 | 3.6875e-05 | -0.00019406 | 35.6871 | -1.1735 | 0.0097198 | 0.098444 | -1.5174e-05 | -0.0013998 | 2.0139e-13 | 0.69972 | 0.30028 | 1e-12 | 2.0139e-13 | 0.69972 | 0.30028 | 1e-12 | 2.0139e-13 | 0.69972 | 0.30028 | 1e-12 | 0.84405 | 0.17913 | -0.023184 | 0.79499 | 0.24445 | -0.039443 | 0.75189 | 0.30507 | -0.056959 | 2 | 0.5 | 0.54243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.42401 | 0.57599 | 0.71201 | 1 | ; | Split AC, SEER 16, Mfg4 EER Slope, Low Degrad. Coef | SA-16-ML | Split-TS | AC | Mfg4 | Low
11609 | 16 | 11.33 | 35847.791 | 0.7657 | 0.2632 | 0.03347 | 0.256 | 0.1356 | 0 | 55 | 1.219 | -0.02746 | 0.00044688 | 0.0085434 | -1.3208e-05 | -0.0001693 | -4.8328 | 0.24281 | -0.0022753 | -0.017325 | -8.8333e-06 | 0.00023623 | -3.3524 | 0.067565 | -0.00024935 | 0.040581 | 7.1375e-05 | -0.00055846 | 77.6441 | -2.4391 | 0.019285 | 0.1302 | 1.7693e-05 | -0.0019366 | -8.397e-14 | 0.73188 | 0.26812 | 1e-12 | -8.397e-14 | 0.73188 | 0.26812 | 1e-12 | -8.397e-14 | 0.73188 | 0.26812 | 1e-12 | 0.72698 | 0.34124 | -0.06822 | 0.67979 | 0.41251 | -0.092295 | 0.63873 | 0.47699 | -0.11572 | 2 | 0.5 | 0.5241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.53199 | 0.46801 | 0.766 | 1 | ; | Split AC, SEER 16, Mfg4 EER Slope, High Degrad. Coef | SA-16-MH | Split-TS | AC | Mfg4 | High
11701 | 17 | 12.4 | 35751.184 | 0.7363 | 0.24257 | 0.02937 | 0.255 | 0.0563 | 0 | 125 | 1.5952 | -0.040384 | 0.00061569 | 0.0097628 | -1.0327e-05 | -0.00023371 | -6.7607 | 0.29982 | -0.0026588 | -0.02409 | -1.1336e-05 | 0.00031407 | -1.089 | 0.061377 | -0.00048639 | -0.0040278 | 0.00015853 | -0.0001395 | 146.8375 | -5.6083 | 0.051724 | 0.98415 | 0.00043145 | -0.015658 | 2.7941e-13 | 0.64825 | 0.35175 | 1e-12 | 2.7941e-13 | 0.64825 | 0.35175 | 1e-12 | 2.7941e-13 | 0.64825 | 0.35175 | 1e-12 | 0.94237 | 0.061722 | -0.0040925 | 0.91707 | 0.091339 | -0.0084093 | 0.89633 | 0.11113 | -0.0074525 | 2 | 0.66667 | 0.57015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3743 | -3.3743 | 1 | 2.1248 | ; | Split AC, SEER 17, Mfg1 EER Slope, Low Degrad. Coef | SA-17-ML | Split-TS | AC | Mfg1 | Low
11702 | 17 | 12.47 | 36479.053 | 0.7479 | 0.2402 | 0.03015 | 0.255 | 0.0505 | 0 | 125 | 1.6049 | -0.040565 | 0.00061792 | 0.0097424 | -1.0071e-05 | -0.00023495 | -7.0688 | 0.30897 | -0.002727 | -0.024 | -1.1137e-05 | 0.00031262 | -1.1231 | 0.062375 | -0.00049264 | -0.0040155 | 0.0001595 | -0.0001418 | 154.1008 | -5.8917 | 0.054281 | 1.055 | 0.00046784 | -0.016727 | 1.2118e-13 | 0.72671 | 0.27329 | 1e-12 | 1.2118e-13 | 0.72671 | 0.27329 | 1e-12 | 1.2118e-13 | 0.72671 | 0.27329 | 1e-12 | 0.94359 | 0.055314 | 0.0010938 | 0.91673 | 0.092644 | -0.0093755 | 0.89623 | 0.11121 | -0.0074415 | 2 | 0.6 | 0.54773 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0077 | -1.0077 | 1 | 1.4031 | ; | Split AC, SEER 17, Mfg1 EER Slope, Med Degrad. Coef | SA-17-MM | Split-TS | AC | Mfg1 | Med
11703 | 17 | 12.68 | 36117.884 | 0.7362 | 0.23708 | 0.02907 | 0.255 | 0.0468 | 0 | 125 | 1.597 | -0.040434 | 0.00061602 | 0.0097577 | -1.0342e-05 | -0.00023361 | -6.7588 | 0.29978 | -0.0026588 | -0.024101 | -1.1369e-05 | 0.00031431 | -1.1078 | 0.061914 | -0.00049014 | -0.0040301 | 0.00015874 | -0.00013982 | 178.2791 | -6.819 | 0.062904 | 1.1968 | 0.00052572 | -0.019045 | 1.6713e-13 | 0.71443 | 0.28557 | 1e-12 | 1.6713e-13 | 0.71443 | 0.28557 | 1e-12 | 1.6713e-13 | 0.71443 | 0.28557 | 1e-12 | 0.9421 | 0.062187 | -0.0042901 | 0.9174 | 0.090238 | -0.0076349 | 0.89425 | 0.12073 | -0.014973 | 2 | 0.66667 | 0.56999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.1126 | -4.1126 | 1 | 2.3709 | ; | Split AC, SEER 17, Mfg1 EER Slope, High Degrad. Coef | SA-17-MH | Split-TS | AC | Mfg1 | High
11704 | 17 | 12.28 | 38000 | 0.8 | 0.247 | 0.03513 | 0.202 | 0.102 | 0.02 | 55 | -0.12264 | 0.020682 | 1.3437e-05 | 0.0050796 | -1.9786e-05 | -9.8563e-05 | 2.1856 | 0.018422 | -0.00053094 | -0.0067341 | -2.9429e-05 | 0.0001365 | 0.40112 | -0.0074856 | 9.0625e-05 | 0.0088081 | 0.00010324 | -0.00016888 | -23.8765 | 0.91424 | -0.0076553 | -0.048714 | 0.00036085 | -0.00010086 | 2.1003e-12 | 0.73734 | 0.26266 | 1e-12 | 2.1003e-12 | 0.73734 | 0.26266 | 1e-12 | 2.1003e-12 | 0.73734 | 0.26266 | 1e-12 | 0.93455 | 0.070059 | -0.004606 | 0.89757 | 0.11313 | -0.010704 | 0.8651 | 0.15227 | -0.017369 | 2 | 0.67416 | 0.71941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.1368 | 2.1368 | 0.30374 | 1 | ; | Split AC, SEER 17, Mfg2 EER Slope, Low Degrad. Coef | SA-17-ML | Split-TS | AC | Mfg2 | Low
11705 | 17 | 12.47 | 37600 | 0.78 | 0.25105 | 0.03205 | 0.162 | 0.0629 | 0.02 | 55 | 0.088908 | 0.0097316 | 0.00012375 | 0.0077242 | -2.3571e-05 | -0.00012844 | 3.2739 | -0.017853 | -0.00022937 | -0.0029327 | -2.7214e-05 | 7.4813e-05 | 0.32014 | -0.0037091 | 5.5937e-05 | 0.0083494 | 0.00010648 | -0.00016919 | -72.8525 | 1.9566 | -0.014006 | 0.27605 | -0.0005948 | -0.0023919 | 1.9909e-13 | 0.72705 | 0.27295 | 1e-12 | 1.9909e-13 | 0.72705 | 0.27295 | 1e-12 | 1.9909e-13 | 0.72705 | 0.27295 | 1e-12 | 0.92781 | 0.078393 | -0.006205 | 0.89224 | 0.11921 | -0.011451 | 0.86065 | 0.15855 | -0.019196 | 2 | 0.6971 | 0.71277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.10333 | 1.1033 | 0.6658 | 1 | ; | Split AC, SEER 17, Mfg2 EER Slope, Med Degrad. Coef | SA-17-MM | Split-TS | AC | Mfg2 | Med
11706 | 17 | 12.67 | 36800 | 0.77 | 0.22812 | 0.03261 | 0.292 | 0.1025 | 0.02 | 55 | -0.57221 | 0.03363 | -6.7188e-05 | 0.0045445 | -1.3571e-05 | -0.00010819 | 2.2017 | 0.018214 | -0.00050594 | -0.0064007 | -1.3298e-05 | 9.0688e-05 | 0.5967 | -0.020343 | 0.00021125 | 0.014207 | 9.5405e-05 | -0.00021881 | -22.6446 | 0.75871 | -0.0069681 | 0.023106 | -0.00036436 | 0.0008145 | 2.179e-12 | 0.62733 | 0.37267 | 1e-12 | 2.179e-12 | 0.62733 | 0.37267 | 1e-12 | 2.179e-12 | 0.62733 | 0.37267 | 1e-12 | 0.84077 | 0.18453 | -0.025303 | 0.80841 | 0.22616 | -0.034573 | 0.77963 | 0.26585 | -0.045485 | 2 | 0.75 | 0.75099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.36195 | 1.3619 | 0.65951 | 1 | ; | Split AC, SEER 17, Mfg2 EER Slope, High Degrad. Coef | SA-17-MH | Split-TS | AC | Mfg2 | High
11707 | 17 | 11.41 | 61342.341 | 0.687 | 0.2517 | 0.02934 | 0.365 | 0.2272 | 0 | 55 | 1.6606 | -0.03945 | 0.00052813 | 0.0079442 | -9.5e-06 | -0.00016609 | -1.2472 | 0.13735 | -0.0014991 | -0.016855 | -6.8333e-06 | 0.00022579 | -2.3019 | 0.058189 | -0.0003832 | 0.021697 | 4.2167e-05 | -0.00020713 | 21.4191 | -0.78653 | 0.0072294 | 0.1001 | 1.5787e-05 | -0.0015437 | -2.0043e-13 | 0.44118 | 0.55882 | 1e-12 | -2.0043e-13 | 0.44118 | 0.55882 | 1e-12 | -2.0043e-13 | 0.44118 | 0.55882 | 1e-12 | 0.75544 | 0.29994 | -0.055385 | 0.71627 | 0.3573 | -0.07357 | 0.68196 | 0.40939 | -0.091344 | 2 | 0.61111 | 0.53992 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.78833 | 0.21167 | 0.91768 | 1 | ; | Split AC, SEER 17, Mfg4 EER Slope, Low Degrad. Coef | SA-17-ML | Split-TS | AC | Mfg4 | Low
11708 | 17 | 12.16 | 51504.454 | 0.767 | 0.2333 | 0.03301 | 0.328 | 0.1203 | 0 | 55 | 2.8137 | -0.069873 | 0.00075391 | 0.0053717 | 2.3333e-06 | -0.00016463 | -0.63853 | 0.12184 | -0.0013811 | -0.018859 | 2.1667e-06 | 0.0002274 | -3.5206 | 0.093118 | -0.00064492 | 0.023051 | 3.6e-05 | -0.00021022 | 65.1211 | -2.088 | 0.016837 | 0.15107 | 2.9396e-05 | -0.0022667 | -1.6098e-14 | 0.8714 | 0.1286 | 1e-12 | -1.6098e-14 | 0.8714 | 0.1286 | 1e-12 | -1.6098e-14 | 0.8714 | 0.1286 | 1e-12 | 0.80537 | 0.23013 | -0.035495 | 0.74664 | 0.31228 | -0.05892 | 0.69549 | 0.38805 | -0.083539 | 2 | 0.41176 | 0.47355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33945 | 0.66055 | 0.61144 | 1 | ; | Split AC, SEER 17, Mfg4 EER Slope, Med Degrad. Coef | SA-17-MM | Split-TS | AC | Mfg4 | Med
11709 | 17 | 12.95 | 33842.341 | 0.7872 | 0.1798 | 0.05319 | 0.365 | 0.425 | 0 | 55 | 1.2385 | -0.026071 | 0.00043398 | 0.0076086 | -7.8333e-06 | -0.00017156 | -5.7242 | 0.26821 | -0.0024529 | -0.017456 | -6.625e-06 | 0.00023298 | -4.0489 | 0.076982 | -0.00026862 | 0.046403 | 7.4875e-05 | -0.0006264 | 17.9602 | -0.53442 | 0.0042014 | 0.029384 | 6.3903e-06 | -0.00044985 | 2.2345e-13 | 1.1828 | -0.18277 | 1e-12 | 2.2345e-13 | 1.1828 | -0.18277 | 1e-12 | 2.2345e-13 | 1.1828 | -0.18277 | 1e-12 | 0.75531 | 0.30035 | -0.055665 | 0.71607 | 0.35794 | -0.074003 | 0.68168 | 0.41027 | -0.091949 | 2 | 0.61111 | 0.56502 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3161 | -0.31614 | 1 | 1.1229 | ; | Split AC, SEER 17, Mfg4 EER Slope, High Degrad. Coef | SA-17-MH | Split-TS | AC | Mfg4 | High
11801 | 18 | 12.97 | 37800 | 0.76 | 0.22318 | 0.03228 | 0.287 | 0.0851 | 0.02 | 55 | 0.27177 | 0.005755 | 0.00015563 | 0.0060751 | -1.7524e-05 | -0.00012175 | 3.78 | -0.042062 | 2.0938e-05 | 0.002411 | -2.2524e-05 | -1.2813e-05 | -0.083989 | 0.0036237 | 1.2813e-05 | 0.011942 | 9.9095e-05 | -0.00019563 | -22.2338 | 0.93676 | -0.0081417 | -0.089204 | 0.00032545 | 0.00040167 | 1.6376e-15 | 0.74224 | 0.25776 | 1e-12 | 1.6376e-15 | 0.74224 | 0.25776 | 1e-12 | 1.6376e-15 | 0.74224 | 0.25776 | 1e-12 | 0.91974 | 0.087775 | -0.0075124 | 0.88458 | 0.12905 | -0.013628 | 0.85337 | 0.16778 | -0.021159 | 2 | 0.70082 | 0.72222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.0925 | 2.0925 | 0.37397 | 1 | ; | Split AC, SEER 18, Mfg2 EER Slope, Low Degrad. Coef | SA-18-LL | Split-TS | AC | Mfg2 | Low
11802 | 18 | 13.22 | 37600 | 0.77 | 0.22729 | 0.03218 | 0.223 | 0.0576 | 0.02 | 55 | 0.54107 | -0.0011103 | 0.00020313 | 0.0053916 | -1.5429e-05 | -0.00011806 | 3.9673 | -0.034837 | -9.125e-05 | -0.0061833 | -6.4524e-06 | 6.6313e-05 | -0.17217 | 0.0067231 | -1.8438e-05 | 0.011609 | 9.6536e-05 | -0.00018375 | -42.0063 | 1.3171 | -0.010184 | 0.10199 | 3.2783e-06 | -0.0014525 | 1.5266e-15 | 0.73003 | 0.26997 | 1e-12 | 1.5266e-15 | 0.73003 | 0.26997 | 1e-12 | 1.5266e-15 | 0.73003 | 0.26997 | 1e-12 | 0.87961 | 0.13371 | -0.013316 | 0.8439 | 0.17937 | -0.023269 | 0.81288 | 0.22004 | -0.032917 | 2 | 0.69835 | 0.71663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.1429 | 2.1429 | 0.3536 | 1 | ; | Split AC, SEER 18, Mfg2 EER Slope, High Degrad. Coef | SA-18-LH | Split-TS | AC | Mfg2 | High
11803 | 18 | 12.73 | 37347.791 | 0.7671 | 0.2325 | 0.03213 | 0.256 | 0.0962 | 0 | 55 | 1.6559 | -0.041377 | 0.00055391 | 0.0094542 | -1.4667e-05 | -0.00017846 | -5.0148 | 0.24532 | -0.0022797 | -0.01539 | -1.2125e-05 | 0.0002173 | -3.8899 | 0.08673 | -0.00041836 | 0.038036 | 7.0125e-05 | -0.00051678 | 118.6549 | -3.7554 | 0.029554 | 0.20043 | -6.2202e-05 | -0.0027004 | -5.5104e-14 | 0.77163 | 0.22837 | 1e-12 | -5.5104e-14 | 0.77163 | 0.22837 | 1e-12 | -5.5104e-14 | 0.77163 | 0.22837 | 1e-12 | 0.79084 | 0.25014 | -0.040981 | 0.74616 | 0.31331 | -0.059473 | 0.70701 | 0.37117 | -0.078181 | 2 | 0.54167 | 0.53848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.82526 | 0.17474 | 0.91991 | 1 | ; | Split AC, SEER 18, Mfg4 EER Slope, Low Degrad. Coef | SA-18-TL | Split-TS | AC | Mfg4 | Low
11804 | 18 | 13.37 | 33259.053 | 0.7775 | 0.219 | 0.03307 | 0.255 | 0.0978 | 0 | 55 | 0.8815 | -0.017876 | 0.00038529 | 0.0090288 | -1.2e-05 | -0.00018269 | -6.0705 | 0.27909 | -0.0025517 | -0.016636 | -1.3583e-05 | 0.00024019 | -3.0252 | 0.058902 | -0.00018268 | 0.039588 | 7.8833e-05 | -0.00056142 | 138.3725 | -4.4071 | 0.035151 | 0.23329 | 1.0801e-05 | -0.0034801 | -1.5941e-14 | 0.93646 | 0.063535 | 1e-12 | -1.5941e-14 | 0.93646 | 0.063535 | 1e-12 | -1.5941e-14 | 0.93646 | 0.063535 | 1e-12 | 0.79113 | 0.24997 | -0.041101 | 0.74666 | 0.31298 | -0.05964 | 0.70766 | 0.37077 | -0.078429 | 2 | 0.54545 | 0.57661 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.32347 | 0.67653 | 0.69249 | 1 | ; | Split AC, SEER 18, Mfg4 EER Slope, Median Degrad. Coef | SA-18-TM | Split-TS | AC | Mfg4 | Median
11805 | 18 | 13.75 | 34047.791 | 0.7944 | 0.2098 | 0.03524 | 0.256 | 0.1169 | 0 | 55 | 1.9684 | -0.04916 | 0.00061328 | 0.0087691 | -1.1042e-05 | -0.00018241 | -5.9167 | 0.2746 | -0.0025115 | -0.016878 | -1.0458e-05 | 0.00023414 | -4.214 | 0.097557 | -0.00050078 | 0.036732 | 7.6625e-05 | -0.00051146 | 113.0348 | -3.5495 | 0.027868 | 0.17472 | -2.8104e-05 | -0.0024612 | 2.9144e-13 | 0.99325 | 0.0067494 | 1e-12 | 2.9144e-13 | 0.99325 | 0.0067494 | 1e-12 | 2.9144e-13 | 0.99325 | 0.0067494 | 1e-12 | 0.74006 | 0.32252 | -0.062578 | 0.69605 | 0.38829 | -0.084339 | 0.65761 | 0.44802 | -0.10563 | 2 | 0.54167 | 0.57033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.46986 | 0.53014 | 0.75702 | 1 | ; | Split AC, SEER 18, Mfg4 EER Slope, High Degrad. Coef | SA-18-TH | Split-TS | AC | Mfg4 | High
11806 | 18 | 13.38 | 36300 | 0.7521 | 0.2032 | 0.03306 | 0.366 | 0.126 | 0.02 | 55 | -1.3163 | 0.023836 | 0.00028728 | 0.020877 | -3.7995e-06 | -0.00039581 | 0.86087 | 0.085337 | -0.0011896 | -0.026126 | -1.3815e-05 | 0.00037207 | 3.2845 | -0.059405 | 0.00034048 | -0.010495 | 0.00021372 | -0.00012011 | 12.0968 | -1.0544 | 0.014129 | 0.48724 | 0.00034254 | -0.0083672 | -2.2551e-15 | 0.94326 | 0.056743 | 1e-12 | -2.2551e-15 | 0.94326 | 0.056743 | 1e-12 | -2.2551e-15 | 0.94326 | 0.056743 | 1e-12 | 0.78543 | 0.25774 | -0.043168 | 0.74888 | 0.31101 | -0.059884 | 0.71713 | 0.35759 | -0.074723 | 2 | 0.66667 | 0.67926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.59542 | 0.40458 | 0.86514 | 1 | ; | Split AC, SEER 18, York EER Slope, Med Degrad. Coef | SA-18-YM | Split-TS | AC | York | Med
11901 | 19 | 13.12 | 38933.116 | 0.792 | 0.2234 | 0.03339 | 0.255 | 0.0734 | 0 | 55 | 3.0891 | -0.080907 | 0.00082279 | 0.008141 | -1.5542e-05 | -0.00015631 | -4.9968 | 0.24631 | -0.0022948 | -0.016408 | -1.025e-05 | 0.00022723 | -5.3704 | 0.13367 | -0.00078685 | 0.035173 | 7.0583e-05 | -0.00047629 | 155.7261 | -4.869 | 0.037865 | 0.24893 | -5.3457e-05 | -0.0034001 | -5.8287e-16 | 0.65664 | 0.34336 | 1e-12 | -5.8287e-16 | 0.65664 | 0.34336 | 1e-12 | -5.8287e-16 | 0.65664 | 0.34336 | 1e-12 | 0.73151 | 0.33459 | -0.066101 | 0.68756 | 0.40059 | -0.088148 | 0.64924 | 0.46032 | -0.10956 | 2 | 0.53846 | 0.52674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2713 | -0.27125 | 1 | 1.1252 | ; | Split AC, SEER 19, Mfg4 EER Slope, Med Degrad. Coef | SA-19-TM | Split-TS | AC | Mfg4 | Med
11902 | 19 | 14 | 25966.252 | 0.7578 | 0.2105 | 0.03081 | 0.255 | 0.0455 | 0 | 125 | 2.1626 | -0.058435 | 0.00069167 | 0.0091461 | -1.9372e-05 | -0.0001644 | -8.3515 | 0.33616 | -0.0028913 | -0.018119 | -1.7366e-05 | 0.00026484 | -2.6205 | 0.10491 | -0.00066454 | -0.0066815 | 0.0002594 | -0.00033491 | 216.1488 | -7.3038 | 0.061219 | 0.8425 | 0.0004031 | -0.013241 | -6.6613e-15 | -0.13474 | 1.1347 | 1e-12 | -6.6613e-15 | -0.13474 | 1.1347 | 1e-12 | -6.6613e-15 | -0.13474 | 1.1347 | 1e-12 | 0.90242 | 0.10451 | -0.0069348 | 0.87634 | 0.14066 | -0.016995 | 0.85514 | 0.16454 | -0.019671 | 2 | 0.98 | 0.87689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.6826 | -59.6826 | 1 | 2.1937 | ; | Split AC, SEER 19, Mfg1 EER Slope, Med Degrad. Coef | SA-19-CM | Split-R | AC | Mfg1 | Med
11903 | 19 | 13.82 | 38000 | 0.78 | 0.22462 | 0.03171 | 0.166 | 0.0186 | 0.02 | 55 | 0.30623 | 0.0055713 | 0.00014719 | 0.0057633 | -1.9464e-05 | -0.00011187 | 3.4488 | -0.015846 | -0.00028094 | -0.0077408 | -2.006e-05 | 0.00012419 | -0.40817 | 0.011653 | -4.3125e-05 | 0.012914 | 9.419e-05 | -0.00019731 | 76.4526 | -2.8713 | 0.026013 | 0.62481 | 0.00050212 | -0.010014 | 1.2212e-15 | 0.75673 | 0.24327 | 1e-12 | 1.2212e-15 | 0.75673 | 0.24327 | 1e-12 | 1.2212e-15 | 0.75673 | 0.24327 | 1e-12 | 0.92848 | 0.075431 | -0.0039093 | 0.8925 | 0.11844 | -0.010938 | 0.86109 | 0.1566 | -0.017691 | 2 | 0.6971 | 0.70526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.0364 | 2.0364 | 0.38317 | 1 | ; | Split AC, SEER 19, Mfg2 EER Slope, Med Degrad. Coef | SA-19-LM | Split-TS | AC | Mfg2 | Med
12001 | 20 | 14.43 | 26498.252 | 0.7577 | 0.204 | 0.03019 | 0.255 | 0.0263 | 0 | 125 | 2.1624 | -0.058443 | 0.00069181 | 0.0091522 | -1.9423e-05 | -0.0001644 | -8.3574 | 0.33637 | -0.0028931 | -0.018125 | -1.7414e-05 | 0.000265 | -2.6386 | 0.10533 | -0.00066657 | -0.0066304 | 0.00025992 | -0.00033651 | 412.8757 | -13.8247 | 0.11484 | 1.449 | 0.00073182 | -0.022841 | 2.4647e-14 | -0.21346 | 1.2135 | 1e-12 | 2.4647e-14 | -0.21346 | 1.2135 | 1e-12 | 2.4647e-14 | -0.21346 | 1.2135 | 1e-12 | 0.92619 | 0.079998 | -0.0061834 | 0.90261 | 0.10329 | -0.0059046 | 0.88059 | 0.12935 | -0.0099469 | 2 | 0.98 | 0.8768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106.3593 | -105.3593 | 1 | 3.1072 | ; | Split AC, SEER 20, Mfg1 EER Slope, Med Degrad. Coef | SA-20-CM | Split-R | AC | Mfg1 | Med
12101 | 21 | 15.03 | 27596.596 | 0.7601 | 0.1828 | 0.02899 | 0.365 | 0.001 | 0 | 125 | 2.1466 | -0.057695 | 0.00068329 | 0.0090413 | -1.9182e-05 | -0.00016247 | -8.2317 | 0.3318 | -0.0028534 | -0.017868 | -1.7149e-05 | 0.0002612 | -2.7821 | 0.10849 | -0.0006763 | -0.0072468 | 0.00027444 | -0.0003518 | 12204.9921 | -408.0183 | 3.389 | 38.0077 | 0.023199 | -0.61276 | -1.5543e-14 | -0.54816 | 1.5482 | 1e-12 | -1.5543e-14 | -0.54816 | 1.5482 | 1e-12 | -1.5543e-14 | -0.54816 | 1.5482 | 1e-12 | 0.93087 | 0.071692 | -0.0025666 | 0.90431 | 0.10917 | -0.013484 | 0.88256 | 0.13386 | -0.016419 | 2 | 0.98 | 0.87844 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1799.8834 | -1798.8834 | 1 | 36.9777 | ; | Split AC, SEER 21, Mfg1 EER Slope, Med Degrad. Coef | SA-21-CM | Split-R | AC | Mfg1 | Med
21001 | 10 | 9.12 | 24890.1122 | 0.7308 | 0.31389 | 0.03515 | 0.365 | 0.2541 | 0 | 100 | 2.6857 | -0.076584 | 0.00079834 | 0.0097026 | -3.2612e-05 | -0.00012031 | -4.3331 | 0.21581 | -0.0020488 | -0.0046574 | -2.4881e-05 | 0.00011599 | -1.015 | 0.067142 | -0.00059398 | -0.0083138 | 0.0001093 | -2.1647e-06 | 43.2878 | -1.2822 | 0.0097177 | 1e-12 | 1e-12 | 1e-12 | 1.28e-05 | 1.1177 | -0.14031 | 0.022646 | 2.6734e-05 | 1.1482 | -0.18271 | 0.03443 | 4.6493e-05 | 1.1763 | -0.22331 | 0.046927 | 0.89342 | 0.11786 | -0.011364 | 0.86849 | 0.14864 | -0.017294 | 0.84637 | 0.17698 | -0.023593 | 1 | 1 | 1 | 6.8 | 3.08 | 22300 | 0.32446 | 0.43219 | 0.0024648 | -2.3318e-05 | 0.0082513 | 0.00012628 | -4.779e-05 | 1.1874 | 0.010345 | 3.3597e-05 | -0.020254 | 0.00015209 | -0.00013988 | 1 | 0 | 0 | 1 | ; | Split HP, SEER 10, Low EER Slope, Low Degrad. Coef | SH-10-LL | Split-R | HP | Low | Low
21002 | 10 | 9.52 | 24596.596 | 0.7276 | 0.3036 | 0.03252 | 0.365 | 0.2016 | 0 | 100 | 2.7788 | -0.075579 | 0.00078796 | 0.0072226 | -1.9665e-05 | -0.00011954 | -3.9429 | 0.20203 | -0.0019456 | -0.0039589 | -3.1427e-05 | 0.00012577 | -1.0983 | 0.06542 | -0.000565 | -0.0055602 | 9.9285e-05 | -1.8295e-05 | 54.5871 | -1.626 | 0.012332 | 1e-12 | 1e-12 | 1e-12 | 7.2478e-05 | 1.2027 | -0.26271 | 0.059969 | 0.00011782 | 1.236 | -0.31431 | 0.078168 | 0.00017345 | 1.2665 | -0.3629 | 0.096274 | 0.82622 | 0.20361 | -0.030176 | 0.80141 | 0.23745 | -0.039377 | 0.77942 | 0.26843 | -0.048548 | 1 | 1 | 1 | 7 | 3.2 | 22600 | 0.31261 | 0.51855 | 0.00010742 | -5.8997e-06 | 0.0080204 | 0.00013588 | -5.2971e-05 | 1.1326 | 0.010803 | 2.6032e-05 | -0.01848 | 0.00011913 | -0.00012491 | 1 | 0 | 0 | 1 | ; | Split HP, SEER 10, Low EER Slope, Med Degrad. Coef | SH-10-LM | Split-R | HP | Low | Med
21003 | 10 | 10.01 | 58800 | 0.7381 | 0.28844 | 0.03146 | 0.365 | 0.1415 | 0.02 | 100 | 0.53344 | -0.0056185 | 0.0001615 | 0.0067088 | -4.675e-05 | -1.53e-05 | 1.7985 | 0.001115 | -0.000265 | 0.007611 | -5e-05 | 7e-06 | 1.0015 | -0.0026135 | 8.65e-05 | -0.0029867 | 0.00015075 | -0.0002029 | 11.0016 | -0.14928 | 0 | 1e-12 | 1e-12 | 1e-12 | 0.00021601 | 1.2854 | -0.39389 | 0.10824 | 0.00031399 | 1.3209 | -0.45319 | 0.13194 | 0.00042614 | 1.3532 | -0.5084 | 0.15482 | 0.76597 | 0.28782 | -0.054621 | 0.74134 | 0.32421 | -0.06666 | 0.71951 | 0.3574 | -0.078308 | 1 | 1 | 1 | 7.2 | 3.1 | 57000 | 0.32258 | 0.49754 | -0.0035468 | 1.864e-05 | 0.016303 | 4.1388e-08 | -3.2506e-05 | 1.0056 | 0.0076815 | 6.6733e-05 | -0.018148 | 0.00023191 | -0.00016098 | 1 | 0 | 0 | 1 | ; | Split HP, SEER 10, Low EER Slope, High Degrad. Coef | SH-10-LH | Split-R | HP | Low | High
21004 | 10 | 8.78 | 17778.5053 | 0.7413 | 0.32807 | 0.03515 | 0.365 | 0.2307 | 0 | 100 | 3.2147 | -0.081674 | 0.00084926 | 0.0030296 | 5.7672e-06 | -0.00014057 | -3.8556 | 0.20894 | -0.0020275 | -0.009746 | -1.5271e-05 | 0.00016059 | -2.0119 | 0.088143 | -0.00077337 | -0.0011726 | 8.0641e-05 | -6.0427e-06 | 44.9736 | -1.3238 | 0.0099629 | 1e-12 | 1e-12 | 1e-12 | 3.5993e-06 | 1.0789 | -0.08972 | 0.010809 | 9.756e-06 | 1.108 | -0.12741 | 0.019366 | 1.977e-05 | 1.1349 | -0.1639 | 0.029026 | 0.92642 | 0.078973 | -0.0054175 | 0.90146 | 0.10819 | -0.0097151 | 0.87929 | 0.13516 | -0.014573 | 1 | 1 | 1 | 6.9 | 3.22 | 16300 | 0.31199 | 0.39388 | 0.000142 | -3.272e-06 | 0.010095 | 0.00012964 | -4.518e-05 | 1.3969 | 0.013881 | 2.9612e-05 | -0.03592 | 0.00033915 | -0.00017466 | 1 | 0 | 0 | 1 | ; | Split HP, SEER 10, Med EER Slope, Low Degrad. Coef | SH-10-ML | Split-R | HP | Med | Low
21005 | 10 | 9.01 | 45244.043 | 0.6861 | 0.32561 | 0.03094 | 0.365 | 0.2695 | 0 | 100 | 0.81128 | -0.018719 | 0.00035371 | 0.0090212 | -3.3219e-05 | -0.00011031 | 0.54049 | 0.067781 | -0.00086934 | -0.005392 | -6.0937e-06 | 6.0938e-05 | -0.38566 | 0.032329 | -0.00020957 | 0.0010332 | 0.00011907 | -0.00015906 | 26.6626 | -0.79875 | 0.0062049 | 1e-12 | 1e-12 | 1e-12 | 1.663e-05 | 1.1277 | -0.15405 | 0.026304 | 3.3211e-05 | 1.1587 | -0.19761 | 0.038895 | 5.6145e-05 | 1.1871 | -0.23924 | 0.052099 | 0.88511 | 0.12799 | -0.013204 | 0.86019 | 0.15916 | -0.019543 | 0.83808 | 0.18783 | -0.026202 | 1 | 1 | 1 | 7.2 | 2.98 | 41000 | 0.33547 | 0.48708 | 0.0022175 | -2.2764e-05 | 0.0080465 | 0.00011543 | -4.9826e-05 | 1.0328 | 0.0029551 | 5.9167e-05 | -0.0059182 | -9.9441e-08 | -7.6341e-05 | 1 | 0 | 0 | 1 | ; | Split HP, SEER 10, Med EER Slope, Med Degrad. Coef | SH-10-MM | Split-R | HP | Med | Med
21006 | 10 | 9.54 | 41810 | 0.7512 | 0.29923 | 0.03468 | 0.365 | 0.1918 | 0.02 | 100 | 0.88897 | -0.016558 | 0.0002515 | 0.0072477 | -4.775e-05 | -2.61e-05 | 0.98267 | 0.030796 | -0.000509 | 0.0042383 | -4.5083e-05 | 3.82e-05 | 0.70283 | 0.0076665 | -3.5e-06 | -0.0059112 | 0.00016375 | -0.0001755 | 8.3471 | -0.10966 | 0 | 1e-12 | 1e-12 | 1e-12 | 8.6274e-05 | 1.2141 | -0.28011 | 0.065975 | 0.00013749 | 1.2477 | -0.33284 | 0.08497 | 0.00019956 | 1.2784 | -0.3824 | 0.10377 | 0.81767 | 0.21514 | -0.033211 | 0.79289 | 0.24935 | -0.042821 | 0.77091 | 0.28066 | -0.05235 | 1 | 1 | 1 | 7.2 | 3.1 | 39000 | 0.32258 | 0.50135 | -0.0032958 | 1.6026e-05 | 0.017694 | 6.2468e-07 | -5.5371e-05 | 1.1925 | 0.0076525 | 5.5889e-05 | -0.024692 | 0.00026254 | -0.00012809 | 1 | 0 | 0 | 1 | ; | Split HP, SEER 10, Med EER Slope, High Degrad. Coef | SH-10-MH | Split-R | HP | Med | High
21007 | 10 | 8.94 | 42244 | 0.7349 | 0.3247 | 0.03314 | 0.365 | 0.1991 | 0 | 100 | 2.5528 | -0.062992 | 0.0006532 | 0.0049664 | -1.631e-05 | -9.2557e-05 | -1.643 | 0.13839 | -0.0014391 | -0.013122 | -1.0762e-05 | 0.0001845 | -1.2598 | 0.069465 | -0.00053187 | -0.0062728 | 0.00014619 | -0.00011474 | 52.5462 | -1.5184 | 0.01118 | 1e-12 | 1e-12 | 1e-12 | 2.1242e-05 | 1.1379 | -0.16819 | 0.030233 | 4.0782e-05 | 1.1692 | -0.21291 | 0.043626 | 6.7211e-05 | 1.1979 | -0.25553 | 0.057533 | 0.8768 | 0.13825 | -0.015181 | 0.8519 | 0.16981 | -0.021928 | 0.8298 | 0.19881 | -0.028946 | 1 | 1 | 1 | 7.2 | 3 | 42000 | 0.32423 | 0.57143 | 0.00022109 | -1.1905e-05 | 0.0092094 | 5.5461e-05 | -2.551e-05 | 1.0876 | 0.0011147 | 0.00011398 | -0.011862 | 0.00013312 | -0.00014002 | 1 | 0 | 0 | 1 | ; | Split HP, SEER 10, High EER Slope, Low Degrad. Coef | SH-10-HL | Split-R | HP | High | Low
21008 | 10 | 9.01 | 37894.894 | 0.7097 | 0.32427 | 0.03167 | 0.365 | 0.225 | 0 | 100 | 1.7413 | -0.040143 | 0.00050117 | 0.005304 | -1.3417e-05 | -0.0001075 | -1.2901 | 0.12608 | -0.0013088 | -0.0068638 | 7.6979e-06 | 4.7187e-05 | -0.58043 | 0.046714 | -0.0003959 | -0.0058191 | 0.00012903 | -6.0312e-05 | 42.1011 | -1.2606 | 0.0096588 | 1e-12 | 1e-12 | 1e-12 | 3.3211e-05 | 1.1587 | -0.19761 | 0.038895 | 5.967e-05 | 1.1907 | -0.24463 | 0.053881 | 9.4115e-05 | 1.22 | -0.28925 | 0.069183 | 0.86019 | 0.15916 | -0.019543 | 0.83532 | 0.19148 | -0.027102 | 0.81326 | 0.22114 | -0.034833 | 1 | 1 | 1 | 7.3 | 3.04 | 32400 | 0.32866 | 0.53054 | 0.0010371 | -4.1152e-06 | 0.0023607 | 0.00011984 | 1.2566e-05 | -0.46921 | 0.033136 | -1.054e-05 | -0.0026813 | 7.3956e-05 | -0.0002541 | 1 | 0 | 0 | 1 | ; | Split HP, SEER 10, High EER Slope, Med Degrad. Coef | SH-10-HM | Split-R | HP | High | Med
21009 | 10 | 9.39 | 47993 | 0.7562 | 0.3069 | 0.03334 | 0.365 | 0.154 | 0 | 100 | 2.8361 | -0.069879 | 0.00069173 | 0.0045196 | -1.6857e-05 | -8.43e-05 | -2.6635 | 0.16954 | -0.0016832 | -0.013263 | -1.2452e-05 | 0.00019369 | -1.5182 | 0.078325 | -0.00060147 | -0.0074392 | 0.00014795 | -0.0001034 | 75.3604 | -2.1833 | 0.016022 | 1e-12 | 1e-12 | 1e-12 | 0.00010194 | 1.2255 | -0.29791 | 0.072258 | 0.00015951 | 1.2595 | -0.35175 | 0.092043 | 0.00022851 | 1.2905 | -0.40227 | 0.11153 | 0.80912 | 0.2268 | -0.036387 | 0.78436 | 0.26139 | -0.046404 | 0.76241 | 0.29301 | -0.056289 | 1 | 1 | 1 | 7.2 | 3.2 | 47000 | 0.31225 | 0.18865 | 0.0091403 | -7.4468e-05 | 0.0080527 | 9.3381e-05 | -1.4691e-05 | 0.94611 | 0.0083744 | 6.12e-05 | -0.015269 | 0.0001579 | -0.00014083 | 1 | 0 | 0 | 1 | ; | Split HP, SEER 10, High EER Slope, High Degrad. Coef | SH-10-HH | Split-R | HP | High | High
21301 | 13 | 11.53 | 25598.642 | 0.75 | 0.2555 | 0.03125 | 0.293 | 0.1129 | 0 | 55 | 3.0075 | -0.075226 | 0.0007541 | 0.0033559 | -1.4219e-05 | -8.5312e-05 | -3.6346 | 0.19506 | -0.0017805 | -0.007642 | 2.0042e-05 | 1.625e-05 | -3.2389 | 0.09682 | -0.00061875 | 0.015587 | 8.8104e-05 | -0.00027438 | 83.5524 | -2.4149 | 0.017654 | 1e-12 | 1e-12 | 1e-12 | 1.663e-05 | 1.1277 | -0.15405 | 0.026304 | 3.3211e-05 | 1.1587 | -0.19761 | 0.038895 | 5.6145e-05 | 1.1871 | -0.23924 | 0.052099 | 0.88511 | 0.12799 | -0.013204 | 0.86019 | 0.15916 | -0.019543 | 0.83808 | 0.18783 | -0.026202 | 1 | 1 | 1 | 8.3 | 3.5 | 21129.2 | 0.29285 | 0.5325 | -0.00049956 | -1.912e-06 | 0.0079586 | 0.00012731 | -4.3601e-05 | 0.86181 | 0.0084487 | 3.6449e-05 | -0.010183 | 6.86e-05 | -9.2633e-05 | 1 | 0 | 0 | 1 | ; | Split HP, SEER 13, Low EER Slope, Low Degrad. Coef | SH-13-LL | Split-R | HP | Low | Low
21302 | 13 | 11.84 | 48930 | 0.7507 | 0.2374 | 0.03168 | 0.365 | 0.1164 | 0 | 55 | 1.1178 | -0.023581 | 0.0003585 | 0.0053237 | -3.0667e-05 | -5.91e-05 | 2.1597 | -0.000701 | -0.000286 | 0.002418 | -4.3167e-05 | 5.2e-05 | 0.99779 | -0.007208 | 0.000192 | 0.0020622 | 0.00018875 | -0.0003576 | 11.1201 | -0.15105 | 0 | 1e-12 | 1e-12 | 1e-12 | 2.6734e-05 | 1.1482 | -0.18271 | 0.03443 | 4.9561e-05 | 1.1799 | -0.22858 | 0.048622 | 7.9822e-05 | 1.2089 | -0.27221 | 0.063229 | 0.86849 | 0.14864 | -0.017294 | 0.84361 | 0.18058 | -0.024448 | 0.82153 | 0.20992 | -0.031823 | 1 | 1 | 1 | 8 | 4.09 | 46000 | 0.2445 | 0.52239 | -0.0028874 | 1.3587e-05 | 0.016094 | -1.6915e-07 | -4.3434e-05 | 1.0249 | 0.0035545 | 2.1474e-05 | -0.014943 | 9.3632e-05 | 3.5437e-05 | 1 | 0 | 0 | 1 | ; | Split HP, SEER 13, Low EER Slope, Med Degrad. Coef | SH-13-LM | Split-R | HP | Low | Med
21303 | 13 | 12.5 | 31370 | 0.7737 | 0.2174 | 0.03506 | 0.365 | 0.1511 | 0 | 55 | 1.2306 | -0.028843 | 0.000367 | 0.0073972 | -4.25e-05 | -4.16e-05 | 0.80346 | 0.036358 | -0.0005775 | 0.0039492 | -5.5e-05 | 7.45e-05 | 0.59526 | 0.004412 | 4.7e-05 | 0.0016515 | 0.00015442 | -0.0002596 | 9.629 | -0.12879 | 0 | 1e-12 | 1e-12 | 1e-12 | 0.00011963 | 1.2372 | -0.31609 | 0.078814 | 0.00018406 | 1.2715 | -0.37103 | 0.099385 | 0.00026049 | 1.3027 | -0.4225 | 0.11955 | 0.80059 | 0.23859 | -0.039704 | 0.77585 | 0.27354 | -0.050126 | 0.75392 | 0.30548 | -0.060364 | 1 | 1 | 1 | 8 | 3.46 | 28200 | 0.28902 | 0.44887 | -0.00087708 | -2.2163e-06 | 0.018922 | 4.8169e-07 | -8.1163e-05 | 1.5705 | 0.0039751 | 4.7938e-05 | -0.033101 | 0.00027456 | -4.0843e-05 | 1 | 0 | 0 | 1 | ; | Split HP, SEER 13, Low EER Slope, High Degrad. Coef | SH-13-LH | Split-R | HP | Low | High
21304 | 13 | 11.12 | 43600 | 0.74 | 0.26056 | 0.02982 | 0.346 | 0.0963 | 0 | 100 | 0.82741 | -0.00885 | 0.00023438 | 0.0022913 | -9.5e-06 | -6.575e-05 | 1.828 | 0.020088 | -0.00048125 | -0.00068342 | -1.775e-05 | 3.325e-05 | 0.63994 | -0.00017656 | 6.9531e-05 | 0.0029365 | 0.00015458 | -0.00025363 | 57.1472 | -1.6475 | 0.012082 | 1e-12 | 1e-12 | 1e-12 | 2.4385e-06 | 1.0698 | -0.078346 | 0.0085766 | 7.2789e-06 | 1.0985 | -0.11487 | 0.016341 | 1.5536e-05 | 1.125 | -0.15035 | 0.025302 | 0.93446 | 0.069814 | -0.0042974 | 0.9095 | 0.098648 | -0.0081949 | 0.88732 | 0.12528 | -0.0127 | 1 | 1 | 1 | 8.3 | 3.4 | 39400 | 0.29106 | 0.44609 | 0 | 0 | 0.010267 | 3.2312e-05 | 0 | 2.0124 | 0 | 0 | -0.039052 | 0.00037259 | 0 | 1 | 0 | 0 | 1 | ; | Split HP, SEER 13, Med EER Slope, Low Degrad. Coef | SH-13-ML | Split-R | HP | Med | Low
21305 | 13 | 11.07 | 42695.9152 | 0.726 | 0.2718 | 0.02811 | 0.292 | 0.0806 | 0 | 55 | 2.1469 | -0.053591 | 0.00057676 | 0.005859 | -2.599e-05 | -7.3437e-05 | -1.7062 | 0.13575 | -0.0013857 | -0.0069019 | -2.6146e-06 | 8.0312e-05 | -1.7948 | 0.059853 | -0.00042656 | 0.0098629 | 9.9313e-05 | -0.00017813 | 90.6476 | -2.6288 | 0.019265 | 1e-12 | 1e-12 | 1e-12 | 1.28e-05 | 1.1177 | -0.14031 | 0.022646 | 2.6734e-05 | 1.1482 | -0.18271 | 0.03443 | 4.6493e-05 | 1.1763 | -0.22331 | 0.046927 | 0.89342 | 0.11786 | -0.011364 | 0.86849 | 0.14864 | -0.017294 | 0.84637 | 0.17698 | -0.023593 | 1 | 1 | 1 | 8.1 | 3.28 | 39500 | 0.30501 | 0.6623 | -0.0032213 | 1.0127e-05 | 0.012603 | 4.4602e-05 | -5.3888e-05 | 0.85347 | 0.012033 | 3.2884e-05 | -0.015984 | 0.00015301 | -0.00013486 | 1 | 0 | 0 | 1 | ; | Split HP, SEER 13, Med EER Slope, Med Degrad. Coef | SH-13-MM | Split-R | HP | Med | Med
21306 | 13 | 11.96 | 37195.9152 | 0.7795 | 0.244 | 0.03226 | 0.292 | 0.0702 | 0 | 55 | 3.8943 | -0.10524 | 0.0010072 | 0.0057953 | -6.8438e-06 | -0.00013406 | -6.8992 | 0.29864 | -0.0027344 | -0.010798 | -3.5104e-05 | 0.00023687 | -3.7316 | 0.12177 | -0.00091445 | 0.0071743 | 0.00010804 | -0.00015375 | 166.9797 | -4.8395 | 0.035257 | 1e-12 | 1e-12 | 1e-12 | 0.00018743 | 1.273 | -0.37355 | 0.10035 | 0.00027598 | 1.3082 | -0.43176 | 0.12326 | 0.00037818 | 1.3402 | -0.48604 | 0.14546 | 0.77475 | 0.27512 | -0.050616 | 0.75009 | 0.31116 | -0.062249 | 0.72824 | 0.34403 | -0.073543 | 1 | 1 | 1 | 8.55 | 3.38 | 34400 | 0.2659 | 0.72904 | -0.0037841 | 1.1628e-05 | 0.011498 | 6.4002e-05 | -6.1669e-05 | 0.92604 | 0.011616 | 5.309e-05 | -0.017186 | 0.00016908 | -0.00017176 | 1 | 0 | 0 | 1 | ; | Split HP, SEER 13, Med EER Slope, High Degrad. Coef | SH-13-MH | Split-R | HP | Med | High
21307 | 13 | 10.71 | 61042 | 0.7887 | 0.2702 | 0.03276 | 0.329 | 0.0516 | 0 | 100 | 2.7252 | -0.06644 | 0.00068411 | 0.0071699 | -2.3268e-05 | -0.00012818 | -3.4771 | 0.19814 | -0.0019158 | -0.015746 | -1.4583e-05 | 0.00022458 | -1.3687 | 0.079355 | -0.00062022 | -0.016303 | 0.00020668 | -7.5478e-05 | 248.216 | -7.227 | 0.052794 | 1e-12 | 1e-12 | 1e-12 | 1.5758e-06 | 1.0607 | -0.067351 | 0.006601 | 5.2959e-06 | 1.0891 | -0.10271 | 0.01357 | 1.2009e-05 | 1.1153 | -0.13716 | 0.021831 | 0.94251 | 0.06078 | -0.0033065 | 0.91754 | 0.089226 | -0.0068034 | 0.89536 | 0.11552 | -0.010954 | 1 | 1 | 1 | 8.1 | 3.56 | 60700 | 0.27383 | 0.29224 | 0.0060638 | -5.7661e-05 | 0.0088136 | 8.4399e-05 | -1.0591e-05 | 0.82119 | 0.004555 | 0.00014675 | -0.0087573 | 0.000176 | -0.0002542 | 1 | 0 | 0 | 1 | ; | Split HP, SEER 13, High EER Slope, Low Degrad. Coef | SH-13-HL | Split-R | HP | High | Low
21308 | 13 | 11.2 | 48595 | 0.7209 | 0.2625 | 0.02881 | 0.329 | 0.1044 | 0 | 100 | 1.8624 | -0.040109 | 0.00048256 | 0.0047862 | -1.1065e-05 | -0.00010936 | -0.34892 | 0.10001 | -0.0011431 | -0.013187 | -7.8929e-06 | 0.00017339 | -0.9082 | 0.052167 | -0.00040011 | -0.0053105 | 0.00016496 | -0.00012178 | 67.2918 | -1.8832 | 0.01334 | 1e-12 | 1e-12 | 1e-12 | 3.3211e-05 | 1.1587 | -0.19761 | 0.038895 | 5.967e-05 | 1.1907 | -0.24463 | 0.053881 | 9.4115e-05 | 1.22 | -0.28925 | 0.069183 | 0.86019 | 0.15916 | -0.019543 | 0.83532 | 0.19148 | -0.027102 | 0.81326 | 0.22114 | -0.034833 | 1 | 1 | 1 | 8.5 | 3.56 | 50000 | 0.28112 | 0.13695 | 0.0078798 | -5.5e-05 | 0.010639 | 8.8056e-05 | -3.4524e-05 | 1.2158 | -0.0013435 | 0.00015533 | -0.016892 | 0.00016416 | -0.00013726 | 1 | 0 | 0 | 1 | ; | Split HP, SEER 13, High EER Slope, Med Degrad. Coef | SH-13-HM | Split-R | HP | High | Med
21309 | 13 | 11.26 | 30086 | 0.7269 | 0.2607 | 0.02908 | 0.328 | 0.0964 | 0 | 100 | 2.0198 | -0.046955 | 0.00053356 | 0.0054815 | -1.625e-05 | -0.00010103 | -0.73682 | 0.10943 | -0.0012023 | -0.012514 | -8.6548e-06 | 0.00016793 | -1.5013 | 0.071962 | -0.00055467 | -0.0054993 | 0.00018843 | -0.00015843 | 78.1346 | -2.1917 | 0.01553 | 1e-12 | 1e-12 | 1e-12 | 8.6274e-05 | 1.2141 | -0.28011 | 0.065975 | 0.00013749 | 1.2477 | -0.33284 | 0.08497 | 0.00019956 | 1.2784 | -0.3824 | 0.10377 | 0.81767 | 0.21514 | -0.033211 | 0.79289 | 0.24935 | -0.042821 | 0.77091 | 0.28066 | -0.05235 | 1 | 1 | 1 | 8 | 3.24 | 32000 | 0.30864 | 0.58963 | -0.0039862 | 2.3438e-05 | 0.011473 | 6.8638e-05 | -3.5342e-05 | 0.3699 | 0.023176 | -1.3028e-05 | -0.019057 | 0.00018968 | -0.00013729 | 1 | 0 | 0 | 1 | ; | Split HP, SEER 13, High EER Slope, High Degrad. Coef | SH-13-HH | Split-R | HP | High | High
21401 | 14 | 12.05 | 35400 | 0.81 | 0.23553 | 0.03672 | 0.304 | 0.1204 | 0 | 100 | 2.0216 | -0.04673 | 0.00053047 | 0.0051336 | -9.5e-06 | -0.00010587 | 0.98241 | 0.051441 | -0.00078906 | -0.0039263 | -3.3583e-05 | 0.000124 | -1.1465 | 0.062342 | -0.00043984 | -0.0045492 | 0.00016325 | -0.00017238 | 34.8843 | -0.95347 | 0.0066826 | 1e-12 | 1e-12 | 1e-12 | 2.4385e-06 | 1.0698 | -0.078346 | 0.0085766 | 7.2789e-06 | 1.0985 | -0.11487 | 0.016341 | 1.5536e-05 | 1.125 | -0.15035 | 0.025302 | 0.93446 | 0.069814 | -0.0042974 | 0.9095 | 0.098648 | -0.0081949 | 0.88732 | 0.12528 | -0.0127 | 1 | 1 | 1 | 8.2 | 3.46 | 32200 | 0.29095 | 0.42287 | 0 | 0 | 0.010207 | 4.4097e-05 | 0 | 2.1337 | 0 | 0 | -0.040808 | 0.00035506 | 0 | 1 | 0 | 0 | 1 | ; | Split HP, SEER 14, Med EER Slope, Low Degrad. Coef | SH-14-ML | Split-R | HP | Med | Low
21402 | 14 | 12.55 | 36950 | 0.7754 | 0.23562 | 0.03274 | 0.255 | 0.087 | 0 | 100 | 1.5702 | -0.043227 | 0.0004735 | 0.010389 | -5.8583e-05 | -4.05e-05 | 0.6838 | 0.04003 | -0.0006105 | 0.003635 | -5.8167e-05 | 8.71e-05 | 0.028526 | 0.027774 | -0.0001115 | -0.003054 | 0.00018858 | -0.0002829 | 14.436 | -0.20054 | 0 | 1e-12 | 1e-12 | 1e-12 | 7.1271e-06 | 1.0979 | -0.11402 | 0.016141 | 1.663e-05 | 1.1277 | -0.15405 | 0.026304 | 3.0936e-05 | 1.1552 | -0.1926 | 0.037377 | 0.91005 | 0.097994 | -0.0080948 | 0.88511 | 0.12799 | -0.013204 | 0.86296 | 0.15564 | -0.018779 | 1 | 1 | 1 | 8.5 | 3.66 | 34400 | 0.28249 | 0.48334 | -0.0018833 | 5.4506e-06 | 0.017815 | -1.6965e-06 | -6.4368e-05 | 1.3857 | 0.0056717 | 5.247e-05 | -0.028076 | 0.00026023 | -8.9704e-05 | 1 | 0 | 0 | 1 | ; | Split HP, SEER 14, Med EER Slope, Med Degrad. Coef | SH-14-MM | Split-R | HP | Med | Med
21403 | 14 | 13.38 | 26120 | 0.7703 | 0.21725 | 0.03369 | 0.263 | 0.1244 | 0 | 100 | 1.3745 | -0.044251 | 0.000499 | 0.013156 | -6.7083e-05 | -4.62e-05 | 0.71073 | 0.027818 | -0.000472 | 0.010752 | -7.05e-05 | 2.5e-05 | 0.29578 | 0.021473 | -6.25e-05 | -0.003101 | 0.00019033 | -0.0002949 | 11.8408 | -0.1618 | 0 | 1e-12 | 1e-12 | 1e-12 | 8.6274e-05 | 1.2141 | -0.28011 | 0.065975 | 0.00013749 | 1.2477 | -0.33284 | 0.08497 | 0.00019956 | 1.2784 | -0.3824 | 0.10377 | 0.81767 | 0.21514 | -0.033211 | 0.79289 | 0.24935 | -0.042821 | 0.77091 | 0.28066 | -0.05235 | 1 | 1 | 1 | 8.5 | 3.68 | 24000 | 0.27174 | 0.34365 | -0.00014023 | -7.8125e-06 | 0.02188 | 2.4132e-06 | -0.00010007 | 2.0345 | 0.0021825 | 3.5281e-05 | -0.048786 | 0.00038872 | 2.2519e-05 | 1 | 0 | 0 | 1 | ; | Split HP, SEER 14, Med EER Slope, High Degrad. Coef | SH-14-MH | Split-R | HP | Med | High
21404 | 14 | 11.6 | 34678 | 0.7343 | 0.2552 | 0.03028 | 0.292 | 0.1128 | 0 | 100 | 2.0556 | -0.046414 | 0.00053256 | 0.0050607 | -1.1107e-05 | -0.00011265 | -1.0564 | 0.11951 | -0.001281 | -0.012413 | -8.8929e-06 | 0.00016636 | -1.0424 | 0.058979 | -0.00046089 | -0.006088 | 0.00015829 | -0.00010849 | 70.7914 | -1.9974 | 0.014265 | 1e-12 | 1e-12 | 1e-12 | 9.5772e-07 | 1.0519 | -0.056737 | 0.0048828 | 3.7387e-06 | 1.0799 | -0.090918 | 0.011055 | 9.109e-06 | 1.1057 | -0.12435 | 0.018613 | 0.95056 | 0.051873 | -0.0024452 | 0.92558 | 0.079928 | -0.0055407 | 0.9034 | 0.10588 | -0.0093364 | 1 | 1 | 1 | 8.2 | 3.38 | 36360 | 0.29591 | 0.12206 | 0.0099825 | -7.6389e-05 | 0.0097357 | 6.3602e-05 | -1.3558e-05 | 0.89151 | 0.0055907 | 0.00012433 | -0.013788 | 0.00017108 | -0.00018905 | 1 | 0 | 0 | 1 | ; | Split HP, SEER 14, High EER Slope, Low Degrad. Coef | SH-14-HL | Split-R | HP | High | Low
21405 | 14 | 12.19 | 23886 | 0.7306 | 0.25206 | 0.02931 | 0.219 | 0.0932 | 0 | 100 | 2.1353 | -0.05279 | 0.00056622 | 0.0069936 | -2.7161e-05 | -8.7878e-05 | -1.2037 | 0.12174 | -0.0012984 | -0.011162 | -1.4494e-05 | 0.00016767 | -1.4994 | 0.07795 | -0.00061978 | -0.0074045 | 0.0001638 | -0.00011247 | 91.9415 | -2.6268 | 0.018948 | 1e-12 | 1e-12 | 1e-12 | 2.1242e-05 | 1.1379 | -0.16819 | 0.030233 | 4.0782e-05 | 1.1692 | -0.21291 | 0.043626 | 6.7211e-05 | 1.1979 | -0.25553 | 0.057533 | 0.8768 | 0.13825 | -0.015181 | 0.8519 | 0.16981 | -0.021928 | 0.8298 | 0.19881 | -0.028946 | 1 | 1 | 1 | 8.6 | 3.52 | 24000 | 0.28439 | -0.26067 | 0.019758 | -0.00014792 | 0.012135 | 7.2586e-05 | -3.8988e-05 | 2.3651 | -0.026065 | 0.00033863 | -0.026283 | 0.0002813 | -0.0001781 | 1 | 0 | 0 | 1 | ; | Split HP, SEER 14, High EER Slope, Med Degrad. Coef | SH-14-HM | Split-R | HP | High | Med
21406 | 14 | 11.77 | 29871 | 0.7249 | 0.25693 | 0.02929 | 0.256 | 0.1082 | 0 | 100 | 2.0281 | -0.047312 | 0.00053756 | 0.0055126 | -1.6327e-05 | -0.00010175 | -0.75112 | 0.11045 | -0.0012138 | -0.012651 | -8.7024e-06 | 0.00016969 | -1.4844 | 0.071787 | -0.000554 | -0.0054032 | 0.00018632 | -0.00015815 | 73.4615 | -2.0837 | 0.014957 | 1e-12 | 1e-12 | 1e-12 | 3.3211e-05 | 1.1587 | -0.19761 | 0.038895 | 5.967e-05 | 1.1907 | -0.24463 | 0.053881 | 9.4115e-05 | 1.22 | -0.28925 | 0.069183 | 0.86019 | 0.15916 | -0.019543 | 0.83532 | 0.19148 | -0.027102 | 0.81326 | 0.22114 | -0.034833 | 1 | 1 | 1 | 8.3 | 3.42 | 32000 | 0.29408 | 0.58963 | -0.0039862 | 2.3438e-05 | 0.011473 | 6.8638e-05 | -3.5342e-05 | 0.3699 | 0.023176 | -1.3028e-05 | -0.019057 | 0.00018968 | -0.00013729 | 1 | 0 | 0 | 1 | ; | Split HP, SEER 14, High EER Slope, High Degrad. Coef | SH-14-HH | Split-R | HP | High | High
21501 | 15 | 12.7 | 35800 | 0.81 | 0.2393 | 0.03631 | 0.188 | 0.1105 | 0 | 100 | 2.1076 | -0.048102 | 0.00054453 | 0.0042147 | -4.5833e-06 | -0.00010812 | 0.11245 | 0.07598 | -0.00097109 | -0.0031148 | -3.8333e-05 | 0.00012537 | -1.1825 | 0.063945 | -0.00046016 | -0.0048318 | 0.00016083 | -0.00016163 | 38.4037 | -1.0561 | 0.0074306 | 1e-12 | 1e-12 | 1e-12 | 9.5772e-07 | 1.0519 | -0.056737 | 0.0048828 | 3.7387e-06 | 1.0799 | -0.090918 | 0.011055 | 9.109e-06 | 1.1057 | -0.12435 | 0.018613 | 0.95056 | 0.051873 | -0.0024452 | 0.92558 | 0.079928 | -0.0055407 | 0.9034 | 0.10588 | -0.0093364 | 1 | 1 | 1 | 8.8 | 3.74 | 32300 | 0.26786 | 0.42204 | 0 | 0 | 0.01019 | 4.4835e-05 | 0 | 2.1186 | 0 | 0 | -0.039322 | 0.00033023 | 0 | 1 | 0 | 0 | 1 | ; | Split HP, SEER 15, Med EER Slope, Low Degrad. Coef | SH-15-ML | Split-R | HP | Med | Low
21502 | 15 | 12.63 | 25597.9576 | 0.7695 | 0.2406 | 0.03125 | 0.219 | 0.0647 | 0 | 55 | 4.0487 | -0.10901 | 0.0011211 | 0.0060803 | 1.3354e-05 | -0.00023187 | -5.4249 | 0.26345 | -0.0025088 | -0.016551 | -3.449e-05 | 0.00030156 | -3.52 | 0.11152 | -0.00092793 | 0.0098018 | 3.6781e-05 | -7.8125e-06 | 185.8794 | -5.4286 | 0.03984 | 1e-12 | 1e-12 | 1e-12 | 7.1271e-06 | 1.0979 | -0.11402 | 0.016141 | 1.663e-05 | 1.1277 | -0.15405 | 0.026304 | 3.0936e-05 | 1.1552 | -0.1926 | 0.037377 | 0.91005 | 0.097994 | -0.0080948 | 0.88511 | 0.12799 | -0.013204 | 0.86296 | 0.15564 | -0.018779 | 1 | 1 | 1 | 8.2 | 3.44 | 21800 | 0.2912 | 0.42366 | -0.00040973 | -5.5046e-06 | 0.015659 | 4.8322e-05 | -6.4056e-05 | 1.2676 | 0.011042 | 4.4075e-05 | -0.030183 | 0.00031695 | -0.00016354 | 1 | 0 | 0 | 1 | ; | Split HP, SEER 15, Med EER Slope, Med Degrad. Coef | SH-15-MM | Split-R | HP | Med | Med
21503 | 15 | 13.01 | 29000 | 0.79 | 0.23565 | 0.03448 | 0.18 | 0.1071 | 0 | 100 | 1.7776 | -0.036891 | 0.00048594 | 0.0027071 | 8.6667e-06 | -0.00012925 | 0.75674 | 0.074072 | -0.00097656 | -0.01424 | 1.1667e-05 | 0.00014325 | -0.42968 | 0.027153 | -0.00021094 | 0.0060317 | 0.00010617 | -0.000153 | 56.439 | -1.6218 | 0.011855 | 1e-12 | 1e-12 | 1e-12 | 1.663e-05 | 1.1277 | -0.15405 | 0.026304 | 3.3211e-05 | 1.1587 | -0.19761 | 0.038895 | 5.6145e-05 | 1.1871 | -0.23924 | 0.052099 | 0.88511 | 0.12799 | -0.013204 | 0.86019 | 0.15916 | -0.019543 | 0.83808 | 0.18783 | -0.026202 | 1 | 1 | 1 | 9 | 3.56 | 26400 | 0.27601 | 0.4436 | 0 | 0 | 0.011315 | 1.1138e-05 | 0 | 1.9018 | 0 | 0 | -0.035434 | 0.00034567 | 0 | 1 | 0 | 0 | 1 | ; | Split HP, SEER 15, Med EER Slope, High Degrad. Coef | SH-15-MH | Split-R | HP | Med | High
21504 | 15 | 12.58 | 36315 | 0.7329 | 0.2392 | 0.02891 | 0.255 | 0.0747 | 0 | 100 | 2.0612 | -0.046637 | 0.00053511 | 0.0050758 | -1.1137e-05 | -0.00011317 | -1.0703 | 0.12034 | -0.00129 | -0.012499 | -8.994e-06 | 0.00016765 | -1.0306 | 0.058993 | -0.00046244 | -0.0061388 | 0.00015742 | -0.0001074 | 122.8494 | -3.54 | 0.025692 | 1e-12 | 1e-12 | 1e-12 | 3.5993e-06 | 1.0789 | -0.08972 | 0.010809 | 9.756e-06 | 1.108 | -0.12741 | 0.019366 | 1.977e-05 | 1.1349 | -0.1639 | 0.029026 | 0.92642 | 0.078973 | -0.0054175 | 0.90146 | 0.10819 | -0.0097151 | 0.87929 | 0.13516 | -0.014573 | 1 | 1 | 1 | 9.4 | 3.92 | 35280 | 0.25551 | 0.12206 | 0.0099825 | -7.6389e-05 | 0.0097357 | 6.3602e-05 | -1.3558e-05 | 0.89151 | 0.0055907 | 0.00012433 | -0.013788 | 0.00017108 | -0.00018905 | 1 | 0 | 0 | 1 | ; | Split HP, SEER 15, High EER Slope, Low Degrad. Coef | SH-15-HL | Split-R | HP | High | Low
21505 | 15 | 12.77 | 32147.447 | 0.776 | 0.23778 | 0.03111 | 0.219 | 0.0443 | 0 | 55 | 3.7929 | -0.10388 | 0.0010096 | 0.0073047 | -7.8021e-06 | -0.00015531 | -7.0875 | 0.30506 | -0.0027945 | -0.010381 | -3.7229e-05 | 0.00023812 | -3.3451 | 0.11845 | -0.00096348 | 0.0018119 | 9.5073e-05 | -4.6563e-05 | 307.2692 | -9.0491 | 0.066834 | 1e-12 | 1e-12 | 1e-12 | 9.6615e-06 | 1.1077 | -0.12697 | 0.019258 | 2.1242e-05 | 1.1379 | -0.16819 | 0.030233 | 3.813e-05 | 1.1657 | -0.20777 | 0.042019 | 0.90173 | 0.10786 | -0.0096605 | 0.8768 | 0.13825 | -0.015181 | 0.85466 | 0.16625 | -0.021118 | 1 | 1 | 1 | 9 | 3.68 | 28000 | 0.27304 | 0.53753 | -0.0012164 | 4.7619e-06 | 0.0095819 | 4.2967e-05 | -6.3776e-06 | -0.97352 | 0.0422 | 2.3555e-05 | -0.0057171 | 0.00024131 | -0.00041345 | 1 | 0 | 0 | 1 | ; | Split HP, SEER 15, High EER Slope, Med Degrad. Coef | SH-15-HM | Split-R | HP | High | Med
21506 | 15 | 13.16 | 19485 | 0.7467 | 0.2351 | 0.03079 | 0.183 | 0.0958 | 0 | 100 | 2.7476 | -0.0651 | 0.00067033 | 0.0032289 | -5.1429e-06 | -0.00010297 | -2.1391 | 0.15614 | -0.001572 | -0.014268 | -1.8155e-06 | 0.00017384 | -1.8255 | 0.080166 | -0.000616 | -0.003625 | 0.0001481 | -0.00012139 | 114.343 | -3.3449 | 0.024675 | 1e-12 | 1e-12 | 1e-12 | 4.9876e-05 | 1.1803 | -0.22911 | 0.048793 | 8.486e-05 | 1.2129 | -0.27841 | 0.065382 | 0.00012897 | 1.2428 | -0.32502 | 0.082084 | 0.84333 | 0.18094 | -0.024534 | 0.81849 | 0.21402 | -0.032911 | 0.79646 | 0.24434 | -0.04136 | 1 | 1 | 1 | 8 | 3.08 | 14946 | 0.32353 | 0.30766 | 0.0052087 | -4.133e-05 | 0.010811 | 6.5888e-05 | -3.7511e-05 | 1.0925 | -0.0017511 | 0.00014986 | -0.012437 | 0.0001764 | -0.00015483 | 1 | 0 | 0 | 1 | ; | Split HP, SEER 15, High EER Slope, High Degrad. Coef | SH-15-HH | Split-R | HP | High | High
21601 | 16 | 11.99 | 36438.8393 | 0.757 | 0.24112 | 0.03019 | 0.329 | 0.0278 | 0 | 125 | 2.2246 | -0.054631 | 0.00070208 | 0.0064348 | -4.1964e-06 | -0.00020258 | -8.4695 | 0.35367 | -0.0030751 | -0.026515 | -8.3006e-06 | 0.00034124 | -1.7844 | 0.074668 | -0.0005469 | 0.0014754 | 0.00014694 | -0.00019319 | 440.1553 | -15.6536 | 0.1364 | 2.0552 | 0.00084413 | -0.032292 | 1.7788e-13 | 0.78336 | 0.21664 | 1e-12 | 1.7788e-13 | 0.78336 | 0.21664 | 1e-12 | 1.7788e-13 | 0.78336 | 0.21664 | 1e-12 | 0.91726 | 0.091913 | -0.0091732 | 0.89341 | 0.1167 | -0.010107 | 0.87168 | 0.14307 | -0.014752 | 2 | 0.6 | 0.54718 | 8.8 | 3.7 | 32230 | 0.27109 | 0.16671 | 0.0096675 | -0.00010472 | 0.0074914 | 0.00011554 | 1.8949e-05 | 0.86245 | 0.0055091 | 0.00017596 | -0.0098178 | 0.00028531 | -0.00038879 | 2.7948 | -1.7948 | 1 | 1.7179 | ; | Split HP, SEER 16, Mfg1 EER Slope, Low Degrad. Coef | SH-16-ML | Split-TS | HP | Mfg1 | Low
21602 | 16 | 12.07 | 35271.573 | 0.7537 | 0.243 | 0.03119 | 0.292 | 0.0674 | 0 | 125 | 2.3304 | -0.059808 | 0.00075491 | 0.0082959 | -7.3006e-06 | -0.00022534 | -8.6653 | 0.35813 | -0.0031061 | -0.025606 | -1.3625e-05 | 0.00034077 | -2.0952 | 0.086363 | -0.00064074 | -0.0011169 | 0.00016045 | -0.00018175 | 192.9014 | -6.7104 | 0.058151 | 0.8062 | 0.00056386 | -0.013358 | 1.3088e-13 | 0.80201 | 0.19799 | 1e-12 | 1.3088e-13 | 0.80201 | 0.19799 | 1e-12 | 1.3088e-13 | 0.80201 | 0.19799 | 1e-12 | 0.8761 | 0.14238 | -0.018478 | 0.85261 | 0.16669 | -0.019295 | 0.82934 | 0.20107 | -0.030413 | 2 | 0.6 | 0.5616 | 8.3 | 3.54 | 31263.1 | 0.28507 | 0.16671 | 0.0096675 | -0.00010472 | 0.0074914 | 0.00011554 | 1.8949e-05 | 0.86245 | 0.0055091 | 0.00017596 | -0.0098178 | 0.00028531 | -0.00038879 | 0.37521 | 0.62479 | 0.75008 | 1 | ; | Split HP, SEER 16, Mfg1 EER Slope, High Degrad. Coef | SH-16-MH | Split-TS | HP | Mfg1 | High
21603 | 16 | 11.77 | 48500 | 0.8 | 0.24815 | 0.03351 | 0.283 | 0.0584 | 0.02 | 55 | 0.35442 | 0.0054356 | 0.00018375 | 0.0043238 | -1.4405e-06 | -0.00014788 | 1.4338 | 0.050127 | -0.00079656 | -0.013316 | -1.2929e-05 | 0.00018306 | 0.17093 | 0.0083766 | -7.375e-05 | 0.0049602 | 0.00011531 | -0.00014344 | -15.4493 | 0.44958 | -0.0027647 | 0.14937 | 0.00034337 | -0.0029145 | 1.4792e-12 | 0.7888 | 0.2112 | 1e-12 | 1.4792e-12 | 0.7888 | 0.2112 | 1e-12 | 1.4792e-12 | 0.7888 | 0.2112 | 1e-12 | 0.92043 | 0.085832 | -0.0062586 | 0.88469 | 0.12898 | -0.013673 | 0.85368 | 0.16677 | -0.020457 | 2 | 0.70154 | 0.70928 | 8.5 | 3.62 | 32400 | 0.2762 | 0.45209 | 0 | 0 | 0.010642 | 2.1602e-05 | 0 | 1.9994 | 0 | 0 | -0.036318 | 0.00032028 | 0 | 0.40588 | 0.59412 | 0.82268 | 1 | ; | Split HP, SEER 16, Mfg2 EER Slope, Low Degrad. Coef | SH-16-ML | Split-TS | HP | Mfg2 | Low
21604 | 16 | 12.06 | 36000 | 0.78 | 0.2361 | 0.03333 | 0.321 | 0.0991 | 0.02 | 55 | -0.10743 | 0.019027 | 7.3125e-05 | 0.0047358 | -9.7381e-06 | -0.00013475 | 1.5358 | 0.044457 | -0.00073937 | -0.010838 | -1.6131e-05 | 0.00015394 | 0.33576 | -0.010139 | 0.00014812 | 0.013219 | 0.0001262 | -0.00026963 | -25.5465 | 0.74809 | -0.006335 | 0.11043 | -0.00050819 | -0.00016379 | 1.7802e-13 | 0.66136 | 0.33864 | 1e-12 | 1.7802e-13 | 0.66136 | 0.33864 | 1e-12 | 1.7802e-13 | 0.66136 | 0.33864 | 1e-12 | 0.7824 | 0.26175 | -0.044152 | 0.74988 | 0.30909 | -0.058975 | 0.7213 | 0.35187 | -0.073172 | 2 | 0.75 | 0.76731 | 8.4 | 3.48 | 33000 | 0.28731 | 0.4614 | 0 | 0 | 0.010763 | 1.4826e-05 | 0 | 2.0036 | 0 | 0 | -0.037453 | 0.00034253 | 0 | -1.17 | 2.17 | 0.45749 | 1 | ; | Split HP, SEER 16, Mfg2 EER Slope, Med Degrad. Coef | SH-16-MM | Split-TS | HP | Mfg2 | Med
21605 | 16 | 12.59 | 37400 | 0.77 | 0.23054 | 0.03209 | 0.292 | 0.0879 | 0.02 | 55 | 1.2198 | -0.014593 | 0.00030219 | 0.0013048 | 7.381e-07 | -0.00011456 | 3.2656 | -0.0025328 | -0.00040406 | -0.013523 | -4.9762e-06 | 0.00016456 | -0.56784 | 0.012601 | -1.1563e-05 | 0.015369 | 0.00011624 | -0.00027238 | -50.3926 | 1.7535 | -0.014079 | -0.0818 | 0.00038899 | 0.00021556 | 1.8811e-12 | 0.79424 | 0.20576 | 1e-12 | 1.8811e-12 | 0.79424 | 0.20576 | 1e-12 | 1.8811e-12 | 0.79424 | 0.20576 | 1e-12 | 0.74822 | 0.31122 | -0.059433 | 0.7159 | 0.36019 | -0.076091 | 0.68818 | 0.40205 | -0.090229 | 2 | 0.75 | 0.75943 | 8.9 | 3.58 | 32800 | 0.27928 | 0.4597 | 0 | 0 | 0.010723 | 1.644e-05 | 0 | 1.9926 | 0 | 0 | -0.036405 | 0.00032525 | 0 | -1.5901 | 2.5901 | 0.35247 | 1 | ; | Split HP, SEER 16, Mfg2 EER Slope, High Degrad. Coef | SH-16-MH | Split-TS | HP | Mfg2 | High
21606 | 16 | 11.06 | 36394.55 | 0.7664 | 0.2656 | 0.03297 | 0.292 | 0.1206 | 0 | 55 | 1.0888 | -0.021486 | 0.00038932 | 0.0077865 | -1.3542e-05 | -0.00015938 | -5.6632 | 0.26803 | -0.0024789 | -0.017495 | -1.4625e-05 | 0.00025566 | -2.4427 | 0.05085 | -0.00021159 | 0.032425 | 5.3417e-05 | -0.00040485 | 91.2317 | -2.8559 | 0.022741 | 0.14232 | 0.00013156 | -0.0024636 | 3.8987e-14 | 0.72779 | 0.27221 | 1e-12 | 3.8987e-14 | 0.72779 | 0.27221 | 1e-12 | 3.8987e-14 | 0.72779 | 0.27221 | 1e-12 | 0.90126 | 0.1082 | -0.0094506 | 0.8517 | 0.16928 | -0.020979 | 0.80802 | 0.22664 | -0.034657 | 2 | 0.5 | 0.52022 | 8.15 | 2.92 | 31900 | 0.34237 | 0.42851 | -0.00097813 | 5.0142e-15 | 0.015309 | 3.9018e-05 | -5.0381e-05 | 1.366 | 0.0034688 | 6.2209e-05 | -0.02346 | 0.00022502 | -9.3635e-05 | 0.14739 | 0.85261 | 0.5737 | 1 | ; | Split HP, SEER 16, Mfg4 EER Slope, Low Degrad. Coef | SH-16-ML | Split-TS | HP | Mfg4 | Low
21607 | 16 | 11.28 | 36394.55 | 0.7664 | 0.2599 | 0.03297 | 0.292 | 0.1206 | 0 | 55 | 1.315 | -0.028179 | 0.00043346 | 0.0079195 | -1.5917e-05 | -0.00015421 | -5.6632 | 0.26803 | -0.0024789 | -0.017495 | -1.4625e-05 | 0.00025566 | -2.7056 | 0.059513 | -0.00028021 | 0.031672 | 5.425e-05 | -0.00039629 | 91.2317 | -2.8559 | 0.022741 | 0.14232 | 0.00013156 | -0.0024636 | 5.4216e-15 | 0.7874 | 0.2126 | 1e-12 | 5.4216e-15 | 0.7874 | 0.2126 | 1e-12 | 5.4216e-15 | 0.7874 | 0.2126 | 1e-12 | 0.90933 | 0.098662 | -0.0079892 | 0.85972 | 0.15911 | -0.018821 | 0.81596 | 0.21597 | -0.031932 | 2 | 0.5 | 0.52022 | 8.2 | 2.94 | 31900 | 0.33595 | 0.42851 | -0.00097813 | 5.0142e-15 | 0.015309 | 3.9018e-05 | -5.0381e-05 | 1.2159 | 0.0073246 | 3.7571e-05 | -0.023236 | 0.00022478 | -9.6407e-05 | -0.014539 | 1.0145 | 0.49273 | 1 | ; | Split HP, SEER 16, Mfg4 EER Slope, Med Degrad. Coef | SH-16-MM | Split-TS | HP | Mfg4 | Med
21608 | 16 | 11.64 | 33094.55 | 0.8157 | 0.2465 | 0.03626 | 0.292 | 0.0974 | 0 | 55 | 2.5028 | -0.058825 | 0.00065365 | 0.0052358 | -5.375e-06 | -0.00014841 | -7.0167 | 0.31248 | -0.0028143 | -0.020423 | -2.9167e-06 | 0.00026407 | -4.0027 | 0.094173 | -0.00054362 | 0.032364 | 5.4917e-05 | -0.00038285 | 145.8186 | -4.5109 | 0.035048 | 0.19204 | 4.6001e-05 | -0.0029194 | 8.2971e-14 | 0.82978 | 0.17022 | 1e-12 | 8.2971e-14 | 0.82978 | 0.17022 | 1e-12 | 8.2971e-14 | 0.82978 | 0.17022 | 1e-12 | 0.74016 | 0.32219 | -0.062346 | 0.69621 | 0.38776 | -0.083972 | 0.65783 | 0.44728 | -0.10511 | 2 | 0.54167 | 0.55411 | 8.25 | 3.14 | 27500 | 0.30283 | 0.32502 | 0.00035532 | -9.697e-06 | 0.018603 | 2.2135e-05 | -6.8571e-05 | 1.5833 | 0.0078304 | 6.4245e-05 | -0.038504 | 0.00041474 | -0.00016799 | 0.85185 | 0.14815 | 0.9321 | 1 | ; | Split HP, SEER 16, Mfg4 EER Slope, High Degrad. Coef | SH-16-MH | Split-TS | HP | Mfg4 | High
21701 | 17 | 12.62 | 36832.093 | 0.7543 | 0.228 | 0.02987 | 0.328 | 0.0245 | 0 | 125 | 2.3241 | -0.059586 | 0.00075278 | 0.0082842 | -7.247e-06 | -0.00022508 | -8.6411 | 0.35723 | -0.0030982 | -0.025533 | -1.3625e-05 | 0.0003399 | -2.0898 | 0.086033 | -0.00063852 | -0.0011284 | 0.00016062 | -0.00018075 | 549.2968 | -19.1349 | 0.16565 | 2.286 | 0.0016515 | -0.03801 | -1.0307e-13 | 0.7937 | 0.2063 | 1e-12 | -1.0307e-13 | 0.7937 | 0.2063 | 1e-12 | -1.0307e-13 | 0.7937 | 0.2063 | 1e-12 | 0.92686 | 0.076963 | -0.0038279 | 0.9024 | 0.10349 | -0.0058866 | 0.87994 | 0.1319 | -0.011832 | 2 | 0.6 | 0.55502 | 9.5 | 3.5 | 32530 | 0.28223 | 0.61532 | 0.0014468 | -5.6871e-05 | 0.0024021 | -0.00011813 | 0.00021584 | 0.99178 | -0.00091762 | 0.0001666 | -0.005442 | 0.00028275 | -0.00033821 | 0.45499 | 0.54501 | 0.78199 | 1 | ; | Split HP, SEER 17, Mfg1 EER Slope, Med Degrad. Coef | SH-17-MM | Split-TS | HP | Mfg1 | Med
21702 | 17 | 12.75 | 36600 | 0.8 | 0.24473 | 0.03292 | 0.162 | 0.0418 | 0.02 | 55 | 0.82596 | -0.010186 | 0.00030969 | 0.0067073 | -8.0357e-06 | -0.00017256 | 2.4113 | 0.021775 | -0.00059531 | -0.012637 | -1.9988e-05 | 0.00018588 | -0.65604 | 0.02847 | -0.00020188 | 0.0053915 | 0.00012189 | -0.00015044 | -37.6282 | 0.78292 | -0.0023655 | 0.42823 | 0.00051917 | -0.0076317 | 1.61e-12 | 0.84038 | 0.15962 | 1e-12 | 1.61e-12 | 0.84038 | 0.15962 | 1e-12 | 1.61e-12 | 0.84038 | 0.15962 | 1e-12 | 0.90428 | 0.10378 | -0.0080564 | 0.86878 | 0.14763 | -0.016407 | 0.83759 | 0.18715 | -0.024745 | 2 | 0.70124 | 0.70492 | 9 | 3.72 | 32800 | 0.26877 | 0.4597 | 0 | 0 | 0.010723 | 1.644e-05 | 0 | 1.9663 | 0 | 0 | -0.035053 | 0.00030839 | 0 | 0.5979 | 0.4021 | 0.87987 | 1 | ; | Split HP, SEER 17, Mfg2 EER Slope, Med Degrad. Coef | SH-17-MM | Split-TS | HP | Mfg2 | Med
21703 | 17 | 12.24 | 33094.55 | 0.8157 | 0.2327 | 0.03626 | 0.292 | 0.0974 | 0 | 55 | 1.9603 | -0.044331 | 0.00055352 | 0.0061708 | -7.5417e-06 | -0.00015601 | -7.1054 | 0.31213 | -0.0028151 | -0.018473 | -1.4125e-05 | 0.000269 | -3.4493 | 0.076764 | -0.00040221 | 0.033132 | 5.8458e-05 | -0.00040274 | 145.8186 | -4.5109 | 0.035048 | 0.19204 | 4.6001e-05 | -0.0029194 | 3.7031e-13 | 0.88923 | 0.11077 | 1e-12 | 3.7031e-13 | 0.88923 | 0.11077 | 1e-12 | 3.7031e-13 | 0.88923 | 0.11077 | 1e-12 | 0.82423 | 0.20506 | -0.029294 | 0.77911 | 0.26649 | -0.045602 | 0.73948 | 0.32313 | -0.062616 | 2 | 0.54167 | 0.5504 | 8.75 | 3.24 | 29000 | 0.29893 | 0.33196 | 0.00023547 | -9.1954e-06 | 0.018417 | 2.1815e-05 | -6.601e-05 | 1.5515 | 0.0085936 | 6.0385e-05 | -0.038365 | 0.00041659 | -0.00017206 | 1.3124 | -0.31235 | 1 | 1.1432 | ; | Split HP, SEER 17, Mfg4 EER Slope, Low Degrad. Coef | SH-17-ML | Split-TS | HP | Mfg4 | Low
21704 | 17 | 12.52 | 33494.55 | 0.8059 | 0.2273 | 0.03583 | 0.292 | 0.1069 | 0 | 55 | 1.9306 | -0.042878 | 0.00054362 | 0.0058455 | -5.375e-06 | -0.00015788 | -7.0167 | 0.31248 | -0.0028143 | -0.020423 | -2.9167e-06 | 0.00026407 | -3.4426 | 0.075943 | -0.00040091 | 0.033477 | 5.4458e-05 | -0.00039554 | 131.1221 | -4.0736 | 0.031825 | 0.18215 | 4.4339e-05 | -0.0027898 | -2.6651e-13 | 0.93877 | 0.061225 | 1e-12 | -2.6651e-13 | 0.93877 | 0.061225 | 1e-12 | -2.6651e-13 | 0.93877 | 0.061225 | 1e-12 | 0.80754 | 0.22741 | -0.034953 | 0.76261 | 0.28981 | -0.05242 | 0.72319 | 0.34717 | -0.070359 | 2 | 0.54167 | 0.55411 | 8.55 | 3.26 | 28700 | 0.29849 | 0.42749 | -0.0024382 | 9.2915e-06 | 0.018525 | 2.1765e-05 | -6.7198e-05 | 1.3028 | 0.015594 | 1.2226e-05 | -0.038766 | 0.00041655 | -0.0001679 | 0.85266 | 0.14734 | 0.93247 | 1 | ; | Split HP, SEER 17, Mfg4 EER Slope, High Degrad. Coef | SH-17-MH | Split-TS | HP | Mfg4 | High
21801 | 18 | 12.88 | 37400 | 0.8 | 0.22694 | 0.0357 | 0.247 | 0.1162 | 0.02 | 55 | 0.42255 | 0.0061091 | 0.00016281 | 0.0028881 | -1.4286e-07 | -0.00013131 | 1.5143 | 0.047518 | -0.00076906 | -0.014273 | -7.9405e-06 | 0.00018569 | -0.42462 | 0.010239 | -1.1875e-05 | 0.014283 | 0.00011125 | -0.0002465 | -29.6457 | 0.91127 | -0.0053472 | 0.089564 | 0.00065253 | -0.0032684 | 2.1372e-15 | 0.79014 | 0.20986 | 1e-12 | 2.1372e-15 | 0.79014 | 0.20986 | 1e-12 | 2.1372e-15 | 0.79014 | 0.20986 | 1e-12 | 0.90184 | 0.10813 | -0.0099711 | 0.86532 | 0.15209 | -0.017409 | 0.83269 | 0.19452 | -0.027212 | 2 | 0.67416 | 0.72553 | 8.45 | 3.32 | 32000 | 0.3012 | 0.46708 | 0 | 0 | 0.010842 | 1.0559e-05 | 0 | 1.9287 | 0 | 0 | -0.034642 | 0.00031664 | 0 | -1.0611 | 2.0611 | 0.3284 | 1 | ; | Split HP, SEER 18, Mfg2 EER Slope, Low Degrad. Coef | SH-18-LL | Split-TS | HP | Mfg2 | Low
21802 | 18 | 12.97 | 36400 | 0.78 | 0.23062 | 0.03365 | 0.224 | 0.1077 | 0.02 | 55 | 0.058225 | 0.015208 | 0.0001 | 0.0040643 | -6.7857e-06 | -0.00013369 | 2.2339 | 0.025405 | -0.00060125 | -0.01231 | -1.1286e-05 | 0.0001625 | 0.5056 | -0.01334 | 0.0001625 | 0.012097 | 0.00012924 | -0.00026031 | -22.1414 | 0.57583 | -0.0037689 | 0.14118 | -0.00013399 | -0.0016846 | -1.0127e-12 | 0.80283 | 0.19717 | 1e-12 | -1.0127e-12 | 0.80283 | 0.19717 | 1e-12 | -1.0127e-12 | 0.80283 | 0.19717 | 1e-12 | 0.93697 | 0.067544 | -0.0045174 | 0.90244 | 0.10697 | -0.0094055 | 0.87165 | 0.14409 | -0.015742 | 2 | 0.71429 | 0.74387 | 9.2 | 3.66 | 32600 | 0.27063 | 0.45795 | 0 | 0 | 0.010708 | 1.7545e-05 | 0 | 1.9701 | 0 | 0 | -0.035421 | 0.00031449 | 0 | -0.93456 | 1.9346 | 0.44727 | 1 | ; | Split HP, SEER 18, Mfg2 EER Slope, Median Degrad. Coef | SH-18-LM | Split-TS | HP | Mfg2 | Median
21803 | 18 | 13.17 | 38500 | 0.8 | 0.22458 | 0.03468 | 0.232 | 0.0902 | 0.02 | 55 | -0.18967 | 0.023847 | 2.625e-05 | 0.0037157 | -5e-06 | -0.000131 | 2.8608 | 0.010002 | -0.00053469 | -0.015908 | -2.2512e-05 | 0.00024881 | 0.55704 | -0.019414 | 0.00021656 | 0.014213 | 0.00011532 | -0.00025444 | -45.2823 | 1.6172 | -0.012281 | -0.057144 | 0.00089391 | -0.0015053 | -8.9929e-13 | 0.87647 | 0.12353 | 1e-12 | -8.9929e-13 | 0.87647 | 0.12353 | 1e-12 | -8.9929e-13 | 0.87647 | 0.12353 | 1e-12 | 0.90952 | 0.099575 | -0.0090935 | 0.87258 | 0.14427 | -0.016851 | 0.84013 | 0.18462 | -0.024744 | 2 | 0.67041 | 0.7013 | 8.75 | 3.5 | 32800 | 0.28573 | 0.4597 | 0 | 0 | 0.010723 | 1.644e-05 | 0 | 2.0078 | 0 | 0 | -0.037186 | 0.00033499 | 0 | -0.40968 | 1.4097 | 0.53539 | 1 | ; | Split HP, SEER 18, Mfg2 EER Slope, High Degrad. Coef | SH-18-LH | Split-TS | HP | Mfg2 | High
21804 | 18 | 12.4 | 38719.4685 | 0.7986 | 0.22191 | 0.03357 | 0.365 | 0.0636 | 0 | 55 | -0.14026 | 0.018157 | 6.7318e-05 | 0.0051715 | -1.6125e-05 | -0.00011378 | -5.5946 | 0.26628 | -0.0024632 | -0.017904 | -1.1917e-05 | 0.00025438 | -1.2625 | 0.0018708 | 0.00026276 | 0.042111 | 6.425e-05 | -0.00056916 | 138.9119 | -4.3498 | 0.034136 | 0.25788 | 6.2406e-05 | -0.0038922 | -5.5141e-15 | 0.67778 | 0.32222 | 1e-12 | -5.5141e-15 | 0.67778 | 0.32222 | 1e-12 | -5.5141e-15 | 0.67778 | 0.32222 | 1e-12 | 0.79893 | 0.23894 | -0.037876 | 0.75394 | 0.30192 | -0.055863 | 0.71452 | 0.35965 | -0.07417 | 2 | 0.53846 | 0.51244 | 8.4 | 3.18 | 32840 | 0.31386 | 0.42674 | -0.00099363 | 4.0601e-07 | 0.015407 | 3.9069e-05 | -5.1549e-05 | 1.2963 | 0.0053686 | 4.9004e-05 | -0.023509 | 0.00022483 | -9.2398e-05 | 1.8505 | -0.85053 | 1 | 1.3926 | ; | Split HP, SEER 18, Mfg4 EER Slope, Median Degrad. Coef | SH-18-TM | Split-TS | HP | Mfg4 | Median
; Other Special/Unique Equipment Items
11799 | 17.4 | 15.1 | 43075 | 0.7025 | 0.1813 | 0.02664 | 0.256 | 0.1007 | 0 | 55 | 0.50263 | 0.0013442 | 0.00021326 | -0.00084022 | 6.558e-05 | -0.00017031 | 1.7262 | 0.022107 | -0.00039474 | 0.00091834 | 6.012e-05 | -0.00016772 | 1.8778 | -0.045256 | 0.00016417 | 0.018079 | -0.00014088 | 0.00016987 | 56.6744 | -1.6656 | 0.012457 | 1e-12 | 1e-12 | 1e-12 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0.97 | 0.03 | 0 | 0.94 | 0.06 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | ; | Split EvapAC, SEER 17.4, Low EER Slope, Neg Degrad. Coef | SA-17-FN | Split-TS | EvapAC | Low | Neg
; ERROR - No Match Found
-99 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1
Note on A98: SAC 3/20/06: Was previously the only "default" 14 SEER equipment (across all climate zones)
Note on A99: SAC 3/20/06: Default 14 SEER equip for climate zones 1-7 ONLY.
Note on A100: SAC 3/20/06: Default 14 SEER equip for climate zones 8-16 ONLY.
Note on C98: SAC 3/20/06: Modified per JJH/PRC conference call
Note on P27: SAC 3/22/05: Value NOT looked-up from this table, but set to 0 all the time for DEER