## Key
2008 DEER Update
Refrigerant Charge Adjustments
October 4, 2008 - kjm
Table Description
RCA Data: Raw data from field measurements
Note that only six commercial rooftop units are included in the sample
Graph TXV vs non-TXV: Graphs of AC performance change for units with and without TXVs
DOE-2.2 Performance Inputs: Graphs and resolution of all units into DOE-2.2 performance inputs
Includes tables of modifiers for DOE-2 keywords
See implementation notes for DEER calculation/simulation procedure

## RCA Data
[11 empty] | Comp-kw/ Overall-kW | CF-kW/ Overall-kW
[11 empty] | 0.92 | 0.08
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 |  |  | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 |  | 36 | 37 |  | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47
Site | Status | Tons | Factory Oz. | Refrig. Adj. Oz. | % Adjust |  | EER | Airflow CFM | Comp&Cond kW | Fan kW | Comp kW | Cond kW | Sup. DB | Sup. WB | Ret. DB | Ret. WB | ODBT | Tot. kBtuh | Sens. kBtuh | Lat. kBtuh | Vintage | Exp Device | Refrig. | Supply RH | Return RH | CF W/Btuh | d Comp Kw fraction | d Cap fraction | d Sen Cap fraction | d Charge fraction | d net Comp fraction | new run fraction | new total kw for same load | % overall energy impact | Cooling-Capacity base fraction | Cool-sh-cap base fraction | Clg-eir - base fraction (comp&cond fan combined) | Clg-eir - base fraction (compressor only) | Eff fraction based on EER | EIR (Based on comp&cond fan energy combined) | EIR (Compressor energy only) | Eff Fraction based on EER | Diffference |  | Residential | Site | d Charge fraction | d Cap fraction | d Sen Cap fraction | % overall energy impact | Clg-eir - base fraction (comp&cond fan combined) | Clg-eir - base fraction (compressor only)
1 | Pre | 4 | 140 | -56 | 40% | -40% | 10.2156 | 1250 | 3.3 | 0.66 | 3.0568 | 0.2432 | 52.45 | 49.34 | 78.6 | 62.98 | 80 | 40.4538 | 34.2078 | 6.246 | New | TXV | R410a | 80.71% | 41.81% | 0.0060118 | 0.085526 | -0.17346 | -0.088203 | 0.4 | -0.0088182 | 0.91895 | 3.4001 | -15.13% | 0.82654 | 0.9118 | 1.3133 | 1.3223 | 0.76489 | 0.26373 | 0.24429 | 0.76489 | 41.76% |  | 0 | 1 | -0.4 | 0.82654 | 0.9118 | -0.15132 | 1.3133 | 1.3223
| Post |  |  |  |  | #DIV/0! | 13.3557 | 1250 | 3.04 | 0.66 | 2.7968 | 0.2432 | 49.5818 | 46.4636 | 78.4273 | 63.2 | 80 | 49.4161 | 37.7347 | 11.6813 |  | TXV | R410a | 79.59% | 42.93% | 0.0049215 |  | 0.22154 | 0.1031 | [10 empty] | 0.20081 | 0.18474 |  |  |  | 2 | 2 | 0.18 | 0.86942 | 0.9362 | -0.04707 | 1.1322 | 1.1307
2 | Pre | 3 | 100 | 18 | 18% | 18% | 10.5424 | 872 | 2.52 | 0.54 | 2.3152 | 0.2048 | 49.6 | 47.1333 | 77.3231 | 62.8077 | 82 | 32.2598 | 25.3518 | 6.9079 | New | TXV | R22 | 83.76% | 44.49% | 0.0063485 | -0.015625 | -0.13058 | -0.063799 | 0.18 | 0.0011422 | 0.94003 | 2.9141 | -4.707% | 0.86942 | 0.9362 | 1.1322 | 1.1307 | 0.87426 | 0.2522 | 0.2317 | 0.87426 | 22.78% |  | 4 | 5 | 0.16 | 0.87425 | 0.88484 | -0.094011 | 1.1309 | 1.1298
| Post |  |  |  |  | #DIV/0! | 12.0587 | 872 | 2.56 | 0.54 | 2.3552 | 0.2048 | 47.375 | 44.875 | 77.125 | 63.1 | 82 | 37.382 | 27.2051 | 10.1769 |  | TXV | R22 | 82.82% | 45.97% | 0.0054786 | [13 empty] | 0.22275 | 0.20493 |  |  |  | 6 | 6 | -0.78021 | 0.87971 | 0.92443 | -0.36397 | 1.5379 | 1.5728
5 | Pre | 3.5 | 100 | 16 | 16% | 16% | 10.424 | 1190 | 2.629 | 0.581 | 2.4163 | 0.21272 | 61.35 | 51.685 | 74.5875 | 62.7325 | 79 | 33.4611 | 16.5892 | 16.8719 | New | TXV | R410a | 51.57% | 51.85% | 0.0063572 | -0.011282 | -0.12575 | -0.11516 | 0.16 | 0.001644 | 0.89673 | 2.9054 | -9.401% | 0.87425 | 0.88484 | 1.1309 | 1.1298 | 0.87589 | 0.25315 | 0.23267 | 0.87589 | 22.55% |  | 8 | 7 | 0.11023 | 0.9166 | 0.94394 | -0.041996 | 1.0763 | 1.075
| Post |  |  |  |  | #DIV/0! | 11.901 | 1190 | 2.659 | 0.581 | 2.4463 | 0.21272 | 59.14 | 49.475 | 74.295 | 62.44 | 79 | 38.5593 | 19.0064 | 19.5529 |  | TXV | R410a | 49.79% | 51.67% | 0.0055167 | [13 empty] | 0.22384 | 0.20594 |  |  |  | 10 | 9 | 0.15 | 0.89564 | 0.92413 | -0.13813 | 1.2197 | 1.2287
6 | Pre | 2.5 | 96 | -74.9 | 78.02% | -78.02% | 7.8583 | 910 | 3.22 | 0.48 | 3.0296 | 0.1904 | 58.72 | 53.42 | 78.64 | 65.81 | 90 | 29.0756 | 18.9109 | 10.1648 | New | TXV | R410a | 71.12% | 50.89% | 0.0065484 | 0.35294 | -0.12029 | -0.075574 | 0.78021 | -0.031354 | 0.92974 | 2.659 | -36.4% | 0.87971 | 0.92443 | 1.5379 | 1.5728 | 0.67542 | 0.35781 | 0.33666 | 0.67542 | 56.08% |  | 12 | 10 | 0.086 | 0.9111 | 0.94329 | -0.027928 | 1.0632 | 1.0602
| Post |  |  |  |  | #DIV/0! | 11.6347 | 910 | 2.38 | 0.48 | 2.1896 | 0.1904 | 56.91 | 51.6 | 78.6 | 65.88 | 90 | 33.2753 | 20.5908 | 12.6845 |  | TXV | R410a | 70.18% | 51.23% | 0.005722 | [13 empty] | 0.23266 | 0.21405 |  |  |  | 14 | 11 | 0.34 | 0.7126 | 0.80643 | -0.11154 | 1.3156 | 1.308
7 | Pre | 5 | 176 | 19.4 | 11.02% | 11.02% | 10.8047 | 1750 | 4.39 | 0.96 | 4.034 | 0.356 | 46.91 | 45.31 | 69.84 | 59.64 | 88 | 57.8049 | 42.6981 | 15.1068 | New | TXV | R22 | 88.81% | 55.17% | 0.0061586 | -0.013483 | -0.083397 | -0.056063 | 0.11023 | 0.00086226 | 0.94691 | 5.1228 | -4.2% | 0.9166 | 0.94394 | 1.0763 | 1.075 | 0.92252 | 0.2453 | 0.2254 | 0.92252 | 14.29% |  | 16 | 15 | -0.30971 | 0.89639 | 0.94145 | -0.26927 | 1.3984 | 1.4231
| Post |  |  |  |  | #DIV/0! | 11.7121 | 1750 | 4.45 | 0.96 | 4.094 | 0.356 | 45.33 | 43.73 | 69.72 | 59.56 | 88 | 63.3624 | 45.4287 | 17.9337 |  | TXV | R22 | 88.45% | 55.26% | 0.0056185 | [13 empty] | 0.22791 | 0.20968 |  |  |  | 18 | 16 | -0.30189 | 0.872 | 0.90016 | -0.19707 | 1.2933 | 1.306
9 | Pre | 4 | 170 | 25.5 | 15% | 15% | 10.3111 | 1350 | 3.3943 | 1.14 | 3.1457 | 0.24857 | 51.0857 | 49.4647 | 74.63 | 63.607 | 86 | 46.7537 | 33.4396 | 13.3141 | New | TXV | R22 | 89.55% | 54.88% | 0.0053166 | 0.092414 | -0.10436 | -0.075875 | 0.15 | -0.0084704 | 0.92948 | 3.9476 | -13.81% | 0.89564 | 0.92413 | 1.2197 | 1.2287 | 0.83169 | 0.22875 | 0.21199 | 0.83169 | 31.81% |  | 20 | 14 | -0.07 | 0.95314 | 0.96369 | -0.066615 | 1.0886 | 1.092
| Post |  |  |  |  | #DIV/0! | 12.3978 | 1350 | 3.1071 | 1.14 | 2.8586 | 0.24857 | 48.6286 | 47.0043 | 74.3071 | 63.1971 | 86 | 52.6551 | 36.5046 | 16.1505 |  | TXV | R22 | 89.02% | 54.38% | 0.0047207 | [13 empty] | 0.18754 | 0.17254 |  |  |  | 22 | 20 | 0.38 | 0.81925 | 0.88406 | -0.046339 | 1.142 | 1.1351
10 | Pre | 5 | 200 | 17.2 | 8.6% | 8.6% | 10.4289 | 1451 | 4.02 | 0.9 | 3.688 | 0.332 | 53.2 | 50.9 | 77.9 | 65.1 | 95 | 51.3102 | 37.46 | 13.8501 | New | TXV | R22 | 85.82% | 50.55% | 0.0064705 | -0.031325 | -0.088904 | -0.056714 | 0.086 | 0.0020378 | 0.94633 | 4.779 | -2.793% | 0.9111 | 0.94329 | 1.0632 | 1.0602 | 0.93022 | 0.25229 | 0.23146 | 0.93022 | 12.51% |  | 24 | 19 | -0.15 | 0.92898 | 0.95376 | -0.098552 | 1.1513 | 1.1578
| Post |  |  |  |  | #DIV/0! | 11.2112 | 1451 | 4.15 | 0.9 | 3.818 | 0.332 | 51.5 | 49.2 | 77.8 | 65 | 95 | 56.6167 | 39.897 | 16.7198 |  | TXV | R22 | 85.37% | 50.49% | 0.005864 | [13 empty] | 0.2373 | 0.21831 |  |  |  | 26 | 16 | 0.07 | 0.93488 | 0.95271 | -0.048655 | 1.0741 | 1.0745
11 | Pre | 3 | 150 | 51 | 34% | 34% | 9.0441 | 1050 | 2.4 | 0.6 | 2.1952 | 0.2048 | 62.4 | 60 | 79.4 | 69.3 | 95 | 27.1324 | 18.5251 | 8.6073 | New | TXV | R22 | 87.31% | 60.61% | 0.0075482 | -0.0625 | -0.2874 | -0.19357 | 0.34 | 0.01666 | 0.83782 | 2.6475 | -11.15% | 0.7126 | 0.80643 | 1.3156 | 1.308 | 0.73467 | 0.28071 | 0.25676 | 0.73467 | 44.16% |  | 28 | 17 | -0.14 | 0.92976 | 0.95755 | -0.043053 | 1.0785 | 1.0788
| Post |  |  |  |  | #DIV/0! | 12.3105 | 1050 | 2.56 | 0.6 | 2.3552 | 0.2048 | 57.4 | 55 | 78.9 | 68.7 | 95 | 38.9013 | 23.4632 | 15.4381 |  | TXV | R22 | 86.26% | 60.03% | 0.0052646 | [13 empty] | 0.21337 | 0.1963 |  |  |  | 30 | 21 | -0.13 | 0.91219 | 0.93363 | -0.080229 | 1.1209 | 1.123
15 | Pre | 4 | 103 | -31.9 | 30.97% | -30.97% | 7.121 | 1164 | 5.0285 | 0.81486 | 4.7078 | 0.3207 | 53.8 | 53.7 | 79.9 | 67.5 | 87 | 41.6108 | 30.3636 | 11.2471 | Old | TXV | R22 | 93.33% | 53.02% | 0.0077071 | 0.2544 | -0.10361 | -0.05855 | 0.30971 | -0.017271 | 0.94469 | 4.5473 | -26.93% | 0.89639 | 0.94145 | 1.3984 | 1.4231 | 0.73333 | 0.38661 | 0.36195 | 0.73333 | 47.56% |  | 32 | 22 | 0.17 | 0.88747 | 0.96937 | 0.04761 | 1.0302 | 1.0218
| Post |  |  |  |  | #DIV/0! | 9.7105 | 1164 | 4.0087 | 0.80479 | 3.688 | 0.3207 | 53 | 51.9 | 79.8 | 67.5 | 87 | 46.7416 | 32.4249 | 14.3167 |  | TXV | R22 | 93.12% | 53.3% | 0.0068611 | [13 empty] | 0.27646 | 0.25435 |  |  |  | 34 | 23 | -0.09 | 0.90825 | 0.90621 | -0.10727 | 1.1283 | 1.1307
16 | Pre | 3 | 53 | -16 | 30.19% | -30.19% | 6.3756 | 1077 | 4.441 | 0.794 | 4.126 | 0.31504 | 46.4 | 45.15 | 65.2 | 58.5 | 70 | 33.3764 | 21.7227 | 11.6538 | Old | TXV | R22 | 91.14% | 67.45% | 0.009439 | 0.12773 | -0.128 | -0.09984 | 0.30189 | -0.015934 | 0.90922 | 4.3024 | -19.71% | 0.872 | 0.90016 | 1.2933 | 1.306 | 0.78011 | 0.42002 | 0.39023 | 0.78011 | 39.68% |  | 36 | 24 | -0.1 | 0.91881 | 0.94164 | -0.066839 | 1.1029 | 1.1042
| Post |  |  |  |  | #DIV/0! | 8.1727 | 1077 | 3.938 | 0.794 | 3.623 | 0.31504 | 43.96 | 42.71 | 65.1 | 58.4 | 70 | 38.6734 | 24.4326 | 14.2408 |  | TXV | R22 | 90.68% | 67.4% | 0.0081462 | [13 empty] | 0.32478 | 0.2988 |  |  |  | 38 | 25 | 0.27 | 0.8618 | 0.90962 | -0.040141 | 1.1004 | 1.0952
14 | Pre | 3.5 | 130 | -9.1 | 7% | -7% | 9.5695 | 1745 | 4.97 | 0.91 | 4.5868 | 0.3832 | 52.6 | 51.586 | 75.1 | 64.5 | 91 | 56.2685 | 41.2376 | 15.0309 | Old | non-TXV | R22 | 93.6% | 56.69% | 0.0068102 | 0.037578 | -0.046858 | -0.036308 | 0.07 | -0.0015224 | 0.96496 | 5.5003 | -6.661% | 0.95314 | 0.96369 | 1.0886 | 1.092 | 0.92158 | 0.28569 | 0.26366 | 0.92158 | 15.34% |  | 40 | 26 | -0.29 | 0.84292 | 0.89475 | -0.14801 | 1.2569 | 1.263
| Post |  |  |  |  | #DIV/0! | 10.3837 | 1745 | 4.79 | 0.91 | 4.4068 | 0.3832 | 51.56 | 50.5467 | 74.96 | 64.24 | 91 | 59.1874 | 42.9082 | 16.2791 |  | non-TXV | R22 | 93.49% | 56.17% | 0.0064744 | [13 empty] | 0.26244 | 0.24145 |  |  |  | 42 | 27 | 0.06 | 0.88127 | 0.92235 | -0.088744 | 1.1574 | 1.1594
20 | Pre | 4 | 112 | 42.56 | 38% | 38% | 8.523 | 1175 | 4.5071 | 0.576 | 4.1217 | 0.3854 | 55.1429 | 52.3286 | 81.4059 | 66.8429 | 90 | 43.3231 | 32.0233 | 11.2997 | Old | non-TXV | R22 | 83.32% | 46.93% | 0.008896 | -0.06444 | -0.18075 | -0.11594 | 0.38 | 0.0089701 | 0.8961 | 4.8331 | -4.634% | 0.81925 | 0.88406 | 1.142 | 1.1351 | 0.86222 | 0.33965 | 0.31061 | 0.86222 | 24.5% |  | 44 | 28 | -0.16 | 0.90517 | 0.92847 | -0.097888 | 1.1438 | 1.1472
| Post |  |  |  |  | #DIV/0! | 9.885 | 1175 | 4.8175 | 0.576 | 4.4321 | 0.3854 | 51.4125 | 48.5875 | 81.325 | 66.762 | 90 | 53.3149 | 36.481 | 16.8339 |  | non-TXV | R22 | 82.09% | 46.88% | 0.0072287 | [13 empty] | 0.29743 | 0.27363 |  |  |  | 46 | 29 | -0.32 | 0.7277 | 0.84819 | -0.18454 | 1.4536 | 1.4605
19 | Pre | 5 | 158 | -23.7 | 15% | -15% | 8.6224 | 1550 | 4.226 | 1.102 | 3.9099 | 0.31611 | 54.7927 | 52.7182 | 74.7213 | 64.4513 | 81 | 45.9404 | 32.4634 | 13.477 | Old | non-TXV | R22 | 87.54% | 57.7% | 0.0068808 | 0.069512 | -0.071021 | -0.046243 | 0.15 | -0.0037607 | 0.9558 | 4.83 | -9.855% | 0.92898 | 0.95376 | 1.1513 | 1.1578 | 0.876 | 0.2902 | 0.26849 | 0.876 | 23.91% |  | 48 | 30 | -0.4 | 0.7627 | 0.82629 | -0.27775 | 1.4987 | 1.515
| Post |  |  |  |  | #DIV/0! | 9.843 | 1550 | 3.9514 | 1.102 | 3.6352 | 0.31611 | 53.54 | 51.4557 | 74.5364 | 64.253 | 81 | 49.7401 | 34.2197 | 15.5204 |  | non-TXV | R22 | 87.2% | 57.55% | 0.0063552 | [13 empty] | 0.25207 | 0.2319 |  |  |  | 50 | 31 | -0.38 | 0.74788 | 0.84789 | -0.19414 | 1.429 | 1.437
16 | Pre | 3.5 | 82 | 5.74 | 7% | 7% | 9.0998 | 1070 | 3.595 | 0.71 | 3.3086 | 0.2864 | 54.375 | 51.7 | 75.8875 | 65.9125 | 84 | 39.1747 | 24.1099 | 15.0648 | Old | non-TXV | R22 | 83.91% | 59.38% | 0.0073108 | 0.0041899 | -0.06512 | -0.047294 | 0.07 | -0.0002289 | 0.95484 | 4.0963 | -4.865% | 0.93488 | 0.95271 | 1.0741 | 1.0745 | 0.92789 | 0.29496 | 0.27146 | 0.92789 | 13.62% |  | 52 | 32 | -0.18 | 0.92183 | 0.9518 | -0.11387 | 1.173 | 1.1807
| Post |  |  |  |  | #DIV/0! | 9.8071 | 1070 | 3.58 | 0.71 | 3.2936 | 0.2864 | 53.1333 | 50.4523 | 75.8167 | 65.8337 | 84 | 42.0723 | 25.4271 | 16.6452 |  | non-TXV | R22 | 83.51% | 59.32% | 0.0068073 | [13 empty] | 0.2746 | 0.25263 |  |  |  | 54 | 33 | -0.23 | 0.88578 | 0.93714 | -0.11323 | 1.1961 | 1.2019
17 | Pre | 3 | 69 | -9.66 | 14% | -14% | 8.1995 | 1073 | 3.2695 | 0.59253 | 3.0086 | 0.26084 | 56.86 | 47.31 | 82.4 | 60.4 | 90 | 31.6663 | 28.5927 | 3.0736 | Old | non-TXV | R22 | 48.36% | 26.28% | 0.0082371 | 0.0027603 | -0.070236 | -0.042445 | 0.14 | -0.00013101 | 0.95928 | 3.6961 | -4.305% | 0.92976 | 0.95755 | 1.0785 | 1.0788 | 0.92346 | 0.33123 | 0.3048 | 0.92346 | 14.38% |  | 56 | 34 | -0.17 | 0.85803 | 0.87807 | -0.129 | 1.1942 | 1.1967
| Post |  |  |  |  | #DIV/0! | 8.8791 | 1073 | 3.2605 | 0.59253 | 2.9996 | 0.26084 | 55.6429 | 46.0429 | 82.391 | 60.262 | 90 | 34.2112 | 29.9498 | 4.2614 |  | non-TXV | R22 | 46.99% | 25.93% | 0.0076243 | [13 empty] | 0.30712 | 0.28255 |  |  |  | 58 | 35 | -0.14 | 0.92385 | 0.98975 | -0.038949 | 1.1193 | 1.1225
21 | Pre | 3 | 78 | -10.14 | 13% | -13% | 9.5922 | 1015 | 2.516 | 0.61003 | 2.3191 | 0.19686 | 41.6322 | 39.7892 | 61.71 | 53.6183 | 64 | 29.9853 | 22.0809 | 7.9044 | Old | non-TXV | R22 | 85.63% | 59.08% | 0.0065651 | 0.022453 | -0.087812 | -0.066367 | 0.13 | -0.0017466 | 0.93776 | 2.8796 | -8.023% | 0.91219 | 0.93363 | 1.1209 | 1.123 | 0.89063 | 0.26778 | 0.24683 | 0.89063 | 20.54% |  | 60 | 36 | -0.22 | 0.73939 | 0.85139 | -0.19629 | 1.4658 | 1.4757
| Post |  |  |  |  | #DIV/0! | 10.7701 | 1015 | 2.4607 | 0.61003 | 2.2639 | 0.19686 | 40.0233 | 38.065 | 61.6583 | 53.4666 | 64 | 33.0723 | 23.7986 | 9.2737 |  | non-TXV | R22 | 84.18% | 58.58% | 0.0059523 | [13 empty] | 0.2389 | 0.21979 |  |  |  | 62 | 37 | -0.08 | 0.75632 | 0.87026 | -0.12283 | 1.3348 | 1.3359
22 | Pre | 3.5 | 164 | 27.88 | 17% | 17% | 11.2507 | 1004 | 3.557 | 0.42177 | 3.2457 | 0.31124 | 56.7583 | 55.4482 | 85.0917 | 71.675 | 94 | 44.7639 | 29.1888 | 15.575 | Old | non-TXV | R22 | 92.34% | 52.49% | 0.0069528 | -0.085714 | -0.11253 | -0.03063 | 0.17 | 0.002842 | 0.97028 | 4.1841 | 4.761% | 0.88747 | 0.96937 | 1.0302 | 1.0218 | 0.95838 | 0.26275 | 0.23976 | 0.95838 | 6.974% |  | 64 | 39 | 0.04 | 0.96543 | 0.97157 | -0.040401 | 1.0512 | 1.0525
| Post |  |  |  |  | #DIV/0! | 11.7394 | 1004 | 3.8904 | 0.42177 | 3.5792 | 0.31124 | 54.9611 | 53.651 | 84.2071 | 71.9786 | 94 | 50.6226 | 30.1566 | 20.466 |  | non-TXV | R22 | 92.1% | 55.76% | 0.0061481 | [13 empty] | 0.25504 | 0.23464 |  |  |  | 66 | 40 | 0.29 | 0.84398 | 0.9204 | -0.071604 | 1.182 | 1.1818
23 | Pre | 4 | 113 | -10.17 | 9% | -9% | 7.5133 | 1266 | 4.2449 | 0.636 | 3.9135 | 0.33137 | 54.15 | 51.49 | 79.23 | 63.58 | 99 | 36.6716 | 33.1756 | 3.496 | Old | non-TXV | R22 | 83.93% | 42.15% | 0.009036 | 0.024828 | -0.091745 | -0.093791 | 0.09 | -0.0027377 | 0.91425 | 4.3684 | -10.73% | 0.90825 | 0.90621 | 1.1283 | 1.1307 | 0.88432 | 0.37299 | 0.34388 | 0.88432 | 21.63% |  | 68 | 41 | -0.48 | 0.698 | 0.80912 | -0.22572 | 1.5392 | 1.5484
| Post |  |  |  |  | #DIV/0! | 8.4962 | 1266 | 4.1421 | 0.636 | 3.8107 | 0.33137 | 52.0375 | 49.6062 | 79.9 | 63.212 | 99 | 40.5952 | 36.8339 | 3.7613 |  | non-TXV | R22 | 84.71% | 39.41% | 0.0081627 | [13 empty] | 0.33056 | 0.30412 |  |  |  | 70 | 42 | 0.09 | 0.89228 | 0.92535 | -0.071341 | 1.1232 | 1.1234
24 | Pre | 4 | 103 | -10.3 | 10% | -10% | 8.8695 | 1062 | 3.7035 | 0.53089 | 3.4111 | 0.29236 | 52.7455 | 49.0137 | 79.6909 | 63.7589 | 82 | 37.5567 | 29.8735 | 7.6832 | Old | non-TXV | R22 | 77.11% | 41.58% | 0.0077845 | 0.013398 | -0.081185 | -0.058358 | 0.1 | -0.00088072 | 0.94486 | 3.9546 | -6.684% | 0.91881 | 0.94164 | 1.1029 | 1.1042 | 0.90465 | 0.32107 | 0.29572 | 0.90465 | 17.98% |  | 72 | 43 | -0.2 | 0.70773 | 0.84154 | -0.17165 | 1.4687 | 1.4736
| Post |  |  |  |  | #DIV/0! | 9.8044 | 1062 | 3.6545 | 0.53089 | 3.3622 | 0.29236 | 51.02 | 47.59 | 79.74 | 63.798 | 82 | 41.0352 | 31.8372 | 9.198 |  | non-TXV | R22 | 78.22% | 41.59% | 0.0071246 | [13 empty] | 0.2911 | 0.26781 |  |  |  | 74 | 44 | -0.1 | 0.76093 | 0.93419 | -0.080981 | 1.3431 | 1.3456
25 | Pre | 3.5 | 67 | 18.09 | 27% | 27% | 8.3936 | 1160 | 3.36 | 0.74121 | 3.0765 | 0.28345 | 54.9867 | 53.22 | 77.1933 | 65.0433 | 88 | 34.4238 | 26.9545 | 7.4692 | Old | non-TXV | R22 | 89.4% | 52.36% | 0.0082341 | -0.051687 | -0.1382 | -0.090377 | 0.27 | 0.0056174 | 0.91711 | 3.9292 | -4.014% | 0.8618 | 0.90962 | 1.1004 | 1.0952 | 0.89124 | 0.31033 | 0.28415 | 0.89124 | 19.01% |  | 76 | 45 | -0.06 | 0.96319 | 0.97631 | -0.042021 | 1.0622 | 1.0643
| Post |  |  |  |  | #DIV/0! | 9.4179 | 1160 | 3.5431 | 0.74121 | 3.2597 | 0.28345 | 52.3583 | 50.925 | 76.9667 | 64.9167 | 88 | 40.3495 | 29.884 | 10.4655 |  | non-TXV | R22 | 90.96% | 52.57% | 0.0070249 | [13 empty] | 0.28202 | 0.25946 |  |  |  | 78 | 46 | -0.13 | 0.90798 | 0.98859 | -0.038719 | 1.1355 | 1.1384
26 | Pre | 4 | 76 | -22.04 | 29% | -29% | 6.7991 | 880 | 5.008 | 0.38709 | 4.6297 | 0.37837 | 56.1304 | 54.7956 | 81.4261 | 70.1291 | 91 | 36.6822 | 23.0094 | 13.6728 | Old | non-TXV | R22 | 92.11% | 57.46% | 0.010315 | 0.058864 | -0.15708 | -0.10525 | 0.29 | -0.0073215 | 0.90478 | 4.6366 | -14.8% | 0.84292 | 0.89475 | 1.2569 | 1.263 | 0.79615 | 0.44976 | 0.41578 | 0.79615 | 36.66% |  | 80 | 47 | 0.14 | 0.68588 | 0.73237 | -0.16431 | 1.3779 | 1.3709
| Post |  |  |  |  | #DIV/0! | 8.54 | 880 | 4.7296 | 0.395 | 4.3513 | 0.37837 | 52.7636 | 51.3415 | 81.1909 | 69.9939 | 91 | 43.7642 | 25.8713 | 17.893 |  | non-TXV | R22 | 91.09% | 57.69% | 0.0086457 | [13 empty] | 0.35782 | 0.3292 |  |  |  | 82 | 49 | 0.19 | 0.88434 | 0.87446 | -0.086786 | 1.0972 | 1.0943
27 | Pre | 3.5 | 66 | 3.96 | 6% | 6% | 6.4266 | 1030 | 3.8535 | 0.74702 | 3.5512 | 0.30224 | 57.946 | 56.5139 | 76.4 | 67.25 | 96 | 29.5654 | 19.8633 | 9.7021 | Old | non-TXV | R22 | 91.8% | 62.67% | 0.010223 | 0.019984 | -0.11873 | -0.077655 | 0.06 | -0.0018985 | 0.92794 | 4.1989 | -8.874% | 0.88127 | 0.92235 | 1.1574 | 1.1594 | 0.85802 | 0.40953 | 0.37741 | 0.85802 | 25.87% |  | 84 | 50 | 0.19 | 0.93065 | 0.90098 | -0.083828 | 1.0664 | 1.0657
| Post |  |  |  |  | #DIV/0! | 7.49 | 1030 | 3.778 | 0.74702 | 3.4757 | 0.30224 | 56.1 | 54.6479 | 76.3 | 67.075 | 96 | 33.8923 | 21.7503 | 12.1419 |  | non-TXV | R22 | 91.42% | 62.34% | 0.0089176 | [13 empty] | 0.35383 | 0.32552 |  |  |  | 86 | 51 | -0.34 | 0.91861 | 0.94467 | -0.095651 | 1.1426 | 1.1473
28 | Pre | 4 | 62 | -9.92 | 16% | -16% | 8.317 | 1027 | 3.9485 | 0.51098 | 3.6434 | 0.30511 | 42.0053 | 40.7053 | 67.2542 | 57.1542 | 71 | 37.0899 | 27.7675 | 9.3224 | Old | non-TXV | R22 | 89.9% | 53.92% | 0.0082263 | 0.035302 | -0.094831 | -0.071533 | 0.16 | -0.0028906 | 0.93324 | 4.0362 | -9.789% | 0.90517 | 0.92847 | 1.1438 | 1.1472 | 0.87394 | 0.34703 | 0.32021 | 0.87394 | 23.59% |  | 88 | 52 | -0.22 | 0.85175 | 0.96045 | -0.055665 | 1.1984 | 1.2005
| Post |  |  |  |  | #DIV/0! | 9.5166 | 1027 | 3.8139 | 0.51098 | 3.5088 | 0.30511 | 39.7111 | 38.4111 | 67.0111 | 56.9111 | 71 | 41.1583 | 30.0412 | 11.1172 |  | non-TXV | R22 | 89.37% | 53.76% | 0.0074131 | [13 empty] | 0.30341 | 0.27913 |  |  |  | 90 | 53 | -0.22 | 0.93006 | 0.91547 | -0.20822 | 1.2418 | 1.2563
29 | Pre | 3.5 | 115 | -36.8 | 32% | -32% | 6.711 | 1048 | 4.7945 | 0.43567 | 4.4319 | 0.3626 | 61.3417 | 59.875 | 87.3083 | 71.9933 | 86 | 35.0997 | 27.8211 | 7.2786 | Old | non-TXV | R22 | 92.05% | 48% | 0.010331 | 0.057808 | -0.2723 | -0.15181 | 0.32 | -0.0109 | 0.8682 | 4.3133 | -18.45% | 0.7277 | 0.84819 | 1.4536 | 1.4605 | 0.68336 | 0.44726 | 0.41343 | 0.68336 | 52.99% |  | 92 | 54 | -0.1 | 0.89743 | 0.94343 | -0.082569 | 1.1505 | 1.1536
| Post |  |  |  |  | #DIV/0! | 9.8206 | 1048 | 4.5325 | 0.43567 | 4.1699 | 0.3626 | 56.6955 | 55.1288 | 87.5769 | 72.1619 | 86 | 48.7903 | 33.0668 | 15.7235 |  | non-TXV | R22 | 90.85% | 47.86% | 0.0074318 | [13 empty] | 0.30768 | 0.28307 |  |  |  | 94 | 55 | 0.13 | 0.88566 | 0.88198 | -0.0087407 | 1.0057 | 0.99502
30 | Pre | 4 | 106 | -42.4 | 40% | -40% | 5.5403 | 1051 | 5.0211 | 0.44929 | 4.6697 | 0.35143 | 48.1 | 45.5857 | 69.0571 | 58.2801 | 71 | 30.3079 | 23.496 | 6.8119 | Old | non-TXV | R22 | 82.97% | 52.39% | 0.011595 | 0.14302 | -0.2373 | -0.17371 | 0.4 | -0.03203 | 0.852 | 4.1255 | -27.78% | 0.7627 | 0.82629 | 1.4987 | 1.515 | 0.66709 | 0.5382 | 0.50053 | 0.66709 | 55.49% |  | 96 | 57 | -0.09 | 0.92983 | 0.99251 | -0.011775 | 1.0811 | 1.0816
| Post |  |  |  |  | #DIV/0! | 8.3052 | 1051 | 4.3929 | 0.44929 | 4.0414 | 0.35143 | 44.1308 | 42.0693 | 69.8308 | 59.0538 | 71 | 40.215 | 28.758 | 11.4571 |  | non-TXV | R22 | 84.79% | 52.89% | 0.0087388 | [13 empty] | 0.35912 | 0.33039 |  |  |  | 98 | 58 | -0.33 | 0.85053 | 0.88921 | -0.16929 | 1.2703 | 1.2785
31 | Pre | 3.5 | 115 | -43.7 | 38% | -38% | 7.1099 | 1032 | 4.8373 | 0.48273 | 4.4752 | 0.36209 | 53.8917 | 52.6684 | 84.486 | 67.333 | 90 | 37.8245 | 32.5973 | 5.2272 | Old | non-TXV | R22 | 92.48% | 41.11% | 0.009573 | 0.068734 | -0.25212 | -0.15211 | 0.38 | -0.012954 | 0.86797 | 4.3476 | -19.41% | 0.74788 | 0.84789 | 1.429 | 1.437 | 0.6965 | 0.41826 | 0.38695 | 0.6965 | 51.26% |  | 100 | 59 | -0.06 | 0.83545 | 0.96229 | -0.079564 | 1.2534 | 1.2583
| Post |  |  |  |  | #DIV/0! | 10.208 | 1032 | 4.5262 | 0.48273 | 4.1641 | 0.36209 | 48.591 | 47.3677 | 84.9867 | 67.5337 | 90 | 51.1309 | 38.7408 | 12.3901 |  | non-TXV | R22 | 91.7% | 40.58% | 0.0070817 | [13 empty] | 0.29269 | 0.26928 |  |  |  | 102 | 60 | 0.24 | 0.95962 | 1.014 | 0.0022914 | 1.0564 | 1.0576
32 | Pre | 3 | 69 | -12.42 | 18% | -18% | 8.1809 | 1204 | 3.0496 | 0.55905 | 2.824 | 0.22561 | 57.7727 | 50.8967 | 75.312 | 61.127 | 75 | 29.5218 | 22.2513 | 7.2705 | Old | non-TXV | R22 | 62.49% | 44.2% | 0.0076423 | 0.081344 | -0.078168 | -0.048202 | 0.18 | -0.0044728 | 0.95401 | 3.2238 | -11.39% | 0.92183 | 0.9518 | 1.173 | 1.1807 | 0.85889 | 0.33116 | 0.30666 | 0.85889 | 26.78% |  | 104 | 61 | -0.09 | 0.82903 | 0.97576 | -0.045614 | 1.2352 | 1.2377
| Post |  |  |  |  | #DIV/0! | 9.5249 | 1204 | 2.8202 | 0.55905 | 2.5946 | 0.22561 | 56.7692 | 49.8932 | 75.271 | 61.086 | 75 | 32.187 | 23.4749 | 8.7121 |  | non-TXV | R22 | 61.84% | 44.17% | 0.0070095 | [13 empty] | 0.28231 | 0.25972 |  |  |  | 106 | 62 | -0.12 | 0.93466 | 0.97632 | -0.076715 | 1.1342 | 1.1398
33 | Pre | 4 | 122 | -28.06 | 23% | -23% | 6.439 | 1118 | 5.1532 | 0.48312 | 4.7641 | 0.38912 | 52.83 | 50.9979 | 78.241 | 64.305 | 80 | 36.2921 | 29.7046 | 6.5875 | Old | non-TXV | R22 | 88.58% | 46.99% | 0.010722 | 0.05946 | -0.11422 | -0.062859 | 0.23 | -0.0042096 | 0.94086 | 5.0309 | -11.32% | 0.88578 | 0.93714 | 1.1961 | 1.2019 | 0.836 | 0.46356 | 0.42855 | 0.836 | 30.1% |  | 108 | 64 | -0.23 | 0.89638 | 0.86197 | -0.18578 | 1.2001 | 1.2074
| Post |  |  |  |  | #DIV/0! | 7.7022 | 1118 | 4.864 | 0.48312 | 4.4749 | 0.38912 | 51.0182 | 49.1061 | 78.2273 | 64.2913 | 80 | 41.1844 | 31.8076 | 9.3767 |  | non-TXV | R22 | 87.69% | 46.98% | 0.0094482 | [13 empty] | 0.38757 | 0.35656 |  |  |  | 110 | 65 | -0.17 | 0.91083 | 0.92542 | -0.1128 | 1.1526 | 1.1573
34 | Pre | 4 | 100 | -17 | 17% | -17% | 7.3323 | 1276 | 3.5691 | 0.74775 | 3.2904 | 0.27865 | 51.621 | 47.071 | 69.1846 | 57.9036 | 76 | 31.6521 | 23.9109 | 7.7412 | Old | non-TXV | R22 | 71.71% | 50.49% | 0.0088034 | 0.024687 | -0.14197 | -0.12193 | 0.17 | -0.0037939 | 0.89132 | 3.771 | -12.9% | 0.85803 | 0.87807 | 1.1942 | 1.1967 | 0.83142 | 0.35613 | 0.32833 | 0.83142 | 30.38% |  | Commerical
| Post |  |  |  |  | #DIV/0! | 8.819 | 1276 | 3.4831 | 0.74775 | 3.2044 | 0.27865 | 48.8308 | 44.6231 | 69.0846 | 57.5996 | 76 | 37.3116 | 27.5855 | 9.7261 |  | non-TXV | R22 | 72.32% | 49.62% | 0.0074681 | [13 empty] | 0.29821 | 0.27435 |  |  |  | 114 | C33 | -0.0705 | 0.75509 | 0.83851 | -0.45652 | 1.8067 | 1.8486 | Outlying datapoint eliminated - DJR 1/17/08
35 | Pre | 3 | 52 | -7.28 | 14% | -14% | 8.5184 | 961 | 2.9727 | 0.52467 | 2.7427 | 0.22999 | 55.27 | 52.09 | 80.44 | 64.75 | 88 | 29.7924 | 25.196 | 4.5964 | Old | non-TXV | R22 | 81.26% | 42.83% | 0.0077196 | 0.034054 | -0.076155 | -0.010254 | 0.14 | -0.0003779 | 0.98985 | 3.365 | -3.895% | 0.92385 | 0.98975 | 1.1193 | 1.1225 | 0.89389 | 0.32125 | 0.29639 | 0.89389 | 20.14% |  | 116 | C37 | -0.035294 | 1.0047 | 1.001 | -0.024555 | 1.0243 | 1.0269
| Post |  |  |  |  | #DIV/0! | 9.5296 | 961 | 2.8748 | 0.52467 | 2.6448 | 0.22999 | 54.3333 | 51.2111 | 79.7611 | 64.9 | 88 | 32.3959 | 25.4756 | 6.9203 |  | non-TXV | R22 | 81.28% | 44.98% | 0.0070992 | [13 empty] | 0.28701 | 0.26405 |  |  |  | 118 | C55 | -0.093976 | 0.96066 | 0.96245 | -0.07649 | 1.0876 | 1.0916
36 | Pre | 3.5 | 99 | -21.78 | 22% | -22% | 6.7997 | 1062 | 2.7889 | 0.64959 | 2.583 | 0.20586 | 53.1864 | 52.0546 | 71.4273 | 61.2663 | 72 | 23.3803 | 20.5296 | 2.8507 | Old | non-TXV | R22 | 92.94% | 56.27% | 0.0088048 | 0.083794 | -0.26061 | -0.14861 | 0.22 | -0.016206 | 0.87062 | 2.8059 | -19.63% | 0.73939 | 0.85139 | 1.4658 | 1.4757 | 0.67631 | 0.37185 | 0.3444 | 0.67631 | 53.86% |  | 120 | C59 | 0.092063 | 0.88237 | 0.93125 | -0.055827 | 1.1228 | 1.1219
| Post |  |  |  |  | #DIV/0! | 10.0541 | 1062 | 2.5732 | 0.64959 | 2.3674 | 0.20586 | 49.4333 | 48.2911 | 71.1917 | 61.1507 | 72 | 32.4026 | 24.5 | 7.9026 |  | non-TXV | R22 | 92.37% | 56.6% | 0.0063532 | [13 empty] | 0.25368 | 0.23339 |  |  |  | 122 | C60 | 0.1372 | 0.85833 | 0.90923 | -0.086787 | 1.1696 | 1.17
37 | Pre | 3 | 63 | -5.04 | 8% | -8% | 5.7269 | 866 | 3.418 | 0.66285 | 3.1471 | 0.27085 | 52.95 | 51.8078 | 78.15 | 63.192 | 88 | 23.3705 | 22.8484 | 0.52203 | Old | non-TXV | R22 | 92.85% | 43.61% | 0.01159 | 0.0095501 | -0.24368 | -0.12974 | 0.08 | -0.0015647 | 0.88516 | 3.5836 | -12.28% | 0.75632 | 0.87026 | 1.3348 | 1.3359 | 0.73304 | 0.4551 | 0.41904 | 0.73304 | 45.08% |  | 124 | C34 | 0.13542 | 0.87944 | 0.89936 | -0.075698 | 1.1177 | 1.116
| Post |  |  |  |  | #DIV/0! | 7.8125 | 866 | 3.3857 | 0.66285 | 3.1148 | 0.27085 | 48.775 | 47.6333 | 78.1 | 63.1417 | 88 | 31.6289 | 26.5919 | 5.037 |  | non-TXV | R22 | 92.27% | 43.57% | 0.0085634 | [13 empty] | 0.34095 | 0.31367
39 | Pre | 4 | 105 | 4.2 | 4% | 4% | 8.013 | 1160 | 4.4111 | 0.7025 | 4.0634 | 0.34774 | 53.96 | 51.26 | 77.612 | 65.312 | 84 | 40.975 | 28.6824 | 12.2927 | Old | non-TXV | R22 | 83.64% | 52.08% | 0.0084865 | 0.014816 | -0.034572 | -0.028433 | 0.04 | -0.00046983 | 0.97235 | 4.9096 | -4.04% | 0.96543 | 0.97157 | 1.0512 | 1.0525 | 0.95134 | 0.34711 | 0.31975 | 0.95134 | 9.495%
| Post |  |  |  |  | #DIV/0! | 8.4228 | 1160 | 4.3467 | 0.7025 | 3.999 | 0.34774 | 53.18 | 50.64 | 77.58 | 65.28 | 84 | 42.5282 | 29.5919 | 12.9363 |  | non-TXV | R22 | 84.37% | 52.06% | 0.0081766 | [13 empty] | 0.33022 | 0.3038
40 | Pre | 4 | 87 | 25.23 | 29% | 29% | 6.8084 | 1180 | 4.2553 | 0.50611 | 3.9141 | 0.34123 | 51.562 | 49.982 | 79.25 | 61.98 | 90 | 32.4177 | 34.1938 | -1.7762 | Old | non-TXV | R22 | 89.9% | 37.18% | 0.010526 | -0.0023779 | -0.15602 | -0.079599 | 0.29 | 0.00021604 | 0.92627 | 4.4197 | -7.16% | 0.84398 | 0.9204 | 1.182 | 1.1818 | 0.8388 | 0.42534 | 0.39123 | 0.8388 | 29.04%
| Post |  |  |  |  | #DIV/0! | 8.1168 | 1180 | 4.2654 | 0.50611 | 3.9242 | 0.34123 | 48.831 | 47.251 | 79.0143 | 61.6713 | 90 | 38.7298 | 37.3004 | 1.4294 |  | non-TXV | R22 | 89.36% | 36.78% | 0.0088106 | [13 empty] | 0.35983 | 0.33105
41 | Pre | 4 | 103 | -49.44 | 48% | -48% | 5.0074 | 1028 | 4.783 | 0.60635 | 4.4268 | 0.35616 | 63.6 | 54.575 | 87.5333 | 65.3333 | 94 | 26.9865 | 25.3451 | 1.6414 | Old | non-TXV | R22 | 56.08% | 29.76% | 0.013198 | 0.074349 | -0.302 | -0.19088 | 0.48 | -0.018972 | 0.83972 | 4.2476 | -22.57% | 0.698 | 0.80912 | 1.5392 | 1.5484 | 0.6403 | 0.56183 | 0.51999 | 0.6403 | 58.4%
| Post |  |  |  |  | #DIV/0! | 7.8204 | 1028 | 4.452 | 0.60635 | 4.0958 | 0.35616 | 57.265 | 49.175 | 87.29 | 65.19 | 94 | 39.5581 | 31.8125 | 7.7456 |  | non-TXV | R22 | 55.98% | 29.84% | 0.0090035 | [13 empty] | 0.36501 | 0.33581
42 | Pre | 3 | 87 | 7.83 | 9% | 9% | 5.4168 | 941 | 3.6372 | 0.57325 | 3.3468 | 0.29034 | 53.93 | 50.54 | 77 | 61.0659 | 94 | 22.8067 | 22.8181 | -0.011399 | Old | non-TXV | R22 | 79.58% | 39.66% | 0.012731 | 0.0021708 | -0.10772 | -0.074652 | 0.09 | -0.00019014 | 0.93053 | 3.9106 | -7.134% | 0.89228 | 0.92535 | 1.1232 | 1.1234 | 0.88246 | 0.50129 | 0.46127 | 0.88246 | 21.43%
| Post |  |  |  |  | #DIV/0! | 6.1383 | 941 | 3.6293 | 0.57325 | 3.3389 | 0.29034 | 51.8522 | 48.8565 | 76.9348 | 60.8418 | 94 | 25.7963 | 24.8168 | 0.97946 |  | non-TXV | R22 | 81.19% | 39.11% | 0.011255 | [13 empty] | 0.44632 | 0.41062
43 | Pre | 4 | 151 | -30.2 | 20% | -20% | 6.7858 | 1048 | 4.9362 | 0.62705 | 4.5563 | 0.3799 | 56.8689 | 53.3742 | 89.0316 | 67.8636 | 102 | 37.751 | 34.547 | 3.204 | Old | non-TXV | R22 | 80.02% | 33.37% | 0.010063 | 0.039469 | -0.29227 | -0.15846 | 0.2 | -0.0078922 | 0.86322 | 4.6405 | -17.16% | 0.70773 | 0.84154 | 1.4687 | 1.4736 | 0.67274 | 0.42233 | 0.38983 | 0.67274 | 54.2%
| Post |  |  |  |  | #DIV/0! | 10.0868 | 1048 | 4.7488 | 0.62705 | 4.3689 | 0.3799 | 51.18 | 47.72 | 89.8571 | 68.6711 | 102 | 54.2249 | 41.4551 | 12.7698 |  | non-TXV | R22 | 78.1% | 33.87% | 0.0070061 | [13 empty] | 0.28755 | 0.26454
44 | Pre | 3 | 61 | -6.1 | 10% | -10% | 5.7317 | 765 | 4.0364 | 0.56332 | 3.7205 | 0.31597 | 59.0083 | 54.86 | 88.6333 | 68.4363 | 100 | 26.3646 | 23.2262 | 3.1384 | Old | non-TXV | R22 | 77.25% | 35.56% | 0.011985 | 0.02198 | -0.23907 | -0.065808 | 0.1 | -0.0016765 | 0.93826 | 4.2343 | -8.098% | 0.76093 | 0.93419 | 1.3431 | 1.3456 | 0.73377 | 0.48702 | 0.44889 | 0.73377 | 45.37%
| Post |  |  |  |  | #DIV/0! | 7.8113 | 765 | 3.9496 | 0.56332 | 3.6336 | 0.31597 | 55.475 | 48.3875 | 87.2438 | 67.0558 | 100 | 35.2521 | 24.9978 | 10.2543 |  | non-TXV | R22 | 59.85% | 34.66% | 0.0089631 | [13 empty] | 0.36261 | 0.3336
45 | Pre | 3 | 71 | -4.26 | 6% | -6% | 6.7135 | 903 | 3.2105 | 0.70488 | 2.9594 | 0.25104 | 56.73 | 54.3657 | 74.4143 | 65.5143 | 84 | 26.2857 | 16.7708 | 9.5149 | Old | non-TXV | R22 | 86.3% | 62.69% | 0.0095503 | 0.023115 | -0.03681 | -0.023695 | 0.06 | -0.00064146 | 0.97685 | 3.7539 | -4.202% | 0.96319 | 0.97631 | 1.0622 | 1.0643 | 0.94217 | 0.3819 | 0.35204 | 0.94217 | 11.3%
| Post |  |  |  |  | #DIV/0! | 7.1255 | 903 | 3.1379 | 0.70488 | 2.8869 | 0.25104 | 56.1231 | 53.7308 | 74.2923 | 65.3923 | 84 | 27.3822 | 17.2362 | 10.146 |  | non-TXV | R22 | 86% | 62.63% | 0.0091678 | [13 empty] | 0.35954 | 0.33077
46 | Pre | 3 | 84 | -10.92 | 13% | -13% | 6.5179 | 943 | 4.8267 | 0.60537 | 4.4522 | 0.37453 | 54.15 | 51.56 | 82.82 | 66.6 | 97 | 35.4061 | 28.0049 | 7.4013 | Old | non-TXV | R22 | 84.34% | 42.77% | 0.010578 | 0.030983 | -0.092021 | -0.011413 | 0.13 | -0.00038407 | 0.98872 | 5.2274 | -3.872% | 0.90798 | 0.98859 | 1.1355 | 1.1384 | 0.87901 | 0.43962 | 0.40551 | 0.87901 | 22.59%
| Post |  |  |  |  | #DIV/0! | 7.4151 | 943 | 4.6817 | 0.60537 | 4.3071 | 0.37453 | 52.975 | 50.1562 | 81.9688 | 66.7488 | 97 | 39.2039 | 28.352 | 10.8518 |  | non-TXV | R22 | 82.64% | 45.24% | 0.0095535 | [13 empty] | 0.38717 | 0.3562
47 | Pre | 4 | 87 | 12.18 | 14% | 14% | 7.3163 | 1091 | 3.8192 | 0.70267 | 3.4959 | 0.3233 | 56.5667 | 51.0584 | 78.4917 | 63.4787 | 83 | 33.0833 | 25.0235 | 8.0598 | Old | non-TXV | R22 | 68.94% | 43.66% | 0.0097723 | -0.054952 | -0.31412 | -0.26763 | 0.14 | 0.022006 | 0.78887 | 3.7423 | -16.43% | 0.68588 | 0.73237 | 1.3779 | 1.3709 | 0.70354 | 0.36737 | 0.33627 | 0.70354 | 48.94%
| Post |  |  |  |  | #DIV/0! | 10.3993 | 1091 | 4.0412 | 0.70267 | 3.7179 | 0.3233 | 47.2964 | 44.4328 | 77.9818 | 63.5998 | 83 | 49.3334 | 35.0442 | 14.2892 |  | non-TXV | R22 | 80.35% | 45.36% | 0.0065534 | [13 empty] | 0.26662 | 0.24529
49 | Pre | 3.5 | 88 | 16.72 | 19% | 19% | 6.116 | 934 | 3.5612 | 0.7352 | 3.2676 | 0.29362 | 56.9148 | 51.9481 | 78.4407 | 63.4777 | 83 | 26.2767 | 21.0342 | 5.2425 | Old | non-TXV | R22 | 72.02% | 43.79% | 0.011174 | -0.029712 | -0.11566 | -0.12554 | 0.19 | 0.0047746 | 0.88846 | 3.914 | -8.679% | 0.88434 | 0.87446 | 1.0972 | 1.0943 | 0.89688 | 0.42223 | 0.38742 | 0.89688 | 18.26%
| Post |  |  |  |  | #DIV/0! | 6.8192 | 934 | 3.6702 | 0.7352 | 3.3766 | 0.29362 | 52.9895 | 49.9611 | 77.9526 | 63.3416 | 83 | 30.0414 | 24.4143 | 5.6271 |  | non-TXV | R22 | 81.39% | 44.6% | 0.0097738 | [13 empty] | 0.38483 | 0.35404
50 | Pre | 4 | 124 | 23.56 | 19% | 19% | 8.6725 | 932 | 3.6549 | 0.7352 | 3.3603 | 0.29461 | 58.9177 | 54.259 | 89.25 | 69.891 | 101 | 38.0734 | 28.8954 | 9.178 | Old | non-TXV | R22 | 74.54% | 38.1% | 0.007738 | -0.0075244 | -0.069347 | -0.099022 | 0.19 | 0.00089879 | 0.9099 | 4.0198 | -8.383% | 0.93065 | 0.90098 | 1.0664 | 1.0657 | 0.93227 | 0.30738 | 0.2826 | 0.93227 | 12.58%
| Post |  |  |  |  | #DIV/0! | 9.3026 | 932 | 3.6826 | 0.7352 | 3.388 | 0.29461 | 55.5167 | 52.5083 | 89.475 | 69.692 | 101 | 41.0973 | 32.3469 | 8.7504 |  | non-TXV | R22 | 82.32% | 37.15% | 0.0071686 | [13 empty] | 0.28823 | 0.26517
51 | Pre | 4 | 82 | -27.88 | 34% | -34% | 8.2458 | 1159 | 4.4796 | 0.62626 | 4.1381 | 0.34144 | 56.3 | 53.2454 | 86.1909 | 67.6819 | 102 | 42.1014 | 35.663 | 6.4383 | Old | non-TXV | R22 | 82.29% | 38.43% | 0.00811 | 0.049564 | -0.081391 | -0.05533 | 0.34 | -0.003077 | 0.94757 | 4.6377 | -9.565% | 0.91861 | 0.94467 | 1.1426 | 1.1473 | 0.87693 | 0.3456 | 0.31925 | 0.87693 | 23.25%
| Post |  |  |  |  | #DIV/0! | 9.403 | 1159 | 4.268 | 0.62626 | 3.9266 | 0.34144 | 54.1826 | 51.8565 | 85.9174 | 67.7084 | 102 | 46.0211 | 37.877 | 8.144 |  | non-TXV | R22 | 85.91% | 39.07% | 0.0074192 | [13 empty] | 0.30248 | 0.27828
52 | Pre | 4 | 100 | -22 | 22% | -22% | 7.1707 | 1053 | 4.0783 | 0.71059 | 3.7587 | 0.31963 | 49.6333 | 48.05 | 78.9917 | 62.2 | 89 | 34.3399 | 32.3596 | 1.9804 | Old | non-TXV | R22 | 89.5% | 38.44% | 0.0093079 | 0.020749 | -0.14825 | -0.039554 | 0.22 | -0.00091854 | 0.96195 | 4.5269 | -5.567% | 0.85175 | 0.96045 | 1.1984 | 1.2005 | 0.82834 | 0.3786 | 0.34893 | 0.82834 | 30.88%
| Post |  |  |  |  | #DIV/0! | 8.6568 | 1053 | 3.9954 | 0.71059 | 3.6758 | 0.31963 | 48.7833 | 47.425 | 79.5167 | 63.7833 | 89 | 40.7389 | 33.7921 | 6.9468 |  | non-TXV | R22 | 90.83% | 42.08% | 0.0078459 | [13 empty] | 0.31592 | 0.29064
53 | Pre | 4 | 122 | -26.84 | 22% | -22% | 6.9112 | 1144 | 4.9871 | 0.81708 | 4.6417 | 0.34545 | 59.2 | 54.2636 | 84.3 | 67.818 | 95 | 40.1138 | 29.637 | 10.4768 | Old | non-TXV | R22 | 73.22% | 42.92% | 0.0086117 | 0.15493 | -0.069942 | -0.084528 | 0.22 | -0.015651 | 0.92206 | 4.735 | -20.82% | 0.93006 | 0.91547 | 1.2418 | 1.2563 | 0.81888 | 0.39674 | 0.36925 | 0.81888 | 34.06%
| Post |  |  |  |  | #DIV/0! | 8.4398 | 1144 | 4.3181 | 0.81708 | 3.9727 | 0.34545 | 56.5469 | 52.9281 | 84.175 | 67.7439 | 95 | 43.3402 | 32.631 | 10.7092 |  | non-TXV | R22 | 79.22% | 42.99% | 0.0079706 | [13 empty] | 0.31949 | 0.29393
54 | Pre | 3.5 | 79 | -7.9 | 10% | -10% | 5.9074 | 870 | 3.8967 | 0.44823 | 3.5948 | 0.30193 | 55.4267 | 52.6267 | 84.2333 | 64.9753 | 92 | 25.667 | 25.9531 | -0.28603 | Old | non-TXV | R22 | 83.48% | 35.07% | 0.011763 | 0.032474 | -0.10257 | -0.056572 | 0.1 | -0.002062 | 0.94646 | 3.9963 | -8.257% | 0.89743 | 0.94343 | 1.1505 | 1.1536 | 0.86682 | 0.489 | 0.45111 | 0.86682 | 24.66%
| Post |  |  |  |  | #DIV/0! | 6.815 | 870 | 3.7741 | 0.44823 | 3.4722 | 0.30193 | 53.6214 | 50.8136 | 84.25 | 64.736 | 92 | 28.7755 | 27.6011 | 1.1744 |  | non-TXV | R22 | 82.9% | 34.38% | 0.010493 | [13 empty] | 0.42504 | 0.39104
55 | Pre | 4 | 93 | 12.09 | 13% | 13% | 7.9931 | 1212 | 4.5779 | 0.65993 | 4.1667 | 0.41115 | 55.7364 | 53.8 | 78.6182 | 67.0732 | 78 | 41.8665 | 28.8911 | 12.9754 | Old | non-TXV | R22 | 88.55% | 55.22% | 0.0098205 | -0.10925 | -0.11434 | -0.11802 | 0.13 | 0.015758 | 0.89444 | 5.1871 | -0.8741% | 0.88566 | 0.88198 | 1.0057 | 0.99502 | 0.9746 | 0.35414 | 0.32234 | 0.9746 | 3.097%
| Post |  |  |  |  | #DIV/0! | 8.2014 | 1212 | 5.1394 | 0.65993 | 4.7282 | 0.41115 | 51.96 | 50.42 | 78.09 | 66.01 | 78 | 47.5625 | 33.0584 | 14.5041 |  | non-TXV | R22 | 90.22% | 53.1% | 0.0086444 | [13 empty] | 0.35212 | 0.32395
57 | Pre | 2.5 | 53 | -4.77 | 9% | -9% | 7.9617 | 770 | 2.6104 | 0.56291 | 2.4027 | 0.20773 | 47.46 | 45.89 | 70.69 | 60.06 | 73 | 25.2648 | 19.0004 | 6.2644 | Old | non-TXV | R22 | 89.14% | 54.01% | 0.0082223 | 0.005276 | -0.070172 | -0.0074945 | 0.09 | -4.3868e-05 | 0.99256 | 3.1361 | -1.177% | 0.92983 | 0.99251 | 1.0811 | 1.0816 | 0.9209 | 0.32771 | 0.30163 | 0.9209 | 14.82%
| Post |  |  |  |  | #DIV/0! | 8.6455 | 770 | 2.5967 | 0.56291 | 2.389 | 0.20773 | 46.86 | 45.36 | 70.28 | 60.55 | 73 | 27.3165 | 19.1584 | 8.1581 |  | non-TXV | R22 | 89.49% | 57.3% | 0.0076047 | [13 empty] | 0.30312 | 0.27887
58 | Pre | 3 | 120 | -39.6 | 33% | -33% | 6.8035 | 968 | 3.6316 | 0.5256 | 3.3627 | 0.2689 | 51.0556 | 49.9 | 70.4944 | 61.9 | 72 | 28.2837 | 19.9567 | 8.327 | Old | non-TXV | R22 | 92.51% | 61.97% | 0.0095073 | 0.08043 | -0.14947 | -0.11079 | 0.33 | -0.010922 | 0.90026 | 3.4992 | -16.93% | 0.85053 | 0.88921 | 1.2703 | 1.2785 | 0.78775 | 0.41209 | 0.38158 | 0.78775 | 37.99%
| Post |  |  |  |  | #DIV/0! | 8.6366 | 968 | 3.3613 | 0.5256 | 3.0924 | 0.2689 | 46.6375 | 45.9562 | 68.625 | 60.6437 | 72 | 33.5695 | 22.6667 | 10.9028 |  | non-TXV | R22 | 95.17% | 63.54% | 0.0080103 | [13 empty] | 0.3244 | 0.29845
59 | Pre | 4 | 134 | -8.04 | 6% | -6% | 4.1213 | 1032 | 7.3365 | 0.62989 | 6.776 | 0.56051 | 64.0923 | 62.1231 | 82.1462 | 72.8462 | 100 | 32.8317 | 19.1719 | 13.6598 | Old | non-TXV | R22 | 89.81% | 64.55% | 0.017072 | 0.047116 | -0.16455 | -0.037705 | 0.06 | -0.0020531 | 0.96366 | 7.3588 | -7.956% | 0.83545 | 0.96229 | 1.2534 | 1.2583 | 0.79229 | 0.71579 | 0.66111 | 0.79229 | 36.79%
| Post |  |  |  |  | #DIV/0! | 5.2017 | 1032 | 7.0064 | 0.62989 | 6.4459 | 0.56051 | 62.6818 | 60.0909 | 81.5091 | 73.0273 | 100 | 39.7216 | 20.0073 | 19.7143 |  | non-TXV | R22 | 86.39% | 67.16% | 0.014111 | [13 empty] | 0.5711 | 0.52541
60 | Pre | 3 | 85 | 20.4 | 24% | 24% | 8.1992 | 906 | 3.7347 | 0.54783 | 3.44 | 0.29473 | 55.8538 | 54 | 81.1538 | 68.6615 | 98 | 35.1135 | 23.745 | 11.3685 | Old | non-TXV | R22 | 89.05% | 53.39% | 0.0083937 | 0.013718 | -0.040379 | 0.014034 | 0.24 | 0.00020479 | 1.0142 | 4.2922 | 0.2291% | 0.95962 | 1.014 | 1.0564 | 1.0576 | 0.94626 | 0.34466 | 0.31746 | 0.94626 | 10.42%
| Post |  |  |  |  | #DIV/0! | 8.6649 | 906 | 3.6842 | 0.54783 | 3.3894 | 0.29473 | 56.9286 | 54.5786 | 81.9071 | 69.6071 | 98 | 36.6697 | 23.3905 | 13.2792 |  | non-TXV | R22 | 86.43% | 54.4% | 0.0080375 | [13 empty] | 0.32627 | 0.30016
61 | Pre | 4 | 142 | -12.78 | 9% | -9% | 6.3168 | 904 | 5.2779 | 0.48808 | 4.8656 | 0.41233 | 57.7154 | 54.4154 | 85.7308 | 69.6615 | 103 | 36.4229 | 26.0274 | 10.3955 | Old | non-TXV | R22 | 81.37% | 44.97% | 0.01132 | 0.024031 | -0.17097 | -0.024236 | 0.09 | -0.00063507 | 0.97634 | 5.5086 | -4.561% | 0.82903 | 0.97576 | 1.2352 | 1.2377 | 0.80493 | 0.47294 | 0.43599 | 0.80493 | 34.83%
| Post |  |  |  |  | #DIV/0! | 7.8477 | 904 | 5.1541 | 0.48808 | 4.7417 | 0.41233 | 54.5143 | 51.4786 | 83.1714 | 69.9357 | 103 | 44.2779 | 26.7152 | 17.5626 |  | non-TXV | R22 | 81.84% | 52.07% | 0.0093122 | [13 empty] | 0.38288 | 0.35225
62 | Pre | 3.5 | 82 | -9.84 | 12% | -12% | 6.9202 | 842 | 4.2472 | 0.48526 | 3.9267 | 0.32052 | 59.9667 | 59.0667 | 83.4 | 72.618 | 91 | 32.75 | 20.2715 | 12.4785 | Old | non-TXV | R22 | 94.99% | 60.06% | 0.009787 | 0.060072 | -0.06534 | -0.02368 | 0.12 | -0.0015761 | 0.97687 | 4.3879 | -7.671% | 0.93466 | 0.97632 | 1.1342 | 1.1398 | 0.8842 | 0.42131 | 0.38952 | 0.8842 | 22.04%
| Post |  |  |  |  | #DIV/0! | 7.8265 | 842 | 4.0066 | 0.48526 | 3.686 | 0.32052 | 58.8727 | 57.9182 | 82.9 | 72.518 | 91 | 35.1553 | 20.8034 | 14.3519 |  | non-TXV | R22 | 94.59% | 61.18% | 0.0091174 | [13 empty] | 0.37147 | 0.34175
64 | Pre | 4 | 109 | -25.07 | 23% | -23% | 9.0308 | 1050 | 4.001 | 0.6476 | 3.7034 | 0.29755 | 49.1512 | 45.2208 | 78.5348 | 62.4258 | 91 | 41.98 | 32.3096 | 9.6705 | Old | non-TXV | R22 | 74.24% | 40.23% | 0.0070878 | 0.075722 | -0.10362 | -0.13803 | 0.23 | -0.012955 | 0.87871 | 3.8373 | -18.58% | 0.89638 | 0.86197 | 1.2001 | 1.2074 | 0.8375 | 0.30901 | 0.28603 | 0.8375 | 30.21%
| Post |  |  |  |  | #DIV/0! | 10.783 | 1050 | 3.7193 | 0.6476 | 3.4218 | 0.29755 | 44.9357 | 42.8143 | 79.3929 | 62.4929 | 91 | 47.0884 | 37.8372 | 9.2512 |  | non-TXV | R22 | 84.62% | 38.4% | 0.0063189 | [13 empty] | 0.25749 | 0.23689
65 | Pre | 4 | 97 | -16.49 | 17% | -17% | 7.514 | 956 | 4.1764 | 0.58807 | 3.8582 | 0.31826 | 55.5 | 48.6 | 83 | 64.2 | 92 | 35.8004 | 27.2977 | 8.5027 | Old | non-TXV | R22 | 60.86% | 35.46% | 0.0088899 | 0.049812 | -0.089167 | -0.074576 | 0.17 | -0.0043093 | 0.9306 | 4.2494 | -11.28% | 0.91083 | 0.92542 | 1.1526 | 1.1573 | 0.86861 | 0.37702 | 0.34829 | 0.86861 | 24.64%
| Post |  |  |  |  | #DIV/0! | 8.6506 | 956 | 3.9783 | 0.58807 | 3.66 | 0.31826 | 52.8533 | 46.8267 | 82.72 | 64.2 | 92 | 39.5016 | 29.6592 | 9.8423 |  | non-TXV | R22 | 63.86% | 36.05% | 0.0080569 | [13 empty] | 0.32711 | 0.30094
[13 empty] | 24: All: |  | 0.036522 | -0.1294 | -0.08113 | 0.20121 | -0.0034334 | 0.92554 | 4.1662 | -10.54% | 0.86664 | 0.91703 | 1.2052
Commercial Units
C33 | Pre | 10.1 | 200 | -14.1 | 7.05% | -7.05% | 5.6111 | 3831 | 12.96 | 1.3983 | 12.2 | 0.76 | 52.0786 | 50.9886 | 65.4143 | 58.9393 | 80 | 72.7195 | 54.7696 |  | New | non-TXV | R22 | 93.06% | 68.57% | 0.010451 | 0.36421 | -0.24491 | -0.16149 | 0.0705 | -0.076258 | 0.86096 | 9.383 | -45.65% | 0.75509 | 0.83851 | 1.8067 | 1.8486 | 0.54475 | 0.5708 | 0.53733 | 0.54475 | 69.85%
| Post |  |  |  |  | #DIV/0! | 10.3004 | 3831 | 9.5 | 1.3983 | 8.74 | 0.76 | 48.9943 | 47.9143 | 65.1114 | 58.7314 |  | 97.8534 | 66.2372 |  |  | non-TXV | R22 | 92.72% | 68.86% | 0.0077667 | [13 empty] | 0.31594 | 0.29066
C37 | Pre | 2 | 85 | -3 | 3.529% | -3.529% | 8.9207 | 818 | 2.1975 | 0.29857 | 2.0267 | 0.17082 | 54.2455 | 52.2182 | 70.6273 | 61.9364 | 95 | 19.6037 | 14.2087 |  | New | non-TXV | R22 | 87.7% | 61.64% | 0.0087136 | 0.029175 | 0.0047294 | 0.0010395 | 0.035294 | 3.2469e-05 | 1.001 | 2.4364 | -2.456% | 1.0047 | 1.001 | 1.0243 | 1.0269 | 0.97649 | 0.36369 | 0.33542 | 0.97649 | 4.671%
| Post |  |  |  |  | #DIV/0! | 9.1355 | 818 | 2.1353 | 0.29857 | 1.9644 | 0.17082 | 53.875 | 52.025 | 70.225 | 61.725 |  | 19.5067 | 14.1929 |  |  | non-TXV | R22 | 88.68% | 62.21% | 0.008757 | [13 empty] | 0.35505 | 0.32664
C55 | Pre | 4 | 166 | -15.6 | 9.398% | -9.398% | 8.5836 | 1020 | 3.5 | 0.3723 | 3.232 | 0.268 | 49.1176 | 46.657 | 67.1824 | 59.1882 | 69 | 30.0427 | 19.695 |  | New | non-TXV | R22 | 83.65% | 62.74% | 0.0089206 | 0.044776 | -0.039337 | -0.037551 | 0.093976 | -0.0018597 | 0.96381 | 3.5876 | -7.649% | 0.96066 | 0.96245 | 1.0876 | 1.0916 | 0.91796 | 0.38148 | 0.35227 | 0.91796 | 15.59%
| Post |  |  |  |  | #DIV/0! | 9.3507 | 1020 | 3.35 | 0.3723 | 3.082 | 0.268 | 47.6 | 46.6 | 66.4 | 59.6 |  | 31.3249 | 20.513 |  |  | non-TXV | R22 | 93.07% | 67.57% | 0.0085555 | [13 empty] | 0.35077 | 0.32271
C59 | Pre | 5 | 126 | 11.6 | 9.206% | 9.206% | 6.1867 | 1445 | 5.885 | 0.52743 | 5.4098 | 0.4752 | 49.1909 | 42.6909 | 72.5182 | 54.7182 | 78 | 36.4086 | 35.8866 |  | Old | non-TXV | R22 | 58.38% | 29.87% | 0.013052 | -0.0092593 | -0.11763 | -0.068754 | 0.092063 | 0.0007179 | 0.93567 | 6.0514 | -5.583% | 0.88237 | 0.93125 | 1.1228 | 1.1219 | 0.88547 | 0.52568 | 0.48323 | 0.88547 | 21.14%
| Post |  |  |  |  | #DIV/0! | 6.9869 | 1445 | 5.94 | 0.52743 | 5.4648 | 0.4752 | 47.8 | 41.34 | 72.96 | 55.04 |  | 41.5021 | 38.669 |  |  | non-TXV | R22 | 57.46% | 29.89% | 0.01145 | [13 empty] | 0.46818 | 0.43073
C60 | Pre | 10 | 250 | 34.3 | 13.72% | 13.72% | 5.5828 | 3655 | 14.6455 | 1.3341 | 13.4784 | 1.1671 | 59.0455 | 48.7455 | 73.9818 | 58.3818 | 78 | 81.7622 | 57.7961 |  | Old | non-TXV | R22 | 46.71% | 38.44% | 0.014274 | 0.0038992 | -0.14167 | -0.090768 | 0.1372 | -0.00041991 | 0.91679 | 14.5977 | -8.679% | 0.85833 | 0.90923 | 1.1696 | 1.17 | 0.84831 | 0.5791 | 0.53295 | 0.84831 | 27.47%
| Post |  |  |  |  | #DIV/0! | 6.5811 | 3655 | 14.5886 | 1.3341 | 13.4215 | 1.1671 | 58.0571 | 47.7571 | 74.6286 | 59.0286 |  | 96.0082 | 64.0204 |  |  | non-TXV | R22 | 45.81% | 38.95% | 0.012156 | [13 empty] | 0.49513 | 0.45552
C34 | Pre | 5 | 192 | 26 | 13.54% | 13.54% | 9.0353 | 1325 | 5.6284 | 0.48363 | 5.1704 | 0.45809 | 55.8444 | 47.7056 | 76.7667 | 63.35 | 95 | 50.8548 | 29.0796 |  | New | TXV | R410 | 54.63% | 47.78% | 0.0090079 | -0.017066 | -0.12056 | -0.10064 | 0.13542 | 0.002018 | 0.90857 | 5.642 | -7.57% | 0.87944 | 0.89936 | 1.1177 | 1.116 | 0.89122 | 0.36586 | 0.33609 | 0.89122 | 20.26%
| Post |  |  |  |  | #DIV/0! | 10.1381 | 1325 | 5.7262 | 0.48363 | 5.2681 | 0.45809 | 53.4167 | 45.3167 | 76.8167 | 63.43 |  | 58.0524 | 32.5183 |  |  | TXV | R410 | 52.81% | 47.91% | 0.007891 | [13 empty] | 0.32734 | 0.30116
[13 empty] | 24: TXV: |  | 0.077879 | -0.11242 | -0.078024 | 0.2818 | -0.0059501 | 0.91999 | 3.7225 | -14.42% | 0.86542 | 0.91167 | 1.2481
[13 empty] | 24: non-TXV: |  | 0.027531 | -0.1331 | -0.081805 | 0.1837 | -0.0028862 | 0.92674 | 4.2627 | -9.702% | 0.8669 | 0.9182 | 1.1958
| full charge: |  | 103 | [9 empty] | 16: size:; 17: 35.2827; 24: dChange >= 20%: |  | 0.080129 | -0.16577 | -0.10314 | 0.32532 | -0.010113 | 0.9083 | 4.1794 | -16.02% | 0.83423 | 0.89686 | 1.304
|  |  | 102.6286 | [9 empty] | 24: d charge <20%: |  | 0.010358 | -0.10758 | -0.067923 | 0.12675 | 0.0005745 | 0.93588 | 4.1583 | -7.262% | 0.88609 | 0.92913 | 1.1458
[13 empty] | 23: OLD; 24: TXV: |  | -0.060036 | 0.17187 | 0.10906 | 0.2818 | -0.055699 | 0.90395 | 3.6624 | 14.39% | 0.85804 | 0.90395 | 1.0779
[13 empty] | 24: non-TXV: |  | -0.024456 | 0.17376 | 0.10091 | 0.1837 | -0.021983 | 0.91246 | 4.1964 | 10.7% | 0.86005 | 0.91246 | 1.0275
[13 empty] | 24: dChange >= 20%: |  | -0.06811 | 0.22109 | 0.12701 | 0.32532 | -0.059332 | 0.89024 | 4.0956 | 16.27% | 0.82645 | 0.89024 | 1.0801
[13 empty] | 24: d charge <20%: |  | -0.0084294 | 0.14482 | 0.08758 | 0.12675 | -0.0092073 | 0.92336 | 4.1043 | 8.415% | 0.87963 | 0.92336 | 1.0104

## Graph TXV vs non-TXV
Residential
Site | d Charge fraction | d Cap fraction | d Sen Cap fraction | eir fraction | % overall energy savings
1 | -0.4 | 0.82654 | 0.9118 | 1.3133 | -0.15132
2 | 0.18 | 0.86942 | 0.9362 | 1.1322 | -0.04707
5 | 0.16 | 0.87425 | 0.88484 | 1.1309 | -0.094011
6 | -0.78021 | 0.87971 | 0.92443 | 1.5379 | -0.36397
7 | 0.11023 | 0.9166 | 0.94394 | 1.0763 | -0.041996
9 | 0.15 | 0.89564 | 0.92413 | 1.2197 | -0.13813
10 | 0.086 | 0.9111 | 0.94329 | 1.0632 | -0.027928
11 | 0.34 | 0.7126 | 0.80643 | 1.3156 | -0.11154
15 | -0.30971 | 0.89639 | 0.94145 | 1.3984 | -0.26927
16 | -0.30189 | 0.872 | 0.90016 | 1.2933 | -0.19707
14 | -0.07 | 0.95314 | 0.96369 | 1.0886 | -0.066615
20 | 0.38 | 0.81925 | 0.88406 | 1.142 | -0.046339
19 | -0.15 | 0.92898 | 0.95376 | 1.1513 | -0.098552
16 | 0.07 | 0.93488 | 0.95271 | 1.0741 | -0.048655
17 | -0.14 | 0.92976 | 0.95755 | 1.0785 | -0.043053
21 | -0.13 | 0.91219 | 0.93363 | 1.1209 | -0.080229
22 | 0.17 | 0.88747 | 0.96937 | 1.0302 | 0.04761
23 | -0.09 | 0.90825 | 0.90621 | 1.1283 | -0.10727
24 | -0.1 | 0.91881 | 0.94164 | 1.1029 | -0.066839
25 | 0.27 | 0.8618 | 0.90962 | 1.1004 | -0.040141
26 | -0.29 | 0.84292 | 0.89475 | 1.2569 | -0.14801
27 | 0.06 | 0.88127 | 0.92235 | 1.1574 | -0.088744
28 | -0.16 | 0.90517 | 0.92847 | 1.1438 | -0.097888
29 | -0.32 | 0.7277 | 0.84819 | 1.4536 | -0.18454
30 | -0.4 | 0.7627 | 0.82629 | 1.4987 | -0.27775
31 | -0.38 | 0.74788 | 0.84789 | 1.429 | -0.19414
32 | -0.18 | 0.92183 | 0.9518 | 1.173 | -0.11387
33 | -0.23 | 0.88578 | 0.93714 | 1.1961 | -0.11323
34 | -0.17 | 0.85803 | 0.87807 | 1.1942 | -0.129
35 | -0.14 | 0.92385 | 0.98975 | 1.1193 | -0.038949
36 | -0.22 | 0.73939 | 0.85139 | 1.4658 | -0.19629
37 | -0.08 | 0.75632 | 0.87026 | 1.3348 | -0.12283
39 | 0.04 | 0.96543 | 0.97157 | 1.0512 | -0.040401
40 | 0.29 | 0.84398 | 0.9204 | 1.182 | -0.071604
41 | -0.48 | 0.698 | 0.80912 | 1.5392 | -0.22572
42 | 0.09 | 0.89228 | 0.92535 | 1.1232 | -0.071341
43 | -0.2 | 0.70773 | 0.84154 | 1.4687 | -0.17165
44 | -0.1 | 0.76093 | 0.93419 | 1.3431 | -0.080981
45 | -0.06 | 0.96319 | 0.97631 | 1.0622 | -0.042021
46 | -0.13 | 0.90798 | 0.98859 | 1.1355 | -0.038719
47 | 0.14 | 0.68588 | 0.73237 | 1.3779 | -0.16431
49 | 0.19 | 0.88434 | 0.87446 | 1.0972 | -0.086786
50 | 0.19 | 0.93065 | 0.90098 | 1.0664 | -0.083828
51 | -0.34 | 0.91861 | 0.94467 | 1.1426 | -0.095651
52 | -0.22 | 0.85175 | 0.96045 | 1.1984 | -0.055665
53 | -0.22 | 0.93006 | 0.91547 | 1.2418 | -0.20822
54 | -0.1 | 0.89743 | 0.94343 | 1.1505 | -0.082569
55 | 0.13 | 0.88566 | 0.88198 | 1.0057 | -0.0087407
57 | -0.09 | 0.92983 | 0.99251 | 1.0811 | -0.011775
58 | -0.33 | 0.85053 | 0.88921 | 1.2703 | -0.16929
59 | -0.06 | 0.83545 | 0.96229 | 1.2534 | -0.079564
60 | 0.24 | 0.95962 | 1.014 | 1.0564 | 0.0022914
61 | -0.09 | 0.82903 | 0.97576 | 1.2352 | -0.045614
62 | -0.12 | 0.93466 | 0.97632 | 1.1342 | -0.076715
64 | -0.23 | 0.89638 | 0.86197 | 1.2001 | -0.18578
65 | -0.17 | 0.91083 | 0.92542 | 1.1526 | -0.1128
Commerical
C37 | -0.035294 | 1.0047 | 1.001 | 1.0243 | -0.024555
C55 | -0.093976 | 0.96066 | 0.96245 | 1.0876 | -0.07649
C59 | 0.092063 | 0.88237 | 0.93125 | 1.1228 | -0.055827
C60 | 0.1372 | 0.85833 | 0.90923 | 1.1696 | -0.086787
C34 | 0.13542 | 0.87944 | 0.89936 | 1.1177 | -0.075698
|  |  | Residential |  | Commerical
|  | Bin | Frequency |  | Frequency
|  | -0.5 | 1 |  | 0
|  | -0.45 | 1 |  | 0
|  | -0.4 | 2 |  | 0
|  | -0.35 | 1 |  | 0
|  | -0.3 | 5 |  | 0
|  | -0.25 | 1 |  | 0
|  | -0.2 | 5 |  | 0
|  | -0.15 | 5 |  | 0
|  | -0.1 | 6 |  | 0
|  | -0.05 | 10 |  | 2
|  | 0 | 0 |  | 1
|  | 0.05 | 1 |  | 0
|  | 0.1 | 4 |  | 1
|  | 0.15 | 4 |  | 2
|  | 0.2 | 5 |  | 0
|  | 0.25 | 1 |  | 0
|  | 0.3 | 2 |  | 0
|  | 0.35 | 1 |  | 0
|  | 0.4 | 1 |  | 0
|  | 0.45 | 0 |  | 0
|  | 0.5 | 0 |  | 0
|  | More | 0 |  | 0

## DOE-2.2 Performance Inputs
[10 empty] | Nonresidential Units |  |  |  | Residential Units (<=5 tons)
Site | Charge adjustment | Cap fraction | Sen Cap fraction | EIR fraction (comp&cond fan combined) | EIR fraction (compressor only) | % overall energy savings |  |  | N | Cap Frac | Sens Cap Frac | EIR Frac (comp and cond fan) | EIR Frac (comp only) | Cap Frac | Sens Cap Frac | EIR Frac (comp and cond fan) | EIR Frac (comp only)
6 | -0.78021 | 0.87971 | 0.92443 | 1.5379 | 1.5728 | -0.36397 |  | dCharge >= -20%: | 17 | 0.82553 | 0.88858 | 1.3473 | 1.3582 | 0.82553 | 0.88858 | 1.3473 | 1.3582
41 | -0.48 | 0.698 | 0.80912 | 1.5392 | 1.5484 | -0.22572 |  | dCharge 0 to -20%: | 22 | 0.90232 | 0.9506 | 1.1498 | 1.1529 | 0.89428 | 0.94748 | 1.1592 | 1.1623
1 | -0.4 | 0.82654 | 0.9118 | 1.3133 | 1.3223 | -0.15132 |  | dCharge 0 to +20%: | 17 | 0.88441 | 0.91196 | 1.1186 | 1.117 | 0.88677 | 0.91168 | 1.1147 | 1.113
30 | -0.4 | 0.7627 | 0.82629 | 1.4987 | 1.515 | -0.27775 |  | dCharge >= +20%: | 5 | 0.83945 | 0.90691 | 1.1593 | 1.1555 | 0.83945 | 0.90691 | 1.1593 | 1.1555
31 | -0.38 | 0.74788 | 0.84789 | 1.429 | 1.437 | -0.19414
51 | -0.34 | 0.91861 | 0.94467 | 1.1426 | 1.1473 | -0.095651 | Nonresidential Implementation Notes ("CA" means Customer Average)
58 | -0.33 | 0.85053 | 0.88921 | 1.2703 | 1.2785 | -0.16929 | COOLING-CAPACITY(CA) = COOLING-CAPACITY(szg) * <Cap Frac>, OUTSIDE-FAN-ELEC(CA) = OUTSIDE-FAN-ELEC(dxDetails) / <Cap Frac>
29 | -0.32 | 0.7277 | 0.84819 | 1.4536 | 1.4605 | -0.18454 |  | (Nonres units are simulated with separate condenser fan)
15 | -0.30971 | 0.89639 | 0.94145 | 1.3984 | 1.4231 | -0.26927 | COOL-SH-CAP(CA) = COOL-SH-CAP(szg) * <Sens Cap Frac>
16 | -0.30189 | 0.872 | 0.90016 | 1.2933 | 1.306 | -0.19707 | COOLING-EIR(CA) = COOLING-EIR(dxDetails & adjusted) * <EIR Frac (comp only)>; adjusted COOLING-EIR is the value of COOLING-EIR after adjustment for difference in referenc EER => dxDetails EER
26 | -0.29 | 0.84292 | 0.89475 | 1.2569 | 1.263 | -0.14801 |  | (Nonres units are simulated with separate condenser fan therefore, EIR includes only the compressor energy)
64 | -0.23 | 0.89638 | 0.86197 | 1.2001 | 1.2074 | -0.18578
33 | -0.23 | 0.88578 | 0.93714 | 1.1961 | 1.2019 | -0.11323 | Residential Implementation Notes ("CA" means Customer Average)
36 | -0.22 | 0.73939 | 0.85139 | 1.4658 | 1.4757 | -0.19629 | COOLING-CAPACITY(CA) = COOLING-CAPACITY(szg) * <Cap Frac>
52 | -0.22 | 0.85175 | 0.96045 | 1.1984 | 1.2005 | -0.055665 | COOL-SH-CAP(CA) = COOL-SH-CAP(szg) * <Sens Cap Frac>
53 | -0.22 | 0.93006 | 0.91547 | 1.2418 | 1.2563 | -0.20822 | COOLING-EIR(CA) = COOLING-EIR(dxDetails & adjusted) * <EIR Frac>; adjusted COOLING-EIR is the value of COOLING-EIR after adjustment for difference in referenc EER => dxDetails EER
43 | -0.2 | 0.70773 | 0.84154 | 1.4687 | 1.4736 | -0.17165
32 | -0.18 | 0.92183 | 0.9518 | 1.173 | 1.1807 | -0.11387
34 | -0.17 | 0.85803 | 0.87807 | 1.1942 | 1.1967 | -0.129
65 | -0.17 | 0.91083 | 0.92542 | 1.1526 | 1.1573 | -0.1128 | Refrigerant Adjustment Needed |  | N | Capacity Multiplier |  | EIR Multiplier
28 | -0.16 | 0.90517 | 0.92847 | 1.1438 | 1.1472 | -0.097888 |  |  |  | Total | Sensible
19 | -0.15 | 0.92898 | 0.95376 | 1.1513 | 1.1578 | -0.098552 | All units
17 | -0.14 | 0.92976 | 0.95755 | 1.0785 | 1.0788 | -0.043053 | Typical (< ±20%) |  | 39 | 0.89337 | 0.93128 | 1.1342
35 | -0.14 | 0.92385 | 0.98975 | 1.1193 | 1.1225 | -0.038949 | High (> ±20%) |  | 22 | 0.83249 | 0.89775 | 1.2533
21 | -0.13 | 0.91219 | 0.93363 | 1.1209 | 1.123 | -0.080229 | Residential (<= 5 tons)
46 | -0.13 | 0.90798 | 0.98859 | 1.1355 | 1.1384 | -0.038719 | Typical (< ±20%) |  | 37 | 0.89053 | 0.92958 | 1.1369
62 | -0.12 | 0.93466 | 0.97632 | 1.1342 | 1.1398 | -0.076715 | High (> ±20%) |  | 19 | 0.83249 | 0.89775 | 1.2533
24 | -0.1 | 0.91881 | 0.94164 | 1.1029 | 1.1042 | -0.066839
54 | -0.1 | 0.89743 | 0.94343 | 1.1505 | 1.1536 | -0.082569
44 | -0.1 | 0.76093 | 0.93419 | 1.3431 | 1.3456 | -0.080981
C55 | -0.093976 | 0.96066 | 0.96245 | 1.0876 | 1.0916 | -0.07649
23 | -0.09 | 0.90825 | 0.90621 | 1.1283 | 1.1307 | -0.10727
57 | -0.09 | 0.92983 | 0.99251 | 1.0811 | 1.0816 | -0.011775
61 | -0.09 | 0.82903 | 0.97576 | 1.2352 | 1.2377 | -0.045614
37 | -0.08 | 0.75632 | 0.87026 | 1.3348 | 1.3359 | -0.12283
14 | -0.07 | 0.95314 | 0.96369 | 1.0886 | 1.092 | -0.066615
45 | -0.06 | 0.96319 | 0.97631 | 1.0622 | 1.0643 | -0.042021
59 | -0.06 | 0.83545 | 0.96229 | 1.2534 | 1.2583 | -0.079564
C37 | -0.035294 | 1.0047 | 1.001 | 1.0243 | 1.0269 | -0.024555
39 | 0.04 | 0.96543 | 0.97157 | 1.0512 | 1.0525 | -0.040401
27 | 0.06 | 0.88127 | 0.92235 | 1.1574 | 1.1594 | -0.088744
16 | 0.07 | 0.93488 | 0.95271 | 1.0741 | 1.0745 | -0.048655
10 | 0.086 | 0.9111 | 0.94329 | 1.0632 | 1.0602 | -0.027928
42 | 0.09 | 0.89228 | 0.92535 | 1.1232 | 1.1234 | -0.071341
C59 | 0.092063 | 0.88237 | 0.93125 | 1.1228 | 1.1219 | -0.055827
7 | 0.11023 | 0.9166 | 0.94394 | 1.0763 | 1.075 | -0.041996
55 | 0.13 | 0.88566 | 0.88198 | 1.0057 | 0.99502 | -0.0087407
C34 | 0.13542 | 0.87944 | 0.89936 | 1.1177 | 1.116 | -0.075698
C60 | 0.1372 | 0.85833 | 0.90923 | 1.1696 | 1.17 | -0.086787
47 | 0.14 | 0.68588 | 0.73237 | 1.3779 | 1.3709 | -0.16431
9 | 0.15 | 0.89564 | 0.92413 | 1.2197 | 1.2287 | -0.13813
5 | 0.16 | 0.87425 | 0.88484 | 1.1309 | 1.1298 | -0.094011
22 | 0.17 | 0.88747 | 0.96937 | 1.0302 | 1.0218 | 0.04761
2 | 0.18 | 0.86942 | 0.9362 | 1.1322 | 1.1307 | -0.04707
49 | 0.19 | 0.88434 | 0.87446 | 1.0972 | 1.0943 | -0.086786
50 | 0.19 | 0.93065 | 0.90098 | 1.0664 | 1.0657 | -0.083828
60 | 0.24 | 0.95962 | 1.014 | 1.0564 | 1.0576 | 0.0022914
25 | 0.27 | 0.8618 | 0.90962 | 1.1004 | 1.0952 | -0.040141
40 | 0.29 | 0.84398 | 0.9204 | 1.182 | 1.1818 | -0.071604
11 | 0.34 | 0.7126 | 0.80643 | 1.3156 | 1.308 | -0.11154
20 | 0.38 | 0.81925 | 0.88406 | 1.142 | 1.1351 | -0.046339