## SUMMARY
|  | Filters: |  |  | % Better than Code:
|  | Code/Meas | Code |  | 10%
|  | Code | % |  | % Better than Code | %
|  | Com Gas Storagelte155kBtuh | 5% |  | Com Gas Storagelte155kBtuh | 5%
|  | Com Gas Storagegt155kBtuh | 5% |  | Com Gas Storagegt155kBtuh | 5%
|  | Com Gas Storage-Type Instantaneousgte200kBtuh | 5% |  | Com Gas Storage-Type Instantaneousgte200kBtuh | 5%
|  | Com Gas Storage-Type Instantaneouslt200kBtuh | 5% |  | Com Gas Storage-Type Instantaneouslt200kBtuh | 5%
|  | Com Gas Instantaneousgte200kBtuh | 5% |  | Com Gas Instantaneousgte200kBtuh | 5%
|  | Com Gas Hot Water Boilergte300kBtuh | 5% |  | Com Gas Hot Water Boilergte300kBtuh | 5%
COMMERCIAL WH TYPE COMMERCIAL WH TYPE COMMERCIAL WH TYPE COMMERCIAL WH TYPE COMMERCIAL WH TYPE COMMERCIAL WH TYPE COMMERCIAL WH TYPE COMMERCIAL WH TYPE COMMERCIAL WH TYPE COMMERCIAL WH TYPE COMMERCIAL WH TYPE COMMERCIAL WH TYPE COMMERCIAL WH TYPE COMMERCIAL WH TYPE COMMERCIAL WH TYPE
|  | Inventory |  | Com Gas Storage | Com Gas Storage | Com Gas Instantaneous | Com Gas Instantaneous | Com Gas Storage-Type Instantaneous | Com Gas Storage-Type Instantaneous | Com Gas Hot Water Boiler | Com Electric Heat Pump
MIN VOL (GAL) | MAX VOL (GAL) | CATEGORY |  | lte155kBtuh | gt155kBtuh | lt200kBtuh | gte200kBtuh | lt200kBtuh | gte200kBtuh | gte300kBtuh | gt12kW
|  | N/A |  | 30 | 114 | 0 | 1 | 2 | 43 | 3 | 0
-0.01 | 2 | 2
2 | 30 | 30
30 | 40 | 40
40 | 50 | 50
50 | 55 | 55
55 | 60 | 60
60 | 75 | 75
75 | 80 | 80
90 | 105 | 100
115 | 120 | 120
TOTAL
|  | Recovery or Thermal Efficiency (bin average), % |  | Com Gas Storage | Com Gas Storage | Com Gas Instantaneous | Com Gas Instantaneous | Com Gas Storage-Type Instantaneous | Com Gas Storage-Type Instantaneous | Com Gas Hot Water Boiler | Com Electric Heat Pump
MIN VOL (GAL) | MAX VOL (GAL) | CATEGORY |  | lte155kBtuh | gt155kBtuh | lt200kBtuh | gte200kBtuh | lt200kBtuh | gte200kBtuh | gte300kBtuh | gt12kW
|  | N/A |  | 80.1667 | 80.2632 | #DIV/0! | 80 | 80 | 80 | 84 | #DIV/0!
-0.01 | 2 | 2
2 | 30 | 30
30 | 40 | 40
40 | 50 | 50
50 | 55 | 55
55 | 60 | 60
60 | 75 | 75
75 | 80 | 80
90 | 105 | 100
115 | 120 | 120
|  | Input (bin average), kBtu/h (gas), kW (electric) |  | Com Gas Storage | Com Gas Storage | Com Gas Instantaneous | Com Gas Instantaneous | Com Gas Storage-Type Instantaneous | Com Gas Storage-Type Instantaneous | Com Gas Hot Water Boiler | Com Electric Heat Pump
MIN VOL (GAL) | MAX VOL (GAL) | CATEGORY |  | lte155kBtuh | gt155kBtuh | lt200kBtuh | gte200kBtuh | lt200kBtuh | gte200kBtuh | gte300kBtuh | gt12kW
|  | N/A |  | 120.6567 | 246.586 | #DIV/0! | 380 | 199.9 | 418.8233 | 1166.6667
-0.01 | 2 | 2
2 | 30 | 30
30 | 40 | 40
40 | 50 | 50
50 | 55 | 55
55 | 60 | 60
60 | 75 | 75
75 | 80 | 80
90 | 105 | 100
115 | 120 | 120
|  | Tank UA (bin average), Btu/h-F |  | Com Gas Storage | Com Gas Storage | Com Gas Instantaneous | Com Gas Instantaneous | Com Gas Storage-Type Instantaneous | Com Gas Storage-Type Instantaneous | Com Gas Hot Water Boiler | Com Electric Heat Pump
MIN VOL (GAL) | MAX VOL (GAL) | CATEGORY |  | lte155kBtuh | gt155kBtuh | lt200kBtuh | gte200kBtuh | lt200kBtuh | gte200kBtuh | gte300kBtuh | gt12kW
|  | N/A |  | 15.5927 | 18.4187 | #DIV/0! | 0 | 12.8571 | 19.5143 | 0 | #DIV/0!
-0.01 | 2 | 2
2 | 30 | 30
30 | 40 | 40
40 | 50 | 50
50 | 55 | 55
55 | 60 | 60
60 | 75 | 75
75 | 80 | 80
90 | 105 | 100
115 | 120 | 120
If #N/A where COUNT>0, is because some WH do not have their EF specified
|  | Volume, |  | Com Gas Storage | Com Gas Storage | Com Gas Instantaneous | Com Gas Instantaneous | Com Gas Storage-Type Instantaneous | Com Gas Storage-Type Instantaneous | Com Gas Hot Water Boiler | Com Electric Heat Pump
MIN VOL (GAL) | MAX VOL (GAL) | CATEGORY |  | lte155kBtuh | gt155kBtuh | lt200kBtuh | gte200kBtuh | lt200kBtuh | gte200kBtuh | gte300kBtuh | gt12kW
|  | N/A |  | 77.6667 | 88.7544 | #DIV/0! | 0.6 | 37 | 77 | 4.1 | #DIV/0!
-0.01 | 2 | 2
2 | 30 | 30
30 | 40 | 40
40 | 50 | 50
50 | 55 | 55
55 | 60 | 60
60 | 75 | 75
75 | 80 | 80
95 | 100 | 100
115 | 120 | 120
Source: https://energy.gov/sites/prod/files/2016/12/f34/WH_Conversion_Final%20Rule.pdf
Note on D63: Williams, Christopher: equal to Standby Loss divided by 70 (assumed temp differential between tank temperature and ambient)

## Tiers
[7 empty] | GPM | FHR | DRAW PATTERN
[7 empty] | 0 | 0 | VERY SMALL DRAW
[7 empty] | 1.7 | 18 | LOW DRAW
| Residential |  | UEF |  |  |  | 2.8 | 51 | MEDIUM DRAW
Tier | Measure | Volume Bin | LOW DRAW | MEDIUM DRAW | HIGH DRAW |  | 4 | 75 | HIGH DRAW
Code | Gas Instantaneous | 2 | 0.81 | 0.81 | 0.81
Code | Gas Storage | 30 | DNQ | 0.5973 | 0.653
Code | Gas Storage | 40 | DNQ | 0.5803 | 0.64
Code | Gas Storage | 50 | DNQ | 0.5633 | 0.627
Code | Gas Storage | 55 | DNQ | 0.5548 | 0.6205
Code | Gas Storage | 60 | DNQ | 0.7657 | 0.7892
Code | Gas Storage | 75 | DNQ | 0.7597 | 0.7847
Code | Gas Storage | 80 | DNQ | 0.7577 | 0.7832
Code | Gas Storage | 100 | DNQ | 0.7497 | 0.7772
Code | Gas Storage | 120 | DNQ | 0.4682 | 0.5517 | Res-Duty Commercial
Code | Integrated HPWH | 30 | 3 | 3 | 3
Code | Integrated HPWH | 40 | 3 | 3 | 3
Code | Integrated HPWH | 50 | 3 | 3 | 3
Code | Integrated HPWH | 55 | 3 | 3 | 3
Code | Integrated HPWH | 60 | 3 | 3 | 3
Code | Integrated HPWH | 75 | 3 | 3 | 3
Code | Integrated HPWH | 80 | 3 | 3 | 3
Code | Integrated HPWH | 100 | 3 | 3 | 3
Code | Integrated HPWH | 120 | 3 | 3 | 3
1 | Gas Instantaneous | 2 | 0.87 | 0.87 | 0.87
1 | Gas Storage | 30 | DNQ | 0.64 | 0.68
1 | Gas Storage | 40 | DNQ | 0.64 | 0.68
1 | Gas Storage | 50 | DNQ | 0.64 | 0.68
1 | Gas Storage | 55 | DNQ | 0.64 | 0.68
1 | Gas Storage | 60 | DNQ | 0.78 | 0.8
1 | Gas Storage | 75 | DNQ | 0.78 | 0.8
1 | Gas Storage | 80 | DNQ | 0.78 | 0.8
1 | Gas Storage | 100 | DNQ | 0.78 | 0.8
1 | Gas Storage | 120 | DNQ | 0.8 | 0.8 | Res-Duty Commercial
1 | Integrated HPWH | 30 | 3.3 | 3.3 | 3.3
1 | Integrated HPWH | 40 | 3.3 | 3.3 | 3.3
1 | Integrated HPWH | 50 | 3.3 | 3.3 | 3.3
1 | Integrated HPWH | 55 | 3.3 | 3.3 | 3.3
1 | Integrated HPWH | 60 | 3.3 | 3.3 | 3.3
1 | Integrated HPWH | 75 | 3.3 | 3.3 | 3.3
1 | Integrated HPWH | 80 | 3.3 | 3.3 | 3.3
1 | Integrated HPWH | 100 | 3.3 | 3.3 | 3.3
1 | Integrated HPWH | 120 | 3.3 | 3.3 | 3.3
2 | Gas Instantaneous | 2 | 0.91 | 0.91 | 0.91
2 | Integrated HPWH | 30 | 3.5 | 3.5 | 3.5
2 | Integrated HPWH | 40 | 3.5 | 3.5 | 3.5
2 | Integrated HPWH | 50 | 3.5 | 3.5 | 3.5
2 | Integrated HPWH | 55 | 3.5 | 3.5 | 3.5
2 | Integrated HPWH | 60 | 3.5 | 3.5 | 3.5
2 | Integrated HPWH | 75 | 3.5 | 3.5 | 3.5
2 | Integrated HPWH | 80 | 3.5 | 3.5 | 3.5
2 | Integrated HPWH | 100 | 3.5 | 3.5 | 3.5
2 | Integrated HPWH | 120 | 3.5 | 3.5 | 3.5
3 | Gas Instantaneous | 2 | 0.95 | 0.95 | 0.95
3 | Integrated HPWH | 30 | 3.75 | 3.75 | 3.75
3 | Integrated HPWH | 40 | 3.75 | 3.75 | 3.75
3 | Integrated HPWH | 50 | 3.75 | 3.75 | 3.75
3 | Integrated HPWH | 55 | 3.75 | 3.75 | 3.75
3 | Integrated HPWH | 60 | 3.75 | 3.75 | 3.75
3 | Integrated HPWH | 75 | 3.75 | 3.75 | 3.75
3 | Integrated HPWH | 80 | 3.75 | 3.75 | 3.75
3 | Integrated HPWH | 100 | 3.75 | 3.75 | 3.75
3 | Integrated HPWH | 120 | 3.75 | 3.75 | 3.75
2 | Gas Storage | 30 | DNQ | DNQ | 0.8
2 | Gas Storage | 40 | DNQ | DNQ | 0.8
2 | Gas Storage | 50 | DNQ | DNQ | 0.8

## Notes
ahri.net data was extracted 7/20/2021. Residential gas storage and residential gas instantaneous The following filters were made for AHRI data: (1) Exclude if Energy Source = HP and RE <=100 (2) Duplicates removed from Model Number column EnergyStar was extracted 7/20/2021. Residential all water heaters. The following filters were made: (1) Canada-only market models were removed (2) Solar heaters removed (3) Propane only heaters removed, NG/Propane heaters remain (4) Water heaters with no input capacity Note that "residential" water heaters may be offered under commercial programs. See definitions for specifications of residential application

## Definitions
Definitions are followed with references to their source:
RES CODE
Electric instantaneous water heater means a water heater that uses electricity as the energy source, has a nameplate input rating of 12 kW or less, and contains no more than one gallon of water per 4,000 Btu per hour of input.
10 CFR 430.2
Electric storage water heater means a water heater that uses electricity as the energy source, has a nameplate input rating of 12 kW or less, and contains more than one gallon of water per 4,000 Btu per hour of input.
10 CFR 430.2
Gas-fired instantaneous water heater means a water heater that uses gas as the main energy source, has a nameplate input rating less than 200,000 Btu/h, and contains no more than one gallon of water per 4,000 Btu per hour of input.
10 CFR 430.2
Gas-fired storage water heater means a water heater that uses gas as the main energy source, has a nameplate input rating of 75,000 Btu/h or less, and contains more than one gallon of water per 4,000 Btu per hour of input.
10 CFR 430.2
Heat pump type units, with a maximum current rating of 24 amperes at a voltage no greater than 250 volts, which are products designed to transfer thermal energy from one temperature level to a higher temperature level for the purpose of heating water, including all ancillary equipment such as fans, storage tanks, pumps, or controls necessary for the device to perform its function.
10 CFR 430.2
COMMERCIAL CODE
The term “storage water heater” means a water heater that heats and stores water within the appliance at a thermostatically controlled temperature for delivery on demand. Such term does not include units with an input rating of 4000 Btu per hour or more per gallon of stored water. (B) The term “instantaneous water heater” means a water heater that has an input rating of at least 4000 Btu per hour per gallon of stored water.
ES
Standby Loss (SL): The average hourly energy, expressed in Btu per hour, required to maintain the stored water temperature based on a 70°F temperature differential between stored water and ambient room temperature.
§ 431.102 Definitions concerning commercial water heaters, hot water supply boilers, unfired hot water storage tanks, and commercial heat pump water heaters.
Hot water supply boiler means a packaged boiler (defined in § 431.82 of this part) that is industrial equipment and that: (1) Has a rated input from 300,000 Btu/h to 12,500,000 Btu/h and of at least 4,000 Btu/h per gallon of stored water; (2) Is suitable for heating potable water; and (3) Meets either or both of the following conditions: (i) It has the temperature and pressure controls necessary for heating potable water for purposes other than space heating; or (ii) The manufacturer's product literature, product markings, product marketing, or product installation and operation instructions indicate that the boiler's intended uses include heating potable water for purposes other than space heating.
§ 431.102
Gas-fired instantaneous water heaters with a rated input both greater than 200,000 Btu/h and not less than 4,000 Btu/h per gallon of stored water;
§ 431.102
Storage-type instantaneous water heater means an instantaneous water heater that includes a storage tank with a storage volume greater than or equal to 10 gallons.
§ 431.102
Gas-fired storage water heaters with a rated input both greater than 75,000 Btu/h and less than 4,000 Btu/h per gallon of stored water;
§ 431.102
Residential-duty commercial water heater means any gas-fired storage, oil-fired storage, or electric instantaneous commercial water heater that meets the following conditions: (1) For models requiring electricity, uses single-phase external power supply; (2) Is not designed to provide outlet hot water at temperatures greater than 180 °F; and (3) Does not meet any of the following criteria:
Energy Star v.2
Commercial heat pump water heaters designed to transfer thermal energy from a low-temperature source to a higher-temperature sink for the purpose of heating potable water, including air-source, water-source, and direct geo-exchange units, with a rated electric power input greater than 12 kW (including all ancillary equipment such as fans, blowers, pumps, storage tanks, piping, and controls, as applicable).

## AHRI Pivot
Com WH TYPE | Com Gas Storage
Count of AHRI Certified Ratings - Thermal Efficiency (%) | Cap Bins
AHRI Certified Ratings - Thermal Efficiency (%) | gt155kBtuh | lte155kBtuh | Total Result
80 | 99 | 26 | 125
81 |  | 3 | 3
82 | 15 | 1 | 16
92 | 4 |  | 4
93 | 1 | 2 | 3
94 | 4 | 5 | 9
95 | 6 | 5 | 11
96 | 9 | 7 | 16
97 | 2 | 2 | 4
Total Result | 140 | 51 | 191

## AHRI
AHRI Certified Reference Number | Old AHRI Reference Number | Model Status | Brand Name | Series Name | Model Number | Energy Source | Heater Type | Rated Volume (gal) | Measured Volume (gal) | Input Rate (MBtu/h) | Input Rate (kW) | AHRI Certified Ratings - Thermal Efficiency (%) | AHRI Certified Ratings - Standby Loss (%/hour) | AHRI Certified Ratings - Standby Loss (Btu/h) | Hot Water Supply Boiler | Btuh per gallon | Com WH TYPE | Cap Bins | VOLUME BIN | CALC'ED UA USING UEF (BTU/HR-F) | WHTYPE+Cap Bin | Com Code TE | CLOSE TO RES CODE? | MIN QUALIFYING COM TE Tier 1 | MAX QUALIFYING COM TE Tier 1 | MIN QUALIFYING COM TE Tier 2 | MAX QUALIFYING COM TE Tier 2 | MIN QUALIFYING COM TE Tier 3 | MAX QUALIFYING COM TE Tier 3 | RES UEF QUALIFIES AS MEASURE TIER 1? | RES UEF QUALIFIES AS MEASURE TIER 2? | RES UEF QUALIFIES AS MEASURE TIER 3? | POTENTIAL DUPLICATE? | AHRI or ES
7056620 |  | Active | BRADFORD WHITE |  | EF100T399E*N2 | Natural Gas | Storage | 100 | 95 | 399 |  | 94 |  | 1075 | No | 3990 | Com Gas Storage | gt155kBtuh | 100 | 15.3571 | Com Gas Storagegt155kBtuh | 0.8 |  | 0.9 | 0.96 | 0.96 | N/A | N/A |  | Y |  |  | N | AHRI
7056629 |  | Active | BRADFORD WHITE |  | D-75T160**N2 | Natural Gas | Storage | 75 | 71.3 | 160 |  | 80 |  | 1051 | No | 2133.3333 | Com Gas Storage | gt155kBtuh | 75 | 15.0143 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
7056635 |  | Active | BRADFORD WHITE |  | D-100S250**** | Natural Gas | Storage | 100 | 95 | 250 |  | 80 |  | 1099 | No | 2500 | Com Gas Storage | gt155kBtuh | 100 | 15.7 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
7056648 |  | Active | BRADFORD WHITE |  | D-100L300**** | Natural Gas | Storage | 100 | 95 | 300 |  | 80 |  | 1236 | No | 3000 | Com Gas Storage | gt155kBtuh | 100 | 17.6571 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
7056653 |  | Active | BRADFORD WHITE |  | D-80T250**N* | Natural Gas | Storage | 80 | 76 | 250 |  | 80 |  | 1099 | No | 3125 | Com Gas Storage | gt155kBtuh | 80 | 15.7 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
7056666 |  | Active | BRADFORD WHITE |  | D-100L250**** | Natural Gas | Storage | 100 | 95 | 250 |  | 80 |  | 1236 | No | 2500 | Com Gas Storage | gt155kBtuh | 100 | 17.6571 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
7056667 |  | Active | BRADFORD WHITE |  | D-100L270**N* | Natural Gas | Storage | 100 | 95 | 270 |  | 80 |  | 1236 | No | 2700 | Com Gas Storage | gt155kBtuh | 100 | 17.6571 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
7056673 |  | Active | BRADFORD WHITE |  | D-100T250**N* | Natural Gas | Storage | 98 | 93.1 | 250 |  | 80 |  | 1238 | No | 2551.0204 | Com Gas Storage | gt155kBtuh | 100 | 17.6857 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
7056695 |  | Active | BRADFORD WHITE |  | UCG100H270*N* | Natural Gas | Storage | 100 | 95 | 270 |  | 82 |  | 1425 | No | 2700 | Com Gas Storage | gt155kBtuh | 100 | 20.3571 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
7056893 |  | Active | BRADFORD WHITE |  | UCG100H199*N* | Natural Gas | Storage | 100 | 95 | 199 |  | 82 |  | 1340 | No | 1990 | Com Gas Storage | gt155kBtuh | 100 | 19.1429 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
7056899 |  | Active | BRADFORD WHITE |  | UCG100H399*N* | Natural Gas | Storage | 100 | 95 | 399 |  | 82 |  | 1500 | No | 3990 | Com Gas Storage | gt155kBtuh | 100 | 21.4286 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
7057161 |  | Active | RHEEM/RUUD |  | G72-250 | Natural Gas | Storage | 72 | 69 | 250 |  | 80 |  | 1245.8 | No | 3472.2222 | Com Gas Storage | gt155kBtuh | 75 | 17.7971 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
7057164 |  | Active | RHEEM/RUUD |  | G100-200 | Natural Gas | Storage | 100 | 97 | 199.9 |  | 80 |  | 1349.8 | No | 1999 | Com Gas Storage | gt155kBtuh | 100 | 19.2829 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
7057165 |  | Active | RHEEM/RUUD |  | G100-250 | Natural Gas | Storage | 100 | 97 | 250 |  | 80 |  | 1412.5 | No | 2500 | Com Gas Storage | gt155kBtuh | 100 | 20.1786 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
7057167 |  | Active | RHEEM/RUUD |  | G100-310 | Natural Gas | Storage | 100 | 103 | 310 |  | 80 |  | 1487.5 | No | 3100 | Com Gas Storage | gt155kBtuh | 100 | 21.25 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
7057173 |  | Active | RHEEM/RUUD |  | G91-200 | Natural Gas | Storage | 91 | 87 | 199.9 |  | 80 |  | 1299 | No | 2196.7033 | Com Gas Storage | gt155kBtuh | 100 | 18.5571 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
7057175 |  | Active | BRADFORD WHITE |  | D100L199**N | Natural Gas | Storage | 100 | 95 | 199.9 |  | 80 |  | 1236 | No | 1999 | Com Gas Storage | gt155kBtuh | 100 | 17.6571 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
7057179 |  | Active | BRADFORD WHITE |  | D100S199**N | Natural Gas | Storage | 100 | 95 | 199.9 |  | 80 |  | 1099 | No | 1999 | Com Gas Storage | gt155kBtuh | 100 | 15.7 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
7057186 |  | Active | BRADFORD WHITE |  | D80T199**N | Natural Gas | Storage | 80 | 76 | 199.9 |  | 80 |  | 1099 | No | 2498.75 | Com Gas Storage | gt155kBtuh | 80 | 15.7 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
7057188 |  | Active | BRADFORD WHITE |  | DM80T199**N | Natural Gas | Storage | 80 | 76 | 199.9 |  | 80 |  | 1099 | No | 2498.75 | Com Gas Storage | gt155kBtuh | 80 | 15.7 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
7057190 |  | Active | BRADFORD WHITE |  | D80T180**N | Natural Gas | Storage | 80 | 76 | 180 |  | 80 |  | 1099 | No | 2250 | Com Gas Storage | gt155kBtuh | 80 | 15.7 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
7057194 |  | Active | BRADFORD WHITE |  | D75T125**N | Natural Gas | Storage | 75 | 71.3 | 125 |  | 80 |  | 1051 | No | 1666.6667 | Com Gas Storage | lte155kBtuh | 75 | 15.0143 | Com Gas Storagelte155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
7057199 |  | Active | BRADFORD WHITE |  | D100T199**N | Natural Gas | Storage | 98 | 95 | 199.9 |  | 80 |  | 1238 | No | 2039.7959 | Com Gas Storage | gt155kBtuh | 100 | 17.6857 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
7057201 |  | Active | BRADFORD WHITE |  | DM100T199**N | Natural Gas | Storage | 100 | 95 | 199.9 |  | 80 |  | 1238 | No | 1999 | Com Gas Storage | gt155kBtuh | 100 | 17.6857 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
7057258 |  | Active | RHEEM/RUUD |  | G100-400(A)-1 | Natural Gas | Storage | 100 | 97 | 399.9 |  | 80 |  | 1599 | No | 3999 | Com Gas Storage | gt155kBtuh | 100 | 22.8429 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
7057271 |  | Active | BRADFORD WHITE |  | EF100T300E*N*2 | Natural Gas | Storage | 100 | 95 | 300 |  | 92 |  | 1044 | No | 3000 | Com Gas Storage | gt155kBtuh | 100 | 14.9143 | Com Gas Storagegt155kBtuh | 0.8 |  | 0.9 | 0.96 | 0.96 | N/A | N/A |  | Y |  |  | N | AHRI
7057272 |  | Active | BRADFORD WHITE |  | EF60T125E*N*2 | Natural Gas | Storage | 60 | 57 | 125 |  | 96 |  | 824 | No | 2083.3333 | Com Gas Storage | lte155kBtuh | 60 | 11.7714 | Com Gas Storagelte155kBtuh | 0.8 |  | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  | Y |  | N | AHRI
7057273 |  | Active | BRADFORD WHITE |  | EF60T150E*N*2 | Natural Gas | Storage | 60 | 57 | 150 |  | 93 |  | 824 | No | 2500 | Com Gas Storage | lte155kBtuh | 60 | 11.7714 | Com Gas Storagelte155kBtuh | 0.8 |  | 0.9 | 0.96 | 0.96 | N/A | N/A |  | Y |  |  | N | AHRI
7057274 |  | Active | BRADFORD WHITE |  | EF60T199E*N*2 | Natural Gas | Storage | 60 | 57 | 199.9 |  | 92 |  | 824 | No | 3331.6667 | Com Gas Storage | gt155kBtuh | 60 | 11.7714 | Com Gas Storagegt155kBtuh | 0.8 |  | 0.9 | 0.96 | 0.96 | N/A | N/A |  | Y |  |  | N | AHRI
7057324 |  | Active | GIANT |  | UG73-125N-US | Natural Gas | Storage | 72 | 69 | 125 |  | 80 |  | 1050 | No | 1736.1111 | Com Gas Storage | lte155kBtuh | 75 | 15 | Com Gas Storagelte155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
7057325 |  | Active | GIANT |  | UG73-150N-US | Natural Gas | Storage | 70 | 66.9 | 150 |  | 80 |  | 1000 | No | 2142.8571 | Com Gas Storage | lte155kBtuh | 75 | 14.2857 | Com Gas Storagelte155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
7057326 |  | Active | GIANT |  | UG73-200N-US | Natural Gas | Storage | 68 | 64.7 | 199.9 |  | 80 |  | 1000 | No | 2939.7059 | Com Gas Storage | gt155kBtuh | 75 | 14.2857 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
7057353 |  | Active | RHEEM/RUUD |  | GN91-200 | Natural Gas | Storage | 91 | 87 | 199.9 |  | 80 |  | 1299.2 | No | 2196.7033 | Com Gas Storage | gt155kBtuh | 100 | 18.56 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
7057354 |  | Active | RHEEM/RUUD |  | GN100-200(A) | Natural Gas | Storage | 100 | 97 | 199.9 |  | 80 |  | 1349.8 | No | 1999 | Com Gas Storage | gt155kBtuh | 100 | 19.2829 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
7057355 |  | Active | RHEEM/RUUD |  | GN100-250(A) | Natural Gas | Storage | 100 | 97 | 250 |  | 80 |  | 1412 | No | 2500 | Com Gas Storage | gt155kBtuh | 100 | 20.1714 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
7057356 |  | Active | RHEEM/RUUD |  | GN100-270(A) | Natural Gas | Storage | 100 | 97 | 270 |  | 80 |  | 1437.5 | No | 2700 | Com Gas Storage | gt155kBtuh | 100 | 20.5357 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
7057357 |  | Active | RHEEM/RUUD |  | GN100-400(A) | Natural Gas | Storage | 100 | 103 | 399.9 |  | 80 |  | 1599.8 | No | 3999 | Com Gas Storage | gt155kBtuh | 100 | 22.8543 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
7057359 |  | Active | RHEEM/RUUD |  | GN75-125 | Natural Gas | Storage | 75 | 74 | 125 |  | 80 |  | 1108.8 | No | 1666.6667 | Com Gas Storage | lte155kBtuh | 75 | 15.84 | Com Gas Storagelte155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
7057360 |  | Active | RHEEM/RUUD |  | GN72-250(A) | Natural Gas | Storage | 72 | 69 | 250 |  | 80 |  | 1245.8 | No | 3472.2222 | Com Gas Storage | gt155kBtuh | 75 | 17.7971 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
7057361 |  | Active | RHEEM/RUUD |  | GN76-200 | Natural Gas | Storage | 76 | 74 | 199.9 |  | 80 |  | 1208.8 | No | 2630.2632 | Com Gas Storage | gt155kBtuh | 80 | 17.2686 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
7057362 |  | Active | RHEEM/RUUD |  | GN82-156 | Natural Gas | Storage | 82 | 78 | 156 |  | 80 |  | 1191 | No | 1902.439 | Com Gas Storage | gt155kBtuh | 100 | 17.0143 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
7057363 |  | Active | RHEEM/RUUD |  | GN65-360(A) | Natural Gas | Storage | 65 | 62 | 360 |  | 80 |  | 1099 | No | 5538.4615 | Com Gas Storage | gt155kBtuh | 75 | 15.7 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
7057372 |  | Active | RHEEM/RUUD |  | GNU37-200 | Natural Gas | Storage | 35 | 34.8 | 199.9 |  | 82 |  | 900 | No | 5711.4286 | Com Gas Storage | gt155kBtuh | 40 | 12.8571 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
7057373 |  | Active | RHEEM/RUUD |  | GNU65-360 | Natural Gas | Storage | 65 | 63 | 360 |  | 80 |  | 1336 | No | 5538.4615 | Com Gas Storage | gt155kBtuh | 75 | 19.0857 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
7057374 |  | Active | RHEEM/RUUD |  | GNU72-250 | Natural Gas | Storage | 72 | 69.1 | 250 |  | 80 |  | 1245 | No | 3472.2222 | Com Gas Storage | gt155kBtuh | 75 | 17.7857 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
7057375 |  | Active | RHEEM/RUUD |  | GNU75-125 | Natural Gas | Storage | 75 | 71.3 | 125 |  | 80 |  | 1108 | No | 1666.6667 | Com Gas Storage | lte155kBtuh | 75 | 15.8286 | Com Gas Storagelte155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
7057376 |  | Active | RHEEM/RUUD |  | GNU76-200 | Natural Gas | Storage | 76 | 73 | 199.9 |  | 80 |  | 1208 | No | 2630.2632 | Com Gas Storage | gt155kBtuh | 80 | 17.2571 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
7057377 |  | Active | RHEEM/RUUD |  | GNU82-156 | Natural Gas | Storage | 82 | 78.2 | 156 |  | 80 |  | 1191 | No | 1902.439 | Com Gas Storage | gt155kBtuh | 100 | 17.0143 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
7057378 |  | Active | RICHMOND |  | TNU100-200 | Natural Gas | Storage | 100 | 97 | 199.9 |  | 82 |  | 1349 | No | 1999 | Com Gas Storage | gt155kBtuh | 100 | 19.2714 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
7057379 |  | Active | RICHMOND |  | TNU100-250 | Natural Gas | Storage | 100 | 97 | 250 |  | 82 |  | 1412 | No | 2500 | Com Gas Storage | gt155kBtuh | 100 | 20.1714 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
7057380 |  | Active | RICHMOND |  | TNU100-270 | Natural Gas | Storage | 100 | 97 | 270 |  | 82 |  | 1437 | No | 2700 | Com Gas Storage | gt155kBtuh | 100 | 20.5286 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
7057381 |  | Active | RICHMOND |  | TNU100-400 | Natural Gas | Storage | 100 | 103 | 399.9 |  | 80 |  | 1599 | No | 3999 | Com Gas Storage | gt155kBtuh | 100 | 22.8429 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
7057382 |  | Active | RICHMOND |  | TNU65-360 | Natural Gas | Storage | 65 | 63 | 360 |  | 80 |  | 1336 | No | 5538.4615 | Com Gas Storage | gt155kBtuh | 75 | 19.0857 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
7057383 |  | Active | RICHMOND |  | TNU72-250 | Natural Gas | Storage | 72 | 69.1 | 250 |  | 80 |  | 1245 | No | 3472.2222 | Com Gas Storage | gt155kBtuh | 75 | 17.7857 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
7057384 |  | Active | RICHMOND |  | TNU75-125 | Natural Gas | Storage | 75 | 71.3 | 125 |  | 80 |  | 1108 | No | 1666.6667 | Com Gas Storage | lte155kBtuh | 75 | 15.8286 | Com Gas Storagelte155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
7057385 |  | Active | RICHMOND |  | TNU76-200 | Natural Gas | Storage | 76 | 73 | 199.9 |  | 80 |  | 1208 | No | 2630.2632 | Com Gas Storage | gt155kBtuh | 80 | 17.2571 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
7057386 |  | Active | RICHMOND |  | TNU82-156 | Natural Gas | Storage | 82 | 78.2 | 156 |  | 80 |  | 1191 | No | 1902.439 | Com Gas Storage | gt155kBtuh | 100 | 17.0143 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
7057387 |  | Active | RICHMOND |  | TNU91-200 | Natural Gas | Storage | 91 | 87.2 | 199.9 |  | 82 |  | 1299 | No | 2196.7033 | Com Gas Storage | gt155kBtuh | 100 | 18.5571 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
7057388 |  | Active | RHEEM/RUUD |  | GNU91-200 | Natural Gas | Storage | 91 | 87.2 | 199.9 |  | 82 |  | 1299 | No | 2196.7033 | Com Gas Storage | gt155kBtuh | 100 | 18.5571 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
7057389 |  | Active | RHEEM/RUUD |  | GNU100-200 | Natural Gas | Storage | 100 | 97 | 199.9 |  | 82 |  | 1349 | No | 1999 | Com Gas Storage | gt155kBtuh | 100 | 19.2714 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
7057391 |  | Active | RHEEM/RUUD |  | GNU100-270 | Natural Gas | Storage | 100 | 97 | 270 |  | 82 |  | 1437 | No | 2700 | Com Gas Storage | gt155kBtuh | 100 | 20.5286 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
7057392 |  | Active | RHEEM/RUUD |  | GNU100-400 | Natural Gas | Storage | 100 | 103 | 399.9 |  | 80 |  | 1599 | No | 3999 | Com Gas Storage | gt155kBtuh | 100 | 22.8429 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
7057393 |  | Active | RICHMOND |  | TNU37-200 | Natural Gas | Storage | 35 | 34.8 | 199.9 |  | 82 |  | 900 | No | 5711.4286 | Com Gas Storage | gt155kBtuh | 40 | 12.8571 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
7057402 |  | Active | RICHMOND |  | T100-200 | Natural Gas | Storage | 100 | 97 | 199.9 |  | 80 |  | 1349.8 | No | 1999 | Com Gas Storage | gt155kBtuh | 100 | 19.2829 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
7057405 |  | Active | RICHMOND |  | T100-310 | Natural Gas | Storage | 100 | 103 | 310 |  | 80 |  | 1487.5 | No | 3100 | Com Gas Storage | gt155kBtuh | 100 | 21.25 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
7057411 |  | Active | RICHMOND |  | T91-200 | Natural Gas | Storage | 91 | 87 | 199.9 |  | 80 |  | 1299 | No | 2196.7033 | Com Gas Storage | gt155kBtuh | 100 | 18.5571 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
7057412 |  | Active | RICHMOND |  | T65-360 | Natural Gas | Storage | 65 | 62 | 360 |  | 80 |  | 1003 | No | 5538.4615 | Com Gas Storage | gt155kBtuh | 75 | 14.3286 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
7057414 |  | Active | RICHMOND |  | T72-250 | Natural Gas | Storage | 72 | 69 | 250 |  | 80 |  | 1245.8 | No | 3472.2222 | Com Gas Storage | gt155kBtuh | 75 | 17.7971 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
7057769 |  | Active | HTP |  | CG125N73 | Natural Gas | Storage | 72 | 69 | 125 |  | 80 |  | 1050 | No | 1736.1111 | Com Gas Storage | lte155kBtuh | 75 | 15 | Com Gas Storagelte155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
7057770 |  | Active | HTP |  | CG150N73 | Natural Gas | Storage | 70 | 66.9 | 150 |  | 80 |  | 1000 | No | 2142.8571 | Com Gas Storage | lte155kBtuh | 75 | 14.2857 | Com Gas Storagelte155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
7057771 |  | Active | HTP |  | CG199N73 | Natural Gas | Storage | 68 | 64.7 | 199.9 |  | 80 |  | 1000 | No | 2939.7059 | Com Gas Storage | gt155kBtuh | 75 | 14.2857 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
7057888 |  | Active | RHEEM-RUUD UNIVERSAL |  | T100-400(A)-1 | Natural Gas | Storage | 100 | 97 | 399.9 |  | 80 |  | 1599 | No | 3999 | Com Gas Storage | gt155kBtuh | 100 | 22.8429 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
7057992 |  | Active | RICHMOND |  | TN76-200 | Natural Gas | Storage | 76 | 74 | 199.9 |  | 80 |  | 1208.8 | No | 2630.2632 | Com Gas Storage | gt155kBtuh | 80 | 17.2686 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
7057993 |  | Active | RICHMOND |  | TN65-360(A) | Natural Gas | Storage | 65 | 62 | 360 |  | 80 |  | 1099 | No | 5538.4615 | Com Gas Storage | gt155kBtuh | 75 | 15.7 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
7057994 |  | Active | RICHMOND |  | TN91-200 | Natural Gas | Storage | 91 | 87 | 199.9 |  | 80 |  | 1299.2 | No | 2196.7033 | Com Gas Storage | gt155kBtuh | 100 | 18.56 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
7057995 |  | Active | RICHMOND |  | TN100-200(A) | Natural Gas | Storage | 100 | 97 | 199.9 |  | 80 |  | 1349.8 | No | 1999 | Com Gas Storage | gt155kBtuh | 100 | 19.2829 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
7057998 |  | Active | RICHMOND |  | TN100-400(A) | Natural Gas | Storage | 100 | 103 | 399.9 |  | 80 |  | 1599.8 | No | 3999 | Com Gas Storage | gt155kBtuh | 100 | 22.8543 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
7058000 |  | Active | RICHMOND |  | TN75-125 | Natural Gas | Storage | 75 | 74 | 125 |  | 80 |  | 1108.8 | No | 1666.6667 | Com Gas Storage | lte155kBtuh | 75 | 15.84 | Com Gas Storagelte155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
7058001 |  | Active | RICHMOND |  | TN72-250(A) | Natural Gas | Storage | 72 | 69 | 250 |  | 80 |  | 1245.8 | No | 3472.2222 | Com Gas Storage | gt155kBtuh | 75 | 17.7971 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
7058002 |  | Active | RICHMOND |  | TN82-156 | Natural Gas | Storage | 82 | 78 | 156 |  | 80 |  | 1191 | No | 1902.439 | Com Gas Storage | gt155kBtuh | 100 | 17.0143 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
7089058 |  | Active | RHEEM/RUUD |  | GNU100-250 | Natural Gas | Storage | 100 | 97 | 250 |  | 82 |  | 1412 | No | 2500 | Com Gas Storage | gt155kBtuh | 100 | 20.1714 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
8482812 |  | Active | BRADFORD WHITE |  | UCG80H125*N* | Natural Gas | Storage | 80 | 76 | 125 |  | 82 |  | 1140 | No | 1562.5 | Com Gas Storage | lte155kBtuh | 80 | 16.2857 | Com Gas Storagelte155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
8482814 |  | Active | BRADFORD WHITE |  | UCG80H199*N* | Natural Gas | Storage | 80 | 76 | 199 |  | 82 |  | 1232 | No | 2487.5 | Com Gas Storage | gt155kBtuh | 80 | 17.6 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
8482835 |  | Active | BRADFORD WHITE |  | UCG80H270*N* | Natural Gas | Storage | 80 | 76 | 270 |  | 82 |  | 1321 | No | 3375 | Com Gas Storage | gt155kBtuh | 80 | 18.8714 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
202887518 |  | Active | BRADFORD WHITE |  | EF120T400*N*3 | Natural Gas | Storage | 119 | 113.1 | 399.9 |  | 94 |  | 1427 | No | 3360.5042 | Com Gas Storage | gt155kBtuh | 120 | 20.3857 | Com Gas Storagegt155kBtuh | 0.8 |  | 0.9 | 0.96 | 0.96 | N/A | N/A |  | Y |  |  | N | AHRI
203120864 |  | Active | LAARS |  | LUHE100T300E*N* | Natural Gas | Storage | 100 | 95 | 300 |  | 92 |  | 1044 | No | 3000 | Com Gas Storage | gt155kBtuh | 100 | 14.9143 | Com Gas Storagegt155kBtuh | 0.8 |  | 0.9 | 0.96 | 0.96 | N/A | N/A |  | Y |  |  | N | AHRI
203120867 |  | Active | LAARS |  | LUHE100T399E*N* | Natural Gas | Storage | 100 | 95 | 399 |  | 94 |  | 1075 | No | 3990 | Com Gas Storage | gt155kBtuh | 100 | 15.3571 | Com Gas Storagegt155kBtuh | 0.8 |  | 0.9 | 0.96 | 0.96 | N/A | N/A |  | Y |  |  | N | AHRI
203120868 |  | Active | LAARS |  | LUHE120T400*N*3 | Natural Gas | Storage | 119 | 113.1 | 399.9 |  | 94 |  | 1427 | No | 3360.5042 | Com Gas Storage | gt155kBtuh | 120 | 20.3857 | Com Gas Storagegt155kBtuh | 0.8 |  | 0.9 | 0.96 | 0.96 | N/A | N/A |  | Y |  |  | N | AHRI
203120872 |  | Active | LAARS |  | LUHE60T125E*N* | Natural Gas | Storage | 60 | 57 | 125 |  | 96 |  | 824 | No | 2083.3333 | Com Gas Storage | lte155kBtuh | 60 | 11.7714 | Com Gas Storagelte155kBtuh | 0.8 |  | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  | Y |  | N | AHRI
203120874 |  | Active | LAARS |  | LUHE60T150E*N* | Natural Gas | Storage | 60 | 57 | 150 |  | 93 |  | 824 | No | 2500 | Com Gas Storage | lte155kBtuh | 60 | 11.7714 | Com Gas Storagelte155kBtuh | 0.8 |  | 0.9 | 0.96 | 0.96 | N/A | N/A |  | Y |  |  | N | AHRI
203120876 |  | Active | LAARS |  | LUHE60T199E*N* | Natural Gas | Storage | 60 | 57 | 199.9 |  | 92 |  | 824 | No | 3331.6667 | Com Gas Storage | gt155kBtuh | 60 | 11.7714 | Com Gas Storagegt155kBtuh | 0.8 |  | 0.9 | 0.96 | 0.96 | N/A | N/A |  | Y |  |  | N | AHRI
204803821 |  | Active | BRADFORD WHITE |  | EF100T199E*N** | Natural Gas | Storage | 100 | 96.5 | 199.9 |  | 97 |  | 1130 | No | 1999 | Com Gas Storage | gt155kBtuh | 100 | 16.1429 | Com Gas Storagegt155kBtuh | 0.8 |  | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  | Y |  | N | AHRI
204803822 |  | Active | BRADFORD WHITE |  | EF100T150E*N** | Natural Gas | Storage | 100 | 96.5 | 150 |  | 97 |  | 1080 | No | 1500 | Com Gas Storage | lte155kBtuh | 100 | 15.4286 | Com Gas Storagelte155kBtuh | 0.8 |  | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  | Y |  | N | AHRI
204803823 |  | Active | BRADFORD WHITE |  | EF100T250E*N** | Natural Gas | Storage | 100 | 96.5 | 250 |  | 96 |  | 1180 | No | 2500 | Com Gas Storage | gt155kBtuh | 100 | 16.8571 | Com Gas Storagegt155kBtuh | 0.8 |  | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  | Y |  | N | AHRI
204820718 |  | Active | LAARS |  | LUHE100T199E*N** | Natural Gas | Storage | 100 | 96.5 | 199.9 |  | 97 |  | 1130 | No | 1999 | Com Gas Storage | gt155kBtuh | 100 | 16.1429 | Com Gas Storagegt155kBtuh | 0.8 |  | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  | Y |  | N | AHRI
204820719 |  | Active | LAARS |  | LUHE100T150E*N** | Natural Gas | Storage | 100 | 96.5 | 150 |  | 97 |  | 1080 | No | 1500 | Com Gas Storage | lte155kBtuh | 100 | 15.4286 | Com Gas Storagelte155kBtuh | 0.8 |  | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  | Y |  | N | AHRI
204820720 |  | Active | LAARS |  | LUHE100T250E*N** | Natural Gas | Storage | 100 | 96.5 | 250 |  | 96 |  | 1180 | No | 2500 | Com Gas Storage | gt155kBtuh | 100 | 16.8571 | Com Gas Storagegt155kBtuh | 0.8 |  | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  | Y |  | N | AHRI
205733370 |  | Active | LOCHINVAR |  | SWR125N | Natural Gas | Storage | 65 | 64.5 | 125 |  | 96 |  | 876 | No | 1923.0769 | Com Gas Storage | lte155kBtuh | 75 | 12.5143 | Com Gas Storagelte155kBtuh | 0.8 |  | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  | Y |  | N | AHRI
205733371 |  | Active | LOCHINVAR |  | SWA150N | Natural Gas | Storage | 90 | 88.6 | 150 |  | 96 |  | 1034 | No | 1666.6667 | Com Gas Storage | lte155kBtuh | 100 | 14.7714 | Com Gas Storagelte155kBtuh | 0.8 |  | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  | Y |  | N | AHRI
205733372 |  | Active | LOCHINVAR |  | SWA200N | Natural Gas | Storage | 90 | 88 | 199 |  | 96 |  | 1085 | No | 2211.1111 | Com Gas Storage | gt155kBtuh | 100 | 15.5 | Com Gas Storagegt155kBtuh | 0.8 |  | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  | Y |  | N | AHRI
205733373 |  | Active | LOCHINVAR |  | SWA400N | Natural Gas | Storage | 110 | 107.2 | 399 |  | 95 |  | 1388 | No | 3627.2727 | Com Gas Storage | gt155kBtuh | 120 | 19.8286 | Com Gas Storagegt155kBtuh | 0.8 |  | 0.9 | 0.96 | 0.96 | N/A | N/A |  | Y |  |  | N | AHRI
205733376 |  | Active | LOCHINVAR |  | SWR150N | Natural Gas | Storage | 90 | 88.6 | 150 |  | 96 |  | 1034 | No | 1666.6667 | Com Gas Storage | lte155kBtuh | 100 | 14.7714 | Com Gas Storagelte155kBtuh | 0.8 |  | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  | Y |  | N | AHRI
205733379 |  | Active | LOCHINVAR |  | SWR200N | Natural Gas | Storage | 90 | 88 | 199 |  | 96 |  | 1085 | No | 2211.1111 | Com Gas Storage | gt155kBtuh | 100 | 15.5 | Com Gas Storagegt155kBtuh | 0.8 |  | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  | Y |  | N | AHRI
205733382 |  | Active | LOCHINVAR |  | SWR400N | Natural Gas | Storage | 110 | 107.2 | 399 |  | 95 |  | 1388 | No | 3627.2727 | Com Gas Storage | gt155kBtuh | 120 | 19.8286 | Com Gas Storagegt155kBtuh | 0.8 |  | 0.9 | 0.96 | 0.96 | N/A | N/A |  | Y |  |  | N | AHRI
205733385 |  | Active | LOCHINVAR |  | SWA285N | Natural Gas | Storage | 110 | 104.9 | 285 |  | 95 |  | 1268 | No | 2590.9091 | Com Gas Storage | gt155kBtuh | 120 | 18.1143 | Com Gas Storagegt155kBtuh | 0.8 |  | 0.9 | 0.96 | 0.96 | N/A | N/A |  | Y |  |  | N | AHRI
205733388 |  | Active | LOCHINVAR |  | SWR285N | Natural Gas | Storage | 110 | 104.9 | 285 |  | 95 |  | 1268 | No | 2590.9091 | Com Gas Storage | gt155kBtuh | 120 | 18.1143 | Com Gas Storagegt155kBtuh | 0.8 |  | 0.9 | 0.96 | 0.96 | N/A | N/A |  | Y |  |  | N | AHRI
205782078 |  | Active | CAMUS HYDRONICS | Vtech | VTNW-0080 | Natural Gas | Storage | 60 | 56.1 | 80 |  | 95 |  | 598 | No | 1333.3333 | Com Gas Storage | lte155kBtuh | 60 | 8.5429 | Com Gas Storagelte155kBtuh | 0.8 |  | 0.9 | 0.96 | 0.96 | N/A | N/A |  | Y |  |  | N | AHRI
205782079 |  | Active | CAMUS HYDRONICS | Vtech | VTNW-0100 | Natural Gas | Storage | 60 | 56.1 | 100 |  | 94 |  | 643 | No | 1666.6667 | Com Gas Storage | lte155kBtuh | 60 | 9.1857 | Com Gas Storagelte155kBtuh | 0.8 |  | 0.9 | 0.96 | 0.96 | N/A | N/A |  | Y |  |  | N | AHRI
205782080 |  | Active | CAMUS HYDRONICS | Vtech | VTNW-0125 | Natural Gas | Storage | 80 | 81.2 | 125 |  | 94 |  | 458 | No | 1562.5 | Com Gas Storage | lte155kBtuh | 80 | 6.5429 | Com Gas Storagelte155kBtuh | 0.8 |  | 0.9 | 0.96 | 0.96 | N/A | N/A |  | Y |  |  | N | AHRI
205782081 |  | Active | CAMUS HYDRONICS | Vtech | VTNW-0150 | Natural Gas | Storage | 80 | 81.2 | 150 |  | 94 |  | 529 | No | 1875 | Com Gas Storage | lte155kBtuh | 80 | 7.5571 | Com Gas Storagelte155kBtuh | 0.8 |  | 0.9 | 0.96 | 0.96 | N/A | N/A |  | Y |  |  | N | AHRI
205782082 |  | Active | CAMUS HYDRONICS | Vtech | VTNW-0199 | Natural Gas | Storage | 100 | 96.6 | 199 |  | 96 |  | 534 | No | 1990 | Com Gas Storage | gt155kBtuh | 100 | 7.6286 | Com Gas Storagegt155kBtuh | 0.8 |  | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  | Y |  | N | AHRI
205782083 |  | Active | CAMUS HYDRONICS | Vtech | VTNW-0250 | Natural Gas | Storage | 100 | 96.6 | 250 |  | 95 |  | 662.5 | No | 2500 | Com Gas Storage | gt155kBtuh | 100 | 9.4643 | Com Gas Storagegt155kBtuh | 0.8 |  | 0.9 | 0.96 | 0.96 | N/A | N/A |  | Y |  |  | N | AHRI
205782084 |  | Active | CAMUS HYDRONICS | Vtech | VTNW-0299 | Natural Gas | Storage | 100 | 96.9 | 299 |  | 95 |  | 1199 | No | 2990 | Com Gas Storage | gt155kBtuh | 100 | 17.1286 | Com Gas Storagegt155kBtuh | 0.8 |  | 0.9 | 0.96 | 0.96 | N/A | N/A |  | Y |  |  | N | AHRI
205782085 |  | Active | CAMUS HYDRONICS | Vtech | VTNW-0399 | Natural Gas | Storage | 100 | 96.9 | 399 |  | 93 |  | 688 | No | 3990 | Com Gas Storage | gt155kBtuh | 100 | 9.8286 | Com Gas Storagegt155kBtuh | 0.8 |  | 0.9 | 0.96 | 0.96 | N/A | N/A |  | Y |  |  | N | AHRI
205805688 |  | Active | BRADFORD WHITE |  | D38T155**N* | Natural Gas | Storage | 38 | 36.1 | 150 |  | 80 |  | 850 | No | 3947.3684 | Com Gas Storage | lte155kBtuh | 40 | 12.1429 | Com Gas Storagelte155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
205976838 |  | Active | LOCHINVAR |  | CGN 180076* 1** | Natural Gas | Storage | 76 | 72.9 | 180 |  | 80 |  | 1160 | No | 2368.4211 | Com Gas Storage | gt155kBtuh | 80 | 16.5714 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
206216205 |  | Active | A. O. SMITH |  | BTL 120 2** | Natural Gas | Storage | 81 | 79.4 | 120 |  | 80 |  | 1130 | No | 1481.4815 | Com Gas Storage | lte155kBtuh | 100 | 16.1429 | Com Gas Storagelte155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
206216206 |  | Active | A. O. SMITH |  | BTL 154 2** | Natural Gas | Storage | 81 | 80.1 | 154 |  | 80 |  | 1170 | No | 1901.2346 | Com Gas Storage | lte155kBtuh | 100 | 16.7143 | Com Gas Storagelte155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
206216207 |  | Active | A. O. SMITH |  | BTL 180 2** | Natural Gas | Storage | 81 | 80.6 | 180 |  | 80 |  | 1200 | No | 2222.2222 | Com Gas Storage | gt155kBtuh | 100 | 17.1429 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
206216208 |  | Active | A. O. SMITH |  | BTL 198 2** | Natural Gas | Storage | 81 | 77 | 199 |  | 80 |  | 1230 | No | 2456.7901 | Com Gas Storage | gt155kBtuh | 100 | 17.5714 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
206216209 |  | Active | A. O. SMITH |  | BTL 199 2** | Natural Gas | Storage | 100 | 95.1 | 199 |  | 80 |  | 1300 | No | 1990 | Com Gas Storage | gt155kBtuh | 100 | 18.5714 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
206216210 |  | Active | A. O. SMITH |  | BTL 275* 2** | Natural Gas | Storage | 100 | 95.3 | 275 |  | 80 |  | 1400 | No | 2750 | Com Gas Storage | gt155kBtuh | 100 | 20 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
206216211 |  | Active | A. O. SMITH |  | BTL 310* 2** | Natural Gas | Storage | 86 | 89.2 | 310 |  | 80 |  | 1400 | No | 3604.6512 | Com Gas Storage | gt155kBtuh | 100 | 20 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
206216214 |  | Active | A. O. SMITH |  | BTL 250* 2** | Natural Gas | Storage | 100 | 95.3 | 250 |  | 80 |  | 1350 | No | 2500 | Com Gas Storage | gt155kBtuh | 100 | 19.2857 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
206217044 |  | Active | AMERICAN |  | BCL380T1206NOX 2** | Natural Gas | Storage | 81 | 79.4 | 120 |  | 80 |  | 1130 | No | 1481.4815 | Com Gas Storage | lte155kBtuh | 100 | 16.1429 | Com Gas Storagelte155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
206217045 |  | Active | LOCHINVAR |  | CLN120080 2** | Natural Gas | Storage | 81 | 79.4 | 120 |  | 80 |  | 1130 | No | 1481.4815 | Com Gas Storage | lte155kBtuh | 100 | 16.1429 | Com Gas Storagelte155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
206217046 |  | Active | RELIANCE WATER HEATERS |  | L81120NE 2** | Natural Gas | Storage | 81 | 79.4 | 120 |  | 80 |  | 1130 | No | 1481.4815 | Com Gas Storage | lte155kBtuh | 100 | 16.1429 | Com Gas Storagelte155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
206217047 |  | Active | STATE |  | SBL81120NE 2** | Natural Gas | Storage | 81 | 79.4 | 120 |  | 80 |  | 1130 | No | 1481.4815 | Com Gas Storage | lte155kBtuh | 100 | 16.1429 | Com Gas Storagelte155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
206217048 |  | Active | AMERICAN |  | BCL380T1546NOX 2** | Natural Gas | Storage | 81 | 80.1 | 154 |  | 80 |  | 1170 | No | 1901.2346 | Com Gas Storage | lte155kBtuh | 100 | 16.7143 | Com Gas Storagelte155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
206217049 |  | Active | LOCHINVAR |  | CLN154080 2** | Natural Gas | Storage | 81 | 80.1 | 154 |  | 80 |  | 1170 | No | 1901.2346 | Com Gas Storage | lte155kBtuh | 100 | 16.7143 | Com Gas Storagelte155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
206217050 |  | Active | RELIANCE WATER HEATERS |  | L81154NE 2** | Natural Gas | Storage | 81 | 80.1 | 154 |  | 80 |  | 1170 | No | 1901.2346 | Com Gas Storage | lte155kBtuh | 100 | 16.7143 | Com Gas Storagelte155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
206217051 |  | Active | STATE |  | SBL81154NE 2** | Natural Gas | Storage | 81 | 80.1 | 154 |  | 80 |  | 1170 | No | 1901.2346 | Com Gas Storage | lte155kBtuh | 100 | 16.7143 | Com Gas Storagelte155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
206217052 |  | Active | AMERICAN |  | BCL380T1806NOX 2** | Natural Gas | Storage | 81 | 80.6 | 180 |  | 80 |  | 1200 | No | 2222.2222 | Com Gas Storage | gt155kBtuh | 100 | 17.1429 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
206217053 |  | Active | LOCHINVAR |  | CLN180080 2** | Natural Gas | Storage | 81 | 80.6 | 180 |  | 80 |  | 1200 | No | 2222.2222 | Com Gas Storage | gt155kBtuh | 100 | 17.1429 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
206217054 |  | Active | RELIANCE WATER HEATERS |  | L81180NE 2** | Natural Gas | Storage | 81 | 80.6 | 180 |  | 80 |  | 1200 | No | 2222.2222 | Com Gas Storage | gt155kBtuh | 100 | 17.1429 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
206217055 |  | Active | STATE |  | SBL81180NE 2** | Natural Gas | Storage | 81 | 80.6 | 180 |  | 80 |  | 1200 | No | 2222.2222 | Com Gas Storage | gt155kBtuh | 100 | 17.1429 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
206217056 |  | Active | AMERICAN |  | BCL380T1996NOX 2** | Natural Gas | Storage | 81 | 77 | 199 |  | 80 |  | 1230 | No | 2456.7901 | Com Gas Storage | gt155kBtuh | 100 | 17.5714 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
206217057 |  | Active | LOCHINVAR |  | CLN199080 2** | Natural Gas | Storage | 81 | 77 | 199 |  | 80 |  | 1230 | No | 2456.7901 | Com Gas Storage | gt155kBtuh | 100 | 17.5714 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
206217058 |  | Active | RELIANCE WATER HEATERS |  | L81199NE 2** | Natural Gas | Storage | 81 | 77 | 199 |  | 80 |  | 1230 | No | 2456.7901 | Com Gas Storage | gt155kBtuh | 100 | 17.5714 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
206217059 |  | Active | STATE |  | SBL81199NE 2** | Natural Gas | Storage | 81 | 77 | 199 |  | 80 |  | 1230 | No | 2456.7901 | Com Gas Storage | gt155kBtuh | 100 | 17.5714 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
206217060 |  | Active | AMERICAN |  | BCL3100T1996NOX 2** | Natural Gas | Storage | 100 | 95.1 | 199 |  | 80 |  | 1300 | No | 1990 | Com Gas Storage | gt155kBtuh | 100 | 18.5714 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
206217061 |  | Active | LOCHINVAR |  | CLN199100 2** | Natural Gas | Storage | 100 | 95.1 | 199 |  | 80 |  | 1300 | No | 1990 | Com Gas Storage | gt155kBtuh | 100 | 18.5714 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
206217062 |  | Active | RELIANCE WATER HEATERS |  | L100199NE 2** | Natural Gas | Storage | 100 | 95.1 | 199 |  | 80 |  | 1300 | No | 1990 | Com Gas Storage | gt155kBtuh | 100 | 18.5714 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
206217063 |  | Active | STATE |  | SBL100199NE 2** | Natural Gas | Storage | 100 | 95.1 | 199 |  | 80 |  | 1300 | No | 1990 | Com Gas Storage | gt155kBtuh | 100 | 18.5714 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
206217064 |  | Active | AMERICAN |  | BCL3100T2506NOX 2** | Natural Gas | Storage | 100 | 95.3 | 250 |  | 80 |  | 1350 | No | 2500 | Com Gas Storage | gt155kBtuh | 100 | 19.2857 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
206217065 |  | Active | AMERICAN |  | ABCL3100T2506NOX 2** | Natural Gas | Storage | 100 | 95.3 | 250 |  | 80 |  | 1350 | No | 2500 | Com Gas Storage | gt155kBtuh | 100 | 19.2857 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
206217066 |  | Active | LOCHINVAR |  | CLN250100* 2** | Natural Gas | Storage | 100 | 95.3 | 250 |  | 80 |  | 1350 | No | 2500 | Com Gas Storage | gt155kBtuh | 100 | 19.2857 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
206217067 |  | Active | RELIANCE WATER HEATERS |  | L100250NE* 2** | Natural Gas | Storage | 100 | 95.3 | 250 |  | 80 |  | 1350 | No | 2500 | Com Gas Storage | gt155kBtuh | 100 | 19.2857 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
206217068 |  | Active | STATE |  | SBL100250NE* 2** | Natural Gas | Storage | 100 | 95.3 | 250 |  | 80 |  | 1350 | No | 2500 | Com Gas Storage | gt155kBtuh | 100 | 19.2857 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
206217069 |  | Active | AMERICAN |  | BCL3100T2756NOX 2** | Natural Gas | Storage | 100 | 95.3 | 275 |  | 80 |  | 1400 | No | 2750 | Com Gas Storage | gt155kBtuh | 100 | 20 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
206217070 |  | Active | AMERICAN |  | ABCL3100T2756NOX 2** | Natural Gas | Storage | 100 | 95.3 | 275 |  | 80 |  | 1400 | No | 2750 | Com Gas Storage | gt155kBtuh | 100 | 20 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
206217071 |  | Active | LOCHINVAR |  | CLN275100* 2** | Natural Gas | Storage | 100 | 95.3 | 275 |  | 80 |  | 1400 | No | 2750 | Com Gas Storage | gt155kBtuh | 100 | 20 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
206217072 |  | Active | RELIANCE WATER HEATERS |  | L100275NE* 2** | Natural Gas | Storage | 100 | 95.3 | 275 |  | 80 |  | 1400 | No | 2750 | Com Gas Storage | gt155kBtuh | 100 | 20 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
206217073 |  | Active | STATE |  | SBL100275NE* 2** | Natural Gas | Storage | 100 | 95.3 | 275 |  | 80 |  | 1400 | No | 2750 | Com Gas Storage | gt155kBtuh | 100 | 20 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
206217074 |  | Active | AMERICAN |  | BCL386T3106NOX 2** | Natural Gas | Storage | 86 | 89.2 | 310 |  | 80 |  | 1400 | No | 3604.6512 | Com Gas Storage | gt155kBtuh | 100 | 20 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
206217075 |  | Active | AMERICAN |  | ABCL386T3106NOX 2** | Natural Gas | Storage | 86 | 89.2 | 310 |  | 80 |  | 1400 | No | 3604.6512 | Com Gas Storage | gt155kBtuh | 100 | 20 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
206217076 |  | Active | LOCHINVAR |  | CLN310085* 2** | Natural Gas | Storage | 86 | 89.2 | 310 |  | 80 |  | 1400 | No | 3604.6512 | Com Gas Storage | gt155kBtuh | 100 | 20 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
206217077 |  | Active | RELIANCE WATER HEATERS |  | L86310NE* 2** | Natural Gas | Storage | 86 | 89.2 | 310 |  | 80 |  | 1400 | No | 3604.6512 | Com Gas Storage | gt155kBtuh | 100 | 20 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
206217078 |  | Active | STATE |  | SBL86310NE* 2** | Natural Gas | Storage | 86 | 89.2 | 310 |  | 80 |  | 1400 | No | 3604.6512 | Com Gas Storage | gt155kBtuh | 100 | 20 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
206313903 |  | Active | LOCHINVAR |  | CGN120070 1** | Natural Gas | Storage | 72 | 67.5 | 120 |  | 80 |  | 1000 | No | 1666.6667 | Com Gas Storage | lte155kBtuh | 75 | 14.2857 | Com Gas Storagelte155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
206313908 |  | Active | LOCHINVAR |  | CGN155080 1** | Natural Gas | Storage | 81 | 79.7 | 154 |  | 80 |  | 1100 | No | 1901.2346 | Com Gas Storage | lte155kBtuh | 100 | 15.7143 | Com Gas Storagelte155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
206313913 |  | Active | LOCHINVAR |  | CGN200100 1** | Natural Gas | Storage | 100 | 95 | 199 |  | 80 |  | 1300 | No | 1990 | Com Gas Storage | gt155kBtuh | 100 | 18.5714 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
206313916 |  | Active | LOCHINVAR |  | CGN200080 1** | Natural Gas | Storage | 81 | 77 | 199 |  | 80 |  | 1200 | No | 2456.7901 | Com Gas Storage | gt155kBtuh | 100 | 17.1429 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
206313921 |  | Active | LOCHINVAR |  | CGN199100* 1** | Natural Gas | Storage | 100 | 95 | 199 |  | 80 |  | 1300 | No | 1990 | Com Gas Storage | gt155kBtuh | 100 | 18.5714 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
206313927 |  | Active | LOCHINVAR |  | CGN250100* 1** | Natural Gas | Storage | 100 | 95 | 250 |  | 80 |  | 1350 | No | 2500 | Com Gas Storage | gt155kBtuh | 100 | 19.2857 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
206313933 |  | Active | LOCHINVAR |  | CGN250065* 1** | Natural Gas | Storage | 65 | 61.8 | 251 |  | 80 |  | 1100 | No | 3861.5385 | Com Gas Storage | gt155kBtuh | 75 | 15.7143 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
206313939 |  | Active | LOCHINVAR |  | CGN275100* 1** | Natural Gas | Storage | 100 | 95 | 275 |  | 80 |  | 1400 | No | 2750 | Com Gas Storage | gt155kBtuh | 100 | 20 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
206313957 |  | Active | LOCHINVAR |  | CGN400100* 1** | Natural Gas | Storage | 100 | 95 | 390 |  | 80 |  | 1525 | No | 3900 | Com Gas Storage | gt155kBtuh | 100 | 21.7857 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
206314787 |  | Active | LOCHINVAR |  | SWN130-035 2** | Natural Gas | Storage | 34 | 33.1 | 130 |  | 96 |  | 650 | No | 3823.5294 | Com Gas Storage | lte155kBtuh | 40 | 9.2857 | Com Gas Storagelte155kBtuh | 0.8 |  | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  | Y |  | N | AHRI
206314789 |  | Active | LOCHINVAR |  | SCN130-035 2** | Natural Gas | Storage | 34 | 33.1 | 130 |  | 96 |  | 650 | No | 3823.5294 | Com Gas Storage | lte155kBtuh | 40 | 9.2857 | Com Gas Storagelte155kBtuh | 0.8 |  | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  | Y |  | N | AHRI
206314809 |  | Active | LOCHINVAR |  | SWN130-050 2** | Natural Gas | Storage | 50 | 47.8 | 130 |  | 95 |  | 750 | No | 2600 | Com Gas Storage | lte155kBtuh | 50 | 10.7143 | Com Gas Storagelte155kBtuh | 0.8 |  | 0.9 | 0.96 | 0.96 | N/A | N/A |  | Y |  |  | N | AHRI
206314811 |  | Active | LOCHINVAR |  | SCN130-050 2** | Natural Gas | Storage | 50 | 47.8 | 130 |  | 95 |  | 750 | No | 2600 | Com Gas Storage | lte155kBtuh | 50 | 10.7143 | Com Gas Storagelte155kBtuh | 0.8 |  | 0.9 | 0.96 | 0.96 | N/A | N/A |  | Y |  |  | N | AHRI
206314820 |  | Active | LOCHINVAR |  | SWN175-050 2** | Natural Gas | Storage | 50 | 48.5 | 175 |  | 96 |  | 800 | No | 3500 | Com Gas Storage | gt155kBtuh | 50 | 11.4286 | Com Gas Storagegt155kBtuh | 0.8 |  | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  | Y |  | N | AHRI
206314822 |  | Active | LOCHINVAR |  | SCN175-050 2** | Natural Gas | Storage | 50 | 48.5 | 175 |  | 96 |  | 800 | No | 3500 | Com Gas Storage | gt155kBtuh | 50 | 11.4286 | Com Gas Storagegt155kBtuh | 0.8 |  | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  | Y |  | N | AHRI
206314831 |  | Active | LOCHINVAR |  | SWN199-050 2** | Natural Gas | Storage | 50 | 48.5 | 199 |  | 96 |  | 800 | No | 3980 | Com Gas Storage | gt155kBtuh | 50 | 11.4286 | Com Gas Storagegt155kBtuh | 0.8 |  | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  | Y |  | N | AHRI
206314833 |  | Active | LOCHINVAR |  | SCN199-050 2** | Natural Gas | Storage | 50 | 48.5 | 199 |  | 96 |  | 800 | No | 3980 | Com Gas Storage | gt155kBtuh | 50 | 11.4286 | Com Gas Storagegt155kBtuh | 0.8 |  | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  | Y |  | N | AHRI
206314842 |  | Active | LOCHINVAR |  | SWN150-050 2** | Natural Gas | Storage | 50 | 47.8 | 150 |  | 95 |  | 750 | No | 3000 | Com Gas Storage | lte155kBtuh | 50 | 10.7143 | Com Gas Storagelte155kBtuh | 0.8 |  | 0.9 | 0.96 | 0.96 | N/A | N/A |  | Y |  |  | N | AHRI
206314844 |  | Active | LOCHINVAR |  | SCN150-050 2** | Natural Gas | Storage | 50 | 47.8 | 150 |  | 95 |  | 750 | No | 3000 | Com Gas Storage | lte155kBtuh | 50 | 10.7143 | Com Gas Storagelte155kBtuh | 0.8 |  | 0.9 | 0.96 | 0.96 | N/A | N/A |  | Y |  |  | N | AHRI
206321976 |  | Active | A. O. SMITH |  | BTX-80 1** | Natural Gas | Storage | 50 | 48 | 76 |  | 94 |  | 320 | No | 1520 | Com Gas Storage | lte155kBtuh | 50 | 4.5714 | Com Gas Storagelte155kBtuh | 0.8 |  | 0.9 | 0.96 | 0.96 | N/A | N/A |  | Y |  |  | N | AHRI
206322264 |  | Active | A. O. SMITH |  | BL-80 1** | Natural Gas | Storage | 74 | 70.3 | 75.1 |  | 80 |  | 1030 | No | 1014.8649 | Com Gas Storage | lte155kBtuh | 75 | 14.7143 | Com Gas Storagelte155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
206322265 |  | Active | A. O. SMITH |  | BL-100 1** | Natural Gas | Storage | 98 | 95.2 | 75.1 |  | 81 |  | 1150 | No | 766.3265 | Com Gas Storage | lte155kBtuh | 100 | 16.4286 | Com Gas Storagelte155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
206322291 |  | Active | AMERICAN |  | UG6275T754*V 1** | Natural Gas | Storage | 74 | 70.3 | 75.1 |  | 80 |  | 1030 | No | 1014.8649 | Com Gas Storage | lte155kBtuh | 75 | 14.7143 | Com Gas Storagelte155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
206322292 |  | Active | STATE |  | SBL7576*E 1** | Natural Gas | Storage | 74 | 70.3 | 75.1 |  | 80 |  | 1030 | No | 1014.8649 | Com Gas Storage | lte155kBtuh | 75 | 14.7143 | Com Gas Storagelte155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
206322293 |  | Active | LOCHINVAR |  | CLN 075100 1** | Natural Gas | Storage | 98 | 95.2 | 75.1 |  | 81 |  | 1150 | No | 766.3265 | Com Gas Storage | lte155kBtuh | 100 | 16.4286 | Com Gas Storagelte155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
206322294 |  | Active | STATE |  | SBL100 76*E 1** | Natural Gas | Storage | 98 | 95.2 | 75.1 |  | 81 |  | 1150 | No | 766.3265 | Com Gas Storage | lte155kBtuh | 100 | 16.4286 | Com Gas Storagelte155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
206322328 |  | Active | LOCHINVAR |  | CLN 075075 1** | Natural Gas | Storage | 74 | 70.3 | 75.1 |  | 80 |  | 1030 | No | 1014.8649 | Com Gas Storage | lte155kBtuh | 75 | 14.7143 | Com Gas Storagelte155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
206331796 |  | Active | STATE |  | SHE-50-76 *E 1** | Natural Gas | Storage | 50 | 48 | 76 |  | 94 |  | 320 | No | 1520 | Com Gas Storage | lte155kBtuh | 50 | 4.5714 | Com Gas Storagelte155kBtuh | 0.8 |  | 0.9 | 0.96 | 0.96 | N/A | N/A |  | Y |  |  | N | AHRI
206551230 |  | Active | BOCK |  | 100W-250SD-NAT-**** | Natural Gas | Storage | 98 | 93.1 | 250 |  | 80 |  | 1238 | No | 2551.0204 | Com Gas Storage | gt155kBtuh | 100 | 17.6857 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
206551232 |  | Active | BOCK |  | 100W-270SD-NA-* | Natural Gas | Storage | 100 | 95 | 270 |  | 80 |  | 1236 | No | 2700 | Com Gas Storage | gt155kBtuh | 100 | 17.6571 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
206551233 |  | Active | BOCK |  | 100W-300SD-NA-* | Natural Gas | Storage | 100 | 95 | 300 |  | 80 |  | 1236 | No | 3000 | Com Gas Storage | gt155kBtuh | 100 | 17.6571 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
206551241 |  | Active | BOCK |  | 80W-250SD-NA-**** | Natural Gas | Storage | 80 | 76 | 250 |  | 80 |  | 1099 | No | 3125 | Com Gas Storage | gt155kBtuh | 80 | 15.7 | Com Gas Storagegt155kBtuh | 0.8 | Y | 0.9 | 0.96 | 0.96 | N/A | N/A |  |  |  |  | N | AHRI
7056651 |  | Active | BRADFORD WHITE |  | D-80T425**** | Natural Gas | Instantaneous | 80 | 76 | 425 |  | 80 |  | 1314 | No | 5312.5 | Com Gas Storage-Type Instantaneous | gte200kBtuh | 80 | 18.7714 | Com Gas Storage-Type Instantaneousgte200kBtuh | 0.8 | Y | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  |  |  |  | N | AHRI
7056670 |  | Active | BRADFORD WHITE |  | D-75T300**** | Natural Gas | Instantaneous | 75 | 71.3 | 300 |  | 80 |  | 1071 | No | 4000 | Com Gas Storage-Type Instantaneous | gte200kBtuh | 75 | 15.3 | Com Gas Storage-Type Instantaneousgte200kBtuh | 0.8 | Y | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  |  |  |  | N | AHRI
7056675 |  | Active | BRADFORD WHITE |  | D-65T399**N* | Natural Gas | Instantaneous | 65 | 61.8 | 399.9 |  | 80 |  | 1000 | No | 6152.3077 | Com Gas Storage-Type Instantaneous | gte200kBtuh | 75 | 14.2857 | Com Gas Storage-Type Instantaneousgte200kBtuh | 0.8 | Y | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  |  |  |  | N | AHRI
7057160 |  | Active | RHEEM/RUUD |  | G65-400 | Natural Gas | Instantaneous | 65 | 62 | 399.9 |  | 80 |  | 1386 | No | 6152.3077 | Com Gas Storage-Type Instantaneous | gte200kBtuh | 75 | 19.8 | Com Gas Storage-Type Instantaneousgte200kBtuh | 0.8 | Y | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  |  |  |  | N | AHRI
7057162 |  | Active | RHEEM/RUUD |  | G72-300 | Natural Gas | Instantaneous | 72 | 69 | 300 |  | 80 |  | 1308 | No | 4166.6667 | Com Gas Storage-Type Instantaneous | gte200kBtuh | 75 | 18.6857 | Com Gas Storage-Type Instantaneousgte200kBtuh | 0.8 | Y | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  |  |  |  | N | AHRI
7057172 |  | Active | RHEEM/RUUD |  | G85-400 | Natural Gas | Instantaneous | 85 | 81 | 399.9 |  | 80 |  | 1514 | No | 4704.7059 | Com Gas Storage-Type Instantaneous | gte200kBtuh | 100 | 21.6286 | Com Gas Storage-Type Instantaneousgte200kBtuh | 0.8 | Y | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  |  |  |  | N | AHRI
7057203 |  | Active | BRADFORD WHITE |  | D80T725**N* | Natural Gas | Instantaneous | 80 | 76 | 725 |  | 80 |  | 1314 | No | 9062.5 | Com Gas Storage-Type Instantaneous | gte200kBtuh | 80 | 18.7714 | Com Gas Storage-Type Instantaneousgte200kBtuh | 0.8 | Y | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  |  |  |  | N | AHRI
7057209 |  | Active | BRADFORD WHITE |  | D80T505*N* | Natural Gas | Instantaneous | 80 | 77.8 | 505 |  | 80 |  | 1314 | No | 6312.5 | Com Gas Storage-Type Instantaneous | gte200kBtuh | 80 | 18.7714 | Com Gas Storage-Type Instantaneousgte200kBtuh | 0.8 | Y | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  |  |  |  | N | AHRI
7057255 |  | Active | BRADFORD WHITE |  | D65T370**N* | Natural Gas | Instantaneous | 65 | 61.7 | 370 |  | 80 |  | 1000 | No | 5692.3077 | Com Gas Storage-Type Instantaneous | gte200kBtuh | 75 | 14.2857 | Com Gas Storage-Type Instantaneousgte200kBtuh | 0.8 | Y | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  |  |  |  | N | AHRI
7057322 |  | Active | GIANT |  | UG65-250N-US | Natural Gas | Instantaneous | 60 | 56.7 | 250 |  | 80 |  | 1100 | No | 4166.6667 | Com Gas Storage-Type Instantaneous | gte200kBtuh | 60 | 15.7143 | Com Gas Storage-Type Instantaneousgte200kBtuh | 0.8 | Y | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  |  |  |  | N | AHRI
7057323 |  | Active | GIANT |  | UG65-300N-US | Natural Gas | Instantaneous | 55 | 52.4 | 300 |  | 80 |  | 1100 | No | 5454.5455 | Com Gas Storage-Type Instantaneous | gte200kBtuh | 55 | 15.7143 | Com Gas Storage-Type Instantaneousgte200kBtuh | 0.8 | Y | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  |  |  |  | N | AHRI
7057358 |  | Active | RHEEM/RUUD |  | GN37-200 | Natural Gas | Instantaneous | 37 | 34 | 199.9 |  | 80 |  | 900 | No | 5402.7027 | Com Gas Storage-Type Instantaneous | lt200kBtuh | 40 | 12.8571 | Com Gas Storage-Type Instantaneouslt200kBtuh | 0.8 | Y | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  |  |  |  | N | AHRI
7057410 |  | Active | RICHMOND |  | T85-400 | Natural Gas | Instantaneous | 85 | 81 | 399.9 |  | 80 |  | 1514 | No | 4704.7059 | Com Gas Storage-Type Instantaneous | gte200kBtuh | 100 | 21.6286 | Com Gas Storage-Type Instantaneousgte200kBtuh | 0.8 | Y | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  |  |  |  | N | AHRI
7057413 |  | Active | RICHMOND |  | T65-400 | Natural Gas | Instantaneous | 65 | 62 | 399.9 |  | 80 |  | 1386 | No | 6152.3077 | Com Gas Storage-Type Instantaneous | gte200kBtuh | 75 | 19.8 | Com Gas Storage-Type Instantaneousgte200kBtuh | 0.8 | Y | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  |  |  |  | N | AHRI
7057415 |  | Active | RICHMOND |  | T72-300 | Natural Gas | Instantaneous | 72 | 69 | 300 |  | 80 |  | 1308 | No | 4166.6667 | Com Gas Storage-Type Instantaneous | gte200kBtuh | 75 | 18.6857 | Com Gas Storage-Type Instantaneousgte200kBtuh | 0.8 | Y | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  |  |  |  | N | AHRI
7057766 |  | Active | HTP |  | CG250N65 | Natural Gas | Instantaneous | 60 | 56.7 | 250 |  | 80 |  | 1100 | No | 4166.6667 | Com Gas Storage-Type Instantaneous | gte200kBtuh | 60 | 15.7143 | Com Gas Storage-Type Instantaneousgte200kBtuh | 0.8 | Y | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  |  |  |  | N | AHRI
7057767 |  | Active | HTP |  | CG300N65 | Natural Gas | Instantaneous | 55 | 52.4 | 300 |  | 80 |  | 1100 | No | 5454.5455 | Com Gas Storage-Type Instantaneous | gte200kBtuh | 55 | 15.7143 | Com Gas Storage-Type Instantaneousgte200kBtuh | 0.8 | Y | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  |  |  |  | N | AHRI
7057999 |  | Active | RICHMOND |  | TN37-200 | Natural Gas | Instantaneous | 37 | 34 | 199.9 |  | 80 |  | 900 | No | 5402.7027 | Com Gas Storage-Type Instantaneous | lt200kBtuh | 40 | 12.8571 | Com Gas Storage-Type Instantaneouslt200kBtuh | 0.8 | Y | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  |  |  |  | N | AHRI
7293280 |  | Active | NORITZ |  | NC380-SV-ASME-NG | Natural Gas | Instantaneous | 0.6 | 0.6 | 380 |  | 80 |  |  | No | 633333.3333 | Com Gas Instantaneous | gte200kBtuh | 2 | 0 | Com Gas Instantaneousgte200kBtuh | 0.8 | Y | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  |  |  |  | N | AHRI
7917735 |  | Active | RHEEM/RUUD |  | GX90-550 (A) | Natural Gas | Instantaneous | 90 | 87.2 | 550 |  | 80 |  | 1668 | No | 6111.1111 | Com Gas Storage-Type Instantaneous | gte200kBtuh | 100 | 23.8286 | Com Gas Storage-Type Instantaneousgte200kBtuh | 0.8 | Y | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  |  |  |  | N | AHRI
7917915 |  | Active | RHEEM/RUUD |  | GX90-640 (A) | Natural Gas | Instantaneous | 90 | 87.2 | 640 |  | 80 |  | 1793 | No | 7111.1111 | Com Gas Storage-Type Instantaneous | gte200kBtuh | 100 | 25.6143 | Com Gas Storage-Type Instantaneousgte200kBtuh | 0.8 | Y | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  |  |  |  | N | AHRI
7917983 |  | Active | RHEEM/RUUD |  | GX90-715 (A) | Natural Gas | Instantaneous | 90 | 87.2 | 715 |  | 80 |  | 1893 | No | 7944.4444 | Com Gas Storage-Type Instantaneous | gte200kBtuh | 100 | 27.0429 | Com Gas Storage-Type Instantaneousgte200kBtuh | 0.8 | Y | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  |  |  |  | N | AHRI
8482837 |  | Active | BRADFORD WHITE |  | UCG80H399*N* | Natural Gas | Instantaneous | 80 | 76 | 399 |  | 80 |  | 1482 | No | 4987.5 | Com Gas Storage-Type Instantaneous | gte200kBtuh | 80 | 21.1714 | Com Gas Storage-Type Instantaneousgte200kBtuh | 0.8 | Y | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  |  |  |  | N | AHRI
202126401 |  | Active | Patterson-Kelley | HiDra | HC-800 | Natural Gas | Instantaneous | 134 | 134 | 800 |  | 94 |  | 1355 | No | 5970.1493 | Com Gas Storage-Type Instantaneous | gte200kBtuh | 120 | 19.3571 | Com Gas Storage-Type Instantaneousgte200kBtuh | 0.8 |  | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  |  | Y |  | N | AHRI
202275071 |  | Active | BRADFORD WHITE |  | D65T625*N | Natural Gas | Instantaneous | 65 | 61.8 | 625 |  | 80 |  | 1600 | No | 9615.3846 | Com Gas Storage-Type Instantaneous | gte200kBtuh | 75 | 22.8571 | Com Gas Storage-Type Instantaneousgte200kBtuh | 0.8 | Y | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  |  |  |  | N | AHRI
202555343 |  | Active | Patterson-Kelley | HiDra | HC-1000 | Natural Gas | Instantaneous | 130 | 130 | 1000 |  | 95 |  | 1490 | No | 7692.3077 | Com Gas Storage-Type Instantaneous | gte200kBtuh | 120 | 21.2857 | Com Gas Storage-Type Instantaneousgte200kBtuh | 0.8 |  | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  |  | Y |  | N | AHRI
202886845 |  | Active | BRADFORD WHITE |  | EF120T500*N*3 | Natural Gas | Instantaneous | 119 | 113.1 | 499.9 |  | 94 |  | 1532 | No | 4200.8403 | Com Gas Storage-Type Instantaneous | gte200kBtuh | 120 | 21.8857 | Com Gas Storage-Type Instantaneousgte200kBtuh | 0.8 |  | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  |  | Y |  | N | AHRI
203120870 |  | Active | LAARS |  | LUHE120T500*N*3 | Natural Gas | Instantaneous | 119 | 113.1 | 499.9 |  | 94 |  | 1532 | No | 4200.8403 | Com Gas Storage-Type Instantaneous | gte200kBtuh | 120 | 21.8857 | Com Gas Storage-Type Instantaneousgte200kBtuh | 0.8 |  | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  |  | Y |  | N | AHRI
205733384 |  | Active | LOCHINVAR |  | SWA500N | Natural Gas | Instantaneous | 110 | 107.3 | 499 |  | 96 |  | 1493 | No | 4536.3636 | Com Gas Storage-Type Instantaneous | gte200kBtuh | 120 | 21.3286 | Com Gas Storage-Type Instantaneousgte200kBtuh | 0.8 |  | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  |  |  | Y | N | AHRI
205782248 |  | Active | CAMUS HYDRONICS | Vtech | VTNW-0499 | Natural Gas | Instantaneous | 115 | 113.3 | 499 |  | 96 |  | 896 | No | 4339.1304 | Com Gas Storage-Type Instantaneous | gte200kBtuh | 120 | 12.8 | Com Gas Storage-Type Instantaneousgte200kBtuh | 0.8 |  | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  |  |  | Y | N | AHRI
205957479 |  | Active | STATE |  | SUS 120 750NEA 1** | Natural Gas | Instantaneous | 120 | 118.6 | 750 |  | 97 |  | 1700 | No | 6250 | Com Gas Storage-Type Instantaneous | gte200kBtuh | 120 | 24.2857 | Com Gas Storage-Type Instantaneousgte200kBtuh | 0.8 |  | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  |  |  | Y | N | AHRI
205957483 |  | Active | STATE |  | SUS 120 10000NEA 1** | Natural Gas | Instantaneous | 120 | 118.6 | 1000 |  | 97 |  | 1700 | No | 8333.3333 | Com Gas Storage-Type Instantaneous | gte200kBtuh | 120 | 24.2857 | Com Gas Storage-Type Instantaneousgte200kBtuh | 0.8 |  | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  |  |  | Y | N | AHRI
206052085 |  | Active | LOCHINVAR | ARMOR | AWH0400N SERIES 1** | Natural Gas | Instantaneous | 4.5 | 4.5 | 399 |  | 99 |  |  | No | 88666.6667 | Com Gas Instantaneous | gte200kBtuh | 10 | 0 | Com Gas Instantaneousgte200kBtuh | 0.8 |  | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  |  |  | Y | N | AHRI
206052086 |  | Active | LOCHINVAR | ARMOR | AWH0500N SERIES 1** | Natural Gas | Instantaneous | 5 | 5 | 500 |  | 99 |  |  | No | 100000 | Com Gas Instantaneous | gte200kBtuh | 10 | 0 | Com Gas Instantaneousgte200kBtuh | 0.8 |  | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  |  |  | Y | N | AHRI
206052087 |  | Active | LOCHINVAR | ARMOR | AWH0650N SERIES 1** | Natural Gas | Instantaneous | 6.4 | 6.4 | 650 |  | 98 |  |  | No | 101562.5 | Com Gas Instantaneous | gte200kBtuh | 10 | 0 | Com Gas Instantaneousgte200kBtuh | 0.8 |  | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  |  |  | Y | N | AHRI
206052088 |  | Active | LOCHINVAR | ARMOR | AWH0800N SERIES 1** | Natural Gas | Instantaneous | 7.4 | 7.4 | 800 |  | 98 |  |  | No | 108108.1081 | Com Gas Instantaneous | gte200kBtuh | 10 | 0 | Com Gas Instantaneousgte200kBtuh | 0.8 |  | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  |  |  | Y | N | AHRI
206052089 |  | Active | LOCHINVAR | ARMOR | AWH1000N SERIES 1** | Natural Gas | Instantaneous | 9.1 | 9.1 | 999 |  | 98 |  |  | No | 109780.2198 | Com Gas Instantaneous | gte200kBtuh | 10 | 0 | Com Gas Instantaneousgte200kBtuh | 0.8 |  | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  |  |  | Y | N | AHRI
206216212 |  | Active | A. O. SMITH |  | BTL 366* 2** | Natural Gas | Instantaneous | 86 | 89.1 | 366 |  | 80 |  | 1440 | No | 4255.814 | Com Gas Storage-Type Instantaneous | gte200kBtuh | 100 | 20.5714 | Com Gas Storage-Type Instantaneousgte200kBtuh | 0.8 | Y | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  |  |  |  | N | AHRI
206216213 |  | Active | A. O. SMITH |  | BTL 400* 2** | Natural Gas | Instantaneous | 86 | 86.3 | 390 |  | 80 |  | 1500 | No | 4534.8837 | Com Gas Storage-Type Instantaneous | gte200kBtuh | 100 | 21.4286 | Com Gas Storage-Type Instantaneousgte200kBtuh | 0.8 | Y | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  |  |  |  | N | AHRI
206217079 |  | Active | AMERICAN |  | BCL386T3666NOX 2** | Natural Gas | Instantaneous | 86 | 89.1 | 366 |  | 80 |  | 1440 | No | 4255.814 | Com Gas Storage-Type Instantaneous | gte200kBtuh | 100 | 20.5714 | Com Gas Storage-Type Instantaneousgte200kBtuh | 0.8 | Y | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  |  |  |  | N | AHRI
206217080 |  | Active | AMERICAN |  | ABCL386T3666NOX 2** | Natural Gas | Instantaneous | 86 | 89.1 | 366 |  | 80 |  | 1440 | No | 4255.814 | Com Gas Storage-Type Instantaneous | gte200kBtuh | 100 | 20.5714 | Com Gas Storage-Type Instantaneousgte200kBtuh | 0.8 | Y | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  |  |  |  | N | AHRI
206217081 |  | Active | LOCHINVAR |  | CLN366085* 2** | Natural Gas | Instantaneous | 86 | 89.1 | 366 |  | 80 |  | 1440 | No | 4255.814 | Com Gas Storage-Type Instantaneous | gte200kBtuh | 100 | 20.5714 | Com Gas Storage-Type Instantaneousgte200kBtuh | 0.8 | Y | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  |  |  |  | N | AHRI
206217082 |  | Active | RELIANCE WATER HEATERS |  | L86366NE* 2** | Natural Gas | Instantaneous | 86 | 89.1 | 366 |  | 80 |  | 1440 | No | 4255.814 | Com Gas Storage-Type Instantaneous | gte200kBtuh | 100 | 20.5714 | Com Gas Storage-Type Instantaneousgte200kBtuh | 0.8 | Y | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  |  |  |  | N | AHRI
206217083 |  | Active | STATE |  | SBL86366NE* 2** | Natural Gas | Instantaneous | 86 | 89.1 | 366 |  | 80 |  | 1440 | No | 4255.814 | Com Gas Storage-Type Instantaneous | gte200kBtuh | 100 | 20.5714 | Com Gas Storage-Type Instantaneousgte200kBtuh | 0.8 | Y | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  |  |  |  | N | AHRI
206217084 |  | Active | AMERICAN |  | BCL386T3906NOX 2** | Natural Gas | Instantaneous | 86 | 86.3 | 390 |  | 80 |  | 1500 | No | 4534.8837 | Com Gas Storage-Type Instantaneous | gte200kBtuh | 100 | 21.4286 | Com Gas Storage-Type Instantaneousgte200kBtuh | 0.8 | Y | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  |  |  |  | N | AHRI
206217085 |  | Active | AMERICAN |  | ABCL386T3906NOX 2** | Natural Gas | Instantaneous | 86 | 86.3 | 390 |  | 80 |  | 1500 | No | 4534.8837 | Com Gas Storage-Type Instantaneous | gte200kBtuh | 100 | 21.4286 | Com Gas Storage-Type Instantaneousgte200kBtuh | 0.8 | Y | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  |  |  |  | N | AHRI
206217087 |  | Active | RELIANCE WATER HEATERS |  | L86390NE* 2** | Natural Gas | Instantaneous | 86 | 86.3 | 390 |  | 80 |  | 1500 | No | 4534.8837 | Com Gas Storage-Type Instantaneous | gte200kBtuh | 100 | 21.4286 | Com Gas Storage-Type Instantaneousgte200kBtuh | 0.8 | Y | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  |  |  |  | N | AHRI
206217088 |  | Active | STATE |  | SBL86390NE* 2** | Natural Gas | Instantaneous | 86 | 86.3 | 390 |  | 80 |  | 1500 | No | 4534.8837 | Com Gas Storage-Type Instantaneous | gte200kBtuh | 100 | 21.4286 | Com Gas Storage-Type Instantaneousgte200kBtuh | 0.8 | Y | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  |  |  |  | N | AHRI
206313945 |  | Active | LOCHINVAR |  | CGN305065* 1** | Natural Gas | Instantaneous | 65 | 61.8 | 305 |  | 80 |  | 1200 | No | 4692.3077 | Com Gas Storage-Type Instantaneous | gte200kBtuh | 75 | 17.1429 | Com Gas Storage-Type Instantaneousgte200kBtuh | 0.8 | Y | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  |  |  |  | N | AHRI
206313951 |  | Active | LOCHINVAR |  | CGN365085* 1** | Natural Gas | Instantaneous | 85 | 77.9 | 365 |  | 80 |  | 1400 | No | 4294.1176 | Com Gas Storage-Type Instantaneous | gte200kBtuh | 100 | 20 | Com Gas Storage-Type Instantaneousgte200kBtuh | 0.8 | Y | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  |  |  |  | N | AHRI
206313963 |  | Active | LOCHINVAR |  | CGN500085* 1** | Natural Gas | Instantaneous | 85 | 82 | 500 |  | 80 |  | 1620 | No | 5882.3529 | Com Gas Storage-Type Instantaneous | gte200kBtuh | 100 | 23.1429 | Com Gas Storage-Type Instantaneousgte200kBtuh | 0.8 | Y | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  |  |  |  | N | AHRI
206314798 |  | Active | LOCHINVAR |  | SWN150-035 2** | Natural Gas | Instantaneous | 34 | 32.5 | 150 |  | 94 |  | 650 | No | 4411.7647 | Com Gas Storage-Type Instantaneous | lt200kBtuh | 40 | 9.2857 | Com Gas Storage-Type Instantaneouslt200kBtuh | 0.8 |  | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  |  | Y |  | N | AHRI
206314800 |  | Active | LOCHINVAR |  | SCN150-035 2** | Natural Gas | Instantaneous | 34 | 32.5 | 150 |  | 94 |  | 650 | No | 4411.7647 | Com Gas Storage-Type Instantaneous | lt200kBtuh | 40 | 9.2857 | Com Gas Storage-Type Instantaneouslt200kBtuh | 0.8 |  | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  |  | Y |  | N | AHRI
206334335 |  | Active | LOCHINVAR |  | CLN400085* 2** | Natural Gas | Instantaneous | 86 | 86.3 | 390 |  | 80 |  | 1500 | No | 4534.8837 | Com Gas Storage-Type Instantaneous | gte200kBtuh | 100 | 21.4286 | Com Gas Storage-Type Instantaneousgte200kBtuh | 0.8 | Y | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  |  |  |  | N | AHRI
206551235 |  | Active | BOCK |  | 66W-370SD-NA-**** | Natural Gas | Instantaneous | 65 | 61.7 | 370 |  | 80 |  | 1000 | No | 5692.3077 | Com Gas Storage-Type Instantaneous | gte200kBtuh | 75 | 14.2857 | Com Gas Storage-Type Instantaneousgte200kBtuh | 0.8 | Y | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  |  |  |  | N | AHRI
206551237 |  | Active | BOCK |  | 66W-399SD-NAT-**** | Natural Gas | Instantaneous | 65 | 61.8 | 399.9 |  | 80 |  | 1000 | No | 6152.3077 | Com Gas Storage-Type Instantaneous | gte200kBtuh | 75 | 14.2857 | Com Gas Storage-Type Instantaneousgte200kBtuh | 0.8 | Y | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  |  |  |  | N | AHRI
206551238 |  | Active | BOCK |  | 75W-300SD-NA-**** | Natural Gas | Instantaneous | 75 | 71.3 | 300 |  | 80 |  | 1071 | No | 4000 | Com Gas Storage-Type Instantaneous | gte200kBtuh | 75 | 15.3 | Com Gas Storage-Type Instantaneousgte200kBtuh | 0.8 | Y | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  |  |  |  | N | AHRI
206551242 |  | Active | BOCK |  | 80W-425SD-NA-**** | Natural Gas | Instantaneous | 80 | 76 | 425 |  | 80 |  | 1314 | No | 5312.5 | Com Gas Storage-Type Instantaneous | gte200kBtuh | 80 | 18.7714 | Com Gas Storage-Type Instantaneousgte200kBtuh | 0.8 | Y | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  |  |  |  | N | AHRI
206551244 |  | Active | BOCK |  | 80W-505SD-NA-* | Natural Gas | Instantaneous | 80 | 77.8 | 505 |  | 80 |  | 1314 | No | 6312.5 | Com Gas Storage-Type Instantaneous | gte200kBtuh | 80 | 18.7714 | Com Gas Storage-Type Instantaneousgte200kBtuh | 0.8 | Y | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  |  |  |  | N | AHRI
206551246 |  | Active | BOCK |  | 66W-625SD-NA-* | Natural Gas | Instantaneous | 65 | 61.8 | 625 |  | 80 |  | 1600 | No | 9615.3846 | Com Gas Storage-Type Instantaneous | gte200kBtuh | 75 | 22.8571 | Com Gas Storage-Type Instantaneousgte200kBtuh | 0.8 | Y | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  |  |  |  | N | AHRI
206551248 |  | Active | BOCK |  | 80W-725SD-NA-* | Natural Gas | Instantaneous | 80 | 76 | 725 |  | 80 |  | 1314 | No | 9062.5 | Com Gas Storage-Type Instantaneous | gte200kBtuh | 80 | 18.7714 | Com Gas Storage-Type Instantaneousgte200kBtuh | 0.8 | Y | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  |  |  |  | N | AHRI
7818573 |  | Active | TRINITY |  | LX600WH | Natural Gas | Instantaneous | 4 | 4 | 600 |  | 96 |  |  | Yes | 150000 | Com Gas Hot Water Boiler | gte300kBtuh | 10 | 0 | Com Gas Hot Water Boilergte300kBtuh | 0.8 |  | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  |  |  | Y | N | AHRI
7818574 |  | Active | TRINITY |  | LX700WH | Natural Gas | Instantaneous | 5.2 | 5.2 | 700 |  | 96 |  |  | Yes | 134615.3846 | Com Gas Hot Water Boiler | gte300kBtuh | 10 | 0 | Com Gas Hot Water Boilergte300kBtuh | 0.8 |  | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  |  |  | Y | N | AHRI
7818575 |  | Active | TRINITY |  | LX800WH | Natural Gas | Instantaneous | 5.2 | 5.2 | 800 |  | 96 |  |  | Yes | 153846.1538 | Com Gas Hot Water Boiler | gte300kBtuh | 10 | 0 | Com Gas Hot Water Boilergte300kBtuh | 0.8 |  | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  |  |  | Y | N | AHRI
201796162 |  | Active | ENERPRO BOILERS |  | EPAW1050 | Natural Gas | Instantaneous | 51 |  | 1050 |  | 96 |  | 883 | Yes | 20588.2353 | Com Gas Hot Water Boiler | gte300kBtuh | 55 | 12.6143 | Com Gas Hot Water Boilergte300kBtuh | 0.8 |  | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  |  |  | Y | N | AHRI
201796163 |  | Active | ENERPRO BOILERS |  | EPAW1600 | Natural Gas | Instantaneous | 66 |  | 1600 |  | 96 |  | 1075 | Yes | 24242.4242 | Com Gas Hot Water Boiler | gte300kBtuh | 75 | 15.3571 | Com Gas Hot Water Boilergte300kBtuh | 0.8 |  | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  |  |  | Y | N | AHRI
201796164 |  | Active | ENERPRO BOILERS |  | EPAW2080 | Natural Gas | Instantaneous | 77 |  | 2080 |  | 96 |  | 1245 | Yes | 27012.987 | Com Gas Hot Water Boiler | gte300kBtuh | 80 | 17.7857 | Com Gas Hot Water Boilergte300kBtuh | 0.8 |  | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  |  |  | Y | N | AHRI
204020989 |  | Active | LAARS | OmniTherm | ONV1250 | Natural Gas | Instantaneous | 4.9 | 4.9 | 1250 |  | 85 |  |  | Yes | 255102.0408 | Com Gas Hot Water Boiler | gte300kBtuh | 10 | 0 | Com Gas Hot Water Boilergte300kBtuh | 0.8 |  | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  | Y |  |  | N | AHRI
204021008 |  | Active | LAARS | OmniTherm | ONV1500 | Natural Gas | Instantaneous | 4.9 | 4.9 | 1500 |  | 84 |  |  | Yes | 306122.449 | Com Gas Hot Water Boiler | gte300kBtuh | 10 | 0 | Com Gas Hot Water Boilergte300kBtuh | 0.8 | Y | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  | Y |  |  | N | AHRI
204021009 |  | Active | LAARS | OmniTherm | ONV1750 | Natural Gas | Instantaneous | 8.9 | 8.9 | 1750 |  | 85 |  |  | Yes | 196629.2135 | Com Gas Hot Water Boiler | gte300kBtuh | 10 | 0 | Com Gas Hot Water Boilergte300kBtuh | 0.8 |  | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  | Y |  |  | N | AHRI
204021917 |  | Active | LAARS | OmniTherm | ONV2000 | Natural Gas | Instantaneous | 10.8 | 10.8 | 2000 |  | 86 |  | 2861.5 | Yes | 185185.1852 | Com Gas Hot Water Boiler | gte300kBtuh | 30 | 40.8786 | Com Gas Hot Water Boilergte300kBtuh | 0.8 |  | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  | Y |  |  | N | AHRI
204021918 |  | Active | LAARS | OmniTherm | ONV2500 | Natural Gas | Instantaneous | 10.8 | 10.8 | 2500 |  | 86 |  | 3486.5 | Yes | 231481.4815 | Com Gas Hot Water Boiler | gte300kBtuh | 30 | 49.8071 | Com Gas Hot Water Boilergte300kBtuh | 0.8 |  | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  | Y |  |  | N | AHRI
204793008 |  | Active | BRADFORD WHITE | Brute OmniTech | BONV1250 | Natural Gas | Instantaneous | 4.9 | 4.9 | 1250 |  | 85 |  |  | Yes | 255102.0408 | Com Gas Hot Water Boiler | gte300kBtuh | 10 | 0 | Com Gas Hot Water Boilergte300kBtuh | 0.8 |  | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  | Y |  |  | N | AHRI
204793009 |  | Active | BRADFORD WHITE | Brute OmniTech | BONV1500 | Natural Gas | Instantaneous | 4.9 | 4.9 | 1500 |  | 84 |  |  | Yes | 306122.449 | Com Gas Hot Water Boiler | gte300kBtuh | 10 | 0 | Com Gas Hot Water Boilergte300kBtuh | 0.8 | Y | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  | Y |  |  | N | AHRI
204793010 |  | Active | BRADFORD WHITE | Brute OmniTech | BONV1750 | Natural Gas | Instantaneous | 8.9 | 8.9 | 1750 |  | 85 |  |  | Yes | 196629.2135 | Com Gas Hot Water Boiler | gte300kBtuh | 10 | 0 | Com Gas Hot Water Boilergte300kBtuh | 0.8 |  | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  | Y |  |  | N | AHRI
204793011 |  | Active | BRADFORD WHITE | Brute OmniTech | BONV2000 | Natural Gas | Instantaneous | 10.8 | 10.8 | 2000 |  | 86 |  | 2861.5 | Yes | 185185.1852 | Com Gas Hot Water Boiler | gte300kBtuh | 30 | 40.8786 | Com Gas Hot Water Boilergte300kBtuh | 0.8 |  | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  | Y |  |  | N | AHRI
204793012 |  | Active | BRADFORD WHITE | Brute OmniTech | BONV2500 | Natural Gas | Instantaneous | 10.8 | 10.8 | 2500 |  | 86 |  | 3486.5 | Yes | 231481.4815 | Com Gas Hot Water Boiler | gte300kBtuh | 30 | 49.8071 | Com Gas Hot Water Boilergte300kBtuh | 0.8 |  | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  | Y |  |  | N | AHRI
204793313 |  | Active | HTP | Elite XL | ELX-2000FVWH | Natural Gas | Instantaneous | 16.3 | 16.3 | 2000 |  | 98 |  | 2032.3 | Yes | 122699.3865 | Com Gas Hot Water Boiler | gte300kBtuh | 30 | 29.0329 | Com Gas Hot Water Boilergte300kBtuh | 0.8 |  | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  |  |  | Y | N | AHRI
204862620 |  | Active | LAARS | OmniTherm | OCV1250 | Natural Gas | Instantaneous | 4.9 | 4.9 | 1250 |  | 90 |  |  | Yes | 255102.0408 | Com Gas Hot Water Boiler | gte300kBtuh | 10 | 0 | Com Gas Hot Water Boilergte300kBtuh | 0.8 |  | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  |  | Y |  | N | AHRI
204862621 |  | Active | LAARS | OmniTherm | OCV1500 | Natural Gas | Instantaneous | 4.9 | 4.9 | 1500 |  | 89 |  |  | Yes | 306122.449 | Com Gas Hot Water Boiler | gte300kBtuh | 10 | 0 | Com Gas Hot Water Boilergte300kBtuh | 0.8 |  | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  | Y |  |  | N | AHRI
204862622 |  | Active | LAARS | OmniTherm | OCV1750 | Natural Gas | Instantaneous | 8.9 | 8.9 | 1750 |  | 88 |  |  | Yes | 196629.2135 | Com Gas Hot Water Boiler | gte300kBtuh | 10 | 0 | Com Gas Hot Water Boilergte300kBtuh | 0.8 |  | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  | Y |  |  | N | AHRI
204862623 |  | Active | LAARS | OmniTherm | OCV2000 | Natural Gas | Instantaneous | 10.8 | 10.8 | 2000 |  | 90 |  | 2861.5 | Yes | 185185.1852 | Com Gas Hot Water Boiler | gte300kBtuh | 30 | 40.8786 | Com Gas Hot Water Boilergte300kBtuh | 0.8 |  | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  |  | Y |  | N | AHRI
204862624 |  | Active | LAARS | OmniTherm | OCV2500 | Natural Gas | Instantaneous | 10.8 | 10.8 | 2500 |  | 90 |  | 3486.5 | Yes | 231481.4815 | Com Gas Hot Water Boiler | gte300kBtuh | 30 | 49.8071 | Com Gas Hot Water Boilergte300kBtuh | 0.8 |  | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  |  | Y |  | N | AHRI
204862721 |  | Active | LAARS | OmniTherm | OCV3000 | Natural Gas | Instantaneous | 11.6 | 11.6 | 3000 |  | 87 |  | 4124 | Yes | 258620.6897 | Com Gas Hot Water Boiler | gte300kBtuh | 30 | 58.9143 | Com Gas Hot Water Boilergte300kBtuh | 0.8 |  | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  | Y |  |  | N | AHRI
205152852 |  | Active | BRADFORD WHITE | Brute OmniTech | BOCV1250 | Natural Gas | Instantaneous | 4.9 | 4.9 | 1250 |  | 90 |  |  | Yes | 255102.0408 | Com Gas Hot Water Boiler | gte300kBtuh | 10 | 0 | Com Gas Hot Water Boilergte300kBtuh | 0.8 |  | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  |  | Y |  | N | AHRI
205152853 |  | Active | BRADFORD WHITE | Brute OmniTech | BOCV1500 | Natural Gas | Instantaneous | 4.9 | 4.9 | 1500 |  | 89 |  |  | Yes | 306122.449 | Com Gas Hot Water Boiler | gte300kBtuh | 10 | 0 | Com Gas Hot Water Boilergte300kBtuh | 0.8 |  | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  | Y |  |  | N | AHRI
205152854 |  | Active | BRADFORD WHITE | Brute OmniTech | BOCV1750 | Natural Gas | Instantaneous | 8.9 | 8.9 | 1750 |  | 88 |  |  | Yes | 196629.2135 | Com Gas Hot Water Boiler | gte300kBtuh | 10 | 0 | Com Gas Hot Water Boilergte300kBtuh | 0.8 |  | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  | Y |  |  | N | AHRI
205152855 |  | Active | BRADFORD WHITE | Brute OmniTech | BOCV2000 | Natural Gas | Instantaneous | 10.8 | 10.8 | 2000 |  | 90 |  | 2861.5 | Yes | 185185.1852 | Com Gas Hot Water Boiler | gte300kBtuh | 30 | 40.8786 | Com Gas Hot Water Boilergte300kBtuh | 0.8 |  | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  |  | Y |  | N | AHRI
205152856 |  | Active | BRADFORD WHITE | Brute OmniTech | BOCV2500 | Natural Gas | Instantaneous | 10.8 | 10.8 | 2500 |  | 90 |  | 3486.5 | Yes | 231481.4815 | Com Gas Hot Water Boiler | gte300kBtuh | 30 | 49.8071 | Com Gas Hot Water Boilergte300kBtuh | 0.8 |  | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  |  | Y |  | N | AHRI
205152857 |  | Active | BRADFORD WHITE | Brute OmniTech | BOCV3000 | Natural Gas | Instantaneous | 11.6 | 11.6 | 3000 |  | 87 |  | 4124 | Yes | 258620.6897 | Com Gas Hot Water Boiler | gte300kBtuh | 30 | 58.9143 | Com Gas Hot Water Boilergte300kBtuh | 0.8 |  | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  | Y |  |  | N | AHRI
206347218 |  | Active | CAMUS HYDRONICS | DynaFlame | DFNW-0500-MS | Natural Gas | Instantaneous | 2.5 | 2.5 | 500 |  | 85 |  |  | Yes | 200000 | Com Gas Hot Water Boiler | gte300kBtuh | 10 | 0 | Com Gas Hot Water Boilergte300kBtuh | 0.8 |  | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  | Y |  |  | N | AHRI
206347219 |  | Active | CAMUS HYDRONICS | DynaFlame | DFNW-0501-MG | Natural Gas | Instantaneous | 2.5 | 2.5 | 500 |  | 86 |  |  | Yes | 200000 | Com Gas Hot Water Boiler | gte300kBtuh | 10 | 0 | Com Gas Hot Water Boilergte300kBtuh | 0.8 |  | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  | Y |  |  | N | AHRI
206347220 |  | Active | CAMUS HYDRONICS | DynaFlame | DFNW-0501-MS | Natural Gas | Instantaneous | 2.5 | 2.5 | 500 |  | 84 |  |  | Yes | 200000 | Com Gas Hot Water Boiler | gte300kBtuh | 10 | 0 | Com Gas Hot Water Boilergte300kBtuh | 0.8 | Y | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  | Y |  |  | N | AHRI
206347221 |  | Active | CAMUS HYDRONICS | DynaFlame | DFNW-0502-MG | Natural Gas | Instantaneous | 3.5 | 3.5 | 500 |  | 92 |  |  | Yes | 142857.1429 | Com Gas Hot Water Boiler | gte300kBtuh | 10 | 0 | Com Gas Hot Water Boilergte300kBtuh | 0.8 |  | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  |  | Y |  | N | AHRI
206347222 |  | Active | CAMUS HYDRONICS | DynaFlame | DFNW-0502-MS | Natural Gas | Instantaneous | 3.5 | 3.5 | 500 |  | 93 |  |  | Yes | 142857.1429 | Com Gas Hot Water Boiler | gte300kBtuh | 10 | 0 | Com Gas Hot Water Boilergte300kBtuh | 0.8 |  | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  |  | Y |  | N | AHRI
206347223 |  | Active | CAMUS HYDRONICS | DynaForce | DRNW-0300-MS | Natural Gas | Instantaneous | 2.5 | 2.5 | 300 |  | 94 |  |  | Yes | 120000 | Com Gas Hot Water Boiler | gte300kBtuh | 10 | 0 | Com Gas Hot Water Boilergte300kBtuh | 0.8 |  | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  |  | Y |  | N | AHRI
206347226 |  | Active | CAMUS HYDRONICS | DynaForce | DRNW-0500-MS | Natural Gas | Instantaneous | 2.9 | 2.9 | 500 |  | 94 |  |  | Yes | 172413.7931 | Com Gas Hot Water Boiler | gte300kBtuh | 10 | 0 | Com Gas Hot Water Boilergte300kBtuh | 0.8 |  | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  |  | Y |  | N | AHRI
206347261 |  | Active | CAMUS HYDRONICS | DynaMax | DMNW-0392 | Natural Gas | Instantaneous | 3.4 | 3.4 | 399 |  | 96 |  |  | Yes | 117352.9412 | Com Gas Hot Water Boiler | gte300kBtuh | 10 | 0 | Com Gas Hot Water Boilergte300kBtuh | 0.8 |  | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  |  |  | Y | N | AHRI
206347262 |  | Active | CAMUS HYDRONICS | Dynamax | DMNW-0502 | Natural Gas | Instantaneous | 4 | 4 | 500 |  | 96 |  |  | Yes | 125000 | Com Gas Hot Water Boiler | gte300kBtuh | 10 | 0 | Com Gas Hot Water Boilergte300kBtuh | 0.8 |  | 0.84 | 0.9 | 0.9 | 0.96 | 0.96 |  |  |  | Y | N | AHRI
Note on X1: Williams, Christopher: This column flags whether the AHRI entry is included in the averaging algorithms on the "SUMMARY" tab. % above code: Code:
Note on Z1: Williams, Christopher: Used to give a measure qualification range dependent on % above measure minimum: =IF(OR(W2="Elec Storage", W2="Gas Storage",W2="Gas Instantaneous"),IFERROR(AI2*(1+INDEX(SUMMARY!$L$7:$N$16,MATCH(AB2,SUMMARY!$K$7:$K$16,0),MATCH(X2,SUMMARY!$L$6:$N$6,0))),""),"")

## EnergyStar Pivot
COM WH TYPE | Com Gas Storage
Count of Thermal Efficiency (TE) | Size Bins
Thermal Efficiency (TE) | gt155kBtuh | lte155kBtuh | Total Result
0.94 | 4 | 5 | 9
0.95 | 36 | 31 | 67
0.96 | 71 | 33 | 104
0.97 | 19 | 8 | 27
0.98 | 1 | 4 | 5
0.99 | 1 |  | 1
Total Result | 132 | 81 | 213

## EnergySTAR
306 ENERGY STAR Unique ID | ENERGY STAR Partner | Brand Name | Model Name | Model Number | Additional Model Information | UPC | Type | Fuel Type | Vent Type | Storage Volume (gallons) | Tank Height (in.) | Height to Vent (in.) | Tank Diameter (in.) | Vent Size (in.) | Vent Size 2 (in.) | Max Heat Output (kBtu/hr) | Input Rate - Gas-fired (kBtu/hr) | Thermal Efficiency (TE) | Standby Loss (Btu/hr) | Electric Input - Electric Heat Pump (kW) | Coefficient of Performance (COPh) | Optional Status and Messaging Features | Date Available On Market | Date Certified | Markets | CB Model Identifier | COM WH TYPE | VOLUME BIN | Input in kBtuh | Size Bins
2324252 | Rheem-Ruud Manufacturing | Rheem | Triton | GHE80SS-130A |  |  | Gas Storage | Propane,Gas | Power Direct Vent | 80 | 51 | 64 | 23.9 | 3 |  | 127.4 | 130 | 0.98 | 950 |  |  |  | 2018-04-05 | 2019-05-03 | United States, Canada | ES_1045829_GHE80SS-130A_08102018195545_4510180 | Com Gas Storage | 80 | 130 | lte155kBtuh
2324253 | Rheem-Ruud Manufacturing | Ruud | Triton | GHE80SU-130A |  |  | Gas Storage | Propane,Gas | Power Direct Vent | 80 | 51 | 64 | 23.9 | 3 |  | 127.4 | 130 | 0.98 | 950 |  |  |  | 2018-04-05 | 2019-05-03 | United States, Canada | ES_1045829_GHE80SU-130A_08102018195548_0475190 | Com Gas Storage | 80 | 130 | lte155kBtuh
2324254 | Rheem-Ruud Manufacturing | Ruud | Triton | GHE80SS-130 |  |  | Gas Storage | Propane,Gas | Power Direct Vent | 80 | 51 | 64 | 23.9 | 3 |  | 127.4 | 130 | 0.98 | 950 |  |  |  | 2018-04-05 | 2019-05-03 | United States, Canada | ES_1045829_GHE80SS-130_08102018195550_4172707 | Com Gas Storage | 80 | 130 | lte155kBtuh
2324259 | Rheem-Ruud Manufacturing | Richmond | Triton | GHE80SU-160 |  |  | Gas Storage | Propane,Gas | Power Direct Vent | 80 | 51 | 64 | 23.9 | 3 |  | 155.2 | 160 | 0.97 | 980 |  |  |  | 2018-04-05 | 2019-05-03 | United States, Canada | ES_1045829_GHE80SU-160_08102018195828_4184258 | Com Gas Storage | 80 | 160 | gt155kBtuh
2324260 | Lochinvar, LLC | Lochinvar | OUTDOOR ARMOR | OA(N,L)151 |  |  | Gas Tankless | Propane,Gas | Direct Vent | 1 |  |  |  | 3 |  | 144 | 150 | 0.96 |  |  |  |  | 2012-10-24 | 2018-08-10 | United States | ES_1028919_OA(N,L)151_08102018201055_1837659 | Com Gas Instantaneous | 2 | 150 | lt200kBtuh
2324261 | Lochinvar, LLC | Lochinvar | OUTDOOR ARMOR | OA(N,L)200 |  |  | Gas Tankless | Propane,Gas | Direct Vent | 1 |  |  |  | 3 |  | 191.904 | 199.9 | 0.96 |  |  |  |  | 2012-10-24 | 2018-08-10 | United States | ES_1028919_OA(N,L)200_08102018201058_8326055 | Com Gas Instantaneous | 2 | 199.9 | lt200kBtuh
2324262 | Lochinvar, LLC | Lochinvar | OUTDOOR ARMOR | OA(N,L)286 |  |  | Gas Tankless | Propane,Gas | Direct Vent | 2 |  |  |  | 4 |  | 273.6 | 285 | 0.96 |  |  |  |  | 2012-10-24 | 2018-08-10 | United States | ES_1028919_OA(N,L)286_08102018201100_2546961 | Com Gas Instantaneous | 2 | 285 | gte200kBtuh
2324263 | Lochinvar, LLC | Lochinvar | OUTDOOR ARMOR | OA(N,L)400 |  |  | Gas Tankless | Gas,Propane | Direct Vent | 3 |  |  |  | 4 |  |  | 399.9 | 0.96 |  |  |  |  | 2012-10-24 | 2018-08-10 | United States | ES_1028919_OA(N,L)400_08102018201103_0496837 | Com Gas Instantaneous | 10 | 399.9 | gte200kBtuh
2324264 | Lochinvar, LLC | Lochinvar | OUTDOOR ARMOR | OA(N,L)501 |  |  | Gas Tankless | Propane,Gas | Direct Vent | 3 |  |  |  | 4 |  | 480 | 500 | 0.96 |  |  |  |  | 2012-10-24 | 2018-08-10 | United States | ES_1028919_OA(N,L)501_08102018201105_8098048 | Com Gas Instantaneous | 10 | 500 | gte200kBtuh
2324265 | Rheem-Ruud Manufacturing | Rheem | Triton | GHE100SU-130 |  |  | Gas Storage | Propane,Gas | Power Direct Vent | 100 | 61 | 73 | 23.9 | 3 |  | 126.1 | 130 | 0.97 | 1050 |  |  |  | 2018-04-05 | 2019-05-03 | United States, Canada | ES_1045829_GHE100SU-130_08102018201241_0544129 | Com Gas Storage | 100 | 130 | lte155kBtuh
2324269 | Rheem-Ruud Manufacturing | Ruud | Triton | GHE100SU-160 |  |  | Gas Storage | Propane,Gas | Power Direct Vent | 100 | 61 | 73 | 23.9 | 3 |  | 155.2 | 160 | 0.97 | 1080 |  |  |  | 2018-03-09 | 2019-05-03 | United States, Canada | ES_1045829_GHE100SU-160_08102018203148_1024449 | Com Gas Storage | 100 | 160 | gt155kBtuh
2324270 | Rheem-Ruud Manufacturing | Rheem | Triton | GHE100SU-160A |  |  | Gas Storage | Propane,Gas | Power Direct Vent | 100 | 61 | 73 | 23.9 | 3 |  | 155.2 | 160 | 0.97 | 1080 |  |  |  | 2018-04-05 | 2019-05-03 | United States, Canada | ES_1045829_GHE100SU-160A_08102018203151_0577508 | Com Gas Storage | 100 | 160 | gt155kBtuh
2324271 | Rheem-Ruud Manufacturing | Rheem | Triton | GHE100SS-160 |  |  | Gas Storage | Propane,Gas | Power Direct Vent | 100 | 61 | 73 | 23.9 | 3 |  | 155.2 | 160 | 0.97 | 1080 |  |  |  | 2018-04-05 | 2019-05-03 | United States, Canada | ES_1045829_GHE100SS-160_08102018203153_1766770 | Com Gas Storage | 100 | 160 | gt155kBtuh
2324272 | Rheem-Ruud Manufacturing | Rheem | Triton | GHE100SS-160A |  |  | Gas Storage | Propane,Gas | Power Direct Vent | 100 | 61 | 73 | 23.9 | 3 |  | 155.2 | 160 | 0.97 | 1080 |  |  |  | 2018-04-05 | 2019-05-03 | United States, Canada | ES_1045829_GHE100SS-160A_08102018203156_7731779 | Com Gas Storage | 100 | 160 | gt155kBtuh
2324280 | Rheem-Ruud Manufacturing | Rheem | Triton | GHE100SU-130A |  |  | Gas Storage | Propane,Gas | Power Direct Vent | 100 | 61 | 73 | 23.9 | 3 |  | 126.1 | 130 | 0.97 | 1050 |  |  |  | 2018-04-05 | 2019-05-03 | United States, Canada | ES_1045829_GHE100SU-130A_08102018203556_5072506 | Com Gas Storage | 100 | 130 | lte155kBtuh
2324281 | Rheem-Ruud Manufacturing | Rheem | Triton | GHE100SS-130 |  |  | Gas Storage | Propane,Gas | Power Direct Vent | 100 | 61 | 73 | 23.9 | 3 |  | 126.1 | 130 | 0.97 | 1050 |  |  |  | 2018-04-05 | 2019-05-03 | United States, Canada | ES_1045829_GHE100SS-130_08102018203559_4833309 | Com Gas Storage | 100 | 130 | lte155kBtuh
2324282 | Rheem-Ruud Manufacturing | Rheem | Triton | GHE100SS-130A |  |  | Gas Storage | Propane,Gas | Power Direct Vent | 100 | 61 | 73 | 23.9 | 3 |  | 126.1 | 130 | 0.97 | 1050 |  |  |  | 2018-04-05 | 2019-05-03 | United States, Canada | ES_1045829_GHE100SS-130A_08102018203601_9926266 | Com Gas Storage | 100 | 130 | lte155kBtuh
2324289 | Rheem-Ruud Manufacturing | Rheem | Triton | GHE100SU-200 |  |  | Gas Storage | Propane,Gas | Power Direct Vent | 100 | 61 | 73 | 23.9 | 3 |  | 194 | 200 | 0.97 | 1100 |  |  |  | 2018-03-20 | 2019-05-03 | United States, Canada | ES_1045829_GHE100SU-200_08102018211612_2648183 | Com Gas Storage | 100 | 200 | gt155kBtuh
2324290 | Rheem-Ruud Manufacturing | Rheem | Triton | GHE100SU-250 |  |  | Gas Storage | Propane,Gas | Power Direct Vent | 100 | 61 | 73 | 23.9 | 3 |  | 240 | 250 | 0.96 | 1155 |  |  |  | 2018-03-20 | 2018-10-29 | United States, Canada | ES_1045829_GHE100SU-250_08102018212026_7057661 | Com Gas Storage | 100 | 250 | gt155kBtuh
2324293 | Rheem-Ruud Manufacturing | Rheem | Triton | GHE80SU-300 |  |  | Gas Storage | Propane,Gas | Power Direct Vent | 80 | 51 | 64 | 23.9 | 3 |  | 285 | 300 | 0.95 | 1105 |  |  |  | 2018-04-05 | 2019-05-03 | United States, Canada | ES_1045829_GHE80SU-300_08102018212739_4731386 | Com Gas Storage | 80 | 300 | gt155kBtuh
2324294 | Rheem-Ruud Manufacturing | Rheem | Triton | GHE80SU-300A |  |  | Gas Storage | Propane,Gas | Power Direct Vent | 80 | 51 | 64 | 23.9 | 3 |  | 285 | 300 | 0.95 | 1105 |  |  |  | 2018-04-05 | 2019-05-03 | United States, Canada | ES_1045829_GHE80SU-300A_08102018212742_7316088 | Com Gas Storage | 80 | 300 | gt155kBtuh
2324295 | Rheem-Ruud Manufacturing | Rheem | Triton | GHE80SS-300 |  |  | Gas Storage | Propane,Gas | Power Direct Vent | 80 | 51 | 64 | 23.9 | 3 |  | 285 | 300 | 0.95 | 1105 |  |  |  | 2018-04-05 | 2019-05-03 | United States, Canada | ES_1045829_GHE80SS-300_08102018212744_7392535 | Com Gas Storage | 80 | 300 | gt155kBtuh
2324296 | Rheem-Ruud Manufacturing | Rheem | Triton | GHE80SS-300A |  |  | Gas Storage | Propane,Gas | Power Direct Vent | 80 | 51 | 64 | 23.9 | 3 |  | 285 | 300 | 0.95 | 1105 |  |  |  | 2018-04-05 | 2019-05-03 | United States, Canada | ES_1045829_GHE80SS-300A_08102018212747_0741388 | Com Gas Storage | 80 | 300 | gt155kBtuh
2324436 | Rheem-Ruud Manufacturing | Rheem | Triton | GHE80SU-160A |  |  | Gas Storage | Propane,Gas | Power Direct Vent | 80 | 51 | 64 | 23.9 | 3 |  | 155.2 | 160 | 0.97 | 980 |  |  |  | 2018-04-05 | 2018-08-17 | United States, Canada | ES_1045829_GHE80SU-160A_08172018190818_5579673 | Com Gas Storage | 80 | 160 | gt155kBtuh
2324437 | Rheem-Ruud Manufacturing | Rheem | Triton | GHE80SS-160 |  |  | Gas Storage | Propane,Gas | Power Direct Vent | 80 | 51 | 64 | 23.9 | 3 |  | 155.2 | 160 | 0.97 | 980 |  |  |  | 2018-04-05 | 2018-08-17 | United States, Canada | ES_1045829_GHE80SS-160_08172018190824_3822813 | Com Gas Storage | 80 | 160 | gt155kBtuh
2324438 | Rheem-Ruud Manufacturing | Rheem | Triton | GHE80SS-160A |  |  | Gas Storage | Propane,Gas | Power Direct Vent | 80 | 51 | 64 | 23.9 | 3 |  | 155.2 | 160 | 0.97 | 980 |  |  |  | 2018-04-05 | 2018-08-17 | United States, Canada | ES_1045829_GHE80SS-160A_08172018190827_2143183 | Com Gas Storage | 80 | 160 | gt155kBtuh
2325638 | Lochinvar, LLC | Lochinvar | OUTDOOR ARMOR | OA(N,L)601 |  |  | Gas Tankless | Gas,Propane | Direct Vent | 3 |  |  |  | 4 |  |  | 600 | 0.96 |  |  |  |  | 2012-10-24 | 2020-12-11 | United States | ES_1028919_OA(N,L)601_09072018193248_4026423 | Com Gas Instantaneous | 10 | 600 | gte200kBtuh
2323940 | Rheem-Ruud Manufacturing | Rheem | Triton | GHE100SU-300 |  |  | Gas Storage | Propane,Gas | Power Direct Vent | 100 | 61 | 73 | 23.9 | 3 |  | 288 | 300 | 0.96 | 1210 |  |  |  | 2018-03-20 | 2019-05-03 | United States, Canada | ES_1045829_GHE100SU-300_08032018141240_9457038 | Com Gas Storage | 100 | 300 | gt155kBtuh
2324081 | Lochinvar, LLC | Lochinvar | ARMOR | AW(N,L)151(PM) |  |  | Gas Tankless | Gas,Propane | Direct Vent | 1 |  |  |  | 3 |  |  | 150 | 0.96 |  |  |  |  | 2012-10-24 | 2020-11-17 | United States, Canada | ES_1028919_AW(N,L)151(PM)_08092018144116_4277545 | Com Gas Instantaneous | 2 | 150 | lt200kBtuh
2324083 | Lochinvar, LLC | Lochinvar | ARMOR | AW(N,L)286(PM) |  |  | Gas Tankless | Gas,Propane | Direct Vent | 2 |  |  |  | 4 |  |  | 285 | 0.96 |  |  |  |  | 2012-10-24 | 2020-11-17 | United States, Canada | ES_1028919_AW(N,L)286(PM)_08092018145303_9865480 | Com Gas Instantaneous | 2 | 285 | gte200kBtuh
2324084 | Lochinvar, LLC | Lochinvar | ARMOR | AW(N,L)501(PM) |  |  | Gas Tankless | Gas,Propane | Direct Vent | 3 |  |  |  | 4 |  |  | 500 | 0.96 |  |  |  |  | 2012-10-24 | 2020-11-17 | United States, Canada | ES_1028919_AW(N,L)501(PM)_08092018145452_8616160 | Com Gas Instantaneous | 10 | 500 | gte200kBtuh
2324086 | Lochinvar, LLC | Lochinvar | ARMOR WALL MOUNT | WA(N,L)125 |  |  | Gas Tankless | Propane,Gas | Direct Vent | 1 |  |  |  | 3 |  | 120 | 125 | 0.96 |  |  |  |  | 2012-12-04 | 2018-12-12 | United States, Canada | ES_1028919_WA(N,L)125_08092018145958_9346448 | Com Gas Instantaneous | 2 | 125 | lt200kBtuh
2324169 | Rheem-Ruud Manufacturing | Rheem | Triton | GHE100SU-200A |  |  | Gas Storage | Propane,Gas | Power Direct Vent | 100 | 61 | 73 | 23.9 | 3 |  | 194 | 200 | 0.97 | 1100 |  |  |  | 2018-03-20 | 2018-08-10 | United States, Canada | ES_1045829_GHE100SU-200A_08102018184656_0743289 | Com Gas Storage | 100 | 200 | gt155kBtuh
2324170 | Rheem-Ruud Manufacturing | Rheem | Triton | GHE100SS-200 |  |  | Gas Storage | Propane,Gas | Power Direct Vent | 100 | 61 | 73 | 23.9 | 3 |  | 194 | 200 | 0.97 | 1100 |  |  |  | 2018-03-20 | 2018-08-10 | United States, Canada | ES_1045829_GHE100SS-200_08102018184659_6522383 | Com Gas Storage | 100 | 200 | gt155kBtuh
2324171 | Rheem-Ruud Manufacturing | Rheem | Triton | GHE100SS-200A |  |  | Gas Storage | Propane,Gas | Power Direct Vent | 100 | 61 | 73 | 23.9 | 3 |  | 194 | 200 | 0.97 | 1100 |  |  |  | 2018-03-20 | 2018-08-10 | United States, Canada | ES_1045829_GHE100SS-200A_08102018184701_6969323 | Com Gas Storage | 100 | 200 | gt155kBtuh
2324189 | Rheem-Ruud Manufacturing | Rheem | Triton | GHE100SU-300A |  |  | Gas Storage | Propane,Gas | Power Direct Vent | 100 | 61 | 73 | 23.9 | 3 |  | 288 | 300 | 0.96 | 1210 |  |  |  | 2018-03-20 | 2019-05-03 | United States, Canada | ES_1045829_GHE100SU-300A_08102018190328_6689446 | Com Gas Storage | 100 | 300 | gt155kBtuh
2324190 | Rheem-Ruud Manufacturing | Rheem | Triton | GHE100SS-300 |  |  | Gas Storage | Propane,Gas | Power Direct Vent | 100 | 61 | 73 | 23.9 | 3 |  | 288 | 300 | 0.96 | 1210 |  |  |  | 2018-03-20 | 2019-05-03 | United States, Canada | ES_1045829_GHE100SS-300_08102018190330_6798913 | Com Gas Storage | 100 | 300 | gt155kBtuh
2324191 | Rheem-Ruud Manufacturing | Rheem | Triton | GHE100SS-300A |  |  | Gas Storage | Propane,Gas | Power Direct Vent | 100 | 61 | 73 | 23.9 | 3 |  | 288 | 300 | 0.96 | 1210 |  |  |  | 2018-03-20 | 2019-05-03 | United States, Canada | ES_1045829_GHE100SS-300A_08102018190333_7988175 | Com Gas Storage | 100 | 300 | gt155kBtuh
2324200 | Rheem-Ruud Manufacturing | Rheem | Triton | GHE100SU-250A |  |  | Gas Storage | Propane,Gas | Power Direct Vent | 100 | 61 | 73 | 23.9 | 3 |  | 240 | 250 | 0.96 | 1155 |  |  |  | 2018-03-20 | 2019-05-03 | United States, Canada | ES_1045829_GHE100SU-250A_08102018191839_4856739 | Com Gas Storage | 100 | 250 | gt155kBtuh
2324201 | Rheem-Ruud Manufacturing | Rheem | Triton | GHE100SS-250 |  |  | Gas Storage | Propane,Gas | Power Direct Vent | 100 | 61 | 73 | 23.9 | 3 |  | 240 | 250 | 0.96 | 1155 |  |  |  | 2018-03-20 | 2019-05-03 | United States, Canada | ES_1045829_GHE100SS-250_08102018191842_4409799 | Com Gas Storage | 100 | 250 | gt155kBtuh
2324202 | Rheem-Ruud Manufacturing | Rheem | Triton | GHE100SS-250A |  |  | Gas Storage | Propane,Gas | Power Direct Vent | 100 | 61 | 73 | 23.9 | 3 |  | 240 | 250 | 0.96 | 1155 |  |  |  | 2018-03-20 | 2019-05-03 | United States, Canada | ES_1045829_GHE100SS-250A_08102018191844_9187111 | Com Gas Storage | 100 | 250 | gt155kBtuh
2324210 | Rheem-Ruud Manufacturing | Rheem | Triton | GHE100SU-400 |  |  | Gas Storage | Propane,Gas | Power Direct Vent | 100 | 61 | 73 | 23.9 | 3 |  | 379.905 | 399.9 | 0.95 | 1310 |  |  |  | 2018-03-21 | 2018-08-10 | United States, Canada | ES_1045829_GHE100SU-400_08102018192457_2577394 | Com Gas Storage | 100 | 399.9 | gt155kBtuh
2324211 | Rheem-Ruud Manufacturing | Rheem | Triton | GHE100SU-400A |  |  | Gas Storage | Propane,Gas | Power Direct Vent | 100 | 61 | 73 | 23.9 | 3 |  | 379.905 | 399.9 | 0.95 | 1310 |  |  |  | 2018-03-21 | 2018-08-10 | United States, Canada | ES_1045829_GHE100SU-400A_08102018192459_7670351 | Com Gas Storage | 100 | 399.9 | gt155kBtuh
2324212 | Rheem-Ruud Manufacturing | Rheem | Triton | GHE100SS-400A |  |  | Gas Storage | Propane,Gas | Power Direct Vent | 100 | 61 | 73 | 23.9 | 3 |  | 379.905 | 399.9 | 0.95 | 1310 |  |  |  | 2018-03-21 | 2018-08-10 | United States, Canada | ES_1045829_GHE100SS-400A_08102018192502_0811461 | Com Gas Storage | 100 | 399.9 | gt155kBtuh
2324217 | Rheem-Ruud Manufacturing | Rheem | Triton | GHE100SS-400 |  |  | Gas Storage | Propane,Gas | Power Direct Vent | 100 | 61 | 73 | 23.9 | 3 |  | 379.905 | 399.9 | 0.95 | 1310 |  |  |  | 2018-03-21 | 2018-08-10 | United States, Canada | ES_1045829_GHE100SS-400_08102018192514_3801011 | Com Gas Storage | 100 | 399.9 | gt155kBtuh
2324232 | Rheem-Ruud Manufacturing | Rheem | Triton | GHE80SU-200 |  |  | Gas Storage | Propane,Gas | Power Direct Vent | 80 | 51 | 64 | 23.9 | 3 |  | 189.905 | 199.9 | 0.95 | 1001 |  |  |  | 2018-03-09 | 2019-05-03 | United States, Canada | ES_1045829_GHE80SU-200_08102018194121_4255688 | Com Gas Storage | 80 | 199.9 | gt155kBtuh
2324233 | Rheem-Ruud Manufacturing | Rheem | Triton | GHE80SU-200A |  |  | Gas Storage | Propane,Gas | Power Direct Vent | 80 | 51 | 64 | 23.9 | 3 |  | 189.905 | 199.9 | 0.95 | 1001 |  |  |  | 2018-03-09 | 2019-05-03 | United States, Canada | ES_1045829_GHE80SU-200A_08102018194124_9348645 | Com Gas Storage | 80 | 199.9 | gt155kBtuh
2324234 | Rheem-Ruud Manufacturing | Rheem | Triton | GHE80SS-200 |  |  | Gas Storage | Propane,Gas | Power Direct Vent | 80 | 51 | 64 | 23.9 | 3 |  | 189.905 | 199.9 | 0.95 | 1001 |  |  |  | 2018-03-09 | 2019-05-03 | United States, Canada | ES_1045829_GHE80SS-200_08102018194126_2489755 | Com Gas Storage | 80 | 199.9 | gt155kBtuh
2324235 | Rheem-Ruud Manufacturing | Rheem | Triton | GHE80SS-200A |  |  | Gas Storage | Propane,Gas | Power Direct Vent | 80 | 51 | 64 | 23.9 | 3 |  | 189.905 | 199.9 | 0.95 | 1001 |  |  |  | 2018-03-09 | 2019-05-03 | United States, Canada | ES_1045829_GHE80SS-200A_08102018194129_9534559 | Com Gas Storage | 80 | 199.9 | gt155kBtuh
2324244 | Rheem-Ruud Manufacturing | Rheem | Triton | GHE80SU-130 |  |  | Gas Storage | Propane,Gas | Power Direct Vent | 80 | 51 | 64 | 23.9 | 3 |  | 127.4 | 130 | 0.98 | 950 |  |  |  | 2018-04-05 | 2019-05-03 | United States, Canada | ES_1045829_GHE80SU-130_08102018194923_6952275 | Com Gas Storage | 80 | 130 | lte155kBtuh
2327620 | A.O. Smith Corporation | American | Polaris | PG10 50 199 3NV 200 |  |  | Gas Storage | Gas | Power Direct Vent | 50 | 63.7 | 6.6 | 22 | 3 |  | 191.04 | 199 | 0.96 | 800 |  |  |  | 2017-02-15 | 2018-10-12 | United States | ES_92897_PG10 50 199 3NV 200_10122018171246_5813369 | Com Gas Storage | 50 | 199 | gt155kBtuh
2327625 | A.O. Smith Corporation | American | Polaris | PG10 50 150 2NV 200 |  |  | Gas Storage | Gas | Power Direct Vent | 50 | 63.7 | 6.6 | 22 | 2 |  | 142.5 | 150 | 0.95 | 750 |  |  |  | 2017-02-15 | 2018-10-12 | United States | ES_92897_PG10 50 150 2NV 200_10122018171257_0744037 | Com Gas Storage | 50 | 150 | lte155kBtuh
2327727 | A.O. Smith Corporation | A. O. Smith | BTX 100 * | BTX 100 * |  |  | Gas Storage | Gas | Power Vent | 50 | 55.7 | 8 | 18 | 2 | 3 | 96 | 100 | 0.96 | 430 |  |  |  | 2007-11-01 | 2018-10-12 | United States, Canada | ES_92897_BTX 100 *_10122018175030_0041076 | Com Gas Storage | 50 | 100 | lte155kBtuh
2327748 | A.O. Smith Corporation | American | Polaris | PG10 34 150 2NV 200 |  |  | Gas Storage-type Instantaneous | Gas | Power Direct Vent | 34 | 48.5 | 6.6 | 22 | 2 |  | 141 | 150 | 0.94 | 650 |  |  |  | 2017-02-15 | 2018-10-12 | United States | ES_92897_PG10 34 150 2NV 200_10122018181643_5806188 | Com Gas Storage-type Instantaneous | 40 | 150 | lt200kBtuh
2327750 | A.O. Smith Corporation | A. O. Smith | Polaris | GSP 150 200 |  |  | Gas Storage-type Instantaneous | Gas | Power Direct Vent | 34 | 48.5 | 6.6 | 22 | 2 |  | 141 | 150 | 0.94 | 650 |  |  |  | 2017-02-15 | 2018-10-12 | United States, Canada | ES_92897_GSP 150 200_10122018181649_0801652 | Com Gas Storage-type Instantaneous | 40 | 150 | lt200kBtuh
2327751 | A.O. Smith Corporation | State | Polaris | GHX 34 150 N 200 |  |  | Gas Storage-type Instantaneous | Gas | Power Direct Vent | 34 | 48.5 | 6.6 | 22 | 2 |  | 141 | 150 | 0.94 | 650 |  |  |  | 2017-02-15 | 2018-10-12 | United States | ES_92897_GHX 34 150 N 200_10122018181651_2306559 | Com Gas Storage-type Instantaneous | 40 | 150 | lt200kBtuh
2327752 | A.O. Smith Corporation | American | Polaris | PR 34 150 N 200 |  |  | Gas Storage-type Instantaneous | Gas | Power Direct Vent | 34 | 48.5 | 6.6 | 22 | 2 |  | 141 | 150 | 0.94 | 650 |  |  |  | 2017-02-15 | 2018-10-12 | Canada | ES_92897_PR 34 150 N 200_10122018181654_5065984 | Com Gas Storage-type Instantaneous | 40 | 150 | lt200kBtuh
2327753 | A.O. Smith Corporation | American | Polaris | PGC3 34 150 2NV 200 |  |  | Gas Storage-type Instantaneous | Gas | Power Direct Vent | 34 | 48.5 | 6.6 | 22 | 2 |  | 141 | 150 | 0.94 | 650 |  |  |  | 2017-02-15 | 2018-10-12 | United States | ES_92897_PGC3 34 150 2NV 200_10122018181657_3190584 | Com Gas Storage-type Instantaneous | 40 | 150 | lt200kBtuh
2327754 | A.O. Smith Corporation | A. O. Smith | Polaris | BSS 150 200 |  |  | Gas Storage-type Instantaneous | Gas | Power Direct Vent | 34 | 48.5 | 6.6 | 22 | 2 |  | 141 | 150 | 0.94 | 650 |  |  |  | 2017-02-15 | 2018-10-12 | United States, Canada | ES_92897_BSS 150 200_10122018181659_4379846 | Com Gas Storage-type Instantaneous | 40 | 150 | lt200kBtuh
2327755 | A.O. Smith Corporation | State | Polaris | SPC 34 150 NE 200 |  |  | Gas Storage-type Instantaneous | Gas | Power Direct Vent | 34 | 48.5 | 6.6 | 22 | 2 |  | 141 | 150 | 0.94 | 650 |  |  |  | 2017-02-15 | 2018-10-12 | United States | ES_92897_SPC 34 150 NE 200_10122018181702_4631017 | Com Gas Storage-type Instantaneous | 40 | 150 | lt200kBtuh
2327756 | A.O. Smith Corporation | American | Polaris | PC 34 150 N 200 |  |  | Gas Storage-type Instantaneous | Gas | Power Direct Vent | 34 | 48.5 | 6.6 | 22 | 2 |  | 141 | 150 | 0.94 | 650 |  |  |  | 2017-02-15 | 2018-10-12 | Canada | ES_92897_PC 34 150 N 200_10122018181704_5820279 | Com Gas Storage-type Instantaneous | 40 | 150 | lt200kBtuh
2327841 | Ariston Thermo USA, LLC | HTP | Phoenix Multi-Fit | PHM130-100 |  |  | Gas Storage | Propane,Gas | Direct Vent | 100 | 63 | 18.2 | 27 | 2 |  | 124.8 | 130 | 0.96 | 422 |  |  |  | 2014-12-10 | 2018-12-12 | United States, Canada | ES_29975_PHM130-100_10122018183717_0987646 | Com Gas Storage | 100 | 130 | lte155kBtuh
2327842 | Ariston Thermo USA, LLC | Westinghouse | Commercial Gas Water Heater Multi-Fit | WGCM100**130 |  |  | Gas Storage | Propane,Gas | Power Direct Vent | 100 | 63 | 18.2 | 27 | 2 |  | 124.8 | 130 | 0.96 | 422 |  |  |  | 2014-12-10 | 2018-12-12 | United States, Canada | ES_29975_WGCM100**130_10122018183720_1446560 | Com Gas Storage | 100 | 130 | lte155kBtuh
2327843 | Noritz America Corporation | Noritz | NCC300OD | NCC300OD (GQ-C5032WZ US) |  |  | Gas Tankless | Propane,Gas | Power Direct Vent | 0 |  |  |  | 2 |  | 291 | 300 | 0.97 |  |  |  |  | 2018-01-01 | 2018-12-12 | United States, Canada | ES_1070591_NCC300OD (GQ-C5032WZ US)_10122018184152_6523247 | Com Gas Instantaneous | 2 | 300 | gte200kBtuh
2327844 | Lochinvar, LLC | Lochinvar | ARMOR CONDENSING | AWH1250(N,L) |  |  | Gas Tankless | Gas,Propane | Direct Vent | 12 |  |  |  | 8 | 6 |  | 1250 | 0.98 |  |  |  |  | 2018-02-19 | 2020-11-18 | United States, Canada | ES_1028919_AWH1250(N,L)_10122018184255_2170675 | Com Gas Instantaneous | 30 | 1250 | gte200kBtuh
2327845 | Lochinvar, LLC | Lochinvar | ARMOR CONDENSING | AWH1500(N,L) |  |  | Gas Tankless | Gas,Propane | Direct Vent | 14 |  |  |  | 8 | 6 |  | 1500 | 0.98 |  |  |  |  | 2018-02-19 | 2020-11-18 | United States, Canada | ES_1028919_AWH1500(N,L)_10122018184257_3152194 | Com Gas Instantaneous | 30 | 1500 | gte200kBtuh
2327846 | Lochinvar, LLC | Lochinvar | ARMOR CONDENSING | AWH2000(N,L) |  |  | Gas Tankless | Gas,Propane | Direct Vent | 18 |  |  |  | 8 |  |  | 1999 | 0.98 |  |  |  |  | 2018-02-19 | 2020-11-19 | United States, Canada | ES_1028919_AWH2000(N,L)_10122018184300_3228641 | Com Gas Instantaneous | 30 | 1999 | gte200kBtuh
2327847 | Ariston Thermo USA, LLC | HTP | Phoenix | PH199-119 |  |  | Gas Storage | Propane,Gas | Power Direct Vent | 119 | 74 | 9.3 | 27 | 3 |  | 191.04 | 199 | 0.96 | 719 |  |  |  | 2007-08-20 | 2018-12-12 | United States, Canada | ES_29975_PH199-119_10122018184300_3054700 | Com Gas Storage | 120 | 199 | gt155kBtuh
2327848 | Lochinvar, LLC | Lochinvar | ARMOR CONDENSING | AWH3000(N,L) |  |  | Gas Tankless | Gas,Propane | Direct Vent | 29 |  |  |  | 10 |  |  | 3000 | 0.98 |  |  |  |  | 2018-02-19 | 2020-11-18 | United States, Canada | ES_1028919_AWH3000(N,L)_10122018184302_8005953 | Com Gas Instantaneous | 30 | 3000 | gte200kBtuh
2327849 | Ariston Thermo USA, LLC | Westinghouse | Commercial Gas Water Heater | WGC119**199 |  |  | Gas Storage | Propane,Gas | Power Direct Vent | 119 | 74 | 9.3 | 27 | 3 |  | 191.04 | 199 | 0.96 | 719 |  |  |  | 2007-08-20 | 2018-12-12 | United States, Canada | ES_29975_WGC119**199_10122018184304_5781106 | Com Gas Storage | 120 | 199 | gt155kBtuh
2327850 | Lochinvar, LLC | Lochinvar | ARMOR CONDENSING | AWH4000(N,L) |  |  | Gas Tankless | Gas,Propane | Direct Vent | 46 |  |  |  | 12 |  |  | 4000 | 0.98 |  |  |  |  | 2018-02-19 | 2020-11-18 | United States, Canada | ES_1028919_AWH4000(N,L)_10122018184306_4287390 | Com Gas Instantaneous | 50 | 4000 | gte200kBtuh
2327851 | Ariston Thermo USA, LLC | HTP | Phoenix | PH160-119 |  |  | Gas Storage | Propane,Gas | Power Direct Vent | 119 | 74 | 9.3 | 27 | 3 |  | 153.6 | 160 | 0.96 | 621 |  |  |  | 2011-03-25 | 2018-12-12 | United States, Canada | ES_29975_PH160-119_10122018184439_1989177 | Com Gas Storage | 120 | 160 | gt155kBtuh
2327852 | Ariston Thermo USA, LLC | Westinghouse | Commercial Gas Water Heater | WGC119**160 |  |  | Gas Storage | Propane,Gas | Power Direct Vent | 119 | 74 | 9.3 | 27 | 3 |  | 153.6 | 160 | 0.96 | 621 |  |  |  | 2011-03-25 | 2018-12-12 | United States, Canada | ES_29975_WGC119**160_10122018184441_6002338 | Com Gas Storage | 120 | 160 | gt155kBtuh
2327854 | Ariston Thermo USA, LLC | HTP | Phoenix | PH160-55 |  |  | Gas Storage | Propane,Gas | Power Direct Vent | 55 | 52 | 5.2 | 23 | 3 |  | 152 | 160 | 0.95 | 596 |  |  |  | 2007-08-20 | 2018-12-12 | United States, Canada | ES_29975_PH160-55_10122018184534_0895471 | Com Gas Storage | 55 | 160 | gt155kBtuh
2327855 | Ariston Thermo USA, LLC | Westinghouse | Commercial Gas Water Heater | WGC055**160 |  |  | Gas Storage | Propane,Gas | Power Direct Vent | 55 | 52 | 5.2 | 23 | 3 |  | 152 | 160 | 0.95 | 596 |  |  |  | 2007-08-20 | 2018-12-12 | United States, Canada | ES_29975_WGC055**160_10122018184536_2084733 | Com Gas Storage | 55 | 160 | gt155kBtuh
2327856 | Ariston Thermo USA, LLC | HTP | Phoenix | PH199-55 |  |  | Gas Storage | Propane,Gas | Power Direct Vent | 55 | 52 | 5.2 | 23 | 3 |  | 189.05 | 199 | 0.95 | 409 |  |  |  | 2007-08-20 | 2018-10-12 | United States, Canada | ES_29975_PH199-55_10122018184558_0495641 | Com Gas Storage | 55 | 199 | gt155kBtuh
2327857 | Ariston Thermo USA, LLC | Westinghouse | Commercial Gas Water Heater | WGC055**199 |  |  | Gas Storage | Propane,Gas | Power Direct Vent | 55 | 52 | 5.2 | 23 | 3 |  | 189.05 | 199 | 0.95 | 409 |  |  |  | 2007-08-20 | 2018-10-12 | United States, Canada | ES_29975_WGC055**199_10122018184600_2556955 | Com Gas Storage | 55 | 199 | gt155kBtuh
2328279 | Lochinvar, LLC | A. O. Smith | XP Plus | PWH1250(N,L)(P)(-CAN) |  |  | Gas Tankless | Gas,Propane | Direct Vent | 12 |  |  |  | 8 | 6 |  | 1250 | 0.98 |  |  |  |  | 2018-08-22 | 2020-11-18 | United States, Canada | ES_1028919_PWH1250(N,L)(P)(-CAN)_10242018153851_8665676 | Com Gas Instantaneous | 30 | 1250 | gte200kBtuh
2328280 | Lochinvar, LLC | A. O. Smith | XP Plus | PWH1500(N,L)(P)(-CAN) |  |  | Gas Tankless | Gas,Propane | Direct Vent | 14 |  |  |  | 8 | 6 |  | 1500 | 0.98 |  |  |  |  | 2018-08-22 | 2020-11-18 | United States, Canada | ES_1028919_PWH1500(N,L)(P)(-CAN)_10242018153856_9549702 | Com Gas Instantaneous | 30 | 1500 | gte200kBtuh
2328281 | Lochinvar, LLC | A. O. Smith | XP Plus | PWH2000(N,L)(P)(-CAN) |  |  | Gas Tankless | Gas,Propane | Direct Vent | 18 |  |  |  | 8 |  |  | 1999 | 0.98 |  |  |  |  | 2018-08-22 | 2020-11-19 | United States, Canada | ES_1028919_PWH2000(N,L)(P)(-CAN)_10242018153859_7849025 | Com Gas Instantaneous | 30 | 1999 | gte200kBtuh
2328282 | Lochinvar, LLC | A. O. Smith | XP Plus | PWH3000(N,L)(P)(-CAN) |  |  | Gas Tankless | Gas,Propane | Direct Vent | 29 |  |  |  | 10 |  |  | 3000 | 0.98 |  |  |  |  | 2018-08-22 | 2020-11-18 | United States, Canada | ES_1028919_PWH3000(N,L)(P)(-CAN)_10242018153902_5101573 | Com Gas Instantaneous | 30 | 3000 | gte200kBtuh
2328283 | Lochinvar, LLC | A. O. Smith | XP Plus | PWH4000(N,L)(P)(-CAN) |  |  | Gas Tankless | Gas,Propane | Direct Vent | 46 |  |  |  | 12 |  |  | 4000 | 0.98 |  |  |  |  | 2018-08-22 | 2020-11-18 | United States, Canada | ES_1028919_PWH4000(N,L)(P)(-CAN)_10242018153905_9256438 | Com Gas Instantaneous | 50 | 4000 | gte200kBtuh
2328284 | Lochinvar, LLC | Lochinvar | OUTDOOR ARMOR | OA(N,L)701 |  |  | Gas Tankless | Gas,Propane | Direct Vent | 4 |  |  |  | 6 |  |  | 700 | 0.96 |  |  |  |  | 2012-10-24 | 2021-03-24 | United States | ES_1028919_OA(N,L)701_10242018154008_7760785 | Com Gas Instantaneous | 10 | 700 | gte200kBtuh
2328286 | Lochinvar, LLC | Lochinvar | ARMOR | AW(N,L)200(PM) |  |  | Gas Tankless | Gas,Propane | Direct Vent | 1 |  |  |  | 3 |  |  | 199.9 | 0.96 |  |  |  |  | 2012-10-24 | 2020-11-19 | United States, Canada | ES_1028919_AW(N,L)200(PM)_10242018154140_6018197 | Com Gas Instantaneous | 2 | 199.9 | lt200kBtuh
2328287 | Lochinvar, LLC | Lochinvar | ARMOR | AW(N,L)601(PM) |  |  | Gas Tankless | Gas,Propane | Direct Vent | 3 |  |  |  | 4 |  |  | 600 | 0.96 |  |  |  |  | 2012-10-24 | 2020-11-17 | United States, Canada | ES_1028919_AW(N,L)601(PM)_10242018154338_0571919 | Com Gas Instantaneous | 10 | 600 | gte200kBtuh
2328288 | Lochinvar, LLC | Lochinvar | ARMOR | AW(N,L)701(PM) |  |  | Gas Tankless | Gas,Propane | Direct Vent | 4 |  |  |  | 4 |  |  | 700 | 0.96 |  |  |  |  | 2012-10-24 | 2020-11-17 | United States, Canada | ES_1028919_AW(N,L)701(PM)_10242018154522_8961960 | Com Gas Instantaneous | 10 | 700 | gte200kBtuh
2328290 | Lochinvar, LLC | Lochinvar | ARMOR | AW(N,L)801(PM) |  |  | Gas Tankless | Gas,Propane | Direct Vent | 4 |  |  |  | 4 |  |  | 800 | 0.96 |  |  |  |  | 2012-10-24 | 2020-11-17 | United States, Canada | ES_1028919_AW(N,L)801(PM)_10242018162142_8147875 | Com Gas Instantaneous | 10 | 800 | gte200kBtuh
2330334 | Watts Heating and Hot Water Solutions LLC | PVI Industries, Lync | 20 L 100 A-GCL | 20 L 100 A-GCL |  |  | Gas Storage | Gas | Power Direct Vent | 100 | 60 | 5 | 23.8 | 3 | 4 | 189.05 | 199 | 0.95 | 1075 |  |  |  | 2014-09-15 | 2014-09-19 | United States, Canada | ES_1129873_20 L 100 A-GCL_12152014105424_2686273 | Com Gas Storage | 100 | 199 | gt155kBtuh
2330408 | Watts Heating and Hot Water Solutions LLC | PVI Industries, Lync | 25 L 100 A-GCL | 25 L 100 A-GCL |  |  | Gas Storage | Gas | Power Direct Vent | 100 | 60 | 5 | 23.8 | 3 | 4 | 237.5 | 250 | 0.95 | 1075 |  |  |  | 2014-09-15 | 2014-12-15 | United States, Canada | ES_1129873_25 L 100 A-GCL_12152014124646_9445154 | Com Gas Storage | 100 | 250 | gt155kBtuh
2330409 | Watts Heating and Hot Water Solutions LLC | PVI Industries, Lync | 30 L 100 A-GCL | 30 L 100 A-GCL |  |  | Gas Storage | Gas | Power Direct Vent | 100 | 60 | 5 | 23.8 | 3 | 4 | 285 | 300 | 0.95 | 1075 |  |  |  | 2014-09-15 | 2014-12-16 | United States, Canada | ES_1129873_30 L 100 A-GCL_12152014125013_4166681 | Com Gas Storage | 100 | 300 | gt155kBtuh
2330435 | Watts Heating and Hot Water Solutions LLC | PVI Industries, Lync | 70 L 130 A-GCML | 70 L 130 A-GCML |  |  | Gas Storage | Gas | Direct Vent | 130 | 66.7 | 9.7 | 27.5 | 6 | 8 | 672 | 700 | 0.96 | 1424 |  |  |  | 2014-11-06 | 2014-12-30 | United States, Canada | ES_1129873_70 L 130 A-GCML_12222014223000_471765 | Com Gas Storage | 120 | 700 | gt155kBtuh
2330446 | Watts Heating and Hot Water Solutions LLC | PVI Industries, Lync | 40 L 130 A-GCL | 40 L 130 A-GCL | ,40 L 130 A-GCML, |  | Gas Storage | Gas | Direct Vent | 130 | 66.7 | 9.7 | 27.5 | 6 | 4 | 383.04 | 399 | 0.96 | 1424 |  |  |  | 2014-11-06 | 2014-12-01 | United States, Canada | ES_1129873_40 L 130 A-GCL_12222014215237_7198449 | Com Gas Storage | 120 | 399 | gt155kBtuh
2331121 | Watts Heating and Hot Water Solutions LLC | PVI Industries, Lync | 65 L 130 A-GCML | 65 L 130 A-GCML |  |  | Gas Storage | Gas | Direct Vent | 130 | 66.7 | 9.7 | 27.5 | 6 | 8 | 624 | 650 | 0.96 | 1424 |  |  |  | 2014-11-06 | 2015-02-18 | United States, Canada | ES_1129873_65 L 130 A-GCML_02182015121256_6195184 | Com Gas Storage | 120 | 650 | gt155kBtuh
2331122 | Watts Heating and Hot Water Solutions LLC | PVI Industries, Lync | 80 L 130 A-GCML | 80 L 130 A-GCML |  |  | Gas Storage | Gas | Direct Vent | 130 | 66.7 | 9.7 | 27.5 | 6 | 8 | 768 | 800 | 0.96 | 1424 |  |  |  | 2014-11-06 | 2014-12-26 | United States, Canada | ES_1129873_80 L 130 A-GCML_12222014222248_5466555 | Com Gas Storage | 120 | 800 | gt155kBtuh
2331124 | Watts Heating and Hot Water Solutions LLC | PVI Industries, Lync | 75 L 130 A-GCML | 75 L 130 A-GCML |  |  | Gas Storage | Gas | Direct Vent | 130 | 66.7 | 9.7 | 27.5 | 6 | 8 | 720 | 750 | 0.96 | 1424 |  |  |  | 2014-11-06 | 2014-12-26 | United States, Canada | ES_1129873_75 L 130 A-GCML_12222014222821_5163995 | Com Gas Storage | 120 | 750 | gt155kBtuh
2331125 | Watts Heating and Hot Water Solutions LLC | PVI Industries, Lync | 60 L 130 A-GCML | 60 L 130 A-GCML |  |  | Gas Storage | Gas | Direct Vent | 130 | 66.7 | 9.7 | 27.5 | 6 | 8 | 576 | 600 | 0.96 | 1424 |  |  |  | 2014-11-06 | 2014-12-26 | United States, Canada | ES_1129873_60 L 130 A-GCML_12222014223120_2059900 | Com Gas Storage | 120 | 600 | gt155kBtuh
2331127 | Watts Heating and Hot Water Solutions LLC | PVI Industries, Lync | 50 L 130A-GCML | 50 L 130A-GCML |  |  | Gas Storage | Gas | Direct Vent | 130 | 66.7 | 9.7 | 27.5 | 6 | 4 | 480 | 500 | 0.96 | 1424 |  |  |  | 2014-11-06 | 2014-12-26 | United States, Canada | ES_1129873_50 L 130 A-GCML_12222014222540_8679468 | Com Gas Storage | 120 | 500 | gt155kBtuh
2332886 | Watts Heating and Hot Water Solutions LLC | PVI Industries, Lync | 100 L 130A-GCML | 100 L 130A-GCML |  |  | Gas Storage | Gas | Direct Vent | 130 | 66.7 | 9.7 | 27.5 | 6 | 8 | 949.05 | 999 | 0.95 | 1185 |  |  |  | 2019-01-29 | 2019-02-01 | United States, Canada | ES_1129873_100 L 130A-GCML_01292019163828_4687311 | Com Gas Storage | 120 | 999 | gt155kBtuh
2333065 | Intellihot Inc | Intellihot | iQ750 | iQ750 | .,iQ751 Gen II,; .,iQ751, |  | Gas Tankless | Gas,Propane | Direct Vent | 4 |  |  |  | 6 |  |  | 714 | 0.94 |  |  |  |  | 2013-08-16 | 2019-01-14 | United States, Canada | ES_1084851_iQ750_02042019143949_6346855 | Com Gas Instantaneous | 10 | 714 | gte200kBtuh
2333068 | Intellihot Inc | Intellihot | iQ250 | iQ250 | .,iQ251 Gen II,; .,iQ251,; .,iQ251D Gen II,; .,iQ251D, |  | Gas Tankless | Gas,Propane | Direct Vent | 1 |  |  |  | 3 |  |  | 250 | 0.96 |  |  |  |  | 2013-04-25 | 2019-01-14 | United States, Canada | ES_1084851_iQ250_02052019114425_2218367 | Com Gas Instantaneous | 2 | 250 | gte200kBtuh
2333069 | Intellihot Inc | Intellihot | iQ1000 | iQ1000 | .,iQ1001 Gen II,; .,iQ1001, |  | Gas Tankless | Gas,Propane | Direct Vent | 4 |  |  |  | 6 |  |  | 952 | 0.94 |  |  |  |  | 2013-08-16 | 2019-01-14 | United States, Canada | ES_1084851_iQ1000_02052019114839_3944442 | Com Gas Instantaneous | 10 | 952 | gte200kBtuh
2333099 | American Standard Water Heaters | American Standard | HE 70-125 AS | HE 70-125 AS |  |  | Gas Storage | Gas | Direct Vent | 70 | 58 | 9.3 | 22 | 2 |  | 121.25 | 125 | 0.97 | 598 |  |  |  | 2012-07-23 | 2019-01-23 | United States | ES_1081272_HE 70-125 AS_02052019132431_2787911 | Com Gas Storage | 75 | 125 | lte155kBtuh
2333104 | American Standard Water Heaters | American Standard | HE 100-150 AS | HE 100-150 AS |  |  | Gas Storage | Gas | Direct Vent | 100 | 66 | 9.3 | 24 | 2 |  | 145.5 | 150 | 0.97 | 767 |  |  |  | 2012-07-23 | 2019-01-23 | United States | ES_1081272_HE 100-150 AS_02052019135450_5112090 | Com Gas Storage | 100 | 150 | lte155kBtuh
2333105 | American Standard Water Heaters | American Standard | HE 100-199 AS | HE 100-199 AS |  |  | Gas Storage | Gas | Direct Vent | 100 | 66 | 9.3 | 24 | 2 |  | 195.02 | 199 | 0.98 | 640 |  |  |  | 2012-07-23 | 2019-01-23 | United States | ES_1081272_HE 100-199 AS_02052019140448_6656463 | Com Gas Storage | 100 | 199 | gt155kBtuh
2333106 | American Standard Water Heaters | American Standard | HE 100-250 AS | HE 100-250 AS |  |  | Gas Storage | Gas | Direct Vent | 100 | 66 | 9.3 | 24 | 2 |  | 240 | 250 | 0.96 | 683 |  |  |  | 2012-07-23 | 2019-01-23 | United States | ES_1081272_HE 100-250 AS_02052019140721_2325032 | Com Gas Storage | 100 | 250 | gt155kBtuh
2333867 | A.O. Smith Corporation | AO Smith | CHP Series | CAHP-120 100 |  |  | Electric Heat Pump | Electric |  | 119 | [5 empty] | 176.0592 |  |  |  | 12 | 4.3 |  | 2019-04-01 | 2019-02-21 | United States | ES_92897_CAHP-120 100_02222019165341_4421300 | Heat Pump | 120 | 40.944 | #N/A
2333868 | A.O. Smith Corporation | Lochinvar | CHP Series | CHPA120PD 100 |  |  | Electric Heat Pump | Electric |  | 119 | [5 empty] | 176.0592 |  |  |  | 12 | 4.3 |  | 2019-04-01 | 2019-02-21 | United States | ES_92897_CHPA120PD 100_02222019165503_4503350 | Heat Pump | 120 | 40.944 | #N/A
2333869 | A.O. Smith Corporation | State | CHP Series | CSHP-120-DHPT 100 |  |  | Electric Heat Pump | Electric |  | 119 | [5 empty] | 176.0592 |  |  |  | 12 | 4.3 |  | 2019-04-01 | 2019-02-21 | United States | ES_92897_CSHP-120-DHPT 100_02222019165437_4477825 | Heat Pump | 120 | 40.944 | #N/A
2334087 | Watts Heating and Hot Water Solutions LLC | PVI Industries, Lync | 90 L 130A-GCML | 90 L 130A-GCML |  |  | Gas Storage | Gas | Direct Vent | 130 | 66.7 | 9.7 | 27.5 | 6 | 8 | 855 | 900 | 0.95 | 969 |  |  |  | 2019-02-28 | 2019-02-28 | United States, Canada | ES_1129873_90 L 130A-GCML_02282019154309_9266473 | Com Gas Storage | 120 | 900 | gt155kBtuh
2327781 | Bradford White Corporation | Bradford White | EF100T399E*N* | EF100T399E*N2 |  |  | Gas Storage | Gas | Power Direct Vent | 100 | 69 | 5 | 26 | 3 | 4 | 375.06 | 399 | 0.94 | 1075 |  |  |  | 2013-04-01 | 2018-11-05 | United States, Canada | ES_92896_EF100T399E*N2_10122018182053_6975820 | Com Gas Storage | 100 | 399 | gt155kBtuh
2327782 | Lochinvar, LLC | Lochinvar | ARMOR WALL MOUNT | WA(N,L)200 |  |  | Gas Tankless | Propane,Gas | Direct Vent | 1 |  |  |  | 3 |  | 191.904 | 199.9 | 0.96 |  |  |  |  | 2012-12-04 | 2018-10-12 | United States, Canada | ES_1028919_WA(N,L)200_10122018182301_7441267 | Com Gas Instantaneous | 2 | 199.9 | lt200kBtuh
2327783 | Lochinvar, LLC | Lochinvar | OUTDOOR ARMOR | OA(N,L)801 |  |  | Gas Tankless | Gas,Propane | Direct Vent | 4 |  |  |  | 6 |  |  | 800 | 0.96 |  |  |  |  | 2012-10-24 | 2021-03-24 | United States | ES_1028919_OA(N,L)801_10122018182509_2573778 | Com Gas Instantaneous | 10 | 800 | gte200kBtuh
2327784 | Ariston Thermo USA, LLC | HTP | Phoenix Multi-Fit | PHM199-100 |  |  | Gas Storage | Propane,Gas | Direct Vent | 100 | 63 | 18.2 | 27 | 3 |  | 189.05 | 199 | 0.95 | 445 |  |  |  | 2014-12-10 | 2018-12-12 | United States, Canada | ES_29975_PHM199-100_10122018182709_2253476 | Com Gas Storage | 100 | 199 | gt155kBtuh
2327785 | Ariston Thermo USA, LLC | Westinghouse | Commercial Gas Water Heater Multi-Fit | WGCM100**199 |  |  | Gas Storage | Propane,Gas | Power Direct Vent | 100 | 63 | 18.2 | 27 | 3 |  | 189.05 | 199 | 0.95 | 445 |  |  |  | 2014-12-10 | 2018-12-12 | United States, Canada | ES_29975_WGCM100**199_10122018182711_2362943 | Com Gas Storage | 100 | 199 | gt155kBtuh
2327786 | NY Thermal Inc. | Trinity | Trinity | LX600WH |  |  | Gas Tankless | Gas | Direct Vent | 4 |  |  |  | 4 |  | 576 | 600 | 0.96 |  |  |  |  | 2014-11-06 | 2018-12-12 | United States, Canada | ES_1016238_LX600WH_10122018182832_3661070 | Com Gas Instantaneous | 10 | 600 | gte200kBtuh
2327787 | Noritz America Corporation | Noritz | NCC300DV | NCC300DV (GQ-C5032WZ-FF US) |  |  | Gas Tankless | Propane,Gas | Power Direct Vent | 0 |  |  |  | 4 | 4 | 291 | 300 | 0.97 |  |  |  |  | 2018-01-01 | 2018-12-12 | United States, Canada | ES_1070591_NCC300DV (GQ-C5032WZ-FF US)_10122018182926_2425661 | Com Gas Instantaneous | 2 | 300 | gte200kBtuh
2327791 | Ariston Thermo USA, LLC | HTP | Phoenix | PH130-55 |  |  | Gas Storage | Propane,Gas | Direct Vent | 55 | 52 | 5.2 | 23 | 2 |  | 122.2 | 130 | 0.94 | 596 |  |  |  | 2007-08-20 | 2018-12-12 | United States, Canada | ES_29975_PH130-55_10122018183310_7986363 | Com Gas Storage | 55 | 130 | lte155kBtuh
2327792 | Ariston Thermo USA, LLC | Westinghouse | Commercial Gas Water Heater | WGC055**130 |  |  | Gas Storage | Propane,Gas | Power Direct Vent | 55 | 52 | 5.2 | 23 | 2 |  | 122.2 | 130 | 0.94 | 596 |  |  |  | 2007-08-20 | 2018-12-12 | United States, Canada | ES_29975_WGC055**130_10122018183312_8095830 | Com Gas Storage | 55 | 130 | lte155kBtuh
2326634 | King Heating Products, Inc. | King Heating Products Inc. | Ecoking Ultimate Volume Water Heater | EK 299-DHW |  |  | Gas Tankless | Gas |  | 0 | [5 empty] | 277394 | 295100 | 0.94 |  |  |  |  | 2018-05-01 | 2018-06-14 | Canada | ES_1125479_EK 299-DHW_06152018163834_0714234 | Com Gas Instantaneous | 2 | 295100 | gte200kBtuh
2326635 | King Heating Products, Inc. | King Heating Products Inc. | Ecoking Ultimate Volume Water Heater | EK 399-DHW |  |  | Gas Tankless | Gas |  | 0 | [5 empty] | 372428 | 396200 | 0.94 |  |  |  |  | 2018-05-01 | 2018-06-14 | Canada | ES_1125479_EK 399-DHW_06152018170239_2159081 | Com Gas Instantaneous | 2 | 396200 | gte200kBtuh
2326636 | King Heating Products, Inc. | King Heating Products Inc. | Ecoking Ultimate Volume Water Heater | EK 499-DHW |  |  | Gas Tankless | Gas |  | 0 | [5 empty] | 445560 | 474000 | 0.94 |  |  |  |  | 2018-05-01 | 2018-06-14 | Canada | ES_1125479_EK 499-DHW_06152018170218_2138744 | Com Gas Instantaneous | 2 | 474000 | gte200kBtuh
2327373 | NY Thermal Inc. | Trinity | Trinity | LX200WH |  |  | Gas Tankless | Propane,Gas | Direct Vent | 1 |  |  |  | 3 |  | 191.04 | 199 | 0.96 |  |  |  |  | 2014-11-06 | 2018-10-11 | United States, Canada | ES_1016238_LX200WH_10112018194810_5970378 | Com Gas Instantaneous | 2 | 199 | lt200kBtuh
2327374 | NY Thermal Inc. | Trinity | Trinity | LX400WH |  |  | Gas Tankless | Propane,Gas | Direct Vent | 2 |  |  |  | 4 |  | 383.04 | 399 | 0.96 |  |  |  |  | 2014-11-06 | 2018-10-11 | United States, Canada | ES_1016238_LX400WH_10112018194813_6603232 | Com Gas Instantaneous | 2 | 399 | gte200kBtuh
2327375 | NY Thermal Inc. | Trinity | Trinity | LX500WH |  |  | Gas Tankless | Propane,Gas | Direct Vent | 3 |  |  |  | 4 |  | 480 | 500 | 0.96 |  |  |  |  | 2014-11-06 | 2018-10-11 | United States, Canada | ES_1016238_LX500WH_10112018194815_1205822 | Com Gas Instantaneous | 10 | 500 | gte200kBtuh
2327376 | NY Thermal Inc. | Trinity | Trinity | LX700WH |  |  | Gas Tankless | Gas | Direct Vent | 5 |  |  |  | 6 |  | 672 | 700 | 0.96 |  |  |  |  | 2014-11-06 | 2018-10-11 | United States, Canada | ES_1016238_LX700WH_10112018194817_6331798 | Com Gas Instantaneous | 10 | 700 | gte200kBtuh
2327377 | NY Thermal Inc. | Trinity | Trinity | LX800WH |  |  | Gas Tankless | Gas | Direct Vent | 5 |  |  |  | 6 |  | 768 | 800 | 0.96 |  |  |  |  | 2014-11-06 | 2018-10-11 | United States, Canada | ES_1016238_LX800WH_10112018194819_7313317 | Com Gas Instantaneous | 10 | 800 | gte200kBtuh
2327390 | NY Thermal Inc. | Trinity | Trinity | LX300WH |  |  | Gas Tankless | Propane,Gas | Direct Vent | 2 |  |  |  | 4 |  | 264 | 275 | 0.96 |  |  |  |  | 2014-11-06 | 2018-10-11 | United States, Canada | ES_1016238_LX300WH_10112018200140_7265310 | Com Gas Instantaneous | 2 | 275 | gte200kBtuh
2327467 | A.O. Smith Corporation | State | STX-199-N-100 | STX-199-N-100 |  |  | Gas Storage | Gas | Power Direct Vent | 119 | 69 | 61.3 | 24 | 4 | 3 | 191.04 | 199 | 0.96 | 1100 |  |  |  | 2017-07-18 | 2018-10-12 | United States, Canada | ES_92897_STX-199-N-100_10122018153717_4154550 | Com Gas Storage | 120 | 199 | gt155kBtuh
2327470 | Lochinvar, LLC | Lochinvar | ARMOR | AW(N,L)400(PM) |  |  | Gas Tankless | Gas,Propane | Direct Vent | 3 |  |  |  | 4 |  |  | 399.9 | 0.96 |  |  |  |  | 2012-10-24 | 2020-11-18 | United States, Canada | ES_1028919_AW(N,L)400(PM)_10122018153901_2021205 | Com Gas Instantaneous | 10 | 399.9 | gte200kBtuh
2327508 | A.O. Smith Corporation | American | Polaris | PC 50 199 N 200 |  |  | Gas Storage | Gas | Power Direct Vent | 50 | 63.7 | 6.6 | 22 | 3 |  | 191.04 | 199 | 0.96 | 800 |  |  |  | 2017-02-15 | 2018-12-10 | Canada | ES_92897_PC 50 199 N 200_10122018162923_5364664 | Com Gas Storage | 50 | 199 | gt155kBtuh
2327512 | A.O. Smith Corporation | American | Polaris | PR 50 199 N 200 |  |  | Gas Storage | Gas | Power Direct Vent | 50 | 63.7 | 6.6 | 22 | 3 |  | 191.04 | 199 | 0.96 | 800 |  |  |  | 2017-02-15 | 2018-12-10 | Canada | ES_92897_PR 50 199 N 200_10122018163418_6279531 | Com Gas Storage | 50 | 199 | gt155kBtuh
2327515 | A.O. Smith Corporation | American | Polaris | PC 50 175 N 200 |  |  | Gas Storage | Gas | Power Direct Vent | 50 | 63.7 | 6.6 | 22 | 3 |  | 168 | 175 | 0.96 | 800 |  |  |  | 2017-02-15 | 2018-12-10 | Canada | ES_92897_PC 50 175 N 200_10122018163800_7096724 | Com Gas Storage | 50 | 175 | gt155kBtuh
2327519 | A.O. Smith Corporation | American | Polaris | PR 50 175 N 200 |  |  | Gas Storage | Gas | Power Direct Vent | 50 | 63.7 | 6.6 | 22 | 3 |  | 168 | 175 | 0.96 | 800 |  |  |  | 2017-02-15 | 2018-12-10 | Canada | ES_92897_PR 50 175 N 200_10122018164135_9220936 | Com Gas Storage | 50 | 175 | gt155kBtuh
2327522 | A.O. Smith Corporation | American | Polaris | PC 50 150 N 200 |  |  | Gas Storage | Gas | Power Direct Vent | 50 | 63.7 | 6.6 | 22 | 2 |  | 142.5 | 150 | 0.95 | 750 |  |  |  | 2017-02-15 | 2018-12-10 | Canada | ES_92897_PC 50 150 N 200_10122018164406_9668238 | Com Gas Storage | 50 | 150 | lte155kBtuh
2327530 | A.O. Smith Corporation | American | Polaris | PC 50 130 N 200 |  |  | Gas Storage | Gas | Power Direct Vent | 50 | 62.3 | 6.6 | 22 | 2 |  | 123.5 | 130 | 0.95 | 750 |  |  |  | 2017-02-15 | 2018-12-10 | Canada | ES_92897_PC 50 130 N 200_10122018165030_1413246 | Com Gas Storage | 50 | 130 | lte155kBtuh
2327536 | Bradford White Corporation | Bradford White | EF60T125E*N*2 | EF60T125E*N*2 |  |  | Gas Storage | Gas | Power Direct Vent | 60 | 48 | 5 | 26 | 3 | 4 | 120 | 125 | 0.96 | 824 |  |  |  | 2013-04-01 | 2018-12-12 | United States, Canada | ES_92896_EF60T125E*N*2_10122018165423_8283867 | Com Gas Storage | 60 | 125 | lte155kBtuh
2327537 | A.O. Smith Corporation | American | Polaris | PC 34 130 N 200 |  |  | Gas Storage | Gas | Power Direct Vent | 34 | 48.5 | 6.6 | 22 | 2 |  | 124.8 | 130 | 0.96 | 650 |  |  |  | 2017-02-15 | 2018-12-10 | Canada | ES_92897_PC 34 130 N 200_10122018165516_8160490 | Com Gas Storage | 40 | 130 | lte155kBtuh
2327539 | A.O. Smith Corporation | American | Polaris | PR 34 130 N 200 |  |  | Gas Storage | Gas | Power Direct Vent | 34 | 48.5 | 6.6 | 22 | 2 |  | 124.8 | 130 | 0.96 | 650 |  |  |  | 2017-02-15 | 2018-12-10 | Canada | ES_92897_PR 34 130 N 200_10122018165701_3170226 | Com Gas Storage | 40 | 130 | lte155kBtuh
2327540 | Ariston Thermo USA, LLC | HTP | Phoenix | PH199-80 |  |  | Gas Storage | Propane,Gas | Power Direct Vent | 80 | 72 | 7.5 | 23 | 3 |  | 189.05 | 199 | 0.95 | 495 |  |  |  | 2007-08-20 | 2018-12-12 | United States, Canada | ES_29975_PH199-80_10122018165748_2686211 | Com Gas Storage | 80 | 199 | gt155kBtuh
2327541 | Ariston Thermo USA, LLC | HTP | Phoenix Multi-Fit | PHM199-80 |  |  | Gas Storage | Propane,Gas | Direct Vent | 80 | 55 | 18.2 | 27 | 3 |  | 191.04 | 199 | 0.96 | 426 |  |  |  | 2014-12-10 | 2018-12-12 | United States, Canada | ES_29975_PHM199-80_10122018165751_4922248 | Com Gas Storage | 80 | 199 | gt155kBtuh
2327542 | Ariston Thermo USA, LLC | Westinghouse | Commercial Gas Water Heater | WGC080**199 |  |  | Gas Storage | Propane,Gas | Power Direct Vent | 80 | 72 | 7.5 | 23 | 3 |  | 189.05 | 199 | 0.95 | 495 |  |  |  | 2007-08-20 | 2018-12-12 | United States, Canada | ES_29975_WGC080**199_10122018165753_4475308 | Com Gas Storage | 80 | 199 | gt155kBtuh
2327544 | Ariston Thermo USA, LLC | Westinghouse | Commercial Gas Water Heater Multi-Fit | WGCM080**199 |  |  | Gas Storage | Propane,Gas | Power Direct Vent | 80 | 55 | 18.2 | 27 | 3 |  | 191.04 | 199 | 0.96 | 426 |  |  |  | 2014-12-10 | 2018-12-12 | United States, Canada | ES_29975_WGCM080**199_10122018165756_8172825 | Com Gas Storage | 80 | 199 | gt155kBtuh
2327554 | Ariston Thermo USA, LLC | HTP | Phoenix | PH130-80 |  |  | Gas Storage | Propane,Gas | Direct Vent | 80 | 72 | 7.5 | 23 | 2 |  | 123.5 | 130 | 0.95 | 498 |  |  |  | 2007-08-20 | 2018-12-12 | United States, Canada | ES_29975_PH130-80_10122018165943_4131059 | Com Gas Storage | 80 | 130 | lte155kBtuh
2327555 | Ariston Thermo USA, LLC | HTP | Phoenix Multi-Fit | PHM130-80 |  |  | Gas Storage | Propane,Gas | Direct Vent | 80 | 55 | 18.2 | 27 | 2 |  | 124.8 | 130 | 0.96 | 395 |  |  |  | 2014-12-10 | 2018-12-12 | United States, Canada | ES_29975_PHM130-80_10122018165945_4763914 | Com Gas Storage | 80 | 130 | lte155kBtuh
2327556 | Ariston Thermo USA, LLC | Westinghouse | Commercial Gas Water Heater | WGC080**130 |  |  | Gas Storage | Propane,Gas | Power Direct Vent | 80 | 72 | 7.5 | 23 | 2 |  | 123.5 | 130 | 0.95 | 498 |  |  |  | 2007-08-20 | 2018-12-12 | United States, Canada | ES_29975_WGC080**130_10122018165948_5048105 | Com Gas Storage | 80 | 130 | lte155kBtuh
2327557 | Ariston Thermo USA, LLC | Westinghouse | Commercial Gas Water Heater Multi-Fit | WGCM080**130 |  |  | Gas Storage | Propane,Gas | Power Direct Vent | 80 | 55 | 18.2 | 27 | 2 |  | 124.8 | 130 | 0.96 | 395 |  |  |  | 2014-12-10 | 2018-12-12 | United States, Canada | ES_29975_WGCM080**130_10122018165950_2092909 | Com Gas Storage | 80 | 130 | lte155kBtuh
2327567 | Ariston Thermo USA, LLC | HTP | Phoenix | PH160-80 |  |  | Gas Storage | Propane,Gas | Direct Vent | 80 | 72 | 7.5 | 23 | 3 |  | 153.6 | 160 | 0.96 | 472 |  |  |  | 2007-08-20 | 2018-12-12 | United States, Canada | ES_29975_PH160-80_10122018170156_0497043 | Com Gas Storage | 80 | 160 | gt155kBtuh
2327568 | Ariston Thermo USA, LLC | Westinghouse | Commercial Gas Water Heater | WGC080**160 |  |  | Gas Storage | Propane,Gas | Power Direct Vent | 80 | 72 | 7.5 | 23 | 3 |  | 153.6 | 160 | 0.96 | 472 |  |  |  | 2007-08-20 | 2018-12-12 | United States, Canada | ES_29975_WGC080**160_10122018170159_8621642 | Com Gas Storage | 80 | 160 | gt155kBtuh
2327569 | Ariston Thermo USA, LLC | HTP | Phoenix | PH130-119 |  |  | Gas Storage | Propane,Gas | Direct Vent | 119 | 74 | 9.3 | 27 | 2 |  | 124.8 | 130 | 0.96 | 697 |  |  |  | 2007-08-20 | 2018-12-12 | United States, Canada | ES_29975_PH130-119_10122018170326_6660119 | Com Gas Storage | 120 | 130 | lte155kBtuh
2327571 | Ariston Thermo USA, LLC | Westinghouse | Commercial Gas Water Heater | WGC119**130 |  |  | Gas Storage | Propane,Gas | Power Direct Vent | 119 | 74 | 9.3 | 27 | 2 |  | 124.8 | 130 | 0.96 | 697 |  |  |  | 2007-08-20 | 2018-12-12 | United States, Canada | ES_29975_WGC119**130_10122018170329_6977329 | Com Gas Storage | 120 | 130 | lte155kBtuh
2327573 | A.O. Smith Corporation | A. O. Smith | AHCG3-100T199-3N 300 | BTH 500A 300 |  |  | Gas Storage-type Instantaneous | Gas | Power Direct Vent | 119 | 62.9 | 11 | 24 | 3 | 4 | 479.904 | 499.9 | 0.96 | 1200 |  |  |  | 2014-05-09 | 2018-10-12 | United States | ES_92897_BTH 500A 300_10122018170453_3128434 | Com Gas Storage-type Instantaneous | 120 | 499.9 | gte200kBtuh
2327579 | A.O. Smith Corporation | American | Polaris | PR 50 130 N 200 |  |  | Gas Storage | Gas | Power Direct Vent | 50 | 62.3 | 6.6 | 22 | 2 |  | 123.5 | 130 | 0.95 | 750 |  |  |  | 2017-02-15 | 2018-12-10 | Canada | ES_92897_PR 50 130 N 200_10122018170655_6123182 | Com Gas Storage | 50 | 130 | lte155kBtuh
2360867 | Lochinvar, LLC | Lochinvar | Shield | SWA500N |  |  | Gas Storage-type Instantaneous | Gas | Power Direct Vent | 110 |  |  |  | 4 |  | 479.04 | 499 | 0.96 | 1493 |  |  |  | 2020-06-01 | 2020-05-28 | United States, Canada | ES_1028919_SWA500N_05132020181548_4553134 | Com Gas Storage-type Instantaneous | 120 | 499 | gte200kBtuh
2360868 | Lochinvar, LLC | Lochinvar | Shield | SWR400N |  |  | Gas Storage | Gas | Power Direct Vent | 110 | 77.5 | 79.4 | 34 | 4 |  | 379.05 | 399 | 0.95 | 1388 |  |  |  | 2020-06-01 | 2020-05-28 | United States, Canada | ES_1028919_SWR400N_05132020181547_9970040 | Com Gas Storage | 120 | 399 | gt155kBtuh
2360872 | Lochinvar, LLC | Lochinvar | Shield | SWR200N |  |  | Gas Storage | Gas | Power Direct Vent | 90 | 76 | 79.5 | 28.3 | 3 |  | 191.04 | 199 | 0.96 | 1085 |  |  |  | 2020-06-01 | 2020-05-28 | United States, Canada | ES_1028919_SWR200N_05132020181545_1056088 | Com Gas Storage | 100 | 199 | gt155kBtuh
2360874 | Lochinvar, LLC | Lochinvar | Shield | SWR150N |  |  | Gas Storage | Gas | Power Direct Vent | 90 | 76 | 79.5 | 28.3 | 3 |  | 144 | 150 | 0.96 | 1034 |  |  |  | 2020-06-01 | 2020-05-28 | United States, Canada | ES_1028919_SWR150N_05132020181543_2581997 | Com Gas Storage | 100 | 150 | lte155kBtuh
2360877 | Lochinvar, LLC | Lochinvar | Shield | SWA200N |  |  | Gas Storage | Gas | Power Direct Vent | 90 | 76 | 79.5 | 28.3 | 3 |  | 191.04 | 199 | 0.96 | 1085 |  |  |  | 2020-06-01 | 2020-05-28 | United States, Canada | ES_1028919_SWA200N_05132020180630_5699182 | Com Gas Storage | 100 | 199 | gt155kBtuh
2360878 | Lochinvar, LLC | Lochinvar | Shield | SWA400N |  |  | Gas Storage | Gas | Power Direct Vent | 110 | 77.5 | 79.4 | 34 | 4 |  | 379.05 | 399 | 0.95 | 1388 |  |  |  | 2020-06-01 | 2020-05-28 | United States, Canada | ES_1028919_SWA400N_05132020180629_420537 | Com Gas Storage | 120 | 399 | gt155kBtuh
2360879 | Lochinvar, LLC | Lochinvar | Shield | SWA150N |  |  | Gas Storage | Gas | Power Direct Vent | 90 | 76 | 79.5 | 28.3 | 3 |  | 144 | 150 | 0.96 | 1034 |  |  |  | 2020-06-01 | 2020-05-28 | United States, Canada | ES_1028919_SWA150N_05132020180629_154650 | Com Gas Storage | 100 | 150 | lte155kBtuh
2360880 | Lochinvar, LLC | Lochinvar | Shield | SWR125N |  |  | Gas Storage | Gas | Power Direct Vent | 65 | 62.5 | 66 | 28.3 | 3 |  | 120 | 125 | 0.96 | 876 |  |  |  | 2020-06-01 | 2020-05-28 | United States, Canada | ES_1028919_SWR125N_05132020180628_1053159 | Com Gas Storage | 75 | 125 | lte155kBtuh
2362760 | Intellihot Inc | Intellihot | IQ Floor Model | iQ3001 | .,iQ2001, |  | Gas Tankless | Gas,Propane | Direct Vent | 12 |  |  |  | 8 | 8 |  | 3001 | 0.94 | 1584 |  |  |  | 2020-07-15 | 2020-07-15 | United States, Canada | ES_1084851_iQ3001_07152020102409_3841596 | Com Gas Instantaneous | 30 | 3001 | gte200kBtuh
2367056 | A.O. Smith Corporation | A. O. Smith | BTH 251* 3** | BTH 251* 3** |  |  | Gas Storage | Gas,Propane | Power Direct Vent | 119 | 62.9 | 11 | 24 | 3 | 4 |  | 250 | 0.96 | 1200 |  |  |  | 2020-09-01 | 2020-10-08 | United States | ES_92897_BTH 251* 3**_09042020125229_1015198 | Com Gas Storage | 120 | 250 | gt155kBtuh
2367057 | A.O. Smith Corporation | American | BTH 500* 3** | AHCG3-119T500-3* 3** |  |  | Gas Storage-type Instantaneous | Gas,Propane | Power Direct Vent | 119 |  |  |  | 4 | 6 |  | 499.9 | 0.96 | 1200 |  |  |  | 2014-05-09 | 2020-10-08 | United States | ES_92897_AHCG3-119T500-3* 3**_09022020134120_5023752 | Com Gas Storage-type Instantaneous | 120 | 499.9 | gte200kBtuh
2367058 | A.O. Smith Corporation | American | BTH 500* 3** | HCG3-119T500-3* 3** |  |  | Gas Storage-type Instantaneous | Gas,Propane | Power Direct Vent | 119 |  |  |  | 4 | 6 |  | 499.9 | 0.96 | 1200 |  |  |  | 2014-05-09 | 2020-10-08 | United States | ES_92897_HCG3-119T500-3* 3**_09022020134117_8518038 | Com Gas Storage-type Instantaneous | 120 | 499.9 | gte200kBtuh
2367059 | A.O. Smith Corporation | American | BTH 400* 3** | AHCG3-119T400-3* 3** |  |  | Gas Storage | Gas,Propane | Power Direct Vent | 119 | 62.9 | 12 | 30 | 4 | 6 |  | 399.9 | 0.95 | 1200 |  |  |  | 2014-05-09 | 2020-10-08 | United States | ES_92897_AHCG3-119T400-3* 3**_09022020132125_1227460 | Com Gas Storage | 120 | 399.9 | gt155kBtuh
2367060 | A.O. Smith Corporation | American | BTH 400* 3** | HCG3-119T400-3* 3** |  |  | Gas Storage | Gas,Propane | Power Direct Vent | 119 | 62.9 | 12 | 30 | 4 | 6 |  | 399.9 | 0.95 | 1200 |  |  |  | 2014-05-09 | 2020-10-08 | United States | ES_92897_HCG3-119T400-3* 3**_09022020132124_9547454 | Com Gas Storage | 120 | 399.9 | gt155kBtuh
2367061 | A.O. Smith Corporation | American | BTH 300* 3** | AHCG3-119T300-3* 3** |  |  | Gas Storage | Gas,Propane | Power Direct Vent | 119 | 62.9 | 12 | 30 | 4 | 6 |  | 300 | 0.96 | 1200 |  |  |  | 2014-05-09 | 2020-10-08 | United States | ES_92897_AHCG3-119T300-3* 3**_09022020132124_6162398 | Com Gas Storage | 120 | 300 | gt155kBtuh
2367062 | A.O. Smith Corporation | American | BTH 300* 3** | HCG3-119T300-3* 3** |  |  | Gas Storage | Gas,Propane | Power Direct Vent | 119 | 62.9 | 12 | 30 | 4 | 6 |  | 300 | 0.96 | 1200 |  |  |  | 2014-05-09 | 2020-10-08 | United States | ES_92897_HCG3-119T300-3* 3**_09022020132124_531661 | Com Gas Storage | 120 | 300 | gt155kBtuh
2367063 | A.O. Smith Corporation | State | BTH 199* 3** | SUF 100 199*E* 3** |  |  | Gas Storage | Gas,Propane | Power Direct Vent | 100 | 62.9 | 11 | 24 | 3 | 4 |  | 199 | 0.97 | 1000 |  |  |  | 2014-05-09 | 2020-10-08 | United States | ES_92897_SUF 100 199*E* 3**_09022020132124_3749249 | Com Gas Storage | 100 | 199 | gt155kBtuh
2367064 | A.O. Smith Corporation | American | BTH 250* 3** | HCG3-100T250-3* 3** |  |  | Gas Storage | Gas,Propane | Power Direct Vent | 100 | 62.9 | 11 | 24 | 3 | 4 |  | 250 | 0.96 | 1000 |  |  |  | 2014-05-09 | 2020-10-08 | United States | ES_92897_HCG3-100T250-3* 3**_09022020132124_7365000 | Com Gas Storage | 100 | 250 | gt155kBtuh
2367065 | A.O. Smith Corporation | American | BTH 199* 3** | HCG3-100T199-3* 3** |  |  | Gas Storage | Gas,Propane | Power Direct Vent | 100 | 62.9 | 11 | 24 | 3 | 4 |  | 199 | 0.97 | 1000 |  |  |  | 2014-05-09 | 2020-10-08 | United States | ES_92897_HCG3-100T199-3* 3**_09022020132123_6300375 | Com Gas Storage | 100 | 199 | gt155kBtuh
2367066 | A.O. Smith Corporation | American | BTH 150* 3** | AHCG3-100T150-3* 3** |  |  | Gas Storage | Gas,Propane | Power Direct Vent | 100 | 62.9 | 11 | 24 | 3 | 4 |  | 150 | 0.96 | 1000 |  |  |  | 2014-05-09 | 2020-10-08 | United States | ES_92897_AHCG3-100T150-3* 3**_09022020132122_712870 | Com Gas Storage | 100 | 150 | lte155kBtuh
2369320 | Lochinvar, LLC | Lochinvar | Shield | SWR285N |  |  | Gas Storage | Gas |  | 110 | 77.5 | 79.4 | 34 | 4 |  | 270.75 | 285 | 0.95 | 1268 |  |  |  | 2020-10-19 | 2020-11-10 | United States, Canada | ES_1028919_SWR285N_09222020130423_2349964 | Com Gas Storage | 120 | 285 | gt155kBtuh
2369323 | Lochinvar, LLC | Lochinvar | Shield | SWA285N |  |  | Gas Storage | Gas |  | 110 | 77.5 | 79.4 | 34 | 4 |  | 270.75 | 285 | 0.95 | 1268 |  |  |  | 2020-10-19 | 2020-11-10 | United States, Canada | ES_1028919_SWA285N_09222020130420_4706779 | Com Gas Storage | 120 | 285 | gt155kBtuh
2369383 | A.O. Smith Corporation | A. O. Smith | ATX-199-*-1** | ATX-199-*-1** |  |  | Gas Storage | Gas,Propane | Power Direct Vent | 119 | 69 | 61.3 | 24 | 4 | 3 |  | 199 | 0.96 | 1100 |  |  |  | 2017-07-18 | 2020-11-11 | United States, Canada | ES_92897_ATX-199-*-1**_11052020142716_8932749 | Com Gas Storage | 120 | 199 | gt155kBtuh
2369384 | Lochinvar, LLC | A. O. Smith | BTX 80 120 | BTX-80 1** |  |  | Gas Storage | Gas | Power Vent | 50 | 50.7 | 71 | 18 | 2 | 3 | 71.44 | 76 | 0.94 | 320 |  |  |  | 2017-02-28 | 2020-11-11 | United States, Canada | ES_1028919_BTX-80 1**_10292020143321_8803590 | Com Gas Storage | 50 | 76 | lte155kBtuh
2369385 | Ariston Thermo USA, LLC | Giant | UGC55S-199 | UGC55S-199 |  |  | Gas Storage | Gas,Propane | Power Direct Vent | 55 | 52 | 5.2 | 23 | 3 |  |  | 199 | 0.95 | 409 |  |  |  | 2020-06-23 | 2020-11-11 | United States, Canada | ES_29975_UGC55S-199_07292020153132_7104318 | Com Gas Storage | 55 | 199 | gt155kBtuh
2369386 | Ariston Thermo USA, LLC | Giant | UGC80S-199 | UGC80S-199 |  |  | Gas Storage | Gas,Propane | Power Direct Vent | 80 | 72 | 7.5 | 23 | 3 |  |  | 199 | 0.95 | 495 |  |  |  | 2020-06-23 | 2020-11-11 | United States, Canada | ES_29975_UGC80S-199_07292020153132_818122 | Com Gas Storage | 80 | 199 | gt155kBtuh
2369387 | Ariston Thermo USA, LLC | Giant | UGC120S-130 | UGC120S-130 |  |  | Gas Storage | Gas,Propane | Direct Vent | 119 | 74 | 9.3 | 27 | 2 |  |  | 130 | 0.96 | 697 |  |  |  | 2020-06-23 | 2020-11-11 | United States, Canada | ES_29975_UGC120S-130_07292020153130_2751059 | Com Gas Storage | 120 | 130 | lte155kBtuh
2369388 | Ariston Thermo USA, LLC | Giant | UGC55S-130 | UGC55S-130 |  |  | Gas Storage | Gas,Propane | Direct Vent | 55 | 52 | 5.2 | 23 | 2 |  |  | 130 | 0.94 | 596 |  |  |  | 2020-06-23 | 2020-11-11 | United States, Canada | ES_29975_UGC55S-130_07292020153126_1579242 | Com Gas Storage | 55 | 130 | lte155kBtuh
2369389 | Ariston Thermo USA, LLC | Giant | UGC55S-160 | UGC55S-160 |  |  | Gas Storage | Gas,Propane | Power Direct Vent | 55 | 52 | 5.2 | 23 | 3 |  |  | 160 | 0.95 | 596 |  |  |  | 2020-06-23 | 2020-11-11 | United States, Canada | ES_29975_UGC55S-160_07292020153127_1300199 | Com Gas Storage | 55 | 160 | gt155kBtuh
2369390 | Intellihot Inc | Intellihot | I250 | I250 |  |  | Gas Tankless | Gas,Propane | Direct Vent | 0 |  |  |  | 3 | 3 |  | 250 | 0.96 |  |  |  |  | 2013-01-01 | 2020-11-11 | United States, Canada | ES_1084851_I250_07092020124018_9800302 | Com Gas Instantaneous | 2 | 250 | gte200kBtuh
2369391 | Ariston Thermo USA, LLC | Giant | UGC80S-130 | UGC80S-130 |  |  | Gas Storage | Gas,Propane | Direct Vent | 80 | 72 | 7.5 | 23 | 2 |  |  | 130 | 0.95 | 498 |  |  |  | 2020-06-23 | 2020-11-11 | United States, Canada | ES_29975_UGC80S-130_07072020095725_1754406 | Com Gas Storage | 80 | 130 | lte155kBtuh
2369392 | Ariston Thermo USA, LLC | Giant | UGC120S-199 | UGC120S-199 |  |  | Gas Storage | Gas,Propane | Power Direct Vent | 119 | 74 | 9.3 | 27 | 3 |  |  | 199 | 0.96 | 719 |  |  |  | 2020-06-23 | 2020-11-11 | United States, Canada | ES_29975_UGC120S-199_07072020095724_8588456 | Com Gas Storage | 120 | 199 | gt155kBtuh
2369393 | Ariston Thermo USA, LLC | Giant | UGC120S-160 | UGC120S-160 |  |  | Gas Storage | Gas,Propane | Power Direct Vent | 119 | 74 | 9.3 | 27 | 3 |  |  | 160 | 0.96 | 621 |  |  |  | 2020-06-23 | 2020-11-11 | United States, Canada | ES_29975_UGC120S-160_07072020095724_1930927 | Com Gas Storage | 120 | 160 | gt155kBtuh
2369394 | Ariston Thermo USA, LLC | Giant | UGC80S-160 | UGC80S-160 |  |  | Gas Storage | Gas,Propane | Direct Vent | 80 | 72 | 7.5 | 23 | 3 |  |  | 160 | 0.96 | 472 |  |  |  | 2020-06-23 | 2020-11-11 | United States, Canada | ES_29975_UGC80S-160_07072020095721_4698726 | Com Gas Storage | 80 | 160 | gt155kBtuh
2369590 | Lochinvar, LLC | A. O. Smith | XP | XWH800(N,L)-(P) |  |  | Gas Tankless | Gas,Propane | Direct Vent | 4 |  |  |  | 4 |  |  | 800 | 0.96 |  |  |  |  | 2016-10-14 | 2020-11-16 | United States, Canada | ES_1028919_XWH800(N,L)-(P)_11132020114821_8122959 | Com Gas Instantaneous | 10 | 800 | gte200kBtuh
2369594 | Lochinvar, LLC | A. O. Smith | XP | XWH500(N,L)-(P) |  |  | Gas Tankless | Gas,Propane | Direct Vent | 3 |  |  |  | 4 |  |  | 500 | 0.96 |  |  |  |  | 2016-10-14 | 2020-11-16 | United States, Canada | ES_1028919_XWH500(N,L)-(P)_11132020114819_319697 | Com Gas Instantaneous | 10 | 500 | gte200kBtuh
2369595 | Lochinvar, LLC | A. O. Smith | XP | XWH285(N,L)-(P) |  |  | Gas Tankless | Gas,Propane | Direct Vent | 2 |  |  |  | 4 |  |  | 285 | 0.96 |  |  |  |  | 2016-10-14 | 2020-11-16 | United States, Canada | ES_1028919_XWH285(N,L)-(P)_11132020114818_9646414 | Com Gas Instantaneous | 2 | 285 | gte200kBtuh
2369596 | Lochinvar, LLC | A. O. Smith | XP | XWH150(N,L)-(P) |  |  | Gas Tankless | Gas,Propane | Direct Vent | 1 |  |  |  | 3 |  |  | 150 | 0.96 |  |  |  |  | 2016-10-14 | 2020-11-16 | United States, Canada | ES_1028919_XWH150(N,L)-(P)_11132020114816_1608990 | Com Gas Instantaneous | 2 | 150 | lt200kBtuh
2369638 | Lochinvar, LLC | A. O. Smith | XP | XWH700(N,L)-(P) |  |  | Gas Tankless | Gas,Propane | Direct Vent | 4 |  |  |  | 4 |  |  | 700 | 0.96 |  |  |  |  | 2016-10-14 | 2020-11-17 | United States, Canada | ES_1028919_XWH700(N,L)-(P)_11132020114820_87928 | Com Gas Instantaneous | 10 | 700 | gte200kBtuh
2369639 | Lochinvar, LLC | A. O. Smith | XP | XWH600(N,L)-(P) |  |  | Gas Tankless | Gas,Propane | Direct Vent | 3 |  |  |  | 4 |  |  | 600 | 0.96 |  |  |  |  | 2016-10-14 | 2020-11-17 | United States, Canada | ES_1028919_XWH600(N,L)-(P)_11132020114820_9920548 | Com Gas Instantaneous | 10 | 600 | gte200kBtuh
2369710 | Lochinvar, LLC | A. O. Smith | XP | XWH400(N,L)-(P) |  |  | Gas Tankless | Gas,Propane | Direct Vent | 3 |  |  |  | 4 |  |  | 399.9 | 0.96 |  |  |  |  | 2016-10-14 | 2020-11-19 | United States, Canada | ES_1028919_XWH400(N,L)-(P)_11132020114819_9424212 | Com Gas Instantaneous | 10 | 399.9 | gte200kBtuh
2369711 | Lochinvar, LLC | A. O. Smith | XP | XWH200(N,L)-(P) |  |  | Gas Tankless | Gas,Propane | Direct Vent | 1 |  |  |  | 3 |  |  | 199.9 | 0.96 |  |  |  |  | 2016-10-14 | 2020-11-19 | United States, Canada | ES_1028919_XWH200(N,L)-(P)_11132020114817_1491514 | Com Gas Instantaneous | 2 | 199.9 | lt200kBtuh
2370805 | Lochinvar, LLC | State | BTX-80 1** | SHE-50-76 *E 1** |  |  | Gas Storage | Gas | Power Vent | 50 | 50.7 | 71 | 18 | 2 | 3 | 71.44 | 76 | 0.94 | 320 |  |  |  | 2017-02-28 | 2020-12-11 | United States, Canada | ES_1028919_SHE-50-76 *E 1**_11092020142317_4581845 | Com Gas Storage | 50 | 76 | lte155kBtuh
2370807 | A.O. Smith Corporation | American | ATX-199-*-1** | MTX-199-*-1** |  |  | Gas Storage | Gas,Propane | Power Direct Vent | 119 | 69 | 61.3 | 24 | 4 | 3 |  | 199 | 0.96 | 1100 |  |  |  | 2017-07-18 | 2020-12-11 | United States | ES_92897_MTX-199-*-1**_11072020014133_7926939 | Com Gas Storage | 120 | 199 | gt155kBtuh
2370808 | A.O. Smith Corporation | State | ATX-199-*-1** | STX-199-*-1** |  |  | Gas Storage | Gas,Propane | Power Direct Vent | 119 | 69 | 61.3 | 24 | 4 | 3 |  | 199 | 0.96 | 1100 |  |  |  | 2017-07-18 | 2020-12-11 | United States | ES_92897_STX-199-*-1**_11072020014105_7192225 | Com Gas Storage | 120 | 199 | gt155kBtuh
2371945 | A.O. Smith Corporation | State | SHE-75-100 *E 3** | SHE-75-100 *E 3** |  |  | Gas Storage | Gas,Propane | Power Vent | 75 | 51.9 | 7.9 | 22.5 | 2 | 3 |  | 100 | 0.96 | 430 |  |  |  | 2013-12-15 | 2021-01-13 | United States | ES_92897_SHE-75-100 *E 3**_11062020145418_3683715 | Com Gas Storage | 75 | 100 | lte155kBtuh
2371947 | A.O. Smith Corporation | State | SHE-50-100 *E 3** | SHE-50-100 *E 3** |  |  | Gas Storage | Gas,Propane | Power Vent | 50 | 55.7 | 8 | 18 | 2 | 3 |  | 100 | 0.96 | 430 |  |  |  | 2007-11-01 | 2021-01-13 | United States | ES_92897_SHE-50-100 *E 3**_11062020145417_1900907 | Com Gas Storage | 50 | 100 | lte155kBtuh
2371949 | A.O. Smith Corporation | A. O. Smith | BTXL 100 3** | BTXL-100 3** |  |  | Gas Storage | Gas,Propane | Power Vent | 75 | 51.9 | 7.9 | 22.5 | 2 | 3 |  | 100 | 0.96 | 430 |  |  |  | 2013-12-15 | 2021-01-13 | United States, Canada | ES_92897_BTXL-100 3**_11062020110718_8143003 | Com Gas Storage | 75 | 100 | lte155kBtuh
2371950 | A.O. Smith Corporation | A. O. Smith | BTX 100 3** | BTX-100 3** |  |  | Gas Storage | Gas,Propane | Power Vent | 50 | 55.7 | 8 | 18 | 2 | 3 |  | 100 | 0.96 | 430 |  |  |  | 2007-11-01 | 2021-01-13 | United States, Canada | ES_92897_BTX-100 3**_11062020110718_17686 | Com Gas Storage | 50 | 100 | lte155kBtuh
2374682 | Lochinvar, LLC | Lochinvar | ARMOR | AWH0400N SERIES 1** |  |  | Gas Tankless | Gas | Direct Vent | 4 |  |  |  | 4 |  | 395.01 | 399 | 0.99 |  |  |  |  | 2021-01-01 | 2021-03-10 | United States, Canada | ES_1028919_AWH0400N SERIES 1**_08262020165118_1371243 | Com Gas Instantaneous | 10 | 399 | gte200kBtuh
2374696 | Lochinvar, LLC | Lochinvar | ARMOR | AWH1000N SERIES 1** |  |  | Gas Tankless | Gas | Direct Vent | 9 |  |  |  | 6 |  | 979.02 | 999 | 0.98 |  |  |  |  | 2021-01-01 | 2021-03-10 | United States, Canada | ES_1028919_AWH1000N SERIES 1**_08262020165517_745409 | Com Gas Instantaneous | 10 | 999 | gte200kBtuh
2374697 | Lochinvar, LLC | Lochinvar | ARMOR | AWH0650N SERIES 1** |  |  | Gas Tankless | Gas | Direct Vent | 6 |  |  |  | 4 | 6 | 637 | 650 | 0.98 |  |  |  |  | 2021-01-01 | 2021-03-10 | United States, Canada | ES_1028919_AWH0650N SERIES 1**_08262020165118_9879046 | Com Gas Instantaneous | 10 | 650 | gte200kBtuh
2374698 | Lochinvar, LLC | Lochinvar | ARMOR | AWH0500N SERIES 1** |  |  | Gas Tankless | Gas | Direct Vent | 5 |  |  |  | 4 |  | 495 | 500 | 0.99 |  |  |  |  | 2021-01-01 | 2021-03-10 | United States, Canada | ES_1028919_AWH0500N SERIES 1**_08262020165118_3051837 | Com Gas Instantaneous | 10 | 500 | gte200kBtuh
2374725 | Lochinvar, LLC | Lochinvar | ARMOR | AWH0800N SERIES 1** |  |  | Gas Tankless | Gas | Direct Vent | 7 |  |  |  | 4 | 6 | 784 | 800 | 0.98 |  |  |  |  | 2021-01-01 | 2021-03-11 | United States, Canada | ES_1028919_AWH0800N SERIES 1**_08262020165517_9926368 | Com Gas Instantaneous | 10 | 800 | gte200kBtuh
2379540 | Navien, Inc. | Navien | NVW-400C | NVW-400C |  |  | Gas Tankless | Gas,Propane | Power Vent | 0 |  |  |  | 3 | 4 |  | 399 | 0.98 |  |  |  |  | 2021-04-01 | 2021-06-14 | United States, Canada | ES_1074959_NVW-400C_06052021013309_5513327 | Com Gas Instantaneous | 2 | 399 | gte200kBtuh
2379541 | Navien, Inc. | Navien | NVW-300C | NVW-300C |  |  | Gas Tankless | Gas,Propane | Power Vent | 0 |  |  |  | 3 | 4 |  | 301 | 0.98 |  |  |  |  | 2021-04-01 | 2021-06-14 | United States, Canada | ES_1074959_NVW-300C_06052021013309_2547578 | Com Gas Instantaneous | 2 | 301 | gte200kBtuh
2381674 | Intellihot Inc | Intellihot | IQ Floor Model | iQ2001 |  |  | Gas Tankless | Gas,Propane | Direct Vent | 8 |  |  |  | 8 | 8 |  | 2000 | 0.96 | 919 |  |  |  | 2020-07-15 | 2021-07-06 | United States, Canada | ES_1084851_iQ2001_07062021163351_2611407 | Com Gas Instantaneous | 10 | 2000 | gte200kBtuh
2383541 | Rheem Sales Company, Inc. | Raypak | HPHD-135HNU-483 | HPHD-135HNU-483 |  |  | Electric Heat Pump | Electric |  | 2 | [5 empty] | 125.9028 |  |  |  | 12.3 | 3 |  | 2021-09-17 | 2021-08-19 | United States, Canada | ES_1128591_HPHD-135HNU-483_081720210855499_6176654 | Heat Pump | 2 | 41.9676 | #N/A
2383542 | Rheem Sales Company, Inc. | Rheem | HPHD-135VNU-483 | HPHD-135VNU-483 |  |  | Electric Heat Pump | Electric |  | 2 | [5 empty] | 125.9028 |  |  |  | 12.3 | 3 |  | 2021-09-17 | 2021-08-19 | United States, Canada | none | Heat Pump | 2 | 41.9676 | #N/A
2367067 | A.O. Smith Corporation | State | BTH 120* 3** | SUF 60 120*E* 3** |  |  | Gas Storage | Gas,Propane | Power Direct Vent | 60 | 41.8 | 11 | 24 | 3 | 4 |  | 120 | 0.95 | 800 |  |  |  | 2014-05-09 | 2020-10-08 | United States | ES_92897_SUF 60 120*E* 3**_09022020132121_5719413 | Com Gas Storage | 60 | 120 | lte155kBtuh
2367068 | A.O. Smith Corporation | American | BTH 120* 3** | HCG3-60T120-3* 3** |  |  | Gas Storage | Gas,Propane | Power Direct Vent | 60 | 41.8 | 11 | 24 | 3 | 4 |  | 120 | 0.95 | 800 |  |  |  | 2014-05-09 | 2020-10-08 | United States | ES_92897_HCG3-60T120-3* 3**_09022020132120_6872630 | Com Gas Storage | 60 | 120 | lte155kBtuh
2367069 | A.O. Smith Corporation | A. O. Smith | BTH 400* 3** | BTH 400* 3** |  |  | Gas Storage | Gas,Propane | Power Direct Vent | 119 | 62.9 | 12 | 30 | 4 | 6 |  | 399.9 | 0.95 | 1200 |  |  |  | 2014-05-09 | 2020-10-08 | United States, Canada | ES_92897_BTH 400* 3**_08282020155520_8618276 | Com Gas Storage | 120 | 399.9 | gt155kBtuh
2367070 | A.O. Smith Corporation | A. O. Smith | BTH 300* 3** | BTH 300* 3** |  |  | Gas Storage | Gas,Propane | Power Direct Vent | 119 | 62.9 | 12 | 30 | 4 | 6 |  | 300 | 0.96 | 1200 |  |  |  | 2014-05-09 | 2020-10-08 | United States, Canada | ES_92897_BTH 300* 3**_08282020155520_5915100 | Com Gas Storage | 120 | 300 | gt155kBtuh
2367071 | A.O. Smith Corporation | A. O. Smith | BTH 250* 3** | BTH 250* 3** |  |  | Gas Storage | Gas,Propane | Power Direct Vent | 100 | 62.9 | 11 | 24 | 3 | 4 |  | 250 | 0.96 | 1000 |  |  |  | 2014-05-09 | 2020-10-08 | United States, Canada | ES_92897_BTH 250* 3**_08282020155520_7266659 | Com Gas Storage | 100 | 250 | gt155kBtuh
2367072 | A.O. Smith Corporation | A. O. Smith | BTH 199* 3** | BTH 199* 3** |  |  | Gas Storage | Gas,Propane | Power Direct Vent | 100 | 62.9 | 11 | 24 | 3 | 4 |  | 199.9 | 0.97 | 1000 |  |  |  | 2014-05-09 | 2020-10-08 | United States, Canada | ES_92897_BTH 199* 3**_08282020155520_8285827 | Com Gas Storage | 100 | 199.9 | gt155kBtuh
2367073 | A.O. Smith Corporation | A. O. Smith | BTH 150* 3** | BTH 150* 3** |  |  | Gas Storage | Gas,Propane | Power Direct Vent | 100 | 62.9 | 11 | 24 | 3 | 4 |  | 150 | 0.96 | 1000 |  |  |  | 2014-05-09 | 2020-10-08 | United States, Canada | ES_92897_BTH 150* 3**_08282020155520_4555250 | Com Gas Storage | 100 | 150 | lte155kBtuh
2367074 | A.O. Smith Corporation | A. O. Smith | BTH 120* 3** | BTH 120* 3** |  |  | Gas Storage | Gas,Propane | Power Direct Vent | 60 | 41.8 | 11 | 24 | 3 | 4 |  | 120 | 0.95 | 800 |  |  |  | 2014-05-09 | 2020-10-08 | United States, Canada | ES_92897_BTH 120* 3**_08282020155519_8044832 | Com Gas Storage | 60 | 120 | lte155kBtuh
2367075 | A.O. Smith Corporation | State | SUF119251*E* 3** | SUF119251*E* 3** |  |  | Gas Storage | Gas,Propane | Power Direct Vent | 119 | 62.9 | 11 | 24 | 3 | 4 |  | 250 | 0.96 | 1200 |  |  |  | 2020-09-01 | 2020-10-08 | United States | ES_92897_SUF119251*E* 3**_09042020133817_4618807 | Com Gas Storage | 120 | 250 | gt155kBtuh
2367076 | A.O. Smith Corporation | State | BTH 500* 3** | SUF 119 500*E* 3** |  |  | Gas Storage-type Instantaneous | Gas,Propane | Power Direct Vent | 119 |  |  |  | 4 | 6 |  | 499.9 | 0.96 | 1200 |  |  |  | 2014-05-09 | 2020-10-08 | United States | ES_92897_SUF 119 500*E* 3**_09022020134121_9958730 | Com Gas Storage-type Instantaneous | 120 | 499.9 | gte200kBtuh
2367077 | A.O. Smith Corporation | State | BTH 400* 3** | SUF 119 400*E* 3** |  |  | Gas Storage | Gas,Propane | Power Direct Vent | 119 | 62.9 | 12 | 30 | 4 | 6 |  | 399.9 | 0.95 | 1200 |  |  |  | 2014-05-09 | 2020-10-08 | United States | ES_92897_SUF 119 400*E* 3**_09022020132125_2810337 | Com Gas Storage | 120 | 399.9 | gt155kBtuh
2367078 | A.O. Smith Corporation | State | BTH 300* 3** | SUF 119 300*E* 3** |  |  | Gas Storage | Gas,Propane | Power Direct Vent | 119 | 62.9 | 12 | 30 | 4 | 6 |  | 300 | 0.96 | 1200 |  |  |  | 2014-05-09 | 2020-10-08 | United States | ES_92897_SUF 119 300*E* 3**_09022020132125_4449604 | Com Gas Storage | 120 | 300 | gt155kBtuh
2367079 | A.O. Smith Corporation | State | BTH 250* 3** | SUF 100 250*E* 3** |  |  | Gas Storage | Gas,Propane | Power Direct Vent | 100 | 62.9 | 11 | 24 | 3 | 4 |  | 250 | 0.96 | 1000 |  |  |  | 2014-05-09 | 2020-10-08 | United States | ES_92897_SUF 100 250*E* 3**_09022020132124_3290858 | Com Gas Storage | 100 | 250 | gt155kBtuh
2367080 | A.O. Smith Corporation | American | BTH 250* 3** | AHCG3-100T250-3* 3** |  |  | Gas Storage | Gas,Propane | Power Direct Vent | 100 | 62.9 | 11 | 24 | 3 | 4 |  | 250 | 0.96 | 1000 |  |  |  | 2014-05-09 | 2020-10-08 | United States | ES_92897_AHCG3-100T250-3* 3**_09022020132124_2103816 | Com Gas Storage | 100 | 250 | gt155kBtuh
2367081 | A.O. Smith Corporation | RELIANCE WATER HEATERS | BTH 199* 3** | RUF 100 199*E* 3** |  |  | Gas Storage | Gas,Propane | Power Direct Vent | 100 | 62.9 | 11 | 24 | 3 | 4 |  | 199 | 0.97 | 1000 |  |  |  | 2014-05-09 | 2020-10-08 | United States | ES_92897_RUF 100 199*E* 3**_09022020132124_6653451 | Com Gas Storage | 100 | 199 | gt155kBtuh
2367082 | A.O. Smith Corporation | American | BTH 199* 3** | AHCG3-100T199-3* 3** |  |  | Gas Storage | Gas,Propane | Power Direct Vent | 100 | 62.9 | 11 | 24 | 3 | 4 |  | 199 | 0.97 | 1000 |  |  |  | 2014-05-09 | 2020-10-08 | United States | ES_92897_AHCG3-100T199-3* 3**_09022020132124_578050 | Com Gas Storage | 100 | 199 | gt155kBtuh
2367083 | A.O. Smith Corporation | State | BTH 150* 3** | SUF 100 150*E* 3** |  |  | Gas Storage | Gas,Propane | Power Direct Vent | 100 | 62.9 | 11 | 24 | 3 | 4 |  | 150 | 0.96 | 1000 |  |  |  | 2014-05-09 | 2020-10-08 | United States | ES_92897_SUF 100 150*E* 3**_09022020132123_4537603 | Com Gas Storage | 100 | 150 | lte155kBtuh
2367084 | A.O. Smith Corporation | American | BTH 150* 3** | HCG3-100T150-3* 3** |  |  | Gas Storage | Gas,Propane | Power Direct Vent | 100 | 62.9 | 11 | 24 | 3 | 4 |  | 150 | 0.96 | 1000 |  |  |  | 2014-05-09 | 2020-10-08 | United States | ES_92897_HCG3-100T150-3* 3**_09022020132122_1677627 | Com Gas Storage | 100 | 150 | lte155kBtuh
2367085 | A.O. Smith Corporation | American | BTH 120* 3** | AHCG3-60T120-3* 3** |  |  | Gas Storage | Gas,Propane | Power Direct Vent | 60 | 41.8 | 11 | 24 | 3 | 4 |  | 120 | 0.95 | 800 |  |  |  | 2014-05-09 | 2020-10-08 | United States | ES_92897_AHCG3-60T120-3* 3**_09022020132121_3837805 | Com Gas Storage | 60 | 120 | lte155kBtuh
2367751 | A.O. Smith Corporation | American | Polaris | PG10 50 199 3*V 2** |  |  | Gas Storage | Gas,Propane | Power Direct Vent | 50 | 63.7 | 6.6 | 22 | 3 |  |  | 199 | 0.96 | 800 |  |  |  | 2017-02-15 | 2020-10-20 | United States | ES_92897_PG10 50 199 3*V 2**_10202020013925_6434271 | Com Gas Storage | 50 | 199 | gt155kBtuh
2367752 | A.O. Smith Corporation | American | Polaris | PG10 50 150 2*V 2** |  |  | Gas Storage | Gas,Propane | Power Direct Vent | 50 | 63.7 | 6.6 | 22 | 2 |  |  | 150 | 0.95 | 750 |  |  |  | 2017-02-15 | 2020-10-20 | United States | ES_92897_PG10 50 150 2*V 2**_10202020013924_5719411 | Com Gas Storage | 50 | 150 | lte155kBtuh
2367753 | A.O. Smith Corporation | State | Polaris | GHX 50 150 * 2** |  |  | Gas Storage | Gas,Propane | Power Direct Vent | 50 | 63.7 | 6.6 | 22 | 2 |  |  | 150 | 0.95 | 750 |  |  |  | 2017-02-15 | 2020-10-20 | United States | ES_92897_GHX 50 150 * 2**_10202020013933_1674318 | Com Gas Storage | 50 | 150 | lte155kBtuh
2367755 | A.O. Smith Corporation | State | Polaris | SPC 50 150 *E 2** |  |  | Gas Storage | Gas,Propane | Power Direct Vent | 50 | 63.7 | 6.6 | 22 | 2 |  |  | 150 | 0.95 | 750 |  |  |  | 2017-02-15 | 2020-10-20 | United States | ES_92897_SPC 50 150 *E 2**_10202020013933_9732279 | Com Gas Storage | 50 | 150 | lte155kBtuh
2367756 | A.O. Smith Corporation | Lochinvar | Polaris | SCN150-050 2** |  |  | Gas Storage | Gas | Power Direct Vent | 50 | 63.7 | 6.6 | 22 | 2 |  | 142.5 | 150 | 0.95 | 750 |  |  |  | 2017-02-15 | 2020-10-20 | United States | ES_92897_SCN150-050 2**_10202020013932_8680871 | Com Gas Storage | 50 | 150 | lte155kBtuh
2367758 | A.O. Smith Corporation | Lochinvar | Polaris | SWN150-050 2** |  |  | Gas Storage | Gas | Power Direct Vent | 50 | 63.7 | 6.6 | 22 | 2 |  | 142.5 | 150 | 0.95 | 750 |  |  |  | 2017-02-15 | 2020-10-20 | United States | ES_92897_SWN150-050 2**_10202020013932_5328816 | Com Gas Storage | 50 | 150 | lte155kBtuh
2367759 | A.O. Smith Corporation | A. O. Smith | Polaris | BTS 150 2** |  |  | Gas Storage | Gas,Propane | Power Direct Vent | 50 | 63.7 | 6.6 | 22 | 2 |  |  | 150 | 0.95 | 750 |  |  |  | 2017-02-15 | 2020-10-20 | United States | ES_92897_BTS 150 2**_10202020013932_1153558 | Com Gas Storage | 50 | 150 | lte155kBtuh
2367760 | A.O. Smith Corporation | A. O. Smith | Polaris | GTP 150 2** |  |  | Gas Storage | Gas,Propane | Power Direct Vent | 50 | 63.7 | 6.6 | 22 | 2 |  |  | 150 | 0.95 | 750 |  |  |  | 2017-02-15 | 2020-10-20 | United States | ES_92897_GTP 150 2**_10202020013932_9021076 | Com Gas Storage | 50 | 150 | lte155kBtuh
2367761 | A.O. Smith Corporation | American | Polaris | PC 50 150 * 200 |  |  | Gas Storage | Gas,Propane | Power Direct Vent | 50 | 63.7 | 6.6 | 22 | 2 |  |  | 150 | 0.95 | 750 |  |  |  | 2017-02-15 | 2020-10-20 | United States | ES_92897_PC 50 150 * 200_10202020013932_7044572 | Com Gas Storage | 50 | 150 | lte155kBtuh
2367762 | A.O. Smith Corporation | American | Polaris | PR 50 150 * 200 |  |  | Gas Storage | Gas,Propane | Power Direct Vent | 50 | 63.7 | 6.6 | 22 | 2 |  |  | 150 | 0.95 | 750 |  |  |  | 2017-02-15 | 2020-10-20 | United States | ES_92897_PR 50 150 * 200_10202020013932_1756203 | Com Gas Storage | 50 | 150 | lte155kBtuh
2367763 | A.O. Smith Corporation | American | Polaris | PGC3 50 150 2*V 200 |  |  | Gas Storage | Gas,Propane | Power Direct Vent | 50 | 63.7 | 6.6 | 22 | 2 |  |  | 150 | 0.95 | 750 |  |  |  | 2017-02-15 | 2020-10-20 | United States | ES_92897_PGC3 50 150 2*V 200_10202020013932_6652187 | Com Gas Storage | 50 | 150 | lte155kBtuh
2367764 | A.O. Smith Corporation | State | Polaris | GHX 50 199 * 2** |  |  | Gas Storage | Gas,Propane | Power Direct Vent | 50 | 63.7 | 6.6 | 22 | 3 |  |  | 199 | 0.96 | 800 |  |  |  | 2017-02-15 | 2020-10-20 | United States | ES_92897_GHX 50 199 * 2**_10202020013932_2417080 | Com Gas Storage | 50 | 199 | gt155kBtuh
2367765 | A.O. Smith Corporation | State | Polaris | SPC 50 199 *E 2** |  |  | Gas Storage | Gas,Propane | Power Direct Vent | 50 | 63.7 | 6.6 | 22 | 3 |  |  | 199 | 0.96 | 800 |  |  |  | 2017-02-15 | 2020-10-20 | United States | ES_92897_SPC 50 199 *E 2**_10202020013932_4518147 | Com Gas Storage | 50 | 199 | gt155kBtuh
2367768 | A.O. Smith Corporation | Lochinvar | Polaris | SCN199-050 2** |  |  | Gas Storage | Gas | Power Direct Vent | 50 | 63.7 | 6.6 | 22 | 3 |  | 191.04 | 199 | 0.96 | 800 |  |  |  | 2017-02-15 | 2020-10-20 | United States | ES_92897_SCN199-050 2**_10202020013931_9037507 | Com Gas Storage | 50 | 199 | gt155kBtuh
2367769 | A.O. Smith Corporation | A. O. Smith | Polaris | GTP 199 2** |  |  | Gas Storage | Gas,Propane | Power Direct Vent | 50 | 63.7 | 6.6 | 22 | 3 |  |  | 199 | 0.96 | 800 |  |  |  | 2017-02-15 | 2020-10-20 | United States | ES_92897_GTP 199 2**_10202020013931_8069088 | Com Gas Storage | 50 | 199 | gt155kBtuh
2367770 | A.O. Smith Corporation | Lochinvar | Polaris | SWN199-050 2** |  |  | Gas Storage | Gas | Power Direct Vent | 50 | 63.7 | 6.6 | 22 | 3 |  | 191.04 | 199 | 0.96 | 800 |  |  |  | 2017-02-15 | 2020-10-20 | United States | ES_92897_SWN199-050 2**_10202020013931_5893002 | Com Gas Storage | 50 | 199 | gt155kBtuh
2367771 | A.O. Smith Corporation | American | Polaris | PR 50 199 * 2** |  |  | Gas Storage | Gas,Propane | Power Direct Vent | 50 | 63.7 | 6.6 | 22 | 3 |  |  | 199 | 0.96 | 800 |  |  |  | 2017-02-15 | 2020-10-20 | United States | ES_92897_PR 50 199 * 2**_10202020013931_8035520 | Com Gas Storage | 50 | 199 | gt155kBtuh
2367772 | A.O. Smith Corporation | A. O. Smith | Polaris | BTS 199 2** |  |  | Gas Storage | Gas,Propane | Power Direct Vent | 50 | 63.7 | 6.6 | 22 | 3 |  |  | 199 | 0.96 | 800 |  |  |  | 2017-02-15 | 2020-10-20 | United States | ES_92897_BTS 199 2**_10202020013931_7657613 | Com Gas Storage | 50 | 199 | gt155kBtuh
2367773 | A.O. Smith Corporation | American | Polaris | PGC3 50 199 3*V 2** |  |  | Gas Storage | Gas,Propane | Power Direct Vent | 50 | 63.7 | 6.6 | 22 | 3 |  |  | 199 | 0.96 | 800 |  |  |  | 2017-02-15 | 2020-10-20 | United States | ES_92897_PGC3 50 199 3*V 2**_10202020013930_2156462 | Com Gas Storage | 50 | 199 | gt155kBtuh
2367774 | A.O. Smith Corporation | State | Polaris | GHX 50 175 * 2** |  |  | Gas Storage | Gas,Propane | Power Direct Vent | 50 | 63.7 | 6.6 | 22 | 3 |  |  | 175 | 0.96 | 800 |  |  |  | 2017-02-15 | 2020-10-20 | United States | ES_92897_GHX 50 175 * 2**_10202020013930_3609229 | Com Gas Storage | 50 | 175 | gt155kBtuh
2367775 | A.O. Smith Corporation | American | Polaris | PC 50 199 * 2** |  |  | Gas Storage | Gas,Propane | Power Direct Vent | 50 | 63.7 | 6.6 | 22 | 3 |  |  | 199 | 0.96 | 800 |  |  |  | 2017-02-15 | 2020-10-20 | United States | ES_92897_PC 50 199 * 2**_10202020013930_7250187 | Com Gas Storage | 50 | 199 | gt155kBtuh
2367776 | A.O. Smith Corporation | State | Polaris | SPC 50 175 *E 2** |  |  | Gas Storage | Gas,Propane | Power Direct Vent | 50 | 63.7 | 6.6 | 22 | 3 |  |  | 175 | 0.96 | 800 |  |  |  | 2017-02-15 | 2020-10-20 | United States | ES_92897_SPC 50 175 *E 2**_10202020013930_2266456 | Com Gas Storage | 50 | 175 | gt155kBtuh
2367777 | A.O. Smith Corporation | Lochinvar | Polaris | SCN175-050 2** |  |  | Gas Storage | Gas | Power Direct Vent | 50 | 63.7 | 6.6 | 22 | 3 |  | 168 | 175 | 0.96 | 800 |  |  |  | 2017-02-15 | 2020-10-20 | United States | ES_92897_SCN175-050 2**_10202020013930_1514736 | Com Gas Storage | 50 | 175 | gt155kBtuh
2367780 | A.O. Smith Corporation | Lochinvar | Polaris | SWN175-050 2** |  |  | Gas Storage | Gas | Power Direct Vent | 50 | 63.7 | 6.6 | 22 | 3 |  | 168 | 175 | 0.96 | 800 |  |  |  | 2017-02-15 | 2020-10-20 | United States | ES_92897_SWN175-050 2**_10202020013929_3607033 | Com Gas Storage | 50 | 175 | gt155kBtuh
2367781 | A.O. Smith Corporation | A. O. Smith | Polaris | GTP 175 2** |  |  | Gas Storage | Gas,Propane | Power Direct Vent | 50 | 63.7 | 6.6 | 22 | 3 |  |  | 175 | 0.96 | 800 |  |  |  | 2017-02-15 | 2020-10-20 | United States | ES_92897_GTP 175 2**_10202020013929_397331 | Com Gas Storage | 50 | 175 | gt155kBtuh
2367782 | A.O. Smith Corporation | A. O. Smith | Polaris | BTS 175 2** |  |  | Gas Storage | Gas,Propane | Power Direct Vent | 50 | 63.7 | 6.6 | 22 | 3 |  |  | 175 | 0.96 | 800 |  |  |  | 2017-02-15 | 2020-10-20 | United States | ES_92897_BTS 175 2**_10202020013929_2549407 | Com Gas Storage | 50 | 175 | gt155kBtuh
2367783 | A.O. Smith Corporation | American | Polaris | PR 50 175 * 2** |  |  | Gas Storage | Gas,Propane | Power Direct Vent | 50 | 63.7 | 6.6 | 22 | 3 |  |  | 175 | 0.96 | 800 |  |  |  | 2017-02-15 | 2020-10-20 | United States | ES_92897_PR 50 175 * 2**_10202020013929_8640062 | Com Gas Storage | 50 | 175 | gt155kBtuh
2367784 | A.O. Smith Corporation | American | Polaris | PGC3 50 175 3*V 2** |  |  | Gas Storage | Gas,Propane | Power Direct Vent | 50 | 63.7 | 6.6 | 22 | 3 |  |  | 175 | 0.96 | 800 |  |  |  | 2017-02-15 | 2020-10-20 | United States | ES_92897_PGC3 50 175 3*V 2**_10202020013929_8356653 | Com Gas Storage | 50 | 175 | gt155kBtuh
2367785 | A.O. Smith Corporation | American | Polaris | PC 50 175 * 2** |  |  | Gas Storage | Gas,Propane | Power Direct Vent | 50 | 63.7 | 6.6 | 22 | 3 |  |  | 175 | 0.96 | 800 |  |  |  | 2017-02-15 | 2020-10-20 | United States | ES_92897_PC 50 175 * 2**_10202020013929_1227957 | Com Gas Storage | 50 | 175 | gt155kBtuh
2367786 | A.O. Smith Corporation | State | Polaris | GHX 50 130 * 2** |  |  | Gas Storage | Gas,Propane | Power Direct Vent | 50 | 62.3 | 6.6 | 22 | 2 |  |  | 130 | 0.95 | 750 |  |  |  | 2017-02-15 | 2020-10-20 | United States | ES_92897_GHX 50 130 * 2**_10202020013929_3234414 | Com Gas Storage | 50 | 130 | lte155kBtuh
2367787 | A.O. Smith Corporation | State | Polaris | SPC 50 130 *E 2** |  |  | Gas Storage | Gas,Propane | Power Direct Vent | 50 | 62.3 | 6.6 | 22 | 2 |  |  | 130 | 0.95 | 750 |  |  |  | 2017-02-15 | 2020-10-20 | United States | ES_92897_SPC 50 130 *E 2**_10202020013928_3531200 | Com Gas Storage | 50 | 130 | lte155kBtuh
2367789 | A.O. Smith Corporation | Lochinvar | Polaris | SCN130-050 2** |  |  | Gas Storage | Gas | Power Direct Vent | 50 | 62.3 | 6.6 | 22 | 2 |  | 123.5 | 130 | 0.95 | 750 |  |  |  | 2017-02-15 | 2020-10-20 | United States | ES_92897_SCN130-050 2**_10202020013928_7135401 | Com Gas Storage | 50 | 130 | lte155kBtuh
2367791 | A.O. Smith Corporation | Lochinvar | Polaris | SWN130-050 2** |  |  | Gas Storage | Gas | Power Direct Vent | 50 | 62.3 | 6.6 | 22 | 2 |  | 123.5 | 130 | 0.95 | 750 |  |  |  | 2017-02-15 | 2020-10-20 | United States | ES_92897_SWN130-050 2**_10202020013928_1485727 | Com Gas Storage | 50 | 130 | lte155kBtuh
2367792 | A.O. Smith Corporation | A. O. Smith | Polaris | GTP 130 2** |  |  | Gas Storage | Gas,Propane | Power Direct Vent | 50 | 62.3 | 6.6 | 22 | 2 |  |  | 130 | 0.95 | 750 |  |  |  | 2017-02-15 | 2020-10-20 | United States | ES_92897_GTP 130 2**_10202020013928_5073794 | Com Gas Storage | 50 | 130 | lte155kBtuh
2367793 | A.O. Smith Corporation | A. O. Smith | Polaris | BTS 130 2** |  |  | Gas Storage | Gas,Propane | Power Direct Vent | 50 | 62.3 | 6.6 | 22 | 2 |  |  | 130 | 0.95 | 750 |  |  |  | 2017-02-15 | 2020-10-20 | United States | ES_92897_BTS 130 2**_10202020013928_7364183 | Com Gas Storage | 50 | 130 | lte155kBtuh
2367794 | A.O. Smith Corporation | American | Polaris | PR 50 130 * 2** |  |  | Gas Storage | Gas,Propane | Power Direct Vent | 50 | 62.3 | 6.6 | 22 | 2 |  |  | 130 | 0.95 | 750 |  |  |  | 2017-02-15 | 2020-10-20 | United States | ES_92897_PR 50 130 * 2**_10202020013928_7166399 | Com Gas Storage | 50 | 130 | lte155kBtuh
2367795 | A.O. Smith Corporation | American | Polaris | PGC3 50 130 2*V 2** |  |  | Gas Storage | Gas,Propane | Power Direct Vent | 50 | 62.3 | 6.6 | 22 | 2 |  |  | 130 | 0.95 | 750 |  |  |  | 2017-02-15 | 2020-10-20 | United States | ES_92897_PGC3 50 130 2*V 2**_10202020013927_4176241 | Com Gas Storage | 50 | 130 | lte155kBtuh
2367796 | A.O. Smith Corporation | American | Polaris | PC 50 130 * 2** |  |  | Gas Storage | Gas,Propane | Power Direct Vent | 50 | 62.3 | 6.6 | 22 | 2 |  |  | 130 | 0.95 | 750 |  |  |  | 2017-02-15 | 2020-10-20 | United States | ES_92897_PC 50 130 * 2**_10202020013927_1683291 | Com Gas Storage | 50 | 130 | lte155kBtuh
2367797 | A.O. Smith Corporation | State | Polaris | GHX 34 130 * 2** |  |  | Gas Storage | Gas,Propane | Power Direct Vent | 34 | 48.5 | 6.6 | 22 | 2 |  |  | 130 | 0.96 | 650 |  |  |  | 2017-02-15 | 2020-10-20 | United States | ES_92897_GHX 34 130 * 2**_10202020013927_8186321 | Com Gas Storage | 40 | 130 | lte155kBtuh
2367798 | A.O. Smith Corporation | State | Polaris | SPC 34 130 *E 2** |  |  | Gas Storage | Gas,Propane | Power Direct Vent | 34 | 48.5 | 6.6 | 22 | 2 |  |  | 130 | 0.96 | 650 |  |  |  | 2017-02-15 | 2020-10-20 | United States | ES_92897_SPC 34 130 *E 2**_10202020013927_5286319 | Com Gas Storage | 40 | 130 | lte155kBtuh
2367800 | A.O. Smith Corporation | Lochinvar | Polaris | SCN130-035 2** |  |  | Gas Storage | Gas | Power Direct Vent | 34 | 48.5 | 6.6 | 22 | 2 |  | 124.8 | 130 | 0.96 | 650 |  |  |  | 2017-02-15 | 2020-10-20 | United States | ES_92897_SCN130-035 2**_10202020013927_1356053 | Com Gas Storage | 40 | 130 | lte155kBtuh
2367802 | A.O. Smith Corporation | Lochinvar | Polaris | SWN130-035 2** |  |  | Gas Storage | Gas | Power Direct Vent | 34 | 48.5 | 6.6 | 22 | 2 |  | 124.8 | 130 | 0.96 | 650 |  |  |  | 2017-02-15 | 2020-10-20 | United States | ES_92897_SWN130-035 2**_10202020013926_6218752 | Com Gas Storage | 40 | 130 | lte155kBtuh
2367803 | A.O. Smith Corporation | A. O. Smith | Polaris | GSP 130 2** |  |  | Gas Storage | Gas,Propane | Power Direct Vent | 34 | 48.5 | 6.6 | 22 | 2 |  |  | 130 | 0.96 | 650 |  |  |  | 2017-02-15 | 2020-10-20 | United States | ES_92897_GSP 130 2**_10202020013926_244043 | Com Gas Storage | 40 | 130 | lte155kBtuh
2367804 | A.O. Smith Corporation | A. O. Smith | Polaris | BSS 130 2** |  |  | Gas Storage | Gas,Propane | Power Direct Vent | 34 | 48.5 | 6.6 | 22 | 2 |  |  | 130 | 0.96 | 650 |  |  |  | 2017-02-15 | 2020-10-20 | United States | ES_92897_BSS 130 2**_10202020013926_5971600 | Com Gas Storage | 40 | 130 | lte155kBtuh
2367805 | A.O. Smith Corporation | American | Polaris | PR 34 130 * 2** |  |  | Gas Storage | Gas,Propane | Power Direct Vent | 34 | 48.5 | 6.6 | 22 | 2 |  |  | 130 | 0.96 | 650 |  |  |  | 2017-02-15 | 2020-10-20 | United States | ES_92897_PR 34 130 * 2**_10202020013925_2286040 | Com Gas Storage | 40 | 130 | lte155kBtuh
2367806 | A.O. Smith Corporation | American | Polaris | PGC3 34 130 2NV 2** |  |  | Gas Storage | Gas,Propane | Power Direct Vent | 34 | 48.5 | 6.6 | 22 | 2 |  |  | 130 | 0.96 | 650 |  |  |  | 2017-02-15 | 2020-10-20 | United States | ES_92897_PGC3 34 130 2NV 2**_10202020013925_1844275 | Com Gas Storage | 40 | 130 | lte155kBtuh
2367807 | A.O. Smith Corporation | American | Polaris | PC 34 130 N 2** |  |  | Gas Storage | Gas,Propane | Power Direct Vent | 34 | 48.5 | 6.6 | 22 | 2 |  |  | 130 | 0.96 | 650 |  |  |  | 2017-02-15 | 2020-10-20 | United States | ES_92897_PC 34 130 N 2**_10202020013925_2623114 | Com Gas Storage | 40 | 130 | lte155kBtuh
2367808 | A.O. Smith Corporation | American | Polaris | PG10 50 175 3*V 2** |  |  | Gas Storage | Gas,Propane | Power Direct Vent | 50 | 63.7 | 6.6 | 22 | 3 |  |  | 175 | 0.96 | 800 |  |  |  | 2017-02-15 | 2020-10-20 | United States | ES_92897_PG10 50 175 3*V 2**_10202020013924_1285704 | Com Gas Storage | 50 | 175 | gt155kBtuh
2367809 | A.O. Smith Corporation | American | Polaris | PG10 50 130 2*V 2** |  |  | Gas Storage | Gas,Propane | Power Direct Vent | 50 | 62.3 | 6.6 | 22 | 2 |  |  | 130 | 0.95 | 750 |  |  |  | 2017-02-15 | 2020-10-20 | United States | ES_92897_PG10 50 130 2*V 2**_10202020013924_9374080 | Com Gas Storage | 50 | 130 | lte155kBtuh
2367810 | A.O. Smith Corporation | American | Polaris | PG10 34 130 2*V 2** |  |  | Gas Storage | Gas,Propane | Power Direct Vent | 34 | 48.5 | 6.6 | 22 | 2 |  |  | 130 | 0.96 | 650 |  |  |  | 2017-02-15 | 2020-10-20 | United States | ES_92897_PG10 34 130 2*V 2**_10202020013924_654608 | Com Gas Storage | 40 | 130 | lte155kBtuh
2367811 | A.O. Smith Corporation | State | Polaris | GHX 34 150 * 2** |  |  | Gas Storage-type Instantaneous | Gas,Propane | Power Direct Vent | 34 |  |  |  | 2 |  |  | 150 | 0.94 | 650 |  |  |  | 2017-02-15 | 2020-10-20 | United States | ES_92897_GHX 34 150 * 2**_10202020013922_9428131 | Com Gas Storage-type Instantaneous | 40 | 150 | lt200kBtuh
2367812 | A.O. Smith Corporation | State | Polaris | SPC 34 150 *E 2** |  |  | Gas Storage-type Instantaneous | Gas,Propane | Power Direct Vent | 34 |  |  |  | 2 |  |  | 150 | 0.94 | 650 |  |  |  | 2017-02-15 | 2020-10-20 | United States | ES_92897_SPC 34 150 *E 2**_10202020013921_6990403 | Com Gas Storage-type Instantaneous | 40 | 150 | lt200kBtuh
2367814 | A.O. Smith Corporation | Lochinvar | Polaris | SCN150-035 2** |  |  | Gas Storage-type Instantaneous | Gas | Power Direct Vent | 34 |  |  |  | 2 |  | 141 | 150 | 0.94 | 650 |  |  |  | 2017-02-15 | 2020-10-20 | United States | ES_92897_SCN150-035 2**_10202020013921_1774043 | Com Gas Storage-type Instantaneous | 40 | 150 | lt200kBtuh
2367816 | A.O. Smith Corporation | Lochinvar | Polaris | SWN150-035 2** |  |  | Gas Storage-type Instantaneous | Gas | Power Direct Vent | 34 |  |  |  | 2 |  | 141 | 150 | 0.94 | 650 |  |  |  | 2017-02-15 | 2020-10-20 | United States | ES_92897_SWN150-035 2**_10202020013920_5092923 | Com Gas Storage-type Instantaneous | 40 | 150 | lt200kBtuh
2367817 | A.O. Smith Corporation | A. O. Smith | Polaris | GSP 150 2** |  |  | Gas Storage-type Instantaneous | Gas,Propane | Power Direct Vent | 34 |  |  |  | 2 |  |  | 150 | 0.94 | 650 |  |  |  | 2017-02-15 | 2020-10-20 | United States | ES_92897_GSP 150 2**_10202020013920_4237640 | Com Gas Storage-type Instantaneous | 40 | 150 | lt200kBtuh
2367818 | A.O. Smith Corporation | A. O. Smith | Polaris | BSS 150 2** |  |  | Gas Storage-type Instantaneous | Gas,Propane | Power Direct Vent | 34 |  |  |  | 2 |  |  | 150 | 0.94 | 650 |  |  |  | 2017-02-15 | 2020-10-20 | United States | ES_92897_BSS 150 2**_10202020013920_6343652 | Com Gas Storage-type Instantaneous | 40 | 150 | lt200kBtuh
2367819 | A.O. Smith Corporation | American | Polaris | PR 34 150 * 2** |  |  | Gas Storage-type Instantaneous | Gas,Propane | Power Direct Vent | 34 |  |  |  | 2 |  |  | 150 | 0.94 | 650 |  |  |  | 2017-02-15 | 2020-10-20 | United States | ES_92897_PR 34 150 * 2**_10202020013920_7446831 | Com Gas Storage-type Instantaneous | 40 | 150 | lt200kBtuh
2367820 | A.O. Smith Corporation | American | Polaris | PGC3 34 150 2*V 2** |  |  | Gas Storage-type Instantaneous | Gas,Propane | Power Direct Vent | 34 |  |  |  | 2 |  |  | 150 | 0.94 | 650 |  |  |  | 2017-02-15 | 2020-10-20 | United States | ES_92897_PGC3 34 150 2*V 2**_10202020013920_6275693 | Com Gas Storage-type Instantaneous | 40 | 150 | lt200kBtuh
2367821 | A.O. Smith Corporation | American | Polaris | PC 34 150 * 2** |  |  | Gas Storage-type Instantaneous | Gas,Propane | Power Direct Vent | 34 |  |  |  | 2 |  |  | 150 | 0.94 | 650 |  |  |  | 2017-02-15 | 2020-10-20 | United States | ES_92897_PC 34 150 * 2**_10202020013919_4893906 | Com Gas Storage-type Instantaneous | 40 | 150 | lt200kBtuh
2367822 | A.O. Smith Corporation | American | Polaris | PG10 34 150 2*V 2** |  |  | Gas Storage-type Instantaneous | Gas,Propane | Power Direct Vent | 34 |  |  |  | 2 |  |  | 150 | 0.94 | 650 |  |  |  | 2017-02-15 | 2020-10-20 | United States | ES_92897_PG10 34 150 2*V 2**_10202020013919_9967277 | Com Gas Storage-type Instantaneous | 40 | 150 | lt200kBtuh
2334938 | Bradford White Corporation | Bradford White | EF120T500*N*3 | EF120T500*N*3 |  |  | Gas Storage-type Instantaneous | Gas | Power Vent | 119 |  |  |  | 4 | 6 | 469.906 | 499.9 | 0.94 | 1532 |  |  |  | 2019-02-11 | 2019-03-19 | United States, Canada | ES_92896_EF120T500*N*3_03192019214604_8923044 | Com Gas Storage-type Instantaneous | 120 | 499.9 | gte200kBtuh
2334939 | Bradford White Corporation | Bradford White | EF120T400*N*3 | EF120T400*N*3 |  |  | Gas Storage | Gas | Power Vent | 119 | 71 | 7.3 | 32 | 4 | 6 | 375.906 | 399.9 | 0.94 | 1427 |  |  |  | 2019-02-11 | 2019-03-19 | United States, Canada | ES_92896_EF120T400*N*3_03192019214703_3446467 | Com Gas Storage | 120 | 399.9 | gt155kBtuh
2334989 | LAARS Heating Systems Company | UHE | LUHE100T199E*N* | LUHE100T199E*N* |  |  | Gas Storage | Gas | Power Direct Vent | 100 | 69 | 5 | 26 | 3 | 4 | 197.901 | 199.9 | 0.99 | 1044 |  |  |  | 2019-03-01 | 2019-03-20 | United States | ES_1108210_LUHE100T199E*N*_03202019214630_9319471 | Com Gas Storage | 100 | 199.9 | gt155kBtuh
2336593 | Bradford White Corporation | Laars | LUHE100T399E*N* | LUHE100T399E*N* |  |  | Gas Storage | Gas | Power Direct Vent | 100 | 69 | 5 | 26 | 3 | 4 | 375.06 | 399 | 0.94 | 1075 |  |  |  | 2019-03-01 | 2019-04-11 | United States, Canada | ES_92896_LUHE100T399E*N*_04112019154205_1186063 | Com Gas Storage | 100 | 399 | gt155kBtuh
2336602 | Bradford White Corporation | Laars | LUHE120T500*N*3 | LUHE120T500*N*3 |  |  | Gas Storage-type Instantaneous | Gas | Power Vent | 119 |  |  |  | 4 | 6 | 469.906 | 499.9 | 0.94 | 1532 |  |  |  | 2019-03-01 | 2019-04-11 | United States, Canada | ES_92896_LUHE120T500*N*3_04112019155417_6611715 | Com Gas Storage-type Instantaneous | 120 | 499.9 | gte200kBtuh
2336607 | Bradford White Corporation | Laars | LUHE60T125E*N* | LUHE60T125E*N* |  |  | Gas Storage | Gas | Power Direct Vent | 60 | 48 | 5 | 26 | 3 | 4 | 120 | 125 | 0.96 | 824 |  |  |  | 2019-03-01 | 2019-04-11 | United States, Canada | ES_92896_LUHE60T125E*N*_04112019155818_8795011 | Com Gas Storage | 60 | 125 | lte155kBtuh
2336610 | Bradford White Corporation | Laars | LUHE120T400*N*3 | LUHE120T400*N*3 |  |  | Gas Storage | Gas | Power Vent | 119 | 71 | 7.3 | 32 | 4 | 6 | 375.906 | 399.9 | 0.94 | 1427 |  |  |  | 2019-03-01 | 2019-04-11 | United States, Canada | ES_92896_LUHE120T400*N*3_04112019155921_2773216 | Com Gas Storage | 120 | 399.9 | gt155kBtuh
2342281 | Watts Heating and Hot Water Solutions LLC | PVI Industries, Lync | 20 L 25A-RGC | 20 L 25A-RGC | ,20 L 25-RGC, |  | Gas Storage | Gas | Direct Vent | 25 | 67 | 81.5 | 12 | 4 | 4 | 191.04 | 199 | 0.96 | 482 |  |  |  | 2019-07-18 | 2019-07-31 | United States, Canada | ES_1129873_20 L 25A-RGC_07122019151929_3133355 | Com Gas Storage | 30 | 199 | gt155kBtuh
2352274 | Intellihot Inc | Intellihot | Neuron | iN501 | Neuron,iN401, |  | Gas Tankless | Gas,Propane | Direct Vent | 2 |  |  |  | 4 | 4 |  |  | 0.96 | 459 |  |  |  | 2019-06-05 | 2020-01-02 | United States, Canada | ES_1084851_iN501_01022020135425_1143808 | Com Gas Instantaneous | 2 | 0 | #N/A
2354156 | Intellihot Inc | Intellihot | iQ1501 | iQ1501 |  |  | Gas Tankless | Gas,Propane | Direct Vent | 6 |  |  |  | 6 |  |  | 1501 | 0.96 | 1010 |  |  |  | 2020-01-27 | 2020-01-27 | United States, Canada | ES_1084851_iQ1501_01272020155132_1423169 | Com Gas Instantaneous | 10 | 1501 | gte200kBtuh
2354357 | Bradford White Corporation | Bradford White | EF100T199E*N** | EF100T199E*N** |  |  | Gas Storage | Gas | Power Direct Vent | 100 | 77.1 | 5 | 28.3 | 4 | 3 | 193.903 | 199.9 | 0.97 | 1130 |  |  |  | 2019-11-20 | 2020-02-03 | United States, Canada | ES_92896_EF100T199E*N**_02042020035345_8160952 | Com Gas Storage | 100 | 199.9 | gt155kBtuh
2354358 | Bradford White Corporation | Bradford White | EF100T150E*N** | EF100T150E*N** |  |  | Gas Storage | Gas | Power Direct Vent | 100 | 77.1 | 5 | 28.3 | 4 | 3 | 145.5 | 150 | 0.97 | 1080 |  |  |  | 2019-11-20 | 2020-02-03 | United States, Canada | ES_92896_EF100T150E*N**_02042020035349_6253315 | Com Gas Storage | 100 | 150 | lte155kBtuh
2354359 | Bradford White Corporation | Bradford White | EF100T250E*N** | EF100T250E*N** |  |  | Gas Storage | Gas | Power Direct Vent | 100 | 77.1 | 5 | 28.3 | 4 | 3 | 240 | 250 | 0.96 | 1180 |  |  |  | 2019-11-20 | 2020-02-03 | United States, Canada | ES_92896_EF100T250E*N**_02042020035353_8598037 | Com Gas Storage | 100 | 250 | gt155kBtuh
2354377 | Bradford White Corporation | Laars | LUHE100T199E*N** | LUHE100T199E*N** |  |  | Gas Storage | Gas | Power Direct Vent | 100 | 77.1 | 5 | 28.3 | 4 | 3 | 193.903 | 199.9 | 0.97 | 1130 |  |  |  | 2019-11-20 | 2020-02-03 | United States, Canada | ES_92896_LUHE100T199E*N**_02042020041953_9562673 | Com Gas Storage | 100 | 199.9 | gt155kBtuh
2354378 | Bradford White Corporation | Laars | LUHE100T150E*N** | LUHE100T150E*N** |  |  | Gas Storage | Gas | Power Direct Vent | 100 | 77.1 | 5 | 28.3 | 4 | 3 | 145.5 | 150 | 0.97 | 1080 |  |  |  | 2019-11-20 | 2020-02-03 | United States, Canada | ES_92896_LUHE100T150E*N**_02042020041956_7861997 | Com Gas Storage | 100 | 150 | lte155kBtuh
2354379 | Bradford White Corporation | Laars | LUHE100T250E*N** | LUHE100T250E*N** |  |  | Gas Storage | Gas | Power Direct Vent | 100 | 77.1 | 5 | 28.3 | 4 | 3 | 240 | 250 | 0.96 | 1180 |  |  |  | 2019-11-20 | 2020-02-03 | United States, Canada | ES_92896_LUHE100T250E*N**_02042020041959_9541627 | Com Gas Storage | 100 | 250 | gt155kBtuh
2
2
2
2
2
2
2
2
2
2
2
2
2
2
2
2
2
2
2
2
2
2
2
2
2
2
2
2
2
2
2
2
2
2
2
2
2
2
2
2
2
2
2
2
2

## LOOKUPS
[24 empty] | MEASURE "ENERGYSTAR UEF" QUALIFIED (Y/N). SEE AHRI tab, column AR. MUST BE >= VALUE SHOWN AND <= VALUE SHOWN *(1+THRESHOLD TABLE VALUE ON SUMMARY TAB) |  |  |  |  | CODE MINIMUM EFFICIENCY (UEF) as given in Title 10 → Chapter II → Subchapter D → Part 430 → Subpart C → §430.32 | [8 empty] | Maximum Standby Loss (%/hr for elec, Btu/hr for gas) as given by Title 10 → Chapter II → Part 431 → Subpart C → §431.110 |  |  |  |  | Minimum thermal efficiency as given by Title 10 → Chapter II → Part 431 → Subpart C → §431.110 |  |  | Instantaneous INPUT range |  |  |  | Com Gas Storage | Com Gas Instantaneous | Com Gas Storage-type Instantaneous | Com Gas Hot Water Boiler
DRAW PATTERN CRITERIA |  |  | RES CODE MINIMUM EFFICIENCY (UEF) | [6 empty] | VOLUME BIN | COEFFICIENTS FOR THE ANALYTICAL UEF CONVERSION FACTOR | [18 empty] | Min Rated Volume | Max Rated Volume | Draw Pattern | c0 | c1 | equation form: c0 - (c1 x V_r) |  |  |  | Size | c0 | c1 | equation form |  | TE | SL | INPUT BIN range | kBTUH | Input Bin Name | 1 | lte155kBtuh | lt200kBtuh | lt200kBtuh
http://www.energy.ca.gov/title24/2016standards/documents/2016_water_heater_efficiency_guide.pdf |  |  | http://www.energy.ca.gov/title24/2016standards/documents/2016_water_heater_efficiency_guide.pdf |  |  | 0 <= FHR < 18 | 18 <= FHR < 51 | 51 <= FHR < 75 | FHR >= 75 |  | https://energy.gov/sites/prod/files/2016/12/f34/WH_Conversion_Final%20Rule.pdf, Table III.7 |  | https://energy.gov/sites/prod/files/2016/12/f34/WH_Conversion_Final%20Rule.pdf, Table III.7 |  | https://energy.gov/sites/prod/files/2016/12/f34/WH_Conversion_Final%20Rule.pdf, Table III.5 |  |  |  |  | https://energy.gov/sites/prod/files/2016/12/f34/WH_Conversion_Final%20Rule.pdf, Table III.9 |  |  |  |  | 55 |  |  |  | Gas Storage | 20 | 55 | VERY SMALL DRAW | 0.3456 | 0.002 | >=20 gal <= 55 gal |  |  | Elec Storage | All | 0.3 | 27 | c0 + c1/Vm (for electric); c0*Q + c1*Vr^0.5 (gas) | Elec Storage |  |  | < 76 | 1 | Small | 156 | gt155kBtuh | lt200kBtuh | lt200kBtuh
GPM | FHR | DRAW PATTERN | IDX | TYPE | VOLUME (GAL) | VERY SMALL DRAW | LOW DRAW | MEDIUM DRAW | HIGH DRAW | VOLUME BIN | GAS INSTANTANEOUS | A | ELEC INSTANTANEOUS | A | STORAGE | A | B | C | D | RESIDENTIAL DUTY | F | G | Tier | TYPE LOOKUP | <= 55 | >55 | N/A | Note | Gas Storage | 20 | 55 | LOW DRAW | 0.5982 | 0.0019 | >=20 gal <= 55 gal | 0.5412 |  | Gas Storage<=155 | <=155 | 0.00125 | 110 | <= 155 MBH | Com Gas Storagelte155kBtuh | 0.8 |  | 76 - 200 | 76 | Medium | 201 | gt155kBtuh | gte200kBtuh | gte200kBtuh
0 | 0 | VERY SMALL DRAW | Gas Instantaneous-2 | Gas Instantaneous | 2 | 0.8 | 0.81 | 0.81 | 0.81 | 2 | VERY SMALL DRAW | 0.026915 | VERY SMALL DRAW | 0.003819 | VERY SMALL DRAW | 0.25027 | 57.5 | 0.039864 | 67.5 | VERY SMALL DRAW | 0.82143 | 0.004352 | 1 | GAS STORAGEVERY SMALL DRAW1 | N/A | N/A | N/A | ES/CEE Tier 1 | Gas Storage | 20 | 55 | MEDIUM DRAW | 0.6483 | 0.0017 | >=20 gal <= 55 gal | 0.5633 |  | Gas Storage>155 | >155 | 0.00125 | 110 | > 155 MBH | Com Gas Storagegt155kBtuh | 0.8 |  | 201 - 2000 | 201 | Large | 300 | gt155kBtuh | gte200kBtuh | gte200kBtuh | gte300kBtuh | Com Gas Storagelte155kBtuh
1.7 | 18 | LOW DRAW | Gas Storage-30 | Gas Storage | 30 | 0.2856 | 0.5412 | 0.5973 | 0.653 | 10 | LOW DRAW | 0.010917 | LOW DRAW | 0.001549 | LOW DRAW | 0.06586 | 57.5 | 0.039864 | 67.5 | LOW DRAW | 0.82143 | 0.001145 | 1 | GAS STORAGELOW DRAW1 | N/A | N/A | N/A | ES/CEE Tier 1 | Gas Storage | 20 | 55 | HIGH DRAW | 0.692 | 0.0013 | >=20 gal <= 55 gal | 0.653 |  | Gas Instantaneous<10 | <10 | 0.00125 | 110 | < 10 gal | Com Gas Storage-Type Instantaneousgte200kBtuh | 0.8 |  | > 2000 | 2001 | Very Large | [5 empty] | Com Gas Storagegt155kBtuh
2.8 | 51 | MEDIUM DRAW | Gas Storage-40 | Gas Storage | 40 | 0.2656 | 0.5222 | 0.5803 | 0.64 | 30 | MEDIUM DRAW | 0.008362 | MEDIUM DRAW | 0.001186 | MEDIUM DRAW | 0.045503 | 57.5 | 0.039864 | 67.5 | MEDIUM DRAW | 0.82143 | 0.0007914 | 1 | GAS STORAGEMEDIUM DRAW1 | 0.64 | 0.78 | N/A | ES/CEE Tier 1 | Gas Storage | 55 | 100 | VERY SMALL DRAW | 0.647 | 0.0006 | > 55 gal <=100 gal |  |  | Gas Instantaneous>=10 | >=10 | 0.00125 | 110 | >= 10 gal | Com Gas Storage-Type Instantaneouslt200kBtuh | 0.8 | [9 empty] | Com Gas Storage-Type Instantaneousgte200kBtuh
4 | 75 | HIGH DRAW | Gas Storage-50 | Gas Storage | 50 | 0.2456 | 0.5032 | 0.5633 | 0.627 | 40 | HIGH DRAW | 0.005534 | HIGH DRAW | 0.000785 | HIGH DRAW | 0.029794 | 57.5 | 0.039864 | 67.5 | HIGH DRAW | 0.82143 | 0.0005181 | 1 | GAS STORAGEHIGH DRAW1 | 0.68 | 0.8 | N/A | ES/CEE Tier 1 | Gas Storage | 55 | 100 | LOW DRAW | 0.7689 | 0.0005 | > 55 gal <=100 gal | [7 empty] | Com Gas Instantaneousgte200kBtuh | 0.8 | [9 empty] | Com Gas Storage-Type Instantaneouslt200kBtuh
|  |  | Gas Storage-55 | Gas Storage | 55 | 0.2356 | 0.4937 | 0.5548 | 0.6205 | 50 | [12 empty] | 1 | GAS INSTANTANEOUS1 | N/A | N/A | 0.87 | ES/CEE Tier 1 | Gas Storage | 55 | 100 | MEDIUM DRAW | 0.7897 | 0.0004 | > 55 gal <=100 gal | [7 empty] | Com Gas Hot Water Boilergte300kBtuh | 0.8 | [9 empty] | Com Gas Instantaneousgte200kBtuh
|  |  | Gas Storage-60 | Gas Storage | 60 | 0.611 | 0.7389 | 0.7657 | 0.7892 | 55 | [12 empty] | 1 | GAS INSTANTANEOUSVERY SMALL DRAW1 | N/A | N/A | 0.87 | ES/CEE Tier 1 | Gas Storage | 55 | 100 | HIGH DRAW | 0.8072 | 0.0003 | > 55 gal <=100 gal | [18 empty] | Com Gas Hot Water Boilergte300kBtuh
|  |  | Gas Storage-75 | Gas Storage | 75 | 0.602 | 0.7314 | 0.7597 | 0.7847 | 60 | [12 empty] | 1 | GAS INSTANTANEOUSLOW DRAW1 | N/A | N/A | 0.87 | ES/CEE Tier 1 | Elec Storage | 20 | 55 | VERY SMALL DRAW | 0.8808 | 0.0008 | >= 20 gal <= 55 gal
|  |  | Gas Storage-80 | Gas Storage | 80 | 0.599 | 0.7289 | 0.7577 | 0.7832 | 75 | [12 empty] | 1 | GAS INSTANTANEOUSMEDIUM DRAW1 | N/A | N/A | 0.87 | ES/CEE Tier 1 | Elec Storage | 20 | 55 | LOW DRAW | 0.9254 | 0.0003 | >= 20 gal <= 55 gal
|  |  | Gas Storage-100 | Gas Storage | 100 | 0.587 | 0.7189 | 0.7497 | 0.7772 | 80 | [12 empty] | 1 | GAS INSTANTANEOUSHIGH DRAW1 | N/A | N/A | 0.87 | ES/CEE Tier 1 | Elec Storage | 20 | 55 | MEDIUM DRAW | 0.9307 | 0.0002 | >= 20 gal <= 55 gal
|  |  | Residential-Duty Gas Storage-30 | Residential-Duty Gas Storage | 30 | 0.2404 | 0.5002 | 0.5672 | 0.6327 | 100 | [12 empty] | 1 | RESIDENTIAL-DUTY GAS STORAGE1 | N/A | N/A | 0.8 | ES v.4.0 - Tier 1 | Elec Storage | 20 | 55 | HIGH DRAW | 0.9349 | 0.0001 | >= 20 gal <= 55 gal
|  |  | Residential-Duty Gas Storage-40 | Residential-Duty Gas Storage | 40 | 0.2314 | 0.4882 | 0.5562 | 0.6237 | 120 | [12 empty] | 1 | RESIDENTIAL-DUTY GAS STORAGEVERY SMALL DRAW1 | N/A | N/A | 0.8 | ES v.4.0 - Tier 1 | Elec Storage | 55 | 100 | VERY SMALL DRAW | 1.9236 | 0.0011 | > 55 gal <= 100 gal |  |  | UEF 24-hour draw volume
|  |  | Residential-Duty Gas Storage-50 | Residential-Duty Gas Storage | 50 | 0.2224 | 0.4762 | 0.5452 | 0.6147 | [13 empty] | 1 | RESIDENTIAL-DUTY GAS STORAGELOW DRAW1 | N/A | N/A | 0.8 | ES v.4.0 - Tier 1 | Elec Storage | 55 | 100 | LOW DRAW | 2.044 | 0.0011 | > 55 gal <= 100 gal |  |  | https://energy.gov/sites/prod/files/2016/12/f34/WH_Conversion_Final%20Rule.pdf, Pg 103, Para (C)
|  |  | Residential-Duty Gas Storage-55 | Residential-Duty Gas Storage | 55 | 0.2179 | 0.4702 | 0.5397 | 0.6102 | [13 empty] | 1 | RESIDENTIAL-DUTY GAS STORAGEMEDIUM DRAW1 | N/A | N/A | 0.8 | ES v.4.0 - Tier 1 | Elec Storage | 55 | 100 | MEDIUM DRAW | 2.1171 | 0.0011 | > 55 gal <= 100 gal |  |  | DRAW PATTERN | Daily Volume | Daily Btu
|  |  | Residential-Duty Gas Storage-60 | Residential-Duty Gas Storage | 60 | 0.2134 | 0.4642 | 0.5342 | 0.6057 | [13 empty] | 1 | RESIDENTIAL-DUTY GAS STORAGEHIGH DRAW1 | N/A | N/A | 0.8 | ES v.4.0 - Tier 1 | Elec Storage | 55 | 100 | HIGH DRAW | 2.2418 | 0.0011 | > 55 gal <= 100 gal |  |  | VERY SMALL DRAW | 10 | 5591.15
|  |  | Residential-Duty Gas Storage-75 | Residential-Duty Gas Storage | 75 | 0.1999 | 0.4462 | 0.5177 | 0.5922 | [13 empty] | 1 | ELEC STORAGE1 | N/A | N/A | N/A |  | Gas Instantaneous |  | 2 | VERY SMALL DRAW | 0.8 | 0 | < 2 gal and > 50,000 Btuh |  |  | LOW DRAW | 38 | 21246.37
|  |  | Residential-Duty Gas Storage-80 | Residential-Duty Gas Storage | 80 | 0.1954 | 0.4402 | 0.5122 | 0.5877 | [13 empty] | 1 | ELEC STORAGEVERY SMALL DRAW1 | N/A | N/A | N/A |  | Gas Instantaneous |  | 2 | LOW DRAW | 0.81 | 0 | < 2 gal and > 50,000 Btuh |  |  | MEDIUM DRAW | 55 | 30751.325
|  |  | Residential-Duty Gas Storage-100 | Residential-Duty Gas Storage | 100 | 0.1774 | 0.4162 | 0.4902 | 0.5697 | [13 empty] | 1 | ELEC STORAGELOW DRAW1 | N/A | N/A | N/A |  | Gas Instantaneous |  | 2 | MEDIUM DRAW | 0.81 | 0 | < 2 gal and > 50,000 Btuh |  |  | HIGH DRAW | 84 | 46965.66
|  |  | Residential-Duty Gas Storage-120 | Residential-Duty Gas Storage | 120 | 0.1594 | 0.3922 | 0.4682 | 0.5517 | [13 empty] | 1 | ELEC STORAGEMEDIUM DRAW1 | N/A | N/A | N/A |  | Gas Instantaneous |  | 2 | HIGH DRAW | 0.81 | 0 | < 2 gal and > 50,000 Btuh
|  |  | Elec Instantaneous-2 | Elec Instantaneous | 2 | 0.91 | 0.91 | 0.91 | 0.92 | [13 empty] | 1 | ELEC STORAGEHIGH DRAW1 | N/A | N/A | N/A |  | Elec Instantaneous |  | 2 | VERY SMALL DRAW | 0.91 | 0 | < 2 gal
|  |  | Residential-Duty Elec Instantaneous-2 | Residential-Duty Elec Instantaneous | 2 | 0.8 | 0.8 | 0.8 | 0.8 | [13 empty] | 1 | ELEC INSTANTANEOUSVERY SMALL DRAW1 | N/A | N/A | N/A |  | Elec Instantaneous |  | 2 | LOW DRAW | 0.91 | 0 | < 2 gal |  |  | UEF test conditions (https://www.law.cornell.edu/cfr/text/10/appendix-E_to_subpart_B_of_part_430)
|  |  | Elec Storage-30 | Elec Storage | 30 | 0.86 | 0.92 | 0.92 | 0.93 | [13 empty] | 1 | ELEC INSTANTANEOUSLOW DRAW1 | N/A | N/A | N/A |  | Elec Instantaneous |  | 2 | MEDIUM DRAW | 0.91 | 0 | < 2 gal |  |  | Median ambient temperature | 67.5 | F
|  |  | Elec Storage-40 | Elec Storage | 40 | 0.85 | 0.91 | 0.92 | 0.93 | [13 empty] | 1 | ELEC INSTANTANEOUSMEDIUM DRAW1 | N/A | N/A | N/A |  | Elec Instantaneous |  | 2 | HIGH DRAW | 0.92 | 0 | < 2 gal |  |  | Set point / outlet temperature | 125 | F
|  |  | Elec Storage-50 | Elec Storage | 50 | 0.84 | 0.91 | 0.92 | 0.93 | [13 empty] | 1 | ELEC INSTANTANEOUSHIGH DRAW1 | N/A | N/A | N/A |  | Residential-Duty Elec Instantaneous |  | 2 | VERY SMALL DRAW | 0.8 | 0 | <= 2gal; > 12 kW and <= 58.6 kW |  |  | Supply water temperature | 58 | F
|  |  | Elec Storage-55 | Elec Storage | 55 | 0.84 | 0.91 | 0.92 | 0.93 | [13 empty] | 1 | RESIDENTIAL-DUTY ELEC INSTANTANEOUSVERY SMALL DRAW1 | N/A | N/A | N/A |  | Residential-Duty Elec Instantaneous |  | 2 | LOW DRAW | 0.8 | 0 | <= 2gal; > 12 kW and <= 58.6 kW
|  |  | Elec Storage-60 | Elec Storage | 60 | 1.86 | 1.98 | 2.05 | 2.18 | [13 empty] | 1 | RESIDENTIAL-DUTY ELEC INSTANTANEOUSLOW DRAW1 | N/A | N/A | N/A |  | Residential-Duty Elec Instantaneous |  | 2 | MEDIUM DRAW | 0.8 | 0 | <= 2gal; > 12 kW and <= 58.6 kW
|  |  | Elec Storage-75 | Elec Storage | 75 | 1.84 | 1.96 | 2.03 | 2.16 | [13 empty] | 1 | RESIDENTIAL-DUTY ELEC INSTANTANEOUSMEDIUM DRAW1 | N/A | N/A | N/A |  | Residential-Duty Elec Instantaneous |  | 2 | HIGH DRAW | 0.8 | 0 | <= 2gal; > 12 kW and <= 58.6 kW
|  |  | Elec Storage-80 | Elec Storage | 80 | 1.84 | 1.96 | 2.03 | 2.15 | [13 empty] | 1 | RESIDENTIAL-DUTY ELEC INSTANTANEOUSHIGH DRAW1 | N/A | N/A | N/A |  | Residential-Duty Gas Storage |  | 120 | VERY SMALL DRAW | 0.2674 | 0.0009 | > 75 kBtuh and <= 105 kBtuh; <= 120 gal
|  |  | Elec Storage-100 | Elec Storage | 100 | 1.8136 | 1.934 | 2.0071 | 2.1318 | [13 empty] | 1 | HEAT PUMP1 | 3.3 | 3.3 | N/A | ES v.4.0 - Tier 1 | Residential-Duty Gas Storage |  | 120 | LOW DRAW | 0.5362 | 0.0012 | > 75 kBtuh and <= 105 kBtuh; <= 120 gal
|  |  | Elec Storage-120 | Elec Storage | 120 | 1.7916 | 1.912 | 1.9851 | 2.1098 | [13 empty] | 1 | HEAT PUMPVERY SMALL DRAW1 | 3.3 | 3.3 | N/A | ES v.4.0 - Tier 1 | Residential-Duty Gas Storage |  | 120 | MEDIUM DRAW | 0.6002 | 0.0011 | > 75 kBtuh and <= 105 kBtuh; <= 120 gal
|  |  | Heat Pump-40 | Heat Pump | 40 | 3 | 3 | 3 | 3 | [13 empty] | 1 | HEAT PUMPLOW DRAW1 | 3.3 | 3.3 | N/A | ES v.4.0 - Tier 1 | Residential-Duty Gas Storage |  | 120 | HIGH DRAW | 0.6597 | 0.0009 | > 75 kBtuh and <= 105 kBtuh; <= 120 gal
|  |  | Heat Pump-50 | Heat Pump | 50 | 3 | 3 | 3 | 3 | [13 empty] | 1 | HEAT PUMPMEDIUM DRAW1 | 3.3 | 3.3 | N/A | ES v.4.0 - Tier 1
|  |  | Heat Pump-75 | Heat Pump | 75 | 3 | 3 | 3 | 3 | [13 empty] | 1 | HEAT PUMPHIGH DRAW1 | 3.3 | 3.3 | N/A | ES v.4.0 - Tier 1 | [8 empty] | Res.Duty Commercial Water Heaters
|  |  | Heat Pump-80 | Heat Pump | 80 | 3 | 3 | 3 | 3 | [13 empty] | 2 | GAS INSTANTANEOUS2 | N/A | N/A | 0.92 | CEE Tier 2
|  |  | Heat Pump-100 | Heat Pump | 100 | 3 | 3 | 3 | 3 | [13 empty] | 2 | GAS INSTANTANEOUSVERY SMALL DRAW2 | N/A | N/A | 0.92 | CEE Tier 2
|  |  | Heat Pump-120 | Heat Pump | 120 | 3 | 3 | 3 | 3 | [13 empty] | 2 | GAS INSTANTANEOUSLOW DRAW2 | N/A | N/A | 0.92 | CEE Tier 2
[23 empty] | 2 | GAS INSTANTANEOUSMEDIUM DRAW2 | N/A | N/A | 0.92 | CEE Tier 2
[23 empty] | 2 | GAS INSTANTANEOUSHIGH DRAW2 | N/A | N/A | 0.92 | CEE Tier 2
[23 empty] | 3 | GAS INSTANTANEOUS3 | N/A | N/A | 0.95 | DEER Tier 3
[23 empty] | 3 | GAS INSTANTANEOUSVERY SMALL DRAW3 | N/A | N/A | 0.95 | DEER Tier 3
[23 empty] | 3 | GAS INSTANTANEOUSLOW DRAW3 | N/A | N/A | 0.95 | DEER Tier 3
[23 empty] | 3 | GAS INSTANTANEOUSMEDIUM DRAW3 | N/A | N/A | 0.95 | DEER Tier 3
[23 empty] | 3 | GAS INSTANTANEOUSHIGH DRAW3 | N/A | N/A | 0.95 | DEER Tier 3
[23 empty] | 2 | HEAT PUMP2 | 3.5 | 3.5 | N/A | DEER Tier 2
[23 empty] | 2 | HEAT PUMPVERY SMALL DRAW2 | 3.5 | 3.5 | N/A | DEER Tier 2
[23 empty] | 2 | HEAT PUMPLOW DRAW2 | 3.5 | 3.5 | N/A | DEER Tier 2
[23 empty] | 2 | HEAT PUMPMEDIUM DRAW2 | 3.5 | 3.5 | N/A | DEER Tier 2
[23 empty] | 2 | HEAT PUMPHIGH DRAW2 | 3.5 | 3.5 | N/A | DEER Tier 2
[23 empty] | 3 | HEAT PUMP3 | 3.75 | 3.75 | N/A | CEE Tier Advanced
[23 empty] | 3 | HEAT PUMPVERY SMALL DRAW3 | 3.75 | 3.75 | N/A | CEE Tier Advanced
[23 empty] | 3 | HEAT PUMPLOW DRAW3 | 3.75 | 3.75 | N/A | CEE Tier Advanced
[23 empty] | 3 | HEAT PUMPMEDIUM DRAW3 | 3.75 | 3.75 | N/A | CEE Tier Advanced
[23 empty] | 3 | HEAT PUMPHIGH DRAW3 | 3.75 | 3.75 | N/A | CEE Tier Advanced
[23 empty] | 2 | GAS STORAGE2 | N/A | N/A | N/A | CEE Tier 2
[23 empty] | 2 | GAS STORAGEVERY SMALL DRAW2 | N/A | N/A | N/A | CEE Tier 2
[23 empty] | 2 | GAS STORAGELOW DRAW2 | N/A | N/A | N/A | CEE Tier 2
[23 empty] | 2 | GAS STORAGEMEDIUM DRAW2 | N/A | N/A | N/A | CEE Tier 2
[23 empty] | 2 | GAS STORAGEHIGH DRAW2 | 0.78 | N/A | N/A | CEE Tier 2
[23 empty] | 2 | RESIDENTIAL-DUTY GAS STORAGE2 | N/A | N/A | N/A | DEER Tier 2
[23 empty] | 2 | RESIDENTIAL-DUTY GAS STORAGEVERY SMALL DRAW2 |  |  |  | DEER Tier 2
[23 empty] | 2 | RESIDENTIAL-DUTY GAS STORAGELOW DRAW2 |  |  |  | DEER Tier 2
[23 empty] | 2 | RESIDENTIAL-DUTY GAS STORAGEMEDIUM DRAW2 |  |  |  | DEER Tier 2
[23 empty] | 2 | RESIDENTIAL-DUTY GAS STORAGEHIGH DRAW2 |  |  |  | DEER Tier 2
[23 empty] | 1 | COM GAS STORAGE1 | N/A | N/A | 0.9
[23 empty] | 1 | COM GAS INSTANTANEOUS1 | N/A | N/A | 0.84
[23 empty] | 1 | COM GAS STORAGE-TYPE INSTANTANEOUS1 | N/A | N/A | 0.84
[23 empty] | 1 | COM GAS HOT WATER BOILER1 | N/A | N/A | 0.84
[23 empty] | 2 | COM GAS STORAGE2 | N/A | N/A | 0.96
[23 empty] | 2 | COM GAS INSTANTANEOUS2 | N/A | N/A | 0.9
[23 empty] | 2 | COM GAS STORAGE-TYPE INSTANTANEOUS2 | N/A | N/A | 0.9
[23 empty] | 2 | COM GAS HOT WATER BOILER2 | N/A | N/A | 0.9
[23 empty] | 3 | COM GAS STORAGE3 | N/A | N/A | N/A
[23 empty] | 3 | COM GAS INSTANTANEOUS3 | N/A | N/A | 0.96
[23 empty] | 3 | COM GAS STORAGE-TYPE INSTANTANEOUS3 | N/A | N/A | 0.96
[23 empty] | 3 | COM GAS HOT WATER BOILER3 | N/A | N/A | 0.96
CFR Title 10 431.110
GAS STORAGE
GAS STORAGEVERY SMALL DRAW
GAS STORAGELOW DRAW
GAS STORAGEMEDIUM DRAW
GAS STORAGEHIGH DRAW
GAS INSTANTANEOUS
GAS INSTANTANEOUSVERY SMALL DRAW
GAS INSTANTANEOUSLOW DRAW
GAS INSTANTANEOUSMEDIUM DRAW
GAS INSTANTANEOUSHIGH DRAW
RESIDENTIAL-DUTY GAS STORAGE
RESIDENTIAL-DUTY GAS STORAGEVERY SMALL DRAW
RESIDENTIAL-DUTY GAS STORAGELOW DRAW
RESIDENTIAL-DUTY GAS STORAGEMEDIUM DRAW
RESIDENTIAL-DUTY GAS STORAGEHIGH DRAW
ELEC STORAGE
ELEC STORAGEVERY SMALL DRAW
ELEC STORAGELOW DRAW
ELEC STORAGEMEDIUM DRAW
ELEC STORAGEHIGH DRAW
ELEC INSTANTANEOUSVERY SMALL DRAW
ELEC INSTANTANEOUSLOW DRAW
ELEC INSTANTANEOUSMEDIUM DRAW
ELEC INSTANTANEOUSHIGH DRAW
RESIDENTIAL-DUTY ELEC INSTANTANEOUSVERY SMALL DRAW
RESIDENTIAL-DUTY ELEC INSTANTANEOUSLOW DRAW
RESIDENTIAL-DUTY ELEC INSTANTANEOUSMEDIUM DRAW
RESIDENTIAL-DUTY ELEC INSTANTANEOUSHIGH DRAW
HEAT PUMP
HEAT PUMPVERY SMALL DRAW
HEAT PUMPLOW DRAW
HEAT PUMPMEDIUM DRAW
HEAT PUMPHIGH DRAW
COM GAS STORAGE
COM GAS INSTANTANEOUS
COM GAS STORAGE-TYPE INSTANTANEOUS
COM GAS HOT WATER BOILER
Note on I35: Williams, Christopher: Arbitrary as there is no code min for HPs. 3.30 is ES minimum
Note on BH15: Williams, Christopher: Added in order to convert UEF to EF to COP

## ES Criteria
https://www.energystar.gov/products/water_heaters/residential_water_heaters_key_product_criteria |  |  |  |  | https://www.energystar.gov/products/water_heaters/commercial_water_heaters/key_product_criteria
effective date: 4/16/2015 |  |  |  |  | effective date 10/1/2018 | [5 empty] | v.4.0 - Res
v.3.2 |  |  |  |  | v.2 | [5 empty] | Storage definition
Meets EF, standby loss and/or TE OR UEF criteria |  |  |  |  | Meets TE, standby loss or COP | [5 empty] | input = 75 kBtuh or less
> 1 gallon per 4 kBtuh input
HP max = 24A @ 250V
Storage Water Heaters <= 75,000 Btu/h and containing > 1 gal per 4,000 Btu/h input |  |  |  |  | Gas-fired storage > 75,000 Btu/h and < 4,000 Btu/h per gallon of stored water
Heat Pump Water Heaters with storage max current of 24A @ 250V or less |  |  | 6 | kW | Gas-fired instantaneous > 200,000 Btu/h and >= 4,000 Btu/h per gallon of stored water | [5 empty] | Instantaneous definition
Instantaneous Water Heaters contain <= 1 gal per 4,000 Btu/h and less than 200,000 Btu/h |  |  |  |  | Gas-fired storage -type instantaneous storage volume >= 10 gallons | [5 empty] | <=1 gallon per 4 kBtuh input
High Capacity Storage Water Heaters > 75,000 Btu/h <= 105,000 Btu/h |  |  |  |  | Electric Heat Pump > 12 kW rated electric input | [5 empty] | input <= 200 kBtuh
Gas Storage res-duty definition
Deliver <= 180 degF water and storage <= 120 gallons
Electric Storage Water Heaters |  |  |  |  | Gas-fired Storage Water Heaters and Gas-Fired Storage Typ Instantaneous | [5 empty] | input > 75 kBtuh and < = 105 kBtuh
| <= 55 gal | > 55 gal | [8 empty] | > 1 gallon per 4 kBtuh
EF >= | 2 | 2.2 |  |  | TE >= | 0.94
FHR >= | 50 | 50 |  |  | SL <= | 0.84 x [(Input rate / 800) + 110 x (Volume)^0.5] | 0.84 | 0.00125 | 110 | 0.5
-----------OR-----------
UEF >= | 2 | 2.2
FHR >= | 45 | 45
Gas Storage Water Heaters |  |  |  |  | Gas-fired instantaneous
| <= 55 gal | > 55 gal
EF >= | 0.67 | 0.77 |  |  | TE >= | 0.94
FHR >= | 67 | 67
------------OR------------
MEDIUM DRAW UEF>= | 0.64 | 0.78
HIGH DRAW UEF >= | 0.68 | 0.8 |  |  | Electric Heat Pump
FHR >= | 67 | 67
[5 empty] | COP >= | 3
Gas Instantaneous Water Heaters
EF >= | 0.9
GPM >= | 2.5
-------------OR------------
UEF >= | 0.87
Max GPM >= | 2.9
High Capacity Storage Gas WH
TE >= | 0.9
Standby loss Btu/h<= | 1889*(TE-0.73)
---------------OR--------------
UEF >= | 0.8